CANOVANAS | 2022-07-21 09:57 | 2022-07-21 09:58 | 2580 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTORCARGA POR EL 2403-02 | R22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 2580 | keep | 0 | Jul | 2022 | 0.0017572 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2022-07-21 09:57 | 2022-07-21 09:58 | 500 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 2403-01 | R22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 500 | keep | 0 | Jul | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-07-21 09:58 | 2022-07-21 10:01 | 343 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 1620-01 Y LLEVA 85% DEL 1336-10. SE CERRO POR SCADA | S22072100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-21 | 1029 | keep | 0 | Jul | 2022 | 0.00070085 | 0.00023362 | Momentary | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2022-07-21 09:58 | 2022-07-21 10:01 | 36 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 1620-01 Y LLEVA 85% DEL 1336-10. SE CERRO POR SCADA | S22072100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-21 | 108 | keep | 0 | Jul | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-07-21 09:58 | 2022-07-21 10:01 | 1073 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 1620-01 Y LLEVA 85% DEL 1336-10. SE CERRO POR SCADA | S22072100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-21 | 3219 | keep | 0 | Jul | 2022 | 0.0021924 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
CANOVANAS | 2022-07-21 09:58 | 2022-07-21 10:01 | 4188 | 0:03 | T | TRANSFORMADOR AVERIADO | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | R22072100017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3 | 2022-07-21 | 12564 | keep | 0 | Jul | 2022 | 0.0085573 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
ARECIBO | 2022-07-21 09:58 | 2022-07-21 16:19 | 10 | 6:21 | P | ANIMAL | 1 X 10 EN TRASFORMADOR POR AVE | A22072100027 | New_Event | Animals | Include | Include | Wildlife | 381 | 2022-07-21 | 3810 | keep | 0 | Jul | 2022 | 0.002595 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-21 09:59 | 2022-07-21 11:10 | 271 | 1:11 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO Y SE CERRO POR SCADA LUEGO DE LAS LLUVIAS Y VIENTOS PASAR | S22072100096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2022-07-21 | 19241 | keep | 0 | Jul | 2022 | 0.013105 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2022-07-21 10:01 | 2022-07-21 12:38 | 10 | 2:37 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR Y SE REPARO BUSHING SECUNDARIO | R22072100040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 157 | 2022-07-21 | 1570 | keep | 0 | Jul | 2022 | 0.0010693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-21 10:02 | 2022-07-21 13:55 | 200 | 3:53 | P | DESGANCHE | SE SECCIONALIZO PARA REPARAR/LEVANTAR CONDUCTOR PRIMARIO DEL SUELO POR BAMBUAS | B22072100009 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-07-21 | 46600 | keep | 0 | Jul | 2022 | 0.031739 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-07-21 10:05 | 2022-07-21 13:48 | 60 | 3:43 | P | DESGANCHE | 1X65 Y 1X40 EN 2 CORTES DE LINEA | R22072100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-07-21 | 13380 | keep | 0 | Jul | 2022 | 0.0091131 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-21 10:06 | 2022-07-21 10:19 | 1483 | 0:13 | P | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y LLEVA PARTE DEL 1204-05 CERRADO POR SCADA | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-07-21 | 19279 | keep | 0 | Jul | 2022 | 0.013131 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-07-21 10:06 | 2022-07-21 10:19 | 2042 | 0:13 | P | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y LLEVA PARTE DEL 1204-05 CERRADO POR SCADA | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-07-21 | 26546 | keep | 0 | Jul | 2022 | 0.01808 | 0.0013908 | Sustained | FALSE | FALSE | Not_TMED_Event | 2042
SAN JUAN | 2022-07-21 10:06 | 2022-07-21 10:19 | 5290 | 0:13 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y LLEVA PARTE DEL 1204-05 CERRADO POR SCADA | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-07-21 | 68770 | keep | 0 | Jul | 2022 | 0.046839 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
HUMACAO | 2022-07-21 10:09 | 2022-07-21 13:24 | 300 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | 3 X 100 Y 1 X 40 EN C/L SE REPARO PUENTE A CORTE DE LINEA | C22072100061 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2022-07-21 | 58500 | keep | 0 | Jul | 2022 | 0.039844 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-07-21 10:13 | 2022-07-21 10:58 | 1825 | 0:45 | T | NO SE REPORTO CAUSA | DISPARO SE RESETEARON BANDERAS Y SE VERIFICO PERSONAL FUERA | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-07-21 | 82125 | keep | 0 | Jul | 2022 | 0.055935 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-07-21 10:13 | 2022-07-21 10:58 | 4398 | 0:45 | T | NO SE REPORTO CAUSA | DISPARO SE RESETEARON BANDERAS Y SE VERIFICO PERSONAL FUERA | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-07-21 | 197910 | keep | 0 | Jul | 2022 | 0.1348 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2022-07-21 10:16 | 2022-07-21 11:41 | 2203 | 1:25 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA 50% EN SERVICIO | S22072100131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-07-21 | 187255 | keep | 0 | Jul | 2022 | 0.12754 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
BARRANQUITAS | 2022-07-21 10:19 | 2022-07-21 10:38 | 1131 | 0:19 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE VERIFICO PERSONAL FUERA. | C22072100064 | New_Event | Primary Wire Break | Include | Include | Equipment | 19 | 2022-07-21 | 21489 | keep | 0 | Jul | 2022 | 0.014636 | 0.00077032 | Sustained | FALSE | FALSE | Not_TMED_Event | 1131
ARECIBO | 2022-07-21 10:22 | 2022-07-21 13:12 | 8 | 2:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE TRANSFORMADOR AVERIADA | A22072100031 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2022-07-21 | 1360 | keep | 0 | Jul | 2022 | 0.00092629 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-07-21 10:24 | 2022-07-21 11:43 | 10 | 1:19 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22072100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-07-21 | 790 | keep | 0 | Jul | 2022 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-07-21 10:24 | 2022-07-21 14:57 | 20 | 4:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRMARIO ABIERTO | M22072100071 | New_Event | Primary Wire Break | Include | Include | Equipment | 273 | 2022-07-21 | 5460 | keep | 0 | Jul | 2022 | 0.0037188 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-07-21 10:27 | 2022-07-21 15:35 | 20 | 5:08 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L Y 1 X 50 EN C/L SE RETEZO LINEA | R22072100027 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 308 | 2022-07-21 | 6160 | keep | 0 | Jul | 2022 | 0.0041955 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-07-21 10:27 | 2022-07-21 12:50 | 10 | 2:23 | P | SECUNDARIA/OTROS | SE REMPLAZO PEDESTAL CON BARRAS SECUNDARIAS | P22072100063 | New_Event |  |  |  |  | 143 | 2022-07-21 | 1430 | keep | 0 | Jul | 2022 | 0.00097397 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-07-21 10:31 | 2022-07-21 10:32 | 1860 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | S22072100184 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-07-21 | 1860 | keep | 0 | Jul | 2022 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
HUMACAO | 2022-07-21 10:33 | 2022-07-21 16:14 | 24 | 5:41 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR | C22072100071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 341 | 2022-07-21 | 8184 | keep | 0 | Jul | 2022 | 0.0055741 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2022-07-21 10:34 | 2022-07-21 12:12 | 10 | 1:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-07-21 | 980 | keep | 0 | Jul | 2022 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-21 10:36 | 2022-07-21 10:37 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22072100099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 4533 | keep | 0 | Jul | 2022 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
SAN JUAN | 2022-07-21 10:44 | 2022-07-21 10:48 | 858 | 0:04 | P | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | S22072100215 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-07-21 | 3432 | keep | 0 | Jul | 2022 | 0.0023375 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-07-21 10:44 | 2022-07-21 10:48 | 1483 | 0:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1303-02 SE CERRO POR CONTROL 30% DE LA CARGA POR EL 1303-02 MAL TIEMPO LLUVIAS | S22072100215 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2022-07-21 | 5932 | keep | 0 | Jul | 2022 | 0.0040403 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-07-21 10:44 | 2022-07-21 10:48 | 400 | 0:04 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL | S22072100215 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 4 | 2022-07-21 | 1600 | keep | 0 | Jul | 2022 | 0.0010898 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-07-21 10:44 | 2022-07-21 10:48 | 2435 | 0:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL MAL TIEMPO LLUVIAS | S22072100215 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2022-07-21 | 9740 | keep | 0 | Jul | 2022 | 0.0066339 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-21 10:45 | 2022-07-21 13:14 | 3 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | B22072100114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-07-21 | 447 | keep | 0 | Jul | 2022 | 0.00030445 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-07-21 10:47 | 2022-07-21 17:44 | 1 | 6:57 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | R22072100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2022-07-21 | 417 | keep | 0 | Jul | 2022 | 0.00028402 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-21 10:53 | 2022-07-21 17:44 | 723 | 6:51 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE BKR 1711-02 SECCIONALIZO PARA REEMPLAZO DE MACHETES QUEMADOS Y SE CERRO PUENTE PRIMARIO Y SE DEJO FUERA EL SU#11,SU-21 Y SU-19 POR AVERIA. EL BKR 1711-02 ESTA LLEVANDO SOLO LA CARGA DEL 1711-05 | B22072100031 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 411 | 2022-07-21 | 297153 | keep | 0 | Jul | 2022 | 0.20239 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-07-21 10:53 | 2022-07-21 16:08 | 1976 | 5:15 | T | TERMINACION SOTERRADA AVERIADA | DISPARO DE BKR SECCIONALIZO PARA REEMPLAZO DE MACHETES QUEMADOS Y SE CERRO PUENTE PRIMARIO Y SE DEJO FUERA EL SU#11 POR AVERIA. SE TRANSFIRIO LA CARGA AL 1716-03. LLEVABA CARGA DEL 1711-05 | B22072100031 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 315 | 2022-07-21 | 622440 | keep | 0 | Jul | 2022 | 0.42394 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
YAUCO | 2022-07-21 10:53 | 2022-07-21 11:45 | 40 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22072100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-07-21 | 2080 | keep | 0 | Jul | 2022 | 0.0014167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-21 10:55 | 2022-07-21 10:57 | 1483 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y LLEVA PARTE DEL 1204-05 CERRADO POR SCADA | S22072100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 2966 | keep | 0 | Jul | 2022 | 0.0020201 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-21 10:55 | 2022-07-21 10:57 | 1500 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL | S22072100000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-07-21 | 3000 | keep | 0 | Jul | 2022 | 0.0020433 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-07-21 10:55 | 2022-07-21 10:57 | 5290 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA 30% DEL 1204-04 Y LLEVA PARTE DEL 1204-05 CERRADO POR SCADA | S22072100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 10580 | keep | 0 | Jul | 2022 | 0.007206 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-21 11:00 | 2022-07-21 11:02 | 207 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL | S22072100000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-07-21 | 414 | keep | 0 | Jul | 2022 | 0.00028197 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
PONCE | 2022-07-21 11:00 | 2022-07-21 12:14 | 8 | 1:14 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 50 KVA A 2.4KV CON PERDIDA DE ACEITE POR OTRO IGUAL CAPACIDAD Y VOLTAJE | P22072100084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 74 | 2022-07-21 | 592 | keep | 0 | Jul | 2022 | 0.00040321 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-07-21 11:02 | 2022-07-21 13:00 | 75 | 1:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | B22072100142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-07-21 | 8850 | keep | 0 | Jul | 2022 | 0.0060277 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-07-21 11:03 | 2022-07-21 17:42 | 20 | 6:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR FUERTES LLUVIAS | A22072100035 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 399 | 2022-07-21 | 7980 | keep | 0 | Jul | 2022 | 0.0054351 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-21 11:04 | 2022-07-21 11:06 | 858 | 0:02 | P | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | S22072100215 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2022-07-21 | 1716 | keep | 0 | Jul | 2022 | 0.0011688 | 0.00058438 | Momentary | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-07-21 11:04 | 2022-07-21 11:06 | 1483 | 0:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL 30% DE SU CARGA POR EL 1303-02 MAL TIEMPO LLUVIAS | S22072100000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2022-07-21 | 2966 | keep | 0 | Jul | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-07-21 11:04 | 2022-07-21 11:06 | 400 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL | S22072100215 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-07-21 | 800 | keep | 0 | Jul | 2022 | 0.00054488 | 0.00027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-07-21 11:04 | 2022-07-21 11:06 | 2435 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE CERRO POR CONTROL MAL TIEMPO LLUVIAS | S22072100215 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2022-07-21 | 4870 | keep | 0 | Jul | 2022 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-21 11:04 | 2022-07-21 11:06 | 450 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | B22072100159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 900 | keep | 0 | Jul | 2022 | 0.00061299 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
SAN JUAN | 2022-07-21 11:05 | 2022-07-21 11:07 | 1825 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE RESETEARON BANDERAS Y SE VERIFICO PERSONAL FUERA | S22072100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 3650 | keep | 0 | Jul | 2022 | 0.002486 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-21 11:05 | 2022-07-21 11:07 | 4398 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE RESETEARON BANDERAS Y SE VERIFICO PERSONAL FUERA | S22072100000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 8796 | keep | 0 | Jul | 2022 | 0.0059909 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-21 11:13 | 2022-07-21 11:16 | 186 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - LLEVA LA CARGA DEL 1711-04 | B22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-21 | 558 | keep | 0 | Jul | 2022 | 0.00038005 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
VEGA BAJA | 2022-07-21 11:16 | 2022-07-21 19:13 | 130 | 7:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22072100037 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 477 | 2022-07-21 | 62010 | keep | 0 | Jul | 2022 | 0.042235 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
VEGA BAJA | 2022-07-21 11:17 | 2022-07-21 14:27 | 60 | 3:10 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | B22072100205 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2022-07-21 | 11400 | keep | 0 | Jul | 2022 | 0.0077645 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-21 11:17 | 2022-07-21 11:18 | 308 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | B22072100000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-07-21 | 308 | keep | 0 | Jul | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-07-21 11:17 | 2022-07-21 11:18 | 1397 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 1397 | keep | 0 | Jul | 2022 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
BAYAMON | 2022-07-21 11:17 | 2022-07-21 11:18 | 2324 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 2324 | keep | 0 | Jul | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
BAYAMON | 2022-07-21 11:17 | 2022-07-21 13:20 | 12 | 2:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 37.5KVA | B22072100113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 123 | 2022-07-21 | 1476 | keep | 0 | Jul | 2022 | 0.0010053 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-21 11:18 | 2022-07-21 12:24 | 200 | 1:06 | P | DESCONECTIVO DEFECTUOSO | SE ENCONTRO 2 MACHETES QUEMADOS EN LA SUBESTACION | B22072100000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 66 | 2022-07-21 | 13200 | keep | 0 | Jul | 2022 | 0.0089905 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-07-21 11:22 | 2022-07-21 16:59 | 3 | 5:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M22072100089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 337 | 2022-07-21 | 1011 | keep | 0 | Jul | 2022 | 0.00068859 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-07-21 11:25 | 2022-07-21 14:50 | 150 | 3:25 | P | ARBOL SOBRE LINEA | SE REALIZO DESGANCHE DE ARBOL SOBRE LINEA Y SE CERRO PUENTE | A22072100038 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 205 | 2022-07-21 | 30750 | keep | 0 | Jul | 2022 | 0.020944 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-07-21 11:26 | 2022-07-21 11:27 | 513 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 11118-10 Y SE CERRO POR SCADA LLEVA 20% 1111-01 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 513 | keep | 0 | Jul | 2022 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-07-21 11:26 | 2022-07-21 11:27 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA LLEVA 20% 1111-01 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 2782 | keep | 0 | Jul | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
YAUCO | 2022-07-21 11:27 | 2022-07-21 13:54 | 11 | 2:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22072100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-07-21 | 1617 | keep | 0 | Jul | 2022 | 0.0011013 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-07-21 11:30 | 2022-07-21 13:51 | 13 | 2:21 | P | DESGANCHE | DESGANCHE Y 1 X 30 EN C/L | R22072100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-07-21 | 1833 | keep | 0 | Jul | 2022 | 0.0012484 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2022-07-21 11:33 | 2022-07-21 14:14 | 100 | 2:41 | P | DESGANCHE | 1 X 65 EN C/L | C22072100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-07-21 | 16100 | keep | 0 | Jul | 2022 | 0.010966 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-07-21 11:35 | 2022-07-21 11:36 | 2450 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C22072100000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-07-21 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-07-21 11:36 | 2022-07-21 14:54 | 80 | 3:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 Y 1 X 40 EN C/L SE REEMPLAZARO PIN POLE TOP | C22072100106 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 198 | 2022-07-21 | 15840 | keep | 0 | Jul | 2022 | 0.010789 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-21 11:38 | 2022-07-21 14:48 | 1 | 3:10 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B22072100263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-07-21 | 190 | keep | 0 | Jul | 2022 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-21 11:41 | 2022-07-21 12:21 | 1100 | 0:40 | P | DESGANCHE | HACIENDO OPERACIONES DISPARO INTERRUPTOR | S22072100131 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-07-21 | 44000 | keep | 0 | Jul | 2022 | 0.029968 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-21 11:46 | 2022-07-21 18:22 | 10 | 6:36 | P | NO SE REPORTO CAUSA | SE ELIMINO PARARRAYO SE ENERGIZO XMR VERIFICADO EN SERVICIO. | B22072100290 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 396 | 2022-07-21 | 3960 | keep | 0 | Jul | 2022 | 0.0026971 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-07-21 11:52 | 2022-07-21 15:52 | 1 | 4:00 | P | DESGANCHE | 1 X 50 EN C/L | C22072100095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-07-21 | 240 | keep | 0 | Jul | 2022 | 0.00016346 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-21 11:54 | 2022-07-21 17:27 | 100 | 5:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS FUERTES | M22072100103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 333 | 2022-07-21 | 33300 | keep | 0 | Jul | 2022 | 0.02268 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-21 12:03 | 2022-07-21 13:18 | 100 | 1:15 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYO | C22072100099 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-07-21 | 7500 | keep | 0 | Jul | 2022 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-07-21 12:08 | 2022-07-21 12:09 | 2286 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22072100072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-21 | 2286 | keep | 0 | Jul | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-07-21 12:08 | 2022-07-21 12:09 | 693 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22072100072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-21 | 693 | keep | 0 | Jul | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
CAGUAS | 2022-07-21 12:08 | 2022-07-21 15:35 | 90 | 3:27 | P | DESGANCHE | 1 X 65 EN C/L | C22072100104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-07-21 | 18630 | keep | 0 | Jul | 2022 | 0.012689 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-07-21 12:08 | 2022-07-21 12:09 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22072100071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-21 | 293 | keep | 0 | Jul | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-07-21 12:08 | 2022-07-21 12:09 | 1215 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22072100071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-21 | 1215 | keep | 0 | Jul | 2022 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
BARRANQUITAS | 2022-07-21 12:12 | 2022-07-21 15:41 | 100 | 3:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L SE DESCRUZO | C22072100108 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 209 | 2022-07-21 | 20900 | keep | 0 | Jul | 2022 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-21 12:12 | 2022-07-21 12:15 | 3630 | 0:03 | T | MAL TIEMPO/RAYOS | DISPARO INTERRUPTOR 6014-02 ONCE DE AGOSTO LLEVA LA CARGA DEL 6014-01 MAL TIEMPO DESCARGAS ELECTRICAS | M22072100122 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 3 | 2022-07-21 | 10890 | keep | 0 | Jul | 2022 | 0.0074171 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
AGUADILLA | 2022-07-21 12:13 | 2022-07-21 17:00 | 100 | 4:47 | P | ARBOL SOBRE LINEA | 2 X 50 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LAS LINEAS | M22072100116 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 287 | 2022-07-21 | 28700 | keep | 0 | Jul | 2022 | 0.019547 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-21 12:15 | 2022-07-21 15:04 | 10 | 2:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072100074 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-07-21 | 1690 | keep | 0 | Jul | 2022 | 0.0011511 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-21 12:15 | 2022-07-21 19:20 | 50 | 7:05 | P | MAL TIEMPO/RAYOS | 1 X 15 EN CINCO TRANSFORMADORES DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | M22072100159 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 425 | 2022-07-21 | 21250 | keep | 0 | Jul | 2022 | 0.014473 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-21 12:18 | 2022-07-21 12:19 | 1352 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS LLEVA LA CARGA DEL 6014-03 | M22072100124 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-07-21 | 1352 | keep | 0 | Jul | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-07-21 12:18 | 2022-07-21 12:19 | 871 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS LA CARGA POR EL 6012-05 | M22072100124 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-07-21 | 871 | keep | 0 | Jul | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2022-07-21 12:21 | 2022-07-21 12:35 | 2203 | 0:14 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO POR SCADA | S22072100131 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-07-21 | 30842 | keep | 0 | Jul | 2022 | 0.021006 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-07-21 12:21 | 2022-07-21 21:32 | 1 | 9:11 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO DE XMR | B22072100348 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 551 | 2022-07-21 | 551 | keep | 0 | Jul | 2022 | 0.00037528 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-21 12:22 | 2022-07-21 16:46 | 1 | 4:24 | P | NO SE REPORTO CAUSA | 1 X 30 Y 1 X 15 EN CORTE DE LINEA Y TRANSFORMADOR | C22072100114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 264 | 2022-07-21 | 264 | keep | 0 | Jul | 2022 | 0.00017981 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-21 12:24 | 2022-07-21 12:25 | 790 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | S22072100000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-07-21 | 790 | keep | 0 | Jul | 2022 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-07-21 12:24 | 2022-07-21 12:25 | 259 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | S22072100000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-07-21 | 259 | keep | 0 | Jul | 2022 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
BAYAMON | 2022-07-21 12:24 | 2022-07-21 15:14 | 308 | 2:50 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR PARA REEMPLAZAR 2 MACHETES QUEMADOS EN LA SUBESTACION | B22072100000 | Additional_clients | Switch Failure | Include | Include | Equipment | 170 | 2022-07-21 | 52360 | keep | 0 | Jul | 2022 | 0.035662 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-07-21 12:25 | 2022-07-21 12:26 | 4369 | 0:01 | T | ANIMAL | RECIERRE | C22072100000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-07-21 | 4369 | keep | 0 | Jul | 2022 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
ARECIBO | 2022-07-21 12:25 | 2022-07-21 17:41 | 1 | 5:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES Y LLUVIAS EVENTO DE SALIO DE MAYAGÃœEZ | M22072100130 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 316 | 2022-07-21 | 316 | keep | 0 | Jul | 2022 | 0.00021523 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-21 12:26 | 2022-07-21 18:34 | 100 | 6:08 | P | ANIMAL | 1 X 50 EN SU CRUCE CON GATO | C22072100168 | 1st_after_momentary | Animals | Include | Include | Wildlife | 368 | 2022-07-21 | 36800 | keep | 0 | Jul | 2022 | 0.025064 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-21 12:35 | 2022-07-21 13:28 | 900 | 0:53 | P | DESGANCHE | SE SECCIONALIZO Y SE CONTINUA HACIENDO OPERACIONES | S22072100131 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-07-21 | 47700 | keep | 0 | Jul | 2022 | 0.032488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-21 12:38 | 2022-07-21 16:23 | 50 | 3:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072100141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-07-21 | 11250 | keep | 0 | Jul | 2022 | 0.0076623 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-21 12:38 | 2022-07-21 16:25 | 50 | 3:47 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B22072100369 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-07-21 | 11350 | keep | 0 | Jul | 2022 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-21 12:41 | 2022-07-21 17:52 | 200 | 5:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REFIRIO SITUACION DE DESGANCHE | M22072100146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-07-21 | 62200 | keep | 0 | Jul | 2022 | 0.042364 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-07-21 13:14 | 2022-07-21 19:30 | 120 | 6:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M22072100174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 376 | 2022-07-21 | 45120 | keep | 0 | Jul | 2022 | 0.030731 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-07-21 13:17 | 2022-07-21 17:13 | 150 | 3:56 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE DEL PISO Y SE REEMPLAZO CAJA PRIMARIA | B22072100437 | New_Event | Primary Wire Break | Include | Include | Equipment | 236 | 2022-07-21 | 35400 | keep | 0 | Jul | 2022 | 0.024111 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-07-21 13:17 | 2022-07-21 13:18 | 1352 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS LLEVA LA CARGA DEL 6014-03 | M22072100176 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-07-21 | 1352 | keep | 0 | Jul | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-07-21 13:17 | 2022-07-21 13:18 | 871 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS LA CARGA POR EL 6012-05 | M22072100176 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-07-21 | 871 | keep | 0 | Jul | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
ARECIBO | 2022-07-21 13:17 | 2022-07-21 14:42 | 15 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA POR LLUVIAS | A22072100068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2022-07-21 | 1275 | keep | 0 | Jul | 2022 | 0.0008684 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-07-21 13:24 | 2022-07-21 16:41 | 100 | 3:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22072100149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2022-07-21 | 19700 | keep | 0 | Jul | 2022 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-21 13:26 | 2022-07-21 14:47 | 4381 | 1:21 | T | ARBOL SOBRE LINEA | ABRIR CORTE DE LINEA PARA SECCIONALIZAR Y REPARAR LINEA PRIMARIA | M22072100181 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 81 | 2022-07-21 | 354861 | keep | 0 | Jul | 2022 | 0.24169 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2022-07-21 13:28 | 2022-07-21 13:49 | 500 | 0:21 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | S22072100131 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 21 | 2022-07-21 | 10500 | keep | 0 | Jul | 2022 | 0.0071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-21 13:32 | 2022-07-21 13:33 | 863 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072100192 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-07-21 | 863 | keep | 0 | Jul | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
BAYAMON | 2022-07-21 13:33 | 2022-07-21 13:34 | 1983 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1801-02 | B22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 1983 | keep | 0 | Jul | 2022 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
MAYAGÃœEZ | 2022-07-21 13:33 | 2022-07-21 14:21 | 80 | 0:48 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072100189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 48 | 2022-07-21 | 3840 | keep | 0 | Jul | 2022 | 0.0026154 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-07-21 13:33 | 2022-07-21 21:35 | 60 | 8:02 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072100253 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 482 | 2022-07-21 | 28920 | keep | 0 | Jul | 2022 | 0.019697 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-07-21 13:34 | 2022-07-21 13:35 | 108 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072100194 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-07-21 | 108 | keep | 0 | Jul | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2022-07-21 13:41 | 2022-07-21 14:24 | 14 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | B22072100179 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2022-07-21 | 602 | keep | 0 | Jul | 2022 | 0.00041002 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2022-07-21 13:42 | 2022-07-21 17:56 | 30 | 4:14 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REALIZO DESGANCHE | C22072100155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-07-21 | 7620 | keep | 0 | Jul | 2022 | 0.0051899 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-21 13:50 | 2022-07-21 14:20 | 1588 | 0:30 | S | TERMINACION SOTERRADA AVERIADA | AL PROBAR EL BKR 1711-02 PROBO MALO Y SE LLEVO LA ALTA. SE ENERGIZO NUEVAMENTE EL XMR Y SE CERRO EL BKR 1711-03 QUE LLEVABA EL 1711-01. | B22072100031 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 30 | 2022-07-21 | 47640 | keep | 0 | Jul | 2022 | 0.032447 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2022-07-21 13:50 | 2022-07-21 14:20 | 13 | 0:30 | S | TERMINACION SOTERRADA AVERIADA | AL PROBAR EL BKR 1711-02 PROBO MALO Y SE LLEVO LA ALTA. SE ENERGIZO NUEVAMENTE EL XMR Y SE CERRO EL BKR 1711-03 QUE LLEVABA EL 1711-01. | B22072100031 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 30 | 2022-07-21 | 390 | keep | 0 | Jul | 2022 | 0.00026563 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2022-07-21 13:52 | 2022-07-21 19:23 | 3 | 5:31 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 Y 1 X 30 EN CORTE DE LINEA Y SE REPARA BAJANTE PRIMARIO | A22721000072 | New_Event | Primary Wire Break | Include | Include | Equipment | 331 | 2022-07-21 | 993 | keep | 0 | Jul | 2022 | 0.00067633 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-07-21 13:54 | 2022-07-21 18:50 | 25 | 4:56 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072100211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-07-21 | 7400 | keep | 0 | Jul | 2022 | 0.0050401 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-07-21 13:57 | 2022-07-21 16:42 | 30 | 2:45 | P | DESGANCHE | 1 X 30 1 X 40 EN C/L Y DESGANCHE | R22072100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-07-21 | 4950 | keep | 0 | Jul | 2022 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-07-21 14:01 | 2022-07-21 14:02 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072100106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 527 | keep | 0 | Jul | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
AGUADILLA | 2022-07-21 14:07 | 2022-07-21 17:29 | 150 | 3:22 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LA LINEAS | M22072100215 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 202 | 2022-07-21 | 30300 | keep | 0 | Jul | 2022 | 0.020637 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-07-21 14:08 | 2022-07-21 17:17 | 100 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22072100218 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2022-07-21 | 18900 | keep | 0 | Jul | 2022 | 0.012873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-21 14:14 | 2022-07-21 14:15 | 1253 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6010-02 | M22072100227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 1253 | keep | 0 | Jul | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-07-21 14:14 | 2022-07-21 14:15 | 1266 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6010-01 | M22072100227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 1266 | keep | 0 | Jul | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
CANOVANAS | 2022-07-21 14:16 | 2022-07-21 15:17 | 150 | 1:01 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | R22072100079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-07-21 | 9150 | keep | 0 | Jul | 2022 | 0.006232 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-07-21 14:21 | 2022-07-21 15:12 | 10 | 0:51 | P | ANIMAL | 1 X 15 EN XMR IGUANA CRUZO LINEAS | P22072100109 | New_Event | Animals | Include | Include | Wildlife | 51 | 2022-07-21 | 510 | keep | 0 | Jul | 2022 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-07-21 14:22 | 2022-07-21 16:45 | 120 | 2:23 | P | DESGANCHE | 2 X 40 EN CORTES DE LINEA | C22072100172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-07-21 | 17160 | keep | 0 | Jul | 2022 | 0.011688 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-07-21 14:34 | 2022-07-21 16:51 | 200 | 2:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REFIRIO SITUACION DE DESGANCHE DE EMERGENCIA | M22072100244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-07-21 | 27400 | keep | 0 | Jul | 2022 | 0.018662 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-07-21 14:43 | 2022-07-21 15:36 | 3699 | 0:53 | P | ANIMAL | 1 X 30 EN C/L AVE | R22072100083 | New_Event | Animals | Include | Include | Wildlife | 53 | 2022-07-21 | 196047 | keep | 0 | Jul | 2022 | 0.13353 | 0.0025194 | Sustained | FALSE | FALSE | Not_TMED_Event | 3699
BAYAMON | 2022-07-21 14:44 | 2022-07-21 18:55 | 120 | 4:11 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22072100520 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-07-21 | 30120 | keep | 0 | Jul | 2022 | 0.020515 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-07-21 14:45 | 2022-07-21 19:13 | 200 | 4:28 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072100248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-07-21 | 53600 | keep | 0 | Jul | 2022 | 0.036507 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-07-21 14:47 | 2022-07-21 18:50 | 348 | 4:03 | P | ARBOL SOBRE LINEA | SE REMOVIO ARBOL SOBRE LAS LINEAS, SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRARON MACHETES DEJANDO EN SERVICIO EL 8% DE LOS CLIENTES RESTANTES | M22072100181 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 243 | 2022-07-21 | 84564 | keep | 0 | Jul | 2022 | 0.057596 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-07-21 14:53 | 2022-07-21 19:15 | 40 | 4:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22072100257 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2022-07-21 | 10480 | keep | 0 | Jul | 2022 | 0.0071379 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-07-21 14:58 | 2022-07-21 19:55 | 100 | 4:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCO PARTIDO | C22072100184 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 297 | 2022-07-21 | 29700 | keep | 0 | Jul | 2022 | 0.020229 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-07-21 15:10 | 2022-07-21 17:00 | 50 | 1:50 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22072100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-07-21 | 5500 | keep | 0 | Jul | 2022 | 0.003746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-07-21 15:24 | 2022-07-21 21:00 | 35 | 5:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 50KVA | C22072100191 | New_Event | Service Transformer Failure | Include | Include | Equipment | 336 | 2022-07-21 | 11760 | keep | 0 | Jul | 2022 | 0.0080097 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-07-21 15:28 | 2022-07-21 18:12 | 79 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | C22072100192 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2022-07-21 | 12956 | keep | 0 | Jul | 2022 | 0.0088243 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2022-07-21 15:32 | 2022-07-21 18:49 | 100 | 3:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L Y SE REEMPLAZO PORTAFUSIBLE | B22072100563 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2022-07-21 | 19700 | keep | 0 | Jul | 2022 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-21 15:38 | 2022-07-21 16:51 | 10 | 1:13 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | R22072100095 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 73 | 2022-07-21 | 730 | keep | 0 | Jul | 2022 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-07-21 15:38 | 2022-07-21 20:20 | 100 | 4:42 | P | CAUSAS EXTERNAS | 3 X 65 EN CORTE DE LINEA CAMION TOCO LINEAS PRIMARIAS Y FUNDIERON FUSIBLES | M22072100285 | New_Event | Damage From Public | Include | Include | Public | 282 | 2022-07-21 | 28200 | keep | 0 | Jul | 2022 | 0.019207 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-21 15:43 | 2022-07-21 16:12 | 8 | 0:29 | P | ARBOL SOBRE LINEA | ABRIR XMR PARA SACAR ARBOL SOBRE LINEA PELIGROSO EMERGENCIA | B22072100575 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 29 | 2022-07-21 | 232 | keep | 0 | Jul | 2022 | 0.00015801 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-07-21 15:52 | 2022-07-21 18:53 | 200 | 3:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTES DE LINEA LLUVIAS | C22072100202 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 181 | 2022-07-21 | 36200 | keep | 0 | Jul | 2022 | 0.024656 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-07-21 16:02 | 2022-07-21 17:43 | 25 | 1:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PRIMARIO | A22072100081 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2022-07-21 | 2525 | keep | 0 | Jul | 2022 | 0.0017198 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-07-21 16:11 | 2022-07-21 17:17 | 20 | 1:06 | P | DESGANCHE | 1 X 140 Y C/L Y DESGANCHE | B22072100517 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-07-21 | 1320 | keep | 0 | Jul | 2022 | 0.00089905 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-07-21 16:12 | 2022-07-21 17:52 | 200 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 40 EN CORTES DE LINEA LLUVIAS | C22072100214 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2022-07-21 | 20000 | keep | 0 | Jul | 2022 | 0.013622 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-07-21 16:13 | 2022-07-21 18:19 | 15 | 2:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO LINEAS SECUNDARIA | A22072100083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 126 | 2022-07-21 | 1890 | keep | 0 | Jul | 2022 | 0.0012873 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-07-21 16:43 | 2022-07-21 18:33 | 35 | 1:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 2 X 80 EN C/L | R22072100099 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2022-07-21 | 3850 | keep | 0 | Jul | 2022 | 0.0026222 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-07-21 17:01 | 2022-07-21 19:16 | 5 | 2:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIAS | A22072100095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 135 | 2022-07-21 | 675 | keep | 0 | Jul | 2022 | 0.00045974 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-07-21 17:25 | 2022-07-22 13:26 | 10 | 20:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA TRAS PATIO | S22072100505 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1201 | 2022-07-21 | 12010 | keep | 0 | Jul | 2022 | 0.00818 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-21 17:27 | 2022-07-21 18:13 | 35 | 0:46 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y 1 X 65 EN C/L | R22072100100 | New_Event | Primary Wire Break | Include | Include | Equipment | 46 | 2022-07-21 | 1610 | keep | 0 | Jul | 2022 | 0.0010966 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2022-07-21 17:36 | 2022-07-21 20:00 | 4 | 2:24 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | P22072100144 | New_Event | Animals | Include | Include | Wildlife | 144 | 2022-07-21 | 576 | keep | 0 | Jul | 2022 | 0.00039231 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-07-21 17:39 | 2022-07-21 19:00 | 135 | 1:21 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | P22072100145 | New_Event | Animals | Include | Include | Wildlife | 81 | 2022-07-21 | 10935 | keep | 0 | Jul | 2022 | 0.0074478 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
BAYAMON | 2022-07-21 17:41 | 2022-07-22 09:01 | 60 | 15:20 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22072100653 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 920 | 2022-07-21 | 55200 | keep | 0 | Jul | 2022 | 0.037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-07-21 17:42 | 2022-07-21 19:06 | 50 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS FUERTES | M22072100323 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2022-07-21 | 4200 | keep | 0 | Jul | 2022 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-21 17:44 | 2022-07-21 23:35 | 64 | 5:51 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REPARO TERMINACIONES DE CABLE SOTERRADO EN EL SU-11 | B22072100698 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 351 | 2022-07-21 | 22464 | keep | 0 | Jul | 2022 | 0.0153 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2022-07-21 17:45 | 2022-07-22 17:44 | 9 | 23:59 | P | SECUNDARIA/DESGANCHE | REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B22072100655 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1439 | 2022-07-21 | 12951 | keep | 0 | Jul | 2022 | 0.0088209 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2022-07-21 17:59 | 2022-07-22 13:22 | 8 | 19:23 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REPARO BAJNTE | C22072100256 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 1163 | 2022-07-21 | 9304 | keep | 0 | Jul | 2022 | 0.0063369 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-07-21 18:35 | 2022-07-22 08:32 | 3 | 13:57 | P | TRANSFORMADOR AVERIADO | SE DIO PUENTE SECUNDARIO Y SE REPARO BUSHING SECUNDARIO (NO FUNDIO) | B22072100667 | New_Event | Service Transformer Failure | Include | Include | Equipment | 837 | 2022-07-21 | 2511 | keep | 0 | Jul | 2022 | 0.0017102 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-07-21 18:36 | 2022-07-22 09:55 | 11 | 15:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | C22072100267 | New_Event | Secondary Wire Break | Include | Include | Equipment | 919 | 2022-07-21 | 10109 | keep | 0 | Jul | 2022 | 0.0068852 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-07-21 18:43 | 2022-07-21 20:15 | 300 | 1:32 | P | ARBOL SOBRE LINEA | 1 X 140 Y 1 X 100 EN CORTES DE LINEA ARBOL SOBRE LINEAS DENTRO DE LOS PREDIOS DE LA AAA | C22072100268 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 92 | 2022-07-21 | 27600 | keep | 0 | Jul | 2022 | 0.018798 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-07-21 18:56 | 2022-07-21 23:23 | 60 | 4:27 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072100333 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 267 | 2022-07-21 | 16020 | keep | 0 | Jul | 2022 | 0.010911 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-07-21 19:11 | 2022-07-21 22:27 | 500 | 3:16 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PIRMARIO ABIERTO EN TRONCAL DE ALIMENTADOR SE ABRIO INTERRUPTOR PARA REALIZAR TRABAJOS BAJO GOI PC-220721-01A | P22072100161 | New_Event | Primary Wire Break | Include | Include | Equipment | 196 | 2022-07-21 | 98000 | keep | 0 | Jul | 2022 | 0.066747 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2022-07-21 19:14 | 2022-07-21 20:24 | 287 | 1:10 | P | ANIMAL | 1 X 80 EN C/L AVE | R22072100106 | New_Event | Animals | Include | Include | Wildlife | 70 | 2022-07-21 | 20090 | keep | 0 | Jul | 2022 | 0.013683 | 0.00019547 | Sustained | FALSE | FALSE | Not_TMED_Event | 287
BAYAMON | 2022-07-21 19:33 | 2022-07-22 12:09 | 41 | 16:36 | P | CABLE SOTERRADO AVERIADO | 1X25 DEL SU-1B @ T-55 | B22072100674 | New_Event | UG Cable Fault | Include | Include | Equipment | 996 | 2022-07-21 | 40836 | keep | 0 | Jul | 2022 | 0.027813 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
HUMACAO | 2022-07-21 19:33 | 2022-07-22 08:17 | 15 | 12:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO | C22072100286 | New_Event | Secondary Wire Break | Include | Include | Equipment | 764 | 2022-07-21 | 11460 | keep | 0 | Jul | 2022 | 0.0078054 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-07-21 19:51 | 2022-07-21 22:22 | 100 | 2:31 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN RISER Y 2 X 100 EN C/L Y SE ELIMINO PARARRAYO | S22072100620 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 151 | 2022-07-21 | 15100 | keep | 0 | Jul | 2022 | 0.010285 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-21 19:55 | 2022-07-22 00:34 | 10 | 4:39 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072100349 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 279 | 2022-07-21 | 2790 | keep | 0 | Jul | 2022 | 0.0019003 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-21 20:09 | 2022-07-21 20:59 | 1 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO ABIERTO | P22072100177 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-07-21 | 50 | keep | 0 | Jul | 2022 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-21 20:17 | 2022-07-21 22:48 | 10 | 2:31 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072100352 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 151 | 2022-07-21 | 1510 | keep | 0 | Jul | 2022 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-07-21 20:18 | 2022-07-22 00:21 | 5 | 4:03 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072100353 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 243 | 2022-07-21 | 1215 | keep | 0 | Jul | 2022 | 0.00082753 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-07-21 20:40 | 2022-07-21 21:40 | 13 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22072100354 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-07-21 | 780 | keep | 0 | Jul | 2022 | 0.00053125 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2022-07-21 20:55 | 2022-07-21 20:57 | 2635 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 5270 | keep | 0 | Jul | 2022 | 0.0035894 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
AGUADILLA | 2022-07-21 20:56 | 2022-07-22 01:00 | 60 | 4:04 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072100349 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 244 | 2022-07-21 | 14640 | keep | 0 | Jul | 2022 | 0.0099712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-21 20:59 | 2022-07-22 11:19 | 59 | 14:20 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22072100640 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 860 | 2022-07-21 | 50740 | keep | 0 | Jul | 2022 | 0.034559 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BAYAMON | 2022-07-21 21:02 | 2022-07-22 14:11 | 4 | 17:09 | P | NO SE REPORTO CAUSA | 1X10 EN XMR (COLINDANCIA CON REGION DE CAGUAS) | C22072100300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1029 | 2022-07-21 | 4116 | keep | 0 | Jul | 2022 | 0.0028034 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-07-21 21:06 | 2022-07-21 21:08 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22072100308 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 4252 | keep | 0 | Jul | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BARRANQUITAS | 2022-07-21 21:09 | 2022-07-22 07:15 | 100 | 10:06 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN C/L RETEZO LINEAS | C22072100304 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 606 | 2022-07-21 | 60600 | keep | 0 | Jul | 2022 | 0.041274 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-21 21:35 | 2022-07-22 09:14 | 10 | 11:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE BUSHING PRIMARIO @ LA CAJA (NO FUNDIO) | B22072100696 | New_Event | Primary Wire Break | Include | Include | Equipment | 699 | 2022-07-21 | 6990 | keep | 0 | Jul | 2022 | 0.0047609 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-21 21:39 | 2022-07-21 22:30 | 30 | 0:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA 1 X 50 EN C/L | R22072100127 | New_Event | Primary Wire Break | Include | Include | Equipment | 51 | 2022-07-21 | 1530 | keep | 0 | Jul | 2022 | 0.0010421 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-21 22:24 | 2022-07-22 08:46 | 70 | 10:22 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | R22072100133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 622 | 2022-07-21 | 43540 | keep | 0 | Jul | 2022 | 0.029655 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-07-21 22:27 | 2022-07-21 23:16 | 1569 | 0:49 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE EN TROCAL Y SE COLOCO INTERRUPTOR EN SERVICIO GOI PC-220721-01A | P22072100205 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 49 | 2022-07-21 | 76881 | keep | 0 | Jul | 2022 | 0.052363 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-21 23:09 | 2022-07-22 01:57 | 2 | 2:48 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072100364 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 168 | 2022-07-21 | 336 | keep | 0 | Jul | 2022 | 0.00022885 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-07-21 23:18 | 2022-07-21 23:21 | 1746 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B22072100706 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-21 | 5238 | keep | 0 | Jul | 2022 | 0.0035676 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
SAN JUAN | 2022-07-21 23:25 | 2022-07-21 23:26 | 512 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1118-10 LLEVA EL 1111-01 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 512 | keep | 0 | Jul | 2022 | 0.00034872 | 0.00034872 | Momentary | FALSE | FALSE | Not_TMED_Event | 512
SAN JUAN | 2022-07-21 23:25 | 2022-07-21 23:26 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1118-10 LLEVA EL 1111-01 | B22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-21 | 2782 | keep | 0 | Jul | 2022 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
PONCE | 2022-07-21 23:53 | 2022-07-22 06:20 | 7 | 6:27 | P | ANIMAL | 1 X 20 EN XMR ANIMAL CRUZO LINEAS | P22072100206 | New_Event | Animals | Include | Include | Wildlife | 387 | 2022-07-21 | 2709 | keep | 0 | Jul | 2022 | 0.0018451 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-07-21 23:54 | 2022-07-21 23:56 | 823 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 1119-04 LLEVA 1116-01 Y 95% DEL 1115-05 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 1646 | keep | 0 | Jul | 2022 | 0.0011211 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
SAN JUAN | 2022-07-21 23:54 | 2022-07-21 23:56 | 343 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1119-04 LLEVA 1119-02 Y 95% DEL 1115-05 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 686 | keep | 0 | Jul | 2022 | 0.00046723 | 0.00023362 | Momentary | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2022-07-21 23:54 | 2022-07-21 23:56 | 2720 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1119-04 LLEVA 1116-01 Y 95% DEL 1115-05 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-21 | 5440 | keep | 0 | Jul | 2022 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-07-22 00:22 | 2022-07-22 04:34 | 35 | 4:12 | P | ARBOL SOBRE LINEA | 2 X 100 EN C/L SE RETIRO ARBOL SOBRE LINEA SE LEVANTO SECUNDARIA Y 2 PORTAFUSIBLES | S22072200004 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 252 | 2022-07-22 | 8820 | keep | 0 | Jul | 2022 | 0.0060073 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-07-22 02:19 | 2022-07-22 12:30 | 6 | 10:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22072200002 | New_Event | Primary Wire Break | Include | Include | Equipment | 611 | 2022-07-22 | 3666 | keep | 0 | Jul | 2022 | 0.0024969 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-07-22 02:19 | 2022-07-22 10:30 | 100 | 8:11 | P | CAUSAS EXTERNAS | SE ABRIO PUENTES Y SE CERRO CORTE DE LINEA PARA PODER TRABAJAR EN REEMPLAZO DEL POSTE PARTIDO A CAUSA DE CAMION | M22072200027 | New_Event | Damage From Public | Include | Include | Public | 491 | 2022-07-22 | 49100 | keep | 0 | Jul | 2022 | 0.033442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-22 02:37 | 2022-07-22 08:49 | 60 | 6:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CL SE REMPLAZO CAJA QUEMADA | R22072200004 | New_Event | Cutout Failure | Include | Include | Equipment | 372 | 2022-07-22 | 22320 | keep | 0 | Jul | 2022 | 0.015202 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-22 02:53 | 2022-07-22 02:56 | 3070 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B22072200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-22 | 9210 | keep | 0 | Jul | 2022 | 0.0062729 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BARRANQUITAS | 2022-07-22 03:23 | 2022-07-22 08:11 | 60 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARAO LA CONEXION DE LINEA A CAJA | C22072200002 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2022-07-22 | 17280 | keep | 0 | Jul | 2022 | 0.011769 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-22 04:56 | 2022-07-22 04:57 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1909-08 LLEVA EL 1907-05 | B22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 2435 | keep | 0 | Jul | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-22 04:56 | 2022-07-22 04:57 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1909-08 LLEVA EL 1907-05 | B22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 2956 | keep | 0 | Jul | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-07-22 05:09 | 2022-07-22 20:24 | 15 | 15:15 | P | DESGANCHE | SE REALIZO DESGANCHE Y 1 X 30 EN C/L | B22072200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 915 | 2022-07-22 | 13725 | keep | 0 | Jul | 2022 | 0.009348 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-07-22 05:23 | 2022-07-22 06:38 | 70 | 1:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHO | C22072200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-07-22 | 5250 | keep | 0 | Jul | 2022 | 0.0035758 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-07-22 05:45 | 2022-07-22 10:31 | 60 | 4:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L SE REMPLAZO CAJA PRIMARIA | B22072200008 | New_Event | Cutout Failure | Include | Include | Equipment | 286 | 2022-07-22 | 17160 | keep | 0 | Jul | 2022 | 0.011688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-22 06:13 | 2022-07-22 06:14 | 1835 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 1835 | keep | 0 | Jul | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
SAN JUAN | 2022-07-22 06:36 | 2022-07-22 06:37 | 3 | 0:01 | T | ANIMAL | RECIERRE | S22072200000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-07-22 | 3 | keep | 0 | Jul | 2022 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-07-22 06:36 | 2022-07-22 09:10 | 100 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22072200005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-07-22 | 15400 | keep | 0 | Jul | 2022 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-22 06:37 | 2022-07-22 11:25 | 1 | 4:48 | P | ANIMAL | 1X15 EN XMR (POR AVE EN EL 13KV) | S22072200160 | 1st_after_momentary | Animals | Include | Include | Wildlife | 288 | 2022-07-22 | 288 | keep | 0 | Jul | 2022 | 0.00019616 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-07-22 06:47 | 2022-07-22 06:48 | 1494 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 1494 | keep | 0 | Jul | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
BARRANQUITAS | 2022-07-22 06:48 | 2022-07-22 06:49 | 3131 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 3131 | keep | 0 | Jul | 2022 | 0.0021325 | 0.0021325 | Momentary | FALSE | FALSE | Not_TMED_Event | 3131
BARRANQUITAS | 2022-07-22 06:49 | 2022-07-22 16:41 | 10 | 9:52 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR | C22072200060 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 592 | 2022-07-22 | 5920 | keep | 0 | Jul | 2022 | 0.0040321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-22 06:55 | 2022-07-22 06:56 | 2697 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22072200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-22 | 2697 | keep | 0 | Jul | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2022-07-22 06:56 | 2022-07-22 10:45 | 200 | 3:49 | P | DESGANCHE | 1 X 100 Y 1 X 65 EN CORTES DE LINEA DISTINTOS SE RETIRO ENREDADERA SOBRE LINEA PRIMARIA | A22072200002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 229 | 2022-07-22 | 45800 | keep | 0 | Jul | 2022 | 0.031194 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-07-22 07:10 | 2022-07-22 10:22 | 100 | 3:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CL SE REMPLAZO CAJA QUEMADA | R22072200013 | New_Event | Cutout Failure | Include | Include | Equipment | 192 | 2022-07-22 | 19200 | keep | 0 | Jul | 2022 | 0.013077 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-07-22 07:55 | 2022-07-22 10:20 | 80 | 2:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LINEA PRIMARIA | A22072200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-07-22 | 11600 | keep | 0 | Jul | 2022 | 0.0079007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-07-22 08:03 | 2022-07-22 19:45 | 1 | 11:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN CORTE DE LINEA SE REPARO LINEA SECUNDARIA | A22072200018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 702 | 2022-07-22 | 702 | keep | 0 | Jul | 2022 | 0.00047813 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-07-22 08:06 | 2022-07-22 09:28 | 10 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22072200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-07-22 | 820 | keep | 0 | Jul | 2022 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-22 08:19 | 2022-07-22 08:20 | 2076 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO - 40% DE SU CARGA TRANSFERIDA AL 1718-03 | B22072200020 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-22 | 2076 | keep | 0 | Jul | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-07-22 08:19 | 2022-07-22 08:20 | 2605 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO - LLEVA 40% DEL 1710-05 | B22072200020 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-22 | 2605 | keep | 0 | Jul | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
MAYAGÃœEZ | 2022-07-22 08:27 | 2022-07-22 12:45 | 60 | 4:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M22072200025 | New_Event | Primary Wire Break | Include | Include | Equipment | 258 | 2022-07-22 | 15480 | keep | 0 | Jul | 2022 | 0.010543 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-22 08:33 | 2022-07-22 08:34 | 2076 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO - 40% DE SU CARGA TRANSFERIDA AL 1718-03 | B22072200023 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-22 | 2076 | keep | 0 | Jul | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-07-22 08:33 | 2022-07-22 08:34 | 2605 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO - LLEVA 40% DEL 1710-05 | B22072200023 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-22 | 2605 | keep | 0 | Jul | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-07-22 08:34 | 2022-07-22 15:13 | 8 | 6:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO PUENTE ABIERTO SE REEMPLAZO CAJA PRIMARIA | B22072200025 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 399 | 2022-07-22 | 3192 | keep | 0 | Jul | 2022 | 0.0021741 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-07-22 08:41 | 2022-07-22 09:30 | 738 | 0:49 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR 1346-02 QUE LLEVA 30% DEL 1346-03 Y SE CERRO POR SCADA | S22072200184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2022-07-22 | 36162 | keep | 0 | Jul | 2022 | 0.02463 | 0.00050265 | Sustained | FALSE | FALSE | Not_TMED_Event | 738
BAYAMON | 2022-07-22 08:42 | 2022-07-22 15:45 | 3 | 7:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22072200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2022-07-22 | 1269 | keep | 0 | Jul | 2022 | 0.00086431 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-07-22 08:54 | 2022-07-22 14:26 | 6 | 5:32 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072200030 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 332 | 2022-07-22 | 1992 | keep | 0 | Jul | 2022 | 0.0013567 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-07-22 08:58 | 2022-07-22 12:24 | 1310 | 3:26 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | CON RISER ABIERTO PROBO MALO. HC-73976 @ CDS PARA DESACOPLAR E INSPECCIONAR SE TRANSFIRIO LA CARGA AL 1520-02 | S22072200219 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 206 | 2022-07-22 | 269860 | keep | 0 | Jul | 2022 | 0.1838 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-07-22 09:02 | 2022-07-22 09:04 | 143 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 1404-06 QUE LLEVA 80% DEL 1404-07 | S22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-22 | 286 | keep | 0 | Jul | 2022 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-07-22 09:02 | 2022-07-22 09:04 | 1085 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 1404-06 QUE LLEVA 80% DEL 1404-07 | S22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-22 | 2170 | keep | 0 | Jul | 2022 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
VEGA BAJA | 2022-07-22 09:09 | 2022-07-22 11:27 | 2 | 2:18 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22072200027 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 138 | 2022-07-22 | 276 | keep | 0 | Jul | 2022 | 0.00018798 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-07-22 09:13 | 2022-07-22 16:30 | 10 | 7:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL DE TRANSFORMADOR | M22072200033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 437 | 2022-07-22 | 4370 | keep | 0 | Jul | 2022 | 0.0029764 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-07-22 09:13 | 2022-07-22 10:50 | 50 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 30 EN CORTES DE LINEA DISTINTOS MAL TIEMPO VIENTOS FUERTES | A22072200029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2022-07-22 | 4850 | keep | 0 | Jul | 2022 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-22 09:15 | 2022-07-22 10:55 | 15 | 1:40 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22072200034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-07-22 | 1500 | keep | 0 | Jul | 2022 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-07-22 09:15 | 2022-07-22 10:45 | 7 | 1:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS DE TRANSFORMADOR PARA REALIZAR DESGANCHE EN LINEAS SECUNDARIAS | M22072100114 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 90 | 2022-07-22 | 630 | keep | 0 | Jul | 2022 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-07-22 09:20 | 2022-07-22 11:29 | 100 | 2:09 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | R22072200020 | New_Event | Primary Wire Break | Include | Include | Equipment | 129 | 2022-07-22 | 12900 | keep | 0 | Jul | 2022 | 0.0087861 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-22 09:30 | 2022-07-22 10:00 | 369 | 0:30 | P | DESGANCHE | SE REALIZO DESGANCHE Y CERRO MACHETE EN LA CALLE ORQUIDEA Y ENTRO EL 30% DE LA CARGA DEL 1346-03 | S22072200184 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-07-22 | 11070 | keep | 0 | Jul | 2022 | 0.0075397 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-22 09:30 | 2022-07-22 10:00 | 726 | 0:30 | P | DESGANCHE | EN DISPARO DE 1346-02 SE REALIZO DESGANCHE Y SE CERRO MACHETES EN LA CALLE ORQUIDEA Y ENTRO EL 30% DE LA CARGA DEL 1346-03 QUE ESTA POR EL 1346-02 | S22072200184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-07-22 | 21780 | keep | 0 | Jul | 2022 | 0.014834 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
HUMACAO | 2022-07-22 09:44 | 2022-07-22 14:13 | 1 | 4:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C22072200043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 269 | 2022-07-22 | 269 | keep | 0 | Jul | 2022 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-07-22 09:45 | 2022-07-22 12:43 | 1 | 2:58 | P | NO SE REPORTO CAUSA | 1X20 EN BANCO DE XMRS DEL CLIENTE | B22072200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2022-07-22 | 178 | keep | 0 | Jul | 2022 | 0.00012123 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-22 09:50 | 2022-07-22 18:08 | 2 | 8:18 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | M22072200040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 498 | 2022-07-22 | 996 | keep | 0 | Jul | 2022 | 0.00067837 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-07-22 09:58 | 2022-07-22 12:30 | 5 | 2:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO DOS BARRA EN EL PEDESTAL | C22072200045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 152 | 2022-07-22 | 760 | keep | 0 | Jul | 2022 | 0.00051763 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-07-22 10:00 | 2022-07-22 10:20 | 1 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22072200020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-07-22 | 20 | keep | 0 | Jul | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-22 10:16 | 2022-07-22 16:23 | 20 | 6:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA ROTA | M22072200046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 367 | 2022-07-22 | 7340 | keep | 0 | Jul | 2022 | 0.0049992 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-07-22 10:18 | 2022-07-22 14:15 | 1633 | 3:57 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE PRIMARIO EN LINEA 1900 | A22072200041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 237 | 2022-07-22 | 387021 | keep | 0 | Jul | 2022 | 0.2636 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
BAYAMON | 2022-07-22 10:20 | 2022-07-22 19:23 | 25 | 9:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22072200036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 543 | 2022-07-22 | 13575 | keep | 0 | Jul | 2022 | 0.0092459 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-07-22 10:27 | 2022-07-22 12:10 | 11 | 1:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | C22072200047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 103 | 2022-07-22 | 1133 | keep | 0 | Jul | 2022 | 0.00077168 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-07-22 10:30 | 2022-07-22 19:30 | 10 | 9:00 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PRIMARIO PARTIDO A CAUSA DE CAMION QUE LO IMPACTO | M22072200027 | New_Event | Damage From Public | Include | Include | Public | 540 | 2022-07-22 | 5400 | keep | 0 | Jul | 2022 | 0.0036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-07-22 10:34 | 2022-07-22 13:05 | 4 | 2:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR PAD MOUNTED DE 37.5 AVERIADO | P22072200025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 151 | 2022-07-22 | 604 | keep | 0 | Jul | 2022 | 0.00041138 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-07-22 10:34 | 2022-07-22 13:05 | 12 | 2:31 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR SE DESGANCHO SECUNDARIO ENRREDARERA | B22072200037 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 151 | 2022-07-22 | 1812 | keep | 0 | Jul | 2022 | 0.0012341 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-07-22 10:49 | 2022-07-22 10:50 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR LA CARGA POR EL 4006-05 | P22072200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 4132 | keep | 0 | Jul | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-07-22 10:49 | 2022-07-22 10:50 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 4006-05 CON LA CARGA DEL 4003-02 | P22072200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 4279 | keep | 0 | Jul | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-07-22 10:49 | 2022-07-22 10:50 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR LLEVA CARGA DEL 4003-02 | P22072200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 464 | keep | 0 | Jul | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
SAN JUAN | 2022-07-22 11:00 | 2022-07-22 13:15 | 30 | 2:15 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE REPLAZO POSTE PARTIDO | S22072200277 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 135 | 2022-07-22 | 4050 | keep | 0 | Jul | 2022 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-22 11:00 | 2022-07-22 15:31 | 5 | 4:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON LAS (3) BARRAS EN PEDESTAL | B22072200038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 271 | 2022-07-22 | 1355 | keep | 0 | Jul | 2022 | 0.00092288 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-07-22 11:30 | 2022-07-22 15:41 | 30 | 4:11 | P | ANIMAL | 1 X 30 EN C/L X AVE | C22072200053 | New_Event | Animals | Include | Include | Wildlife | 251 | 2022-07-22 | 7530 | keep | 0 | Jul | 2022 | 0.0051286 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-07-22 11:45 | 2022-07-22 16:49 | 300 | 5:04 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 Y 1 X 65 EN DIFERENTES C/L SE REPARO ALAMBRE PRIMARIO PARTIDO | P22072200035 | New_Event | Primary Wire Break | Include | Include | Equipment | 304 | 2022-07-22 | 91200 | keep | 0 | Jul | 2022 | 0.062116 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-07-22 11:48 | 2022-07-22 14:12 | 40 | 2:24 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN C/L DESGANCHE | R22072200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-07-22 | 5760 | keep | 0 | Jul | 2022 | 0.0039231 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-22 11:51 | 2022-07-22 12:43 | 7 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22072200289 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2022-07-22 | 364 | keep | 0 | Jul | 2022 | 0.00024792 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-07-22 11:54 | 2022-07-22 15:30 | 40 | 3:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072200056 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 216 | 2022-07-22 | 8640 | keep | 0 | Jul | 2022 | 0.0058847 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-22 12:09 | 2022-07-22 18:29 | 30 | 6:20 | P | CABLE SOTERRADO AVERIADO | SE INSTALO AEREO PROVICIONAL DE T-54 @ T53 | B22072100674 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 380 | 2022-07-22 | 11400 | keep | 0 | Jul | 2022 | 0.0077645 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-07-22 12:15 | 2022-07-22 13:40 | 1 | 1:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 X 37.5 KVA | A22072200059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2022-07-22 | 85 | keep | 0 | Jul | 2022 | 5.7893e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-22 12:18 | 2022-07-23 11:20 | 28 | 23:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO EN PEDESTAL | S22072200298 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1382 | 2022-07-22 | 38696 | keep | 0 | Jul | 2022 | 0.026356 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2022-07-22 12:51 | 2022-07-22 12:54 | 3432 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO 1204-02 LLEVA 80% DE SU CARGA Y LLEVA 10% DEL 1204-03 CERRAR POR SCADA | S22072200300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-22 | 10296 | keep | 0 | Jul | 2022 | 0.0070126 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-07-22 12:51 | 2022-07-22 12:54 | 138 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO 1204-02 LLEVA 80% DE SU CARGA Y LLEVA 10% DEL 1204-03 CERRAR POR SCADA | S22072200300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-22 | 414 | keep | 0 | Jul | 2022 | 0.00028197 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
PONCE | 2022-07-22 12:57 | 2022-07-22 16:11 | 8 | 3:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO CAJA QUEMADA EN XMR | P22072200046 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2022-07-22 | 1552 | keep | 0 | Jul | 2022 | 0.0010571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-07-22 13:07 | 2022-07-22 13:08 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22072200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 1746 | keep | 0 | Jul | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
VEGA BAJA | 2022-07-22 13:13 | 2022-07-22 15:25 | 50 | 2:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072200064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-07-22 | 6600 | keep | 0 | Jul | 2022 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-22 13:36 | 2022-07-22 13:37 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072200062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 1825 | keep | 0 | Jul | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-07-22 13:46 | 2022-07-22 13:47 | 681 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1520-02 QUE LLEVA LA CARGA DEL 1530-09 | S22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 681 | keep | 0 | Jul | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-07-22 13:52 | 2022-07-22 13:53 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1520-02 QUE LLEVA LA CARGA DEL 1530-09 | S22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 1310 | keep | 0 | Jul | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
HUMACAO | 2022-07-22 13:55 | 2022-07-22 17:35 | 58 | 3:40 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO Y REMPLAZO HERRAJE DE LA CAJA | C22072200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-07-22 | 12760 | keep | 0 | Jul | 2022 | 0.0086908 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
MAYAGÃœEZ | 2022-07-22 14:03 | 2022-07-22 16:26 | 6 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | M22072200065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-07-22 | 858 | keep | 0 | Jul | 2022 | 0.00058438 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-07-22 14:08 | 2022-07-22 15:47 | 1 | 1:39 | P | OTRAS CAUSAS | 1 X 40 EN C/L Y SE ELIMINO GUY WIRE | R22072200041 | New_Event | Other Causes | Include | Include | Other | 99 | 2022-07-22 | 99 | keep | 0 | Jul | 2022 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-22 14:12 | 2022-07-22 17:45 | 100 | 3:33 | P | ARBOL SOBRE LINEA | 2 X 50 EN CORTE DE LINEA SE RETIRO ARBOLES SOBRE LAS LINEAS | M22072200067 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 213 | 2022-07-22 | 21300 | keep | 0 | Jul | 2022 | 0.014507 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-07-22 14:24 | 2022-07-22 17:54 | 58 | 3:30 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22072200069 | New_Event | Animals | Include | Include | Wildlife | 210 | 2022-07-22 | 12180 | keep | 0 | Jul | 2022 | 0.0082957 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
GUAYAMA | 2022-07-22 14:55 | 2022-07-22 15:00 | 1 | 0:05 | P | ANIMAL | 1 X 20 EN C/L AVE CRUZO LINEAS | P22072200059 | New_Event | Animals | Include | Include | Wildlife | 5 | 2022-07-22 | 5 | keep | 0 | Jul | 2022 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-07-22 15:00 | 2022-07-24 18:20 | 2 | 51:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA | A22072400049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3080 | 2022-07-22 | 6160 | keep | 0 | Jul | 2022 | 0.0041955 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-07-22 15:23 | 2022-07-22 18:24 | 20 | 3:01 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE SE REEMPLAZO PARARRAYO | R22072200043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-07-22 | 3620 | keep | 0 | Jul | 2022 | 0.0024656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-07-22 15:37 | 2022-07-22 18:50 | 40 | 3:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22072200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-07-22 | 7720 | keep | 0 | Jul | 2022 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-22 15:47 | 2022-07-22 15:48 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR | B22072200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-22 | 5252 | keep | 0 | Jul | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
ARECIBO | 2022-07-22 15:52 | 2022-07-22 17:35 | 30 | 1:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072200080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-07-22 | 3090 | keep | 0 | Jul | 2022 | 0.0021046 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-07-22 16:00 | 2022-07-26 13:19 | 2 | 93:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS RELACIONADO A WR-6176921 CREADO COMO FALTA DE SERVICIO. CLIENTE SIN SERVICIO DESDE EL DIA 22 LE CREARON UN WR | M22072600109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5599 | 2022-07-22 | 11198 | keep | 0 | Jul | 2022 | 0.0076269 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-07-22 16:13 | 2022-07-22 20:39 | 261 | 4:26 | P | CONDUCTOR ROTO O ABIERTO | LEVANTO CONDUCTOR NO FUNDIO | C22072200083 | New_Event | Primary Wire Break | Include | Include | Equipment | 266 | 2022-07-22 | 69426 | keep | 0 | Jul | 2022 | 0.047286 | 0.00017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 261
CANOVANAS | 2022-07-22 16:33 | 2022-07-22 17:53 | 18 | 1:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22072200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-07-22 | 1440 | keep | 0 | Jul | 2022 | 0.00098078 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-07-22 16:39 | 2022-07-23 10:42 | 8 | 18:03 | P | NO SE REPORTO CAUSA | NO SE PUDO HACER PRUEBA A XMR CON FUSIBLE FUNDIDO, POR ABEJAS. SE PASO CARGA A OTRO XMR | S22072200327 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1083 | 2022-07-22 | 8664 | keep | 0 | Jul | 2022 | 0.005901 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-07-22 16:52 | 2022-07-22 16:56 | 12 | 0:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO TRANSFORMADOR PARA QUE PERSONAL DE LOW VOLTAGE RETIRARA PELIGRO EN BASE DE CONTADOR DE CLIENTE | R22072200044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 4 | 2022-07-22 | 48 | keep | 0 | Jul | 2022 | 3.2693e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-07-22 17:03 | 2022-07-22 18:29 | 1 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22072200087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2022-07-22 | 86 | keep | 0 | Jul | 2022 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-07-22 17:08 | 2022-07-23 10:32 | 50 | 17:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22072200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1044 | 2022-07-22 | 52200 | keep | 0 | Jul | 2022 | 0.035553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-07-22 17:18 | 2022-07-22 19:23 | 102 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R22072200052 | New_Event | Primary Wire Break | Include | Include | Equipment | 125 | 2022-07-22 | 12750 | keep | 0 | Jul | 2022 | 0.008684 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
BARRANQUITAS | 2022-07-22 17:19 | 2022-07-22 17:41 | 1 | 0:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22072200089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2022-07-22 | 22 | keep | 0 | Jul | 2022 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-22 17:25 | 2022-07-22 18:54 | 1 | 1:29 | P | ANIMAL | 1 X 50 Y 1 X 80 EN C/LS CRUCE X AVE | C22072200090 | New_Event | Animals | Include | Include | Wildlife | 89 | 2022-07-22 | 89 | keep | 0 | Jul | 2022 | 6.0617e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-22 17:29 | 2022-07-22 20:06 | 4 | 2:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22072200332 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-07-22 | 628 | keep | 0 | Jul | 2022 | 0.00042773 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-07-22 17:35 | 2022-07-22 18:40 | 15 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR REPARAR BAJANTES SECUNDARIOS | A22072200062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-07-22 | 975 | keep | 0 | Jul | 2022 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-07-22 17:52 | 2022-07-23 00:18 | 40 | 6:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072200105 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 386 | 2022-07-22 | 15440 | keep | 0 | Jul | 2022 | 0.010516 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-22 17:54 | 2022-07-22 18:18 | 8 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR SE REPARO SECUNDARIA | B22072200043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2022-07-22 | 192 | keep | 0 | Jul | 2022 | 0.00013077 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-07-22 18:01 | 2022-07-23 09:55 | 90 | 15:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22072200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 954 | 2022-07-22 | 85860 | keep | 0 | Jul | 2022 | 0.058479 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-07-22 18:06 | 2022-07-22 22:54 | 155 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE DE LINEA A RISER | S22072200333 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2022-07-22 | 44640 | keep | 0 | Jul | 2022 | 0.030404 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
MAYAGÃœEZ | 2022-07-22 18:37 | 2022-07-22 18:38 | 1444 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DEL INTERRUPTOR CARGA POR 6014-02 | M22072200071 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-07-22 | 1444 | keep | 0 | Jul | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-07-22 18:37 | 2022-07-22 18:38 | 3630 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-01 | M22072200071 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-07-22 | 3630 | keep | 0 | Jul | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
CAGUAS | 2022-07-22 18:38 | 2022-07-22 21:14 | 55 | 2:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO CAJA QUEMADA | C22072200098 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2022-07-22 | 8580 | keep | 0 | Jul | 2022 | 0.0058438 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
FAJARDO | 2022-07-22 19:07 | 2022-07-23 09:27 | 1 | 14:20 | P | NO SE REPORTO CAUSA | 1X8AMP. EN BANCO DE XMRS DE ELLOS | R22072200058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 860 | 2022-07-22 | 860 | keep | 0 | Jul | 2022 | 0.00058574 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-22 19:08 | 2022-07-22 21:41 | 80 | 2:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REFIRIO SITUACION DE DESGANCHE PARA ATENDER | M22072200143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-07-22 | 12240 | keep | 0 | Jul | 2022 | 0.0083366 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-07-22 19:26 | 2022-07-22 19:33 | 1444 | 0:07 | T | ARBOL SOBRE LINEA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR AVERIA DE LINEAS PRIMARIAS VIVAS EN SUELO A CAUSA DE ARBOL QUE CAYO SOBRE LAS LINEAS. SE CERRO INTERRUPTOR POR SCADA. LLEVA LA CARGA DEL 6014-01 | M22072200071 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 7 | 2022-07-22 | 10108 | keep | 0 | Jul | 2022 | 0.0068845 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-07-22 19:26 | 2022-07-22 19:33 | 3630 | 0:07 | T | ARBOL SOBRE LINEA | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR AVERIA DE LINEAS PRIMARIAS VIVAS EN SUELO A CAUSA DE ARBOL QUE CAYO SOBRE LAS LINEAS. SE CERRO INTERRUPTOR POR SCADA. LLEVA LA CARGA DEL 6014-01 | M22072200071 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 7 | 2022-07-22 | 25410 | keep | 0 | Jul | 2022 | 0.017307 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-07-22 19:33 | 2022-07-23 02:05 | 400 | 6:32 | P | ARBOL SOBRE LINEA | SE REPARO LINEA PRIMARIA Y SE CERRO MACHETES | M22072200071 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 392 | 2022-07-22 | 156800 | keep | 0 | Jul | 2022 | 0.1068 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-22 19:44 | 2022-07-23 09:11 | 27 | 13:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO PORTAFUSIBLES | S22072200340 | New_Event | Cutout Failure | Include | Include | Equipment | 807 | 2022-07-22 | 21789 | keep | 0 | Jul | 2022 | 0.01484 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CAGUAS | 2022-07-22 19:45 | 2022-07-22 20:38 | 76 | 0:53 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L NO CAUSA | C22072200107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2022-07-22 | 4028 | keep | 0 | Jul | 2022 | 0.0027435 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
MAYAGÃœEZ | 2022-07-22 20:27 | 2022-07-23 17:54 | 50 | 21:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L Y 1 X 15 EN XMR MAL TIEMPO LLUVIAS | P22072200081 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1287 | 2022-07-22 | 64350 | keep | 0 | Jul | 2022 | 0.043828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-07-22 20:30 | 2022-07-22 21:28 | 6 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES SECUNDARIOS | A22072200117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2022-07-22 | 348 | keep | 0 | Jul | 2022 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-07-22 20:31 | 2022-07-22 22:20 | 20 | 1:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | A22072200124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 109 | 2022-07-22 | 2180 | keep | 0 | Jul | 2022 | 0.0014848 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-07-22 20:34 | 2022-07-23 16:28 | 8 | 19:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | B22072200074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1194 | 2022-07-22 | 9552 | keep | 0 | Jul | 2022 | 0.0065058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-07-22 20:57 | 2022-07-23 10:56 | 130 | 13:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22072200120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 839 | 2022-07-22 | 109070 | keep | 0 | Jul | 2022 | 0.074287 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BARRANQUITAS | 2022-07-22 21:02 | 2022-07-23 09:42 | 10 | 12:40 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C22072200139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 760 | 2022-07-22 | 7600 | keep | 0 | Jul | 2022 | 0.0051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-07-22 21:16 | 2022-07-23 10:45 | 15 | 13:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1X25 EN C/L Y SE RETEZO CONDUCTOR PRIMARIO ARRIADO | R22072200062 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 809 | 2022-07-22 | 12135 | keep | 0 | Jul | 2022 | 0.0082651 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-07-22 21:57 | 2022-07-23 20:56 | 15 | 22:59 | P | EMPALME SOTERRADO AVERIADO | SE REPARO EMPALME SOTERRADO | B22072200075 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 1379 | 2022-07-22 | 20685 | keep | 0 | Jul | 2022 | 0.014088 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-07-22 21:57 | 2022-07-23 14:33 | 51 | 16:36 | P | EMPALME SOTERRADO AVERIADO | 1 X 50 EN SU-B, 1 X 40 EN CL DE AEREO PROVICIONAL Y 1 X 30 RISER | B22072200075 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 996 | 2022-07-22 | 50796 | keep | 0 | Jul | 2022 | 0.034597 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
VEGA BAJA | 2022-07-22 22:42 | 2022-07-23 10:50 | 30 | 12:08 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22072200091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 728 | 2022-07-22 | 21840 | keep | 0 | Jul | 2022 | 0.014875 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-22 22:49 | 2022-07-23 10:44 | 12 | 11:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B22072200094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 715 | 2022-07-22 | 8580 | keep | 0 | Jul | 2022 | 0.0058438 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-07-22 23:33 | 2022-07-23 05:45 | 45 | 6:12 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO Y REMPLAZO CAJA AVERIADA Y BAJANTE PRIMARIO | R22072200068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2022-07-22 | 16740 | keep | 0 | Jul | 2022 | 0.011402 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-07-22 23:39 | 2022-07-23 01:15 | 80 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072200227 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2022-07-22 | 7680 | keep | 0 | Jul | 2022 | 0.0052308 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-07-23 00:14 | 2022-07-23 02:23 | 255 | 2:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN C/L MAL TIEMPO LLUVIAS | R22072300002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 129 | 2022-07-23 | 32895 | keep | 0 | Jul | 2022 | 0.022405 | 0.00017368 | Sustained | FALSE | FALSE | Not_TMED_Event | 255
BAYAMON | 2022-07-23 00:23 | 2022-07-23 00:24 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 3070 | keep | 0 | Jul | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-07-23 00:24 | 2022-07-23 10:20 | 12 | 9:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22072300015 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 596 | 2022-07-23 | 7152 | keep | 0 | Jul | 2022 | 0.0048712 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-23 00:38 | 2022-07-23 08:48 | 97 | 8:10 | P | NO SE REPORTO CAUSA | 1 X 30 C/L | B22072300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 490 | 2022-07-23 | 47530 | keep | 0 | Jul | 2022 | 0.032372 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
YAUCO | 2022-07-23 02:39 | 2022-07-23 12:12 | 15 | 9:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22072300003 | New_Event | Cutout Failure | Include | Include | Equipment | 573 | 2022-07-23 | 8595 | keep | 0 | Jul | 2022 | 0.005854 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-07-23 03:28 | 2022-07-23 08:30 | 80 | 5:02 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN C/L TENSOR CRUZO BAJANTE | B22072300010 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 302 | 2022-07-23 | 24160 | keep | 0 | Jul | 2022 | 0.016455 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-07-23 03:29 | 2022-07-23 03:30 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 4006-05 CON CARGA 4003-01 | P22072300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 4132 | keep | 0 | Jul | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-07-23 03:29 | 2022-07-23 03:30 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 4006-05 CON CARGA 4003-02 | P22072300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 4279 | keep | 0 | Jul | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-07-23 03:29 | 2022-07-23 03:30 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO TIENE LA CARGA DEL 4003-01 Y 4003-02 | P22072300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 464 | keep | 0 | Jul | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
VEGA BAJA | 2022-07-23 03:36 | 2022-07-23 09:36 | 11 | 6:00 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | B22072300011 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 360 | 2022-07-23 | 3960 | keep | 0 | Jul | 2022 | 0.0026971 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-07-23 04:21 | 2022-07-23 11:21 | 50 | 7:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22072300001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 420 | 2022-07-23 | 21000 | keep | 0 | Jul | 2022 | 0.014303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-07-23 04:26 | 2022-07-23 04:27 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22072300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 4188 | keep | 0 | Jul | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
PONCE | 2022-07-23 05:32 | 2022-07-23 05:33 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22072300014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 2113 | keep | 0 | Jul | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
ARECIBO | 2022-07-23 06:10 | 2022-07-23 08:18 | 30 | 2:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072300003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 128 | 2022-07-23 | 3840 | keep | 0 | Jul | 2022 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-07-23 06:18 | 2022-07-23 09:25 | 3744 | 3:07 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR DEBIDO A LINEA PRIMARIA EN EL SUELO SE ABRIO C/L EN CARR 503 KM 4.4 BO TIBES Y SE COLOCO INTERRUPTOR EN SERVICIO | P22072300017 | New_Event | Primary Wire Break | Include | Include | Equipment | 187 | 2022-07-23 | 700128 | keep | 0 | Jul | 2022 | 0.47685 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
GUAYAMA | 2022-07-23 06:20 | 2022-07-23 11:10 | 40 | 4:50 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMA | P22072300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2022-07-23 | 11600 | keep | 0 | Jul | 2022 | 0.0079007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-07-23 06:35 | 2022-07-23 10:34 | 75 | 3:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-07-23 | 17925 | keep | 0 | Jul | 2022 | 0.012209 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-07-23 06:55 | 2022-07-23 12:20 | 357 | 5:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REMPLAZO CAJA | B22072300027 | New_Event | Cutout Failure | Include | Include | Equipment | 325 | 2022-07-23 | 116025 | keep | 0 | Jul | 2022 | 0.079024 | 0.00024315 | Sustained | FALSE | FALSE | Not_TMED_Event | 357
VEGA BAJA | 2022-07-23 07:00 | 2022-07-23 18:50 | 80 | 11:50 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22072300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 710 | 2022-07-23 | 56800 | keep | 0 | Jul | 2022 | 0.038686 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-07-23 07:17 | 2022-07-23 07:18 | 1417 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1417 | keep | 0 | Jul | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
MAYAGÃœEZ | 2022-07-23 07:35 | 2022-07-23 19:03 | 75 | 11:28 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | M22072300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 688 | 2022-07-23 | 51600 | keep | 0 | Jul | 2022 | 0.035145 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-07-23 07:48 | 2022-07-23 09:50 | 40 | 2:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072300005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-07-23 | 4880 | keep | 0 | Jul | 2022 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-07-23 07:57 | 2022-07-23 11:10 | 30 | 3:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-07-23 | 5790 | keep | 0 | Jul | 2022 | 0.0039435 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-07-23 08:00 | 2022-07-23 20:05 | 100 | 12:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M22072300124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 725 | 2022-07-23 | 72500 | keep | 0 | Jul | 2022 | 0.049379 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-07-23 08:21 | 2022-07-23 09:05 | 20 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON BAJANTES SECUNDARIOS QUEMADOS | C22072300020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2022-07-23 | 880 | keep | 0 | Jul | 2022 | 0.00059936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-07-23 08:29 | 2022-07-23 15:10 | 25 | 6:41 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22072300051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 401 | 2022-07-23 | 10025 | keep | 0 | Jul | 2022 | 0.006828 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-07-23 08:35 | 2022-07-23 16:34 | 50 | 7:59 | P | DESGANCHE | 1X 50 EN C/L DESGANCHE | P22072300054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 479 | 2022-07-23 | 23950 | keep | 0 | Jul | 2022 | 0.016312 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-07-23 08:38 | 2022-07-23 17:07 | 50 | 8:29 | P | ANIMAL | 1 X 50 EN C/L Y 1 X 10 EN XMR CRUCE X AVE | R22072300016 | New_Event | Animals | Include | Include | Wildlife | 509 | 2022-07-23 | 25450 | keep | 0 | Jul | 2022 | 0.017334 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-23 08:58 | 2022-07-23 12:50 | 405 | 3:52 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE SECCIONALIZO LINEAS PRIMARIAS PARTIDAS | M22072300030 | New_Event | Primary Wire Break | Include | Include | Equipment | 232 | 2022-07-23 | 93960 | keep | 0 | Jul | 2022 | 0.063996 | 0.00027584 | Sustained | FALSE | FALSE | Not_TMED_Event | 405
MAYAGÃœEZ | 2022-07-23 09:00 | 2022-07-23 22:20 | 80 | 13:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072300096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 800 | 2022-07-23 | 64000 | keep | 0 | Jul | 2022 | 0.04359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-23 09:03 | 2022-07-23 17:41 | 10 | 8:38 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO | B22072300062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 518 | 2022-07-23 | 5180 | keep | 0 | Jul | 2022 | 0.0035281 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-23 09:10 | 2022-07-23 13:10 | 112 | 4:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA | B22072300065 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2022-07-23 | 26880 | keep | 0 | Jul | 2022 | 0.018308 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
CANOVANAS | 2022-07-23 09:23 | 2022-07-23 13:33 | 2106 | 4:10 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR | R22072300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2022-07-23 | 526500 | keep | 0 | Jul | 2022 | 0.3586 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
PONCE | 2022-07-23 09:25 | 2022-07-23 12:30 | 50 | 3:05 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE C/L PARA SECCIONALIZAR AVERIA Y LEVANTAR LINEA PRIMARIA | P22072300066 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 185 | 2022-07-23 | 9250 | keep | 0 | Jul | 2022 | 0.0063001 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-23 09:25 | 2022-07-23 12:10 | 100 | 2:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22072300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-07-23 | 16500 | keep | 0 | Jul | 2022 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-07-23 09:27 | 2022-07-23 09:28 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-23 | 476 | keep | 0 | Jul | 2022 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-07-23 09:27 | 2022-07-23 09:28 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-23 | 1655 | keep | 0 | Jul | 2022 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-07-23 09:27 | 2022-07-23 09:28 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-23 | 361 | keep | 0 | Jul | 2022 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-07-23 09:27 | 2022-07-23 09:28 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-23 | 2842 | keep | 0 | Jul | 2022 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-07-23 09:27 | 2022-07-23 09:28 | 1702 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-23 | 1702 | keep | 0 | Jul | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-07-23 09:27 | 2022-07-23 09:28 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-23 | 918 | keep | 0 | Jul | 2022 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2022-07-23 09:27 | 2022-07-23 09:28 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-23 | 1725 | keep | 0 | Jul | 2022 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
AGUADILLA | 2022-07-23 09:31 | 2022-07-23 13:00 | 30 | 3:29 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-07-23 | 6270 | keep | 0 | Jul | 2022 | 0.0042705 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-07-23 09:35 | 2022-07-23 12:00 | 1 | 2:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L PORTA FUSIBLE AVERIADO | P22072300065 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2022-07-23 | 145 | keep | 0 | Jul | 2022 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-23 09:37 | 2022-07-23 09:38 | 681 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1520-02 QUE LLEVA EL 1530-09 | S22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 681 | keep | 0 | Jul | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-07-23 09:37 | 2022-07-23 09:38 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1520-02 QUE LLEVA EL 1530-09 | S22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1310 | keep | 0 | Jul | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-07-23 09:38 | 2022-07-23 11:49 | 61 | 2:11 | P | DESGANCHE | 1 X 80 EN C/L SE RETIRO RAMA | S22072300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-07-23 | 7991 | keep | 0 | Jul | 2022 | 0.0054426 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BARRANQUITAS | 2022-07-23 09:38 | 2022-07-23 11:42 | 24 | 2:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE SAFADO HACIA CAJA PRIMARIA | C22072300028 | New_Event | Primary Wire Break | Include | Include | Equipment | 124 | 2022-07-23 | 2976 | keep | 0 | Jul | 2022 | 0.0020269 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
HUMACAO | 2022-07-23 09:43 | 2022-07-23 12:14 | 100 | 2:31 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | C22072300034 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 151 | 2022-07-23 | 15100 | keep | 0 | Jul | 2022 | 0.010285 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-23 09:47 | 2022-07-23 13:45 | 45 | 3:58 | P | DESGANCHE | 1 X 65 EN C/L REALIZO DESGANCHE | R22072300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2022-07-23 | 10710 | keep | 0 | Jul | 2022 | 0.0072945 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-07-23 09:49 | 2022-07-23 11:20 | 250 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 65 EN CORTES DE LINEA DISTINTOS MAL TIEMPO VIENTOS FUERTES | M22072300040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2022-07-23 | 22750 | keep | 0 | Jul | 2022 | 0.015495 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2022-07-23 09:58 | 2022-07-23 09:59 | 1245 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
SAN JUAN | 2022-07-23 10:17 | 2022-07-23 10:19 | 4398 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-23 | 8796 | keep | 0 | Jul | 2022 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
VEGA BAJA | 2022-07-23 10:20 | 2022-07-23 16:49 | 500 | 6:29 | P | LINEA DE TRANSMISION 38KV | OVER HEAD DE LINEA 2200 SOBRE PRIMARIA SE REMOVIO OVERHEAD Y SE REALIZO DESGANCHE, 3 X 100 EN C/L | B22072300081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 389 | 2022-07-23 | 194500 | keep | 0 | Jul | 2022 | 0.13247 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
FAJARDO | 2022-07-23 10:31 | 2022-07-23 12:36 | 6 | 2:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REMPLAZO CAJA PRIMARIA | R22072300067 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2022-07-23 | 750 | keep | 0 | Jul | 2022 | 0.00051082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-07-23 10:33 | 2022-07-23 15:30 | 30 | 4:57 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y 1 X 80 EN C/L | S22072300023 | New_Event | Primary Wire Break | Include | Include | Equipment | 297 | 2022-07-23 | 8910 | keep | 0 | Jul | 2022 | 0.0060686 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-07-23 10:34 | 2022-07-23 12:20 | 40 | 1:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072300069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-07-23 | 4240 | keep | 0 | Jul | 2022 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-23 10:46 | 2022-07-23 10:47 | 4664 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072300072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 4664 | keep | 0 | Jul | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
BAYAMON | 2022-07-23 10:46 | 2022-07-23 13:30 | 25 | 2:44 | P | ANIMAL | 1 X 20 EN C/L SE RETIRO AVE | B22072300092 | New_Event | Animals | Include | Include | Wildlife | 164 | 2022-07-23 | 4100 | keep | 0 | Jul | 2022 | 0.0027925 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-07-23 10:52 | 2022-07-23 20:34 | 15 | 9:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072300021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 582 | 2022-07-23 | 8730 | keep | 0 | Jul | 2022 | 0.005946 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-07-23 10:56 | 2022-07-23 10:57 | 4538 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 30% POR 1619-02 | S2207230000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 4538 | keep | 0 | Jul | 2022 | 0.0030908 | 0.0030908 | Momentary | FALSE | FALSE | Not_TMED_Event | 4538
MAYAGÃœEZ | 2022-07-23 10:57 | 2022-07-23 21:50 | 50 | 10:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072300079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 653 | 2022-07-23 | 32650 | keep | 0 | Jul | 2022 | 0.022238 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-07-23 11:13 | 2022-07-23 22:08 | 60 | 10:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE MASIVO | A22072300023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 655 | 2022-07-23 | 39300 | keep | 0 | Jul | 2022 | 0.026767 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-07-23 11:16 | 2022-07-23 20:03 | 30 | 8:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072300024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 527 | 2022-07-23 | 15810 | keep | 0 | Jul | 2022 | 0.010768 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-07-23 11:18 | 2022-07-23 11:20 | 6244 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22072300026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-23 | 12488 | keep | 0 | Jul | 2022 | 0.0085055 | 0.0042528 | Momentary | FALSE | FALSE | Not_TMED_Event | 6244
BARRANQUITAS | 2022-07-23 11:21 | 2022-07-23 11:23 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-23 | 1740 | keep | 0 | Jul | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2022-07-23 11:32 | 2022-07-23 14:27 | 70 | 2:55 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE RETEZO CONDUCTOR PRIMARIO | C22072300055 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 175 | 2022-07-23 | 12250 | keep | 0 | Jul | 2022 | 0.0083434 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-07-23 11:34 | 2022-07-23 16:17 | 2276 | 4:43 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 283 | 2022-07-23 | 644108 | keep | 0 | Jul | 2022 | 0.4387 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-07-23 11:34 | 2022-07-23 16:17 | 777 | 4:43 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 283 | 2022-07-23 | 219891 | keep | 0 | Jul | 2022 | 0.14977 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-07-23 11:34 | 2022-07-23 16:17 | 12 | 4:43 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 283 | 2022-07-23 | 3396 | keep | 0 | Jul | 2022 | 0.002313 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-07-23 11:34 | 2022-07-23 16:17 | 1290 | 4:43 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22072300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 283 | 2022-07-23 | 365070 | keep | 0 | Jul | 2022 | 0.24865 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
AGUADILLA | 2022-07-23 11:37 | 2022-07-23 16:45 | 30 | 5:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22072300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-07-23 | 9240 | keep | 0 | Jul | 2022 | 0.0062933 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-07-23 11:42 | 2022-07-23 14:37 | 3 | 2:55 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE CON AVE | C22073000058 | New_Event | Animals | Include | Include | Wildlife | 175 | 2022-07-23 | 525 | keep | 0 | Jul | 2022 | 0.00035758 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-07-23 11:42 | 2022-07-23 12:57 | 60 | 1:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22072300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-07-23 | 4500 | keep | 0 | Jul | 2022 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-07-23 11:47 | 2022-07-23 12:09 | 73 | 0:22 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C22072300110 | New_Event | Animals | Include | Include | Wildlife | 22 | 2022-07-23 | 1606 | keep | 0 | Jul | 2022 | 0.0010938 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2022-07-23 11:53 | 2022-07-23 14:15 | 30 | 2:22 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22072300113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-07-23 | 4260 | keep | 0 | Jul | 2022 | 0.0029015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-07-23 11:53 | 2022-07-23 11:54 | 11 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22072300087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 11 | keep | 0 | Jul | 2022 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-07-23 12:07 | 2022-07-23 14:00 | 50 | 1:53 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R22072300116 | New_Event | Animals | Include | Include | Wildlife | 113 | 2022-07-23 | 5650 | keep | 0 | Jul | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-23 12:10 | 2022-07-23 18:47 | 100 | 6:37 | P | DESGANCHE | DESGANCHE Y 2 X 50 EN C/L | B22072300128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 397 | 2022-07-23 | 39700 | keep | 0 | Jul | 2022 | 0.027039 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-23 12:12 | 2022-07-23 16:35 | 23 | 4:23 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | B22072300129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2022-07-23 | 6049 | keep | 0 | Jul | 2022 | 0.0041199 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-07-23 12:16 | 2022-07-23 18:20 | 8 | 6:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22072300132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 364 | 2022-07-23 | 2912 | keep | 0 | Jul | 2022 | 0.0019833 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-07-23 12:17 | 2022-07-23 16:20 | 25 | 4:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22072300031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-07-23 | 6075 | keep | 0 | Jul | 2022 | 0.0041377 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-07-23 12:19 | 2022-07-23 17:30 | 30 | 5:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M22072300095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-07-23 | 9330 | keep | 0 | Jul | 2022 | 0.0063546 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-07-23 12:20 | 2022-07-23 12:30 | 100 | 0:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22072300119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-07-23 | 1000 | keep | 0 | Jul | 2022 | 0.0006811 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-07-23 12:20 | 2022-07-24 09:28 | 60 | 21:08 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA SE RETIROO LAGARTIJO | C22072300271 | New_Event | Animals | Include | Include | Wildlife | 1268 | 2022-07-23 | 76080 | keep | 0 | Jul | 2022 | 0.051818 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-23 12:30 | 2022-07-23 17:56 | 6 | 5:26 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE REALIZO DESGANCHE SECUNDARIO | S22072300045 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 326 | 2022-07-23 | 1956 | keep | 0 | Jul | 2022 | 0.0013322 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-07-23 12:33 | 2022-07-23 14:05 | 36 | 1:32 | P | DESGANCHE | 1 X 65 EN C/L | S22072300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-07-23 | 3312 | keep | 0 | Jul | 2022 | 0.0022558 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BARRANQUITAS | 2022-07-23 12:34 | 2022-07-24 10:11 | 50 | 21:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C22072300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1297 | 2022-07-23 | 64850 | keep | 0 | Jul | 2022 | 0.044169 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-07-23 12:41 | 2022-07-23 17:26 | 7 | 4:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO MACETILLA QUEMADA | A22072300033 | New_Event | Cutout Failure | Include | Include | Equipment | 285 | 2022-07-23 | 1995 | keep | 0 | Jul | 2022 | 0.0013588 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-07-23 12:44 | 2022-07-23 17:34 | 40 | 4:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | P22072300097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 290 | 2022-07-23 | 11600 | keep | 0 | Jul | 2022 | 0.0079007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-23 12:46 | 2022-07-24 12:10 | 30 | 23:24 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22072300148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1404 | 2022-07-23 | 42120 | keep | 0 | Jul | 2022 | 0.028688 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-07-23 12:50 | 2022-07-23 16:55 | 130 | 4:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO Y SE CERRO PUENTES | M22072300030 | New_Event | Primary Wire Break | Include | Include | Equipment | 245 | 2022-07-23 | 31850 | keep | 0 | Jul | 2022 | 0.021693 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2022-07-23 12:52 | 2022-07-23 15:28 | 200 | 2:36 | P | DESGANCHE | 2 X 100 EN C/L | B22072300151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-07-23 | 31200 | keep | 0 | Jul | 2022 | 0.02125 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-07-23 12:57 | 2022-07-23 12:58 | 1825 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072300100 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-23 | 1825 | keep | 0 | Jul | 2022 | 0.001243 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-23 12:58 | 2022-07-23 17:16 | 65 | 4:18 | P | CABLE SOTERRADO AVERIADO | SE REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L 1 X 50 EN C/L 1 X 40 EN RISER SE DEJO FUERA DEL T-2 HACIA T-1 | B22072300153 | New_Event | UG Cable Fault | Include | Include | Equipment | 258 | 2022-07-23 | 16770 | keep | 0 | Jul | 2022 | 0.011422 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-07-23 12:58 | 2022-07-23 13:12 | 60 | 0:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22072300088 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-07-23 | 840 | keep | 0 | Jul | 2022 | 0.00057212 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-23 13:05 | 2022-07-23 18:12 | 6 | 5:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR REALIZO DESGANCHE | C22072300088 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 307 | 2022-07-23 | 1842 | keep | 0 | Jul | 2022 | 0.0012546 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-07-23 13:07 | 2022-07-23 13:56 | 1565 | 0:49 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C22072300089 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 49 | 2022-07-23 | 76685 | keep | 0 | Jul | 2022 | 0.05223 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BAYAMON | 2022-07-23 13:10 | 2022-07-23 16:06 | 15 | 2:56 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | ABRIR XMR SE REMPLAZO POSTE SECUNDARIO | B22072300157 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 176 | 2022-07-23 | 2640 | keep | 0 | Jul | 2022 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-07-23 13:12 | 2022-07-23 13:13 | 1825 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072300103 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-23 | 1825 | keep | 0 | Jul | 2022 | 0.001243 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-07-23 13:13 | 2022-07-23 15:10 | 20 | 1:57 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | R22072300136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2022-07-23 | 2340 | keep | 0 | Jul | 2022 | 0.0015938 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-07-23 13:13 | 2022-07-23 14:10 | 60 | 0:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22072300088 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-07-23 | 3420 | keep | 0 | Jul | 2022 | 0.0023293 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-07-23 13:20 | 2022-07-23 13:21 | 2286 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22072300142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 2286 | keep | 0 | Jul | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
PONCE | 2022-07-23 13:27 | 2022-07-23 15:50 | 50 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO VIENTOS | P22072300107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2022-07-23 | 7150 | keep | 0 | Jul | 2022 | 0.0048698 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-23 13:33 | 2022-07-24 09:53 | 30 | 20:20 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE DESPEGO BAJANTE PRIMARIO TRANSFORMADOR | S22072300066 | New_Event | Primary Wire Break | Include | Include | Equipment | 1220 | 2022-07-23 | 36600 | keep | 0 | Jul | 2022 | 0.024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-23 13:33 | 2022-07-23 14:33 | 526 | 1:00 | P | DESGANCHE | SE REALIZO DESGANCHE EN VARIOS PUNTOS, SE REMPLAZO DISCO Y ELIMINO BANCO DE CAPACITORES EN DESHUSO | R22072300022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-07-23 | 31560 | keep | 0 | Jul | 2022 | 0.021495 | 0.00035826 | Sustained | FALSE | FALSE | Not_TMED_Event | 526
GUAYAMA | 2022-07-23 13:48 | 2022-07-23 13:49 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 4006-05 CON CARGA DEL 4003-01 | P22072300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 4132 | keep | 0 | Jul | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-07-23 13:48 | 2022-07-23 13:49 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 4006-05 CON CARGA 4003-02 | P22072300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 4279 | keep | 0 | Jul | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-07-23 13:48 | 2022-07-23 13:49 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO TIENE LA CARGA DEL 4003-01 Y 4003-02 | P22072300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 464 | keep | 0 | Jul | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
BARRANQUITAS | 2022-07-23 13:56 | 2022-07-23 15:22 | 626 | 1:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | ESPACIADORES EN LA LINEA ROTOS | C22072300089 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 86 | 2022-07-23 | 53836 | keep | 0 | Jul | 2022 | 0.036667 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-23 14:01 | 2022-07-23 15:15 | 250 | 1:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M22072300115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 74 | 2022-07-23 | 18500 | keep | 0 | Jul | 2022 | 0.0126 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-07-23 14:06 | 2022-07-23 17:26 | 36 | 3:20 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22072300046 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-07-23 | 7200 | keep | 0 | Jul | 2022 | 0.0049039 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-23 14:17 | 2022-07-23 18:05 | 70 | 3:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | M22072300123 | New_Event | Primary Wire Break | Include | Include | Equipment | 228 | 2022-07-23 | 15960 | keep | 0 | Jul | 2022 | 0.01087 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-07-23 14:19 | 2022-07-24 00:30 | 50 | 10:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072300127 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 611 | 2022-07-23 | 30550 | keep | 0 | Jul | 2022 | 0.020807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-07-23 14:33 | 2022-07-23 14:40 | 2106 | 0:07 | T | DESGANCHE | DISPARO, PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR LA AVERIA | R22072300022 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-07-23 | 14742 | keep | 0 | Jul | 2022 | 0.010041 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-23 14:36 | 2022-07-23 18:30 | 90 | 3:54 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | M22072300135 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 234 | 2022-07-23 | 21060 | keep | 0 | Jul | 2022 | 0.014344 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-07-23 14:40 | 2022-07-23 15:24 | 526 | 0:44 | P | DESGANCHE | SE REALIZO DESGANCHE EN VARIOS PUNTOS, SE REMPLAZO DISCO Y ELIMINO BANCO DE CAPACITORES EN DESHUSO | R22072300022 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-07-23 | 23144 | keep | 0 | Jul | 2022 | 0.015763 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-07-23 15:01 | 2022-07-23 16:26 | 80 | 1:25 | P | DESGANCHE | 1 X 65 EN C/L REALIZO DESGANCHE | R22072300176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-07-23 | 6800 | keep | 0 | Jul | 2022 | 0.0046314 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-07-23 15:09 | 2022-07-23 15:10 | 2906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 2906 | keep | 0 | Jul | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2022-07-23 15:22 | 2022-07-23 15:23 | 1565 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO | C22072300089 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-07-23 | 1565 | keep | 0 | Jul | 2022 | 0.0010659 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-07-23 15:23 | 2022-07-23 17:08 | 626 | 1:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON ESPACIADORES EN LA LINEA ROTOS Y SE LLEVO LINEA AL CABLE GUIA | C22072300089 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 105 | 2022-07-23 | 65730 | keep | 0 | Jul | 2022 | 0.044768 | 0.00042637 | Sustained | FALSE | FALSE | Not_TMED_Event | 626
CANOVANAS | 2022-07-23 15:55 | 2022-07-23 17:56 | 30 | 2:01 | P | ARBOL SOBRE LINEA | ABRIO C/L PARA RETIRAR ARBOL DE LAS LINEAS Y LEVANTAR SECUNDARIA | R22072300184 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 121 | 2022-07-23 | 3630 | keep | 0 | Jul | 2022 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-07-23 16:14 | 2022-07-23 16:15 | 1245 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
CANOVANAS | 2022-07-23 16:17 | 2022-07-23 18:13 | 1 | 1:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | R22072300189 | New_Event | Cutout Failure | Include | Include | Equipment | 116 | 2022-07-23 | 116 | keep | 0 | Jul | 2022 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-23 16:17 | 2022-07-23 19:50 | 10 | 3:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22072300199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-07-23 | 2130 | keep | 0 | Jul | 2022 | 0.0014507 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-07-23 16:24 | 2022-07-23 17:49 | 934 | 1:25 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | M22072300220 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-07-23 | 79390 | keep | 0 | Jul | 2022 | 0.054072 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-07-23 16:24 | 2022-07-23 17:49 | 4 | 1:25 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | M22072300220 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-07-23 | 340 | keep | 0 | Jul | 2022 | 0.00023157 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-07-23 16:24 | 2022-07-23 17:49 | 1479 | 1:25 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | M22072300220 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-07-23 | 125715 | keep | 0 | Jul | 2022 | 0.085624 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-07-23 16:24 | 2022-07-23 17:49 | 1841 | 1:25 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22072300221 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-07-23 | 156485 | keep | 0 | Jul | 2022 | 0.10658 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-07-23 16:24 | 2022-07-23 17:49 | 1950 | 1:25 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22072300221 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 85 | 2022-07-23 | 165750 | keep | 0 | Jul | 2022 | 0.11289 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
BARRANQUITAS | 2022-07-23 16:30 | 2022-07-23 17:46 | 275 | 1:16 | P | ARBOL SOBRE LINEA | 3 X 100 EN CORTES DE LINEA SE RETIRO ARBOL SOBRE LINEAS | C22072300235 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 76 | 2022-07-23 | 20900 | keep | 0 | Jul | 2022 | 0.014235 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
BARRANQUITAS | 2022-07-23 16:38 | 2022-07-23 17:45 | 133 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22072300239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-07-23 | 8911 | keep | 0 | Jul | 2022 | 0.0060692 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:01 | 4132 | 1:08 | T | LINEA DE TRANSMISION 38KV | OVER HEAD PARTIDO DE LINEA 3700 CRUZO LINEAS DE ALIMENTADOR LLEVA CARGA DE 4003-01 Y 4003-02 SON 8875 CLIENTES | P22072300195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-07-23 | 280976 | keep | 0 | Jul | 2022 | 0.19137 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:01 | 4279 | 1:08 | T | LINEA DE TRANSMISION 38KV | OVER HEAD PARTIDO DE LINEA 3700 CRUZO LINEAS DE ALIMENTADOR LLEVA CARGA DE 4003-01 Y 4003-02 SON 8875 CLIENTES | P22072300195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-07-23 | 290972 | keep | 0 | Jul | 2022 | 0.19818 | 0.0029144 | Sustained | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:01 | 464 | 1:08 | T | LINEA DE TRANSMISION 38KV | OVER HEAD PARTIDO DE LINEA 3700 CRUZO LINEAS DE ALIMENTADOR LLEVA CARGA DE 4003-01 Y 4003-02 SON 8875 CLIENTES | P22072300195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-07-23 | 31552 | keep | 0 | Jul | 2022 | 0.02149 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 2100 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 153300 | keep | 0 | Jul | 2022 | 0.10441 | 0.0014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 2100
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 922 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 67306 | keep | 0 | Jul | 2022 | 0.045842 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 1676 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 122348 | keep | 0 | Jul | 2022 | 0.083331 | 0.0011415 | Sustained | FALSE | FALSE | Not_TMED_Event | 1676
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 2844 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 207612 | keep | 0 | Jul | 2022 | 0.1414 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 2775 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 202575 | keep | 0 | Jul | 2022 | 0.13797 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 1457 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 106361 | keep | 0 | Jul | 2022 | 0.072442 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 1086 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 79278 | keep | 0 | Jul | 2022 | 0.053996 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 2134 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 155782 | keep | 0 | Jul | 2022 | 0.1061 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 1464 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 106872 | keep | 0 | Jul | 2022 | 0.07279 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 1833 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 133809 | keep | 0 | Jul | 2022 | 0.091137 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 1565 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 114245 | keep | 0 | Jul | 2022 | 0.077812 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-07-23 16:53 | 2022-07-23 18:06 | 977 | 1:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | P22072300394 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 73 | 2022-07-23 | 71321 | keep | 0 | Jul | 2022 | 0.048576 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
ARECIBO | 2022-07-23 16:58 | 2022-07-23 21:26 | 1 | 4:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22072300141 | New_Event | Cutout Failure | Include | Include | Equipment | 268 | 2022-07-23 | 268 | keep | 0 | Jul | 2022 | 0.00018253 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-23 17:00 | 2022-07-23 19:38 | 18 | 2:38 | P | TRANSFORMADOR AVERIADO | 1 X 25 EN XMR REMPLAZO XMR QUEMADO DE 37.5 KVA X 37.5 KVA | C22072300241 | New_Event | Service Transformer Failure | Include | Include | Equipment | 158 | 2022-07-23 | 2844 | keep | 0 | Jul | 2022 | 0.001937 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-07-23 17:02 | 2022-07-23 17:03 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1702 | keep | 0 | Jul | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
HUMACAO | 2022-07-23 17:11 | 2022-07-23 19:17 | 80 | 2:06 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22072300247 | New_Event | Animals | Include | Include | Wildlife | 126 | 2022-07-23 | 10080 | keep | 0 | Jul | 2022 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-07-23 17:12 | 2022-07-23 23:11 | 30 | 5:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO SE ENCONTRO CAUSA | P22072300396 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 359 | 2022-07-23 | 10770 | keep | 0 | Jul | 2022 | 0.0073354 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-23 17:16 | 2022-07-24 19:30 | 30 | 26:14 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVICIONAL DEL T-2 AL T-1 | B22072300153 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1574 | 2022-07-23 | 47220 | keep | 0 | Jul | 2022 | 0.032161 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-07-23 17:43 | 2022-07-23 22:00 | 187 | 4:17 | P | ANIMAL | 1 X 40 EN C/L CRUCE DE FASE POR AVE | P22072300284 | New_Event | Animals | Include | Include | Wildlife | 257 | 2022-07-23 | 48059 | keep | 0 | Jul | 2022 | 0.032733 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
SAN JUAN | 2022-07-23 17:55 | 2022-07-23 17:56 | 164 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SU CARGA POR 1531-02 | S22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 164 | keep | 0 | Jul | 2022 | 0.0001117 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
PONCE | 2022-07-23 17:59 | 2022-07-24 11:05 | 100 | 17:06 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22072300314 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1026 | 2022-07-23 | 102600 | keep | 0 | Jul | 2022 | 0.06988 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-23 18:05 | 2022-07-23 18:06 | 164 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SU CARGA POR 1531-02 | S22072300000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 164 | keep | 0 | Jul | 2022 | 0.0001117 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-07-23 18:06 | 2022-07-23 21:06 | 250 | 3:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PROVICIONAL AEREO Y 1 X 100 EN SU-3 | B22072300215 | New_Event | Primary Wire Break | Include | Include | Equipment | 180 | 2022-07-23 | 45000 | keep | 0 | Jul | 2022 | 0.030649 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2022-07-23 18:13 | 2022-07-24 13:29 | 30 | 19:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22072300218 | New_Event | Cutout Failure | Include | Include | Equipment | 1156 | 2022-07-23 | 34680 | keep | 0 | Jul | 2022 | 0.02362 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-23 18:29 | 2022-07-23 18:30 | 1647 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22072300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1647 | keep | 0 | Jul | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
CANOVANAS | 2022-07-23 18:58 | 2022-07-23 20:08 | 7 | 1:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22072300198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-07-23 | 490 | keep | 0 | Jul | 2022 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-07-23 19:00 | 2022-07-23 19:01 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2207230000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 2234 | keep | 0 | Jul | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CANOVANAS | 2022-07-23 19:23 | 2022-07-23 19:24 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22072300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1648 | keep | 0 | Jul | 2022 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
PONCE | 2022-07-23 19:25 | 2022-07-23 19:26 | 1979 | 0:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSAS RECIERRE | P22072300356 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 1979 | keep | 0 | Jul | 2022 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
MAYAGÃœEZ | 2022-07-23 19:26 | 2022-07-24 08:43 | 20 | 13:17 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M22072300201 | New_Event | Animals | Include | Include | Wildlife | 797 | 2022-07-23 | 15940 | keep | 0 | Jul | 2022 | 0.010857 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-07-23 19:38 | 2022-07-23 21:49 | 1 | 2:11 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22072300223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-07-23 | 131 | keep | 0 | Jul | 2022 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-07-23 19:56 | 2022-07-24 13:34 | 10 | 17:38 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P22072300365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1058 | 2022-07-23 | 10580 | keep | 0 | Jul | 2022 | 0.007206 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-23 20:09 | 2022-07-23 21:10 | 30 | 1:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072300225 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-07-23 | 1830 | keep | 0 | Jul | 2022 | 0.0012464 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-07-23 20:16 | 2022-07-23 23:17 | 100 | 3:01 | P | CONDUCTOR ROTO O ABIERTO | 2 X 200 C/L SE REPARO NEUTRAL PRIMARIO | P22072300371 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2022-07-23 | 18100 | keep | 0 | Jul | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-07-23 20:19 | 2022-07-23 22:26 | 25 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072300227 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2022-07-23 | 3175 | keep | 0 | Jul | 2022 | 0.0021625 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-07-23 20:30 | 2022-07-24 09:05 | 50 | 12:35 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE | C22072300269 | New_Event | Animals | Include | Include | Wildlife | 755 | 2022-07-23 | 37750 | keep | 0 | Jul | 2022 | 0.025711 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-23 20:51 | 2022-07-24 01:23 | 238 | 4:32 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y 1 X 100 EN C/L | S22072300123 | New_Event | Primary Wire Break | Include | Include | Equipment | 272 | 2022-07-23 | 64736 | keep | 0 | Jul | 2022 | 0.044091 | 0.0001621 | Sustained | FALSE | FALSE | Not_TMED_Event | 238
BAYAMON | 2022-07-23 20:56 | 2022-07-24 09:46 | 11 | 12:50 | P | TERMINACION SOTERRADA AVERIADA | SE REMPLAZO PISTOLA EN T-5 1 X 15 EN PROVISIONAL | B22072300237 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 770 | 2022-07-23 | 8470 | keep | 0 | Jul | 2022 | 0.0057689 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-07-23 21:23 | 2022-07-24 12:55 | 4 | 15:32 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B22072300243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 932 | 2022-07-23 | 3728 | keep | 0 | Jul | 2022 | 0.0025391 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-07-23 21:27 | 2022-07-24 03:03 | 40 | 5:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES EN SALIDA DEL TRANSFORMADOR | M22072300218 | New_Event | Secondary Wire Break | Include | Include | Equipment | 336 | 2022-07-23 | 13440 | keep | 0 | Jul | 2022 | 0.0091539 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-23 21:39 | 2022-07-24 05:43 | 10 | 8:04 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072300220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 484 | 2022-07-23 | 4840 | keep | 0 | Jul | 2022 | 0.0032965 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-07-23 23:20 | 2022-07-24 10:54 | 4 | 11:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRASFORMADOR | C22072300273 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 694 | 2022-07-23 | 2776 | keep | 0 | Jul | 2022 | 0.0018907 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-07-23 23:50 | 2022-07-23 23:51 | 240 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22072300207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-23 | 240 | keep | 0 | Jul | 2022 | 0.00016346 | 0.00016346 | Momentary | FALSE | FALSE | Not_TMED_Event | 240
SAN JUAN | 2022-07-24 00:11 | 2022-07-24 09:44 | 28 | 9:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | S22072400001 | New_Event | Cutout Failure | Include | Include | Equipment | 573 | 2022-07-24 | 16044 | keep | 0 | Jul | 2022 | 0.010927 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
PONCE | 2022-07-24 00:11 | 2022-07-24 00:12 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22072400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 3744 | keep | 0 | Jul | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
SAN JUAN | 2022-07-24 00:52 | 2022-07-24 00:55 | 1825 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22072400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-07-24 | 5475 | keep | 0 | Jul | 2022 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2022-07-24 01:21 | 2022-07-24 14:30 | 50 | 13:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 789 | 2022-07-24 | 39450 | keep | 0 | Jul | 2022 | 0.026869 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-07-24 01:32 | 2022-07-24 09:00 | 2 | 7:28 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A22072400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 448 | 2022-07-24 | 896 | keep | 0 | Jul | 2022 | 0.00061026 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-07-24 01:33 | 2022-07-24 01:34 | 1859 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE LLUVIA FUERTE | B22072400005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-07-24 | 1859 | keep | 0 | Jul | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2022-07-24 01:34 | 2022-07-24 09:23 | 100 | 7:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | B22072400010 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 469 | 2022-07-24 | 46900 | keep | 0 | Jul | 2022 | 0.031943 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-07-24 01:43 | 2022-07-24 11:02 | 30 | 9:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN RISER SE RETORNO CONDUCTOR SAFADO DE RISER A CAJA | R22072400001 | New_Event | Primary Wire Break | Include | Include | Equipment | 559 | 2022-07-24 | 16770 | keep | 0 | Jul | 2022 | 0.011422 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-24 02:57 | 2022-07-24 22:49 | 200 | 19:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22072400009 | New_Event | Cutout Failure | Include | Include | Equipment | 1192 | 2022-07-24 | 238400 | keep | 0 | Jul | 2022 | 0.16237 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-07-24 03:49 | 2022-07-24 03:51 | 1825 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22072400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-07-24 | 3650 | keep | 0 | Jul | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-07-24 03:53 | 2022-07-24 03:55 | 892 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22072400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-24 | 1784 | keep | 0 | Jul | 2022 | 0.0012151 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
CANOVANAS | 2022-07-24 04:26 | 2022-07-24 09:57 | 12 | 5:31 | P | CABLE SOTERRADO AVERIADO | 1 X 65 EN RISER AVERIA DEL SU2 A SU4 SE JUMPIO FASE | R22072400005 | New_Event | UG Cable Fault | Include | Include | Equipment | 331 | 2022-07-24 | 3972 | keep | 0 | Jul | 2022 | 0.0027053 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-07-24 04:28 | 2022-07-24 08:51 | 100 | 4:23 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072400013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2022-07-24 | 26300 | keep | 0 | Jul | 2022 | 0.017913 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-07-24 05:18 | 2022-07-24 05:19 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22072400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 527 | keep | 0 | Jul | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
AGUADILLA | 2022-07-24 05:19 | 2022-07-24 11:05 | 40 | 5:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072400003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 346 | 2022-07-24 | 13840 | keep | 0 | Jul | 2022 | 0.0094264 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-24 05:26 | 2022-07-24 19:35 | 300 | 14:09 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO | M22072400015 | New_Event | Primary Pole Failure | Include | Include | Equipment | 849 | 2022-07-24 | 254700 | keep | 0 | Jul | 2022 | 0.17348 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-07-24 05:27 | 2022-07-24 05:29 | 68 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1102-01 LLEVANDO CARGA 1102-04, 1102-05, 1105-04 Y 1105-05 SE CERRO POR SCADA | S22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-24 | 136 | keep | 0 | Jul | 2022 | 9.2629e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-07-24 05:27 | 2022-07-24 05:29 | 536 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1102-01 LLEVANDO CARGA 1102-04, 1102-05, 1105-04 Y 1105-05 SE CERRO POR SCADA | S22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-24 | 1072 | keep | 0 | Jul | 2022 | 0.00073013 | 0.00036507 | Momentary | FALSE | FALSE | Not_TMED_Event | 536
SAN JUAN | 2022-07-24 05:27 | 2022-07-24 05:29 | 348 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1102-01 | S22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-24 | 696 | keep | 0 | Jul | 2022 | 0.00047404 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-07-24 05:27 | 2022-07-24 05:29 | 559 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1102-01 LLEVANDO CARGA 1102-04, 1102-05, 1105-04 Y 1105-05 SE CERRO POR SCADA | S22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-24 | 1118 | keep | 0 | Jul | 2022 | 0.00076146 | 0.00038073 | Momentary | FALSE | FALSE | Not_TMED_Event | 559
SAN JUAN | 2022-07-24 05:27 | 2022-07-24 05:29 | 370 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1102-01 LLEVANDO CARGA 1102-04, 1102-05, 1105-04 Y 1105-05 SE CERRO POR SCADA | S22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-24 | 740 | keep | 0 | Jul | 2022 | 0.00050401 | 0.00025201 | Momentary | FALSE | FALSE | Not_TMED_Event | 370
MAYAGÃœEZ | 2022-07-24 05:43 | 2022-07-24 05:45 | 1444 | 0:02 | T | DESGANCHE | DISPARO DEL INTERRUPTOR 6014-02 EL CUAL LLEVA LA CARGA DEL 6014-01 | M22072400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-07-24 | 2888 | keep | 0 | Jul | 2022 | 0.001967 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-07-24 05:43 | 2022-07-24 05:45 | 3630 | 0:02 | T | DESGANCHE | DISPARO DEL INTERRUPTOR LLEVA LA CARGA DEL 6014-01 | M22072400019 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-07-24 | 7260 | keep | 0 | Jul | 2022 | 0.0049448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-24 05:46 | 2022-07-24 11:46 | 10 | 6:00 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072300220 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 360 | 2022-07-24 | 3600 | keep | 0 | Jul | 2022 | 0.0024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-07-24 06:15 | 2022-07-24 06:16 | 1394 | 0:01 | T | ANIMAL | RECIERRE | R22072400000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-07-24 | 1394 | keep | 0 | Jul | 2022 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2022-07-24 06:16 | 2022-07-24 11:47 | 55 | 5:31 | P | ANIMAL | 1 X 65 EN C/L AVE | R22072400007 | 1st_after_momentary | Animals | Include | Include | Wildlife | 331 | 2022-07-24 | 18205 | keep | 0 | Jul | 2022 | 0.012399 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
VEGA BAJA | 2022-07-24 06:23 | 2022-07-24 10:35 | 1 | 4:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072400023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 252 | 2022-07-24 | 252 | keep | 0 | Jul | 2022 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-07-24 06:36 | 2022-07-24 09:15 | 40 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072400008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2022-07-24 | 6360 | keep | 0 | Jul | 2022 | 0.0043318 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-07-24 06:38 | 2022-07-24 14:55 | 59 | 8:17 | P | DESGANCHE | SE REALIZO DEGANCHE 1 X 65 EN C/L | B22072400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2022-07-24 | 29323 | keep | 0 | Jul | 2022 | 0.019972 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
PONCE | 2022-07-24 06:46 | 2022-07-24 08:35 | 70 | 1:49 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P22072400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-07-24 | 7630 | keep | 0 | Jul | 2022 | 0.0051968 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-07-24 06:50 | 2022-07-24 09:31 | 55 | 2:41 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22072400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-07-24 | 8855 | keep | 0 | Jul | 2022 | 0.0060311 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-07-24 07:12 | 2022-07-24 07:51 | 207 | 0:39 | T | NO SE REPORTO CAUSA | DISPARO SE LIMPIARON BANDERAS Y NO OPERA POR CONTROL NI ELECTRICAMENTE SE OPERO MECANICAMENTE 100% EN SERVICIO | S22072400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2022-07-24 | 8073 | keep | 0 | Jul | 2022 | 0.0054985 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
BAYAMON | 2022-07-24 07:35 | 2022-07-24 11:45 | 204 | 4:10 | P | ANIMAL | 1 X 80 SE REMOVIO AVE | B22072400024 | New_Event | Animals | Include | Include | Wildlife | 250 | 2022-07-24 | 51000 | keep | 0 | Jul | 2022 | 0.034736 | 0.00013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 204
MAYAGÃœEZ | 2022-07-24 07:42 | 2022-07-24 10:00 | 40 | 2:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M22072400026 | New_Event | Primary Wire Break | Include | Include | Equipment | 138 | 2022-07-24 | 5520 | keep | 0 | Jul | 2022 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-24 07:51 | 2022-07-24 10:19 | 10 | 2:28 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M22072400029 | New_Event | Animals | Include | Include | Wildlife | 148 | 2022-07-24 | 1480 | keep | 0 | Jul | 2022 | 0.001008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-07-24 08:03 | 2022-07-24 16:29 | 10 | 8:26 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE NECESITA DESGANCHE | M22072400031 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 506 | 2022-07-24 | 5060 | keep | 0 | Jul | 2022 | 0.0034463 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-24 08:08 | 2022-07-24 10:45 | 279 | 2:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22072400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-07-24 | 43803 | keep | 0 | Jul | 2022 | 0.029834 | 0.00019003 | Sustained | FALSE | FALSE | Not_TMED_Event | 279
SAN JUAN | 2022-07-24 08:15 | 2022-07-24 08:17 | 1825 | 0:02 | T | DESGANCHE | DISPARO NO RECERRO SE PROBO QUEDO EN SERVICIO | S22072400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-07-24 | 3650 | keep | 0 | Jul | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-07-24 08:22 | 2022-07-24 14:27 | 7 | 6:05 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22072400031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 365 | 2022-07-24 | 2555 | keep | 0 | Jul | 2022 | 0.0017402 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-07-24 08:22 | 2022-07-24 13:10 | 25 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22072400009 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2022-07-24 | 7200 | keep | 0 | Jul | 2022 | 0.0049039 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-07-24 08:29 | 2022-07-24 13:21 | 100 | 4:52 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R22072400017 | New_Event | Animals | Include | Include | Wildlife | 292 | 2022-07-24 | 29200 | keep | 0 | Jul | 2022 | 0.019888 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-24 08:39 | 2022-07-24 11:19 | 23 | 2:40 | P | ANIMAL | 1 X 30 EN C/L RATA | R22072400019 | New_Event | Animals | Include | Include | Wildlife | 160 | 2022-07-24 | 3680 | keep | 0 | Jul | 2022 | 0.0025064 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
UTUADO | 2022-07-24 08:51 | 2022-07-24 13:25 | 70 | 4:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22072400011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 274 | 2022-07-24 | 19180 | keep | 0 | Jul | 2022 | 0.013063 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-07-24 09:27 | 2022-07-24 12:08 | 50 | 2:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | C22072400008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 161 | 2022-07-24 | 8050 | keep | 0 | Jul | 2022 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-07-24 09:51 | 2022-07-24 13:56 | 50 | 4:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22072400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-07-24 | 12250 | keep | 0 | Jul | 2022 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-07-24 09:51 | 2022-07-24 13:59 | 93 | 4:08 | P | SECUNDARIA/DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHO SECUNDARIA | C22072400027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 248 | 2022-07-24 | 23064 | keep | 0 | Jul | 2022 | 0.015709 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
SAN JUAN | 2022-07-24 09:55 | 2022-07-24 10:45 | 1825 | 0:50 | T | DESGANCHE | DISPARO SE ABRIO MACHETE CALLE PROVIDENCIA ESQ. LOIZA Y SE CERRO INTERRUPTOR 10% EN SERVICIO | S22072400054 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-07-24 | 91250 | keep | 0 | Jul | 2022 | 0.06215 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2022-07-24 10:05 | 2022-07-24 11:10 | 60 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22072400044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-07-24 | 3900 | keep | 0 | Jul | 2022 | 0.0026563 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-24 10:35 | 2022-07-26 14:59 | 15 | 52:24 | P | ARBOL SOBRE LINEA | 2 X 25 EN C/L SE RETIRO ARBOL DE LAS LINEAS Y REMPLAZO POSTE SECUNDARIO | C22072400017 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 3144 | 2022-07-24 | 47160 | keep | 0 | Jul | 2022 | 0.03212 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-07-24 10:38 | 2022-07-24 20:31 | 2 | 9:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON BAJANTES SECUNDARIOS DE TRANSFORMADOR | M22072400053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 593 | 2022-07-24 | 1186 | keep | 0 | Jul | 2022 | 0.00080778 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2022-07-24 10:44 | 2022-07-24 10:45 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 449 | keep | 0 | Jul | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
SAN JUAN | 2022-07-24 10:45 | 2022-07-24 11:42 | 1643 | 0:57 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO CONECTOR QUEMADO BAJANTE A MACHETE Y CERRO MACHETE 100% EN SERVICIO | S22072400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-07-24 | 93651 | keep | 0 | Jul | 2022 | 0.063785 | 0.001119 | Sustained | FALSE | FALSE | Not_TMED_Event | 1643
CAGUAS | 2022-07-24 10:49 | 2022-07-24 11:38 | 80 | 0:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C22072400023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2022-07-24 | 3920 | keep | 0 | Jul | 2022 | 0.0026699 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-07-24 11:14 | 2022-07-24 11:15 | 978 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072400032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 978 | keep | 0 | Jul | 2022 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
HUMACAO | 2022-07-24 11:21 | 2022-07-24 15:05 | 32 | 3:44 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO | C22072400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-07-24 | 7168 | keep | 0 | Jul | 2022 | 0.0048821 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2022-07-24 11:32 | 2022-07-24 11:33 | 681 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1530-09 | S22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 681 | keep | 0 | Jul | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-07-24 11:32 | 2022-07-24 11:33 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1520-02 | S22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 1310 | keep | 0 | Jul | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-07-24 11:35 | 2022-07-24 13:33 | 39 | 1:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22072400086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-07-24 | 4602 | keep | 0 | Jul | 2022 | 0.0031344 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
GUAYAMA | 2022-07-24 11:38 | 2022-07-24 12:56 | 146 | 1:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 140 EN CORTE DE LINEA FUERTE BRISA | P22072400036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 78 | 2022-07-24 | 11388 | keep | 0 | Jul | 2022 | 0.0077563 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
MAYAGÃœEZ | 2022-07-24 11:38 | 2022-07-24 11:39 | 4641 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-24 | 4641 | keep | 0 | Jul | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
CANOVANAS | 2022-07-24 11:39 | 2022-07-24 14:11 | 80 | 2:32 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22072400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-07-24 | 12160 | keep | 0 | Jul | 2022 | 0.0082821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-07-24 11:39 | 2022-07-24 14:20 | 1 | 2:41 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA CLIENTE RETIRANDO UN ARBOL | M22072400063 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-07-24 | 161 | keep | 0 | Jul | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-24 11:40 | 2022-07-24 14:50 | 15 | 3:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO PARTIDO | M22072400012 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2022-07-24 | 2850 | keep | 0 | Jul | 2022 | 0.0019411 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-07-24 11:43 | 2022-07-24 12:54 | 60 | 1:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE REPARO ALAMBRE PRIMARIO | P22072400037 | New_Event | Primary Wire Break | Include | Include | Equipment | 71 | 2022-07-24 | 4260 | keep | 0 | Jul | 2022 | 0.0029015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-07-24 11:51 | 2022-07-24 13:25 | 80 | 1:34 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22072400044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-07-24 | 7520 | keep | 0 | Jul | 2022 | 0.0051218 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-07-24 11:57 | 2022-07-24 11:58 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072400062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 1192 | keep | 0 | Jul | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CANOVANAS | 2022-07-24 12:18 | 2022-07-24 15:51 | 40 | 3:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZARON AISLADORES, SE RETEZO LINEA Y 1 X 65 EN C/L | R22072400036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 213 | 2022-07-24 | 8520 | keep | 0 | Jul | 2022 | 0.0058029 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-07-24 12:20 | 2022-07-24 15:14 | 40 | 2:54 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L RETEZO LINEA | C22072400053 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 174 | 2022-07-24 | 6960 | keep | 0 | Jul | 2022 | 0.0047404 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-07-24 12:22 | 2022-07-24 15:35 | 100 | 3:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22072400060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2022-07-24 | 19300 | keep | 0 | Jul | 2022 | 0.013145 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-07-24 12:30 | 2022-07-24 16:25 | 70 | 3:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | A22072400040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 235 | 2022-07-24 | 16450 | keep | 0 | Jul | 2022 | 0.011204 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-07-24 12:32 | 2022-07-24 13:30 | 6 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA | B22072400063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2022-07-24 | 348 | keep | 0 | Jul | 2022 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-07-24 12:39 | 2022-07-24 15:41 | 100 | 3:02 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO | C22072400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-07-24 | 18200 | keep | 0 | Jul | 2022 | 0.012396 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-07-24 12:45 | 2022-07-24 12:46 | 1702 | 0:01 | T | ANIMAL | RECIERRE | C22072400000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-07-24 | 1702 | keep | 0 | Jul | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BAYAMON | 2022-07-24 12:45 | 2022-07-24 16:30 | 6 | 3:45 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO | B22072400057 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 225 | 2022-07-24 | 1350 | keep | 0 | Jul | 2022 | 0.00091948 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-07-24 12:46 | 2022-07-24 16:18 | 40 | 3:32 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C22072400081 | 1st_after_momentary | Animals | Include | Include | Wildlife | 212 | 2022-07-24 | 8480 | keep | 0 | Jul | 2022 | 0.0057757 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-07-24 12:46 | 2022-07-24 19:00 | 50 | 6:14 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 Y 2 X 65 EN CORTES DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | M22072400065 | New_Event | Primary Wire Break | Include | Include | Equipment | 374 | 2022-07-24 | 18700 | keep | 0 | Jul | 2022 | 0.012736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-24 12:56 | 2022-07-24 12:57 | 2858 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 2858 | keep | 0 | Jul | 2022 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BARRANQUITAS | 2022-07-24 12:57 | 2022-07-24 12:58 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 2203 | keep | 0 | Jul | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2022-07-24 12:59 | 2022-07-24 15:00 | 50 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | A22072400036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2022-07-24 | 6050 | keep | 0 | Jul | 2022 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-07-24 13:17 | 2022-07-24 14:50 | 7 | 1:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22072400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-07-24 | 651 | keep | 0 | Jul | 2022 | 0.00044339 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-07-24 13:21 | 2022-07-24 15:31 | 2635 | 2:10 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LA LINEA 6500 | C22072400093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-07-24 | 342550 | keep | 0 | Jul | 2022 | 0.23331 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-07-24 13:21 | 2022-07-24 15:31 | 2280 | 2:10 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LA LINEA 6500 | C22072400093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-07-24 | 296400 | keep | 0 | Jul | 2022 | 0.20188 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-07-24 13:21 | 2022-07-24 15:31 | 1617 | 2:10 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LA LINEA 6500 | C22072400093 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-07-24 | 210210 | keep | 0 | Jul | 2022 | 0.14317 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
BAYAMON | 2022-07-24 13:26 | 2022-07-24 15:57 | 350 | 2:31 | P | ANIMAL | 1 X 100 EN C/L AVE | B22072400068 | New_Event | Animals | Include | Include | Wildlife | 151 | 2022-07-24 | 52850 | keep | 0 | Jul | 2022 | 0.035996 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2022-07-24 13:28 | 2022-07-24 13:29 | 959 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 959 | keep | 0 | Jul | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-07-24 13:32 | 2022-07-24 13:33 | 2147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 2147 | keep | 0 | Jul | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-07-24 13:54 | 2022-07-24 13:55 | 959 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-24 | 959 | keep | 0 | Jul | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
ARECIBO | 2022-07-24 13:56 | 2022-07-24 16:50 | 1 | 2:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN RISER SE REMPLAZO CAJA QUEMADA | A22072400045 | New_Event | Cutout Failure | Include | Include | Equipment | 174 | 2022-07-24 | 174 | keep | 0 | Jul | 2022 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-24 14:01 | 2022-07-24 14:09 | 1444 | 0:08 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 6014-2 EL CUAL ESTA LLEVANDO LA CARGA DEL 6014-01 | M22072400092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 8 | 2022-07-24 | 11552 | keep | 0 | Jul | 2022 | 0.007868 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-07-24 14:01 | 2022-07-24 14:09 | 3630 | 0:08 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | M22072400092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 8 | 2022-07-24 | 29040 | keep | 0 | Jul | 2022 | 0.019779 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
UTUADO | 2022-07-24 14:07 | 2022-07-25 14:10 | 10 | 24:03 | P | CONDUCTOR ROTO O ABIERTO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22072400047 | New_Event | Primary Wire Break | Include | Include | Equipment | 1443 | 2022-07-24 | 14430 | keep | 0 | Jul | 2022 | 0.0098282 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-07-24 14:08 | 2022-07-24 17:31 | 100 | 3:23 | P | DESGANCHE | 1 X 40 Y 1 X 80 EN C/LS DESGANCHE | C22072400132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-07-24 | 20300 | keep | 0 | Jul | 2022 | 0.013826 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-07-24 14:11 | 2022-07-24 17:28 | 200 | 3:17 | P | PARARRAYOS DEFECTUOSO | 1 X 80 Y 1 X 100 EN C/LS ELIMINO PARARRAYO AVERIADO | C22072400133 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 197 | 2022-07-24 | 39400 | keep | 0 | Jul | 2022 | 0.026835 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-07-24 14:13 | 2022-07-24 15:46 | 1 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22072400135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-07-24 | 93 | keep | 0 | Jul | 2022 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-07-24 14:18 | 2022-07-24 17:50 | 30 | 3:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA | A22072400061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-07-24 | 6360 | keep | 0 | Jul | 2022 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-07-24 14:21 | 2022-07-24 19:24 | 1 | 5:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | A22072400049 | New_Event | Primary Wire Break | Include | Include | Equipment | 303 | 2022-07-24 | 303 | keep | 0 | Jul | 2022 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-24 14:23 | 2022-07-24 17:53 | 4 | 3:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22072400095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 210 | 2022-07-24 | 840 | keep | 0 | Jul | 2022 | 0.00057212 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-07-24 14:29 | 2022-07-25 12:23 | 40 | 21:54 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22072400050 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1314 | 2022-07-24 | 52560 | keep | 0 | Jul | 2022 | 0.035798 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-24 14:30 | 2022-07-24 20:59 | 5 | 6:29 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO BAJANTE PRIMARIO SAFADO DE LA CAJA PRIMARIA | M22072400100 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 389 | 2022-07-24 | 1945 | keep | 0 | Jul | 2022 | 0.0013247 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-07-24 14:30 | 2022-07-24 19:50 | 70 | 5:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22072400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2022-07-24 | 22400 | keep | 0 | Jul | 2022 | 0.015257 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-07-24 14:35 | 2022-07-24 19:35 | 150 | 5:00 | P | DESGANCHE | 2 X 100 EN C/L Y DESGANCHE | B22072400111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-07-24 | 45000 | keep | 0 | Jul | 2022 | 0.030649 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-07-24 14:40 | 2022-07-24 21:28 | 22 | 6:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 65 EN C/L | S22072400100 | New_Event | Cutout Failure | Include | Include | Equipment | 408 | 2022-07-24 | 8976 | keep | 0 | Jul | 2022 | 0.0061135 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2022-07-24 14:43 | 2022-07-24 15:51 | 65 | 1:08 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO | C22072400151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-07-24 | 4420 | keep | 0 | Jul | 2022 | 0.0030104 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BARRANQUITAS | 2022-07-24 14:45 | 2022-07-25 10:00 | 15 | 19:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22072400153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1155 | 2022-07-24 | 17325 | keep | 0 | Jul | 2022 | 0.0118 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-07-24 14:46 | 2022-07-24 15:55 | 60 | 1:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | A22072400055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 69 | 2022-07-24 | 4140 | keep | 0 | Jul | 2022 | 0.0028197 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-07-24 14:47 | 2022-07-24 18:40 | 300 | 3:53 | P | MAL TIEMPO/RAYOS | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072400106 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 233 | 2022-07-24 | 69900 | keep | 0 | Jul | 2022 | 0.047609 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-07-24 14:48 | 2022-07-24 17:03 | 125 | 2:15 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | R22072400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-07-24 | 16875 | keep | 0 | Jul | 2022 | 0.011493 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-07-24 15:01 | 2022-07-24 16:16 | 20 | 1:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22072400114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-07-24 | 1500 | keep | 0 | Jul | 2022 | 0.0010216 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-07-24 15:12 | 2022-07-24 18:12 | 40 | 3:00 | P | DESGANCHE | DESGANCHO Y LEVANTO CONDUCTOR NO FUNDIO | C22072400166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-07-24 | 7200 | keep | 0 | Jul | 2022 | 0.0049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-24 15:21 | 2022-07-24 18:32 | 100 | 3:11 | P | MAL TIEMPO/RAYOS | 2 X 65 EN ENTRADA CONVERTIDOR Y 1 X 140 EN SALIDA DEL CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072400129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 191 | 2022-07-24 | 19100 | keep | 0 | Jul | 2022 | 0.013009 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-07-24 15:23 | 2022-07-24 18:24 | 1 | 3:01 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHO | C22072400173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-07-24 | 181 | keep | 0 | Jul | 2022 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-24 15:36 | 2022-07-24 16:52 | 200 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072400135 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2022-07-24 | 15200 | keep | 0 | Jul | 2022 | 0.010353 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-07-24 16:00 | 2022-07-24 18:00 | 40 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA FUERTES VIENTOS | A22072400066 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2022-07-24 | 4800 | keep | 0 | Jul | 2022 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-24 16:04 | 2022-07-24 22:41 | 200 | 6:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22072400150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 397 | 2022-07-24 | 79400 | keep | 0 | Jul | 2022 | 0.054079 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-07-24 16:11 | 2022-07-25 07:13 | 200 | 15:02 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C25207240021 | New_Event | Animals | Include | Include | Wildlife | 902 | 2022-07-24 | 180400 | keep | 0 | Jul | 2022 | 0.12287 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-07-24 16:11 | 2022-07-25 07:02 | 25 | 14:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | C22072400191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 891 | 2022-07-24 | 22275 | keep | 0 | Jul | 2022 | 0.015171 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-07-24 16:24 | 2022-07-24 18:17 | 30 | 1:53 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22072400192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-07-24 | 3390 | keep | 0 | Jul | 2022 | 0.0023089 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-24 17:36 | 2022-07-24 18:05 | 6 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R22072400048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2022-07-24 | 174 | keep | 0 | Jul | 2022 | 0.00011851 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-07-24 18:00 | 2022-07-24 19:17 | 75 | 1:17 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072400178 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 77 | 2022-07-24 | 5775 | keep | 0 | Jul | 2022 | 0.0039333 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-07-24 18:24 | 2022-07-25 14:51 | 10 | 20:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B22072400176 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1227 | 2022-07-24 | 12270 | keep | 0 | Jul | 2022 | 0.008357 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-07-24 19:01 | 2022-07-24 20:38 | 75 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072400184 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2022-07-24 | 7275 | keep | 0 | Jul | 2022 | 0.004955 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-07-24 19:49 | 2022-07-25 15:44 | 20 | 19:55 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22072400074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1195 | 2022-07-24 | 23900 | keep | 0 | Jul | 2022 | 0.016278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-07-24 19:50 | 2022-07-24 21:56 | 150 | 2:06 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | R22072400058 | New_Event | Animals | Include | Include | Wildlife | 126 | 2022-07-24 | 18900 | keep | 0 | Jul | 2022 | 0.012873 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-07-24 20:03 | 2022-07-24 21:17 | 5 | 1:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS EN TRANSFORMADOR | M22072400186 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2022-07-24 | 370 | keep | 0 | Jul | 2022 | 0.00025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-07-24 20:08 | 2022-07-25 13:11 | 8 | 17:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN SERVICIO | C22072400253 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1023 | 2022-07-24 | 8184 | keep | 0 | Jul | 2022 | 0.0055741 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-07-24 20:15 | 2022-07-24 23:55 | 300 | 3:40 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 140 EN CORTE DE LINEA LINEAS PRIMARIAS CRUZADAS | A22072400077 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 220 | 2022-07-24 | 66000 | keep | 0 | Jul | 2022 | 0.044952 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-07-24 21:29 | 2022-07-25 02:37 | 5630 | 5:08 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 115KV, PT DE 115 KV AVERIADO SE PASO PARTE DE LA CARGA AL 3205-07 | C22072400299 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 308 | 2022-07-24 | 1734040 | keep | 0 | Jul | 2022 | 1.181 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-07-24 21:29 | 2022-07-25 01:00 | 2126 | 3:31 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 115KV, PT DE 115KV AVERIADO, SE TRANSFIRIO LA CARGA AL 2605-01 | C22072400299 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 211 | 2022-07-24 | 448586 | keep | 0 | Jul | 2022 | 0.30553 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-24 21:29 | 2022-07-25 19:57 | 551 | 22:28 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA HUMACAO TC 115KV, SE REMPLAZO PT DE 115KV AVERIADO | C22072400299 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1348 | 2022-07-24 | 742748 | keep | 0 | Jul | 2022 | 0.50588 | 0.00037528 | Sustained | FALSE | FALSE | Not_TMED_Event | 551
VEGA BAJA | 2022-07-24 21:34 | 2022-07-25 12:20 | 1 | 14:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 886 | 2022-07-24 | 886 | keep | 0 | Jul | 2022 | 0.00060345 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-24 22:20 | 2022-07-25 01:26 | 1825 | 3:06 | T | CONDUCTOR ROTO O ABIERTO | SE REPARARON CONECTORES LINEA A MACHETES | S22072400138 | New_Event | Primary Wire Break | Include | Include | Equipment | 186 | 2022-07-24 | 339450 | keep | 0 | Jul | 2022 | 0.2312 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
CANOVANAS | 2022-07-24 23:48 | 2022-07-25 08:31 | 13 | 8:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN RISER SE REMPLAZO DE PORTA FUSIBLE. | R22072400073 | New_Event | Cutout Failure | Include | Include | Equipment | 523 | 2022-07-24 | 6799 | keep | 0 | Jul | 2022 | 0.0046308 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-07-24 23:58 | 2022-07-25 | 892 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22072400156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-24 | 1784 | keep | 0 | Jul | 2022 | 0.0012151 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-07-25 00:03 | 2022-07-25 00:05 | 726 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 LLEVANDO CARGA 1346-04 SE CERRO POR SCADA | S22072500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-25 | 1452 | keep | 0 | Jul | 2022 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-07-25 00:03 | 2022-07-25 00:05 | 3932 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 LLEVANDO CARGA 1346-04 SE CERRO POR SCADA | S22072500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-25 | 7864 | keep | 0 | Jul | 2022 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
CANOVANAS | 2022-07-25 01:01 | 2022-07-25 01:02 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22072500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 4085 | keep | 0 | Jul | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
HUMACAO | 2022-07-25 01:08 | 2022-07-25 01:09 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2605-01 | C22072500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 01:08 | 2022-07-25 01:09 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-07-25 01:17 | 2022-07-25 01:18 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2605-01 | C22072500026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 01:17 | 2022-07-25 01:18 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-07-25 01:26 | 2022-07-25 01:27 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2605-01 | C22072500026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 01:26 | 2022-07-25 01:27 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-07-25 01:28 | 2022-07-25 01:29 | 428 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1328-01 LLEVANDO CARGA 1342-01 Y 1342-03 SE CERRO POR SCADA | S22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 428 | keep | 0 | Jul | 2022 | 0.00029151 | 0.00029151 | Momentary | FALSE | FALSE | Not_TMED_Event | 428
SAN JUAN | 2022-07-25 01:28 | 2022-07-25 01:29 | 356 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1328-01 LLEVANDO CARGA 1342-01 Y 1342-03 SE CERRO POR SCADA | S22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 356 | keep | 0 | Jul | 2022 | 0.00024247 | 0.00024247 | Momentary | FALSE | FALSE | Not_TMED_Event | 356
SAN JUAN | 2022-07-25 01:28 | 2022-07-25 01:29 | 29 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1328-01 LLEVANDO CARGA 1342-01 Y 1342-03 SE CERRO POR SCADA | S22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 29 | keep | 0 | Jul | 2022 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
HUMACAO | 2022-07-25 01:39 | 2022-07-25 01:40 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2605-01 | C22072500026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 01:39 | 2022-07-25 01:40 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-07-25 01:48 | 2022-07-25 01:49 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1825 | keep | 0 | Jul | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-07-25 01:51 | 2022-07-25 01:54 | 1825 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22072500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-25 | 5475 | keep | 0 | Jul | 2022 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
BAYAMON | 2022-07-25 01:51 | 2022-07-25 01:54 | 723 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO CARGA 1711-02 SE CERRO POR SCADA | B22072500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-25 | 2169 | keep | 0 | Jul | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-07-25 01:51 | 2022-07-25 01:54 | 1812 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1716-03 LLEVANDO CARGA 1711-02 SE CERRO POR SCADA | B22072500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-25 | 5436 | keep | 0 | Jul | 2022 | 0.0037024 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
HUMACAO | 2022-07-25 01:55 | 2022-07-25 01:56 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2605-01 | C22072500039 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 01:55 | 2022-07-25 01:56 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500039 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
VEGA BAJA | 2022-07-25 02:33 | 2022-07-25 02:34 | 1923 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22072500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1923 | keep | 0 | Jul | 2022 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
CAGUAS | 2022-07-25 02:35 | 2022-07-25 02:37 | 4634 | 0:02 | T | DISPARO DE BARRA DE TRANSMISION | SE ABRIO EL BKR PARA CERRAR MACHETES N/O Y ENERGIZAR PARTE DEL 2603-08 | C22072500044 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-07-25 | 9268 | keep | 0 | Jul | 2022 | 0.0063124 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
HUMACAO | 2022-07-25 02:37 | 2022-07-25 20:00 | 322 | 17:23 | P | DISPARO DE BARRA DE TRANSMISION | SE REMPLAZO PT DE 115KV AVERIADO Y SE NORMALIZARON LAS CARGAS | C22072400299 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 1043 | 2022-07-25 | 335846 | keep | 0 | Jul | 2022 | 0.22874 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-07-25 02:41 | 2022-07-25 10:23 | 36 | 7:42 | P | DESGANCHE | 1 X 40 CL 1 X 65 CL DESGANCHE | R22072500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 462 | 2022-07-25 | 16632 | keep | 0 | Jul | 2022 | 0.011328 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-07-25 02:45 | 2022-07-25 11:40 | 100 | 8:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-25 NO CAUSA | S22072500014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 535 | 2022-07-25 | 53500 | keep | 0 | Jul | 2022 | 0.036439 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-07-25 02:58 | 2022-07-25 04:30 | 70 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072500009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2022-07-25 | 6440 | keep | 0 | Jul | 2022 | 0.0043863 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-07-25 03:00 | 2022-07-25 03:01 | 863 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 863 | keep | 0 | Jul | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-07-25 03:05 | 2022-07-25 03:06 | 863 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072500002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 863 | keep | 0 | Jul | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-07-25 03:08 | 2022-07-25 03:09 | 863 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072500003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 863 | keep | 0 | Jul | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-07-25 03:11 | 2022-07-25 05:27 | 863 | 2:16 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR INDICA SE PATRULLO Y NO IDENTIFICO CAUSA AL DISPARO SE CERRO POR CONTROL SCADA | M22072500005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-07-25 | 117368 | keep | 0 | Jul | 2022 | 0.079939 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
BARRANQUITAS | 2022-07-25 03:12 | 2022-07-25 07:26 | 15 | 4:14 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22071500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 254 | 2022-07-25 | 3810 | keep | 0 | Jul | 2022 | 0.002595 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-07-25 04:01 | 2022-07-25 13:57 | 10 | 9:56 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE | B22072500007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 596 | 2022-07-25 | 5960 | keep | 0 | Jul | 2022 | 0.0040593 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-25 04:14 | 2022-07-25 12:40 | 200 | 8:26 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A22072500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 506 | 2022-07-25 | 101200 | keep | 0 | Jul | 2022 | 0.068927 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-07-25 05:04 | 2022-07-25 06:41 | 1825 | 1:37 | T | PROBLEMA DEL CLIENTE | DISPARO SE ABRIO MACHETE CALLE MCLEARY ESQ. ATLANTIC Y SE CERRO INTERRUPTOR 99% EN SERVICIO CONTINUAN PATRULLANDO | S22072500020 | New_Event | Customer-Related Interruption | Include | Include | Public | 97 | 2022-07-25 | 177025 | keep | 0 | Jul | 2022 | 0.12057 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
HUMACAO | 2022-07-25 05:08 | 2022-07-25 05:09 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2605-01 | C22072500064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 05:08 | 2022-07-25 05:09 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-07-25 05:47 | 2022-07-25 05:48 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2605-01 | C22072500064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 05:47 | 2022-07-25 05:48 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500064 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
VEGA BAJA | 2022-07-25 06:04 | 2022-07-25 13:58 | 15 | 7:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 15 EN XMR | B22072500011 | New_Event | Cutout Failure | Include | Include | Equipment | 474 | 2022-07-25 | 7110 | keep | 0 | Jul | 2022 | 0.0048426 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-07-25 06:17 | 2022-07-25 09:25 | 100 | 3:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072500020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 188 | 2022-07-25 | 18800 | keep | 0 | Jul | 2022 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-25 06:28 | 2022-07-25 09:14 | 80 | 2:46 | P | ANIMAL | 1 X 20 EN XMR Y 1 X 40 EN C/L AVE | B22072500013 | New_Event | Animals | Include | Include | Wildlife | 166 | 2022-07-25 | 13280 | keep | 0 | Jul | 2022 | 0.0090449 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-07-25 06:29 | 2022-07-25 10:16 | 30 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22072500020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2022-07-25 | 6810 | keep | 0 | Jul | 2022 | 0.0046383 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-25 06:34 | 2022-07-25 09:03 | 25 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R22072500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-07-25 | 3725 | keep | 0 | Jul | 2022 | 0.0025371 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-07-25 06:34 | 2022-07-25 07:40 | 100 | 1:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22072500023 | New_Event | Cutout Failure | Include | Include | Equipment | 66 | 2022-07-25 | 6600 | keep | 0 | Jul | 2022 | 0.0044952 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-07-25 06:35 | 2022-07-25 08:49 | 30 | 2:14 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A22072500021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-07-25 | 4020 | keep | 0 | Jul | 2022 | 0.002738 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-25 06:35 | 2022-07-25 10:46 | 76 | 4:11 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 65 EN COVENTIDOR 2 X 80 EN RISER 3 X 100 EN RISER | B22072500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-07-25 | 19076 | keep | 0 | Jul | 2022 | 0.012993 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
SAN JUAN | 2022-07-25 06:41 | 2022-07-25 07:45 | 7 | 1:04 | P | PROBLEMA DEL CLIENTE | SE ABRIO MACHETE PARA PATRULLAR Y SE ENCONTRO EN COND. GRANADA #1757 FUSIBLE FUNDIDO EN RISER A SUBEST. AL REPONER FUNDIO HAY QUE HACER PRUEBA DE CABLE Y SE CERRO MACHETE 100% EN SERVICIO | S22072500033 | Partial_restoration | Customer-Related Interruption | Include | Include | Public | 64 | 2022-07-25 | 448 | keep | 0 | Jul | 2022 | 0.00030513 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-07-25 06:46 | 2022-07-25 15:08 | 40 | 8:22 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO | C22072500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 502 | 2022-07-25 | 20080 | keep | 0 | Jul | 2022 | 0.013676 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-07-25 06:48 | 2022-07-25 06:49 | 2126 | 0:01 | T | DESGANCHE | RECIERRE DEL 2605-01 | C22072500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 06:48 | 2022-07-25 06:49 | 2450 | 0:01 | T | DESGANCHE | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
MAYAGÃœEZ | 2022-07-25 06:48 | 2022-07-25 09:20 | 100 | 2:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M22072500025 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 152 | 2022-07-25 | 15200 | keep | 0 | Jul | 2022 | 0.010353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-25 06:52 | 2022-07-25 08:19 | 11 | 1:27 | P | ANIMAL | 1X15 EN XMR CRUCE DE AVE | R22072500008 | New_Event | Animals | Include | Include | Wildlife | 87 | 2022-07-25 | 957 | keep | 0 | Jul | 2022 | 0.00065181 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-07-25 06:53 | 2022-07-25 09:33 | 25 | 2:40 | P | DESGANCHE | 1 X 50 EN C/L | C22072500080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-07-25 | 4000 | keep | 0 | Jul | 2022 | 0.0027244 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-07-25 06:56 | 2022-07-25 08:20 | 50 | 1:24 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE REPARO BAJANTE PRIMARIO | C22072500082 | New_Event | Primary Wire Break | Include | Include | Equipment | 84 | 2022-07-25 | 4200 | keep | 0 | Jul | 2022 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-07-25 07:00 | 2022-07-25 07:01 | 2126 | 0:01 | T | DESGANCHE | RECIERRE DEL 2605-01 | C22072500083 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 07:00 | 2022-07-25 07:01 | 2450 | 0:01 | T | DESGANCHE | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500083 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2022-07-25 07:01 | 2022-07-25 07:02 | 112 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 112 | keep | 0 | Jul | 2022 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
HUMACAO | 2022-07-25 07:09 | 2022-07-25 07:10 | 2126 | 0:01 | T | DESGANCHE | RECIERRE DEL 2605-01 | C22072500089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 07:09 | 2022-07-25 07:10 | 2450 | 0:01 | T | DESGANCHE | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500089 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-07-25 07:15 | 2022-07-25 17:49 | 58 | 10:34 | P | DESGANCHE | 1 X 25 Y 1 X 30 DESGANCHO | C22072500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 634 | 2022-07-25 | 36772 | keep | 0 | Jul | 2022 | 0.025045 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
HUMACAO | 2022-07-25 07:19 | 2022-07-25 10:18 | 2126 | 2:59 | T | DESGANCHE | DISPARO DE BKR 2605-01 SE SECCIONALIZO LA CARGA DEL 2603-09 ENTRANDO 60% EN SERVICIO | C22072500099 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-07-25 | 380554 | keep | 0 | Jul | 2022 | 0.25919 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 07:19 | 2022-07-25 09:35 | 2450 | 2:16 | T | DESGANCHE | DISPARO DE INTERRUPTOR ABRIO AMARRE CONTRA EL 2603-09 Y SE CERRO POR CONTROL | C22072500099 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-07-25 | 333200 | keep | 0 | Jul | 2022 | 0.22694 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-07-25 07:24 | 2022-07-25 10:36 | 10 | 3:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REPARO PUENTE ABIERTO SECUNDARIO | S22072500038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 192 | 2022-07-25 | 1920 | keep | 0 | Jul | 2022 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-07-25 07:25 | 2022-07-25 07:27 | 1000 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO PARTE POR 1620-05 | S22072500039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-25 | 2000 | keep | 0 | Jul | 2022 | 0.0013622 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
CANOVANAS | 2022-07-25 07:25 | 2022-07-25 07:27 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA PARTE DEL 1206-03 | S22072500039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-25 | 3230 | keep | 0 | Jul | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
BARRANQUITAS | 2022-07-25 07:26 | 2022-07-25 07:27 | 2280 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 9902-03 LLEVA 9902-02 | C22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2280 | keep | 0 | Jul | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-07-25 07:26 | 2022-07-25 07:27 | 1617 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 9902-03 LLEVA 9902-02 | C22072500000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1617 | keep | 0 | Jul | 2022 | 0.0011013 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-07-25 07:27 | 2022-07-25 08:10 | 15 | 0:43 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22071500012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 43 | 2022-07-25 | 645 | keep | 0 | Jul | 2022 | 0.00043931 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-07-25 07:31 | 2022-07-25 08:44 | 1066 | 1:13 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO LINEAS CRUZADAS SE CERRO INTERRUPTOR | A22072500038 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 73 | 2022-07-25 | 77818 | keep | 0 | Jul | 2022 | 0.053001 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2022-07-25 07:44 | 2022-07-25 12:19 | 100 | 4:35 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | B22072500021 | New_Event | Primary Wire Break | Include | Include | Equipment | 275 | 2022-07-25 | 27500 | keep | 0 | Jul | 2022 | 0.01873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-07-25 07:49 | 2022-07-25 11:45 | 10 | 3:56 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072500068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-07-25 | 2360 | keep | 0 | Jul | 2022 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-07-25 07:49 | 2022-07-25 11:15 | 80 | 3:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072500033 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 206 | 2022-07-25 | 16480 | keep | 0 | Jul | 2022 | 0.011224 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-07-25 08:00 | 2022-07-25 12:07 | 80 | 4:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22072500118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2022-07-25 | 19760 | keep | 0 | Jul | 2022 | 0.013458 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-07-25 08:27 | 2022-07-25 13:45 | 1250 | 5:18 | T | DESGANCHE | DISPARO DE BKR SE ABRIO AMARRE CONTRA EL 2901-04 Y SE CERRO POR CONTROL | C22072500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2022-07-25 | 397500 | keep | 0 | Jul | 2022 | 0.27074 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-07-25 08:27 | 2022-07-25 15:30 | 1827 | 7:03 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR CONTINUAN PATRULLANDO | C22072500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 423 | 2022-07-25 | 772821 | keep | 0 | Jul | 2022 | 0.52636 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2022-07-25 08:32 | 2022-07-25 20:34 | 16 | 12:02 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B22072500149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 722 | 2022-07-25 | 11552 | keep | 0 | Jul | 2022 | 0.007868 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-07-25 08:32 | 2022-07-25 17:33 | 4 | 9:01 | P | SECUNDARIA/DESGANCHE | SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE | B22072500112 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 541 | 2022-07-25 | 2164 | keep | 0 | Jul | 2022 | 0.0014739 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-07-25 08:35 | 2022-07-25 13:30 | 5 | 4:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE PRIMARIO | S22072500048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2022-07-25 | 1475 | keep | 0 | Jul | 2022 | 0.0010046 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-07-25 08:44 | 2022-07-25 11:25 | 40 | 2:41 | P | DESGANCHE | 1 X 65 EN C/L BAMBUA SOBRE LINEA | C22072500150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-07-25 | 6440 | keep | 0 | Jul | 2022 | 0.0043863 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-07-25 08:44 | 2022-07-25 13:00 | 1000 | 4:16 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS SE CERRO MACHETES | A22072500038 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 256 | 2022-07-25 | 256000 | keep | 0 | Jul | 2022 | 0.17436 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-25 08:45 | 2022-07-25 12:00 | 100 | 3:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | B22072500034 | New_Event | Cutout Failure | Include | Include | Equipment | 195 | 2022-07-25 | 19500 | keep | 0 | Jul | 2022 | 0.013281 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-25 08:59 | 2022-07-25 11:10 | 80 | 2:11 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA 3 X 40 EN RISER SE REALIZO DESGANCHE PRIMARIO | S22072500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-07-25 | 10480 | keep | 0 | Jul | 2022 | 0.0071379 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-07-25 09:11 | 2022-07-25 13:49 | 58 | 4:38 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22072500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-07-25 | 16124 | keep | 0 | Jul | 2022 | 0.010982 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2022-07-25 09:22 | 2022-07-25 12:36 | 60 | 3:14 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE PRIMARIO | S22072500065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-07-25 | 11640 | keep | 0 | Jul | 2022 | 0.007928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-07-25 09:25 | 2022-07-25 14:35 | 30 | 5:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C22072500188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 310 | 2022-07-25 | 9300 | keep | 0 | Jul | 2022 | 0.0063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-25 09:28 | 2022-07-25 14:25 | 30 | 4:57 | P | DESGANCHE | DESGANCHE 1 X 40 EN C/L | B22072500040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-07-25 | 8910 | keep | 0 | Jul | 2022 | 0.0060686 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-07-25 09:30 | 2022-07-25 12:20 | 30 | 2:50 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22072500056 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2022-07-25 | 5100 | keep | 0 | Jul | 2022 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-25 09:33 | 2022-07-25 09:45 | 40 | 0:12 | P | DESGANCHE | 1X80 EN CL DESGANCHE | R22072500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2022-07-25 | 480 | keep | 0 | Jul | 2022 | 0.00032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-07-25 09:34 | 2022-07-25 14:20 | 1 | 4:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON LINEAS SECUNDARIAS PARTIDAS Y CONEXIONES SECUNDARIAS | A22072500051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 286 | 2022-07-25 | 286 | keep | 0 | Jul | 2022 | 0.00019479 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-25 09:39 | 2022-07-25 11:45 | 45 | 2:06 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA IGUANA CRUZO FASES | M22072500058 | New_Event | Animals | Include | Include | Wildlife | 126 | 2022-07-25 | 5670 | keep | 0 | Jul | 2022 | 0.0038618 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2022-07-25 09:40 | 2022-07-25 09:41 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 4132 | keep | 0 | Jul | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-07-25 09:40 | 2022-07-25 09:41 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1945 | keep | 0 | Jul | 2022 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2022-07-25 09:40 | 2022-07-25 09:41 | 215 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 215 | keep | 0 | Jul | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BARRANQUITAS | 2022-07-25 09:44 | 2022-07-25 18:26 | 83 | 8:42 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C22072500198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 522 | 2022-07-25 | 43326 | keep | 0 | Jul | 2022 | 0.029509 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
MAYAGÃœEZ | 2022-07-25 09:45 | 2022-07-25 16:00 | 300 | 6:15 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR BAMBUS SOBRE LINEAS | M22072500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 375 | 2022-07-25 | 112500 | keep | 0 | Jul | 2022 | 0.076623 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-07-25 09:45 | 2022-07-25 10:00 | 5 | 0:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE TRANSFORMADOR AVERIADA | M22072500053 | New_Event | Cutout Failure | Include | Include | Equipment | 15 | 2022-07-25 | 75 | keep | 0 | Jul | 2022 | 5.1082e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-07-25 10:05 | 2022-07-25 12:12 | 40 | 2:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22072500208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2022-07-25 | 5080 | keep | 0 | Jul | 2022 | 0.00346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-07-25 10:09 | 2022-07-25 12:45 | 7 | 2:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22072500049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-07-25 | 1092 | keep | 0 | Jul | 2022 | 0.00074376 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-07-25 10:18 | 2022-07-25 12:50 | 800 | 2:32 | P | DESGANCHE | SE REEMPLAZO 2 PIN POLE TOP, SE ELIMINO PARARRAYO Y DESGANCHE Y SE CERRO MACHETE | C22072500099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-07-25 | 121600 | keep | 0 | Jul | 2022 | 0.082821 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
YAUCO | 2022-07-25 10:18 | 2022-07-26 09:50 | 15 | 23:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M22072500538 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1412 | 2022-07-25 | 21180 | keep | 0 | Jul | 2022 | 0.014426 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-07-25 10:19 | 2022-07-25 12:31 | 191 | 2:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA QUEMADA | R22072500027 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2022-07-25 | 25212 | keep | 0 | Jul | 2022 | 0.017172 | 0.00013009 | Sustained | FALSE | FALSE | Not_TMED_Event | 191
FAJARDO | 2022-07-25 10:27 | 2022-07-25 11:07 | 36 | 0:40 | P | DESGANCHE | 1 X 30 EN C/L 1 X 40 EN C/L DESGANCHE | R22072500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-07-25 | 1440 | keep | 0 | Jul | 2022 | 0.00098078 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BARRANQUITAS | 2022-07-25 10:29 | 2022-07-25 21:09 | 10 | 10:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | C22072500219 | New_Event | Service Transformer Failure | Include | Include | Equipment | 640 | 2022-07-25 | 6400 | keep | 0 | Jul | 2022 | 0.004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-07-25 10:30 | 2022-07-25 17:55 | 16 | 7:25 | P | ARBOL SOBRE LINEA | 2 X 15 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR ARBOL SOBRE LINEA | M22072500134 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 445 | 2022-07-25 | 7120 | keep | 0 | Jul | 2022 | 0.0048494 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-07-25 10:35 | 2022-07-25 20:13 | 25 | 9:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO | B22072500025 | New_Event | Primary Pole Failure | Include | Include | Equipment | 578 | 2022-07-25 | 14450 | keep | 0 | Jul | 2022 | 0.0098418 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-07-25 10:36 | 2022-07-25 10:37 | 3495 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE BKR 3010-01. 20% POR EL 3604-06 | C22072500225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 3495 | keep | 0 | Jul | 2022 | 0.0023804 | 0.0023804 | Momentary | FALSE | FALSE | Not_TMED_Event | 3495
CANOVANAS | 2022-07-25 10:43 | 2022-07-25 12:15 | 60 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO VIENTOS | R22072500032 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2022-07-25 | 5520 | keep | 0 | Jul | 2022 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-07-25 10:58 | 2022-07-25 16:41 | 40 | 5:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES VIENTOS | C22072500237 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 343 | 2022-07-25 | 13720 | keep | 0 | Jul | 2022 | 0.0093446 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-07-25 11:02 | 2022-07-25 14:10 | 10 | 3:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR LINEA SECUNDARIA PARTIDA | P22072500056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 188 | 2022-07-25 | 1880 | keep | 0 | Jul | 2022 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-25 11:19 | 2022-07-25 11:20 | 878 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRA DE INTERRUPTOR | B22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 878 | keep | 0 | Jul | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
BARRANQUITAS | 2022-07-25 11:28 | 2022-07-25 20:07 | 40 | 8:39 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | C22072500259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 519 | 2022-07-25 | 20760 | keep | 0 | Jul | 2022 | 0.01414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-25 11:30 | 2022-07-25 14:13 | 10 | 2:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | B22072500074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 163 | 2022-07-25 | 1630 | keep | 0 | Jul | 2022 | 0.0011102 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-25 11:36 | 2022-07-26 20:17 | 65 | 32:41 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO CABLE SOTERRADO DE RISER A T25 Y SE REALIZARON TERMINACIONES | B22072500077 | New_Event | UG Cable Fault | Include | Include | Equipment | 1961 | 2022-07-25 | 127465 | keep | 0 | Jul | 2022 | 0.086816 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-07-25 11:47 | 2022-07-25 17:56 | 50 | 6:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S22072500099 | New_Event | Cutout Failure | Include | Include | Equipment | 369 | 2022-07-25 | 18450 | keep | 0 | Jul | 2022 | 0.012566 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-07-25 11:47 | 2022-07-25 14:03 | 80 | 2:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON DOS AISLADORES PRIMARIOS PARTIDOS | A22072500072 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 136 | 2022-07-25 | 10880 | keep | 0 | Jul | 2022 | 0.0074103 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-07-25 11:50 | 2022-07-25 14:33 | 6 | 2:43 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA REPARAR Y LEVANTAR SECUNDARIA | C22072500205 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 163 | 2022-07-25 | 978 | keep | 0 | Jul | 2022 | 0.00066611 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-07-25 11:57 | 2022-07-25 16:19 | 10 | 4:22 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B22072500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-07-25 | 2620 | keep | 0 | Jul | 2022 | 0.0017845 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-07-25 12:00 | 2022-07-25 21:44 | 70 | 9:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M22072500360 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 584 | 2022-07-25 | 40880 | keep | 0 | Jul | 2022 | 0.027843 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-07-25 12:04 | 2022-07-25 12:05 | 681 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1530-09 | S22072500129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 681 | keep | 0 | Jul | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-07-25 12:04 | 2022-07-25 12:05 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1520-02 | S22072500129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1310 | keep | 0 | Jul | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
AGUADILLA | 2022-07-25 12:04 | 2022-07-25 14:32 | 2 | 2:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M22072500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-07-25 | 296 | keep | 0 | Jul | 2022 | 0.0002016 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2022-07-25 12:15 | 2022-07-25 13:00 | 8 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO DE LINEA SECUNDARIA AVERIADA | P22072500054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-07-25 | 360 | keep | 0 | Jul | 2022 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-07-25 12:22 | 2022-07-25 14:40 | 100 | 2:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | M22072500090 | New_Event | Primary Wire Break | Include | Include | Equipment | 138 | 2022-07-25 | 13800 | keep | 0 | Jul | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-07-25 12:22 | 2022-07-25 20:23 | 55 | 8:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L REMPLAZO PIN POLET TOP | C22072500288 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 481 | 2022-07-25 | 26455 | keep | 0 | Jul | 2022 | 0.018018 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-07-25 12:24 | 2022-07-26 08:52 | 20 | 20:28 | P | CAUSAS EXTERNAS | 2 X 65 EN CORTE DE LINEA PERSONA AJENA A LUMA DESGANCHANDO TUMBO ARBOL Y CRUZO LINEA | S22072500104 | New_Event | Damage From Public | Include | Include | Public | 1228 | 2022-07-25 | 24560 | keep | 0 | Jul | 2022 | 0.016728 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-25 12:27 | 2022-07-25 15:23 | 15 | 2:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REMPLAZAR SECUNDARIA ABIERTA | S22072500105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 176 | 2022-07-25 | 2640 | keep | 0 | Jul | 2022 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-07-25 12:31 | 2022-07-25 18:00 | 10 | 5:29 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO | P22072500069 | New_Event | Primary Wire Break | Include | Include | Equipment | 329 | 2022-07-25 | 3290 | keep | 0 | Jul | 2022 | 0.0022408 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-07-25 12:32 | 2022-07-25 14:15 | 65 | 1:43 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P22072500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-07-25 | 6695 | keep | 0 | Jul | 2022 | 0.0045599 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2022-07-25 12:45 | 2022-07-25 16:13 | 43 | 3:28 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO, REMPLAZO PIN POLE TOP | C22072500302 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-07-25 | 8944 | keep | 0 | Jul | 2022 | 0.0060917 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
ARECIBO | 2022-07-25 12:48 | 2022-07-25 18:20 | 30 | 5:32 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA Y SE REALIZO DESGANCHE | A22072500081 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 332 | 2022-07-25 | 9960 | keep | 0 | Jul | 2022 | 0.0067837 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-07-25 12:50 | 2022-07-25 16:55 | 60 | 4:05 | P | DESGANCHE | SE REALIZO DESGANCHE, SE SUBIO LINEA PRIMARIA, LINEA NEUTRAL Y SECUNDARIA. NO FUNDIO | C22072500307 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-07-25 | 14700 | keep | 0 | Jul | 2022 | 0.010012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-25 12:54 | 2022-07-25 12:55 | 2126 | 0:01 | T | SOBRECARGA | RECIERRE DEL 2605-01 CARGA POR EL 2605-01 | C22072500000 | New_Event | Trip Due To Overload | Include | Include | Other | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 12:54 | 2022-07-25 12:55 | 2450 | 0:01 | T | SOBRECARGA | RECIERRE LLEVA EL 2603-09 | C22072500000 | New_Event | Trip Due To Overload | Include | Include | Other | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
MAYAGÃœEZ | 2022-07-25 12:55 | 2022-07-25 15:45 | 5 | 2:50 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M22072500096 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 170 | 2022-07-25 | 850 | keep | 0 | Jul | 2022 | 0.00057893 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-07-25 13:00 | 2022-07-25 14:10 | 20 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REMPLAZAR 60 PIES LINEA SECUNDARIA Y CONECTORES | S22072500101 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-07-25 | 1400 | keep | 0 | Jul | 2022 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-07-25 13:02 | 2022-07-25 13:03 | 2126 | 0:01 | T | SOBRECARGA | RECIERRE DEL 2605-01 | C22072500318 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 13:02 | 2022-07-25 13:03 | 2450 | 0:01 | T | SOBRECARGA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500318 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2022-07-25 13:05 | 2022-07-25 16:51 | 20 | 3:46 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | B22072500098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-07-25 | 4520 | keep | 0 | Jul | 2022 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-07-25 13:06 | 2022-07-25 21:26 | 60 | 8:20 | P | ARBOL SOBRE LINEA | 2 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22072500083 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 500 | 2022-07-25 | 30000 | keep | 0 | Jul | 2022 | 0.020433 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-25 13:09 | 2022-07-25 13:10 | 2126 | 0:01 | T | SOBRECARGA | RECIERRE DEL 2605-01 | C22072500324 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 1 | 2022-07-25 | 2126 | keep | 0 | Jul | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 13:09 | 2022-07-25 13:10 | 2450 | 0:01 | T | SOBRECARGA | RECIERRE LLEVA LA CARGA DEL 2603-09 | C22072500324 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 1 | 2022-07-25 | 2450 | keep | 0 | Jul | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-07-25 13:19 | 2022-07-25 13:26 | 2126 | 0:07 | T | SOBRECARGA | DISPARO DEL 2605-01, SE ABRIO MACHETES DEL 2603-09 Y SE DEJO FUERA UN 40% DEL ALIMENTADOR POR SOBRE CARGA | C22072500336 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 7 | 2022-07-25 | 14882 | keep | 0 | Jul | 2022 | 0.010136 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-07-25 13:19 | 2022-07-25 13:26 | 2450 | 0:07 | T | SOBRECARGA | DISPARO LLEVA EL 2603-09 | C22072500336 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 7 | 2022-07-25 | 17150 | keep | 0 | Jul | 2022 | 0.011681 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
BARRANQUITAS | 2022-07-25 13:25 | 2022-07-25 15:36 | 64 | 2:11 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C22072500101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-07-25 | 8384 | keep | 0 | Jul | 2022 | 0.0057103 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
HUMACAO | 2022-07-25 13:26 | 2022-07-25 19:59 | 800 | 6:33 | P | SOBRECARGA | SE CERRARON MACHETES 100% EN SERVICIO | C22072500336 | Partial_restoration | Trip Due To Overload | Include | Include | Other | 393 | 2022-07-25 | 314400 | keep | 0 | Jul | 2022 | 0.21414 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-07-25 13:26 | 2022-07-25 13:27 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 3973 | keep | 0 | Jul | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-07-25 13:26 | 2022-07-25 13:27 | 2484 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2484 | keep | 0 | Jul | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
GUAYAMA | 2022-07-25 13:29 | 2022-07-25 13:30 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 527 | keep | 0 | Jul | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-07-25 13:39 | 2022-07-25 15:28 | 1 | 1:49 | P | NO SE REPORTO CAUSA | 3 X 80 EN RISER | C22072500358 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-07-25 | 109 | keep | 0 | Jul | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-07-25 13:45 | 2022-07-25 17:00 | 85 | 3:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22072500080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-07-25 | 16575 | keep | 0 | Jul | 2022 | 0.011289 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2022-07-25 13:46 | 2022-07-25 13:47 | 3688 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22072500089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 3688 | keep | 0 | Jul | 2022 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
AGUADILLA | 2022-07-25 13:50 | 2022-07-25 13:51 | 1245 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072500110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
BARRANQUITAS | 2022-07-25 13:52 | 2022-07-25 13:53 | 2635 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 ABRIO BKR 6550 | C22072500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-25 | 2635 | keep | 0 | Jul | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-07-25 13:52 | 2022-07-25 13:53 | 2280 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 ABRIO BKR 6550 | C22072500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-25 | 2280 | keep | 0 | Jul | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-07-25 13:52 | 2022-07-25 13:53 | 1617 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 ABRIO BKR 6550 | C22072500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-25 | 1617 | keep | 0 | Jul | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BARRANQUITAS | 2022-07-25 13:54 | 2022-07-25 14:50 | 2635 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 ABRIO BKR 6550 | C22072500450 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-07-25 | 147560 | keep | 0 | Jul | 2022 | 0.1005 | 0.0017947 | Sustained | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-07-25 13:54 | 2022-07-25 14:50 | 2280 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 ABRIO BKR 6550 | C22072500450 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-07-25 | 127680 | keep | 0 | Jul | 2022 | 0.086962 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
BARRANQUITAS | 2022-07-25 13:54 | 2022-07-25 14:50 | 1617 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6500 ABRIO BKR 6550 | C22072500450 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-07-25 | 90552 | keep | 0 | Jul | 2022 | 0.061675 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-07-25 13:55 | 2022-07-25 14:46 | 15 | 0:51 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA ENDEREZAR POSTE PRIMARIO Y RELOCALILZAR LINEAS PRIMARIAS | M22072500108 | New_Event | Primary Pole Failure | Include | Include | Equipment | 51 | 2022-07-25 | 765 | keep | 0 | Jul | 2022 | 0.00052104 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-07-25 14:02 | 2022-07-25 14:03 | 1843 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1843 | keep | 0 | Jul | 2022 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
SAN JUAN | 2022-07-25 14:04 | 2022-07-25 14:05 | 681 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1530-09 | S22072500129 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 681 | keep | 0 | Jul | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-07-25 14:04 | 2022-07-25 14:05 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1520-02 | S22072500129 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1310 | keep | 0 | Jul | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
AGUADILLA | 2022-07-25 14:09 | 2022-07-25 14:10 | 1245 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22072500115 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
SAN JUAN | 2022-07-25 14:10 | 2022-07-25 15:19 | 442 | 1:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETE Y SE ESTABLECE GOI PARA REMPLAZAR AISLADOR PARTIDO | S22072500133 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 69 | 2022-07-25 | 30498 | keep | 0 | Jul | 2022 | 0.020772 | 0.00030104 | Sustained | FALSE | FALSE | Not_TMED_Event | 442
CAGUAS | 2022-07-25 14:13 | 2022-07-25 15:59 | 65 | 1:46 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO | C22072500399 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-07-25 | 6890 | keep | 0 | Jul | 2022 | 0.0046927 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-07-25 14:21 | 2022-07-25 14:22 | 1671 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22072500125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1671 | keep | 0 | Jul | 2022 | 0.0011381 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
YAUCO | 2022-07-25 14:21 | 2022-07-25 20:42 | 65 | 6:21 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN CORTES DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2022-07-25 | 24765 | keep | 0 | Jul | 2022 | 0.016867 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-07-25 14:26 | 2022-07-25 18:56 | 4 | 4:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR BARRA DEL NEUTRAL EN PEDESTAL | C22072500415 | New_Event | Secondary Wire Break | Include | Include | Equipment | 270 | 2022-07-25 | 1080 | keep | 0 | Jul | 2022 | 0.00073558 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-07-25 14:33 | 2022-07-25 20:50 | 120 | 6:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M22072500132 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 377 | 2022-07-25 | 45240 | keep | 0 | Jul | 2022 | 0.030813 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-07-25 14:35 | 2022-07-25 14:36 | 878 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22072500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 878 | keep | 0 | Jul | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
YAUCO | 2022-07-25 14:40 | 2022-07-25 16:35 | 138 | 1:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22072500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-07-25 | 15870 | keep | 0 | Jul | 2022 | 0.010809 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2022-07-25 14:45 | 2022-07-25 18:14 | 7 | 3:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR 40 PIES SECUNDARIA Y CONECTORES Y SE HIZO DESGANCHE SECUNDARIO | S22072500045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 209 | 2022-07-25 | 1463 | keep | 0 | Jul | 2022 | 0.00099644 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-07-25 14:45 | 2022-07-25 18:33 | 30 | 3:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | A22072500097 | New_Event | Primary Wire Break | Include | Include | Equipment | 228 | 2022-07-25 | 6840 | keep | 0 | Jul | 2022 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-07-25 14:46 | 2022-07-25 16:40 | 20 | 1:54 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO TRASPATIO Y SE CERRO CORTE DE LINEA | S22072500136 | New_Event | Primary Wire Break | Include | Include | Equipment | 114 | 2022-07-25 | 2280 | keep | 0 | Jul | 2022 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-07-25 14:50 | 2022-07-25 21:22 | 40 | 6:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M22072500150 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 392 | 2022-07-25 | 15680 | keep | 0 | Jul | 2022 | 0.01068 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-07-25 14:59 | 2022-07-25 15:00 | 2362 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C22072500463 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-07-25 | 2362 | keep | 0 | Jul | 2022 | 0.0016087 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
PONCE | 2022-07-25 15:00 | 2022-07-25 20:05 | 8 | 5:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P22072500109 | New_Event | Primary Wire Break | Include | Include | Equipment | 305 | 2022-07-25 | 2440 | keep | 0 | Jul | 2022 | 0.0016619 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-07-25 15:00 | 2022-07-26 09:44 | 80 | 18:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | M22072500160 | New_Event | Primary Wire Break | Include | Include | Equipment | 1124 | 2022-07-25 | 89920 | keep | 0 | Jul | 2022 | 0.061244 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-07-25 15:00 | 2022-07-25 16:32 | 2362 | 1:32 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | C22072500463 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 92 | 2022-07-25 | 217304 | keep | 0 | Jul | 2022 | 0.148 | 0.0016087 | Sustained | FALSE | FALSE | Not_TMED_Event | 2362
CAGUAS | 2022-07-25 15:14 | 2022-07-25 15:15 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR | C22072500560 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1342 | keep | 0 | Jul | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
SAN JUAN | 2022-07-25 15:15 | 2022-07-25 15:17 | 74 | 0:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO SU CARGA POR 1529-11 | S22072500139 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-07-25 | 148 | keep | 0 | Jul | 2022 | 0.0001008 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-07-25 15:15 | 2022-07-25 15:17 | 1370 | 0:02 | T | DESCONECTIVO DEFECTUOSO | DISPARO LLEVA 1521-02 SE PROBO QUEDO EN SERVICIO | S22072500139 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2022-07-25 | 2740 | keep | 0 | Jul | 2022 | 0.0018662 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
SAN JUAN | 2022-07-25 15:20 | 2022-07-25 15:39 | 1825 | 0:19 | T | NO SE REPORTO CAUSA | DISPARO PERSONAL TRABAJANDO EN SU ZONA DE GOI ESCUCHO EXPLOSION SE VERIFICO NO SE ENCONTRO NADA SE PROBO QUEDO EN SERVICIO | S22072500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2022-07-25 | 34675 | keep | 0 | Jul | 2022 | 0.023617 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
AGUADILLA | 2022-07-25 15:20 | 2022-07-25 16:10 | 2 | 0:50 | P | ERROR HUMANO | 1 X 100 EN CORTE DE LINEA PERSONAL DE DESGANCHE TIRO RAMA SOBRE LINEA | M22072500155 | New_Event | Human Error | Include | Include | Other | 50 | 2022-07-25 | 100 | keep | 0 | Jul | 2022 | 6.811e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-07-25 15:21 | 2022-07-25 19:10 | 80 | 3:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072500100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 229 | 2022-07-25 | 18320 | keep | 0 | Jul | 2022 | 0.012478 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-25 15:24 | 2022-07-25 20:49 | 118 | 5:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA PRIMARIA Y DESGANCHE | B22072500117 | New_Event | Cutout Failure | Include | Include | Equipment | 325 | 2022-07-25 | 38350 | keep | 0 | Jul | 2022 | 0.02612 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
YAUCO | 2022-07-25 15:25 | 2022-07-25 21:53 | 70 | 6:28 | P | CONDUCTOR ARRIADO O CRUZADO | SE DESPEGO LINEA PEGANDO A TIERRA DEL POSTE Y SE CERRO PUENTE | M22072500157 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 388 | 2022-07-25 | 27160 | keep | 0 | Jul | 2022 | 0.018499 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-07-25 15:27 | 2022-07-25 20:45 | 150 | 5:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO PUENTE ABIERTO | M22072500158 | New_Event | Primary Wire Break | Include | Include | Equipment | 318 | 2022-07-25 | 47700 | keep | 0 | Jul | 2022 | 0.032488 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-07-25 15:28 | 2022-07-25 17:20 | 2842 | 1:52 | T | DESGANCHE | DISPARO RETIRO RAMAS DE LA LINEA | C22072500480 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-07-25 | 318304 | keep | 0 | Jul | 2022 | 0.2168 | 0.0019357 | Sustained | FALSE | FALSE | Not_TMED_Event | 2842
HUMACAO | 2022-07-25 15:30 | 2022-07-25 16:09 | 730 | 0:39 | P | DESGANCHE | REALIZO DESGANCHE, EN SERVICIO | C22072500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 39 | 2022-07-25 | 28470 | keep | 0 | Jul | 2022 | 0.019391 | 0.0004972 | Sustained | FALSE | FALSE | Not_TMED_Event | 730
YAUCO | 2022-07-25 15:30 | 2022-07-25 21:53 | 100 | 6:23 | P | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES PRIMARIOS. SE SEGUIRA PATRULLANDO | M22072500390 | New_Event | Primary Wire Break | Include | Include | Equipment | 383 | 2022-07-25 | 38300 | keep | 0 | Jul | 2022 | 0.026086 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-25 15:31 | 2022-07-25 18:37 | 437 | 3:06 | T | DESGANCHE | DISPARO SE PATRULLO SE RETIRO RAMA SOBRE LINEA CON VARETA DE PISO Y SE CERRO INTERRUPTOR SU CARGA POR 1530-07 | S22072500226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-07-25 | 81282 | keep | 0 | Jul | 2022 | 0.055361 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2022-07-25 15:31 | 2022-07-25 18:37 | 643 | 3:06 | T | DESGANCHE | DISPARO SE PATRULLO SE RETIRO RAMA SOBRE LINEA CON VARETA DE PISO Y SE CERRO INTERRUPTOR LLEVA 1530-06 | S22072500226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-07-25 | 119598 | keep | 0 | Jul | 2022 | 0.081458 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2022-07-25 15:39 | 2022-07-25 19:05 | 22 | 3:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PODRIDO DE 75 KVA CON PARARRAYOS Y CAJA | S22072500239 | New_Event | Service Transformer Failure | Include | Include | Equipment | 206 | 2022-07-25 | 4532 | keep | 0 | Jul | 2022 | 0.0030867 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
VEGA BAJA | 2022-07-25 15:39 | 2022-07-26 08:00 | 44 | 16:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22072500123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 981 | 2022-07-25 | 43164 | keep | 0 | Jul | 2022 | 0.029399 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2022-07-25 15:53 | 2022-07-25 17:31 | 2 | 1:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO EN MAL ESTADO Y SE RETEZO LINEAS PRIMARIAS | S22072500193 | New_Event | Primary Pole Failure | Include | Include | Equipment | 98 | 2022-07-25 | 196 | keep | 0 | Jul | 2022 | 0.00013349 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-07-25 15:55 | 2022-07-25 15:56 | 1835 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072500510 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 1835 | keep | 0 | Jul | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
AGUADILLA | 2022-07-25 15:55 | 2022-07-25 15:56 | 1245 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR | M22072500171 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-07-25 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2022-07-25 16:00 | 2022-07-26 10:39 | 100 | 18:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M22072500177 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1119 | 2022-07-25 | 111900 | keep | 0 | Jul | 2022 | 0.076215 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-07-25 16:15 | 2022-07-25 19:43 | 101 | 3:28 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L LEVANTO CONDUCTOR | C22072500525 | New_Event | Primary Wire Break | Include | Include | Equipment | 208 | 2022-07-25 | 21008 | keep | 0 | Jul | 2022 | 0.014308 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
SAN JUAN | 2022-07-25 16:27 | 2022-07-25 16:40 | 20 | 0:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REMPLAZAR 60 PIES LINEA SECUNDARIA Y CONECTORES | S22072500101 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 13 | 2022-07-25 | 260 | keep | 0 | Jul | 2022 | 0.00017708 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-25 16:29 | 2022-07-25 20:39 | 74 | 4:10 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO N/O SU CARGA POR 1529-11 89% EN SERVICIO 1521-02 | S22072500275 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 250 | 2022-07-25 | 18500 | keep | 0 | Jul | 2022 | 0.0126 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-07-25 16:29 | 2022-07-25 17:42 | 1370 | 1:13 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO N/O CONTRA 1521-2 Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO CONTINUAN PATRULLANDO 1521-2 | S22072500218 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 73 | 2022-07-25 | 100010 | keep | 0 | Jul | 2022 | 0.068116 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
YAUCO | 2022-07-25 16:30 | 2022-07-25 17:27 | 20 | 0:57 | P | DESGANCHE | 1 X 802 EN CORTE DE LINEA POR DESGANCHE | P22072500136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-07-25 | 1140 | keep | 0 | Jul | 2022 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-07-25 16:32 | 2022-07-25 18:57 | 2244 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | LEVANTO CONDUCTOR Y CERRO MACHETES | C22072500566 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 145 | 2022-07-25 | 325380 | keep | 0 | Jul | 2022 | 0.22161 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-25 16:51 | 2022-07-25 22:51 | 130 | 6:00 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA A MACHETE | B22072500136 | New_Event | Primary Wire Break | Include | Include | Equipment | 360 | 2022-07-25 | 46800 | keep | 0 | Jul | 2022 | 0.031875 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
YAUCO | 2022-07-25 16:52 | 2022-07-25 17:50 | 42 | 0:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | P22072500133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 58 | 2022-07-25 | 2436 | keep | 0 | Jul | 2022 | 0.0016591 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BARRANQUITAS | 2022-07-25 17:04 | 2022-07-25 18:28 | 15 | 1:24 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR REPARO SECUNDARIA AVERIADA POR CAMION | C22072500570 | New_Event | Damage From Public | Include | Include | Public | 84 | 2022-07-25 | 1260 | keep | 0 | Jul | 2022 | 0.00085818 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-07-25 17:08 | 2022-07-25 17:10 | 2216 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22072500141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-25 | 4432 | keep | 0 | Jul | 2022 | 0.0030186 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
AGUADILLA | 2022-07-25 17:09 | 2022-07-25 17:10 | 1245 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR | M22072500000 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-07-25 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2022-07-25 17:13 | 2022-07-26 11:30 | 80 | 18:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | A22072500114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1097 | 2022-07-25 | 87760 | keep | 0 | Jul | 2022 | 0.059773 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-07-25 17:15 | 2022-07-25 17:16 | 1245 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR | M22072500000 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-07-25 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
YAUCO | 2022-07-25 17:19 | 2022-07-26 13:50 | 15 | 20:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | P22072500145 | New_Event | Cutout Failure | Include | Include | Equipment | 1231 | 2022-07-25 | 18465 | keep | 0 | Jul | 2022 | 0.012576 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-07-25 17:20 | 2022-07-26 09:01 | 1 | 15:41 | P | NO SE REPORTO CAUSA | 3 X 80 EN RISER | C22072500358 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 941 | 2022-07-25 | 941 | keep | 0 | Jul | 2022 | 0.00064091 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-25 17:23 | 2022-07-25 17:24 | 1245 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE DE INTERRUPTOR | M22072500000 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-07-25 | 1245 | keep | 0 | Jul | 2022 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
MAYAGÃœEZ | 2022-07-25 17:24 | 2022-07-25 19:14 | 100 | 1:50 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASES | M22072500238 | New_Event | Animals | Include | Include | Wildlife | 110 | 2022-07-25 | 11000 | keep | 0 | Jul | 2022 | 0.007492 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-07-25 17:24 | 2022-07-25 17:25 | 1192 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | M22072500000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-07-25 | 1192 | keep | 0 | Jul | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-07-25 17:36 | 2022-07-25 17:37 | 1192 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | M22072500000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2022-07-25 | 1192 | keep | 0 | Jul | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CAGUAS | 2022-07-25 17:37 | 2022-07-26 12:50 | 30 | 19:13 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22072500589 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1153 | 2022-07-25 | 34590 | keep | 0 | Jul | 2022 | 0.023559 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-07-25 17:37 | 2022-07-25 23:00 | 150 | 5:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMAARIA Y SE CERRO MACHETES | M22072500286 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 323 | 2022-07-25 | 48450 | keep | 0 | Jul | 2022 | 0.032999 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-07-25 17:55 | 2022-07-26 16:35 | 2 | 22:40 | P | ARBOL SOBRE LINEA | SE REEMPLAZO POSTE PRIMARIO PARTIDO | M22072500134 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 1360 | 2022-07-25 | 2720 | keep | 0 | Jul | 2022 | 0.0018526 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-07-25 18:00 | 2022-07-25 18:40 | 375 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABREN MACHETES PARA CERRAR PUENTE ABIERTO | P22072500069 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 40 | 2022-07-25 | 15000 | keep | 0 | Jul | 2022 | 0.010216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-25 18:09 | 2022-07-25 19:24 | 1245 | 1:15 | T | ARBOL SOBRE LINEA | SE ABRIO MACHETES PARA SECCIONALIZAR ARBOL SOBRE LINEA | M22072500280 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 75 | 2022-07-25 | 93375 | keep | 0 | Jul | 2022 | 0.063597 | 0.00084796 | Sustained | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2022-07-25 18:16 | 2022-07-25 23:10 | 4882 | 4:54 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA REPARAR LINEA PRIMARIA ROTA EN TRONCAL ALIMENTADOR | M22072500193 | New_Event | Primary Wire Break | Include | Include | Equipment | 294 | 2022-07-25 | 1435308 | keep | 0 | Jul | 2022 | 0.97758 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
BARRANQUITAS | 2022-07-25 18:26 | 2022-07-26 10:27 | 5 | 16:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | C22072500616 | New_Event | Primary Wire Break | Include | Include | Equipment | 961 | 2022-07-25 | 4805 | keep | 0 | Jul | 2022 | 0.0032727 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-07-25 18:30 | 2022-07-25 20:07 | 50 | 1:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | M22072500306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-07-25 | 4850 | keep | 0 | Jul | 2022 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-25 18:37 | 2022-07-25 18:53 | 1370 | 0:16 | T | DESCONECTIVO DEFECTUOSO | DISPARO AL CERRAR N/O CONTRA 1521-2 SE ABRIO AMARRE Y CONTINUAN PATRULLANDO | S22072500218 | Partial_restoration | Switch Failure | Include | Include | Equipment | 16 | 2022-07-25 | 21920 | keep | 0 | Jul | 2022 | 0.01493 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-25 18:37 | 2022-07-26 14:05 | 30 | 19:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072500320 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1168 | 2022-07-25 | 35040 | keep | 0 | Jul | 2022 | 0.023866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-07-25 18:42 | 2022-07-26 09:50 | 10 | 15:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA POR LLUVIAS | A22072500125 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 908 | 2022-07-25 | 9080 | keep | 0 | Jul | 2022 | 0.0061843 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-07-25 19:20 | 2022-07-25 19:21 | 3114 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 3114 | keep | 0 | Jul | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-07-25 19:20 | 2022-07-25 19:21 | 2696 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072500176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2696 | keep | 0 | Jul | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
AGUADILLA | 2022-07-25 19:24 | 2022-07-25 20:06 | 100 | 0:42 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA | M22072500385 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 42 | 2022-07-25 | 4200 | keep | 0 | Jul | 2022 | 0.0028606 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-07-25 19:43 | 2022-07-25 21:25 | 378 | 1:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22072500190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-07-25 | 38556 | keep | 0 | Jul | 2022 | 0.02626 | 0.00025745 | Sustained | FALSE | FALSE | Not_TMED_Event | 378
BAYAMON | 2022-07-25 19:47 | 2022-07-25 20:56 | 7 | 1:09 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y SE REALIZO DESGANCHE | B22072500133 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 69 | 2022-07-25 | 483 | keep | 0 | Jul | 2022 | 0.00032897 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-07-25 20:06 | 2022-07-25 20:08 | 1245 | 0:02 | T | ARBOL SOBRE LINEA | SE ABRIO INTERRUPTOR PARA CERRAR MACHETES | M22072500385 | Additional_clients | Vegetation Uprooted Tree | Include | Include | Vegetation | 2 | 2022-07-25 | 2490 | keep | 0 | Jul | 2022 | 0.0016959 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-25 20:17 | 2022-07-26 01:30 | 80 | 5:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES PARA SECCIONALIZAR POSTE PRIMARIO | M22072500456 | New_Event | Primary Pole Failure | Include | Include | Equipment | 313 | 2022-07-25 | 25040 | keep | 0 | Jul | 2022 | 0.017055 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-07-25 20:31 | 2022-07-26 08:55 | 4 | 12:24 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22072500671 | New_Event | Vegetation Contact | Include | Include | Vegetation | 744 | 2022-07-25 | 2976 | keep | 0 | Jul | 2022 | 0.0020269 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-07-25 20:32 | 2022-07-25 21:17 | 12 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE TRANSFORMADOR PARA REPARAR PUENTE PRIMARIO DE LINEA A CAJA TRANSFORMADOR | S22072500091 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2022-07-25 | 540 | keep | 0 | Jul | 2022 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-07-25 20:39 | 2022-07-26 14:27 | 8 | 17:48 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO 2 MACHETES Y 3 PARARRAYOS Y SE CERRO MACHETES 100% EN SERVICIO | S22072500218 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1068 | 2022-07-25 | 8544 | keep | 0 | Jul | 2022 | 0.0058193 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-25 20:45 | 2022-07-26 10:20 | 15 | 13:35 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA | M22072500483 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 815 | 2022-07-25 | 12225 | keep | 0 | Jul | 2022 | 0.0083264 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-07-25 20:47 | 2022-07-25 22:40 | 80 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072500138 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2022-07-25 | 9040 | keep | 0 | Jul | 2022 | 0.0061571 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-07-25 20:48 | 2022-07-25 20:51 | 2450 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL NO CAUSA | C22072500673 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-25 | 7350 | keep | 0 | Jul | 2022 | 0.0050061 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
YAUCO | 2022-07-25 20:52 | 2022-07-25 23:20 | 100 | 2:28 | P | DESGANCHE | 1 X 100 EN C/L SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22072500214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-07-25 | 14800 | keep | 0 | Jul | 2022 | 0.01008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-07-25 21:20 | 2022-07-26 08:35 | 1 | 11:15 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A22072500140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 675 | 2022-07-25 | 675 | keep | 0 | Jul | 2022 | 0.00045974 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-25 21:22 | 2022-07-25 22:37 | 148 | 1:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22072500165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-07-25 | 11100 | keep | 0 | Jul | 2022 | 0.0075602 | 0.0001008 | Sustained | FALSE | FALSE | Not_TMED_Event | 148
SAN JUAN | 2022-07-25 21:24 | 2022-07-26 10:42 | 16 | 13:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO PORTA FUSIBLE 1 X 20 EN RISER A PM | S22072500280 | New_Event | Cutout Failure | Include | Include | Equipment | 798 | 2022-07-25 | 12768 | keep | 0 | Jul | 2022 | 0.0086962 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2022-07-25 21:33 | 2022-07-26 10:52 | 50 | 13:19 | P | ARBOL SOBRE LINEA | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ARBOL SOBRE LINEA PRIMARIA | A22072500142 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 799 | 2022-07-25 | 39950 | keep | 0 | Jul | 2022 | 0.02721 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-25 21:35 | 2022-07-25 21:48 | 342 | 0:13 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE PRIMARIO | S22072500125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 13 | 2022-07-25 | 4446 | keep | 0 | Jul | 2022 | 0.0030282 | 0.00023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 342
HUMACAO | 2022-07-25 21:51 | 2022-07-26 09:50 | 35 | 11:59 | P | DESGANCHE | SE CERRO PUENTE PRIMARIO Y DESGANCHE | C22072500696 | New_Event | Vegetation Contact | Include | Include | Vegetation | 719 | 2022-07-25 | 25165 | keep | 0 | Jul | 2022 | 0.01714 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2022-07-25 21:53 | 2022-07-25 21:54 | 2952 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22072500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 2952 | keep | 0 | Jul | 2022 | 0.0020106 | 0.0020106 | Momentary | FALSE | FALSE | Not_TMED_Event | 2952
YAUCO | 2022-07-25 21:54 | 2022-07-26 08:55 | 70 | 11:01 | P | CONDUCTOR ARRIADO O CRUZADO | SE DESPEGO LINEA PEGANDO A TIERRA DEL POSTE Y SE CERRO PUENTE | M22072500157 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 661 | 2022-07-25 | 46270 | keep | 0 | Jul | 2022 | 0.031514 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-07-25 21:54 | 2022-07-26 08:55 | 100 | 11:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES PRIMARIOS. SE SEGUIRA PATRULLANDO | M22072500390 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 661 | 2022-07-25 | 66100 | keep | 0 | Jul | 2022 | 0.04502 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-25 22:11 | 2022-07-25 22:12 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072500171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-25 | 325 | keep | 0 | Jul | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BARRANQUITAS | 2022-07-25 22:34 | 2022-07-26 06:34 | 80 | 8:00 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22072500700 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2022-07-25 | 38400 | keep | 0 | Jul | 2022 | 0.026154 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-07-25 22:42 | 2022-07-26 09:36 | 100 | 10:54 | P | DESGANCHE | 1X65 EN C/L (SE REALIZO DESGANCHE PRIMARIO) | R22072500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 654 | 2022-07-25 | 65400 | keep | 0 | Jul | 2022 | 0.044544 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-07-25 23:21 | 2022-07-26 16:49 | 25 | 17:28 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE Y SE LEVANTO CONDUCTOR | C22072500716 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2022-07-25 | 26200 | keep | 0 | Jul | 2022 | 0.017845 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-07-25 23:37 | 2022-07-26 03:53 | 5 | 4:16 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO LINEA SECUNDARIA | P22072500255 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 256 | 2022-07-25 | 1280 | keep | 0 | Jul | 2022 | 0.0008718 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-07-25 23:37 | 2022-07-26 10:42 | 35 | 11:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS | M22072500563 | New_Event | Vegetation Contact | Include | Include | Vegetation | 665 | 2022-07-25 | 23275 | keep | 0 | Jul | 2022 | 0.015852 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-07-25 23:53 | 2022-07-26 08:41 | 60 | 8:48 | P | PROBLEMA DEL CLIENTE | 2 X 100 EN C/L Y SE DEJO CLIENTE FUERA POR AVERIA INTERNA | C22072500719 | New_Event | Customer-Related Interruption | Include | Include | Public | 528 | 2022-07-25 | 31680 | keep | 0 | Jul | 2022 | 0.021577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-07-26 00:39 | 2022-07-26 00:40 | 2092 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 2092 | keep | 0 | Jul | 2022 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
ARECIBO | 2022-07-26 00:40 | 2022-07-26 11:13 | 50 | 10:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A22072600001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 633 | 2022-07-26 | 31650 | keep | 0 | Jul | 2022 | 0.021557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-26 01:30 | 2022-07-26 21:52 | 4 | 20:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON PUENTES PRIMARIOS | M22072500456 | New_Event | Primary Wire Break | Include | Include | Equipment | 1222 | 2022-07-26 | 4888 | keep | 0 | Jul | 2022 | 0.0033292 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-07-26 01:38 | 2022-07-26 12:05 | 23 | 10:27 | P | ANIMAL | 1 X 65 1 X 80 EN RISER AVE CRUZO FASE | P22072600011 | New_Event | Animals | Include | Include | Wildlife | 627 | 2022-07-26 | 14421 | keep | 0 | Jul | 2022 | 0.0098221 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
VEGA BAJA | 2022-07-26 02:17 | 2022-07-26 11:35 | 33 | 9:18 | P | ANIMAL | 1 X 65 EN C/L SE RETIRO CULEBRA | B22072600007 | New_Event | Animals | Include | Include | Wildlife | 558 | 2022-07-26 | 18414 | keep | 0 | Jul | 2022 | 0.012542 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
GUAYAMA | 2022-07-26 02:36 | 2022-07-26 11:00 | 10 | 8:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | P22072600020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 504 | 2022-07-26 | 5040 | keep | 0 | Jul | 2022 | 0.0034327 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-07-26 02:38 | 2022-07-26 10:13 | 5 | 7:35 | P | DESGANCHE | 1X10 EN XMR (POR DESGANCHE PRIMARIO) | R22072600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2022-07-26 | 2275 | keep | 0 | Jul | 2022 | 0.0015495 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-07-26 04:28 | 2022-07-26 04:29 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 2234 | keep | 0 | Jul | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-07-26 04:52 | 2022-07-26 09:35 | 52 | 4:43 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22072600019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2022-07-26 | 14716 | keep | 0 | Jul | 2022 | 0.010023 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
ARECIBO | 2022-07-26 04:54 | 2022-07-26 11:58 | 30 | 7:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZA CAJA PRIMARIA | A22072600003 | New_Event | Cutout Failure | Include | Include | Equipment | 424 | 2022-07-26 | 12720 | keep | 0 | Jul | 2022 | 0.0086635 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-07-26 05:23 | 2022-07-26 09:50 | 83 | 4:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22072600038 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2022-07-26 | 22161 | keep | 0 | Jul | 2022 | 0.015094 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
PONCE | 2022-07-26 05:33 | 2022-07-26 05:34 | 1979 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22072600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 1979 | keep | 0 | Jul | 2022 | 0.0013479 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
BARRANQUITAS | 2022-07-26 06:01 | 2022-07-26 06:02 | 2343 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 2343 | keep | 0 | Jul | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
BARRANQUITAS | 2022-07-26 06:17 | 2022-07-26 19:00 | 20 | 12:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIO C/L PARA REMPLAZAR POSTE PRIMARIO PARTIDO Y RELOCALIZAR XMR | C22072600025 | New_Event | Primary Pole Failure | Include | Include | Equipment | 763 | 2022-07-26 | 15260 | keep | 0 | Jul | 2022 | 0.010394 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-07-26 06:33 | 2022-07-26 11:30 | 8 | 4:57 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR POR ALAMBRE CRUZADO | A22072600047 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 297 | 2022-07-26 | 2376 | keep | 0 | Jul | 2022 | 0.0016183 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-07-26 06:44 | 2022-07-26 10:30 | 50 | 3:46 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A22072600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-07-26 | 11300 | keep | 0 | Jul | 2022 | 0.0076964 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-26 06:49 | 2022-07-27 16:00 | 20 | 33:11 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO @ T-8 | S22072600002 | New_Event | UG Cable Fault | Include | Include | Equipment | 1991 | 2022-07-26 | 39820 | keep | 0 | Jul | 2022 | 0.027121 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-07-26 06:49 | 2022-07-26 16:40 | 37 | 9:51 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER PROVISIONAL AEREO 1X 30 EN C/L | S22072600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 591 | 2022-07-26 | 21867 | keep | 0 | Jul | 2022 | 0.014894 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
VEGA BAJA | 2022-07-26 07:01 | 2022-07-26 10:27 | 40 | 3:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIAS | A22072600013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 206 | 2022-07-26 | 8240 | keep | 0 | Jul | 2022 | 0.0056122 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-26 07:11 | 2022-07-26 07:12 | 2435 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO 1909-08 LLEVA LA CARGA DEL 1907-05 | S22072600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-26 | 2435 | keep | 0 | Jul | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-26 07:11 | 2022-07-26 07:12 | 2956 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO LLEVA 1907-05 | S22072600000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-26 | 2956 | keep | 0 | Jul | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-07-26 07:12 | 2022-07-26 12:25 | 136 | 5:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 1 X 80 EN C/L SE REMPLAZO CAJA QUEMADA | S22072600006 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 313 | 2022-07-26 | 42568 | keep | 0 | Jul | 2022 | 0.028993 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
GUAYAMA | 2022-07-26 07:24 | 2022-07-26 12:50 | 44 | 5:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22072600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-07-26 | 14344 | keep | 0 | Jul | 2022 | 0.0097696 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2022-07-26 07:29 | 2022-07-26 12:15 | 60 | 4:46 | P | NO SE REPORTO CAUSA | 1 X 80 EN PROVISIONAL AEREO | B22072600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 286 | 2022-07-26 | 17160 | keep | 0 | Jul | 2022 | 0.011688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-26 07:53 | 2022-07-26 10:20 | 85 | 2:27 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 30 EN C/L | B22072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-07-26 | 12495 | keep | 0 | Jul | 2022 | 0.0085103 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2022-07-26 08:01 | 2022-07-26 10:14 | 30 | 2:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | A22072600019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 133 | 2022-07-26 | 3990 | keep | 0 | Jul | 2022 | 0.0027176 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-07-26 08:08 | 2022-07-27 10:08 | 100 | 25:60 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M22072600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1560 | 2022-07-26 | 156000 | keep | 0 | Jul | 2022 | 0.10625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-07-26 08:11 | 2022-07-26 11:50 | 10 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22072600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-07-26 | 2190 | keep | 0 | Jul | 2022 | 0.0014916 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-07-26 08:17 | 2022-07-27 12:29 | 1 | 28:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA | M22072600065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1692 | 2022-07-26 | 1692 | keep | 0 | Jul | 2022 | 0.0011524 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-07-26 08:28 | 2022-07-26 08:56 | 1 | 0:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22072600054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2022-07-26 | 28 | keep | 0 | Jul | 2022 | 1.9071e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-26 08:41 | 2022-07-26 14:24 | 1 | 5:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C22072600135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2022-07-26 | 343 | keep | 0 | Jul | 2022 | 0.00023362 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-26 08:48 | 2022-07-27 09:32 | 13 | 24:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR Y SE REPARO BAJANTE SECUNDARIO | C22072600180 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1484 | 2022-07-26 | 19292 | keep | 0 | Jul | 2022 | 0.01314 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
YAUCO | 2022-07-26 08:55 | 2022-07-26 09:18 | 2952 | 0:23 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE RETIRO PERSONAL DE LA LINEA Y SE CERRO INTERRUPTOR RELACIONADO EVENTO 390 | M22072600028 | New_Event | Primary Wire Break | Include | Include | Equipment | 23 | 2022-07-26 | 67896 | keep | 0 | Jul | 2022 | 0.046244 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
CAGUAS | 2022-07-26 08:57 | 2022-07-26 11:19 | 14 | 2:22 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 30 EN C/L Y SE REPARO CRUCETA | C22072600068 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 142 | 2022-07-26 | 1988 | keep | 0 | Jul | 2022 | 0.001354 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-07-26 09:05 | 2022-07-26 14:26 | 25 | 5:21 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22072600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-07-26 | 8025 | keep | 0 | Jul | 2022 | 0.0054658 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-07-26 09:17 | 2022-07-26 11:54 | 150 | 2:37 | P | DESGANCHE | 1 X 100 EN PROVISIONAL DESGANCHE PRIMARIO | S22072600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-07-26 | 23550 | keep | 0 | Jul | 2022 | 0.01604 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-07-26 09:18 | 2022-07-26 10:44 | 100 | 1:26 | P | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES PRIMARIOS. SE SEGUIRA PATRULLANDO | M22072500390 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 86 | 2022-07-26 | 8600 | keep | 0 | Jul | 2022 | 0.0058574 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-07-26 09:21 | 2022-07-26 12:43 | 1 | 3:22 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE PUENTES PARA REGAR NEUTRAL PARTIDO E INSTALAR POSTE | A22072600036 | New_Event | Primary Pole Failure | Include | Include | Equipment | 202 | 2022-07-26 | 202 | keep | 0 | Jul | 2022 | 0.00013758 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-26 09:28 | 2022-07-26 19:04 | 10 | 9:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA | A22072600039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 576 | 2022-07-26 | 5760 | keep | 0 | Jul | 2022 | 0.0039231 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-07-26 09:35 | 2022-07-26 11:22 | 10 | 1:47 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22072600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-07-26 | 1070 | keep | 0 | Jul | 2022 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-26 09:35 | 2022-07-26 16:06 | 300 | 6:31 | P | DESGANCHE | SE ABRIO C/L TOTAL PARA QUE WRIGHT TREE SERVICE REALIZARA DESGANCHE | B22072600063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2022-07-26 | 117300 | keep | 0 | Jul | 2022 | 0.079892 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-07-26 09:40 | 2022-07-26 10:00 | 1 | 0:20 | P | TRANSFORMADOR AVERIADO | SE ABRE TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO | S22072500120 | New_Event | Service Transformer Failure | Include | Include | Equipment | 20 | 2022-07-26 | 20 | keep | 0 | Jul | 2022 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-07-26 09:40 | 2022-07-26 13:27 | 5 | 3:47 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | R22072600017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-07-26 | 1135 | keep | 0 | Jul | 2022 | 0.00077304 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-07-26 09:40 | 2022-07-26 14:21 | 3 | 4:41 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | C22072600094 | New_Event | Animals | Include | Include | Wildlife | 281 | 2022-07-26 | 843 | keep | 0 | Jul | 2022 | 0.00057416 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-07-26 09:43 | 2022-07-26 09:50 | 12 | 0:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIO | S22072500276 | New_Event | Secondary Wire Break | Include | Include | Equipment | 7 | 2022-07-26 | 84 | keep | 0 | Jul | 2022 | 5.7212e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-07-26 10:05 | 2022-07-26 12:32 | 1 | 2:27 | P | DESGANCHE | 2 X 65 EN RISER SE RETIRO RAMAS SOBRE LAS LINEAS | M22072600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-07-26 | 147 | keep | 0 | Jul | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-26 10:12 | 2022-07-26 11:45 | 50 | 1:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE PRIMARIO | S22072600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-07-26 | 4650 | keep | 0 | Jul | 2022 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-07-26 10:12 | 2022-07-26 14:30 | 4 | 4:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR FUERTES VIENTOS | A22072600046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 258 | 2022-07-26 | 1032 | keep | 0 | Jul | 2022 | 0.00070289 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-07-26 10:24 | 2022-07-26 11:30 | 1 | 1:06 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | B22072600090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-07-26 | 66 | keep | 0 | Jul | 2022 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-07-26 10:44 | 2022-07-26 10:51 | 2952 | 0:07 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR AL HACER PRUEBA EN CORTE DE LINEA SE RETIRO PERSONAL DE LA LINEA Y SE CERRO INTERRUPTOR RELACIONADO EVENTO 390 | M22072600065 | New_Event | Primary Wire Break | Include | Include | Equipment | 7 | 2022-07-26 | 20664 | keep | 0 | Jul | 2022 | 0.014074 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
AGUADILLA | 2022-07-26 10:49 | 2022-07-26 11:40 | 1 | 0:51 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 10 EN TRANSFORMADOR SE ENDEREZO CRUCETA | M22072600066 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 51 | 2022-07-26 | 51 | keep | 0 | Jul | 2022 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-07-26 10:51 | 2022-07-26 12:19 | 100 | 1:28 | P | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES PRIMARIOS. SE SEGUIRA PATRULLANDO | M22072500390 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 88 | 2022-07-26 | 8800 | keep | 0 | Jul | 2022 | 0.0059936 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-26 10:54 | 2022-07-26 14:25 | 19 | 3:31 | P | NO SE REPORTO CAUSA | 1X 40 EN C/L Y 1 X 40 SU | B22072600100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-07-26 | 4009 | keep | 0 | Jul | 2022 | 0.0027305 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
FAJARDO | 2022-07-26 10:57 | 2022-07-26 11:36 | 7 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | R22072600024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2022-07-26 | 273 | keep | 0 | Jul | 2022 | 0.00018594 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-07-26 10:57 | 2022-07-26 14:39 | 4 | 3:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ELIMINO LA BANDERA DE ALUMINIO Y SE COLOCO CONDUCTORES EN EL BUSHING SECUNDARIO DEL XMR | C22072600111 | New_Event | Secondary Wire Break | Include | Include | Equipment | 222 | 2022-07-26 | 888 | keep | 0 | Jul | 2022 | 0.00060481 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-07-26 11:15 | 2022-07-26 12:00 | 20 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M22072500401 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-07-26 | 900 | keep | 0 | Jul | 2022 | 0.00061299 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-26 11:22 | 2022-07-26 15:34 | 50 | 4:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | S22072600045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2022-07-26 | 12600 | keep | 0 | Jul | 2022 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-26 11:24 | 2022-07-26 11:25 | 1085 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO TENIA H.O. SE VERIFICO CON PERSONAL DE CAMPO EDWARD BEAN Y ELLOS INDICARON QUE NO FUERON Y SE PROCEDIO A CERRAR INTERRUPTOR QUEDO EN SERVICIO | S22072600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 1085 | keep | 0 | Jul | 2022 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
HUMACAO | 2022-07-26 11:31 | 2022-07-26 19:09 | 12 | 7:38 | P | SECUNDARIA/OTROS | 1 X 10 EN XMR REMPLAZO SECUNDARIA SOTERRADA, 2 PEDESTALES Y 6 BARRAS | C22072600117 | New_Event |  |  |  |  | 458 | 2022-07-26 | 5496 | keep | 0 | Jul | 2022 | 0.0037433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-07-26 11:43 | 2022-07-26 15:14 | 60 | 3:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22072600087 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2022-07-26 | 12660 | keep | 0 | Jul | 2022 | 0.0086227 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-26 11:45 | 2022-07-26 13:30 | 15 | 1:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE MONTURA PARA REMPLAZAR CAJAS Y AISLACION Y PARARRAYOS Y SE RELOCALIZO NEUTRAL | S22072600030 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2022-07-26 | 1575 | keep | 0 | Jul | 2022 | 0.0010727 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-07-26 11:45 | 2022-07-26 20:11 | 40 | 8:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | S22072600051 | New_Event | Primary Pole Failure | Include | Include | Equipment | 506 | 2022-07-26 | 20240 | keep | 0 | Jul | 2022 | 0.013785 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-26 11:46 | 2022-07-27 09:45 | 40 | 21:59 | P | DESGANCHE | 1 X 50 EN TRANSFORMADOR POR DESGANCHE | M22072600286 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1319 | 2022-07-26 | 52760 | keep | 0 | Jul | 2022 | 0.035935 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-07-26 11:55 | 2022-07-26 13:02 | 20 | 1:07 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22072600123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-07-26 | 1340 | keep | 0 | Jul | 2022 | 0.00091267 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-07-26 11:59 | 2022-07-26 12:00 | 4279 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | P22072600091 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-07-26 | 4279 | keep | 0 | Jul | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-07-26 11:59 | 2022-07-26 12:00 | 464 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | P22072600091 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-07-26 | 464 | keep | 0 | Jul | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-07-26 12:00 | 2022-07-26 14:24 | 258 | 2:24 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA GLOBO DE HELIO EN LINEA PRIMARIA | P22072600096 | 1st_after_momentary | Damage From Public | Include | Include | Public | 144 | 2022-07-26 | 37152 | keep | 0 | Jul | 2022 | 0.025304 | 0.00017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 258
YAUCO | 2022-07-26 12:11 | 2022-07-27 10:03 | 5 | 21:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA VERIFICAR SOTERRADO Y SE REEMPLAZA BARRA | M22072600102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1312 | 2022-07-26 | 6560 | keep | 0 | Jul | 2022 | 0.004468 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-07-26 12:15 | 2022-07-26 14:08 | 12 | 1:53 | P | OTRAS CAUSAS | SE ABRIO XMR PARA CONECTAR CLIENTE COMERCIAL NUEVO Y SE SUBIO TAP | B22072600112 | New_Event | Other Causes | Include | Include | Other | 113 | 2022-07-26 | 1356 | keep | 0 | Jul | 2022 | 0.00092357 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-07-26 12:17 | 2022-07-26 14:45 | 17 | 2:28 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO BAJANTE PRIMARIO EN TRANSFORMADOR | P22072600099 | New_Event | Primary Wire Break | Include | Include | Equipment | 148 | 2022-07-26 | 2516 | keep | 0 | Jul | 2022 | 0.0017136 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
YAUCO | 2022-07-26 12:19 | 2022-07-26 13:22 | 2952 | 1:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR NO CERRO POR SCADA CERRADO MANUAL ELECTRICO | M22072600096 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 63 | 2022-07-26 | 185976 | keep | 0 | Jul | 2022 | 0.12667 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-26 12:27 | 2022-07-26 15:57 | 116 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA A MACHETE | S22072600056 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2022-07-26 | 24360 | keep | 0 | Jul | 2022 | 0.016591 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
SAN JUAN | 2022-07-26 12:30 | 2022-07-26 15:20 | 18 | 2:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PODRIDO 5O KVA POR 50 KVA 1 X 15 EN TRANSFORMADOR | S22072600072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 170 | 2022-07-26 | 3060 | keep | 0 | Jul | 2022 | 0.0020842 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-07-26 12:34 | 2022-07-26 15:41 | 200 | 3:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072600103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 187 | 2022-07-26 | 37400 | keep | 0 | Jul | 2022 | 0.025473 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-07-26 12:42 | 2022-07-26 17:12 | 12 | 4:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE RETEZARON LINEAS PRIMARIAS Y SE ENDEREZO POSTE | M22072600107 | New_Event | Primary Pole Failure | Include | Include | Equipment | 270 | 2022-07-26 | 3240 | keep | 0 | Jul | 2022 | 0.0022067 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-07-26 12:55 | 2022-07-26 14:05 | 15 | 1:10 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR PAJARO CRUZO FASE | P22072600101 | New_Event | Animals | Include | Include | Wildlife | 70 | 2022-07-26 | 1050 | keep | 0 | Jul | 2022 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-07-26 13:00 | 2022-07-26 13:39 | 8 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22072600057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2022-07-26 | 312 | keep | 0 | Jul | 2022 | 0.0002125 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-07-26 13:00 | 2022-07-26 13:26 | 1 | 0:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22072600063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-07-26 | 26 | keep | 0 | Jul | 2022 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-07-26 13:22 | 2022-07-26 21:45 | 100 | 8:23 | P | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES PRIMARIOS. SE SEGUIRA PATRULLANDO | M22072500390 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 503 | 2022-07-26 | 50300 | keep | 0 | Jul | 2022 | 0.034259 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-07-26 13:32 | 2022-07-26 16:35 | 5 | 3:03 | P | SECUNDARIA/DESGANCHE | 1 X10 EN XMR SE DESGANCHO BAJANTE SECUNDARIO | C22072600131 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 183 | 2022-07-26 | 915 | keep | 0 | Jul | 2022 | 0.0006232 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-07-26 13:34 | 2022-07-26 15:33 | 4 | 1:59 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | C22072600133 | New_Event | Animals | Include | Include | Wildlife | 119 | 2022-07-26 | 476 | keep | 0 | Jul | 2022 | 0.0003242 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-07-26 13:45 | 2022-07-26 15:16 | 12 | 1:31 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR Y SE HIZO DESGANCHE SECUNDARIO | S22072600077 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 91 | 2022-07-26 | 1092 | keep | 0 | Jul | 2022 | 0.00074376 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-07-26 13:45 | 2022-07-26 15:20 | 12 | 1:35 | P | OTRAS CAUSAS | SE ABRE TRANSFORMADOR PARA REEMPLAZO DE HERRAJES | P22072600106 | New_Event | Other Causes | Include | Include | Other | 95 | 2022-07-26 | 1140 | keep | 0 | Jul | 2022 | 0.00077645 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-07-26 13:51 | 2022-07-26 15:00 | 20 | 1:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | A22072600069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 69 | 2022-07-26 | 1380 | keep | 0 | Jul | 2022 | 0.00093991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-07-26 13:56 | 2022-07-26 16:37 | 11 | 2:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE DESGANCHO Y REPARO BAJANTE SECUNDARIO NO FUNDIO | C22072500366 | New_Event | Secondary Wire Break | Include | Include | Equipment | 161 | 2022-07-26 | 1771 | keep | 0 | Jul | 2022 | 0.0012062 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-07-26 14:32 | 2022-07-26 16:45 | 10 | 2:13 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR SE DESGANCHO ENREDADERA EN SECUNDARIA | S22072600091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-07-26 | 1330 | keep | 0 | Jul | 2022 | 0.00090586 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-26 14:32 | 2022-07-26 16:27 | 7 | 1:55 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN CORTE DE LINEA SE RETIRO BAMBUS | A22072600074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 115 | 2022-07-26 | 805 | keep | 0 | Jul | 2022 | 0.00054828 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-07-26 14:34 | 2022-07-26 21:08 | 100 | 6:34 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARARON PUENTES PRIMARIOS ABIERTOS | M22072600138 | New_Event | Primary Wire Break | Include | Include | Equipment | 394 | 2022-07-26 | 39400 | keep | 0 | Jul | 2022 | 0.026835 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-26 14:38 | 2022-07-26 17:06 | 50 | 2:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22072600141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-07-26 | 7400 | keep | 0 | Jul | 2022 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-07-26 14:40 | 2022-07-26 18:30 | 10 | 3:50 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO PUENTE PRIMARIO EN TRANSFORMADOR | P22072600116 | New_Event | Primary Wire Break | Include | Include | Equipment | 230 | 2022-07-26 | 2300 | keep | 0 | Jul | 2022 | 0.0015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-26 14:46 | 2022-07-26 15:56 | 2000 | 1:10 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR (1619-02) SE TRANSFIRIO CARGA DEL 1619-02 AL 1619-03 MEDIANTE G.O.I. SJ-220706-50 RECIERRA, SE QUEDA ABIERTO Y NO CAMBIA INDICACION POR SCADA HC-MON73981-1 | R22072600124 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 70 | 2022-07-26 | 140000 | keep | 0 | Jul | 2022 | 0.095353 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2022-07-26 14:49 | 2022-07-26 17:52 | 9 | 3:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA | B22072600125 | New_Event | Service Transformer Failure | Include | Include | Equipment | 183 | 2022-07-26 | 1647 | keep | 0 | Jul | 2022 | 0.0011218 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-07-26 14:58 | 2022-07-27 10:31 | 70 | 19:33 | P | CONDUCTOR ROTO O ABIERTO | SE DESPEGO LINEA PEGANDO A TIERRA DEL POSTE Y SE CERRO PUENTE | M22072500146 | New_Event | Primary Wire Break | Include | Include | Equipment | 1173 | 2022-07-26 | 82110 | keep | 0 | Jul | 2022 | 0.055925 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-07-26 14:59 | 2022-07-26 16:00 | 1 | 1:01 | P | NO SE REPORTO CAUSA | 2 X 30 EN XMR NO SE REPORTO CAUSA | C22072600141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-07-26 | 61 | keep | 0 | Jul | 2022 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-07-26 15:00 | 2022-07-26 17:24 | 100 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO REPORTO CAUSA | A22072600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-07-26 | 14400 | keep | 0 | Jul | 2022 | 0.0098078 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-07-26 15:14 | 2022-07-26 17:50 | 16 | 2:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO DE CONECCIONEA EN LINEA SECUNDARIA | P22072600122 | New_Event | Secondary Wire Break | Include | Include | Equipment | 156 | 2022-07-26 | 2496 | keep | 0 | Jul | 2022 | 0.0017 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-07-26 15:24 | 2022-07-26 17:19 | 30 | 1:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S22072600101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-07-26 | 3450 | keep | 0 | Jul | 2022 | 0.0023498 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-07-26 15:30 | 2022-07-26 16:45 | 15 | 1:15 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22072600081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-07-26 | 1125 | keep | 0 | Jul | 2022 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-07-26 15:39 | 2022-07-26 16:51 | 172 | 1:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 65 EN CORTE DE LINEA SE REAMPLAZO AISLADOR Y CAJA | S22072600030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 72 | 2022-07-26 | 12384 | keep | 0 | Jul | 2022 | 0.0084347 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2022-07-26 15:53 | 2022-07-26 19:06 | 66 | 3:13 | P | DESGANCHE | 2 X 40 EN C/L | C22072600147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-07-26 | 12738 | keep | 0 | Jul | 2022 | 0.0086758 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BAYAMON | 2022-07-26 15:54 | 2022-07-26 16:21 | 10 | 0:27 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE RELOCALIZO SECUNDARIA Y ELIMINAR POSTE SECUNDARIO PARTIDO | B22072600132 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 27 | 2022-07-26 | 270 | keep | 0 | Jul | 2022 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-07-26 15:54 | 2022-07-27 13:10 | 8 | 21:16 | P | TRANSFORMADOR AVERIADO | SE ABRE EN EL T-13A HACIA T-13 PARA REMPLAZO DE PM 75 KVA @ 7.620 KV | P22072600125 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1276 | 2022-07-26 | 10208 | keep | 0 | Jul | 2022 | 0.0069526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-07-26 16:00 | 2022-07-26 18:34 | 27 | 2:34 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L SE REMOVIO GRUA PRIVADA TOCANDO LINEA | S22072600112 | New_Event | Damage From Public | Include | Include | Public | 154 | 2022-07-26 | 4158 | keep | 0 | Jul | 2022 | 0.002832 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2022-07-26 16:03 | 2022-07-26 19:46 | 45 | 3:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072600166 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 223 | 2022-07-26 | 10035 | keep | 0 | Jul | 2022 | 0.0068348 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-07-26 16:19 | 2022-07-26 17:34 | 10 | 1:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR POR MACETILLA QUEMADA | M22072600175 | New_Event | Cutout Failure | Include | Include | Equipment | 75 | 2022-07-26 | 750 | keep | 0 | Jul | 2022 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-26 16:22 | 2022-07-26 16:36 | 14 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON CONEXIONES EN BAJANTES SECUNDARIOS | B22072600131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2022-07-26 | 196 | keep | 0 | Jul | 2022 | 0.00013349 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2022-07-26 16:31 | 2022-07-26 17:00 | 1 | 0:29 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L NO CAUSA | C22072600150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 29 | 2022-07-26 | 29 | keep | 0 | Jul | 2022 | 1.9752e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-07-26 16:37 | 2022-07-26 17:41 | 50 | 1:04 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22072600137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-07-26 | 3200 | keep | 0 | Jul | 2022 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-26 16:57 | 2022-07-26 17:33 | 6 | 0:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE TRANSFORMADOR SE LEVANTO SECUNDARIA SE DESGANCHO Y SE REMPLAZO CAJA DE TRANSFORMADOR | S22072600104 | New_Event | Cutout Failure | Include | Include | Equipment | 36 | 2022-07-26 | 216 | keep | 0 | Jul | 2022 | 0.00014712 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-07-26 16:58 | 2022-07-26 18:48 | 25 | 1:50 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE PRIMARIO | S22072600123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-07-26 | 2750 | keep | 0 | Jul | 2022 | 0.001873 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-07-26 17:04 | 2022-07-27 10:00 | 12 | 16:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ABIERTA | P22072600130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1016 | 2022-07-26 | 12192 | keep | 0 | Jul | 2022 | 0.0083039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-07-26 17:13 | 2022-07-26 18:23 | 15 | 1:10 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR SE RETESO SECUNDARIA Y SE HIZO DESGANCHE SECUNDARIO | S22072600125 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 70 | 2022-07-26 | 1050 | keep | 0 | Jul | 2022 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-07-26 17:22 | 2022-07-26 18:29 | 170 | 1:07 | P | CAUSAS EXTERNAS | SE RETIRO POSTE DE COMUNICACIONES DEL 4KV/SE LEVANTO CONDUCTOR PRIMARIO QUE CAYO ENCIMA DEL CABLE DE TELEFONO (NO FUNDIO) | R22072600200 | New_Event | Damage From Public | Include | Include | Public | 67 | 2022-07-26 | 11390 | keep | 0 | Jul | 2022 | 0.0077577 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
SAN JUAN | 2022-07-26 17:33 | 2022-07-26 17:37 | 314 | 0:04 | T | ERROR HUMANO | DISPARO AL CERRAR CAJA PRIMARIA DE TRANSFORMADOR SE LE MOVIO CAJA PRIMARIA Y SE PEGO A NEUTRAL | S22072600130 | New_Event | Human Error | Include | Include | Other | 4 | 2022-07-26 | 1256 | keep | 0 | Jul | 2022 | 0.00085546 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
HUMACAO | 2022-07-26 17:35 | 2022-07-26 17:48 | 1 | 0:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22072600153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-07-26 | 13 | keep | 0 | Jul | 2022 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-26 17:37 | 2022-07-26 17:49 | 6 | 0:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR SE LEVANTO SECUNDARIA SE DESGANCHO Y SE REMPLAZO CAJA DE TRANSFORMADOR | S22072600104 | New_Event | Secondary Wire Break | Include | Include | Equipment | 12 | 2022-07-26 | 72 | keep | 0 | Jul | 2022 | 4.9039e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-07-26 17:38 | 2022-07-26 17:40 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22072600155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-26 | 3758 | keep | 0 | Jul | 2022 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
UTUADO | 2022-07-26 17:45 | 2022-07-27 19:55 | 25 | 26:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 30 EN MONTURA SE REMPLAZO POSTE PARTIDO Y SE REGARON TRAMOS DE LINEA PRIMARIA | A22072600087 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1570 | 2022-07-26 | 39250 | keep | 0 | Jul | 2022 | 0.026733 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-07-26 17:46 | 2022-07-26 18:40 | 10 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON CONEXIONES SECUNDARIAS | B22072600143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2022-07-26 | 540 | keep | 0 | Jul | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-26 17:55 | 2022-07-26 19:24 | 12 | 1:29 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | R22072600204 | New_Event | Animals | Include | Include | Wildlife | 89 | 2022-07-26 | 1068 | keep | 0 | Jul | 2022 | 0.00072741 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-07-26 18:12 | 2022-07-27 10:27 | 2 | 16:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE CORTE DE LINEA PARA REMPLAZO CAJA QUEMADA | S22072600130 | New_Event | Cutout Failure | Include | Include | Equipment | 975 | 2022-07-26 | 1950 | keep | 0 | Jul | 2022 | 0.0013281 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-07-26 18:39 | 2022-07-26 20:04 | 8 | 1:25 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | R22072600209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-07-26 | 680 | keep | 0 | Jul | 2022 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-07-26 18:46 | 2022-07-26 22:40 | 8 | 3:54 | P | SECUNDARIA/OTROS | 1 X 15 EN TRANSFORMADOR PEDESTAL SECUNDARIO ROTO | M22072600219 | New_Event |  |  |  |  | 234 | 2022-07-26 | 1872 | keep | 0 | Jul | 2022 | 0.001275 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-07-26 18:46 | 2022-07-26 20:57 | 4 | 2:11 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO, SE REPARO SECUNDARIA Y SE BAJO TAP DEL 4 AL 3 | B22072600148 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 131 | 2022-07-26 | 524 | keep | 0 | Jul | 2022 | 0.00035689 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-07-26 18:59 | 2022-07-27 04:05 | 30 | 9:06 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | P22072600141 | New_Event | Primary Wire Break | Include | Include | Equipment | 546 | 2022-07-26 | 16380 | keep | 0 | Jul | 2022 | 0.011156 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-07-26 19:00 | 2022-07-26 19:20 | 6 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO PARTIDO | A22072600085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-07-26 | 120 | keep | 0 | Jul | 2022 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-07-26 19:01 | 2022-07-27 12:40 | 6 | 17:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C22072600159 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1059 | 2022-07-26 | 6354 | keep | 0 | Jul | 2022 | 0.0043277 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-07-26 19:14 | 2022-07-27 08:51 | 12 | 13:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y PARARRAYO | C22072600160 | New_Event | Cutout Failure | Include | Include | Equipment | 817 | 2022-07-26 | 9804 | keep | 0 | Jul | 2022 | 0.0066775 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-26 19:15 | 2022-07-27 11:20 | 1 | 16:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L EVENTO TRANSFERIDO DE CAGUAS | C22072600161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 965 | 2022-07-26 | 965 | keep | 0 | Jul | 2022 | 0.00065726 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-07-26 19:16 | 2022-07-27 12:17 | 15 | 17:01 | P | DESGANCHE | 1 X 40 EN C/L SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22072600143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1021 | 2022-07-26 | 15315 | keep | 0 | Jul | 2022 | 0.010431 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-07-26 19:27 | 2022-07-26 21:11 | 80 | 1:44 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22072600228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-07-26 | 8320 | keep | 0 | Jul | 2022 | 0.0056667 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-26 19:31 | 2022-07-27 13:00 | 25 | 17:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | B22072600150 | New_Event | Primary Wire Break | Include | Include | Equipment | 1049 | 2022-07-26 | 26225 | keep | 0 | Jul | 2022 | 0.017862 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-07-26 19:34 | 2022-07-26 19:35 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 1922 | keep | 0 | Jul | 2022 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2022-07-26 19:35 | 2022-07-27 00:13 | 58 | 4:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L CONECTO BAJANTE DE LINEA A CAJA | C22072600170 | New_Event | Primary Wire Break | Include | Include | Equipment | 278 | 2022-07-26 | 16124 | keep | 0 | Jul | 2022 | 0.010982 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
AGUADILLA | 2022-07-26 19:39 | 2022-07-26 21:15 | 6 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22072600234 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2022-07-26 | 576 | keep | 0 | Jul | 2022 | 0.00039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-07-26 19:40 | 2022-07-27 09:12 | 15 | 13:32 | P | DESGANCHE | 1 X 20 EN C/L Y 1 X 8 EN XMR SE RETIRO BAMBUA SOBRE LINEA | C22072600168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 812 | 2022-07-26 | 12180 | keep | 0 | Jul | 2022 | 0.0082957 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-07-26 19:49 | 2022-07-27 06:47 | 40 | 10:58 | P | ANIMAL | 1 X 50 EN C/L SE REEMPLAZO PORTAFUSIBLE CRUCE POR AVE | C22072600172 | New_Event | Animals | Include | Include | Wildlife | 658 | 2022-07-26 | 26320 | keep | 0 | Jul | 2022 | 0.017926 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-07-26 20:04 | 2022-07-26 20:05 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R22072600212 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 7621 | keep | 0 | Jul | 2022 | 0.0051906 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-07-26 20:05 | 2022-07-26 20:19 | 8 | 0:14 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | R22072600209 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 14 | 2022-07-26 | 112 | keep | 0 | Jul | 2022 | 7.6283e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-07-26 20:06 | 2022-07-26 20:59 | 6 | 0:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | A22072600096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 53 | 2022-07-26 | 318 | keep | 0 | Jul | 2022 | 0.00021659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-07-26 20:09 | 2022-07-26 21:18 | 80 | 1:09 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | R22072600213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-07-26 | 5520 | keep | 0 | Jul | 2022 | 0.0037596 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-26 20:27 | 2022-07-26 21:19 | 6 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON BARRAS SECUNDARIAS EN PEDESTAL | S22072600133 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2022-07-26 | 312 | keep | 0 | Jul | 2022 | 0.0002125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-07-26 20:39 | 2022-07-27 06:50 | 15 | 10:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REPARO SECUNDARIA TRASPATIO | S22072600146 | New_Event | Secondary Wire Break | Include | Include | Equipment | 611 | 2022-07-26 | 9165 | keep | 0 | Jul | 2022 | 0.0062422 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-07-26 21:02 | 2022-07-27 10:10 | 6 | 13:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22072600099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 788 | 2022-07-26 | 4728 | keep | 0 | Jul | 2022 | 0.0032202 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-07-26 21:17 | 2022-07-27 08:30 | 15 | 11:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE AVERIADO | A22072600102 | New_Event | Cutout Failure | Include | Include | Equipment | 673 | 2022-07-26 | 10095 | keep | 0 | Jul | 2022 | 0.0068757 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-07-26 21:47 | 2022-07-27 10:10 | 13 | 12:23 | P | CAUSAS EXTERNAS | 1 X 20 EN TRANSFORMADOR CONDUCTOR SECUNDARIO CRUZADO CON BRAZO DE FOCO | P22072600148 | New_Event | Damage From Public | Include | Include | Public | 743 | 2022-07-26 | 9659 | keep | 0 | Jul | 2022 | 0.0065787 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-07-26 21:49 | 2022-07-26 22:30 | 100 | 0:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072600265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2022-07-26 | 4100 | keep | 0 | Jul | 2022 | 0.0027925 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-07-26 22:14 | 2022-07-26 23:54 | 200 | 1:40 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R22072600023 | New_Event | Animals | Include | Include | Wildlife | 100 | 2022-07-26 | 20000 | keep | 0 | Jul | 2022 | 0.013622 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-07-26 22:17 | 2022-07-27 11:19 | 60 | 13:02 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | M22072600291 | New_Event | Primary Wire Break | Include | Include | Equipment | 782 | 2022-07-26 | 46920 | keep | 0 | Jul | 2022 | 0.031957 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-07-26 22:18 | 2022-07-27 11:22 | 1 | 13:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | A22072600107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 784 | 2022-07-26 | 784 | keep | 0 | Jul | 2022 | 0.00053398 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-26 22:46 | 2022-07-27 14:54 | 200 | 16:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072600298 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 968 | 2022-07-26 | 193600 | keep | 0 | Jul | 2022 | 0.13186 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-07-26 22:54 | 2022-07-27 05:05 | 236 | 6:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO PORTAFUSIBLE | S22072600155 | New_Event | Cutout Failure | Include | Include | Equipment | 371 | 2022-07-26 | 87556 | keep | 0 | Jul | 2022 | 0.059634 | 0.00016074 | Sustained | FALSE | FALSE | Not_TMED_Event | 236
SAN JUAN | 2022-07-26 23:00 | 2022-07-26 23:01 | 8679 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-03 LLEVANDO 85% 1204-05 Y CON 10% DE SU CARGA POR 1620-02 | S22072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 8679 | keep | 0 | Jul | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-07-26 23:00 | 2022-07-26 23:01 | 3720 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1206-03 LLEVANDO 85% 1204-05 Y CON 10% DE SU CARGA POR 1620-02 | S22072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-26 | 3720 | keep | 0 | Jul | 2022 | 0.0025337 | 0.0025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 3720
ARECIBO | 2022-07-26 23:34 | 2022-07-27 10:58 | 10 | 11:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS AVERIADAS DE TRANSFORMADOR | A22072600108 | New_Event | Cutout Failure | Include | Include | Equipment | 684 | 2022-07-26 | 6840 | keep | 0 | Jul | 2022 | 0.0046587 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-26 23:37 | 2022-07-27 10:18 | 1 | 10:41 | P | TERMINACION SOTERRADA AVERIADA | 1X65 EN C/L, 1X40 EN SU-4 & SE REMPLAZO TERMINACION QUEMADA EN SU-4 | R22072600244 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 641 | 2022-07-26 | 641 | keep | 0 | Jul | 2022 | 0.00043658 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-26 23:37 | 2022-07-27 03:15 | 70 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | M22072600307 | New_Event | Primary Wire Break | Include | Include | Equipment | 218 | 2022-07-26 | 15260 | keep | 0 | Jul | 2022 | 0.010394 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-07-26 23:48 | 2022-07-26 23:50 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1346-06 Y 1303-01 Y SU CARGA POR 1303-05 SE CERRO POR SCADA | S22072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-26 | 3362 | keep | 0 | Jul | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-07-26 23:48 | 2022-07-26 23:50 | 1598 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1346-06 Y 1303-01 Y SU CARGA POR 1303-05 SE CERRO POR SCADA | S22072600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-26 | 3196 | keep | 0 | Jul | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
AGUADILLA | 2022-07-26 23:51 | 2022-07-27 08:17 | 100 | 8:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M22072600309 | New_Event | Vegetation Contact | Include | Include | Vegetation | 506 | 2022-07-26 | 50600 | keep | 0 | Jul | 2022 | 0.034463 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-27 00:45 | 2022-07-27 03:35 | 75 | 2:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO LNEA A PARARRAYO EN XMR HACIENDO CONTACTO CON CRUCETA SE REMPLAZO PARARRAYO Y CAJA PRIMARIA | S22072700001 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2022-07-27 | 12750 | keep | 0 | Jul | 2022 | 0.008684 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-07-27 00:45 | 2022-07-27 02:48 | 892 | 2:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1437-04 LLEVANDO 10% 1301-02 SE SECCIONALIZO PUENTE LINEA PARARRAYO EN XMR HACIENDO CONTACTO CON CRUCETA. SE CERRO POR SCADA 100% 1437-04 EN SERVICIO FUERA 10% 1301-02 | S22072700001 | New_Event | Primary Wire Break | Include | Include | Equipment | 123 | 2022-07-27 | 109716 | keep | 0 | Jul | 2022 | 0.074727 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
CANOVANAS | 2022-07-27 01:28 | 2022-07-27 08:59 | 80 | 7:31 | P | DESGANCHE | 1X50 EN C/L SE DESGANCHO ENRREDADERA EN PRIMARIA | R22072700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2022-07-27 | 36080 | keep | 0 | Jul | 2022 | 0.024574 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-27 01:29 | 2022-07-27 01:31 | 651 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-27 | 1302 | keep | 0 | Jul | 2022 | 0.00088679 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
CAGUAS | 2022-07-27 01:42 | 2022-07-27 01:44 | 3108 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CERRADO X CONTROL | C22072700004 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-07-27 | 6216 | keep | 0 | Jul | 2022 | 0.0042337 | 0.0021168 | Momentary | FALSE | FALSE | Not_TMED_Event | 3108
BAYAMON | 2022-07-27 01:42 | 2022-07-27 10:00 | 50 | 8:18 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN C/L SE DESGANCHO | B22072700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 498 | 2022-07-27 | 24900 | keep | 0 | Jul | 2022 | 0.016959 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-07-27 01:44 | 2022-07-27 11:33 | 20 | 9:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA, PUENTE PRIMARIO Y HOT CLAMP | C22072700022 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 589 | 2022-07-27 | 11780 | keep | 0 | Jul | 2022 | 0.0080233 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-07-27 01:51 | 2022-07-27 12:16 | 10 | 10:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22072700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 625 | 2022-07-27 | 6250 | keep | 0 | Jul | 2022 | 0.0042568 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-27 02:09 | 2022-07-27 09:30 | 50 | 7:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22072700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 441 | 2022-07-27 | 22050 | keep | 0 | Jul | 2022 | 0.015018 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-07-27 04:37 | 2022-07-27 09:33 | 10 | 4:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22072700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-07-27 | 2960 | keep | 0 | Jul | 2022 | 0.002016 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-27 04:59 | 2022-07-27 10:45 | 30 | 5:46 | P | ANIMAL | 1 X 30 EN C/L SE RETIRO IGUANA | B22072700015 | New_Event | Animals | Include | Include | Wildlife | 346 | 2022-07-27 | 10380 | keep | 0 | Jul | 2022 | 0.0070698 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-07-27 05:41 | 2022-07-27 07:56 | 25 | 2:15 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22072700008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-07-27 | 3375 | keep | 0 | Jul | 2022 | 0.0022987 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-07-27 05:41 | 2022-07-27 07:44 | 80 | 2:03 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C22072700012 | New_Event | Animals | Include | Include | Wildlife | 123 | 2022-07-27 | 9840 | keep | 0 | Jul | 2022 | 0.006702 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-07-27 05:59 | 2022-07-27 12:08 | 80 | 6:09 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETEZARON LINEAS PRIMARIAS Y SE REALIZO DESGANCHE MASIVO | A22072700007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-07-27 | 29520 | keep | 0 | Jul | 2022 | 0.020106 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-27 06:09 | 2022-07-27 06:10 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 320 | keep | 0 | Jul | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
GUAYAMA | 2022-07-27 06:40 | 2022-07-27 12:20 | 60 | 5:40 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L LINEA PRIMARIA ARRIADA | P22072700003 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 340 | 2022-07-27 | 20400 | keep | 0 | Jul | 2022 | 0.013894 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-27 06:46 | 2022-07-27 06:47 | 1210 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECERRO | B22072700000 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-07-27 | 1210 | keep | 0 | Jul | 2022 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
YAUCO | 2022-07-27 06:48 | 2022-07-27 13:12 | 4 | 6:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARA BAJANTE SECUNDARIO | P22072700005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 384 | 2022-07-27 | 1536 | keep | 0 | Jul | 2022 | 0.0010462 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-07-27 07:08 | 2022-07-27 09:49 | 11 | 2:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN TRANSFORMADORES DIFERENTES SE REMPLAZO PORTAFUSIBLE | S22072700039 | New_Event | Cutout Failure | Include | Include | Equipment | 161 | 2022-07-27 | 1771 | keep | 0 | Jul | 2022 | 0.0012062 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-07-27 07:08 | 2022-07-27 10:05 | 49 | 2:57 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN PROVISIONAL A T-43 AVERIA NUEVA T-43 A T-44 AVERIA VIEJA SU-6 A T-44 SE QUEDO FUERA T-44 | S22072700026 | New_Event | UG Cable Fault | Include | Include | Equipment | 177 | 2022-07-27 | 8673 | keep | 0 | Jul | 2022 | 0.0059071 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
GUAYAMA | 2022-07-27 07:15 | 2022-07-27 11:16 | 74 | 4:01 | P | ANIMAL | 1 X 65 EN C/L CRUCE DE FASE PRIMARIA POR AVE | P22072700009 | New_Event | Animals | Include | Include | Wildlife | 241 | 2022-07-27 | 17834 | keep | 0 | Jul | 2022 | 0.012147 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
HUMACAO | 2022-07-27 07:19 | 2022-07-27 07:21 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-27 | 4252 | keep | 0 | Jul | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2022-07-27 07:32 | 2022-07-27 07:34 | 143 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 80% DEL 1404-07 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-27 | 286 | keep | 0 | Jul | 2022 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-07-27 07:32 | 2022-07-27 07:34 | 1085 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 80% POR 1404-06 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-27 | 2170 | keep | 0 | Jul | 2022 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-07-27 07:49 | 2022-07-27 10:42 | 1746 | 2:53 | T | PROBLEMA DEL CLIENTE | SE SECCIONALIZO ALIMENTADOR (AVERIA SUB. CUARTEL DE POLICIA Y VILLA PESQUERA)ENTRO 60% DE ALIMENTADOR | B22072700039 | New_Event | Customer-Related Interruption | Include | Include | Public | 173 | 2022-07-27 | 302058 | keep | 0 | Jul | 2022 | 0.20573 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
CAGUAS | 2022-07-27 08:23 | 2022-07-27 08:24 | 2417 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C22072700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 2417 | keep | 0 | Jul | 2022 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
CANOVANAS | 2022-07-27 08:29 | 2022-07-27 11:31 | 1 | 3:02 | P | DESGANCHE | 1X50 EN C/L SE REALIZO DESGANCHE PRIMARIO | R22072700019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-07-27 | 182 | keep | 0 | Jul | 2022 | 0.00012396 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-27 08:29 | 2022-07-27 12:15 | 30 | 3:46 | P | DESGANCHE | SE REALIZO DESGANCHE SE RETEZO LINEA PRIMARIA Y REPARO SECUNDARIA | C22072700027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-07-27 | 6780 | keep | 0 | Jul | 2022 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-27 08:30 | 2022-07-27 08:31 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 3438 | keep | 0 | Jul | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
SAN JUAN | 2022-07-27 08:30 | 2022-07-27 11:20 | 20 | 2:50 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L SE RETEZO LINEA | S22072700046 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 170 | 2022-07-27 | 3400 | keep | 0 | Jul | 2022 | 0.0023157 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-07-27 08:31 | 2022-07-27 15:10 | 1 | 6:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | B22072700052 | New_Event | Cutout Failure | Include | Include | Equipment | 399 | 2022-07-27 | 399 | keep | 0 | Jul | 2022 | 0.00027176 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-27 08:31 | 2022-07-27 12:20 | 50 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22072700057 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-07-27 | 11450 | keep | 0 | Jul | 2022 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-07-27 08:31 | 2022-07-27 21:05 | 7 | 12:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22072700012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 754 | 2022-07-27 | 5278 | keep | 0 | Jul | 2022 | 0.0035948 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-07-27 08:38 | 2022-07-27 11:55 | 60 | 3:17 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B22072700051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-07-27 | 11820 | keep | 0 | Jul | 2022 | 0.0080505 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-07-27 08:58 | 2022-07-27 10:47 | 12 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN XMR Y SE REMPLAZO PERNO EN CAJA PRIMARIA Y EN CRUCETA | R22072700021 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2022-07-27 | 1308 | keep | 0 | Jul | 2022 | 0.00089087 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-27 09:08 | 2022-07-27 09:42 | 1210 | 0:34 | T | CONDUCTOR ARRIADO O CRUZADO | SE DESPEGO BAJANTE DE RISER DE CRUCETA Y SE CERRO POR CONTROL | B22072700063 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 34 | 2022-07-27 | 41140 | keep | 0 | Jul | 2022 | 0.02802 | 0.00082413 | Sustained | FALSE | FALSE | Not_TMED_Event | 1210
GUAYAMA | 2022-07-27 09:08 | 2022-07-27 11:50 | 65 | 2:42 | P | ANIMAL | 1 X 65 EN C/L CRUCE DE FASE PRIMARIA POR AVE | P22072700009 | New_Event | Animals | Include | Include | Wildlife | 162 | 2022-07-27 | 10530 | keep | 0 | Jul | 2022 | 0.0071719 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-07-27 09:15 | 2022-07-27 13:29 | 200 | 4:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO PARTIDO | A22072700023 | New_Event | Primary Wire Break | Include | Include | Equipment | 254 | 2022-07-27 | 50800 | keep | 0 | Jul | 2022 | 0.0346 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-07-27 09:16 | 2022-07-27 09:20 | 2178 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 3015-07 LLEVA EL 3103-05 SE CERRO POR SCADA | C22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-27 | 8712 | keep | 0 | Jul | 2022 | 0.0059337 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
AGUADILLA | 2022-07-27 09:23 | 2022-07-27 15:17 | 18 | 5:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA X 50KVA Y SE REEMPLAZARON BAJANTES SECUNDARIOS | A22072700024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 354 | 2022-07-27 | 6372 | keep | 0 | Jul | 2022 | 0.0043399 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-07-27 09:28 | 2022-07-27 09:29 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 1342 | keep | 0 | Jul | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2022-07-27 09:29 | 2022-07-27 12:29 | 80 | 3:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22072700042 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-07-27 | 14400 | keep | 0 | Jul | 2022 | 0.0098078 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-07-27 09:32 | 2022-07-27 14:01 | 10 | 4:29 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR SE REEMPLAZO SECUNDARIA A CAUSA DE IMPACTO POR CAMION | C22072700039 | New_Event | Damage From Public | Include | Include | Public | 269 | 2022-07-27 | 2690 | keep | 0 | Jul | 2022 | 0.0018321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-07-27 09:40 | 2022-07-27 13:32 | 1 | 3:52 | P | ANIMAL | 1 X 15 EN C/L CRUCE POR AVE | C22072700044 | New_Event | Animals | Include | Include | Wildlife | 232 | 2022-07-27 | 232 | keep | 0 | Jul | 2022 | 0.00015801 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-27 10:01 | 2022-07-27 10:32 | 1 | 0:31 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C22072700048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2022-07-27 | 31 | keep | 0 | Jul | 2022 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-07-27 10:04 | 2022-07-27 11:53 | 40 | 1:49 | P | NO SE REPORTO CAUSA | 1X25 DE RISER @ T-11 | R22072700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-07-27 | 4360 | keep | 0 | Jul | 2022 | 0.0029696 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-27 10:05 | 2022-07-27 21:04 | 12 | 10:59 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL A T-44 | S22072700026 | New_Event | UG Cable Fault | Include | Include | Equipment | 659 | 2022-07-27 | 7908 | keep | 0 | Jul | 2022 | 0.0053861 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-27 10:20 | 2022-07-27 12:30 | 12 | 2:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA TRABAJOS DE ENDEREZAR POSTE PRIMARIO | B22072700085 | New_Event | Primary Pole Failure | Include | Include | Equipment | 130 | 2022-07-27 | 1560 | keep | 0 | Jul | 2022 | 0.0010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-07-27 10:23 | 2022-07-27 12:00 | 12 | 1:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO 3 BARRAS EN PEDESTAL | C22072700052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 97 | 2022-07-27 | 1164 | keep | 0 | Jul | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-07-27 10:27 | 2022-07-27 12:38 | 37 | 2:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE CORTE DE LINE APARA REMPLAZO CAJA QUEMADA EN AZOTEA 2 X 40 EN CORTE DE LINEA Y 2 CAJAS QUEMADAS | S22072600130 | Additional_clients | Cutout Failure | Include | Include | Equipment | 131 | 2022-07-27 | 4847 | keep | 0 | Jul | 2022 | 0.0033013 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-27 10:42 | 2022-07-27 12:00 | 698 | 1:18 | P | PROBLEMA DEL CLIENTE | SE SECCIONALIZO ALIMENTADOR (AVERIA SUB. CUARTEL DE POLICIA Y VILLA PESQUERA) ENTRO 20% | B22072700039 | New_Event | Customer-Related Interruption | Include | Include | Public | 78 | 2022-07-27 | 54444 | keep | 0 | Jul | 2022 | 0.037082 | 0.0004754 | Sustained | FALSE | FALSE | Not_TMED_Event | 698
PONCE | 2022-07-27 10:55 | 2022-07-27 11:44 | 171 | 0:49 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV PONCE TC | P22072700033 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 49 | 2022-07-27 | 8379 | keep | 0 | Jul | 2022 | 0.0057069 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
PONCE | 2022-07-27 10:55 | 2022-07-27 11:44 | 120 | 0:49 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV PONCE TC | P22072700033 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 49 | 2022-07-27 | 5880 | keep | 0 | Jul | 2022 | 0.0040048 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-07-27 10:55 | 2022-07-27 11:44 | 2446 | 0:49 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV PONCE TC | P22072700033 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 49 | 2022-07-27 | 119854 | keep | 0 | Jul | 2022 | 0.081632 | 0.001666 | Sustained | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2022-07-27 10:55 | 2022-07-27 11:44 | 752 | 0:49 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV PONCE TC | P22072700033 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 49 | 2022-07-27 | 36848 | keep | 0 | Jul | 2022 | 0.025097 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
PONCE | 2022-07-27 10:55 | 2022-07-27 11:44 | 113 | 0:49 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV PONCE TC | P22072700033 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 49 | 2022-07-27 | 5537 | keep | 0 | Jul | 2022 | 0.0037712 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
PONCE | 2022-07-27 11:04 | 2022-07-27 11:07 | 562 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22072700054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-07-27 | 1686 | keep | 0 | Jul | 2022 | 0.0011483 | 0.00038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2022-07-27 11:04 | 2022-07-27 11:07 | 688 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22072700054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-07-27 | 2064 | keep | 0 | Jul | 2022 | 0.0014058 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2022-07-27 11:04 | 2022-07-27 11:07 | 658 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22072700054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-07-27 | 1974 | keep | 0 | Jul | 2022 | 0.0013445 | 0.00044816 | Momentary | FALSE | FALSE | Not_TMED_Event | 658
PONCE | 2022-07-27 11:04 | 2022-07-27 11:07 | 4009 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22072700054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-07-27 | 12027 | keep | 0 | Jul | 2022 | 0.0081915 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
PONCE | 2022-07-27 11:04 | 2022-07-27 11:07 | 234 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22072700054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-07-27 | 702 | keep | 0 | Jul | 2022 | 0.00047813 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2022-07-27 11:04 | 2022-07-27 11:07 | 2468 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 17900 | P22072700054 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-07-27 | 7404 | keep | 0 | Jul | 2022 | 0.0050428 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
CANOVANAS | 2022-07-27 11:13 | 2022-07-27 12:02 | 1 | 0:49 | P | NO SE REPORTO CAUSA | 3 X 20 EN C/L & 3 X 10 EN BANCO DE XMRS | R22072700037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-07-27 | 49 | keep | 0 | Jul | 2022 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-27 11:33 | 2022-07-27 13:45 | 20 | 2:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO CAJA | B22072700097 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2022-07-27 | 2640 | keep | 0 | Jul | 2022 | 0.0017981 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-27 11:35 | 2022-07-27 11:37 | 225 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SU CARGA POR 1303-05 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22072700000 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-07-27 | 450 | keep | 0 | Jul | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-07-27 11:35 | 2022-07-27 11:37 | 870 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO LLEVA 1303-04 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22072700000 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-07-27 | 1740 | keep | 0 | Jul | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-07-27 11:37 | 2022-07-27 11:52 | 261 | 0:15 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN EL SUELO PERTENECIENTE AL 1303-05 | S22072700068 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 15 | 2022-07-27 | 3915 | keep | 0 | Jul | 2022 | 0.0026665 | 0.00017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 261
SAN JUAN | 2022-07-27 11:52 | 2022-07-27 12:50 | 225 | 0:58 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE SECCIONALIZO ALAMBRE EN EL PISO SE ABRIO MACHETE Y SE CERRO INTERRUPTOR 100% POR 1303-05 | S22072700068 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 58 | 2022-07-27 | 13050 | keep | 0 | Jul | 2022 | 0.0088883 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-07-27 11:52 | 2022-07-27 12:50 | 870 | 0:58 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE SECCIONALIZO ALAMBRE EN EL PISO SE ABRIO MACHETE Y SE CERRO INTERRUPTOR 70% EN SERVICIO Y 100% EN SERVICIO 1303-04 | S22072700068 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 58 | 2022-07-27 | 50460 | keep | 0 | Jul | 2022 | 0.034368 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-27 11:52 | 2022-07-27 13:20 | 60 | 1:28 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22072700103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-07-27 | 5280 | keep | 0 | Jul | 2022 | 0.0035962 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-27 12:00 | 2022-07-27 12:32 | 698 | 0:32 | P | PROBLEMA DEL CLIENTE | SE SECCIONALIZO ALIMENTADOR (AVERIA SUB. CUARTEL DE POLICIA Y VILLA PESQUERA) ENTRO 20% ADICIONAL | B22072700039 | Partial_restoration | Customer-Related Interruption | Include | Include | Public | 32 | 2022-07-27 | 22336 | keep | 0 | Jul | 2022 | 0.015213 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-27 12:12 | 2022-07-27 13:56 | 30 | 1:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M22072700132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-07-27 | 3120 | keep | 0 | Jul | 2022 | 0.002125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-07-27 12:21 | 2022-07-27 12:53 | 10 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REMPLAZAR 25 PIES SECUNDARIA TRAS PATIO | S22072700041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2022-07-27 | 320 | keep | 0 | Jul | 2022 | 0.00021795 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-27 12:23 | 2022-07-27 14:35 | 30 | 2:12 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22072700106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-07-27 | 3960 | keep | 0 | Jul | 2022 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-27 12:27 | 2022-07-27 16:36 | 12 | 4:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | B22072700107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 249 | 2022-07-27 | 2988 | keep | 0 | Jul | 2022 | 0.0020351 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-27 12:32 | 2022-07-27 12:35 | 1746 | 0:03 | T | PROBLEMA DEL CLIENTE | SE SECCIONALIZO ALIMENTADOR (AVERIA SUB. CUARTEL DE POLICIA Y VILLA PESQUERA) SE DEJO FUERA PARA QUE REPAREN | B22072700039 | Additional_clients | Customer-Related Interruption | Include | Include | Public | 3 | 2022-07-27 | 5238 | keep | 0 | Jul | 2022 | 0.0035676 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-07-27 12:34 | 2022-07-27 13:14 | 20 | 0:40 | P | ARBOL SOBRE LINEA | ABRIO C/L Y RETIRO ARBOL SOBRE LINEA DE EMERGENCIA NO FUNDIO | C22070600121 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 40 | 2022-07-27 | 800 | keep | 0 | Jul | 2022 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-07-27 12:41 | 2022-07-27 13:42 | 40 | 1:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X40 EN C/L Y 1X30 EN OTRO C/L (POR LLUVIAS) | R22072700040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 61 | 2022-07-27 | 2440 | keep | 0 | Jul | 2022 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-27 12:50 | 2022-07-27 15:06 | 261 | 2:16 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR 1303-05 PARA LEVANTAR CONDUCTOR PRIMARIO | S22072700068 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 136 | 2022-07-27 | 35496 | keep | 0 | Jul | 2022 | 0.024176 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-07-27 12:50 | 2022-07-27 16:50 | 115 | 4:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO DE CAJA PRIMARIA 1 X 65 1 X 80 EN CORTE DE LINEA | P22072700064 | New_Event | Cutout Failure | Include | Include | Equipment | 240 | 2022-07-27 | 27600 | keep | 0 | Jul | 2022 | 0.018798 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CAGUAS | 2022-07-27 12:56 | 2022-07-28 07:51 | 25 | 18:55 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C22072700076 | New_Event | Animals | Include | Include | Wildlife | 1135 | 2022-07-27 | 28375 | keep | 0 | Jul | 2022 | 0.019326 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-07-27 12:59 | 2022-07-27 14:40 | 31 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA FUERTE BRISA | P22072700065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2022-07-27 | 3131 | keep | 0 | Jul | 2022 | 0.0021325 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2022-07-27 13:00 | 2022-07-27 15:08 | 1498 | 2:08 | T | DESGANCHE | SE REALIZO DESGANCHE DE PISO Y SE CERRO BKR POR CONTROL | B22072700109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-07-27 | 191744 | keep | 0 | Jul | 2022 | 0.1306 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
CANOVANAS | 2022-07-27 13:04 | 2022-07-27 15:28 | 3766 | 2:24 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PRIMARIO PARTIDO FRENTE A LA SUBESTACION MEDIANTE G.O.I. SJ-220727-50 - CARGA TRANSFERIDA AL 2306-03 (BKR SPARE) | R22072700042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 144 | 2022-07-27 | 542304 | keep | 0 | Jul | 2022 | 0.36936 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
BAYAMON | 2022-07-27 13:09 | 2022-07-27 15:14 | 50 | 2:05 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22072700121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-07-27 | 6250 | keep | 0 | Jul | 2022 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-27 13:10 | 2022-07-27 19:12 | 60 | 6:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22072700143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-07-27 | 21720 | keep | 0 | Jul | 2022 | 0.014793 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-07-27 13:18 | 2022-07-27 13:19 | 4027 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | B22072700000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-07-27 | 4027 | keep | 0 | Jul | 2022 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2022-07-27 13:19 | 2022-07-27 17:02 | 300 | 3:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REMPLAZO AISLADOR | B22072700141 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 223 | 2022-07-27 | 66900 | keep | 0 | Jul | 2022 | 0.045565 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-07-27 13:20 | 2022-07-27 14:52 | 5 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO BARRA EN PEDESTAL Y BAJANTE SECUNDARIO | C22072400244 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2022-07-27 | 460 | keep | 0 | Jul | 2022 | 0.0003133 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-07-27 13:23 | 2022-07-27 16:02 | 50 | 2:39 | P | TERMINACION SOTERRADA AVERIADA | 1X50 EN C/L, 1X25 EN OTRO C/L Y SE REMPLAZO TERMINACION EN RISER | R22072700082 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 159 | 2022-07-27 | 7950 | keep | 0 | Jul | 2022 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-07-27 13:23 | 2022-07-27 18:03 | 50 | 4:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22072700149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2022-07-27 | 14000 | keep | 0 | Jul | 2022 | 0.0095353 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-27 13:28 | 2022-07-27 16:30 | 38 | 3:02 | P | ANIMAL | 1 X 40 EN C/L IGUANA | B22072700145 | New_Event | Animals | Include | Include | Wildlife | 182 | 2022-07-27 | 6916 | keep | 0 | Jul | 2022 | 0.0047105 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
MAYAGÃœEZ | 2022-07-27 13:31 | 2022-07-27 17:30 | 60 | 3:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22072700151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-07-27 | 14340 | keep | 0 | Jul | 2022 | 0.0097669 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-07-27 13:38 | 2022-07-27 18:35 | 150 | 4:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22072700158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-07-27 | 44550 | keep | 0 | Jul | 2022 | 0.030343 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-07-27 14:00 | 2022-07-27 16:32 | 1 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | DESGANCHE SE RECONECTO RISER A CAJA PRIMARIA | B22072700210 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2022-07-27 | 152 | keep | 0 | Jul | 2022 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-27 14:02 | 2022-07-27 20:00 | 100 | 5:58 | P | MAL TIEMPO/RAYOS | 1 X 65 Y 1 X 80 EN CORTES DE LINEA DESCARGAS ELECTRICAS | M22072700176 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 358 | 2022-07-27 | 35800 | keep | 0 | Jul | 2022 | 0.024383 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-07-27 14:04 | 2022-07-27 15:03 | 650 | 0:59 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | A22072700051 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 59 | 2022-07-27 | 38350 | keep | 0 | Jul | 2022 | 0.02612 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
CAGUAS | 2022-07-27 14:06 | 2022-07-28 12:00 | 3 | 21:54 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 15KVA X 37.5KVA, CAJA PRIMARIA Y PARARRAYO. | C22072700086 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1314 | 2022-07-27 | 3942 | keep | 0 | Jul | 2022 | 0.0026849 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-07-27 14:07 | 2022-07-27 17:22 | 1497 | 3:15 | T | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO CARGA AL 7201-04 POR AUXILIAR DE LINEA QUEMADO TENIA 60 CLIENTES DEL 7201-04 | M22072700183 | New_Event | Switch Failure | Include | Include | Equipment | 195 | 2022-07-27 | 291915 | keep | 0 | Jul | 2022 | 0.19882 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
AGUADILLA | 2022-07-27 14:10 | 2022-07-27 19:30 | 600 | 5:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22072700181 | New_Event | Cutout Failure | Include | Include | Equipment | 320 | 2022-07-27 | 192000 | keep | 0 | Jul | 2022 | 0.13077 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
AGUADILLA | 2022-07-27 14:11 | 2022-07-27 22:10 | 80 | 7:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | M22072700184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 479 | 2022-07-27 | 38320 | keep | 0 | Jul | 2022 | 0.0261 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-07-27 14:18 | 2022-07-27 15:57 | 15 | 1:39 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | C22072700090 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 99 | 2022-07-27 | 1485 | keep | 0 | Jul | 2022 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-07-27 14:20 | 2022-07-27 18:38 | 25 | 4:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M22072700193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 258 | 2022-07-27 | 6450 | keep | 0 | Jul | 2022 | 0.0043931 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-07-27 14:27 | 2022-07-27 20:24 | 60 | 5:57 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L Y SE RETEZO LINDA PRIMARIA | C22072700091 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 357 | 2022-07-27 | 21420 | keep | 0 | Jul | 2022 | 0.014589 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-27 14:27 | 2022-07-27 14:28 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 2234 | keep | 0 | Jul | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
AGUADILLA | 2022-07-27 14:33 | 2022-07-27 21:56 | 60 | 7:23 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072700210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 443 | 2022-07-27 | 26580 | keep | 0 | Jul | 2022 | 0.018104 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-07-27 14:36 | 2022-07-27 16:27 | 5 | 1:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22072700057 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2022-07-27 | 555 | keep | 0 | Jul | 2022 | 0.00037801 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-07-27 14:38 | 2022-07-27 16:57 | 25 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L EVENTO TRANSFERIDO DE CAGUAS | C22072700093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-07-27 | 3475 | keep | 0 | Jul | 2022 | 0.0023668 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-07-27 14:45 | 2022-07-27 16:46 | 30 | 2:01 | P | DESGANCHE | 2 X 40 EN C/L Y DESGANCHE DE BAMBUA | B22072700203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-07-27 | 3630 | keep | 0 | Jul | 2022 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-07-27 14:46 | 2022-07-27 14:47 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 527 | keep | 0 | Jul | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
BARRANQUITAS | 2022-07-27 14:48 | 2022-07-27 17:58 | 40 | 3:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIR C/L MONOFASICO PARA ENDEREZAR POSTE A PUNTO DE CAERSE ENERGIZADO POR DISCO PARTIDO EMERGENCIA | C22072700099 | New_Event | Primary Pole Failure | Include | Include | Equipment | 190 | 2022-07-27 | 7600 | keep | 0 | Jul | 2022 | 0.0051763 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-27 14:49 | 2022-07-27 15:57 | 10 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES EN BAJANTE SECUNDARIO | S22072700117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2022-07-27 | 680 | keep | 0 | Jul | 2022 | 0.00046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-07-27 14:49 | 2022-07-27 19:18 | 20 | 4:29 | P | CAUSAS EXTERNAS | SE CERRO NEUTRAL Y LINEA PRIMARIA ABIERTA A CAUSA DE IMPACTO POR CAMION | C22072700102 | New_Event | Damage From Public | Include | Include | Public | 269 | 2022-07-27 | 5380 | keep | 0 | Jul | 2022 | 0.0036643 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-07-27 14:49 | 2022-07-27 16:04 | 80 | 1:15 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22072700100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-07-27 | 6000 | keep | 0 | Jul | 2022 | 0.0040866 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-07-27 14:58 | 2022-07-27 18:14 | 40 | 3:16 | P | ARBOL SOBRE LINEA | 2 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M22072700233 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 196 | 2022-07-27 | 7840 | keep | 0 | Jul | 2022 | 0.0053398 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-07-27 14:59 | 2022-07-27 15:00 | 2113 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | P22072700084 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-07-27 | 2113 | keep | 0 | Jul | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-07-27 15:00 | 2022-07-27 16:03 | 888 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PRIMARIO EN EL PISO | P22072700120 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 63 | 2022-07-27 | 55944 | keep | 0 | Jul | 2022 | 0.038103 | 0.00060481 | Sustained | FALSE | FALSE | Not_TMED_Event | 888
SAN JUAN | 2022-07-27 15:06 | 2022-07-27 15:11 | 225 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | S22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-07-27 | 1125 | keep | 0 | Jul | 2022 | 0.00076623 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-07-27 15:06 | 2022-07-27 15:11 | 870 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | S22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-07-27 | 4350 | keep | 0 | Jul | 2022 | 0.0029628 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-07-27 15:11 | 2022-07-27 15:47 | 261 | 0:36 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR 1303-05 PARA LEVANTAR CONDUCTOR PRIMARIO | S22072700068 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 36 | 2022-07-27 | 9396 | keep | 0 | Jul | 2022 | 0.0063996 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-07-27 15:16 | 2022-07-27 18:05 | 367 | 2:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22072700090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-07-27 | 62023 | keep | 0 | Jul | 2022 | 0.042244 | 0.00024996 | Sustained | FALSE | FALSE | Not_TMED_Event | 367
PONCE | 2022-07-27 15:30 | 2022-07-27 15:31 | 1717 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072700092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 1717 | keep | 0 | Jul | 2022 | 0.0011694 | 0.0011694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1717
SAN JUAN | 2022-07-27 15:36 | 2022-07-27 19:10 | 200 | 3:34 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN MACHETE | B22072700228 | New_Event | Primary Wire Break | Include | Include | Equipment | 214 | 2022-07-27 | 42800 | keep | 0 | Jul | 2022 | 0.029151 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-07-27 15:51 | 2022-07-27 15:52 | 5069 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072700096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 5069 | keep | 0 | Jul | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
YAUCO | 2022-07-27 15:56 | 2022-07-28 08:49 | 200 | 16:53 | P | ARBOL SOBRE LINEA | 1 X 80 EN C/L SE REALIZA DESGANCHE DE ARBOL SOBRE LINEA PRIMARIAS | P22072700101 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1013 | 2022-07-27 | 202600 | keep | 0 | Jul | 2022 | 0.13799 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-07-27 15:57 | 2022-07-27 15:58 | 5069 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072700102 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 5069 | keep | 0 | Jul | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
CANOVANAS | 2022-07-27 15:58 | 2022-07-27 17:32 | 40 | 1:34 | P | DESGANCHE | 1X50 EN C/L, 1X40 EN OTRO C/L - SE REALIZO DESGANCHE PRIMARIO | R22072700133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-07-27 | 3760 | keep | 0 | Jul | 2022 | 0.0025609 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-07-27 16:03 | 2022-07-27 16:43 | 2113 | 0:40 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR POR ALAMBRE EN EL PISO | P22072700106 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 40 | 2022-07-27 | 84520 | keep | 0 | Jul | 2022 | 0.057566 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-27 16:18 | 2022-07-27 19:35 | 10 | 3:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO PALMA | M22072700264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-07-27 | 1970 | keep | 0 | Jul | 2022 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-27 16:20 | 2022-07-27 16:21 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1710-02 QUE LLEVA LA CARGA DEL 1710-01 SE CERRO POR CONTROL | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 5809 | keep | 0 | Jul | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
SAN JUAN | 2022-07-27 16:29 | 2022-07-27 18:29 | 40 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22072700139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-07-27 | 4800 | keep | 0 | Jul | 2022 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-07-27 16:39 | 2022-07-27 19:38 | 40 | 2:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22072700067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-07-27 | 7160 | keep | 0 | Jul | 2022 | 0.0048766 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-07-27 16:43 | 2022-07-27 18:55 | 20 | 2:12 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/L DESGANCHE | C22072700123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-07-27 | 2640 | keep | 0 | Jul | 2022 | 0.0017981 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-07-27 16:43 | 2022-07-27 18:55 | 888 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PRIMARIO EN EL PISO | P22072700120 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 132 | 2022-07-27 | 117216 | keep | 0 | Jul | 2022 | 0.079835 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-27 16:51 | 2022-07-27 18:00 | 14 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO XMR Y SE REPARO SECUNDARIA | S22072700135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2022-07-27 | 966 | keep | 0 | Jul | 2022 | 0.00065794 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-07-27 16:53 | 2022-07-27 16:55 | 1026 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL 1647-08 | R22072700136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-27 | 2052 | keep | 0 | Jul | 2022 | 0.0013976 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2022-07-27 16:53 | 2022-07-27 16:55 | 1474 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA LA CARGA DEL 1646-02 | R22072700136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-27 | 2948 | keep | 0 | Jul | 2022 | 0.0020079 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
BARRANQUITAS | 2022-07-27 16:59 | 2022-07-27 18:10 | 8 | 1:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22072700128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-07-27 | 568 | keep | 0 | Jul | 2022 | 0.00038686 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-07-27 17:04 | 2022-07-27 17:22 | 937 | 0:18 | P | DESCONECTIVO DEFECTUOSO | LLEVA PARCIAL DE LA CARGA POR 7201-05 95% | M22072700183 | New_Event | Switch Failure | Include | Include | Equipment | 18 | 2022-07-27 | 16866 | keep | 0 | Jul | 2022 | 0.011487 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2022-07-27 17:09 | 2022-07-27 17:10 | 290 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22072700144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 290 | keep | 0 | Jul | 2022 | 0.00019752 | 0.00019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 290
MAYAGÃœEZ | 2022-07-27 17:09 | 2022-07-27 21:35 | 35 | 4:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | M22072700282 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 266 | 2022-07-27 | 9310 | keep | 0 | Jul | 2022 | 0.006341 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-07-27 17:09 | 2022-07-27 18:28 | 10 | 1:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22072700070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-07-27 | 790 | keep | 0 | Jul | 2022 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-27 17:10 | 2022-07-27 19:36 | 80 | 2:26 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22072700268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2022-07-27 | 11680 | keep | 0 | Jul | 2022 | 0.0079552 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-07-27 17:12 | 2022-07-27 18:27 | 2 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BARRAS SECUNDARIAS EN PM | A22072700071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2022-07-27 | 150 | keep | 0 | Jul | 2022 | 0.00010216 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-07-27 17:15 | 2022-07-27 18:31 | 12 | 1:16 | P | PARARRAYOS DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON PARARRAYOS EN XMR | S22072700145 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 76 | 2022-07-27 | 912 | keep | 0 | Jul | 2022 | 0.00062116 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-07-27 17:39 | 2022-07-27 21:39 | 25 | 4:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072700078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 240 | 2022-07-27 | 6000 | keep | 0 | Jul | 2022 | 0.0040866 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-07-27 17:45 | 2022-07-27 19:00 | 5 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO NEUTRAL SECUNDARIO | S22072700148 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2022-07-27 | 375 | keep | 0 | Jul | 2022 | 0.00025541 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-07-27 17:53 | 2022-07-28 14:27 | 8 | 20:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA AVERIADA | P22072700139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1234 | 2022-07-27 | 9872 | keep | 0 | Jul | 2022 | 0.0067238 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-07-27 18:04 | 2022-07-28 14:20 | 20 | 20:16 | P | ARBOL SOBRE LINEA | 2 X 25 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22072700080 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1216 | 2022-07-27 | 24320 | keep | 0 | Jul | 2022 | 0.016564 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-07-27 18:07 | 2022-07-27 20:25 | 50 | 2:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22072700081 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 138 | 2022-07-27 | 6900 | keep | 0 | Jul | 2022 | 0.0046996 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-27 18:09 | 2022-07-27 21:38 | 14 | 3:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONECTORES EN SECUNDARIA | S22072700151 | New_Event | Secondary Wire Break | Include | Include | Equipment | 209 | 2022-07-27 | 2926 | keep | 0 | Jul | 2022 | 0.0019929 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-07-27 18:39 | 2022-07-27 18:40 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 95% 1717-02 | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 5961 | keep | 0 | Jul | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-07-27 18:39 | 2022-07-27 18:40 | 865 | 0:01 | P | NO SE REPORTO CAUSA | FEEDER 1713-05 RECERRO Y LLEVA 95% DEL 1717-02 | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 865 | keep | 0 | Jul | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
ARECIBO | 2022-07-27 18:48 | 2022-07-27 23:00 | 150 | 4:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | A22072700085 | New_Event | Primary Wire Break | Include | Include | Equipment | 252 | 2022-07-27 | 37800 | keep | 0 | Jul | 2022 | 0.025745 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-07-27 18:50 | 2022-07-27 20:24 | 30 | 1:34 | P | ARBOL SOBRE LINEA | 1X50 EN C/L SE RETIRO ARBOL DE PRIMARIA | R22072700140 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 94 | 2022-07-27 | 2820 | keep | 0 | Jul | 2022 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-07-27 18:51 | 2022-07-27 22:10 | 100 | 3:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22072700090 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2022-07-27 | 19900 | keep | 0 | Jul | 2022 | 0.013554 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-07-27 18:58 | 2022-07-27 19:00 | 2113 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR POR ALAMBRE EN EL PISO | P22072700170 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 2 | 2022-07-27 | 4226 | keep | 0 | Jul | 2022 | 0.0028783 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-27 19:10 | 2022-07-27 19:11 | 73 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22072700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 73 | keep | 0 | Jul | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
PONCE | 2022-07-27 19:15 | 2022-07-27 21:56 | 179 | 2:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22072700178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-07-27 | 28819 | keep | 0 | Jul | 2022 | 0.019628 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
SAN JUAN | 2022-07-27 19:19 | 2022-07-28 10:26 | 10 | 15:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE DIERON CONECTORES EN BAJANTE SECUNDARIO | S22072700154 | New_Event | Secondary Wire Break | Include | Include | Equipment | 907 | 2022-07-27 | 9070 | keep | 0 | Jul | 2022 | 0.0061775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-27 19:22 | 2022-07-27 19:23 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R22072700141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 4188 | keep | 0 | Jul | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
AGUADILLA | 2022-07-27 19:46 | 2022-07-28 01:37 | 8 | 5:51 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR | M22072700310 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 351 | 2022-07-27 | 2808 | keep | 0 | Jul | 2022 | 0.0019125 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-07-27 19:50 | 2022-07-27 20:40 | 888 | 0:50 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | P22072700172 | New_Event | Primary Wire Break | Include | Include | Equipment | 50 | 2022-07-27 | 44400 | keep | 0 | Jul | 2022 | 0.030241 | 0.00060481 | Sustained | FALSE | FALSE | Not_TMED_Event | 888
PONCE | 2022-07-27 20:09 | 2022-07-27 22:54 | 168 | 2:45 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22072700195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-07-27 | 27720 | keep | 0 | Jul | 2022 | 0.01888 | 0.00011442 | Sustained | FALSE | FALSE | Not_TMED_Event | 168
HUMACAO | 2022-07-27 20:15 | 2022-07-28 14:46 | 15 | 18:31 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | C22072700143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1111 | 2022-07-27 | 16665 | keep | 0 | Jul | 2022 | 0.01135 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-07-27 20:18 | 2022-07-27 20:25 | 4 | 0:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22072700156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-07-27 | 28 | keep | 0 | Jul | 2022 | 1.9071e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-07-27 20:21 | 2022-07-28 15:20 | 20 | 18:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22072700100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1139 | 2022-07-27 | 22780 | keep | 0 | Jul | 2022 | 0.015515 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-07-27 20:22 | 2022-07-28 00:56 | 40 | 4:34 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO | R22072700145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2022-07-27 | 10960 | keep | 0 | Jul | 2022 | 0.0074648 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-27 20:48 | 2022-07-27 22:37 | 30 | 1:49 | P | NO SE REPORTO CAUSA | 2 X 40 EN C/L | B22072700290 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-07-27 | 3270 | keep | 0 | Jul | 2022 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-27 20:53 | 2022-07-27 21:29 | 4188 | 0:36 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO EL ALIMENTADOR EN SERVICIO 35% DEL ALIMENTADOR | R22072700150 | New_Event | Primary Wire Break | Include | Include | Equipment | 36 | 2022-07-27 | 150768 | keep | 0 | Jul | 2022 | 0.10269 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
HUMACAO | 2022-07-27 21:24 | 2022-07-28 13:47 | 14 | 16:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | C22072700148 | New_Event | Secondary Wire Break | Include | Include | Equipment | 983 | 2022-07-27 | 13762 | keep | 0 | Jul | 2022 | 0.0093732 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-07-27 21:29 | 2022-07-27 21:48 | 2722 | 0:19 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES CONDUCTOR EN EL SUELO 40% DEL ALIMENTADOR EN SERVICIO | R22072700150 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 19 | 2022-07-27 | 51718 | keep | 0 | Jul | 2022 | 0.035225 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-07-27 21:35 | 2022-07-28 10:09 | 200 | 12:34 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L Y SE REPARO PUENTE DE LINEA A CAJA | C22072700150 | New_Event | Primary Wire Break | Include | Include | Equipment | 754 | 2022-07-27 | 150800 | keep | 0 | Jul | 2022 | 0.10271 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-07-27 21:38 | 2022-07-28 12:24 | 5 | 14:46 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A22072700112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 886 | 2022-07-27 | 4430 | keep | 0 | Jul | 2022 | 0.0030173 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-07-27 21:48 | 2022-07-27 22:17 | 2513 | 0:29 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES EN SERVICIO 55% DEL ALIMENTADOR | R22072700150 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 29 | 2022-07-27 | 72877 | keep | 0 | Jul | 2022 | 0.049636 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-27 21:56 | 2022-07-28 14:08 | 1 | 16:12 | P | DESGANCHE | 2 X 5 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE TRANSFORMADOR | M22072700210 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 972 | 2022-07-27 | 972 | keep | 0 | Jul | 2022 | 0.00066202 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-07-27 21:59 | 2022-07-28 08:41 | 1 | 10:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22072700293 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 642 | 2022-07-27 | 642 | keep | 0 | Jul | 2022 | 0.00043726 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-07-27 22:15 | 2022-07-28 09:37 | 10 | 11:22 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y DESGANCHE SECUNDARIO | C22072700156 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 682 | 2022-07-27 | 6820 | keep | 0 | Jul | 2022 | 0.0046451 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-27 22:17 | 2022-07-27 23:06 | 1885 | 0:49 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y CERRO MACHETES EN SERVICIO 100% DEL ALIMENTADOR | R22072700150 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 49 | 2022-07-27 | 92365 | keep | 0 | Jul | 2022 | 0.062909 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-07-27 23:00 | 2022-07-28 08:00 | 182 | 9:00 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 Y 1 X 80 EN C/L SE LEVANTO LINEA PRIMARIA | B22072700298 | New_Event | Primary Wire Break | Include | Include | Equipment | 540 | 2022-07-27 | 98280 | keep | 0 | Jul | 2022 | 0.066938 | 0.00012396 | Sustained | FALSE | FALSE | Not_TMED_Event | 182
BAYAMON | 2022-07-27 23:12 | 2022-07-28 11:20 | 50 | 12:08 | P | DESGANCHE | 2 X 40 EN C/L SE DESGANCHO | B22072700304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 728 | 2022-07-27 | 36400 | keep | 0 | Jul | 2022 | 0.024792 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-07-27 23:49 | 2022-07-27 23:50 | 500 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22072700230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-27 | 500 | keep | 0 | Jul | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-07-28 00:52 | 2022-07-28 03:01 | 1085 | 2:09 | T | DESGANCHE | SE CERRO INTERRUPTOR ABRIENDO MACHETES PARA DAR SERVICIO POR PARTES AL NO ENCONTRAR CAUSA. 60% EN SERVICIO | S22072800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-07-28 | 139965 | keep | 0 | Jul | 2022 | 0.09533 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
CANOVANAS | 2022-07-28 01:26 | 2022-07-28 09:00 | 38 | 7:34 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN C/L SE ABRIO PUENTE POR ALAMBRE EN EL SUELO PARA PERSONAL DE CONT REPARE ALAMBRE EN EL SUELO | R22072800002 | New_Event | Primary Wire Break | Include | Include | Equipment | 454 | 2022-07-28 | 17252 | keep | 0 | Jul | 2022 | 0.01175 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2022-07-28 01:27 | 2022-07-28 09:24 | 1 | 7:57 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22072800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 477 | 2022-07-28 | 477 | keep | 0 | Jul | 2022 | 0.00032488 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-07-28 02:50 | 2022-07-28 02:51 | 1835 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 1835 | keep | 0 | Jul | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
SAN JUAN | 2022-07-28 03:01 | 2022-07-28 05:01 | 434 | 2:00 | P | DESGANCHE | ALIMENTADOR SECCIONALIZADO PARA LOCALIZAR AVERIA | S22072800001 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-07-28 | 52080 | keep | 0 | Jul | 2022 | 0.035471 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-28 03:07 | 2022-07-28 12:01 | 29 | 8:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22072800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 534 | 2022-07-28 | 15486 | keep | 0 | Jul | 2022 | 0.010547 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2022-07-28 03:59 | 2022-07-28 05:30 | 4009 | 1:31 | T | DESGANCHE | DISPARO INTERRUPTOR SE SECCIONALIZA ALIMENTADOR Y SE COLOCA EN SERVICIO | P22072800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-07-28 | 364819 | keep | 0 | Jul | 2022 | 0.24848 | 0.0027305 | Sustained | FALSE | FALSE | Not_TMED_Event | 4009
VEGA BAJA | 2022-07-28 04:52 | 2022-07-28 08:45 | 31 | 3:53 | P | DESGANCHE | 1 X 50 EN C/L | B22072800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-07-28 | 7223 | keep | 0 | Jul | 2022 | 0.0049196 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2022-07-28 05:01 | 2022-07-28 05:02 | 1085 | 0:01 | T | DESGANCHE | DISPARO DE ALIMENTADOR AL TRATAR DE CERRAR MACHETES PARA NORMALIZAR CARGAS. NO SE ENCONTRO CAUSA | S22072800001 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-28 | 1085 | keep | 0 | Jul | 2022 | 0.00073899 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-28 05:02 | 2022-07-28 05:09 | 434 | 0:07 | P | DESGANCHE | TRANSFIRIO EL 40% AL 1519-01 (QUE ESTA POR 1519-05) CERRANDO N/O, SE DA SERVICIO/LUEGO SE NORMALIZA CARGA. HABIA PASADO ANTES/SE DIO SERVICIO DE ESA FORMA DESGANCHE MASIVO - SJ-220728-01 SE GENERO HC-73989-1 POR PROTECCION (G/R NO CERRO POR SCADA) | S22072800001 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-07-28 | 3038 | keep | 0 | Jul | 2022 | 0.0020692 | 0.0002956 | Sustained | FALSE | FALSE | Not_TMED_Event | 434
PONCE | 2022-07-28 05:30 | 2022-07-28 06:30 | 228 | 1:00 | P | DESGANCHE | 2 X 200 EN C/L SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22072800012 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-07-28 | 13680 | keep | 0 | Jul | 2022 | 0.0093174 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-28 05:46 | 2022-07-28 06:39 | 45 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | 1X40 EN C/L - TRASPATIO - SE LEVANTO/ANCLO 4KV (INICIALMENTE ERA PASANTE) | S22072800066 | New_Event | Primary Wire Break | Include | Include | Equipment | 53 | 2022-07-28 | 2385 | keep | 0 | Jul | 2022 | 0.0016244 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-07-28 05:59 | 2022-07-28 06:00 | 4641 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR AVE CRUZO LINEAS | M22072800006 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-07-28 | 4641 | keep | 0 | Jul | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-07-28 06:00 | 2022-07-28 16:32 | 60 | 10:32 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22072800115 | 1st_after_momentary | Animals | Include | Include | Wildlife | 632 | 2022-07-28 | 37920 | keep | 0 | Jul | 2022 | 0.025827 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-28 06:04 | 2022-07-28 11:17 | 45 | 5:13 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S22072800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-07-28 | 14085 | keep | 0 | Jul | 2022 | 0.0095932 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-07-28 06:04 | 2022-07-28 10:40 | 15 | 4:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22072800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-07-28 | 4140 | keep | 0 | Jul | 2022 | 0.0028197 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-07-28 06:08 | 2022-07-28 09:40 | 20 | 3:32 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-07-28 | 4240 | keep | 0 | Jul | 2022 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-07-28 06:19 | 2022-07-28 12:09 | 20 | 5:50 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS | A22072800003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-07-28 | 7000 | keep | 0 | Jul | 2022 | 0.0047677 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-28 06:41 | 2022-07-28 19:05 | 60 | 12:24 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO - TRASPATIO | S22072700038 | New_Event | Primary Pole Failure | Include | Include | Equipment | 744 | 2022-07-28 | 44640 | keep | 0 | Jul | 2022 | 0.030404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-07-28 06:54 | 2022-07-28 11:02 | 60 | 4:08 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | C22072800010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-07-28 | 14880 | keep | 0 | Jul | 2022 | 0.010135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-07-28 07:17 | 2022-07-28 09:45 | 30 | 2:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-07-28 | 4440 | keep | 0 | Jul | 2022 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-07-28 07:30 | 2022-07-28 15:59 | 9 | 8:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN XMR, SE REMPLAZO CAJA PRIMARIA | S22072800069 | New_Event | Cutout Failure | Include | Include | Equipment | 509 | 2022-07-28 | 4581 | keep | 0 | Jul | 2022 | 0.0031201 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2022-07-28 08:04 | 2022-07-28 13:28 | 8 | 5:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO PUENTES | M22072800018 | New_Event | Primary Wire Break | Include | Include | Equipment | 324 | 2022-07-28 | 2592 | keep | 0 | Jul | 2022 | 0.0017654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-07-28 08:05 | 2022-07-28 12:20 | 3 | 4:15 | P | PROBLEMA DEL CLIENTE | CON SWITCH FORM BY- 220728-01 SE DESCONECTO SERVICIO A CUARTEL DE POLICIA MUNICIPAL | B22072800017 | New_Event | Customer-Related Interruption | Include | Include | Public | 255 | 2022-07-28 | 765 | keep | 0 | Jul | 2022 | 0.00052104 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-07-28 08:19 | 2022-07-29 17:13 | 13 | 32:54 | P | CABLE SOTERRADO AVERIADO | SE CONSTUYO AEREO PROVISIONAL (DE OTRO EXISTENTE) @ T-55 | S22072800073 | New_Event | UG Cable Fault | Include | Include | Equipment | 1974 | 2022-07-28 | 25662 | keep | 0 | Jul | 2022 | 0.017478 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2022-07-28 08:19 | 2022-07-28 13:19 | 8 | 5:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN RISER Y 2 X 50 EN C/L Y SE ELIMINO CAJA PRIMARIAS Y PARRARAYOS ABANDONADOS | C22072800022 | New_Event | Cutout Failure | Include | Include | Equipment | 300 | 2022-07-28 | 2400 | keep | 0 | Jul | 2022 | 0.0016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-07-28 08:25 | 2022-07-28 12:20 | 1 | 3:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTOR EN BAJANTE SECUNDARIO | P22072800064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 235 | 2022-07-28 | 235 | keep | 0 | Jul | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-28 08:30 | 2022-07-28 12:45 | 453 | 4:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | B22072800022 | New_Event | Primary Pole Failure | Include | Include | Equipment | 255 | 2022-07-28 | 115515 | keep | 0 | Jul | 2022 | 0.078677 | 0.00030854 | Sustained | FALSE | FALSE | Not_TMED_Event | 453
SAN JUAN | 2022-07-28 08:31 | 2022-07-28 10:51 | 4 | 2:20 | P | PROBLEMA DEL CLIENTE | SE DESENERGIZO CAJA SECA POR DESCONECTE DE CLIENTE PARA QUE REPARE SU SUBESTACION PRIVADA G.O.I. SJ 220728-02 | R22072800025 | New_Event | Customer-Related Interruption | Include | Include | Public | 140 | 2022-07-28 | 560 | keep | 0 | Jul | 2022 | 0.00038141 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-07-28 08:42 | 2022-07-28 10:24 | 25 | 1:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZAR 2 CAJA PRIMARIA | C22072800024 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-07-28 | 2550 | keep | 0 | Jul | 2022 | 0.0017368 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-07-28 08:53 | 2022-07-28 17:35 | 15 | 8:42 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE XMR 37.5KVA X 37.5KVA | C22072800027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 522 | 2022-07-28 | 7830 | keep | 0 | Jul | 2022 | 0.005333 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-07-28 09:00 | 2022-07-28 19:26 | 4 | 10:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE Y XMR Y LINEAS DEL SUELO | R22072800002 | New_Event | Primary Pole Failure | Include | Include | Equipment | 626 | 2022-07-28 | 2504 | keep | 0 | Jul | 2022 | 0.0017055 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-07-28 09:10 | 2022-07-28 12:00 | 1 | 2:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA @ CAJA EN XMR | S22072800080 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2022-07-28 | 170 | keep | 0 | Jul | 2022 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-28 09:10 | 2022-07-28 16:33 | 3 | 7:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22072800031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 443 | 2022-07-28 | 1329 | keep | 0 | Jul | 2022 | 0.00090518 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-07-28 09:16 | 2022-07-28 09:19 | 342 | 0:03 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - 85% DE SU CARGA TRANSFERIDA AL 1620-03 | S22072800083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-28 | 1026 | keep | 0 | Jul | 2022 | 0.0006988 | 0.00023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 342
SAN JUAN | 2022-07-28 09:16 | 2022-07-28 09:19 | 36 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1620-03 | S22072800083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-28 | 108 | keep | 0 | Jul | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-07-28 09:16 | 2022-07-28 09:19 | 1073 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1620-01 LLEVA 85% DEL 1336-10 | S22072800083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-28 | 3219 | keep | 0 | Jul | 2022 | 0.0021924 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2022-07-28 09:21 | 2022-07-28 11:48 | 50 | 2:27 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | S22072800083 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-07-28 | 7350 | keep | 0 | Jul | 2022 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-07-28 09:24 | 2022-07-28 12:40 | 50 | 3:16 | P | CAUSAS EXTERNAS | 2 X 30 EN C/L EXCAVADORA TUMBO BAMBUA SOBRE LINEA | C22072800034 | New_Event | Damage From Public | Include | Include | Public | 196 | 2022-07-28 | 9800 | keep | 0 | Jul | 2022 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-07-28 09:27 | 2022-07-28 09:28 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 4006-04 CON CARGA 4003-03 | P22072800073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 1945 | keep | 0 | Jul | 2022 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
GUAYAMA | 2022-07-28 09:27 | 2022-07-28 09:28 | 215 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO TIENE LA CARGA DE L 4003-03 | P22072800073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 215 | keep | 0 | Jul | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-07-28 09:41 | 2022-07-28 12:40 | 20 | 2:59 | P | DESGANCHE | 1 X 100 1 X 80 1 X 50 SE DESGANCHO | B22072800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-07-28 | 3580 | keep | 0 | Jul | 2022 | 0.0024383 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-07-28 09:42 | 2022-07-28 14:40 | 3 | 4:58 | P | DESGANCHE | 1X80 EN C/L | S22072800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-07-28 | 894 | keep | 0 | Jul | 2022 | 0.0006089 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-07-28 09:54 | 2022-07-28 15:50 | 7 | 5:56 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22072800034 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 356 | 2022-07-28 | 2492 | keep | 0 | Jul | 2022 | 0.0016973 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-07-28 09:58 | 2022-07-28 14:45 | 6 | 4:47 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M22072800035 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 287 | 2022-07-28 | 1722 | keep | 0 | Jul | 2022 | 0.0011728 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-07-28 10:00 | 2022-07-28 10:04 | 271 | 0:04 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S22072800096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-28 | 1084 | keep | 0 | Jul | 2022 | 0.00073831 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2022-07-28 10:00 | 2022-07-28 16:05 | 15 | 6:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO 600 PIES LINEA SECUNDARIA | B22072800037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 365 | 2022-07-28 | 5475 | keep | 0 | Jul | 2022 | 0.003729 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-07-28 10:04 | 2022-07-28 10:08 | 2891 | 0:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE BREAKER SE CERRO POR CONTROL | R22072800000 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2022-07-28 | 11564 | keep | 0 | Jul | 2022 | 0.0078762 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
CANOVANAS | 2022-07-28 10:08 | 2022-07-28 17:19 | 1 | 7:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 40 EN C/L SE REMPLAZARON 2 CAJAS PRIMARIAS | R22072800037 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 431 | 2022-07-28 | 431 | keep | 0 | Jul | 2022 | 0.00029355 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-07-28 10:10 | 2022-07-28 14:53 | 15 | 4:43 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA RELOCALIZAR LINEA SECUNDARIA | B22072800039 | New_Event |  |  |  |  | 283 | 2022-07-28 | 4245 | keep | 0 | Jul | 2022 | 0.0028913 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-07-28 10:13 | 2022-07-28 13:26 | 1 | 3:13 | P | NO SE REPORTO CAUSA | 1 SMU20 X 100 EN SU-8 Y 1 X 30 EN RISER | C22072800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2022-07-28 | 193 | keep | 0 | Jul | 2022 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-07-28 10:22 | 2022-07-28 12:15 | 100 | 1:53 | P | DESGANCHE | 1 X 100 EN C/L SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22072800081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-07-28 | 11300 | keep | 0 | Jul | 2022 | 0.0076964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-28 10:47 | 2022-07-28 17:23 | 30 | 6:36 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO (RADIAL) | S22072800104 | New_Event | Primary Pole Failure | Include | Include | Equipment | 396 | 2022-07-28 | 11880 | keep | 0 | Jul | 2022 | 0.0080914 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-07-28 10:52 | 2022-07-28 14:56 | 1 | 4:04 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A22072800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2022-07-28 | 244 | keep | 0 | Jul | 2022 | 0.00016619 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-28 10:53 | 2022-07-28 10:54 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 4431 | keep | 0 | Jul | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
SAN JUAN | 2022-07-28 11:00 | 2022-07-28 19:00 | 14 | 8:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO DOS POSTES DE 35' (RADIAL) | S22072800098 | New_Event | Primary Pole Failure | Include | Include | Equipment | 480 | 2022-07-28 | 6720 | keep | 0 | Jul | 2022 | 0.004577 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-07-28 11:00 | 2022-07-28 12:24 | 8 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22072800025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2022-07-28 | 672 | keep | 0 | Jul | 2022 | 0.0004577 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-07-28 11:00 | 2022-07-28 12:00 | 1 | 1:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22072800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-07-28 | 60 | keep | 0 | Jul | 2022 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-28 11:03 | 2022-07-28 14:14 | 4 | 3:11 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO Y DESGANCHE SECUNDARIO | C22072800052 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 191 | 2022-07-28 | 764 | keep | 0 | Jul | 2022 | 0.00052036 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-07-28 11:29 | 2022-07-28 12:04 | 10 | 0:35 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | P22072800079 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 35 | 2022-07-28 | 350 | keep | 0 | Jul | 2022 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-07-28 11:33 | 2022-07-28 13:00 | 1 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA TRIFASICA NO SE REPORTO CAUSA | P22072800092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-07-28 | 87 | keep | 0 | Jul | 2022 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-28 11:37 | 2022-07-28 14:19 | 60 | 2:42 | P | DESGANCHE | 1X40 EN C/L - DESGANCHE PRIMARIO | S22072800112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-07-28 | 9720 | keep | 0 | Jul | 2022 | 0.0066202 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-07-28 12:07 | 2022-07-29 19:40 | 100 | 31:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1893 | 2022-07-28 | 189300 | keep | 0 | Jul | 2022 | 0.12893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-28 12:08 | 2022-07-28 12:09 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1909-08 Y LLEVA LA CARGA DEL 1907-05 | S22072800116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 2435 | keep | 0 | Jul | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-28 12:08 | 2022-07-28 12:09 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1907-05 | S22072800116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 2956 | keep | 0 | Jul | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-07-28 12:09 | 2022-07-28 14:00 | 60 | 1:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22072800118 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-07-28 | 6660 | keep | 0 | Jul | 2022 | 0.0045361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-07-28 12:12 | 2022-07-28 14:25 | 114 | 2:13 | P | ANIMAL | 1 X 65 EN C/L SE INSTALO RIGIDO 15KV SE RETIRO CHANGO | R22072800030 | New_Event | Animals | Include | Include | Wildlife | 133 | 2022-07-28 | 15162 | keep | 0 | Jul | 2022 | 0.010327 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
CAGUAS | 2022-07-28 12:28 | 2022-07-28 15:07 | 150 | 2:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L Y 1 X 80 EN C/L | C22072800068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-07-28 | 23850 | keep | 0 | Jul | 2022 | 0.016244 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-07-28 12:29 | 2022-07-28 17:50 | 50 | 5:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22072800096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-07-28 | 16050 | keep | 0 | Jul | 2022 | 0.010932 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-07-28 12:34 | 2022-07-28 21:24 | 200 | 8:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M22072800060 | New_Event | Primary Pole Failure | Include | Include | Equipment | 530 | 2022-07-28 | 106000 | keep | 0 | Jul | 2022 | 0.072196 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-07-28 12:38 | 2022-07-28 17:00 | 40 | 4:22 | P | CAUSAS EXTERNAS | 1 X 40 Y 1 X 50 EN C/L CLIENTE CORTANDO ARBOL | C22072800077 | New_Event | Damage From Public | Include | Include | Public | 262 | 2022-07-28 | 10480 | keep | 0 | Jul | 2022 | 0.0071379 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-07-28 12:40 | 2022-07-28 12:41 | 4027 | 0:01 | T | DESGANCHE | RECERRO | B22072800053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-28 | 4027 | keep | 0 | Jul | 2022 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2022-07-28 12:41 | 2022-07-28 13:00 | 20 | 0:19 | P | DESGANCHE | 1 X 100 1 X 80 1 X 50 SE DESGANCHO | B22072800038 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 19 | 2022-07-28 | 380 | keep | 0 | Jul | 2022 | 0.00025882 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-07-28 12:53 | 2022-07-28 14:54 | 2530 | 2:01 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEAS SE CERRO INTERRUPTOR | M22072800064 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 121 | 2022-07-28 | 306130 | keep | 0 | Jul | 2022 | 0.2085 | 0.0017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 2530
VEGA BAJA | 2022-07-28 12:55 | 2022-07-28 14:27 | 30 | 1:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22072800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2022-07-28 | 2760 | keep | 0 | Jul | 2022 | 0.0018798 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-28 12:56 | 2022-07-28 15:00 | 80 | 2:04 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | S22072800125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-07-28 | 9920 | keep | 0 | Jul | 2022 | 0.0067565 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-07-28 13:05 | 2022-07-28 13:10 | 934 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22072800050 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-07-28 | 4670 | keep | 0 | Jul | 2022 | 0.0031807 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-07-28 13:05 | 2022-07-28 13:10 | 4 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22072800050 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-07-28 | 20 | keep | 0 | Jul | 2022 | 1.3622e-05 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-07-28 13:05 | 2022-07-28 13:10 | 1479 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22072800050 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-07-28 | 7395 | keep | 0 | Jul | 2022 | 0.0050367 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-07-28 13:05 | 2022-07-28 13:10 | 1841 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22072800050 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-07-28 | 9205 | keep | 0 | Jul | 2022 | 0.0062695 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-07-28 13:05 | 2022-07-28 13:10 | 1950 | 0:05 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22072800050 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-07-28 | 9750 | keep | 0 | Jul | 2022 | 0.0066407 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
BARRANQUITAS | 2022-07-28 13:16 | 2022-07-29 12:23 | 1 | 23:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | C22072800090 | New_Event | Primary Wire Break | Include | Include | Equipment | 1387 | 2022-07-28 | 1387 | keep | 0 | Jul | 2022 | 0.00094468 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-28 13:23 | 2022-07-28 14:32 | 40 | 1:09 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S22072800134 | New_Event | Primary Wire Break | Include | Include | Equipment | 69 | 2022-07-28 | 2760 | keep | 0 | Jul | 2022 | 0.0018798 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-07-28 13:36 | 2022-07-28 18:31 | 10 | 4:55 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C22072800098 | New_Event | Animals | Include | Include | Wildlife | 295 | 2022-07-28 | 2950 | keep | 0 | Jul | 2022 | 0.0020092 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-07-28 13:55 | 2022-07-29 15:16 | 50 | 25:21 | P | DESGANCHE | 1 X 50 EN C/L Y SE REALIZO DESGANCHE PRIMARIO | C22072800097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1521 | 2022-07-28 | 76050 | keep | 0 | Jul | 2022 | 0.051797 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-07-28 14:01 | 2022-07-28 18:25 | 50 | 4:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22072800081 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 264 | 2022-07-28 | 13200 | keep | 0 | Jul | 2022 | 0.0089905 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-07-28 14:01 | 2022-07-28 15:28 | 4 | 1:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR LA MISMA CAPACIDAD | A22072800054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 87 | 2022-07-28 | 348 | keep | 0 | Jul | 2022 | 0.00023702 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-07-28 14:06 | 2022-07-29 11:58 | 10 | 21:52 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO VIVO/NEUTRAL EN BAJANTE SECUNDARIO | S22072800147 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1312 | 2022-07-28 | 13120 | keep | 0 | Jul | 2022 | 0.008936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-07-28 14:07 | 2022-07-28 14:08 | 1428 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072800089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 1428 | keep | 0 | Jul | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
AGUADILLA | 2022-07-28 14:09 | 2022-07-28 17:30 | 15 | 3:21 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA | M22072800090 | New_Event | Primary Wire Break | Include | Include | Equipment | 201 | 2022-07-28 | 3015 | keep | 0 | Jul | 2022 | 0.0020535 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-07-28 14:11 | 2022-07-28 14:12 | 1185 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 1185 | keep | 0 | Jul | 2022 | 0.0008071 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
CAGUAS | 2022-07-28 14:12 | 2022-07-28 16:19 | 8 | 2:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22072800106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2022-07-28 | 1016 | keep | 0 | Jul | 2022 | 0.00069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-07-28 14:12 | 2022-07-28 17:55 | 100 | 3:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22072800105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-07-28 | 22300 | keep | 0 | Jul | 2022 | 0.015188 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-28 14:14 | 2022-07-28 18:57 | 60 | 4:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L Y SE REMPLAZO CAJA PRIMARIA | S22072800150 | New_Event | Cutout Failure | Include | Include | Equipment | 283 | 2022-07-28 | 16980 | keep | 0 | Jul | 2022 | 0.011565 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-28 14:23 | 2022-07-28 17:37 | 12 | 3:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE FIJO CAJA PRIMARIA QUE ESTABA SOBRE LINEA SECUNDARIA Y SE REEMPLAZO PORTA FUSIBLE | C22072800110 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2022-07-28 | 2328 | keep | 0 | Jul | 2022 | 0.0015856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-28 14:32 | 2022-07-28 15:02 | 57 | 0:30 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR CONTROL | S22072800000 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 30 | 2022-07-28 | 1710 | keep | 0 | Jul | 2022 | 0.0011647 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-07-28 14:32 | 2022-07-28 14:33 | 2039 | 0:01 | T | DESGANCHE | RECIERRE POR DESGANCHE | P22072800104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-28 | 2039 | keep | 0 | Jul | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2022-07-28 14:33 | 2022-07-28 16:55 | 85 | 2:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22072800109 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-07-28 | 12070 | keep | 0 | Jul | 2022 | 0.0082208 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2022-07-28 14:38 | 2022-07-28 14:39 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072800102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 312 | keep | 0 | Jul | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
ARECIBO | 2022-07-28 14:40 | 2022-07-28 14:41 | 1222 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO SE CERRO POR SCADA NO SE REPORTO CAUSA | A22072800062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 1222 | keep | 0 | Jul | 2022 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
CANOVANAS | 2022-07-28 14:45 | 2022-07-28 15:47 | 10 | 1:02 | P | DESGANCHE | ABRIR C/L PARA DESGANCHAR Y SE REPARAR CONDUCTOR PRIMARIO | R22072800024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-07-28 | 620 | keep | 0 | Jul | 2022 | 0.00042228 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-28 14:54 | 2022-07-28 16:25 | 30 | 1:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22072800063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-07-28 | 2730 | keep | 0 | Jul | 2022 | 0.0018594 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-28 15:02 | 2022-07-28 17:14 | 40 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S22072800134 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 132 | 2022-07-28 | 5280 | keep | 0 | Jul | 2022 | 0.0035962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-28 15:04 | 2022-07-28 22:25 | 5 | 7:21 | P | CONDUCTOR ROTO O ABIERTO | 2 X 20 EN TRANSFORMADOR SE REPARO BAJANTE | A22072800066 | New_Event | Primary Wire Break | Include | Include | Equipment | 441 | 2022-07-28 | 2205 | keep | 0 | Jul | 2022 | 0.0015018 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-07-28 15:28 | 2022-07-28 15:29 | 3654 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO SE CERRO POR SCADA NO SE REPORTO CAUSA | A22072800071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 3654 | keep | 0 | Jul | 2022 | 0.0024887 | 0.0024887 | Momentary | FALSE | FALSE | Not_TMED_Event | 3654
VEGA BAJA | 2022-07-28 15:29 | 2022-07-28 19:33 | 4 | 4:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR LA MISMA CAPACIDAD | A22072800054 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 244 | 2022-07-28 | 976 | keep | 0 | Jul | 2022 | 0.00066475 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-07-28 15:30 | 2022-07-29 10:49 | 40 | 19:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M22072800114 | New_Event | Primary Wire Break | Include | Include | Equipment | 1159 | 2022-07-28 | 46360 | keep | 0 | Jul | 2022 | 0.031576 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-28 15:31 | 2022-07-28 18:15 | 18 | 2:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22072800074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 164 | 2022-07-28 | 2952 | keep | 0 | Jul | 2022 | 0.0020106 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-07-28 15:45 | 2022-07-28 21:41 | 1 | 5:56 | P | CONDUCTOR ARRIADO O CRUZADO | 3 X 30 EN RISER Y 3 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22072800085 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 356 | 2022-07-28 | 356 | keep | 0 | Jul | 2022 | 0.00024247 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-07-28 15:50 | 2022-07-28 21:02 | 95 | 5:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE CORTE DE LINEA PARA SECCIONALIZAR AVERIA DE CAJA PRIMARIA QUEMADA Y AREA DE DESGANCHE 1 X 40 EN CORTE DE LINEA, SE HIZO EVENTO P22072800137 CON 65 CLIENTES FUERA | P22072800113 | New_Event | Cutout Failure | Include | Include | Equipment | 312 | 2022-07-28 | 29640 | keep | 0 | Jul | 2022 | 0.020188 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2022-07-28 15:50 | 2022-07-28 17:05 | 1 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M22072800071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2022-07-28 | 75 | keep | 0 | Jul | 2022 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-07-28 15:50 | 2022-07-29 18:35 | 16 | 26:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | A22072800060 | New_Event | Primary Wire Break | Include | Include | Equipment | 1605 | 2022-07-28 | 25680 | keep | 0 | Jul | 2022 | 0.017491 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2022-07-28 15:53 | 2022-07-28 15:54 | 390 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072800120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 390 | keep | 0 | Jul | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2022-07-28 15:54 | 2022-07-28 19:10 | 150 | 3:16 | P | LINEA DE TRANSMISION 38KV | 3 X 140 EN CORTE DE LINEA SE SECCIONALIZO LINEAS CRUZADAS POR OVER HEAD DE LINEA 2700 | M22072800124 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 196 | 2022-07-28 | 29400 | keep | 0 | Jul | 2022 | 0.020024 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-07-28 15:55 | 2022-07-28 16:10 | 250 | 0:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABREN MACHETES PARA REEMPLAZO DE AISLADOR | P22072800108 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 15 | 2022-07-28 | 3750 | keep | 0 | Jul | 2022 | 0.0025541 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-07-28 15:57 | 2022-07-28 16:59 | 1 | 1:02 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | S22072800159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-07-28 | 62 | keep | 0 | Jul | 2022 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-07-28 16:02 | 2022-07-29 12:24 | 12 | 20:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR T-3 DE 75KVA X 100KVA | C22072800127 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1222 | 2022-07-28 | 14664 | keep | 0 | Jul | 2022 | 0.0099876 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-07-28 16:03 | 2022-07-28 20:19 | 2825 | 4:16 | T | CAUSAS EXTERNAS | SE RETIRO CAMION QUE CRUZO LINEAS SE REPARO NEUTRAL PRIMARIO PARTIDO Y SE CERRO INTERRUPTOR | M22072800125 | New_Event | Damage From Public | Include | Include | Public | 256 | 2022-07-28 | 723200 | keep | 0 | Jul | 2022 | 0.49257 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
SAN JUAN | 2022-07-28 16:05 | 2022-07-28 18:47 | 12 | 2:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONECCIONES SECUNDARIAS - TRASPATIO | S22072800160 | New_Event | Secondary Wire Break | Include | Include | Equipment | 162 | 2022-07-28 | 1944 | keep | 0 | Jul | 2022 | 0.001324 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-07-28 16:07 | 2022-07-28 18:30 | 40 | 2:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22072800128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 143 | 2022-07-28 | 5720 | keep | 0 | Jul | 2022 | 0.0038959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-28 16:40 | 2022-07-28 19:30 | 85 | 2:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22072800141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-07-28 | 14450 | keep | 0 | Jul | 2022 | 0.0098418 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2022-07-28 16:52 | 2022-07-28 19:25 | 20 | 2:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO TRAMO DE LINEA SECUNDARIA AVERIADA | P22072800126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 153 | 2022-07-28 | 3060 | keep | 0 | Jul | 2022 | 0.0020842 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-07-28 16:55 | 2022-07-28 17:15 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22072800048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-07-28 | 160 | keep | 0 | Jul | 2022 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-07-28 17:02 | 2022-07-28 17:42 | 6 | 0:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22072800139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-07-28 | 240 | keep | 0 | Jul | 2022 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-07-28 17:06 | 2022-07-28 17:07 | 1253 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800162 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 1253 | keep | 0 | Jul | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-07-28 17:06 | 2022-07-28 17:07 | 1266 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800162 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 1266 | keep | 0 | Jul | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-07-28 17:06 | 2022-07-28 17:07 | 411 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800162 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 411 | keep | 0 | Jul | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2022-07-28 17:06 | 2022-07-28 17:07 | 1617 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 1617 | keep | 0 | Jul | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-07-28 17:06 | 2022-07-28 17:07 | 1017 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 1017 | keep | 0 | Jul | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-07-28 17:06 | 2022-07-28 17:07 | 828 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 828 | keep | 0 | Jul | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-07-28 17:06 | 2022-07-28 17:07 | 863 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 863 | keep | 0 | Jul | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-07-28 17:06 | 2022-07-28 17:07 | 309 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 309 | keep | 0 | Jul | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-07-28 17:06 | 2022-07-28 17:07 | 176 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 176 | keep | 0 | Jul | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-07-28 17:06 | 2022-07-28 17:07 | 974 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 MAL TIEMPO EN EL AREA | M22072800165 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-07-28 | 974 | keep | 0 | Jul | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
AGUADILLA | 2022-07-28 17:39 | 2022-07-29 07:12 | 100 | 13:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M22072800174 | New_Event | Primary Wire Break | Include | Include | Equipment | 813 | 2022-07-28 | 81300 | keep | 0 | Jul | 2022 | 0.055373 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-28 17:44 | 2022-07-29 10:47 | 22 | 17:03 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M22072800180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1023 | 2022-07-28 | 22506 | keep | 0 | Jul | 2022 | 0.015329 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
UTUADO | 2022-07-28 17:46 | 2022-07-28 21:10 | 7 | 3:24 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22072800088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-07-28 | 1428 | keep | 0 | Jul | 2022 | 0.0009726 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-07-28 17:50 | 2022-07-28 22:10 | 150 | 4:20 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22072800183 | New_Event | Primary Wire Break | Include | Include | Equipment | 260 | 2022-07-28 | 39000 | keep | 0 | Jul | 2022 | 0.026563 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-07-28 18:08 | 2022-07-28 18:39 | 4 | 0:31 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGACHO Y SE REPARO SECUNDARIA | R22072800040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 31 | 2022-07-28 | 124 | keep | 0 | Jul | 2022 | 8.4456e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-07-28 18:10 | 2022-07-28 19:20 | 7 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22072800089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-07-28 | 490 | keep | 0 | Jul | 2022 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-07-28 18:12 | 2022-07-28 22:40 | 60 | 4:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072800202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-07-28 | 16080 | keep | 0 | Jul | 2022 | 0.010952 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-07-28 18:33 | 2022-07-29 06:10 | 60 | 11:37 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22072800207 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 697 | 2022-07-28 | 41820 | keep | 0 | Jul | 2022 | 0.028483 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-28 19:05 | 2022-07-28 22:02 | 65 | 2:57 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C22072800015 | New_Event | Animals | Include | Include | Wildlife | 177 | 2022-07-28 | 11505 | keep | 0 | Jul | 2022 | 0.007836 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-07-28 19:09 | 2022-07-28 19:10 | 350 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1100-02 | S22072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 350 | keep | 0 | Jul | 2022 | 0.00023838 | 0.00023838 | Momentary | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2022-07-28 19:09 | 2022-07-28 19:10 | 215 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1100-01 | S22072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-28 | 215 | keep | 0 | Jul | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2022-07-28 19:09 | 2022-07-28 19:13 | 823 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 1119-04 LLEVA 1119-02 Y 95% DEL 1115-05 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-28 | 3292 | keep | 0 | Jul | 2022 | 0.0022422 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
SAN JUAN | 2022-07-28 19:09 | 2022-07-28 19:13 | 863 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1119-04 LLEVA 1119-02 Y 95% DEL 1115-05 | S22072100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-28 | 3452 | keep | 0 | Jul | 2022 | 0.0023511 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2022-07-28 19:09 | 2022-07-28 19:13 | 2720 | 0:04 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA 1119-02 Y 95% 1115-05 | S22072800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-28 | 10880 | keep | 0 | Jul | 2022 | 0.0074103 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-07-28 19:15 | 2022-07-28 19:38 | 4 | 0:23 | P | PROBLEMA DEL CLIENTE | SE DESENERGIZO NUEVAMENTE CAJA SECA PARA RECONECTE DE CLIENTE (YA REPARO SUBESTACION PRIVADA) G.O.I. SJ 220728-02 | R22072800025 | New_Event | Customer-Related Interruption | Include | Include | Public | 23 | 2022-07-28 | 92 | keep | 0 | Jul | 2022 | 6.2661e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-07-28 19:20 | 2022-07-28 20:45 | 10 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22072800139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2022-07-28 | 850 | keep | 0 | Jul | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-07-28 19:24 | 2022-07-28 21:08 | 36 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22072800151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-07-28 | 3744 | keep | 0 | Jul | 2022 | 0.00255 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-07-28 19:28 | 2022-07-28 21:10 | 6 | 1:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22072800077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-07-28 | 612 | keep | 0 | Jul | 2022 | 0.00041683 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-07-28 19:30 | 2022-07-29 00:25 | 171 | 4:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO CAJA A LINEA EN C/L | C22072800153 | New_Event | Primary Wire Break | Include | Include | Equipment | 295 | 2022-07-28 | 50445 | keep | 0 | Jul | 2022 | 0.034358 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
CANOVANAS | 2022-07-28 19:43 | 2022-07-28 21:00 | 69 | 1:17 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L SE DESPEGO PUENTE CRUZADO | R22072800045 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 77 | 2022-07-28 | 5313 | keep | 0 | Jul | 2022 | 0.0036187 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2022-07-28 20:00 | 2022-07-28 20:23 | 10 | 0:23 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA REMPLAZO DE PEDESTAL | B22072700271 | New_Event |  |  |  |  | 23 | 2022-07-28 | 230 | keep | 0 | Jul | 2022 | 0.00015665 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-07-28 20:07 | 2022-07-29 03:00 | 10 | 6:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | A22072800097 | New_Event | Secondary Wire Break | Include | Include | Equipment | 413 | 2022-07-28 | 4130 | keep | 0 | Jul | 2022 | 0.0028129 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-28 20:19 | 2022-07-28 23:03 | 196 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 Y 1 X 100 EN C/L SE SECCIONALIZO CONDUCTOR EN EL SUELO | R22072800050 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2022-07-28 | 32144 | keep | 0 | Jul | 2022 | 0.021893 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
CAGUAS | 2022-07-28 20:23 | 2022-07-28 23:09 | 150 | 2:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C22072800165 | New_Event | Cutout Failure | Include | Include | Equipment | 166 | 2022-07-28 | 24900 | keep | 0 | Jul | 2022 | 0.016959 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-07-28 20:36 | 2022-07-29 10:09 | 100 | 13:33 | P | LINEA DE TRANSMISION 38KV | FASE DE LA LINEA 3800 EN EL SUELO | C22072800177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 813 | 2022-07-28 | 81300 | keep | 0 | Jul | 2022 | 0.055373 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-07-28 20:48 | 2022-07-29 12:24 | 4 | 15:36 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN RISER T3 AVERIADO SE TRABAJARA MANANA | C22072800127 | New_Event | Service Transformer Failure | Include | Include | Equipment | 936 | 2022-07-28 | 3744 | keep | 0 | Jul | 2022 | 0.00255 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-07-28 21:00 | 2022-07-28 21:01 | 1097 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22072800243 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-07-28 | 1097 | keep | 0 | Jul | 2022 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
PONCE | 2022-07-28 21:02 | 2022-07-29 14:14 | 65 | 17:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA QUEMADA Y SE DESGANCHO | P22072800137 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 1032 | 2022-07-28 | 67080 | keep | 0 | Jul | 2022 | 0.045688 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-28 21:02 | 2022-07-28 23:55 | 400 | 2:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072800238 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 173 | 2022-07-28 | 69200 | keep | 0 | Jul | 2022 | 0.047132 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2022-07-28 21:07 | 2022-07-28 22:50 | 8 | 1:43 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR REPARAR BAJANTE PRIMARIO | M22072800241 | New_Event | Primary Wire Break | Include | Include | Equipment | 103 | 2022-07-28 | 824 | keep | 0 | Jul | 2022 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-07-28 21:16 | 2022-07-29 00:06 | 725 | 2:50 | P | TRANSFORMADOR AVERIADO | 1 X 80 SE CORRIGIO PUNTO CALIENTE EN BUSHING CONVERTIDOR | C22072800202 | New_Event | Service Transformer Failure | Include | Include | Equipment | 170 | 2022-07-28 | 123250 | keep | 0 | Jul | 2022 | 0.083945 | 0.00049379 | Sustained | FALSE | FALSE | Not_TMED_Event | 725
CANOVANAS | 2022-07-28 23:03 | 2022-07-29 17:42 | 90 | 18:39 | P | DESGANCHE | SE REALIZO DESGANCHE LEVANTO CONDUCTOR Y CERRO C/L | R22072800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1119 | 2022-07-28 | 100710 | keep | 0 | Jul | 2022 | 0.068593 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-07-28 23:03 | 2022-07-29 09:20 | 32 | 10:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L 1 X 15 EN XMR SE REMPLAZO CAJA EN XMR | B22072800084 | New_Event | Cutout Failure | Include | Include | Equipment | 617 | 2022-07-28 | 19744 | keep | 0 | Jul | 2022 | 0.013448 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
GUAYAMA | 2022-07-28 23:12 | 2022-07-29 11:15 | 100 | 12:03 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA EN TRONCAL SE ABRE INTERRUPTOR PARA REPARAR AVERIA | P22072800147 | New_Event | Primary Wire Break | Include | Include | Equipment | 723 | 2022-07-28 | 72300 | keep | 0 | Jul | 2022 | 0.049243 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-28 23:37 | 2022-07-29 10:10 | 51 | 10:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22072800093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 633 | 2022-07-28 | 32283 | keep | 0 | Jul | 2022 | 0.021988 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
ARECIBO | 2022-07-29 00:35 | 2022-07-29 10:00 | 15 | 9:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22072900002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 565 | 2022-07-29 | 8475 | keep | 0 | Jul | 2022 | 0.0057723 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-07-29 01:21 | 2022-07-29 01:23 | 315 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22072900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-29 | 630 | keep | 0 | Jul | 2022 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
HUMACAO | 2022-07-29 01:46 | 2022-07-29 07:31 | 146 | 5:45 | P | ANIMAL | 1 X 50 EN C/L AVE | C22072900003 | New_Event | Animals | Include | Include | Wildlife | 345 | 2022-07-29 | 50370 | keep | 0 | Jul | 2022 | 0.034307 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
MAYAGÃœEZ | 2022-07-29 02:04 | 2022-07-29 09:24 | 15 | 7:20 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | M22072900001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 440 | 2022-07-29 | 6600 | keep | 0 | Jul | 2022 | 0.0044952 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-07-29 02:15 | 2022-07-29 11:25 | 313 | 9:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REMPLAZO CAJA | B22072900010 | New_Event | Cutout Failure | Include | Include | Equipment | 550 | 2022-07-29 | 172150 | keep | 0 | Jul | 2022 | 0.11725 | 0.00021318 | Sustained | FALSE | FALSE | Not_TMED_Event | 313
BAYAMON | 2022-07-29 02:50 | 2022-07-29 11:40 | 10 | 8:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L 1 X 40 EN RISER SE REMPLAZO CAJA | S22072900006 | New_Event | Cutout Failure | Include | Include | Equipment | 530 | 2022-07-29 | 5300 | keep | 0 | Jul | 2022 | 0.0036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-07-29 03:09 | 2022-07-29 15:30 | 4 | 12:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 741 | 2022-07-29 | 2964 | keep | 0 | Jul | 2022 | 0.0020188 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-07-29 03:37 | 2022-07-29 03:39 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22073000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-29 | 4252 | keep | 0 | Jul | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2022-07-29 04:48 | 2022-07-29 20:09 | 30 | 15:21 | P | CONDUCTOR ROTO O ABIERTO | 3X25 EN BANCO DE XMRS SE CERRO PUENTE DE LINEA @ CAJA EN BANCO DE XMRS | S22072900117 | New_Event | Primary Wire Break | Include | Include | Equipment | 921 | 2022-07-29 | 27630 | keep | 0 | Jul | 2022 | 0.018819 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-07-29 05:18 | 2022-07-29 07:17 | 100 | 1:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARA | C22072900006 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2022-07-29 | 11900 | keep | 0 | Jul | 2022 | 0.008105 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-29 05:47 | 2022-07-29 12:33 | 60 | 6:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X65 EN C/L Y SE REMPLAZO AISLADOR (PIN-POLE TOP) | S22072900008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 406 | 2022-07-29 | 24360 | keep | 0 | Jul | 2022 | 0.016591 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-07-29 06:01 | 2022-07-29 18:25 | 100 | 12:24 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | C22072900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 744 | 2022-07-29 | 74400 | keep | 0 | Jul | 2022 | 0.050674 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-07-29 06:14 | 2022-07-29 06:15 | 2201 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22072900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 2201 | keep | 0 | Jul | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
SAN JUAN | 2022-07-29 06:17 | 2022-07-29 06:18 | 218 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S22072900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 218 | keep | 0 | Jul | 2022 | 0.00014848 | 0.00014848 | Momentary | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2022-07-29 06:17 | 2022-07-29 08:28 | 409 | 2:11 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO AVERIA POR CONDUCTOR PRIMARIO EN EL SUELO MEDIANTE G.O.I. SJ-220729-01 QUEDA 10% SIN SERVICIO | S22072900011 | New_Event | Primary Wire Break | Include | Include | Equipment | 131 | 2022-07-29 | 53579 | keep | 0 | Jul | 2022 | 0.036492 | 0.00027857 | Sustained | FALSE | FALSE | Not_TMED_Event | 409
BAYAMON | 2022-07-29 06:29 | 2022-07-29 06:30 | 1983 | 0:01 | T | NO SE REPORTO CAUSA | BKR 1801-02 DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1711-04 | B22072900030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 1983 | keep | 0 | Jul | 2022 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-07-29 06:29 | 2022-07-29 06:30 | 186 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1711-04 | B22072900030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 186 | keep | 0 | Jul | 2022 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2022-07-29 06:30 | 2022-07-29 09:53 | 1 | 3:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B22072900041 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 203 | 2022-07-29 | 203 | keep | 0 | Jul | 2022 | 0.00013826 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-29 06:32 | 2022-07-29 10:39 | 30 | 4:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22072900031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2022-07-29 | 7410 | keep | 0 | Jul | 2022 | 0.0050469 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-07-29 06:42 | 2022-07-29 08:58 | 40 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22072900007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2022-07-29 | 5440 | keep | 0 | Jul | 2022 | 0.0037052 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-07-29 07:03 | 2022-07-29 07:04 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 2608 | keep | 0 | Jul | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
BAYAMON | 2022-07-29 07:18 | 2022-07-29 07:19 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1909-08 LLEVA LA CARGA DEL 1907-05 | S22072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 2435 | keep | 0 | Jul | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-29 07:18 | 2022-07-29 07:19 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1907-05 | S22072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 2956 | keep | 0 | Jul | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
PONCE | 2022-07-29 07:22 | 2022-07-29 07:23 | 2308 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA CICLO DE RECIERRE Y QUEDA EN SERVICIO | P22072900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-07-29 | 2308 | keep | 0 | Jul | 2022 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
PONCE | 2022-07-29 07:23 | 2022-07-29 11:45 | 1000 | 4:22 | P | DESGANCHE | 2 X 140 EN C/L SE REALIZO DESGANCHE | P22072900012 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-07-29 | 262000 | keep | 0 | Jul | 2022 | 0.17845 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
YAUCO | 2022-07-29 07:26 | 2022-07-29 10:03 | 20 | 2:37 | P | CAUSAS EXTERNAS | 1 X 40 C/L CAMION TIENE CONTACTO CON TENSOR POSTE PRIMARIO Y CRUZA FASE | P22072900009 | New_Event | Damage From Public | Include | Include | Public | 157 | 2022-07-29 | 3140 | keep | 0 | Jul | 2022 | 0.0021386 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-07-29 08:01 | 2022-07-29 11:15 | 1 | 3:14 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L MAL TIEMPO RAYOS | R22072900003 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 194 | 2022-07-29 | 194 | keep | 0 | Jul | 2022 | 0.00013213 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-29 08:21 | 2022-07-29 08:59 | 271 | 0:38 | T | LINEA DE TRANSMISION 38KV | PERSONAL RETIRO OVHGW DE LA LINEA LINEA 3900 | S22072900039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-07-29 | 10298 | keep | 0 | Jul | 2022 | 0.0070139 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2022-07-29 08:25 | 2022-07-29 10:20 | 60 | 1:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22072900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-07-29 | 6900 | keep | 0 | Jul | 2022 | 0.0046996 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-29 08:28 | 2022-07-29 11:05 | 46 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. SJ-220729-01 - EN SERVICIO TOTAL | S22072900011 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 157 | 2022-07-29 | 7222 | keep | 0 | Jul | 2022 | 0.0049189 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-07-29 08:29 | 2022-07-29 19:30 | 40 | 11:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22072900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 661 | 2022-07-29 | 26440 | keep | 0 | Jul | 2022 | 0.018008 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-07-29 08:37 | 2022-07-29 10:11 | 15 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS SE REEMPLAZO BARRA SOTERRADA | M22072900024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2022-07-29 | 1410 | keep | 0 | Jul | 2022 | 0.00096034 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-07-29 08:39 | 2022-07-29 08:56 | 67 | 0:17 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR Y SE RETIRO OVERHEAD DE LINEA 3900 SOBRE ALIMENTADOR | S22072900043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-07-29 | 1139 | keep | 0 | Jul | 2022 | 0.00077577 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2022-07-29 08:42 | 2022-07-29 18:10 | 6 | 9:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 25 KVA | A22072900017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 568 | 2022-07-29 | 3408 | keep | 0 | Jul | 2022 | 0.0023212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-07-29 08:45 | 2022-07-29 09:30 | 4 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR CONECTORES DE LOS BAJANTE SECUNDARIOS | R22072900025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-07-29 | 180 | keep | 0 | Jul | 2022 | 0.0001226 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-07-29 08:58 | 2022-07-29 12:27 | 1 | 3:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22072900041 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 209 | 2022-07-29 | 209 | keep | 0 | Jul | 2022 | 0.00014235 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-29 09:10 | 2022-07-29 14:16 | 8 | 5:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA | M22072900031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 306 | 2022-07-29 | 2448 | keep | 0 | Jul | 2022 | 0.0016673 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-07-29 09:48 | 2022-07-29 11:50 | 1 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22072900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-07-29 | 122 | keep | 0 | Jul | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-29 09:55 | 2022-07-29 11:32 | 4622 | 1:37 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR 2 POSTES PARTIDOS 95% EN SERVICIO | B22072900072 | New_Event | Primary Pole Failure | Include | Include | Equipment | 97 | 2022-07-29 | 448334 | keep | 0 | Jul | 2022 | 0.30536 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
CAGUAS | 2022-07-29 09:58 | 2022-07-29 14:19 | 1 | 4:21 | P | ANIMAL | 1 X 40 EN C/L AVE | C22072900036 | New_Event | Animals | Include | Include | Wildlife | 261 | 2022-07-29 | 261 | keep | 0 | Jul | 2022 | 0.00017777 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-29 10:08 | 2022-07-29 12:50 | 1 | 2:42 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y DESGANCHE SECUNDARIO | C22072900039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 162 | 2022-07-29 | 162 | keep | 0 | Jul | 2022 | 0.00011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-07-29 10:09 | 2022-07-29 16:13 | 598 | 6:04 | T | LINEA DE TRANSMISION 38KV | SE TRANSFIRIO LA CARGA DEL 3403-01 AL 3405-03 LINEA 3800 TIENE UNA FASE EN EL SUELO | C22072800177 | Additional_clients | 38 kV Transmission Line Source | Include | Include | Power supply | 364 | 2022-07-29 | 217672 | keep | 0 | Jul | 2022 | 0.14826 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-07-29 10:10 | 2022-07-29 16:35 | 12 | 6:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINE SECUNDARIA | B22072900091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 385 | 2022-07-29 | 4620 | keep | 0 | Jul | 2022 | 0.0031467 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-07-29 10:34 | 2022-07-29 18:11 | 26 | 7:37 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | C22072900046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2022-07-29 | 11882 | keep | 0 | Jul | 2022 | 0.0080928 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-07-29 11:06 | 2022-07-29 14:34 | 1 | 3:28 | P | NO SE REPORTO CAUSA | 2X50 EN RISER | S22072900068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-07-29 | 208 | keep | 0 | Jul | 2022 | 0.00014167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-07-29 11:15 | 2022-07-29 12:20 | 3718 | 1:05 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE COLOCA INTERRUPTOR EN SERVICIO | P22072800147 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 65 | 2022-07-29 | 241670 | keep | 0 | Jul | 2022 | 0.1646 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-07-29 11:15 | 2022-07-29 15:56 | 1 | 4:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA | A22072900035 | New_Event | Primary Wire Break | Include | Include | Equipment | 281 | 2022-07-29 | 281 | keep | 0 | Jul | 2022 | 0.00019139 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-29 11:29 | 2022-07-29 14:50 | 13 | 3:21 | P | ANIMAL | 1 X 25 EN XMR SE RETIRO AVE | B22072900130 | New_Event | Animals | Include | Include | Wildlife | 201 | 2022-07-29 | 2613 | keep | 0 | Jul | 2022 | 0.0017797 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
YAUCO | 2022-07-29 11:30 | 2022-07-29 12:50 | 20 | 1:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA A 4.16KV AVERIADO | P22072900039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 80 | 2022-07-29 | 1600 | keep | 0 | Jul | 2022 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-07-29 11:32 | 2022-07-30 04:33 | 231 | 17:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZARON DOS POSTES Y SE NORMALIZO LAS CARGAS DEL ALIMENTADOR 100% EN SERVICIO | B22072900072 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1021 | 2022-07-29 | 235851 | keep | 0 | Jul | 2022 | 0.16064 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
CAGUAS | 2022-07-29 11:32 | 2022-07-29 14:01 | 15 | 2:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN C/L Y SE ATACHO LINEA A POSTE | C22072900052 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 149 | 2022-07-29 | 2235 | keep | 0 | Jul | 2022 | 0.0015222 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-07-29 11:48 | 2022-07-30 09:12 | 1 | 21:24 | P | NO SE REPORTO CAUSA | 1X30 EN RISER | B22072900135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1284 | 2022-07-29 | 1284 | keep | 0 | Jul | 2022 | 0.00087453 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-07-29 11:57 | 2022-07-29 19:40 | 10 | 7:43 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B22072900136 | New_Event | Primary Wire Break | Include | Include | Equipment | 463 | 2022-07-29 | 4630 | keep | 0 | Jul | 2022 | 0.0031535 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-29 12:07 | 2022-07-29 13:50 | 1 | 1:43 | P | PROBLEMA DEL CLIENTE | 2 X 40 EN SU SE ELIMINO PARARAYO EN RISER PRIVADO | B22072900137 | New_Event | Customer-Related Interruption | Include | Include | Public | 103 | 2022-07-29 | 103 | keep | 0 | Jul | 2022 | 7.0153e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-07-29 12:09 | 2022-07-29 15:47 | 60 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE LINEA @ CAJA EN C/L | S22072900079 | New_Event | Primary Wire Break | Include | Include | Equipment | 218 | 2022-07-29 | 13080 | keep | 0 | Jul | 2022 | 0.0089087 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-29 12:17 | 2022-07-29 12:23 | 350 | 0:06 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1100-02 | S22072900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-07-29 | 2100 | keep | 0 | Jul | 2022 | 0.0014303 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2022-07-29 12:17 | 2022-07-29 12:23 | 215 | 0:06 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1100-01 | S22072900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-07-29 | 1290 | keep | 0 | Jul | 2022 | 0.00087861 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2022-07-29 12:17 | 2022-07-29 13:29 | 824 | 1:12 | P | DESCONECTIVO DEFECTUOSO | 95% DE SU CARGA TRANSFERIDA AL 1119-04 SE SECCIONALIZO AVERIA POR MACHETE QUEMADO MEDIANTE G.O.I. SJ-220729-029-04 - EN SERVICIO - SOLO QUEDA SIN SERVICIO 2% DEL 1119-04 | S22072900085 | New_Event | Switch Failure | Include | Include | Equipment | 72 | 2022-07-29 | 59328 | keep | 0 | Jul | 2022 | 0.040408 | 0.00056122 | Sustained | FALSE | FALSE | Not_TMED_Event | 824
SAN JUAN | 2022-07-29 12:17 | 2022-07-29 13:29 | 343 | 1:12 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO AVERIA POR MACHETE QUEMADO MEDIANTE G.O.I. SJ-220729-029-04 - EN SERVICIO - SOLO QUEDA SIN SERVICIO 2% DEL 1119-04 | S22072900085 | New_Event | Switch Failure | Include | Include | Equipment | 72 | 2022-07-29 | 24696 | keep | 0 | Jul | 2022 | 0.01682 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2022-07-29 12:17 | 2022-07-29 13:29 | 2720 | 1:12 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO AVERIA POR MACHETE QUEMADO MEDIANTE G.O.I. SJ-220729-02 LLEVA CARGA DEL 1116-01 Y 95% DEL 1115-05 - SOLO QUEDA 4 CLIENTES SIN SERVICIO DEL 1119-04 | S22072900085 | New_Event | Switch Failure | Include | Include | Equipment | 72 | 2022-07-29 | 195840 | keep | 0 | Jul | 2022 | 0.13339 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
BAYAMON | 2022-07-29 12:37 | 2022-07-29 12:38 | 1180 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 1180 | keep | 0 | Jul | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
MAYAGÃœEZ | 2022-07-29 12:38 | 2022-07-29 15:32 | 60 | 2:54 | P | DESGANCHE | 1 X 140 EN CONVERTIDOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22072900059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-07-29 | 10440 | keep | 0 | Jul | 2022 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-07-29 12:45 | 2022-07-29 15:32 | 13 | 2:47 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | C22072900062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-07-29 | 2171 | keep | 0 | Jul | 2022 | 0.0014787 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2022-07-29 12:45 | 2022-07-30 10:14 | 50 | 21:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO LLUVIAS | M22072900092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1289 | 2022-07-29 | 64450 | keep | 0 | Jul | 2022 | 0.043897 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-07-29 12:56 | 2022-07-29 13:10 | 10 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22072900014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2022-07-29 | 140 | keep | 0 | Jul | 2022 | 9.5353e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-29 13:00 | 2022-07-29 15:00 | 30 | 2:00 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22072900144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-07-29 | 3600 | keep | 0 | Jul | 2022 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-07-29 13:05 | 2022-07-30 15:07 | 40 | 26:02 | P | CABLE SOTERRADO AVERIADO | REPARO CONDUCTOR PRIMARIO SOTERRADO DEL T - 18 @ T - 6 | C22072900066 | New_Event | UG Cable Fault | Include | Include | Equipment | 1562 | 2022-07-29 | 62480 | keep | 0 | Jul | 2022 | 0.042555 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-29 13:06 | 2022-07-29 13:08 | 3708 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S22072900110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-29 | 7416 | keep | 0 | Jul | 2022 | 0.005051 | 0.0025255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3708
CANOVANAS | 2022-07-29 13:08 | 2022-07-29 17:13 | 100 | 4:05 | P | TERMINACION SOTERRADA AVERIADA | 1 X 100 EN C/L 2 X 80 EN RISER Y SE REEMPLAZO TERMINACION Y PARRRAYO | R22072900025 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 245 | 2022-07-29 | 24500 | keep | 0 | Jul | 2022 | 0.016687 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-29 13:08 | 2022-07-29 17:42 | 90 | 4:34 | P | DESGANCHE | SE LEVANTO CONDUCTOR PRIMARIO Y DESGANCHE | R22072900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2022-07-29 | 24660 | keep | 0 | Jul | 2022 | 0.016796 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-07-29 13:12 | 2022-07-29 13:13 | 997 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22072900069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 997 | keep | 0 | Jul | 2022 | 0.00067905 | 0.00067905 | Momentary | FALSE | FALSE | Not_TMED_Event | 997
VEGA BAJA | 2022-07-29 13:21 | 2022-07-29 18:00 | 60 | 4:39 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22072900148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-07-29 | 16740 | keep | 0 | Jul | 2022 | 0.011402 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-07-29 13:26 | 2022-07-29 15:07 | 3 | 1:41 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE DESGANCHO EN SECUNDARIA | A22072900049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 101 | 2022-07-29 | 303 | keep | 0 | Jul | 2022 | 0.00020637 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-07-29 13:29 | 2022-07-29 15:35 | 4 | 2:06 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO MEDIANTE G.O.I. SJ-220729-02 | S22072900085 | Partial_restoration | Switch Failure | Include | Include | Equipment | 126 | 2022-07-29 | 504 | keep | 0 | Jul | 2022 | 0.00034327 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-07-29 13:32 | 2022-07-29 16:55 | 80 | 3:23 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L 1 X 15 EN XMR SE LEVANTO CONDUCTOR EVENTO TRANSFERIDO DE ARECIBO | A22072900050 | New_Event | Primary Wire Break | Include | Include | Equipment | 203 | 2022-07-29 | 16240 | keep | 0 | Jul | 2022 | 0.011061 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-07-29 14:00 | 2022-07-29 15:13 | 60 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22072900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-07-29 | 4380 | keep | 0 | Jul | 2022 | 0.0029832 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-07-29 14:09 | 2022-07-29 14:12 | 2113 | 0:03 | T | DESGANCHE | ADAM SOTO PATRULLO EL BREAKER E INDICA VARIOS PUNTOS DE DESGANCHE | P22072900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-07-29 | 6339 | keep | 0 | Jul | 2022 | 0.0043175 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
AGUADILLA | 2022-07-29 14:18 | 2022-07-29 19:40 | 20 | 5:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22072900090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-07-29 | 6440 | keep | 0 | Jul | 2022 | 0.0043863 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-29 14:21 | 2022-07-29 14:25 | 1681 | 0:04 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1303-04 | S22072900138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-29 | 6724 | keep | 0 | Jul | 2022 | 0.0045797 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-07-29 14:21 | 2022-07-29 19:51 | 500 | 5:30 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO FRENTE @ LA SUBESTACION MEDIANTE G.O.I. SJ-220729-03 LLEVA LA CARGA DEL 1303-04 | S22072900136 | New_Event | Switch Failure | Include | Include | Equipment | 330 | 2022-07-29 | 165000 | keep | 0 | Jul | 2022 | 0.11238 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-07-29 14:21 | 2022-07-29 14:25 | 1598 | 0:04 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1303-04 | S22072900138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-29 | 6392 | keep | 0 | Jul | 2022 | 0.0043536 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
GUAYAMA | 2022-07-29 14:23 | 2022-07-29 17:00 | 5 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN XMR SAFADO | P22072900083 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2022-07-29 | 785 | keep | 0 | Jul | 2022 | 0.00053466 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-07-29 14:38 | 2022-07-31 07:17 | 18 | 40:39 | P | EMPALME SOTERRADO AVERIADO | SE REMPLAZO PISTOLA Y SE CERRO PUENTE ABIERTO EN CAJAS SECAS Y PISTOLA EN VS-3 | S22072900148 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 2439 | 2022-07-29 | 43902 | keep | 0 | Jul | 2022 | 0.029901 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2022-07-29 14:46 | 2022-07-29 15:00 | 52 | 0:14 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR BAMBUS SOBRE LINEAS PRIMARIAS | A22072900059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-07-29 | 728 | keep | 0 | Jul | 2022 | 0.00049584 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
GUAYAMA | 2022-07-29 14:54 | 2022-07-29 16:03 | 50 | 1:09 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | P22072900088 | New_Event | Animals | Include | Include | Wildlife | 69 | 2022-07-29 | 3450 | keep | 0 | Jul | 2022 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-07-29 15:13 | 2022-07-29 16:35 | 30 | 1:22 | P | ANIMAL | 1 X 40 EN C/L AVE | C22072900094 | New_Event | Animals | Include | Include | Wildlife | 82 | 2022-07-29 | 2460 | keep | 0 | Jul | 2022 | 0.0016755 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-07-29 15:18 | 2022-07-29 17:10 | 80 | 1:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M22072900111 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2022-07-29 | 8960 | keep | 0 | Jul | 2022 | 0.0061026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-07-29 15:19 | 2022-07-30 15:14 | 37 | 23:55 | P | CABLE SOTERRADO AVERIADO | TRABAJO COMPLETADO SE REPARO TRAMO DE T-50 @ SU-14 MEDIANTE GOI SJ-220729-04A | S22072900158 | New_Event | UG Cable Fault | Include | Include | Equipment | 1435 | 2022-07-29 | 53095 | keep | 0 | Jul | 2022 | 0.036163 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2022-07-29 15:23 | 2022-07-30 11:44 | 1 | 20:21 | P | SECUNDARIA/DESGANCHE | 2X20 EN BANCO DE XMRS | B22072900167 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1221 | 2022-07-29 | 1221 | keep | 0 | Jul | 2022 | 0.00083162 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-29 15:30 | 2022-07-29 18:00 | 3 | 2:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22072900108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 150 | 2022-07-29 | 450 | keep | 0 | Jul | 2022 | 0.00030649 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-07-29 15:34 | 2022-07-29 15:35 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 5630 | keep | 0 | Jul | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
GUAYAMA | 2022-07-29 15:35 | 2022-07-29 15:36 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072900096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 527 | keep | 0 | Jul | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
BAYAMON | 2022-07-29 15:42 | 2022-07-29 15:43 | 3871 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B22072900000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-29 | 3871 | keep | 0 | Jul | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
CAGUAS | 2022-07-29 15:42 | 2022-07-29 20:00 | 30 | 4:18 | P | DESGANCHE | 1 X 65 EN C/L | C22072900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-07-29 | 7740 | keep | 0 | Jul | 2022 | 0.0052717 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-07-29 15:42 | 2022-07-29 19:27 | 206 | 3:45 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | C22072900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-07-29 | 46350 | keep | 0 | Jul | 2022 | 0.031569 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
BAYAMON | 2022-07-29 15:43 | 2022-07-29 18:55 | 41 | 3:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA | B22072900172 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 192 | 2022-07-29 | 7872 | keep | 0 | Jul | 2022 | 0.0053616 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
MAYAGÃœEZ | 2022-07-29 15:45 | 2022-07-29 16:00 | 20 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22072900044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2022-07-29 | 300 | keep | 0 | Jul | 2022 | 0.00020433 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-07-29 15:58 | 2022-07-29 19:00 | 4 | 3:02 | P | DESGANCHE | 2 X 50 EN X/L DESGANCHE | P22072900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-07-29 | 728 | keep | 0 | Jul | 2022 | 0.00049584 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-07-29 16:00 | 2022-07-29 16:45 | 3 | 0:45 | P | TRANSFORMADOR AVERIADO | ABRIR MONTURA DE TRANSFORMADORES PARA RETIRAR TRANSFORMADOR CON ESCAPE DE ACEITE FUERA DE USO | M22072900115 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2022-07-29 | 135 | keep | 0 | Jul | 2022 | 9.1948e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-07-29 16:01 | 2022-07-29 18:16 | 150 | 2:15 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22072900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-07-29 | 20250 | keep | 0 | Jul | 2022 | 0.013792 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-07-29 16:23 | 2022-07-29 17:33 | 7 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES EN BAJANTE DE NEUTRAL SECUNDARIO | S22072900166 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-07-29 | 490 | keep | 0 | Jul | 2022 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-07-29 16:55 | 2022-07-30 14:51 | 12 | 21:56 | P | SECUNDARIA/DESGANCHE | SE ABRIO C/L PARA DESGANCHAR Y REPARAR SECUNDARIA | S22072900172 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1316 | 2022-07-29 | 15792 | keep | 0 | Jul | 2022 | 0.010756 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-07-29 16:59 | 2022-07-29 18:40 | 20 | 1:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22072900084 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 101 | 2022-07-29 | 2020 | keep | 0 | Jul | 2022 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-29 17:00 | 2022-07-29 21:52 | 10 | 4:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE DE BUSHING @ GROUND EN XMR (NO FUNDIO) | S22072900175 | New_Event | Secondary Wire Break | Include | Include | Equipment | 292 | 2022-07-29 | 2920 | keep | 0 | Jul | 2022 | 0.0019888 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-29 17:00 | 2022-07-29 21:10 | 15 | 4:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO (CLIENTES CON PROBLEMAS DE VOLTAJE) | B22072800081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 250 | 2022-07-29 | 3750 | keep | 0 | Jul | 2022 | 0.0025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-07-29 17:01 | 2022-07-29 19:03 | 60 | 2:02 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | C22072900114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-07-29 | 7320 | keep | 0 | Jul | 2022 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-29 17:30 | 2022-07-29 17:44 | 413 | 0:14 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL (VARIAS VECES HABIA DADO FAIL TO OPERATE) 10% DE SU CARGA POR 1620-02 | S22072900184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2022-07-29 | 5782 | keep | 0 | Jul | 2022 | 0.0039381 | 0.00028129 | Sustained | FALSE | FALSE | Not_TMED_Event | 413
SAN JUAN | 2022-07-29 17:30 | 2022-07-29 17:44 | 3718 | 0:14 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL (HABIA DADO FAIL TO OPERATE) LLEVA 10% DEL 1206-03 | S22072900184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2022-07-29 | 52052 | keep | 0 | Jul | 2022 | 0.035452 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
AGUADILLA | 2022-07-29 17:55 | 2022-07-29 20:40 | 50 | 2:45 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22072900095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-07-29 | 8250 | keep | 0 | Jul | 2022 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-07-29 18:04 | 2022-07-29 22:30 | 150 | 4:26 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA SE ABRIERON PUENTES PARA SECCIONALIZAR | M22072900173 | New_Event | Primary Wire Break | Include | Include | Equipment | 266 | 2022-07-29 | 39900 | keep | 0 | Jul | 2022 | 0.027176 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-07-29 18:11 | 2022-07-29 21:49 | 40 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA | A22072900097 | New_Event | Primary Wire Break | Include | Include | Equipment | 218 | 2022-07-29 | 8720 | keep | 0 | Jul | 2022 | 0.0059392 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-07-29 18:25 | 2022-07-29 18:45 | 2 | 0:20 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS ARRIADAS | M22072900138 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 20 | 2022-07-29 | 40 | keep | 0 | Jul | 2022 | 2.7244e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-07-29 18:36 | 2022-07-29 21:35 | 50 | 2:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A22072900101 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2022-07-29 | 8950 | keep | 0 | Jul | 2022 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-07-29 18:41 | 2022-07-30 12:28 | 54 | 17:47 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN C/L DEJO FUERA XMR QUEMADO | C22072900128 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1067 | 2022-07-29 | 57618 | keep | 0 | Jul | 2022 | 0.039243 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BARRANQUITAS | 2022-07-29 18:48 | 2022-07-30 12:32 | 10 | 17:44 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22072900129 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1064 | 2022-07-29 | 10640 | keep | 0 | Jul | 2022 | 0.0072469 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-07-29 19:08 | 2022-07-29 20:21 | 1 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 15 XMR Y 1 X 20 EN RISER | R22072900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2022-07-29 | 73 | keep | 0 | Jul | 2022 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-07-29 19:16 | 2022-07-30 08:38 | 1 | 13:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES LLUVIAS | C22072900135 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 802 | 2022-07-29 | 802 | keep | 0 | Jul | 2022 | 0.00054624 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-07-29 19:28 | 2022-07-29 20:54 | 8 | 1:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO PORTAFUSIBLE | R22072900046 | New_Event | Cutout Failure | Include | Include | Equipment | 86 | 2022-07-29 | 688 | keep | 0 | Jul | 2022 | 0.00046859 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-07-29 19:28 | 2022-07-29 23:01 | 134 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L LLUVIAS | C22072900139 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2022-07-29 | 28542 | keep | 0 | Jul | 2022 | 0.01944 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
AGUADILLA | 2022-07-29 19:39 | 2022-07-29 23:10 | 150 | 3:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | M22072900173 | New_Event | Primary Wire Break | Include | Include | Equipment | 211 | 2022-07-29 | 31650 | keep | 0 | Jul | 2022 | 0.021557 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-07-29 19:51 | 2022-07-29 19:52 | 2999 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072900161 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-07-29 | 2999 | keep | 0 | Jul | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2022-07-29 19:52 | 2022-07-30 10:29 | 60 | 14:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR VIENTOS | M22072900188 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 877 | 2022-07-29 | 52620 | keep | 0 | Jul | 2022 | 0.035839 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-29 19:56 | 2022-07-30 09:26 | 40 | 13:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 80 EN C/L | S22072900233 | New_Event | Cutout Failure | Include | Include | Equipment | 810 | 2022-07-29 | 32400 | keep | 0 | Jul | 2022 | 0.022067 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-07-29 20:18 | 2022-07-30 09:15 | 7 | 12:57 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR CRUCE DE FASE POR RATA | P22072900116 | New_Event | Animals | Include | Include | Wildlife | 777 | 2022-07-29 | 5439 | keep | 0 | Jul | 2022 | 0.0037045 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-07-29 20:39 | 2022-07-30 07:24 | 88 | 10:45 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22072900151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2022-07-29 | 56760 | keep | 0 | Jul | 2022 | 0.038659 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
MAYAGÃœEZ | 2022-07-29 20:52 | 2022-07-29 20:53 | 3147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22072900179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 3147 | keep | 0 | Jul | 2022 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
CANOVANAS | 2022-07-29 21:19 | 2022-07-30 04:15 | 30 | 6:56 | P | ANIMAL | 1 X 65 EN C/L AVE | R22072900047 | New_Event | Animals | Include | Include | Wildlife | 416 | 2022-07-29 | 12480 | keep | 0 | Jul | 2022 | 0.0085001 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-07-29 21:36 | 2022-07-30 05:00 | 100 | 7:24 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22072900114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 444 | 2022-07-29 | 44400 | keep | 0 | Jul | 2022 | 0.030241 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-07-29 22:11 | 2022-07-29 22:12 | 2308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22072900127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 2308 | keep | 0 | Jul | 2022 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
SAN JUAN | 2022-07-29 22:19 | 2022-07-29 22:20 | 225 | 0:01 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO 1303-05 FRENTE @ LA SUBESTACION MEDIANTE G.O.I. SJ-220729-03 LLEVA LA CARGA DEL 1303-04 | S22072900136 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-07-29 | 225 | keep | 0 | Jul | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
CANOVANAS | 2022-07-29 22:25 | 2022-07-30 10:24 | 26 | 11:59 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22072900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 719 | 2022-07-29 | 18694 | keep | 0 | Jul | 2022 | 0.012732 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
MAYAGÃœEZ | 2022-07-29 22:25 | 2022-07-30 00:25 | 200 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22072900194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2022-07-29 | 24000 | keep | 0 | Jul | 2022 | 0.016346 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-07-29 22:30 | 2022-07-30 12:43 | 150 | 14:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARA PARTIDA Y SE CERRO CORTE DE LINEA | M22072900173 | New_Event | Primary Wire Break | Include | Include | Equipment | 853 | 2022-07-29 | 127950 | keep | 0 | Jul | 2022 | 0.087146 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-07-29 22:32 | 2022-07-30 08:49 | 10 | 10:17 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22072900161 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 617 | 2022-07-29 | 6170 | keep | 0 | Jul | 2022 | 0.0042024 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-07-29 22:54 | 2022-07-30 10:12 | 50 | 11:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22072900212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 678 | 2022-07-29 | 33900 | keep | 0 | Jul | 2022 | 0.023089 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-07-29 22:55 | 2022-07-30 08:20 | 91 | 9:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO PORTAFUSIBLES | R22072900054 | New_Event | Cutout Failure | Include | Include | Equipment | 565 | 2022-07-29 | 51415 | keep | 0 | Jul | 2022 | 0.035019 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
BARRANQUITAS | 2022-07-29 23:01 | 2022-07-29 23:02 | 2859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22072900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-29 | 2859 | keep | 0 | Jul | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
BARRANQUITAS | 2022-07-29 23:02 | 2022-07-30 10:40 | 134 | 11:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L LLUVIAS | C22072900139 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 698 | 2022-07-29 | 93532 | keep | 0 | Jul | 2022 | 0.063704 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-07-29 23:12 | 2022-07-30 09:20 | 20 | 10:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | M22072900217 | New_Event | Primary Wire Break | Include | Include | Equipment | 608 | 2022-07-29 | 12160 | keep | 0 | Jul | 2022 | 0.0082821 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-07-29 23:55 | 2022-07-30 11:16 | 35 | 11:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | M22072900219 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 681 | 2022-07-29 | 23835 | keep | 0 | Jul | 2022 | 0.016234 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-07-30 00:32 | 2022-07-30 12:19 | 60 | 11:47 | P | DESGANCHE | 1 X 100 EN C/L | S22073000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 707 | 2022-07-30 | 42420 | keep | 0 | Jul | 2022 | 0.028892 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-07-30 00:42 | 2022-07-30 09:54 | 100 | 9:12 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | M22073000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 552 | 2022-07-30 | 55200 | keep | 0 | Jul | 2022 | 0.037596 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-07-30 00:56 | 2022-07-30 10:05 | 40 | 9:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR ENREDADERA | M22073000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 549 | 2022-07-30 | 21960 | keep | 0 | Jul | 2022 | 0.014957 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-07-30 01:53 | 2022-07-30 04:00 | 200 | 2:07 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P2207300048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-07-30 | 25400 | keep | 0 | Jul | 2022 | 0.0173 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-07-30 03:04 | 2022-07-30 11:42 | 50 | 8:38 | P | NO SE REPORTO CAUSA | 1X65 EN C/L PRINCIPAL Y 1X50 C/L EN OTRO C/L | B22073000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 518 | 2022-07-30 | 25900 | keep | 0 | Jul | 2022 | 0.01764 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-30 03:12 | 2022-07-30 14:49 | 12 | 11:37 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22073000024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 697 | 2022-07-30 | 8364 | keep | 0 | Jul | 2022 | 0.0056967 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-30 03:17 | 2022-07-30 15:24 | 60 | 12:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22073000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 727 | 2022-07-30 | 43620 | keep | 0 | Jul | 2022 | 0.029709 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-07-30 03:20 | 2022-07-30 09:40 | 60 | 6:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22073000014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2022-07-30 | 22800 | keep | 0 | Jul | 2022 | 0.015529 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-30 03:23 | 2022-07-30 17:18 | 36 | 13:55 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN RISER PARARRAYO 1 X 80 EN OTRO C/L SE INSTALO TIGUERO | S22073000026 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 835 | 2022-07-30 | 30060 | keep | 0 | Jul | 2022 | 0.020474 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2022-07-30 03:36 | 2022-07-30 12:02 | 15 | 8:26 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22073000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 506 | 2022-07-30 | 7590 | keep | 0 | Jul | 2022 | 0.0051695 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-07-30 03:54 | 2022-07-30 08:57 | 194 | 5:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | R22073000002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 303 | 2022-07-30 | 58782 | keep | 0 | Jul | 2022 | 0.040036 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
CANOVANAS | 2022-07-30 04:15 | 2022-07-30 04:19 | 3012 | 0:04 | T | ANIMAL | DISPARO DE BKR SE CERRO POR CONTROL | R22073000000 | New_Event | Animals | Include | Include | Wildlife | 4 | 2022-07-30 | 12048 | keep | 0 | Jul | 2022 | 0.0082058 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
CANOVANAS | 2022-07-30 04:15 | 2022-07-30 04:18 | 2106 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO POR CONTROL | R22073000000 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-07-30 | 6318 | keep | 0 | Jul | 2022 | 0.0043032 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2022-07-30 04:19 | 2022-07-30 09:41 | 30 | 5:22 | P | ANIMAL | 1 X 65 EN C/L AVE | R22072900047 | 1st_after_momentary | Animals | Include | Include | Wildlife | 322 | 2022-07-30 | 9660 | keep | 0 | Jul | 2022 | 0.0065794 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-30 04:28 | 2022-07-30 04:30 | 2106 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO POR CONTROL | R22073000000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2022-07-30 | 4212 | keep | 0 | Jul | 2022 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
BAYAMON | 2022-07-30 04:34 | 2022-07-30 17:49 | 231 | 13:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZARON DOS POSTES Y SE NORMALIZO LAS CARGAS DEL ALIMENTADOR 100% EN SERVICIO | B22072900072 | New_Event | Primary Pole Failure | Include | Include | Equipment | 795 | 2022-07-30 | 183645 | keep | 0 | Jul | 2022 | 0.12508 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
SAN JUAN | 2022-07-30 04:48 | 2022-07-30 16:20 | 40 | 11:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22073000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 692 | 2022-07-30 | 27680 | keep | 0 | Jul | 2022 | 0.018853 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-07-30 04:52 | 2022-07-30 04:54 | 2106 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO POR CONTROL | R22073000000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2022-07-30 | 4212 | keep | 0 | Jul | 2022 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CANOVANAS | 2022-07-30 04:56 | 2022-07-30 08:22 | 2106 | 3:26 | T | CONDUCTOR ROTO O ABIERTO | SE LEVANTO PRIMARIA MEDIANTE GOI SJ-220730-50 Y SE NORMALIZO LA CARGA | R22073000006 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 206 | 2022-07-30 | 433836 | keep | 0 | Jul | 2022 | 0.29548 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
VEGA BAJA | 2022-07-30 05:00 | 2022-07-30 11:12 | 30 | 6:12 | P | DESGANCHE | 1X40 EN C/L | B22073000007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 372 | 2022-07-30 | 11160 | keep | 0 | Jul | 2022 | 0.007601 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-07-30 05:08 | 2022-07-30 06:20 | 230 | 1:12 | P | DESGANCHE | SE REMOVIO RAMA DE LINEA | S22073000034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-07-30 | 16560 | keep | 0 | Jul | 2022 | 0.011279 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
BAYAMON | 2022-07-30 05:16 | 2022-07-30 16:45 | 10 | 11:29 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L 1 3 X 50 EN RISER LOTE 5 | S22073000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 689 | 2022-07-30 | 6890 | keep | 0 | Jul | 2022 | 0.0046927 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-30 05:18 | 2022-07-30 10:16 | 50 | 4:58 | P | ANIMAL | 1X50 EN C/L AVE CRUZO LINEAS | B22073000031 | New_Event | Animals | Include | Include | Wildlife | 298 | 2022-07-30 | 14900 | keep | 0 | Jul | 2022 | 0.010148 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-07-30 05:29 | 2022-07-30 05:30 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22073000110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 2379 | keep | 0 | Jul | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
SAN JUAN | 2022-07-30 05:46 | 2022-07-30 16:25 | 29 | 10:39 | P | SECUNDARIA/DESGANCHE | 1 X 15 XMR SE DESGANCHO | S22073000048 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 639 | 2022-07-30 | 18531 | keep | 0 | Jul | 2022 | 0.012621 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2022-07-30 06:08 | 2022-07-30 06:49 | 1085 | 0:41 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO AREA Y SE REALIZO DESGANCHE A VARETA | S22073000068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2022-07-30 | 44485 | keep | 0 | Jul | 2022 | 0.030299 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
VEGA BAJA | 2022-07-30 06:24 | 2022-07-30 06:26 | 908 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22073000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-30 | 1816 | keep | 0 | Jul | 2022 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-07-30 06:39 | 2022-07-30 06:40 | 221 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 75% DE SU CARGA POR EL 1014-16 | S22073000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 221 | keep | 0 | Jul | 2022 | 0.00015052 | 0.00015052 | Momentary | FALSE | FALSE | Not_TMED_Event | 221
SAN JUAN | 2022-07-30 06:39 | 2022-07-30 06:40 | 295 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA EL 75% DEL 1013-13 SE CERRO POR SCADA | S22073000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 295 | keep | 0 | Jul | 2022 | 0.00020092 | 0.00020092 | Momentary | FALSE | FALSE | Not_TMED_Event | 295
SAN JUAN | 2022-07-30 06:49 | 2022-07-30 08:02 | 542 | 1:13 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO AREA Y SE REALIZO DESGANCHE A VARETA | S22073000068 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-07-30 | 39566 | keep | 0 | Jul | 2022 | 0.026948 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-30 06:54 | 2022-07-30 11:50 | 150 | 4:56 | P | DESGANCHE | 2 X 65 EN C/L Y SE REALIZO DESGANCHE | S22073000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-07-30 | 44400 | keep | 0 | Jul | 2022 | 0.030241 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-07-30 07:01 | 2022-07-30 09:50 | 40 | 2:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22073000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-07-30 | 6760 | keep | 0 | Jul | 2022 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-30 07:02 | 2022-07-30 13:16 | 30 | 6:14 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22073000013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 374 | 2022-07-30 | 11220 | keep | 0 | Jul | 2022 | 0.0076419 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-07-30 07:02 | 2022-07-30 12:50 | 50 | 5:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE DE ARBOL | P22073000118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2022-07-30 | 17400 | keep | 0 | Jul | 2022 | 0.011851 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-07-30 07:07 | 2022-07-30 11:37 | 37 | 4:30 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | C22073000015 | New_Event | Animals | Include | Include | Wildlife | 270 | 2022-07-30 | 9990 | keep | 0 | Jul | 2022 | 0.0068041 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CAGUAS | 2022-07-30 07:11 | 2022-07-30 15:21 | 100 | 8:10 | P | MAL TIEMPO/RAYOS | 1 X 40 Y 1 X 65 EN C/LS Y 1 X 10, 1 X 15 Y 1 X 15 EN XMRS RAYOS | C22073000017 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 490 | 2022-07-30 | 49000 | keep | 0 | Jul | 2022 | 0.033374 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-07-30 07:32 | 2022-07-30 07:33 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22073000121 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 2379 | keep | 0 | Jul | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-07-30 07:33 | 2022-07-30 09:24 | 8 | 1:51 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN TRANSFORMADOR AVERIA EN PANEL ELECTRICO DE CLIENTE | P22073000120 | New_Event | Customer-Related Interruption | Include | Include | Public | 111 | 2022-07-30 | 888 | keep | 0 | Jul | 2022 | 0.00060481 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-07-30 07:43 | 2022-07-30 11:45 | 40 | 4:02 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO BAMBU | P22073000123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-07-30 | 9680 | keep | 0 | Jul | 2022 | 0.006593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-07-30 07:57 | 2022-07-30 07:58 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22073000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 3332 | keep | 0 | Jul | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
FAJARDO | 2022-07-30 07:59 | 2022-07-30 10:23 | 1 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 5 EN BANCO DE XMR | R22073000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-07-30 | 144 | keep | 0 | Jul | 2022 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-30 08:03 | 2022-07-30 12:28 | 80 | 4:25 | P | DESGANCHE | 2X65 EN C/L | B22073000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2022-07-30 | 21200 | keep | 0 | Jul | 2022 | 0.014439 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-07-30 08:04 | 2022-07-30 10:30 | 50 | 2:26 | P | ERROR HUMANO | 1 X 65 EN C/L FUSIBLE MAL INSTALADO | C22073000044 | New_Event | Human Error | Include | Include | Other | 146 | 2022-07-30 | 7300 | keep | 0 | Jul | 2022 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-07-30 08:08 | 2022-07-30 14:31 | 22 | 6:23 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C22073000045 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 383 | 2022-07-30 | 8426 | keep | 0 | Jul | 2022 | 0.0057389 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2022-07-30 08:17 | 2022-07-30 08:19 | 172 | 0:02 | T | PROBLEMA DEL CLIENTE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22073000000 | New_Event | Customer-Related Interruption | Include | Include | Public | 2 | 2022-07-30 | 344 | keep | 0 | Jul | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CANOVANAS | 2022-07-30 08:19 | 2022-07-30 17:33 | 1 | 9:14 | P | PROBLEMA DEL CLIENTE | 1 X 80 EN C/L CONTAMINACION EN SUB. CLIENTE | R22073000056 | 1st_after_momentary | Customer-Related Interruption | Include | Include | Public | 554 | 2022-07-30 | 554 | keep | 0 | Jul | 2022 | 0.00037733 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-07-30 08:30 | 2022-07-30 12:20 | 30 | 3:50 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L Y 1 X 10 EN XMR RAYOS | C22073000057 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 230 | 2022-07-30 | 6900 | keep | 0 | Jul | 2022 | 0.0046996 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-07-30 08:41 | 2022-07-30 09:23 | 60 | 0:42 | P | ANIMAL | 1 X 30 Y 1 X 20 EN C/LS CRUCE X AVE | C22073000063 | New_Event | Animals | Include | Include | Wildlife | 42 | 2022-07-30 | 2520 | keep | 0 | Jul | 2022 | 0.0017164 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-07-30 08:43 | 2022-07-30 17:54 | 25 | 9:11 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22073000095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 551 | 2022-07-30 | 13775 | keep | 0 | Jul | 2022 | 0.0093821 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-07-30 08:48 | 2022-07-30 11:40 | 30 | 2:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22073000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-07-30 | 5160 | keep | 0 | Jul | 2022 | 0.0035145 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-30 08:49 | 2022-07-30 13:36 | 90 | 4:47 | P | ARBOL SOBRE LINEA | 1X80 EN C/L Y SE RETIRO ARBOL COMPLETO DE PRIMARIA (TRASPATIO) | B22073000028 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 287 | 2022-07-30 | 25830 | keep | 0 | Jul | 2022 | 0.017593 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-07-30 08:52 | 2022-07-30 08:53 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22073000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 5252 | keep | 0 | Jul | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BARRANQUITAS | 2022-07-30 08:53 | 2022-07-30 08:54 | 2565 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 3502-02 | C22073000074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 2565 | keep | 0 | Jul | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-07-30 08:53 | 2022-07-30 08:54 | 3565 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 3502-01 | C22073000074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 3565 | keep | 0 | Jul | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
HUMACAO | 2022-07-30 08:56 | 2022-07-30 13:40 | 49 | 4:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO POSTAFUSIBLE QUEMADO | C22073000073 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2022-07-30 | 13916 | keep | 0 | Jul | 2022 | 0.0094781 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
HUMACAO | 2022-07-30 09:01 | 2022-07-30 09:35 | 1 | 0:34 | P | MAL TIEMPO/RAYOS | 2 X 20 EN BANCO DE XMRS Y 2 X 80 EN C/L RAYOS | C22073000078 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 34 | 2022-07-30 | 34 | keep | 0 | Jul | 2022 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-07-30 09:03 | 2022-07-30 12:18 | 30 | 3:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L VIENTOS | C22073000079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2022-07-30 | 5850 | keep | 0 | Jul | 2022 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-30 09:06 | 2022-07-30 09:07 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1907-05 | S22073000097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 2956 | keep | 0 | Jul | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
FAJARDO | 2022-07-30 09:07 | 2022-07-30 11:27 | 50 | 2:20 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22073000035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-07-30 | 7000 | keep | 0 | Jul | 2022 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-30 09:11 | 2022-07-30 13:07 | 9 | 3:56 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B22073000030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 236 | 2022-07-30 | 2124 | keep | 0 | Jul | 2022 | 0.0014466 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-07-30 09:12 | 2022-07-30 10:59 | 20 | 1:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22073000098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-07-30 | 2140 | keep | 0 | Jul | 2022 | 0.0014575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-07-30 09:13 | 2022-07-30 09:14 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22073000088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 1702 | keep | 0 | Jul | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
VEGA BAJA | 2022-07-30 09:15 | 2022-07-30 11:30 | 12 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR REPARAR SECUNDARIAS PERSONAL LOW VOLTAGE REALIZARA LOS TRABAJOS | A22073000006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2022-07-30 | 1620 | keep | 0 | Jul | 2022 | 0.0011034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-30 09:34 | 2022-07-30 10:28 | 20 | 0:54 | P | ANIMAL | 1X40 EN C/L POR CONTACTO DE AVE | B22073000037 | New_Event | Animals | Include | Include | Wildlife | 54 | 2022-07-30 | 1080 | keep | 0 | Jul | 2022 | 0.00073558 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-07-30 09:43 | 2022-08-01 11:17 | 50 | 49:34 | P | CONDUCTOR ARRIADO O CRUZADO | SE INSTALARON AISLADORES PARA DESPEGAR PUENTES DEL POSTE | R22073000057 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 2974 | 2022-07-30 | 148700 | keep | 0 | Jul | 2022 | 0.10128 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-07-30 09:50 | 2022-07-30 19:17 | 40 | 9:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C22073000104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 567 | 2022-07-30 | 22680 | keep | 0 | Jul | 2022 | 0.015447 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-30 09:51 | 2022-07-30 18:59 | 50 | 9:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA | S22073000111 | New_Event | Cutout Failure | Include | Include | Equipment | 548 | 2022-07-30 | 27400 | keep | 0 | Jul | 2022 | 0.018662 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-07-30 10:03 | 2022-07-30 15:12 | 6 | 5:09 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22073000011 | New_Event | Primary Wire Break | Include | Include | Equipment | 309 | 2022-07-30 | 1854 | keep | 0 | Jul | 2022 | 0.0012628 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-07-30 10:07 | 2022-07-30 12:45 | 15 | 2:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L FUERTE VIENTO | P22073000141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 158 | 2022-07-30 | 2370 | keep | 0 | Jul | 2022 | 0.0016142 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-07-30 10:13 | 2022-07-30 12:09 | 8 | 1:56 | P | SECUNDARIA/OTROS | SE ABRIO EN T-21, SE REMPLAZO PEDESTAL Y BARRAS | B22073000048 | New_Event |  |  |  |  | 116 | 2022-07-30 | 928 | keep | 0 | Jul | 2022 | 0.00063206 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-07-30 10:17 | 2022-07-30 15:36 | 44 | 5:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L VIENTOS | C22073000115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 319 | 2022-07-30 | 14036 | keep | 0 | Jul | 2022 | 0.0095599 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BARRANQUITAS | 2022-07-30 10:18 | 2022-07-30 16:08 | 40 | 5:50 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO | C22073000116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-07-30 | 14000 | keep | 0 | Jul | 2022 | 0.0095353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-30 10:20 | 2022-07-30 10:56 | 681 | 0:36 | T | DESGANCHE | SE ABRIO N/O Y SE SECCIONALIZO AVERIA SE REALIZO DESGANCHE PRIMARIO SE CERRO BKR POR CONTROL 80% EN SERVICIO | S22073000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-07-30 | 24516 | keep | 0 | Jul | 2022 | 0.016698 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
YAUCO | 2022-07-30 10:39 | 2022-07-30 16:05 | 150 | 5:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22073000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-07-30 | 48900 | keep | 0 | Jul | 2022 | 0.033306 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-07-30 10:43 | 2022-07-30 12:42 | 40 | 1:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 EN C/L POR LLUVIAS | B22073000053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 119 | 2022-07-30 | 4760 | keep | 0 | Jul | 2022 | 0.003242 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-30 10:56 | 2022-07-30 12:02 | 544 | 1:06 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO | S22073000117 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-07-30 | 35904 | keep | 0 | Jul | 2022 | 0.024454 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-07-30 10:56 | 2022-07-30 12:02 | 1310 | 1:06 | T | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO CARGA POR EL 1520-02 | S22073000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-07-30 | 86460 | keep | 0 | Jul | 2022 | 0.058888 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-07-30 11:07 | 2022-07-30 13:39 | 100 | 2:32 | P | DESGANCHE | 2 X 100 EN C/L | S22073000139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-07-30 | 15200 | keep | 0 | Jul | 2022 | 0.010353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-07-30 11:09 | 2022-07-30 21:29 | 20 | 10:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA QUEMADO | B22073000060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 620 | 2022-07-30 | 12400 | keep | 0 | Jul | 2022 | 0.0084456 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-07-30 11:10 | 2022-07-30 14:10 | 10 | 3:00 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE ENDEREZO POSTE Y SE REPARO SECUNDARIA | S22073000142 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 180 | 2022-07-30 | 1800 | keep | 0 | Jul | 2022 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-07-30 11:17 | 2022-07-30 12:22 | 4 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C22073000147 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-07-30 | 260 | keep | 0 | Jul | 2022 | 0.00017708 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-07-30 11:24 | 2022-07-30 13:48 | 22 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L VIENTOS FUERTES | C22073000148 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2022-07-30 | 3168 | keep | 0 | Jul | 2022 | 0.0021577 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2022-07-30 11:35 | 2022-07-30 14:41 | 5 | 3:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA FIJAR BAJANTE SECUNDARIO | P22073000156 | New_Event | Secondary Wire Break | Include | Include | Equipment | 186 | 2022-07-30 | 930 | keep | 0 | Jul | 2022 | 0.00063342 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-07-30 11:49 | 2022-07-31 08:45 | 100 | 20:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU | M22073000065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1256 | 2022-07-30 | 125600 | keep | 0 | Jul | 2022 | 0.085546 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-07-30 11:50 | 2022-07-30 12:21 | 6 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA DE PEDESTAL | R22072900028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2022-07-30 | 186 | keep | 0 | Jul | 2022 | 0.00012668 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-07-30 11:51 | 2022-07-30 16:40 | 50 | 4:49 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22073000066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-07-30 | 14450 | keep | 0 | Jul | 2022 | 0.0098418 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-30 12:10 | 2022-07-30 12:11 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22073000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 1362 | keep | 0 | Jul | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2022-07-30 12:11 | 2022-07-30 14:29 | 100 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 65 EN C/L | B22073000070 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-07-30 | 13800 | keep | 0 | Jul | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-07-30 12:14 | 2022-07-30 13:42 | 125 | 1:28 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO | C22073000162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-07-30 | 11000 | keep | 0 | Jul | 2022 | 0.007492 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BARRANQUITAS | 2022-07-30 12:20 | 2022-07-30 14:48 | 40 | 2:28 | P | DESGANCHE | 1 X 40 EN C/L SE RETIRO RAMA | C22073000166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-07-30 | 5920 | keep | 0 | Jul | 2022 | 0.0040321 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-07-30 12:24 | 2022-07-30 15:22 | 35 | 2:58 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22073000169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-07-30 | 6230 | keep | 0 | Jul | 2022 | 0.0042432 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-07-30 12:28 | 2022-07-31 10:18 | 11 | 21:50 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO 25 KVA X 37.5 KVA | C22073000165 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1310 | 2022-07-30 | 14410 | keep | 0 | Jul | 2022 | 0.0098146 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-07-30 12:34 | 2022-07-30 16:40 | 221 | 4:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22073000076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2022-07-30 | 54366 | keep | 0 | Jul | 2022 | 0.037028 | 0.00015052 | Sustained | FALSE | FALSE | Not_TMED_Event | 221
HUMACAO | 2022-07-30 12:42 | 2022-07-30 14:39 | 6 | 1:57 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYOS | C22073000177 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-07-30 | 702 | keep | 0 | Jul | 2022 | 0.00047813 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-07-30 12:42 | 2022-07-30 17:16 | 1 | 4:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22073000019 | New_Event | Primary Wire Break | Include | Include | Equipment | 274 | 2022-07-30 | 274 | keep | 0 | Jul | 2022 | 0.00018662 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-07-30 12:51 | 2022-07-30 14:27 | 25 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22073000179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-07-30 | 2400 | keep | 0 | Jul | 2022 | 0.0016346 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-07-30 12:51 | 2022-07-30 18:39 | 85 | 5:48 | P | CAUSAS EXTERNAS | 1X 140 C/L LINEA PRIMARIA CRUZADA CON MENSAJERO CABLE TELEFONO | P22073000162 | New_Event | Damage From Public | Include | Include | Public | 348 | 2022-07-30 | 29580 | keep | 0 | Jul | 2022 | 0.020147 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2022-07-30 12:51 | 2022-07-30 12:53 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22073000081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-07-30 | 6774 | keep | 0 | Jul | 2022 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2022-07-30 12:53 | 2022-07-30 14:20 | 311 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B22073000089 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-07-30 | 27057 | keep | 0 | Jul | 2022 | 0.018428 | 0.00021182 | Sustained | FALSE | FALSE | Not_TMED_Event | 311
BAYAMON | 2022-07-30 12:54 | 2022-07-30 17:59 | 15 | 5:05 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | B22073000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-07-30 | 4575 | keep | 0 | Jul | 2022 | 0.003116 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-07-30 12:55 | 2022-07-30 15:14 | 277 | 2:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN C/L | P22073000163 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2022-07-30 | 38503 | keep | 0 | Jul | 2022 | 0.026224 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
SAN JUAN | 2022-07-30 12:56 | 2022-07-30 16:03 | 120 | 3:07 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S22073000212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-07-30 | 22440 | keep | 0 | Jul | 2022 | 0.015284 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2022-07-30 13:25 | 2022-07-30 15:03 | 7 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIAS | C22073000194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2022-07-30 | 686 | keep | 0 | Jul | 2022 | 0.00046723 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-07-30 13:28 | 2022-07-30 17:56 | 42 | 4:28 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S22073000230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2022-07-30 | 11256 | keep | 0 | Jul | 2022 | 0.0076664 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2022-07-30 13:36 | 2022-07-30 15:55 | 30 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22073000099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-07-30 | 4170 | keep | 0 | Jul | 2022 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-07-30 13:36 | 2022-07-31 15:12 | 100 | 25:36 | P | CABLE SOTERRADO AVERIADO | 3 X 40 EN RISER HACIA SU-2A-4 SE REEMPLAZO CABLE SOTERRADO DEL SU-2A-4 AL SU-2A-3 | R22073000047 | New_Event | UG Cable Fault | Include | Include | Equipment | 1536 | 2022-07-30 | 153600 | keep | 0 | Jul | 2022 | 0.10462 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-07-30 13:42 | 2022-07-31 11:58 | 60 | 22:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22073000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1336 | 2022-07-30 | 80160 | keep | 0 | Jul | 2022 | 0.054597 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-30 13:49 | 2022-07-30 13:50 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22073000101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 5961 | keep | 0 | Jul | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-07-30 14:02 | 2022-07-30 17:00 | 50 | 2:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22073000102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2022-07-30 | 8900 | keep | 0 | Jul | 2022 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-07-30 14:02 | 2022-07-30 15:44 | 65 | 1:42 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYOS | C22073000020 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2022-07-30 | 6630 | keep | 0 | Jul | 2022 | 0.0045157 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-07-30 14:06 | 2022-07-30 14:10 | 1483 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 20% DEL 1204-05 CERRADO POR SCADA | S2207300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-30 | 5932 | keep | 0 | Jul | 2022 | 0.0040403 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-07-30 14:06 | 2022-07-30 14:10 | 2042 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 20% DEL 1204-05 CERRADO POR SCADA | S2207300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-30 | 8168 | keep | 0 | Jul | 2022 | 0.0055632 | 0.0013908 | Momentary | FALSE | FALSE | Not_TMED_Event | 2042
SAN JUAN | 2022-07-30 14:06 | 2022-07-30 14:10 | 5290 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 20% DEL 1204-05 CERRADO POR SCADA | S2207300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-07-30 | 21160 | keep | 0 | Jul | 2022 | 0.014412 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
FAJARDO | 2022-07-30 14:06 | 2022-07-30 14:55 | 8 | 0:49 | P | NO SE REPORTO CAUSA | 1 X 10 XMR | R22073000048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2022-07-30 | 392 | keep | 0 | Jul | 2022 | 0.00026699 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-07-30 14:06 | 2022-07-30 18:35 | 50 | 4:29 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO NEUTRAL PRIMARIO Y SE ABRIO PUENTES PARA SECCIONALIZAR LINEA ZAFADA DE AISLADOR (PORTON CERRADO NO HAY ACCESO), QUEDA UN SOLO CLIENTE SIN SERVICIO | A22073000029 | New_Event | Primary Wire Break | Include | Include | Equipment | 269 | 2022-07-30 | 13450 | keep | 0 | Jul | 2022 | 0.0091607 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-30 14:09 | 2022-07-30 16:41 | 100 | 2:32 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S22073000255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-07-30 | 15200 | keep | 0 | Jul | 2022 | 0.010353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-07-30 14:10 | 2022-07-30 14:13 | 4028 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22073000107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-07-30 | 12084 | keep | 0 | Jul | 2022 | 0.0082304 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
MAYAGÃœEZ | 2022-07-30 14:11 | 2022-07-31 11:00 | 22 | 20:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22073000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1249 | 2022-07-30 | 27478 | keep | 0 | Jul | 2022 | 0.018715 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2022-07-30 14:15 | 2022-07-30 14:45 | 12 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22073000067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-07-30 | 360 | keep | 0 | Jul | 2022 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-07-30 14:16 | 2022-07-31 11:09 | 30 | 20:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22073000087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1253 | 2022-07-30 | 37590 | keep | 0 | Jul | 2022 | 0.025602 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-30 14:20 | 2022-07-30 15:20 | 15 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA | B22073000069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-07-30 | 900 | keep | 0 | Jul | 2022 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-07-30 14:23 | 2022-07-30 16:13 | 80 | 1:50 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22073000208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-07-30 | 8800 | keep | 0 | Jul | 2022 | 0.0059936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-07-30 14:32 | 2022-07-30 14:33 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22073000090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 312 | keep | 0 | Jul | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
GUAYAMA | 2022-07-30 14:34 | 2022-07-30 14:35 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22073000169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 3718 | keep | 0 | Jul | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2022-07-30 14:34 | 2022-07-30 16:20 | 50 | 1:46 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22073000091 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 106 | 2022-07-30 | 5300 | keep | 0 | Jul | 2022 | 0.0036098 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-30 14:38 | 2022-07-31 09:30 | 18 | 18:52 | P | DESGANCHE | 1 X 40 Y 1 X 20 C/L DESGANCHE | B22073000164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1132 | 2022-07-30 | 20376 | keep | 0 | Jul | 2022 | 0.013878 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-07-30 15:10 | 2022-07-31 09:39 | 80 | 18:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22073000096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1109 | 2022-07-30 | 88720 | keep | 0 | Jul | 2022 | 0.060427 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-07-30 15:10 | 2022-07-30 16:50 | 5 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22073000060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2022-07-30 | 500 | keep | 0 | Jul | 2022 | 0.00034055 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-07-30 15:12 | 2022-07-30 15:52 | 705 | 0:40 | S | DESGANCHE | DISPARO DEL INTERRUPTOR PORTATIL EL CUAL LLEVA TODA LA CARGA DE LA SUBESTACION SE RETIRO BAMBUS SOBRE LAS LINEAS DEL ALIMENTADOR 8104-02 | A22073000035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-07-30 | 28200 | keep | 0 | Jul | 2022 | 0.019207 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2022-07-30 15:12 | 2022-07-30 16:14 | 1521 | 1:02 | S | DESGANCHE | DISPARO DEL INTERRUPTOR PORTATIL EL CUAL LLEVA TODA LA CARGA DE LA SUBESTACION SE RETIRO BAMBUS SOBRE LAS LINEAS DEL ALIMENTADOR 8104-02 | A22073000035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-07-30 | 94302 | keep | 0 | Jul | 2022 | 0.064229 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2022-07-30 15:12 | 2022-07-30 15:52 | 882 | 0:40 | S | DESGANCHE | DISPARO DEL INTERRUPTOR PORTATIL EL CUAL LLEVA TODA LA CARGA DE LA SUBESTACION SE RETIRO BAMBUS SOBRE LAS LINEAS DEL ALIMENTADOR 8104-02 | A22073000035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-07-30 | 35280 | keep | 0 | Jul | 2022 | 0.024029 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
ARECIBO | 2022-07-30 15:14 | 2022-07-30 17:01 | 50 | 1:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22073000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-07-30 | 5350 | keep | 0 | Jul | 2022 | 0.0036439 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-07-30 15:18 | 2022-07-30 15:19 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22073000099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 1192 | keep | 0 | Jul | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
VEGA BAJA | 2022-07-30 15:33 | 2022-07-30 17:10 | 12 | 1:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22073000116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 97 | 2022-07-30 | 1164 | keep | 0 | Jul | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-07-30 15:45 | 2022-08-01 14:13 | 16 | 46:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | S22073000304 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2788 | 2022-07-30 | 44608 | keep | 0 | Jul | 2022 | 0.030382 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-07-30 15:53 | 2022-07-30 15:54 | 1085 | 0:01 | T | PROTECCION DEFECTUOSA | DISPARO AL NORMALIZAR G/R, SE CERRO POR SCADA, HC-73998 @ RELES PARA VERIFICAR | S22073000000 | New_Event | Protection Miscoordination | Include | Include | Other | 1 | 2022-07-30 | 1085 | keep | 0 | Jul | 2022 | 0.00073899 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
CAGUAS | 2022-07-30 15:53 | 2022-07-30 18:02 | 30 | 2:09 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22073000222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-07-30 | 3870 | keep | 0 | Jul | 2022 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-07-30 16:04 | 2022-07-30 17:38 | 1 | 1:34 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22073000120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-07-30 | 94 | keep | 0 | Jul | 2022 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-07-30 16:05 | 2022-07-30 16:06 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22073000109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 3458 | keep | 0 | Jul | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
FAJARDO | 2022-07-30 16:08 | 2022-07-30 19:14 | 36 | 3:06 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO BAMBUAS | R22073000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-07-30 | 6696 | keep | 0 | Jul | 2022 | 0.0045606 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2022-07-30 16:09 | 2022-07-30 20:30 | 6 | 4:21 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C22073000224 | New_Event | Animals | Include | Include | Wildlife | 261 | 2022-07-30 | 1566 | keep | 0 | Jul | 2022 | 0.0010666 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-07-30 16:30 | 2022-07-30 18:22 | 200 | 1:52 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22073000119 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 112 | 2022-07-30 | 22400 | keep | 0 | Jul | 2022 | 0.015257 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-07-30 16:40 | 2022-07-30 19:20 | 80 | 2:40 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L CERRO PUENTE Y REMPLAZO PORTAFUSIBLE | C22073000226 | New_Event | Primary Wire Break | Include | Include | Equipment | 160 | 2022-07-30 | 12800 | keep | 0 | Jul | 2022 | 0.008718 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-07-30 16:55 | 2022-07-30 19:10 | 120 | 2:15 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22073000132 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 135 | 2022-07-30 | 16200 | keep | 0 | Jul | 2022 | 0.011034 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-07-30 16:59 | 2022-07-30 19:14 | 4 | 2:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A22073000069 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2022-07-30 | 540 | keep | 0 | Jul | 2022 | 0.00036779 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-07-30 17:23 | 2022-07-31 10:25 | 63 | 17:02 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22073000228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1022 | 2022-07-30 | 64386 | keep | 0 | Jul | 2022 | 0.043853 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
VEGA BAJA | 2022-07-30 17:39 | 2022-07-30 22:35 | 50 | 4:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTES VIENTOS | A22073000071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 296 | 2022-07-30 | 14800 | keep | 0 | Jul | 2022 | 0.01008 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-07-30 17:50 | 2022-07-31 11:30 | 5 | 17:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22073000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1060 | 2022-07-30 | 5300 | keep | 0 | Jul | 2022 | 0.0036098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-07-30 18:15 | 2022-07-30 19:19 | 121 | 1:04 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/LS | R22073000063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-07-30 | 7744 | keep | 0 | Jul | 2022 | 0.0052744 | 8.2413e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 121
AGUADILLA | 2022-07-30 18:35 | 2022-07-31 11:15 | 1 | 16:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES ROTOS Y SE CERRO PUENTES | A22073000002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1000 | 2022-07-30 | 1000 | keep | 0 | Jul | 2022 | 0.0006811 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-07-30 18:36 | 2022-07-31 20:00 | 10 | 25:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | A22073000079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1524 | 2022-07-30 | 15240 | keep | 0 | Jul | 2022 | 0.01038 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-07-30 19:19 | 2022-07-30 19:20 | 4622 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22073000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 4622 | keep | 0 | Jul | 2022 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
VEGA BAJA | 2022-07-30 19:22 | 2022-07-31 10:17 | 30 | 14:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22073000084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 895 | 2022-07-30 | 26850 | keep | 0 | Jul | 2022 | 0.018287 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-07-30 19:45 | 2022-07-31 14:00 | 40 | 18:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22073000168 | New_Event | Primary Wire Break | Include | Include | Equipment | 1095 | 2022-07-30 | 43800 | keep | 0 | Jul | 2022 | 0.029832 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-07-30 19:55 | 2022-07-30 21:17 | 6 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | C22073000258 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-07-30 | 492 | keep | 0 | Jul | 2022 | 0.0003351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-07-30 19:59 | 2022-07-31 04:36 | 120 | 8:37 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M22073000170 | New_Event | Primary Wire Break | Include | Include | Equipment | 517 | 2022-07-30 | 62040 | keep | 0 | Jul | 2022 | 0.042255 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-07-30 20:19 | 2022-07-30 21:53 | 19 | 1:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO PORTAFUSIBLES | R22073000283 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2022-07-30 | 1786 | keep | 0 | Jul | 2022 | 0.0012164 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
AGUADILLA | 2022-07-30 20:24 | 2022-07-30 22:40 | 6 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A22073000089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2022-07-30 | 816 | keep | 0 | Jul | 2022 | 0.00055577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-07-30 20:27 | 2022-07-30 21:33 | 40 | 1:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B22073000144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-07-30 | 2640 | keep | 0 | Jul | 2022 | 0.0017981 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-07-30 20:54 | 2022-07-31 06:34 | 37 | 9:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22073000263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 580 | 2022-07-30 | 21460 | keep | 0 | Jul | 2022 | 0.014616 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
YAUCO | 2022-07-30 21:41 | 2022-07-31 10:37 | 150 | 12:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22073000198 | New_Event | Cutout Failure | Include | Include | Equipment | 776 | 2022-07-30 | 116400 | keep | 0 | Jul | 2022 | 0.07928 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-07-30 21:47 | 2022-07-30 21:48 | 4622 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22073000000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-30 | 4622 | keep | 0 | Jul | 2022 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
SAN JUAN | 2022-07-30 22:09 | 2022-07-31 13:00 | 9 | 14:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | S22073000400 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 891 | 2022-07-30 | 8019 | keep | 0 | Jul | 2022 | 0.0054617 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2022-07-30 22:15 | 2022-07-30 22:46 | 15 | 0:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA DE XMR | C22073000269 | New_Event | Primary Wire Break | Include | Include | Equipment | 31 | 2022-07-30 | 465 | keep | 0 | Jul | 2022 | 0.00031671 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-07-30 22:17 | 2022-07-31 09:00 | 125 | 10:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L EN SALIDA DE CONVERTIDOR FUERTES VIENTOS | P22073000199 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 643 | 2022-07-30 | 80375 | keep | 0 | Jul | 2022 | 0.054743 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-07-30 22:30 | 2022-07-31 17:42 | 107 | 19:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | S22073000403 | New_Event | Cutout Failure | Include | Include | Equipment | 1152 | 2022-07-30 | 123264 | keep | 0 | Jul | 2022 | 0.083955 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
VEGA BAJA | 2022-07-30 23:05 | 2022-07-31 14:08 | 12 | 15:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22073000102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 903 | 2022-07-30 | 10836 | keep | 0 | Jul | 2022 | 0.0073804 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-07-30 23:06 | 2022-07-31 12:45 | 40 | 13:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22073000228 | New_Event | Cutout Failure | Include | Include | Equipment | 819 | 2022-07-30 | 32760 | keep | 0 | Jul | 2022 | 0.022313 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-07-30 23:38 | 2022-07-31 10:58 | 10 | 11:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMLAZO CAJA PRIMARIA Y SE REEMPLAZO BAJANTE SECUNDARIO 1 X 20 EN XMR | S22073000410 | New_Event | Cutout Failure | Include | Include | Equipment | 680 | 2022-07-30 | 6800 | keep | 0 | Jul | 2022 | 0.0046314 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-07-30 23:49 | 2022-07-31 11:30 | 70 | 11:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22073000104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 701 | 2022-07-30 | 49070 | keep | 0 | Jul | 2022 | 0.033421 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-07-31 01:34 | 2022-07-31 09:31 | 17 | 7:57 | P | ANIMAL | 1 X 20 EN RISER CRUCE X REPTIL | R22073100003 | New_Event | Animals | Include | Include | Wildlife | 477 | 2022-07-31 | 8109 | keep | 0 | Jul | 2022 | 0.005523 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
PONCE | 2022-07-31 02:30 | 2022-07-31 02:31 | 2696 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22073100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 2696 | keep | 0 | Jul | 2022 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
FAJARDO | 2022-07-31 02:54 | 2022-07-31 02:55 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 2722 | keep | 0 | Jul | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2022-07-31 03:57 | 2022-07-31 07:38 | 118 | 3:41 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R22073100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-07-31 | 26078 | keep | 0 | Jul | 2022 | 0.017762 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
VEGA BAJA | 2022-07-31 04:23 | 2022-07-31 08:20 | 200 | 3:57 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 Y 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22073100001 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 237 | 2022-07-31 | 47400 | keep | 0 | Jul | 2022 | 0.032284 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-07-31 04:43 | 2022-07-31 12:35 | 40 | 7:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22073100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 472 | 2022-07-31 | 18880 | keep | 0 | Jul | 2022 | 0.012859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-07-31 06:34 | 2022-07-31 09:35 | 110 | 3:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22073100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-07-31 | 19910 | keep | 0 | Jul | 2022 | 0.013561 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
CANOVANAS | 2022-07-31 06:51 | 2022-07-31 12:41 | 52 | 5:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22073100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-07-31 | 18200 | keep | 0 | Jul | 2022 | 0.012396 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2022-07-31 06:56 | 2022-07-31 06:57 | 1681 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 1681 | keep | 0 | Jul | 2022 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-07-31 06:56 | 2022-07-31 06:57 | 1598 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 1598 | keep | 0 | Jul | 2022 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BARRANQUITAS | 2022-07-31 07:10 | 2022-07-31 09:44 | 40 | 2:34 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22073100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-07-31 | 6160 | keep | 0 | Jul | 2022 | 0.0041955 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-07-31 07:17 | 2022-07-31 07:18 | 2435 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL 1909-08 QUE LLEVA 1907-05 | S22073100000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-07-31 | 2435 | keep | 0 | Jul | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-31 07:17 | 2022-07-31 07:18 | 2956 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE 1909-08 QUE LLEVA 1907-05 | S22073100000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-07-31 | 2956 | keep | 0 | Jul | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-07-31 07:18 | 2022-07-31 10:56 | 14 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE CERRO PUENTE DE LINEA A CAJA | S22073100041 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 218 | 2022-07-31 | 3052 | keep | 0 | Jul | 2022 | 0.0020787 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-07-31 07:18 | 2022-07-31 10:56 | 18 | 3:38 | P | EMPALME SOTERRADO AVERIADO | SE REMPARO EMPALME AVERIADO Y SE REEMPLAZO PISTOLA EN VS-3 | S22072900148 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 218 | 2022-07-31 | 3924 | keep | 0 | Jul | 2022 | 0.0026726 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-07-31 07:21 | 2022-07-31 07:22 | 57 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | S22073100000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-07-31 | 57 | keep | 0 | Jul | 2022 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2022-07-31 07:22 | 2022-07-31 14:11 | 25 | 6:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN C/L 3 X 40 EN RISER SE REMPLAZAO CAJA PRIMARIA Y 2 PARARRAYOS | B22073100000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 409 | 2022-07-31 | 10225 | keep | 0 | Jul | 2022 | 0.0069642 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-07-31 07:47 | 2022-08-01 09:25 | 200 | 25:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22073100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1538 | 2022-07-31 | 307600 | keep | 0 | Jul | 2022 | 0.2095 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-07-31 07:50 | 2022-07-31 12:07 | 175 | 4:17 | P | DESGANCHE | 3 X 65 Y 1 X 50 EN C/LS SE DESGANCHO LEVANTO CONDUCTOR Y REMPLAZO CAJA QUEMADA | C22073100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-07-31 | 44975 | keep | 0 | Jul | 2022 | 0.030632 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CANOVANAS | 2022-07-31 08:11 | 2022-07-31 08:12 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22073100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 2675 | keep | 0 | Jul | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
BAYAMON | 2022-07-31 08:20 | 2022-07-31 09:05 | 34 | 0:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L AISLADOR | B22073100009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 45 | 2022-07-31 | 1530 | keep | 0 | Jul | 2022 | 0.0010421 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-07-31 08:24 | 2022-07-31 08:44 | 34 | 0:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22073100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-07-31 | 680 | keep | 0 | Jul | 2022 | 0.00046314 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
AGUADILLA | 2022-07-31 08:28 | 2022-07-31 20:45 | 20 | 12:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22073100016 | New_Event | Cutout Failure | Include | Include | Equipment | 737 | 2022-07-31 | 14740 | keep | 0 | Jul | 2022 | 0.010039 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-07-31 08:29 | 2022-07-31 08:30 | 661 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22073100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 661 | keep | 0 | Jul | 2022 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
MAYAGÃœEZ | 2022-07-31 08:33 | 2022-07-31 10:35 | 30 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER MAL TIEMPO VIENTOS FUERTES | M22073100024 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2022-07-31 | 3660 | keep | 0 | Jul | 2022 | 0.0024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-07-31 08:40 | 2022-07-31 15:40 | 60 | 7:00 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22073100025 | New_Event | Primary Wire Break | Include | Include | Equipment | 420 | 2022-07-31 | 25200 | keep | 0 | Jul | 2022 | 0.017164 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-07-31 08:54 | 2022-07-31 08:55 | 2448 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22073100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 2448 | keep | 0 | Jul | 2022 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
BAYAMON | 2022-07-31 08:58 | 2022-07-31 12:19 | 93 | 3:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22073100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-07-31 | 18693 | keep | 0 | Jul | 2022 | 0.012732 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
UTUADO | 2022-07-31 08:59 | 2022-07-31 11:15 | 30 | 2:16 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22073100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-07-31 | 4080 | keep | 0 | Jul | 2022 | 0.0027789 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-07-31 09:05 | 2022-07-31 12:26 | 8 | 3:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22073100033 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 201 | 2022-07-31 | 1608 | keep | 0 | Jul | 2022 | 0.0010952 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-07-31 09:08 | 2022-07-31 13:23 | 45 | 4:15 | P | DESGANCHE | 1 X 40 DESGANCHO Y RETEZO LINEAS | C22073100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2022-07-31 | 11475 | keep | 0 | Jul | 2022 | 0.0078156 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-07-31 09:39 | 2022-07-31 14:25 | 60 | 4:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22073100041 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 286 | 2022-07-31 | 17160 | keep | 0 | Jul | 2022 | 0.011688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-07-31 09:54 | 2022-08-01 14:20 | 7 | 28:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 KVA X 37.5KVA | B22073100016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1706 | 2022-07-31 | 11942 | keep | 0 | Jul | 2022 | 0.0081336 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-07-31 10:21 | 2022-07-31 11:29 | 17 | 1:08 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA Y SE REALIZO DESGANCHE | R22073100007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 68 | 2022-07-31 | 1156 | keep | 0 | Jul | 2022 | 0.00078735 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2022-07-31 10:23 | 2022-08-01 10:42 | 50 | 24:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA AVERIADA NO FUNDIO | R22073100073 | New_Event | Cutout Failure | Include | Include | Equipment | 1459 | 2022-07-31 | 72950 | keep | 0 | Jul | 2022 | 0.049686 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-07-31 10:23 | 2022-07-31 12:57 | 25 | 2:34 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22073100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2022-07-31 | 3850 | keep | 0 | Jul | 2022 | 0.0026222 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-07-31 10:32 | 2022-07-31 13:10 | 80 | 2:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REMPLAZO AISLADOR | S22073100078 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 158 | 2022-07-31 | 12640 | keep | 0 | Jul | 2022 | 0.008609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-07-31 10:56 | 2022-07-31 11:36 | 4622 | 0:40 | T | DESGANCHE | CERRADO SE RETIRO TRONCO SECO DE MACHETE Y SE CERRO POR SCADA | B22073100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-07-31 | 184880 | keep | 0 | Jul | 2022 | 0.12592 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2022-07-31 10:56 | 2022-07-31 11:28 | 2435 | 0:32 | T | EMPALME SOTERRADO AVERIADO | DISPARO DEL 1909-08 QUE LLEVA 1907-05 SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S22073100083 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 32 | 2022-07-31 | 77920 | keep | 0 | Jul | 2022 | 0.053071 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-07-31 10:56 | 2022-07-31 11:28 | 2956 | 0:32 | T | EMPALME SOTERRADO AVERIADO | SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA 1909-08 QUE LLEVA 1907-05 | S22073100083 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 32 | 2022-07-31 | 94592 | keep | 0 | Jul | 2022 | 0.064426 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
ARECIBO | 2022-07-31 11:16 | 2022-07-31 13:50 | 4 | 2:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22073100038 | New_Event | Primary Wire Break | Include | Include | Equipment | 154 | 2022-07-31 | 616 | keep | 0 | Jul | 2022 | 0.00041955 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-07-31 11:28 | 2022-07-31 12:53 | 18 | 1:25 | P | EMPALME SOTERRADO AVERIADO | SE REMPARO EMPALME AVERIADO Y SE REEMPLAZO PISTOLA EN VS-3 | S22072900148 | Partial_restoration | UG Cable Splice Failure | Include | Include | Equipment | 85 | 2022-07-31 | 1530 | keep | 0 | Jul | 2022 | 0.0010421 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-07-31 11:46 | 2022-07-31 16:24 | 50 | 4:38 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22073100026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-07-31 | 13900 | keep | 0 | Jul | 2022 | 0.0094672 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-07-31 11:51 | 2022-07-31 15:12 | 120 | 3:21 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22073100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-07-31 | 24120 | keep | 0 | Jul | 2022 | 0.016428 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-07-31 11:53 | 2022-07-31 12:18 | 7 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22073100006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-07-31 | 175 | keep | 0 | Jul | 2022 | 0.00011919 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-07-31 11:53 | 2022-07-31 11:54 | 966 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 966 | keep | 0 | Jul | 2022 | 0.00065794 | 0.00065794 | Momentary | FALSE | FALSE | Not_TMED_Event | 966
BAYAMON | 2022-07-31 12:01 | 2022-07-31 12:20 | 1000 | 0:19 | P | ERROR HUMANO | BY-220731-01 SE REALIZAN OPERACIONES PARA CORREGIR FASEO EN ALIMENTADOR QUE OCASIONABA FASES INVERTIDAS EN CLIENTES TRIFASICOS | B22073100041 | New_Event | Human Error | Include | Include | Other | 19 | 2022-07-31 | 19000 | keep | 0 | Jul | 2022 | 0.012941 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
AGUADILLA | 2022-07-31 12:06 | 2022-07-31 16:00 | 150 | 3:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22073100073 | New_Event | Primary Wire Break | Include | Include | Equipment | 234 | 2022-07-31 | 35100 | keep | 0 | Jul | 2022 | 0.023906 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-07-31 12:13 | 2022-07-31 13:45 | 20 | 1:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO SE ENCONTRO CAUSA | P22073100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2022-07-31 | 1840 | keep | 0 | Jul | 2022 | 0.0012532 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-07-31 12:20 | 2022-07-31 12:48 | 1200 | 0:28 | P | ERROR HUMANO | BY-220731-01 SE REALIZAN OPERACIONES PARA CORREGIR FASEO EN ALIMENTADOR QUE OCASIONABA FASES INVERTIDAS EN CLIENTES TRIFASICOS | B22073100041 | Additional_clients | Human Error | Include | Include | Other | 28 | 2022-07-31 | 33600 | keep | 0 | Jul | 2022 | 0.022885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-07-31 12:29 | 2022-07-31 14:20 | 42 | 1:51 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA | P22073100018 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 111 | 2022-07-31 | 4662 | keep | 0 | Jul | 2022 | 0.0031753 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CAGUAS | 2022-07-31 12:31 | 2022-07-31 13:58 | 1 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22073100038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-07-31 | 87 | keep | 0 | Jul | 2022 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-07-31 12:32 | 2022-07-31 16:20 | 30 | 3:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22073100053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 228 | 2022-07-31 | 6840 | keep | 0 | Jul | 2022 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-07-31 12:35 | 2022-07-31 15:35 | 15 | 3:00 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO LA SECUNDARIA | S22073100135 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 180 | 2022-07-31 | 2700 | keep | 0 | Jul | 2022 | 0.001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-07-31 12:35 | 2022-07-31 15:45 | 157 | 3:10 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA IGUANA CRUZO FASE | P22070310019 | New_Event | Animals | Include | Include | Wildlife | 190 | 2022-07-31 | 29830 | keep | 0 | Jul | 2022 | 0.020317 | 0.00010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 157
BARRANQUITAS | 2022-07-31 12:42 | 2022-07-31 15:06 | 61 | 2:24 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE DE CAJA A LINEA NO FUNDIO | C22073100041 | New_Event | Primary Wire Break | Include | Include | Equipment | 144 | 2022-07-31 | 8784 | keep | 0 | Jul | 2022 | 0.0059827 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BARRANQUITAS | 2022-07-31 12:44 | 2022-07-31 15:59 | 140 | 3:15 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C22073100042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-07-31 | 27300 | keep | 0 | Jul | 2022 | 0.018594 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CANOVANAS | 2022-07-31 12:59 | 2022-07-31 15:34 | 132 | 2:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE DE PENCA | R22073100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-07-31 | 20460 | keep | 0 | Jul | 2022 | 0.013935 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
BAYAMON | 2022-07-31 13:18 | 2022-07-31 13:39 | 5 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22073100009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2022-07-31 | 105 | keep | 0 | Jul | 2022 | 7.1515e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-07-31 13:42 | 2022-07-31 13:43 | 329 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22073100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 329 | keep | 0 | Jul | 2022 | 0.00022408 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
BAYAMON | 2022-07-31 13:45 | 2022-07-31 17:47 | 12 | 4:02 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE CERRO XMR | B22073100099 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 242 | 2022-07-31 | 2904 | keep | 0 | Jul | 2022 | 0.0019779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-07-31 13:55 | 2022-07-31 15:40 | 80 | 1:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22073100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-07-31 | 8400 | keep | 0 | Jul | 2022 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-07-31 14:35 | 2022-07-31 18:16 | 16 | 3:41 | P | ANIMAL | 1 X 30 EN C/L PALOMA | B22073100103 | New_Event | Animals | Include | Include | Wildlife | 221 | 2022-07-31 | 3536 | keep | 0 | Jul | 2022 | 0.0024084 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2022-07-31 14:46 | 2022-07-31 16:10 | 10 | 1:24 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P22073100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-07-31 | 840 | keep | 0 | Jul | 2022 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-07-31 15:03 | 2022-07-31 18:50 | 72 | 3:47 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN CORTE DE LINEA TRANSFORMADOR AVERIADO SE VA A REEMPLAZAR CON EL EVENTO R22073100067 | R22073100045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 227 | 2022-07-31 | 16344 | keep | 0 | Jul | 2022 | 0.011132 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
YAUCO | 2022-07-31 15:06 | 2022-07-31 18:25 | 60 | 3:19 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22073100091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-07-31 | 11940 | keep | 0 | Jul | 2022 | 0.0081323 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-07-31 15:14 | 2022-07-31 16:50 | 12 | 1:36 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | P22073100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-07-31 | 1152 | keep | 0 | Jul | 2022 | 0.00078462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-07-31 15:19 | 2022-07-31 17:06 | 20 | 1:47 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA Y SE RETEZO LINEA PRIMARIA | B22073100106 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 107 | 2022-07-31 | 2140 | keep | 0 | Jul | 2022 | 0.0014575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-07-31 15:22 | 2022-07-31 18:20 | 20 | 2:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22073100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-07-31 | 3560 | keep | 0 | Jul | 2022 | 0.0024247 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-07-31 15:43 | 2022-07-31 15:44 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22073100117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 990 | keep | 0 | Jul | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
HUMACAO | 2022-07-31 15:47 | 2022-07-31 19:22 | 65 | 3:35 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/L SE DESGANCHO | C22073100072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-07-31 | 13975 | keep | 0 | Jul | 2022 | 0.0095183 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-07-31 15:50 | 2022-07-31 21:04 | 5 | 5:14 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | S22073100154 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 314 | 2022-07-31 | 1570 | keep | 0 | Jul | 2022 | 0.0010693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-07-31 16:00 | 2022-07-31 16:01 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22073100075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 6197 | keep | 0 | Jul | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
GUAYAMA | 2022-07-31 16:00 | 2022-07-31 16:01 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22073100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 527 | keep | 0 | Jul | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
FAJARDO | 2022-07-31 16:07 | 2022-07-31 17:06 | 27 | 0:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R22073100053 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2022-07-31 | 1593 | keep | 0 | Jul | 2022 | 0.001085 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2022-07-31 16:26 | 2022-07-31 17:20 | 6 | 0:54 | P | TRANSFORMADOR AVERIADO | ABRIR CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO, TRANSFORMADOR NECESITA SER REEMPLAZADO | R22073100055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 54 | 2022-07-31 | 324 | keep | 0 | Jul | 2022 | 0.00022067 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-07-31 16:59 | 2022-08-01 11:23 | 1 | 18:24 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CAJA EN RISER PARA CERRAR PUENTE PRIMARIO | P22073100036 | New_Event | Primary Wire Break | Include | Include | Equipment | 1104 | 2022-07-31 | 1104 | keep | 0 | Jul | 2022 | 0.00075193 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-07-31 17:00 | 2022-08-01 15:20 | 7 | 22:20 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REPARO SECUNDARIA Y SE DESGANCHO | B22073100111 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1340 | 2022-07-31 | 9380 | keep | 0 | Jul | 2022 | 0.0063887 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-07-31 18:00 | 2022-07-31 18:50 | 30 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22073100111 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-07-31 | 1500 | keep | 0 | Jul | 2022 | 0.0010216 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-07-31 18:26 | 2022-07-31 18:27 | 2067 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR AVE CRUZO BUSHING PRIMARIO EN TRANSFORMADOR | M22073100115 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-07-31 | 2067 | keep | 0 | Jul | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2022-07-31 18:27 | 2022-07-31 21:00 | 6 | 2:33 | P | ANIMAL | 1 X 5 EN TRANSFORMADOR AVE CRUZO BUSHING PRIMARIO | M22073100119 | 1st_after_momentary | Animals | Include | Include | Wildlife | 153 | 2022-07-31 | 918 | keep | 0 | Jul | 2022 | 0.00062525 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-07-31 18:50 | 2022-07-31 22:23 | 23 | 3:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50 KVA AVERIADO | R22073100067 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 213 | 2022-07-31 | 4899 | keep | 0 | Jul | 2022 | 0.0033367 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-07-31 19:09 | 2022-08-01 08:04 | 129 | 12:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LA LINEA | C22073100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 775 | 2022-07-31 | 99975 | keep | 0 | Jul | 2022 | 0.068093 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
CANOVANAS | 2022-07-31 19:11 | 2022-07-31 21:28 | 80 | 2:17 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PUENTE DE CAJA A LINEA | R22073100068 | New_Event | Primary Wire Break | Include | Include | Equipment | 137 | 2022-07-31 | 10960 | keep | 0 | Jul | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-07-31 19:49 | 2022-08-01 06:48 | 28 | 10:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22073100089 | New_Event | Cutout Failure | Include | Include | Equipment | 659 | 2022-07-31 | 18452 | keep | 0 | Jul | 2022 | 0.012568 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2022-07-31 19:51 | 2022-08-01 12:03 | 16 | 16:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22073100131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 972 | 2022-07-31 | 15552 | keep | 0 | Jul | 2022 | 0.010592 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-07-31 19:58 | 2022-08-01 10:40 | 32 | 14:42 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | B22073100132 | New_Event | Primary Wire Break | Include | Include | Equipment | 882 | 2022-07-31 | 28224 | keep | 0 | Jul | 2022 | 0.019223 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2022-07-31 20:09 | 2022-07-31 20:10 | 651 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22073100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 651 | keep | 0 | Jul | 2022 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2022-07-31 20:14 | 2022-08-01 10:58 | 16 | 14:44 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | B22073100134 | New_Event | Primary Wire Break | Include | Include | Equipment | 884 | 2022-07-31 | 14144 | keep | 0 | Jul | 2022 | 0.0096334 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2022-07-31 20:34 | 2022-07-31 20:35 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22073100121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 1192 | keep | 0 | Jul | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
FAJARDO | 2022-07-31 20:37 | 2022-08-01 00:21 | 33 | 3:44 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | R22073100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2022-07-31 | 7392 | keep | 0 | Jul | 2022 | 0.0050347 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
CAGUAS | 2022-07-31 20:45 | 2022-07-31 23:35 | 550 | 2:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22073100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2022-07-31 | 93500 | keep | 0 | Jul | 2022 | 0.063682 | 0.0003746 | Sustained | FALSE | FALSE | Not_TMED_Event | 550
BAYAMON | 2022-07-31 20:58 | 2022-08-01 09:59 | 50 | 13:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-1 1 X 40 EN RISER | S22073100180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 781 | 2022-07-31 | 39050 | keep | 0 | Jul | 2022 | 0.026597 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-07-31 20:59 | 2022-08-01 14:56 | 12 | 17:57 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22073100181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1077 | 2022-07-31 | 12924 | keep | 0 | Jul | 2022 | 0.0088025 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-07-31 21:12 | 2022-08-01 07:15 | 10 | 10:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | C22073100104 | New_Event | Cutout Failure | Include | Include | Equipment | 603 | 2022-07-31 | 6030 | keep | 0 | Jul | 2022 | 0.004107 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-07-31 21:20 | 2022-08-01 13:39 | 29 | 16:19 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1X10 EN XMR SE DESCRUZO SECUNDARIA | C22073100105 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 979 | 2022-07-31 | 28391 | keep | 0 | Jul | 2022 | 0.019337 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
GUAYAMA | 2022-07-31 21:48 | 2022-08-01 01:45 | 316 | 3:57 | P | NO SE REPORTO CAUSA | 1 X 140 EN CONVERTIDOR NO CAUSA | P22073100045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2022-07-31 | 74892 | keep | 0 | Jul | 2022 | 0.051009 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
MAYAGÃœEZ | 2022-07-31 22:30 | 2022-08-01 02:48 | 50 | 4:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22073100126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 258 | 2022-07-31 | 12900 | keep | 0 | Jul | 2022 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-07-31 22:44 | 2022-08-01 07:48 | 12 | 9:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22073100177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 544 | 2022-07-31 | 6528 | keep | 0 | Jul | 2022 | 0.0044462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-07-31 22:53 | 2022-08-01 02:39 | 120 | 3:46 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C22073100114 | New_Event | Animals | Include | Include | Wildlife | 226 | 2022-07-31 | 27120 | keep | 0 | Jul | 2022 | 0.018471 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-07-31 23:08 | 2022-08-01 13:15 | 150 | 14:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22073100128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 847 | 2022-07-31 | 127050 | keep | 0 | Jul | 2022 | 0.086533 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-07-31 23:09 | 2022-07-31 23:10 | 4098 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22073100076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-07-31 | 4098 | keep | 0 | Jul | 2022 | 0.0027911 | 0.0027911 | Momentary | FALSE | FALSE | Not_TMED_Event | 4098
FAJARDO | 2022-07-31 23:19 | 2022-08-01 04:21 | 500 | 5:02 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO PARTIDO | R22073100080 | New_Event | Primary Wire Break | Include | Include | Equipment | 302 | 2022-07-31 | 151000 | keep | 0 | Jul | 2022 | 0.10285 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
YAUCO | 2022-08-01 01:01 | 2022-08-01 07:48 | 2952 | 6:47 | T | CAUSAS EXTERNAS | DISPARO DE INTERRUPTOR POR POSTES PRIMARIOS PARTIDOS. SE ABRIERON PUENTES PRIMARIOS PARA SECCIONALIZAR ACCIDENTE VEHICULAR | M22080100002 | New_Event | Damage From Public | Include | Include | Public | 407 | 2022-08-01 | 1201464 | keep | 0 | Aug | 2022 | 0.81831 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
CAGUAS | 2022-08-01 01:27 | 2022-08-01 08:40 | 138 | 7:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22080100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2022-08-01 | 59754 | keep | 0 | Aug | 2022 | 0.040698 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
MAYAGÃœEZ | 2022-08-01 01:32 | 2022-08-01 05:14 | 80 | 3:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22080100011 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2022-08-01 | 17760 | keep | 0 | Aug | 2022 | 0.012096 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-08-01 01:40 | 2022-08-01 09:25 | 16 | 7:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP | C22080100009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 465 | 2022-08-01 | 7440 | keep | 0 | Aug | 2022 | 0.0050674 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-08-01 02:00 | 2022-08-01 08:21 | 30 | 6:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | B22080100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 381 | 2022-08-01 | 11430 | keep | 0 | Aug | 2022 | 0.0077849 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-08-01 02:54 | 2022-08-01 02:55 | 693 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 693 | keep | 0 | Aug | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2022-08-01 06:17 | 2022-08-01 09:15 | 10 | 2:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL SECUNDARIO PARTIDO | M22080100024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 178 | 2022-08-01 | 1780 | keep | 0 | Aug | 2022 | 0.0012123 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-01 06:29 | 2022-08-01 09:03 | 10 | 2:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080100003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 154 | 2022-08-01 | 1540 | keep | 0 | Aug | 2022 | 0.0010489 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-01 06:33 | 2022-08-01 08:49 | 25 | 2:16 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M22080100025 | New_Event | Animals | Include | Include | Wildlife | 136 | 2022-08-01 | 3400 | keep | 0 | Aug | 2022 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-01 06:37 | 2022-08-01 12:50 | 4 | 6:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2022-08-01 | 1492 | keep | 0 | Aug | 2022 | 0.0010162 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-08-01 06:44 | 2022-08-01 09:20 | 50 | 2:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-08-01 | 7800 | keep | 0 | Aug | 2022 | 0.0053125 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-01 06:48 | 2022-08-02 09:08 | 1 | 26:20 | P | DESGANCHE | SE REALIZO DESGANCHE Y 1 X 100 EN C/L | S22080100010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1580 | 2022-08-01 | 1580 | keep | 0 | Aug | 2022 | 0.0010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-01 07:10 | 2022-08-01 14:55 | 1 | 7:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M22080100027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 465 | 2022-08-01 | 465 | keep | 0 | Aug | 2022 | 0.00031671 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-01 07:13 | 2022-08-01 14:23 | 40 | 7:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22080100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 430 | 2022-08-01 | 17200 | keep | 0 | Aug | 2022 | 0.011715 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-01 07:28 | 2022-08-01 09:26 | 50 | 1:58 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22080100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-08-01 | 5900 | keep | 0 | Aug | 2022 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-01 07:31 | 2022-08-01 19:15 | 23 | 11:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 SE REMPLAZO CAJA PRIMARIA | S22080100018 | New_Event | Cutout Failure | Include | Include | Equipment | 704 | 2022-08-01 | 16192 | keep | 0 | Aug | 2022 | 0.011028 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
MAYAGÃœEZ | 2022-08-01 07:34 | 2022-08-01 16:00 | 10 | 8:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KV @ 4 KV POR UNO DE LA MISMA CAPACIDAD | M22080100030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 506 | 2022-08-01 | 5060 | keep | 0 | Aug | 2022 | 0.0034463 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-01 07:37 | 2022-08-01 10:35 | 30 | 2:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22080100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-08-01 | 5340 | keep | 0 | Aug | 2022 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-01 07:38 | 2022-08-01 08:54 | 10 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22080100041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2022-08-01 | 760 | keep | 0 | Aug | 2022 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-08-01 07:48 | 2022-08-01 13:30 | 2805 | 5:42 | P | CAUSAS EXTERNAS | SE TRANSFIRIO PARTE DE LA CARGA DEL 6501-04 AL 6501-01 | M22080100032 | Partial_restoration | Damage From Public | Include | Include | Public | 342 | 2022-08-01 | 959310 | keep | 0 | Aug | 2022 | 0.65338 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-01 07:54 | 2022-08-01 07:55 | 661 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22080100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 661 | keep | 0 | Aug | 2022 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
YAUCO | 2022-08-01 07:55 | 2022-08-01 13:33 | 96 | 5:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L, NO SE ENCONTRO CAUSA | P22080100080 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 338 | 2022-08-01 | 32448 | keep | 0 | Aug | 2022 | 0.0221 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
BAYAMON | 2022-08-01 07:56 | 2022-08-01 11:35 | 28 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22080100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-08-01 | 6132 | keep | 0 | Aug | 2022 | 0.0041765 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2022-08-01 08:14 | 2022-08-01 16:50 | 12 | 8:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22080100033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 516 | 2022-08-01 | 6192 | keep | 0 | Aug | 2022 | 0.0042173 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-08-01 08:19 | 2022-08-01 12:47 | 2 | 4:28 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN MONTURA DESGANCHE | P22080100039 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 268 | 2022-08-01 | 536 | keep | 0 | Aug | 2022 | 0.00036507 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-01 08:25 | 2022-08-01 17:15 | 1 | 8:50 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A22080100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 530 | 2022-08-01 | 530 | keep | 0 | Aug | 2022 | 0.00036098 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-01 08:37 | 2022-08-01 11:05 | 15 | 2:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO Y REEMPLAZO CONECTORES. | C22080100063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 148 | 2022-08-01 | 2220 | keep | 0 | Aug | 2022 | 0.001512 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-01 08:37 | 2022-08-01 10:52 | 46 | 2:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 CORTE DE LINEA MAL TIEMPO VIENTO | C22080100061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 135 | 2022-08-01 | 6210 | keep | 0 | Aug | 2022 | 0.0042296 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
CAGUAS | 2022-08-01 08:59 | 2022-08-01 16:28 | 1 | 7:29 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22080100065 | New_Event | Animals | Include | Include | Wildlife | 449 | 2022-08-01 | 449 | keep | 0 | Aug | 2022 | 0.00030581 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-01 09:13 | 2022-08-01 09:14 | 6197 | 0:01 | T | ANIMAL | RECIERRE | C22080100000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-01 | 6197 | keep | 0 | Aug | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2022-08-01 09:14 | 2022-08-01 10:40 | 200 | 1:26 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22080100072 | 1st_after_momentary | Animals | Include | Include | Wildlife | 86 | 2022-08-01 | 17200 | keep | 0 | Aug | 2022 | 0.011715 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-08-01 09:15 | 2022-08-01 09:16 | 3833 | 0:01 | T | ANIMAL | RECIERRE | C22080100073 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-01 | 3833 | keep | 0 | Aug | 2022 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2022-08-01 09:16 | 2022-08-01 12:10 | 80 | 2:54 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22080100074 | 1st_after_momentary | Animals | Include | Include | Wildlife | 174 | 2022-08-01 | 13920 | keep | 0 | Aug | 2022 | 0.0094808 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-01 09:21 | 2022-08-01 10:30 | 1 | 1:09 | P | ANIMAL | 1 X 50 Y 1 X 65 EN C/L GATO CRUZO LINEA | B22080100051 | New_Event | Animals | Include | Include | Wildlife | 69 | 2022-08-01 | 69 | keep | 0 | Aug | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-01 09:22 | 2022-08-01 12:17 | 80 | 2:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMP | M22080100051 | New_Event | Cutout Failure | Include | Include | Equipment | 175 | 2022-08-01 | 14000 | keep | 0 | Aug | 2022 | 0.0095353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-01 09:27 | 2022-08-01 11:10 | 8 | 1:43 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REEMPLAZARON CONECTORES DEL NEUTRAL PRIMARIO | M22080100052 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 103 | 2022-08-01 | 824 | keep | 0 | Aug | 2022 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-01 09:34 | 2022-08-01 17:46 | 1 | 8:12 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | C22080100083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 492 | 2022-08-01 | 492 | keep | 0 | Aug | 2022 | 0.0003351 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-01 09:38 | 2022-08-01 14:25 | 1 | 4:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO SE REPORTO CAUSA | A22080100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2022-08-01 | 287 | keep | 0 | Aug | 2022 | 0.00019547 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-01 09:46 | 2022-08-01 11:00 | 5 | 1:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR BARRAS EN PEDESTAL | S22080100027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 74 | 2022-08-01 | 370 | keep | 0 | Aug | 2022 | 0.00025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-01 09:47 | 2022-08-01 13:45 | 1 | 3:58 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | C22080100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2022-08-01 | 238 | keep | 0 | Aug | 2022 | 0.0001621 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-01 09:53 | 2022-08-01 16:50 | 25 | 6:57 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22080100062 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 417 | 2022-08-01 | 10425 | keep | 0 | Aug | 2022 | 0.0071004 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-08-01 10:02 | 2022-08-01 15:00 | 100 | 4:58 | P | DESGANCHE | 1 X 40 EN RISER Y 1 X 50 EN C/L DESGANCHO Y SE REEMPLAZO CAJA AVERIADA | R22080100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-08-01 | 29800 | keep | 0 | Aug | 2022 | 0.020297 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-01 10:04 | 2022-08-01 15:12 | 12 | 5:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A22080100019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2022-08-01 | 3696 | keep | 0 | Aug | 2022 | 0.0025173 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-01 10:10 | 2022-08-01 11:10 | 15 | 1:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080100021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 60 | 2022-08-01 | 900 | keep | 0 | Aug | 2022 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-01 10:35 | 2022-08-01 10:37 | 3630 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-01 | 7260 | keep | 0 | Aug | 2022 | 0.0049448 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
GUAYAMA | 2022-08-01 11:02 | 2022-08-01 12:17 | 15 | 1:15 | P | DESGANCHE | 1 X 80 EN C/L SE RETIRO BAMBU | P22080100075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-08-01 | 1125 | keep | 0 | Aug | 2022 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-01 11:08 | 2022-08-01 12:20 | 407 | 1:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO PUENTE ABIERTO EN TRONCAL TRASPATIO | B22080100139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 72 | 2022-08-01 | 29304 | keep | 0 | Aug | 2022 | 0.019959 | 0.00027721 | Sustained | FALSE | FALSE | Not_TMED_Event | 407
SAN JUAN | 2022-08-01 11:11 | 2022-08-01 12:30 | 15 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22073100172 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2022-08-01 | 1185 | keep | 0 | Aug | 2022 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-01 11:27 | 2022-08-01 13:16 | 1 | 1:49 | P | NO SE REPORTO CAUSA | 2 X 8 EN BANCO DE XMR | B22080100071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-08-01 | 109 | keep | 0 | Aug | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-01 11:42 | 2022-08-01 11:44 | 513 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% 1111-01 SE CERRO POR SCADA | S22080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-01 | 1026 | keep | 0 | Aug | 2022 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-08-01 11:42 | 2022-08-01 11:44 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1118-10 LLEVANDO 20% 1111-01 SE CERRO POR SCADA | S22080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-01 | 5564 | keep | 0 | Aug | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2022-08-01 11:56 | 2022-08-01 14:54 | 23 | 2:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO (COLINDANCIA CON REGION CAROLINA) | R22080100054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 178 | 2022-08-01 | 4094 | keep | 0 | Aug | 2022 | 0.0027884 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
YAUCO | 2022-08-01 12:03 | 2022-08-01 12:04 | 1268 | 0:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA PODER ABRIR MACHETE SOLIDO DEFECTUOSO | M22080100087 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-01 | 1268 | keep | 0 | Aug | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
BARRANQUITAS | 2022-08-01 12:10 | 2022-08-01 15:03 | 17 | 2:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR 75 PIES DE SECUNDARIA | C22073100082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 173 | 2022-08-01 | 2941 | keep | 0 | Aug | 2022 | 0.0020031 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-08-01 12:11 | 2022-08-01 13:28 | 2 | 1:17 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22080100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2022-08-01 | 154 | keep | 0 | Aug | 2022 | 0.00010489 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-08-01 12:15 | 2022-08-01 15:23 | 96 | 3:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LINEA | C22080100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-08-01 | 18048 | keep | 0 | Aug | 2022 | 0.012292 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
YAUCO | 2022-08-01 12:16 | 2022-08-01 15:00 | 12 | 2:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22080100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-08-01 | 1968 | keep | 0 | Aug | 2022 | 0.0013404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 959 | keep | 0 | Aug | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 LLEVA LA CARGA DEL 1706-03 | B22080100079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 CARGA POR EL 1706-02 | B22080100079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 663 | keep | 0 | Aug | 2022 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 1372 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA PARTE DE SU CARGA TRANSFERIDA AL 1707-01 | B22080100078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1372 | keep | 0 | Aug | 2022 | 0.00093446 | 0.00093446 | Momentary | FALSE | FALSE | Not_TMED_Event | 1372
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1221 | keep | 0 | Aug | 2022 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1100 | keep | 0 | Aug | 2022 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1514 | keep | 0 | Aug | 2022 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-08-01 12:20 | 2022-08-01 12:21 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1105 | keep | 0 | Aug | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-08-01 12:21 | 2022-08-01 18:32 | 407 | 6:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO PUENTE ABIERTO EN TRONCAL TRASPATIO | B22080100139 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 371 | 2022-08-01 | 150997 | keep | 0 | Aug | 2022 | 0.10284 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-01 12:29 | 2022-08-01 14:34 | 40 | 2:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22080100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-08-01 | 5000 | keep | 0 | Aug | 2022 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-08-01 12:31 | 2022-08-01 15:54 | 93 | 3:23 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO DE MACHETE A LINEA GOI CG-220801-01 | C22080100126 | New_Event | Primary Wire Break | Include | Include | Equipment | 203 | 2022-08-01 | 18879 | keep | 0 | Aug | 2022 | 0.012858 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
ARECIBO | 2022-08-01 12:45 | 2022-08-01 16:15 | 150 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | A22080100038 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2022-08-01 | 31500 | keep | 0 | Aug | 2022 | 0.021455 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-01 12:55 | 2022-08-01 15:15 | 5 | 2:20 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE | B22080100082 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 140 | 2022-08-01 | 700 | keep | 0 | Aug | 2022 | 0.00047677 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-01 12:59 | 2022-08-01 16:36 | 5 | 3:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22080100085 | New_Event | Secondary Wire Break | Include | Include | Equipment | 217 | 2022-08-01 | 1085 | keep | 0 | Aug | 2022 | 0.00073899 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-01 13:02 | 2022-08-01 21:45 | 36 | 8:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L, SE REEMPLAZO CAJA PRIMARIA SE DEJO FUERA T-18 Y T-17 CON PUENTE ABIERTO ANTES DE RISER. SE REFIRIO A SOTERRADO. | B22080100086 | New_Event | Primary Wire Break | Include | Include | Equipment | 523 | 2022-08-01 | 18828 | keep | 0 | Aug | 2022 | 0.012824 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-08-01 13:11 | 2022-08-01 16:45 | 60 | 3:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22080100098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2022-08-01 | 12840 | keep | 0 | Aug | 2022 | 0.0087453 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-01 13:24 | 2022-08-01 17:04 | 93 | 3:40 | P | DESGANCHE | SE DESGANCHO Y SE CERRO INTELLIRUPTER | S22080100050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-08-01 | 20460 | keep | 0 | Aug | 2022 | 0.013935 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2022-08-01 13:45 | 2022-08-01 14:45 | 10 | 1:00 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | S22080100060 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 60 | 2022-08-01 | 600 | keep | 0 | Aug | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-01 13:55 | 2022-08-01 15:00 | 13 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22080100046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-08-01 | 845 | keep | 0 | Aug | 2022 | 0.00057553 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2022-08-01 13:58 | 2022-08-01 19:12 | 1 | 5:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | R22080100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 314 | 2022-08-01 | 314 | keep | 0 | Aug | 2022 | 0.00021386 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-01 13:59 | 2022-08-01 19:10 | 34 | 5:11 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMDOR CRUCE POR AVE | C22080100141 | New_Event | Animals | Include | Include | Wildlife | 311 | 2022-08-01 | 10574 | keep | 0 | Aug | 2022 | 0.0072019 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
GUAYAMA | 2022-08-01 14:15 | 2022-08-01 14:16 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080100096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 527 | keep | 0 | Aug | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CAGUAS | 2022-08-01 14:22 | 2022-08-01 16:14 | 123 | 1:52 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22080100146 | New_Event | Animals | Include | Include | Wildlife | 112 | 2022-08-01 | 13776 | keep | 0 | Aug | 2022 | 0.0093828 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
CANOVANAS | 2022-08-01 14:26 | 2022-08-01 17:10 | 15 | 2:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR REPARO BAJANTE Y LINEA SECUNDARIA | R22080100066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 164 | 2022-08-01 | 2460 | keep | 0 | Aug | 2022 | 0.0016755 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-01 14:42 | 2022-08-01 19:53 | 40 | 5:11 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080100115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-08-01 | 12440 | keep | 0 | Aug | 2022 | 0.0084728 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-01 14:53 | 2022-08-01 15:58 | 36 | 1:05 | P | ANIMAL | 1 X 25 EN C/L CRUCE X LAGARTIJO | R22080100068 | New_Event | Animals | Include | Include | Wildlife | 65 | 2022-08-01 | 2340 | keep | 0 | Aug | 2022 | 0.0015938 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-08-01 14:58 | 2022-08-02 11:03 | 8 | 20:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DESGANCHE, SE REMPLAZARON 2 CAJAS PRIMARIAS, SE REPARO BAJANTE LINE A CAJA Y 2 X 20 EN XMR | S22080100089 | New_Event | Cutout Failure | Include | Include | Equipment | 1205 | 2022-08-01 | 9640 | keep | 0 | Aug | 2022 | 0.0065658 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-01 15:04 | 2022-08-01 18:10 | 40 | 3:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-08-01 | 7440 | keep | 0 | Aug | 2022 | 0.0050674 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-01 15:05 | 2022-08-01 15:06 | 390 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR | M22080100123 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-01 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2022-08-01 15:05 | 2022-08-01 16:38 | 12 | 1:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 KVA X 37.5KVA | B22080100097 | New_Event | Service Transformer Failure | Include | Include | Equipment | 93 | 2022-08-01 | 1116 | keep | 0 | Aug | 2022 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-01 15:07 | 2022-08-01 15:08 | 390 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR | M22080100124 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-01 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2022-08-01 15:08 | 2022-08-01 18:30 | 25 | 3:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REMPLAZO CAJAS PRIMARIAS QUEMADAS DEL TRANSFORMADOR | M22080100150 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 202 | 2022-08-01 | 5050 | keep | 0 | Aug | 2022 | 0.0034395 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-08-01 15:25 | 2022-08-01 15:26 | 1613 | 0:01 | T | DESGANCHE | RECIERRE | R22080100072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-01 | 1613 | keep | 0 | Aug | 2022 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2022-08-01 15:26 | 2022-08-01 17:48 | 2 | 2:22 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHO Y REEMPLAZO CAJA QUEMADA | R22080100079 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-08-01 | 284 | keep | 0 | Aug | 2022 | 0.00019343 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-08-01 15:32 | 2022-08-01 15:33 | 2457 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22080100163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 2457 | keep | 0 | Aug | 2022 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
HUMACAO | 2022-08-01 15:54 | 2022-08-01 18:02 | 3025 | 2:08 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE DE MACHETE A LINEA GOI CG-220801-01 | C22080100126 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 128 | 2022-08-01 | 387200 | keep | 0 | Aug | 2022 | 0.26372 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-01 15:59 | 2022-08-01 16:54 | 115 | 0:55 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22080100106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2022-08-01 | 6325 | keep | 0 | Aug | 2022 | 0.0043079 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
SAN JUAN | 2022-08-01 16:07 | 2022-08-02 11:57 | 15 | 19:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR CONECTORES SECUNDARIOS | S22080100115 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1190 | 2022-08-01 | 17850 | keep | 0 | Aug | 2022 | 0.012158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-08-01 16:07 | 2022-08-02 07:05 | 1 | 14:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO SE ENCONTRO CAUSA | P22080100111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 898 | 2022-08-01 | 898 | keep | 0 | Aug | 2022 | 0.00061162 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-01 16:13 | 2022-08-01 16:14 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080100114 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 527 | keep | 0 | Aug | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-08-01 16:14 | 2022-08-01 17:00 | 1 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES EN LINEA SECUNDARIA Y SE REPARO PUENTE SECUNDARIO | P22080100113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2022-08-01 | 46 | keep | 0 | Aug | 2022 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-01 16:15 | 2022-08-01 18:30 | 20 | 2:15 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M22080100140 | New_Event | Animals | Include | Include | Wildlife | 135 | 2022-08-01 | 2700 | keep | 0 | Aug | 2022 | 0.001839 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-01 16:35 | 2022-08-01 17:25 | 3 | 0:50 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARAR REMPLAZAR BUSHING SECUNDARIO | A22080100059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 50 | 2022-08-01 | 150 | keep | 0 | Aug | 2022 | 0.00010216 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-08-01 16:47 | 2022-08-01 18:06 | 1131 | 1:19 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTE DE LINEA A LINEA GOI CG-220801-02 | C22080100190 | New_Event | Primary Wire Break | Include | Include | Equipment | 79 | 2022-08-01 | 89349 | keep | 0 | Aug | 2022 | 0.060855 | 0.00077032 | Sustained | FALSE | FALSE | Not_TMED_Event | 1131
VEGA BAJA | 2022-08-01 17:03 | 2022-08-01 18:06 | 10 | 1:03 | P | SECUNDARIA/DESGANCHE | SE REPARO CONECTORES SECUNDARIAS DESGANCHE SECUNDARIO | B22080100054 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 63 | 2022-08-01 | 630 | keep | 0 | Aug | 2022 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-01 17:28 | 2022-08-01 17:54 | 1604 | 0:26 | T | CONDUCTOR ROTO O ABIERTO | INTERRUPTOR DISPARO EN OPERACION DE CERRAR PUENTE DE LINEA A LINEA EN EL 9703-02 SE DEJO FUERA POR SEGURIDAD | C22080100202 | New_Event | Primary Wire Break | Include | Include | Equipment | 26 | 2022-08-01 | 41704 | keep | 0 | Aug | 2022 | 0.028404 | 0.0010925 | Sustained | FALSE | FALSE | Not_TMED_Event | 1604
CANOVANAS | 2022-08-01 17:33 | 2022-08-01 19:09 | 40 | 1:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L Y 1 X 50 SM 4 EN SU - 2 REEMPLAZO CAJA AVERIADA | R22080100080 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2022-08-01 | 3840 | keep | 0 | Aug | 2022 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-01 17:36 | 2022-08-01 18:25 | 22 | 0:49 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA RETIRAR POSTE SECUNDARIO PARTIDO SOBRE RESIDENCIA. SE REEMPLAZARA MAÃ‘ANA | C22080100204 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 49 | 2022-08-01 | 1078 | keep | 0 | Aug | 2022 | 0.00073422 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2022-08-01 17:40 | 2022-08-01 18:05 | 137 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | P22080100093 | New_Event | Primary Wire Break | Include | Include | Equipment | 25 | 2022-08-01 | 3425 | keep | 0 | Aug | 2022 | 0.0023328 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BARRANQUITAS | 2022-08-01 17:53 | 2022-08-01 22:10 | 150 | 4:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22080100213 | New_Event | Cutout Failure | Include | Include | Equipment | 257 | 2022-08-01 | 38550 | keep | 0 | Aug | 2022 | 0.026256 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-01 17:54 | 2022-08-01 20:20 | 100 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S22080100139 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2022-08-01 | 14600 | keep | 0 | Aug | 2022 | 0.009944 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-01 17:57 | 2022-08-01 20:00 | 40 | 2:03 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN C/L, XMR DE 50 KVA QUEMADO PENDIENTE A REEMPLAZO | R22080100085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 123 | 2022-08-01 | 4920 | keep | 0 | Aug | 2022 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-01 18:05 | 2022-08-01 18:30 | 12 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22080100125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-08-01 | 300 | keep | 0 | Aug | 2022 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-08-01 18:12 | 2022-08-01 21:45 | 15 | 3:33 | P | ANIMAL | 1 X 25 EN TRANSFORMADOR PAJARO CRUZO FASE | P22080100127 | New_Event | Animals | Include | Include | Wildlife | 213 | 2022-08-01 | 3195 | keep | 0 | Aug | 2022 | 0.0021761 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-08-01 18:15 | 2022-08-01 18:42 | 425 | 0:27 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN TRONCAL SE ABRIO INTERRUPTOR PARA REPARARLO 6501-01 LLEVA EL 95% DEL 6501-04 | M22080100155 | New_Event | Primary Wire Break | Include | Include | Equipment | 27 | 2022-08-01 | 11475 | keep | 0 | Aug | 2022 | 0.0078156 | 0.00028947 | Sustained | FALSE | FALSE | Not_TMED_Event | 425
YAUCO | 2022-08-01 18:15 | 2022-08-01 18:42 | 960 | 0:27 | P | CAUSAS EXTERNAS | PUENTE ABIERTO EN TRONCAL SE ABRIO INTERRUPTOR PARA REPARARLO 6501-01 LLEVA EL 95% DEL 6501-04 | M22080100155 | New_Event | Damage From Public | Include | Include | Public | 27 | 2022-08-01 | 25920 | keep | 0 | Aug | 2022 | 0.017654 | 0.00065385 | Sustained | FALSE | FALSE | Not_TMED_Event | 960
VEGA BAJA | 2022-08-01 18:18 | 2022-08-01 18:19 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22080100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 2697 | keep | 0 | Aug | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
BAYAMON | 2022-08-01 18:32 | 2022-08-01 19:44 | 1221 | 1:12 | T | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BKR PARA REPARAR PUENTE ABIERTO EN TRONCAL TRASPATIO | B22080100139 | Additional_clients | Secondary Wire Break | Include | Include | Equipment | 72 | 2022-08-01 | 87912 | keep | 0 | Aug | 2022 | 0.059876 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-01 18:32 | 2022-08-01 19:30 | 150 | 0:58 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN CORTES DE LINEA DISTINTOS NO SE ENCONTRO CAUSA | A22080100069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-08-01 | 8700 | keep | 0 | Aug | 2022 | 0.0059255 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-08-01 18:42 | 2022-08-02 15:57 | 25 | 21:15 | P | CAUSAS EXTERNAS | PUENTE ABIERTO EN TRONCAL SE QUEDO VARIAS TRANSFORMADORES FUERA | M22080100155 | Partial_restoration | Damage From Public | Include | Include | Public | 1275 | 2022-08-01 | 31875 | keep | 0 | Aug | 2022 | 0.02171 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-01 18:59 | 2022-08-01 19:00 | 641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1206-01 QUE LLEVA 1206-02 | S22080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 641 | keep | 0 | Aug | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-08-01 18:59 | 2022-08-01 19:00 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1206-01 PARCIAL QUE LLEVA 1206-02 | S22080100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-01 | 733 | keep | 0 | Aug | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-08-01 19:02 | 2022-08-02 11:00 | 40 | 15:58 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO CABLE DE RISER A T-4 | S22080100153 | New_Event | UG Cable Fault | Include | Include | Equipment | 958 | 2022-08-01 | 38320 | keep | 0 | Aug | 2022 | 0.0261 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-01 19:16 | 2022-08-02 10:26 | 18 | 15:10 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO | C22080100227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 910 | 2022-08-01 | 16380 | keep | 0 | Aug | 2022 | 0.011156 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-08-01 19:34 | 2022-08-01 22:40 | 70 | 3:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080100172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-08-01 | 13020 | keep | 0 | Aug | 2022 | 0.0088679 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-08-01 19:41 | 2022-08-01 20:35 | 60 | 0:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO REPORTO CAUSA | A22080100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-08-01 | 3240 | keep | 0 | Aug | 2022 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-01 19:43 | 2022-08-02 13:53 | 13 | 18:10 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTORES PRIMARIOS Y SE CERRO CORTE DE LINEA | R22080100092 | New_Event | Primary Wire Break | Include | Include | Equipment | 1090 | 2022-08-01 | 14170 | keep | 0 | Aug | 2022 | 0.0096511 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
YAUCO | 2022-08-01 19:44 | 2022-08-01 19:47 | 3973 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DEL ALIMENTADOR TENIA EL RECIERRE EN OFF | P22080100143 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-01 | 11919 | keep | 0 | Aug | 2022 | 0.008118 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-08-01 19:44 | 2022-08-01 19:47 | 2484 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DEL ALIMENTADOR TENIA EL RECIERRE EN OFF | P22080100143 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-01 | 7452 | keep | 0 | Aug | 2022 | 0.0050755 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
HUMACAO | 2022-08-01 19:46 | 2022-08-01 22:31 | 1 | 2:45 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22080100234 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-08-01 | 165 | keep | 0 | Aug | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-01 19:47 | 2022-08-01 22:31 | 1324 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SALIDA DEL ALIMENTADOR | P22080100150 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 164 | 2022-08-01 | 217136 | keep | 0 | Aug | 2022 | 0.14789 | 0.00090177 | Sustained | FALSE | FALSE | Not_TMED_Event | 1324
YAUCO | 2022-08-01 19:47 | 2022-08-01 22:31 | 828 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SALIDA DEL ALIMENTADOR | P22080100150 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 164 | 2022-08-01 | 135792 | keep | 0 | Aug | 2022 | 0.092487 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
CANOVANAS | 2022-08-01 20:00 | 2022-08-02 09:52 | 11 | 13:52 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO QUEMADO 50 KVA X 50 KVA | R22080100085 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 832 | 2022-08-01 | 9152 | keep | 0 | Aug | 2022 | 0.0062334 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 959 | keep | 0 | Aug | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 LLEVA LA CARGA DE 1706-03 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 CARGA POR 1706-02 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 663 | keep | 0 | Aug | 2022 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 1372 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA PARTE DE SU CARGA TRANSFERIDA AL 1707-01 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1372 | keep | 0 | Aug | 2022 | 0.00093446 | 0.00093446 | Momentary | FALSE | FALSE | Not_TMED_Event | 1372
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1221 | keep | 0 | Aug | 2022 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1100 | keep | 0 | Aug | 2022 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1514 | keep | 0 | Aug | 2022 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1105 | keep | 0 | Aug | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 4176 | keep | 0 | Aug | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 252 | keep | 0 | Aug | 2022 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 2147 | keep | 0 | Aug | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-08-01 20:11 | 2022-08-01 20:12 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 2858 | keep | 0 | Aug | 2022 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 959 | keep | 0 | Aug | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 LLEVA LA CARGA DEL 1706-03 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 CARGA POR EL 1706-02 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 663 | keep | 0 | Aug | 2022 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 1372 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA PARTE DE SU CARGA TRANSFERIDA AL 1707-01 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1372 | keep | 0 | Aug | 2022 | 0.00093446 | 0.00093446 | Momentary | FALSE | FALSE | Not_TMED_Event | 1372
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1221 | keep | 0 | Aug | 2022 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1100 | keep | 0 | Aug | 2022 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1514 | keep | 0 | Aug | 2022 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-08-01 20:25 | 2022-08-01 20:26 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 10000 | B22080100000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-01 | 1105 | keep | 0 | Aug | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
CAGUAS | 2022-08-01 20:31 | 2022-08-02 06:17 | 15 | 9:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22080100238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 586 | 2022-08-01 | 8790 | keep | 0 | Aug | 2022 | 0.0059868 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-01 20:50 | 2022-08-02 02:26 | 100 | 5:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22080100241 | New_Event | Cutout Failure | Include | Include | Equipment | 336 | 2022-08-01 | 33600 | keep | 0 | Aug | 2022 | 0.022885 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-01 20:58 | 2022-08-02 08:29 | 100 | 11:31 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S22080100170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 691 | 2022-08-01 | 69100 | keep | 0 | Aug | 2022 | 0.047064 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-08-01 21:18 | 2022-08-01 23:19 | 190 | 2:01 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | P22080100224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-08-01 | 22990 | keep | 0 | Aug | 2022 | 0.015658 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
AGUADILLA | 2022-08-01 21:26 | 2022-08-02 01:24 | 65 | 3:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M22080100185 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 238 | 2022-08-01 | 15470 | keep | 0 | Aug | 2022 | 0.010537 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2022-08-01 21:40 | 2022-08-01 22:00 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M22080100167 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 20 | 2022-08-01 | 160 | keep | 0 | Aug | 2022 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-01 21:45 | 2022-08-02 23:07 | 10 | 25:22 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO DE OTRO EXISTENTE @ T-17 | B22080100086 | New_Event | UG Cable Fault | Include | Include | Equipment | 1522 | 2022-08-01 | 15220 | keep | 0 | Aug | 2022 | 0.010366 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-01 22:17 | 2022-08-02 09:00 | 18 | 10:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22080100175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 643 | 2022-08-01 | 11574 | keep | 0 | Aug | 2022 | 0.007883 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
YAUCO | 2022-08-01 22:31 | 2022-08-01 23:16 | 3973 | 0:45 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE ALIMENTADOR PARA PODER CERRAR PUENTE ABIERTO | P22080100274 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 45 | 2022-08-01 | 178785 | keep | 0 | Aug | 2022 | 0.12177 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-01 22:31 | 2022-08-01 23:16 | 2484 | 0:45 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE ALIMENTADOR PARA CERRAR PUENTE ABIERTO | P22080100274 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 45 | 2022-08-01 | 111780 | keep | 0 | Aug | 2022 | 0.076133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-01 22:35 | 2022-08-02 09:20 | 45 | 10:45 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22080100094 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 645 | 2022-08-01 | 29025 | keep | 0 | Aug | 2022 | 0.019769 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
FAJARDO | 2022-08-02 00:30 | 2022-08-02 07:53 | 8 | 7:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R22080200001 | New_Event | Cutout Failure | Include | Include | Equipment | 443 | 2022-08-02 | 3544 | keep | 0 | Aug | 2022 | 0.0024138 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-02 02:45 | 2022-08-02 15:45 | 12 | 13:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTORES EN SALIDA DE TRANSFORMADOR | A22080200136 | New_Event | Secondary Wire Break | Include | Include | Equipment | 780 | 2022-08-02 | 9360 | keep | 0 | Aug | 2022 | 0.0063751 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-08-02 04:09 | 2022-08-02 15:58 | 60 | 11:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE REPARO LINEA PRIMARIA PARTIDA | P22080200017 | New_Event | Primary Wire Break | Include | Include | Equipment | 709 | 2022-08-02 | 42540 | keep | 0 | Aug | 2022 | 0.028974 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-02 04:24 | 2022-08-02 10:49 | 80 | 6:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22080200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2022-08-02 | 30800 | keep | 0 | Aug | 2022 | 0.020978 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-02 04:59 | 2022-08-02 09:51 | 23 | 4:52 | P | ANIMAL | 1 X 40 EN AEREO PROVISIONAL CRUCE POR AVE | R22080200002 | New_Event | Animals | Include | Include | Wildlife | 292 | 2022-08-02 | 6716 | keep | 0 | Aug | 2022 | 0.0045742 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BARRANQUITAS | 2022-08-02 05:56 | 2022-08-02 13:28 | 20 | 7:32 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO | C22080200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 452 | 2022-08-02 | 9040 | keep | 0 | Aug | 2022 | 0.0061571 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-02 06:09 | 2022-08-02 09:44 | 80 | 3:35 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C22080200004 | New_Event | Animals | Include | Include | Wildlife | 215 | 2022-08-02 | 17200 | keep | 0 | Aug | 2022 | 0.011715 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-02 06:14 | 2022-08-02 10:25 | 125 | 4:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22080200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-08-02 | 31375 | keep | 0 | Aug | 2022 | 0.021369 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-08-02 06:30 | 2022-08-02 10:45 | 250 | 4:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M22080200019 | New_Event | Cutout Failure | Include | Include | Equipment | 255 | 2022-08-02 | 63750 | keep | 0 | Aug | 2022 | 0.04342 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
VEGA BAJA | 2022-08-02 06:39 | 2022-08-02 10:57 | 6 | 4:18 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080200012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-08-02 | 1548 | keep | 0 | Aug | 2022 | 0.0010543 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-02 06:52 | 2022-08-02 09:00 | 40 | 2:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080200023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 128 | 2022-08-02 | 5120 | keep | 0 | Aug | 2022 | 0.0034872 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-02 06:58 | 2022-08-02 19:00 | 9 | 12:02 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | M22080200033 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 722 | 2022-08-02 | 6498 | keep | 0 | Aug | 2022 | 0.0044258 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2022-08-02 07:01 | 2022-08-02 11:55 | 150 | 4:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080200026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 294 | 2022-08-02 | 44100 | keep | 0 | Aug | 2022 | 0.030036 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-08-02 07:13 | 2022-08-02 12:42 | 150 | 5:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTE VIENTOS | P22080200028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 329 | 2022-08-02 | 49350 | keep | 0 | Aug | 2022 | 0.033612 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-02 07:31 | 2022-08-02 12:23 | 7 | 4:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR Y 1 80 EN SU | B22080200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2022-08-02 | 2044 | keep | 0 | Aug | 2022 | 0.0013922 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-02 07:39 | 2022-08-02 11:42 | 8 | 4:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5 KVA AVERIADO | B22080200012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 243 | 2022-08-02 | 1944 | keep | 0 | Aug | 2022 | 0.001324 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-02 07:40 | 2022-08-02 12:45 | 2 | 5:05 | P | CONDUCTOR ARRIADO O CRUZADO | SE SEPARO PUENTE PRIMARIO PEGADO A ESTRUCTURA Y SE SUBIO SECUNDARIA NUEVA PARA TALLER Y OFICINAS AAA | B22080200013 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 305 | 2022-08-02 | 610 | keep | 0 | Aug | 2022 | 0.00041547 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-02 08:03 | 2022-08-02 13:30 | 12 | 5:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONECTORES SECUNDARIOS | M22080200039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 327 | 2022-08-02 | 3924 | keep | 0 | Aug | 2022 | 0.0026726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-02 08:08 | 2022-08-02 09:32 | 1 | 1:24 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO | C22080200031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-08-02 | 84 | keep | 0 | Aug | 2022 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-02 08:34 | 2022-08-02 11:44 | 100 | 3:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A22080200030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 190 | 2022-08-02 | 19000 | keep | 0 | Aug | 2022 | 0.012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-02 08:39 | 2022-08-03 14:25 | 1 | 29:46 | P | OTRAS CAUSAS | 1 X 50 EN RISER SE RETIRO EQUIPO DE MEDICION AVERIADO Y SE NOTIFICO PARA QUE LO REMPLACEN RELACIONADO WR6182738 SIN SERVCIO DESDE EL DIA 2 Y EVENTO CREADO EL DIA 3 | A22080300046 | New_Event | Other Causes | Include | Include | Other | 1786 | 2022-08-02 | 1786 | keep | 0 | Aug | 2022 | 0.0012164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-02 08:50 | 2022-08-02 12:00 | 12 | 3:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR ALREDEDOR DE 200' LINEA 3/2 | P22080200041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 190 | 2022-08-02 | 2280 | keep | 0 | Aug | 2022 | 0.0015529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-02 08:58 | 2022-08-02 11:27 | 40 | 2:29 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C22080200043 | New_Event | Animals | Include | Include | Wildlife | 149 | 2022-08-02 | 5960 | keep | 0 | Aug | 2022 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-02 09:10 | 2022-08-02 13:43 | 45 | 4:33 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO | C22080200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2022-08-02 | 12285 | keep | 0 | Aug | 2022 | 0.0083673 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-08-02 09:14 | 2022-08-02 10:42 | 1022 | 1:28 | T | DESGANCHE | SE ABRIO INTERRUPTOR DE EMERGENCIA PARA RETIRAR RAMAS DE ARBOL SOBRE LA SALIDA DEL INTERRUPTOR | A22080200074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-08-02 | 89936 | keep | 0 | Aug | 2022 | 0.061255 | 0.00069608 | Sustained | FALSE | FALSE | Not_TMED_Event | 1022
SAN JUAN | 2022-08-02 09:16 | 2022-08-02 13:45 | 68 | 4:29 | T | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA POR FUEGO EN SUBESTACION | S22080200207 | New_Event | Power Transformer Failure | Include | Include | Equipment | 269 | 2022-08-02 | 18292 | keep | 0 | Aug | 2022 | 0.012459 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-08-02 09:16 | 2022-08-02 13:45 | 536 | 4:29 | T | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA POR FUEGO EN SUBESTACION | S22080200207 | New_Event | Power Transformer Failure | Include | Include | Equipment | 269 | 2022-08-02 | 144184 | keep | 0 | Aug | 2022 | 0.098203 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
SAN JUAN | 2022-08-02 09:16 | 2022-08-02 13:45 | 348 | 4:29 | T | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA POR FUEGO EN SUBESTACION | S22080200207 | New_Event | Power Transformer Failure | Include | Include | Equipment | 269 | 2022-08-02 | 93612 | keep | 0 | Aug | 2022 | 0.063759 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-08-02 09:16 | 2022-08-02 13:55 | 559 | 4:39 | T | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA POR FUEGO EN SUBESTACION TAPIA | S22080200207 | New_Event | Power Transformer Failure | Include | Include | Equipment | 279 | 2022-08-02 | 155961 | keep | 0 | Aug | 2022 | 0.10622 | 0.00038073 | Sustained | FALSE | FALSE | Not_TMED_Event | 559
SAN JUAN | 2022-08-02 09:16 | 2022-08-02 13:45 | 300 | 4:29 | P | POWER TRANSFORMER AVERIADO | SE RETIRA CARGA POR FUEGO EN SUBESTACION TAPIA | S22080200207 | New_Event | Power Transformer Failure | Include | Include | Equipment | 269 | 2022-08-02 | 80700 | keep | 0 | Aug | 2022 | 0.054964 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-02 09:24 | 2022-08-02 10:01 | 1 | 0:37 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 SMU 20 EN SUBESTACION PRIVADA Y SE LLEVO RISER A CAJA PRIMARIA | B22080200020 | New_Event | Primary Wire Break | Include | Include | Equipment | 37 | 2022-08-02 | 37 | keep | 0 | Aug | 2022 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-02 09:24 | 2022-08-02 10:36 | 3522 | 1:12 | S | LINEA DE TRANSMISION 38KV | CERRADA PARCIALMENTE LINEA 1900 | M22080200085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 253584 | keep | 0 | Aug | 2022 | 0.17271 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
AGUADILLA | 2022-08-02 09:24 | 2022-08-02 10:36 | 1337 | 1:12 | S | LINEA DE TRANSMISION 38KV | CERRADA PARCIALMENTE LINEA 1900 | M22080200085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 96264 | keep | 0 | Aug | 2022 | 0.065565 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-02 09:24 | 2022-08-02 10:36 | 2825 | 1:12 | S | LINEA DE TRANSMISION 38KV | CERRADA PARCIALMENTE LINEA 1900 | M22080200085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 203400 | keep | 0 | Aug | 2022 | 0.13853 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
AGUADILLA | 2022-08-02 09:24 | 2022-08-02 10:36 | 1287 | 1:12 | S | LINEA DE TRANSMISION 38KV | CERRADA PARCIALMENTE LINEA 1900 | M22080200085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 92664 | keep | 0 | Aug | 2022 | 0.063113 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
AGUADILLA | 2022-08-02 09:24 | 2022-08-02 10:36 | 1417 | 1:12 | S | LINEA DE TRANSMISION 38KV | CERRADA PARCIALMENTE LINEA 1900 | M22080200089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 102024 | keep | 0 | Aug | 2022 | 0.069488 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
AGUADILLA | 2022-08-02 09:24 | 2022-08-02 10:36 | 80 | 1:12 | S | LINEA DE TRANSMISION 38KV | CERRADA PARCIALMENTE LINEA 1900 | M22080200089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 5760 | keep | 0 | Aug | 2022 | 0.0039231 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-08-02 09:24 | 2022-08-02 10:36 | 1633 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A22080200062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 117576 | keep | 0 | Aug | 2022 | 0.08008 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2022-08-02 09:24 | 2022-08-02 10:36 | 1624 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1900 | A22080200062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-02 | 116928 | keep | 0 | Aug | 2022 | 0.079639 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
AGUADILLA | 2022-08-02 09:29 | 2022-08-02 16:32 | 10 | 7:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA DE TRANSFORMADOR | A22080200047 | New_Event | Cutout Failure | Include | Include | Equipment | 423 | 2022-08-02 | 4230 | keep | 0 | Aug | 2022 | 0.002881 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-02 09:31 | 2022-08-02 10:44 | 40 | 1:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080200052 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 73 | 2022-08-02 | 2920 | keep | 0 | Aug | 2022 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-02 09:35 | 2022-08-02 10:20 | 1 | 0:45 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22080200047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-08-02 | 45 | keep | 0 | Aug | 2022 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-02 09:36 | 2022-08-02 19:30 | 40 | 9:54 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080200082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 594 | 2022-08-02 | 23760 | keep | 0 | Aug | 2022 | 0.016183 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-02 09:43 | 2022-08-02 11:00 | 10 | 1:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22080200093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2022-08-02 | 770 | keep | 0 | Aug | 2022 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-02 09:45 | 2022-08-02 13:28 | 400 | 3:43 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA | A22080200067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-08-02 | 89200 | keep | 0 | Aug | 2022 | 0.060754 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2022-08-02 09:47 | 2022-08-02 10:41 | 10 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES EN BAJANTE SECUNDARIO | B22080200024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2022-08-02 | 540 | keep | 0 | Aug | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-02 09:48 | 2022-08-02 12:50 | 13 | 3:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R22080200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2022-08-02 | 2366 | keep | 0 | Aug | 2022 | 0.0016115 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-08-02 09:55 | 2022-08-02 22:11 | 2 | 12:16 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE LINEA @ CAJA EN XMR | S22080200068 | New_Event | Primary Wire Break | Include | Include | Equipment | 736 | 2022-08-02 | 1472 | keep | 0 | Aug | 2022 | 0.0010026 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-02 10:00 | 2022-08-02 17:50 | 5 | 7:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO LINEA SECUNDARIA AVERIADA | S22080200091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 470 | 2022-08-02 | 2350 | keep | 0 | Aug | 2022 | 0.0016006 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-08-02 10:03 | 2022-08-02 10:04 | 2722 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | R22080200027 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-02 | 2722 | keep | 0 | Aug | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2022-08-02 10:04 | 2022-08-02 15:16 | 363 | 5:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y AISLADOR Y PIN POLE TOP | R22080200031 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 312 | 2022-08-02 | 113256 | keep | 0 | Aug | 2022 | 0.077138 | 0.00024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 363
CAGUAS | 2022-08-02 10:09 | 2022-08-02 10:39 | 11 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C22080200058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-08-02 | 330 | keep | 0 | Aug | 2022 | 0.00022476 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-08-02 10:17 | 2022-08-02 16:53 | 40 | 6:36 | P | CONDUCTOR ROTO O ABIERTO | REPARO BAJANTE PRIMARIO NO FUNDIO | C22080200059 | New_Event | Primary Wire Break | Include | Include | Equipment | 396 | 2022-08-02 | 15840 | keep | 0 | Aug | 2022 | 0.010789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-02 10:18 | 2022-08-02 10:20 | 573 | 0:02 | T | ERROR HUMANO | PERSONAL DE CAMPO CON ORDEN PARA ABRIR INTERRUPTOR 1704-01 ABRIO POR ERROR 1704-04 . LLEVA CARGA 1704-05 | B22080200028 | New_Event | Human Error | Include | Include | Other | 2 | 2022-08-02 | 1146 | keep | 0 | Aug | 2022 | 0.00078054 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2022-08-02 10:18 | 2022-08-02 10:20 | 1313 | 0:02 | T | ERROR HUMANO | PERSONAL DE CAMPO CON ORDEN PARA ABRIR INTERRUPTOR 1704-01 ABRIO POR ERROR 1704-04 . LLEVA CARGA 1704-05 | B22080200028 | New_Event | Human Error | Include | Include | Other | 2 | 2022-08-02 | 2626 | keep | 0 | Aug | 2022 | 0.0017886 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
UTUADO | 2022-08-02 10:25 | 2022-08-02 13:00 | 5 | 2:35 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA RETIRAR 2 POSTES QUE NO DABAN SERVICIO | A22080200088 | New_Event | Primary Pole Failure | Include | Include | Equipment | 155 | 2022-08-02 | 775 | keep | 0 | Aug | 2022 | 0.00052785 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-08-02 10:29 | 2022-08-02 10:31 | 1268 | 0:02 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIR INTERRUPTOR PARA ABRIR N/O ENTRE 6501-1 Y 6501-04 | M22080200138 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2 | 2022-08-02 | 2536 | keep | 0 | Aug | 2022 | 0.0017273 | 0.00086363 | Momentary | FALSE | FALSE | Not_TMED_Event | 1268
YAUCO | 2022-08-02 10:32 | 2022-08-02 14:21 | 1 | 3:49 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN MACHETES | M22080200144 | New_Event | Primary Wire Break | Include | Include | Equipment | 229 | 2022-08-02 | 229 | keep | 0 | Aug | 2022 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-02 10:46 | 2022-08-02 13:30 | 150 | 2:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080200153 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 164 | 2022-08-02 | 24600 | keep | 0 | Aug | 2022 | 0.016755 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-02 11:00 | 2022-08-02 11:01 | 641 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR LLEVA EL 1206-02 | S22080200000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-02 | 641 | keep | 0 | Aug | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-08-02 11:00 | 2022-08-02 11:01 | 733 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR CARGA POR EL 1206-01 | S22080200000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-02 | 733 | keep | 0 | Aug | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 821 | 0:02 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 60% POR EL 1206-04 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 1642 | keep | 0 | Aug | 2022 | 0.0011184 | 0.00055918 | Momentary | FALSE | FALSE | Not_TMED_Event | 821
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 1977 | 0:02 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 40% POR EL 1206-04 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 3954 | keep | 0 | Aug | 2022 | 0.0026931 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 8679 | 0:02 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 85% DE LA CARGA POR EL 1206-03 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 17358 | keep | 0 | Aug | 2022 | 0.011822 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 641 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 LLEVA LA CARGA DEL 1206-02 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 1282 | keep | 0 | Aug | 2022 | 0.00087316 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 733 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 CARGA POR EL 1206-01 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 1466 | keep | 0 | Aug | 2022 | 0.00099849 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 4133 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 LLEVA 10% DEL 1620-02 Y EL 85% DEL 1204-05 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 8266 | keep | 0 | Aug | 2022 | 0.0056299 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 1799 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 LLEVA EL 20% DEL 1303-02 LLEVA 40% 1204-04 Y 60% DEL 1204-03 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 3598 | keep | 0 | Aug | 2022 | 0.0024506 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 487 | 0:02 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 20% DE LA CARGA POR EL 1206-04 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 974 | keep | 0 | Aug | 2022 | 0.00066339 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-08-02 11:02 | 2022-08-02 11:04 | 743 | 0:02 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 10% POR EL 1206-03 | S22080200113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-02 | 1486 | keep | 0 | Aug | 2022 | 0.0010121 | 0.00050605 | Momentary | FALSE | FALSE | Not_TMED_Event | 743
FAJARDO | 2022-08-02 11:03 | 2022-08-02 14:10 | 2 | 3:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMDOR DE 50 KVA X 50 KVA Y BRAZO AISLATIVO | R22080200040 | New_Event | Service Transformer Failure | Include | Include | Equipment | 187 | 2022-08-02 | 374 | keep | 0 | Aug | 2022 | 0.00025473 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 821 | 0:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 60% POR EL 1206-04 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 821 | keep | 0 | Aug | 2022 | 0.00055918 | 0.00055918 | Momentary | FALSE | FALSE | Not_TMED_Event | 821
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 1977 | 0:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 40% POR EL 1206-04 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 1977 | keep | 0 | Aug | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 8679 | 0:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 85% DE LA CARGA POR EL 1206-03 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 8679 | keep | 0 | Aug | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 641 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 LLEVA LA CARGA DEL 1206-02 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 641 | keep | 0 | Aug | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 733 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 CARGA POR EL 1206-01 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 733 | keep | 0 | Aug | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 4133 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 LEVA 10% DEL 1620-02 Y 85% DEL 1204-05 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 4133 | keep | 0 | Aug | 2022 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 1799 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 LLEVA EL 20% DEL 1303-02 LLEVA 40% 1204-04 Y 60% DEL 1204-03 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 1799 | keep | 0 | Aug | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 487 | 0:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 20% DE LA CARGA POR EL 1206-04 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 487 | keep | 0 | Aug | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-08-02 11:05 | 2022-08-02 11:06 | 743 | 0:01 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 39700 10% POR EL 1206-03 | S22080200113 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 743 | keep | 0 | Aug | 2022 | 0.00050605 | 0.00050605 | Momentary | FALSE | FALSE | Not_TMED_Event | 743
SAN JUAN | 2022-08-02 11:06 | 2022-08-02 12:18 | 641 | 1:12 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO N/O CONTRA 1206-02 Y SE CERRO POR CONTROL SE SECCIONALIZO MACHETE QUEMADO SALIDA DEL 1206-02 | S22080200113 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 72 | 2022-08-02 | 46152 | keep | 0 | Aug | 2022 | 0.031434 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-08-02 11:06 | 2022-08-02 15:17 | 733 | 4:11 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO N/O CONTRA 1206-01 Y SE CERRO POR CONTROL SE SECCIONALIZO MACHETE QUEMADO SALIDA DEL 1206-02 | S22080200113 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 251 | 2022-08-02 | 183983 | keep | 0 | Aug | 2022 | 0.12531 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
BARRANQUITAS | 2022-08-02 11:19 | 2022-08-02 13:15 | 1308 | 1:56 | P | OTRAS CAUSAS | ABRIR C/L PARA RELOCALIZAR TENSOR, INSTALO VARETA AISLATIVA | C22080200065 | New_Event | Other Causes | Include | Include | Other | 116 | 2022-08-02 | 151728 | keep | 0 | Aug | 2022 | 0.10334 | 0.00089087 | Sustained | FALSE | FALSE | Not_TMED_Event | 1308
CANOVANAS | 2022-08-02 11:29 | 2022-08-02 11:59 | 1 | 0:30 | P | DESGANCHE | 2 X30 EN CORTE DE LINEA Y 2 X 20 EN RISER SE RETIRO BEJUCO DE LA LINEA | R22080200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-08-02 | 30 | keep | 0 | Aug | 2022 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-02 11:36 | 2022-08-02 13:08 | 8 | 1:32 | P | CONDUCTOR ROTO O ABIERTO | ABRIO C/L PARA REPARAR CONDUCTOR PRIMARIO ROTO | C22080200066 | New_Event | Primary Wire Break | Include | Include | Equipment | 92 | 2022-08-02 | 736 | keep | 0 | Aug | 2022 | 0.00050129 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-02 11:38 | 2022-08-02 12:40 | 5 | 1:02 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE DE FASE POR AVE | P22080200065 | New_Event | Animals | Include | Include | Wildlife | 62 | 2022-08-02 | 310 | keep | 0 | Aug | 2022 | 0.00021114 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-02 11:45 | 2022-08-02 16:10 | 27 | 4:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO QUE NO REGULA VOLTAJE DE 25KVA POR UNO DE 50KVA Y SE REMPLAZAO BAJANTES PRIMARIOS Y SECUNDARIOS | M22080200176 | New_Event | Service Transformer Failure | Include | Include | Equipment | 265 | 2022-08-02 | 7155 | keep | 0 | Aug | 2022 | 0.0048732 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-08-02 11:49 | 2022-08-02 13:37 | 150 | 1:48 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZO DESGANCHE EN AEREO PROVISIONAL Y SE LLEVO PUENTE DE LINEA A CAJA EN C/L | B22080200037 | New_Event | Primary Wire Break | Include | Include | Equipment | 108 | 2022-08-02 | 16200 | keep | 0 | Aug | 2022 | 0.011034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-08-02 11:55 | 2022-08-02 15:05 | 10 | 3:10 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR SE RETIRO IGUANA | A22080200107 | New_Event | Animals | Include | Include | Wildlife | 190 | 2022-08-02 | 1900 | keep | 0 | Aug | 2022 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-02 11:59 | 2022-08-02 19:24 | 8 | 7:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA AVERIADO Y 150 PIES DE SECUNDARIA | R22080200042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 445 | 2022-08-02 | 3560 | keep | 0 | Aug | 2022 | 0.0024247 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-08-02 12:19 | 2022-08-02 15:13 | 30 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22080200108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-02 | 5220 | keep | 0 | Aug | 2022 | 0.0035553 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-02 12:20 | 2022-08-02 12:55 | 4 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22080100113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-08-02 | 140 | keep | 0 | Aug | 2022 | 9.5353e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-08-02 12:23 | 2022-08-02 12:24 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22080200076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 527 | keep | 0 | Aug | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-08-02 12:31 | 2022-08-02 14:52 | 1 | 2:21 | P | DESGANCHE | 2 X 40 EN C/L SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22080200075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-08-02 | 141 | keep | 0 | Aug | 2022 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-02 12:35 | 2022-08-02 12:43 | 11 | 0:08 | P | PROBLEMA DEL CLIENTE | 3 X 10 EN MONTURA XMR SE ABRIO EN SU PARA PODER CONECTAR MONTURA XMR BOMBAS AAA | B22080200038 | New_Event | Customer-Related Interruption | Include | Include | Public | 8 | 2022-08-02 | 88 | keep | 0 | Aug | 2022 | 5.9936e-05 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-08-02 12:40 | 2022-08-02 15:58 | 68 | 3:18 | P | DESGANCHE | 1 X 50 EN C/L Y SE REALIZO DESGANCHE | B22080200046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 198 | 2022-08-02 | 13464 | keep | 0 | Aug | 2022 | 0.0091703 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BARRANQUITAS | 2022-08-02 12:45 | 2022-08-02 15:34 | 56 | 2:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | C22080200074 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 169 | 2022-08-02 | 9464 | keep | 0 | Aug | 2022 | 0.0064459 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
ARECIBO | 2022-08-02 12:47 | 2022-08-02 14:30 | 40 | 1:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A22080200114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-08-02 | 4120 | keep | 0 | Aug | 2022 | 0.0028061 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-02 13:00 | 2022-08-02 13:22 | 37 | 0:22 | P | ANIMAL | 1 X 20 EN C/L Y 1 X 15 EN XMR CRUCE X AVE | C22080200077 | New_Event | Animals | Include | Include | Wildlife | 22 | 2022-08-02 | 814 | keep | 0 | Aug | 2022 | 0.00055441 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
ARECIBO | 2022-08-02 13:15 | 2022-08-02 13:57 | 2 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REEMPLAZO BARRAS SECUNDARIAS DAÃ‘ADAS | A22080200117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2022-08-02 | 84 | keep | 0 | Aug | 2022 | 5.7212e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-02 13:16 | 2022-08-02 13:44 | 4702 | 0:28 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR POR AISLADOR PARTIDO EN EL TRONCAL ENTRO EN SERVICIO EL 25% | B22080200052 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 28 | 2022-08-02 | 131656 | keep | 0 | Aug | 2022 | 0.08967 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
MAYAGÃœEZ | 2022-08-02 13:24 | 2022-08-02 14:47 | 2 | 1:23 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE SEPARARON LINEAS CRUZADAS | M22080200197 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 83 | 2022-08-02 | 166 | keep | 0 | Aug | 2022 | 0.00011306 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-08-02 13:44 | 2022-08-02 16:00 | 30 | 2:16 | P | TRANSFORMADOR AVERIADO | SE ABRE EN SU-X PARA REMPLAZAR PM T-22 75KVA A 7.620 KV ABIERTO EN T-23 POR AVERIA SOTERRADADA PREVIA | P22080200083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 136 | 2022-08-02 | 4080 | keep | 0 | Aug | 2022 | 0.0027789 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-02 13:44 | 2022-08-02 16:09 | 3526 | 2:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO Y SE LLEVO CONDUCTOR AL AISLADOR | B22080200052 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 145 | 2022-08-02 | 511270 | keep | 0 | Aug | 2022 | 0.34822 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-02 13:57 | 2022-08-02 19:24 | 60 | 5:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22080200209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-08-02 | 19620 | keep | 0 | Aug | 2022 | 0.013363 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-02 13:59 | 2022-08-02 16:40 | 300 | 2:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CRUCETA ROTA POR BRAZO AISLADOR Y SE RETIRO BAMBUAS CAIDAS SOBRE LAS LINEAS | M22080200211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-08-02 | 48300 | keep | 0 | Aug | 2022 | 0.032897 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-02 14:04 | 2022-08-02 17:06 | 1 | 3:02 | P | ANIMAL | 1 X 20 EN MONTURA XMR BOMBAS AAA AVE CRUZO LINEAS | B22080200065 | New_Event | Animals | Include | Include | Wildlife | 182 | 2022-08-02 | 182 | keep | 0 | Aug | 2022 | 0.00012396 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-02 14:04 | 2022-08-02 15:40 | 1 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22080200212 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2022-08-02 | 96 | keep | 0 | Aug | 2022 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-02 14:07 | 2022-08-02 17:26 | 10 | 3:19 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO PALMAS SOBRE LINEA | A22080200122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-08-02 | 1990 | keep | 0 | Aug | 2022 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-02 14:08 | 2022-08-02 14:09 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080200082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 1017 | keep | 0 | Aug | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
FAJARDO | 2022-08-02 14:15 | 2022-08-02 14:16 | 20 | 0:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRNASFORMADOR AVERIADO | R22080200054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-08-02 | 20 | keep | 0 | Aug | 2022 | 1.3622e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-08-02 14:16 | 2022-08-02 17:28 | 12 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE PRIMARIO | A22080200124 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2022-08-02 | 2304 | keep | 0 | Aug | 2022 | 0.0015692 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-02 14:20 | 2022-08-02 17:05 | 60 | 2:45 | P | DESGANCHE | 1 X 50 EN BOOSTER REQUIERE DESGANCHE | M22080200216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-08-02 | 9900 | keep | 0 | Aug | 2022 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-08-02 14:21 | 2022-08-02 15:34 | 78 | 1:13 | P | ANIMAL | 1X 40 EN RISER Y 1 X 50 EN CL CRUZE POR AVE | R22080200052 | New_Event | Animals | Include | Include | Wildlife | 73 | 2022-08-02 | 5694 | keep | 0 | Aug | 2022 | 0.0038782 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
UTUADO | 2022-08-02 14:21 | 2022-08-02 16:38 | 25 | 2:17 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR POR RAYOS | A22080200125 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 137 | 2022-08-02 | 3425 | keep | 0 | Aug | 2022 | 0.0023328 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-02 14:22 | 2022-08-02 14:26 | 68 | 0:04 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL QUEDO EN 0 AMP. | S22080200000 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-08-02 | 272 | keep | 0 | Aug | 2022 | 0.00018526 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-08-02 14:22 | 2022-08-02 14:26 | 536 | 0:04 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL QUEDO EN 0 AMP. | S22080200000 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-08-02 | 2144 | keep | 0 | Aug | 2022 | 0.0014603 | 0.00036507 | Momentary | FALSE | FALSE | Not_TMED_Event | 536
SAN JUAN | 2022-08-02 14:22 | 2022-08-02 14:26 | 348 | 0:04 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL QUEDO EN 0 AMP. | S22080200000 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-08-02 | 1392 | keep | 0 | Aug | 2022 | 0.00094808 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-08-02 14:22 | 2022-08-02 14:26 | 300 | 0:04 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL QUEDO EN 0 AMP. | S22080200000 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-08-02 | 1200 | keep | 0 | Aug | 2022 | 0.00081731 | 0.00020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-02 14:22 | 2022-08-02 14:26 | 733 | 0:04 | T | CONDUCTOR ROTO O ABIERTO | DISPARO LLEVA 1102-01,4,5 Y 90% DEL 1105-05 SE CERRO POR CONTROL QUEDO EN 0 AMP. | S22080200000 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2022-08-02 | 2932 | keep | 0 | Aug | 2022 | 0.001997 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
VEGA BAJA | 2022-08-02 14:24 | 2022-08-02 16:12 | 6 | 1:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 50KVA | A22080200126 | New_Event | Service Transformer Failure | Include | Include | Equipment | 108 | 2022-08-02 | 648 | keep | 0 | Aug | 2022 | 0.00044135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-08-02 14:25 | 2022-08-02 16:25 | 90 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | A22080200128 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2022-08-02 | 10800 | keep | 0 | Aug | 2022 | 0.0073558 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-08-02 14:26 | 2022-08-02 15:07 | 68 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 41 | 2022-08-02 | 2788 | keep | 0 | Aug | 2022 | 0.0018989 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-08-02 14:26 | 2022-08-02 15:07 | 536 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 41 | 2022-08-02 | 21976 | keep | 0 | Aug | 2022 | 0.014968 | 0.00036507 | Sustained | FALSE | FALSE | Not_TMED_Event | 536
SAN JUAN | 2022-08-02 14:26 | 2022-08-02 15:07 | 348 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 41 | 2022-08-02 | 14268 | keep | 0 | Aug | 2022 | 0.0097179 | 0.00023702 | Sustained | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-08-02 14:26 | 2022-08-02 15:07 | 300 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 41 | 2022-08-02 | 12300 | keep | 0 | Aug | 2022 | 0.0083775 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-02 14:26 | 2022-08-02 15:07 | 733 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR ALAMBRE EN EL PISO DESPUES DE SALIDA RISER LLEVA 1102-1,4,5 Y 90% DEL 1105-05 | S22080200207 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 41 | 2022-08-02 | 30053 | keep | 0 | Aug | 2022 | 0.020469 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
PONCE | 2022-08-02 14:26 | 2022-08-02 17:00 | 1979 | 2:34 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV CANAS T.C. | P22080200173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 154 | 2022-08-02 | 304766 | keep | 0 | Aug | 2022 | 0.20757 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2022-08-02 14:26 | 2022-08-02 15:55 | 3114 | 1:29 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV CANAS T.C. | P22080200173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 89 | 2022-08-02 | 277146 | keep | 0 | Aug | 2022 | 0.18876 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-08-02 14:26 | 2022-08-02 17:57 | 5069 | 3:31 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV CANAS T.C. | P22080200173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 211 | 2022-08-02 | 1069559 | keep | 0 | Aug | 2022 | 0.72847 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2022-08-02 14:26 | 2022-08-02 15:55 | 2696 | 1:29 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV CANAS T.C. | P22080200173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 89 | 2022-08-02 | 239944 | keep | 0 | Aug | 2022 | 0.16342 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2022-08-02 14:26 | 2022-08-02 15:55 | 5063 | 1:29 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV CANAS T.C. | P22080200173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 89 | 2022-08-02 | 450607 | keep | 0 | Aug | 2022 | 0.30691 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
YAUCO | 2022-08-02 14:26 | 2022-08-02 14:27 | 3036 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22080200221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 3036 | keep | 0 | Aug | 2022 | 0.0020678 | 0.0020678 | Momentary | FALSE | FALSE | Not_TMED_Event | 3036
BARRANQUITAS | 2022-08-02 14:27 | 2022-08-02 14:28 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080200082 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 1017 | keep | 0 | Aug | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
PONCE | 2022-08-02 14:30 | 2022-08-02 14:31 | 1712 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE COLOCA RR EN OFF Y SE REALIZA PRUEBA QUEDANDO EN SERVICIO | P22080200098 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-02 | 1712 | keep | 0 | Aug | 2022 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
YAUCO | 2022-08-02 14:30 | 2022-08-02 14:31 | 2064 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | M22080200223 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-02 | 2064 | keep | 0 | Aug | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
AGUADILLA | 2022-08-02 14:30 | 2022-08-02 21:41 | 6 | 7:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | M22080200035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 431 | 2022-08-02 | 2586 | keep | 0 | Aug | 2022 | 0.0017613 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-08-02 14:31 | 2022-08-02 19:40 | 50 | 5:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTE LLUVIA | P22080200215 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 309 | 2022-08-02 | 15450 | keep | 0 | Aug | 2022 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-02 14:31 | 2022-08-02 15:05 | 688 | 0:34 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO EN TRONCAL DE ALIMENTADOR | M22080200238 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 34 | 2022-08-02 | 23392 | keep | 0 | Aug | 2022 | 0.015932 | 0.00046859 | Sustained | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2022-08-02 14:59 | 2022-08-02 15:00 | 2113 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE DE INTERUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P22080200165 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2022-08-02 | 2113 | keep | 0 | Aug | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
MAYAGÃœEZ | 2022-08-02 15:01 | 2022-08-03 15:00 | 10 | 23:59 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES Y SE INSTALO POSTE PRIMARIO SE CERRO PEUNTES | M22080200235 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1439 | 2022-08-02 | 14390 | keep | 0 | Aug | 2022 | 0.009801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-02 15:01 | 2022-08-02 19:40 | 4 | 4:39 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 50 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | M22080200235 | New_Event | Primary Pole Failure | Include | Include | Equipment | 279 | 2022-08-02 | 1116 | keep | 0 | Aug | 2022 | 0.0007601 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-02 15:05 | 2022-08-02 17:10 | 12 | 2:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO ENREDADERA | R22080200056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-08-02 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-08-02 15:05 | 2022-08-02 19:12 | 2064 | 4:07 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR DE EMERGENCIA A PETICION DE MIGUEL SANCHEZ POR LINEA PRIMARIA ROTA EN EL TRONCAL DEL ALIMENTADOR SE REPARO Y SE CERRO EL INTERRUPTOR | M22080200238 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 247 | 2022-08-02 | 509808 | keep | 0 | Aug | 2022 | 0.34723 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-02 15:06 | 2022-08-02 16:54 | 7 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA Y COMPLETAR EL NEUTRAL | C22080200092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2022-08-02 | 756 | keep | 0 | Aug | 2022 | 0.00051491 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-02 15:07 | 2022-08-02 16:44 | 68 | 1:37 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 97 | 2022-08-02 | 6596 | keep | 0 | Aug | 2022 | 0.0044925 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-02 15:07 | 2022-08-02 16:44 | 536 | 1:37 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 97 | 2022-08-02 | 51992 | keep | 0 | Aug | 2022 | 0.035412 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-02 15:07 | 2022-08-02 16:44 | 348 | 1:37 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 97 | 2022-08-02 | 33756 | keep | 0 | Aug | 2022 | 0.022991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-02 15:07 | 2022-08-02 16:44 | 300 | 1:37 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR ALAMBRE EN EL PISO DESPUES DE SALIDA RISER | S22080200207 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 97 | 2022-08-02 | 29100 | keep | 0 | Aug | 2022 | 0.01982 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-02 15:07 | 2022-08-02 16:44 | 733 | 1:37 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR ALAMBRE EN EL PISO DESPUES DE SALIDA RISER LLEVA 1102-1,4,5 Y 90% DEL 1105-05 | S22080200207 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 97 | 2022-08-02 | 71101 | keep | 0 | Aug | 2022 | 0.048427 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-02 15:07 | 2022-08-02 15:23 | 7 | 0:16 | P | PROBLEMA DEL CLIENTE | SE ABRE T-33 PARA RECONECTAR TOMA DE CLIENTE | S22080200193 | New_Event | Customer-Related Interruption | Include | Include | Public | 16 | 2022-08-02 | 112 | keep | 0 | Aug | 2022 | 7.6283e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-08-02 15:10 | 2022-08-02 18:50 | 54 | 3:40 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO | C22080200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-08-02 | 11880 | keep | 0 | Aug | 2022 | 0.0080914 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2022-08-02 15:16 | 2022-08-02 15:17 | 641 | 0:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA CERRAR N/O EN B.I. SE REMPLAZO MACHETE | S22080200113 | Partial_restoration | Switch Failure | Include | Include | Equipment | 1 | 2022-08-02 | 641 | keep | 0 | Aug | 2022 | 0.00043658 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-02 15:17 | 2022-08-03 19:02 | 40 | 27:45 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO CABLE DE RISER A T-4 | S22080100153 | New_Event | UG Cable Fault | Include | Include | Equipment | 1665 | 2022-08-02 | 66600 | keep | 0 | Aug | 2022 | 0.045361 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-02 15:21 | 2022-08-02 17:59 | 60 | 2:38 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE DE BAMBUAS | A22080200143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-08-02 | 9480 | keep | 0 | Aug | 2022 | 0.0064568 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-02 15:25 | 2022-08-02 19:30 | 60 | 4:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080200252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-08-02 | 14700 | keep | 0 | Aug | 2022 | 0.010012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-08-02 15:28 | 2022-08-02 15:29 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22080200181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 2379 | keep | 0 | Aug | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
CANOVANAS | 2022-08-02 15:29 | 2022-08-02 16:23 | 7 | 0:54 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R22080200059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 54 | 2022-08-02 | 378 | keep | 0 | Aug | 2022 | 0.00025745 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-02 15:32 | 2022-08-02 16:00 | 4 | 0:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO XMR | B22080200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2022-08-02 | 112 | keep | 0 | Aug | 2022 | 7.6283e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-08-02 15:35 | 2022-08-02 21:09 | 80 | 5:34 | P | DESGANCHE | 3 X 65 Y 2 X 40 EN DISTINTOS CORTES DE LINEA SE REALIZO DESGANCHE MASIVO | M22080200259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 334 | 2022-08-02 | 26720 | keep | 0 | Aug | 2022 | 0.018199 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-02 15:38 | 2022-08-02 15:50 | 2391 | 0:12 | T | NO SE REPORTO CAUSA | DISPARO TENIA R/R OFF SE VERIFICO CON PERSONAL TRABAJANDO EN V.L. Y INDICARON QUE SE PODIA CERRAR Y SE CERRO POR CONTROL | S22080200214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-08-02 | 28692 | keep | 0 | Aug | 2022 | 0.019542 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2022-08-02 15:39 | 2022-08-02 17:30 | 100 | 1:51 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22080200100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-08-02 | 11100 | keep | 0 | Aug | 2022 | 0.0075602 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-08-02 15:47 | 2022-08-02 18:35 | 234 | 2:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22080200192 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 168 | 2022-08-02 | 39312 | keep | 0 | Aug | 2022 | 0.026775 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2022-08-02 15:47 | 2022-08-02 18:35 | 2468 | 2:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 200 | P22080200192 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 168 | 2022-08-02 | 414624 | keep | 0 | Aug | 2022 | 0.2824 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
HUMACAO | 2022-08-02 15:57 | 2022-08-02 19:12 | 55 | 3:15 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22080200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-08-02 | 10725 | keep | 0 | Aug | 2022 | 0.0073047 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
YAUCO | 2022-08-02 15:57 | 2022-08-02 18:59 | 2952 | 3:02 | T | CAUSAS EXTERNAS | SE ABRIO INTERRUPTOR PARA PODER CERRAR PUENTES PRIMARIOS ABIERTOS EN EL TRONCAL DEL ALIMENTADOR EN AVERIA DE TRES POSTES PRIMARIOS ROTOS | M22080200273 | New_Event | Damage From Public | Include | Include | Public | 182 | 2022-08-02 | 537264 | keep | 0 | Aug | 2022 | 0.36593 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
PONCE | 2022-08-02 15:58 | 2022-08-02 15:59 | 2113 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22080200194 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2022-08-02 | 2113 | keep | 0 | Aug | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-08-02 16:00 | 2022-08-02 16:01 | 2113 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22080200196 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2022-08-02 | 2113 | keep | 0 | Aug | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2022-08-02 16:06 | 2022-08-02 16:07 | 688 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22080200218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 688 | keep | 0 | Aug | 2022 | 0.00046859 | 0.00046859 | Momentary | FALSE | FALSE | Not_TMED_Event | 688
GUAYAMA | 2022-08-02 16:07 | 2022-08-02 17:50 | 50 | 1:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L CAJA PRIMARIA AVERIADA | P22080200203 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2022-08-02 | 5150 | keep | 0 | Aug | 2022 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-02 16:08 | 2022-08-02 17:29 | 2113 | 1:21 | T | TERMINACION SOTERRADA AVERIADA | DISPARO INTERRUPTOR SE ABRE MACHETES PONCE BY-PASS Y SE REALIZA PRUEBA QUEDANDO EN SERVICIO | P22080200205 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 81 | 2022-08-02 | 171153 | keep | 0 | Aug | 2022 | 0.11657 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
SAN JUAN | 2022-08-02 16:20 | 2022-08-02 19:12 | 89 | 2:52 | P | CONDUCTOR ROTO O ABIERTO | SE ESTABLECE GOI SJ-220802-03 PARA LEVANTAR LINEA PRIMARIA | S22080200197 | New_Event | Primary Wire Break | Include | Include | Equipment | 172 | 2022-08-02 | 15308 | keep | 0 | Aug | 2022 | 0.010426 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
CANOVANAS | 2022-08-02 16:24 | 2022-08-02 18:58 | 1 | 2:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R22080200060 | New_Event | Cutout Failure | Include | Include | Equipment | 154 | 2022-08-02 | 154 | keep | 0 | Aug | 2022 | 0.00010489 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-02 16:27 | 2022-08-02 21:12 | 20 | 4:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M22080200284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-08-02 | 5700 | keep | 0 | Aug | 2022 | 0.0038822 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-02 16:35 | 2022-08-02 16:36 | 6 | 0:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON CONECTORES SECUNDARIOS | S22080200221 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1 | 2022-08-02 | 6 | keep | 0 | Aug | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-08-02 16:38 | 2022-08-02 19:01 | 100 | 2:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A22080200151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-08-02 | 14300 | keep | 0 | Aug | 2022 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-02 16:51 | 2022-08-02 20:07 | 70 | 3:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y SE REMPLAZO CAJA PRIMARIA | S22080200235 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2022-08-02 | 13720 | keep | 0 | Aug | 2022 | 0.0093446 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-08-02 16:51 | 2022-08-03 11:37 | 114 | 18:46 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22080200235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1126 | 2022-08-02 | 128364 | keep | 0 | Aug | 2022 | 0.087428 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
BARRANQUITAS | 2022-08-02 16:52 | 2022-08-02 18:03 | 40 | 1:11 | P | CONDUCTOR ROTO O ABIERTO | ABRIR XMR PARA REMPLAZAR BAJANTES PRIMARIOS Y SECUNDARIOS | C22080100152 | New_Event | Primary Wire Break | Include | Include | Equipment | 71 | 2022-08-02 | 2840 | keep | 0 | Aug | 2022 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-02 17:11 | 2022-08-02 18:11 | 290 | 1:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22080200111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-08-02 | 17400 | keep | 0 | Aug | 2022 | 0.011851 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
PONCE | 2022-08-02 17:29 | 2022-08-03 14:23 | 10 | 20:54 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN RISER Y SE REMPLAZO CAJA SECA EN MH 16 FUERTES LLUVIAS | P22080200261 | New_Event | UG Cable Fault | Include | Include | Equipment | 1254 | 2022-08-02 | 12540 | keep | 0 | Aug | 2022 | 0.0085409 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-02 17:42 | 2022-08-02 17:44 | 215 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-02 | 430 | keep | 0 | Aug | 2022 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-08-02 17:45 | 2022-08-02 20:01 | 110 | 2:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22080200115 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-08-02 | 14960 | keep | 0 | Aug | 2022 | 0.010189 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
VEGA BAJA | 2022-08-02 17:47 | 2022-08-02 19:34 | 100 | 1:47 | P | CONDUCTOR ROTO O ABIERTO | REPARAR BAJANTE PRIMARIO | A22080200155 | New_Event | Primary Wire Break | Include | Include | Equipment | 107 | 2022-08-02 | 10700 | keep | 0 | Aug | 2022 | 0.0072877 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-08-02 18:11 | 2022-08-02 20:30 | 150 | 2:19 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | P22080200257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-08-02 | 20850 | keep | 0 | Aug | 2022 | 0.014201 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-08-02 18:16 | 2022-08-02 19:06 | 6 | 0:50 | P | CAUSAS EXTERNAS | 1 X 10 EN TRANSFORMADOR VEHICULO IMPACTO POSTE | R22080200063 | New_Event | Damage From Public | Include | Include | Public | 50 | 2022-08-02 | 300 | keep | 0 | Aug | 2022 | 0.00020433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-08-02 18:25 | 2022-08-02 20:58 | 73 | 2:33 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 65 EN RISER EN ENTRADA DE RISER Y 2 X 65 EN SALIDA DE RISER SWITCHING UNIT CONTAMINADO | P22080200026 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 153 | 2022-08-02 | 11169 | keep | 0 | Aug | 2022 | 0.0076072 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
CANOVANAS | 2022-08-02 18:31 | 2022-08-02 18:42 | 4 | 0:11 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R22080200064 | New_Event | Animals | Include | Include | Wildlife | 11 | 2022-08-02 | 44 | keep | 0 | Aug | 2022 | 2.9968e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-08-02 18:34 | 2022-08-03 12:35 | 8 | 18:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS PARTIDAS | M22080200309 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1081 | 2022-08-02 | 8648 | keep | 0 | Aug | 2022 | 0.0058901 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-02 18:40 | 2022-08-02 19:15 | 15 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R22080200065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-08-02 | 525 | keep | 0 | Aug | 2022 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-02 18:41 | 2022-08-03 08:40 | 2 | 13:59 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A22080200163 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 839 | 2022-08-02 | 1678 | keep | 0 | Aug | 2022 | 0.0011429 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2022-08-02 18:43 | 2022-08-03 09:38 | 15 | 14:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN XMR MAL TIEMPO LLUVIAS | P22080200266 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 895 | 2022-08-02 | 13425 | keep | 0 | Aug | 2022 | 0.0091437 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-02 18:44 | 2022-08-02 22:36 | 6 | 3:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A22080200164 | New_Event | Cutout Failure | Include | Include | Equipment | 232 | 2022-08-02 | 1392 | keep | 0 | Aug | 2022 | 0.00094808 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-02 18:54 | 2022-08-02 21:20 | 60 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22080200314 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2022-08-02 | 8760 | keep | 0 | Aug | 2022 | 0.0059664 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-08-02 19:05 | 2022-08-02 19:42 | 1 | 0:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA AVERIADA | P22080200271 | New_Event | Cutout Failure | Include | Include | Equipment | 37 | 2022-08-02 | 37 | keep | 0 | Aug | 2022 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-02 19:21 | 2022-08-03 12:08 | 3 | 16:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | P22080200277 | New_Event | Primary Wire Break | Include | Include | Equipment | 1007 | 2022-08-02 | 3021 | keep | 0 | Aug | 2022 | 0.0020576 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-08-02 19:23 | 2022-08-02 19:25 | 2826 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-02 | 5652 | keep | 0 | Aug | 2022 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
YAUCO | 2022-08-02 19:30 | 2022-08-02 21:12 | 100 | 1:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080200082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-08-02 | 10200 | keep | 0 | Aug | 2022 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-02 19:52 | 2022-08-02 19:53 | 641 | 0:01 | T | OTRAS CAUSAS | DISPARO AL CERRAR 1105-01 PARA NORMALIZAR CARGA EN V.L.D2022-00343 LLEVA 1105-01 HAY QUE FASEAR | S22080200000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-08-02 | 641 | keep | 0 | Aug | 2022 | 0.00043658 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-08-02 19:52 | 2022-08-02 19:53 | 308 | 0:01 | T | OTRAS CAUSAS | DISPARO AL CERRAR 1105-01 PARA NORMALIZAR CARGA EN V.L.D2022-00343 LLEVA 1105-01 HAY QUE FASEAR | S22080200000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-08-02 | 308 | keep | 0 | Aug | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2022-08-02 19:56 | 2022-08-03 08:55 | 4 | 12:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080200166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 779 | 2022-08-02 | 3116 | keep | 0 | Aug | 2022 | 0.0021223 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-02 20:22 | 2022-08-02 22:06 | 3754 | 1:44 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO PARA REEMPLAZAR MACHETE QUEMADO Y SE NORMALIZO | R22080200070 | New_Event | Switch Failure | Include | Include | Equipment | 104 | 2022-08-02 | 390416 | keep | 0 | Aug | 2022 | 0.26591 | 0.0025568 | Sustained | FALSE | FALSE | Not_TMED_Event | 3754
AGUADILLA | 2022-08-02 20:44 | 2022-08-02 23:00 | 180 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22080200337 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2022-08-02 | 24480 | keep | 0 | Aug | 2022 | 0.016673 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
PONCE | 2022-08-02 20:45 | 2022-08-03 07:00 | 12 | 10:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 8 EN XMR SE DESCONECTO TOMA SOTERRADA AVERIADA | P22080200295 | New_Event | Secondary Wire Break | Include | Include | Equipment | 615 | 2022-08-02 | 7380 | keep | 0 | Aug | 2022 | 0.0050265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-08-02 20:54 | 2022-08-03 01:55 | 150 | 5:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M22080200342 | New_Event | Cutout Failure | Include | Include | Equipment | 301 | 2022-08-02 | 45150 | keep | 0 | Aug | 2022 | 0.030751 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-08-02 21:00 | 2022-08-03 03:25 | 40 | 6:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTES VIENTOS | M22080200371 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 385 | 2022-08-02 | 15400 | keep | 0 | Aug | 2022 | 0.010489 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-08-02 21:09 | 2022-08-03 10:44 | 80 | 13:35 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22080200300 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2022-08-02 | 65200 | keep | 0 | Aug | 2022 | 0.044407 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-08-02 21:14 | 2022-08-03 09:43 | 23 | 12:29 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P22080200304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 749 | 2022-08-02 | 17227 | keep | 0 | Aug | 2022 | 0.011733 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2022-08-02 21:16 | 2022-08-03 02:30 | 45 | 5:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA CAJA EN MALAS CONDICIONES SE REFIRIO PARA CAMBIO | M22080200306 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2022-08-02 | 14130 | keep | 0 | Aug | 2022 | 0.0096239 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-08-02 21:17 | 2022-08-02 23:19 | 100 | 2:02 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA @ ENTRADA DE PROVISIONAL AEREO (NO FUNDIO) | B22080200129 | New_Event | Primary Wire Break | Include | Include | Equipment | 122 | 2022-08-02 | 12200 | keep | 0 | Aug | 2022 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-08-02 21:24 | 2022-08-03 05:11 | 5 | 7:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR FUERTES VIENTOS | M22080200359 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 467 | 2022-08-02 | 2335 | keep | 0 | Aug | 2022 | 0.0015904 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-02 21:41 | 2022-08-02 21:42 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO 1709-05 Y 50% DE SU CARGA 1909-07 | B22080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 766 | keep | 0 | Aug | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-08-02 21:41 | 2022-08-02 21:42 | 2364 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1709-03 LLEVANDO 1709-05 Y 50% DE SU CARGA 1909-07 | B22080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 2364 | keep | 0 | Aug | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
AGUADILLA | 2022-08-02 21:41 | 2022-08-03 15:58 | 7 | 18:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 15KVA X 15KVA | M22080200362 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1097 | 2022-08-02 | 7679 | keep | 0 | Aug | 2022 | 0.0052301 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-08-02 22:04 | 2022-08-03 09:52 | 186 | 11:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO PENCAS DE PALMA DE LA LINEA | C22080200160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 708 | 2022-08-02 | 131688 | keep | 0 | Aug | 2022 | 0.089692 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
SAN JUAN | 2022-08-02 22:35 | 2022-08-02 22:37 | 514 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1520-05 | S22080200300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-02 | 1028 | keep | 0 | Aug | 2022 | 0.00070017 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-08-02 22:35 | 2022-08-02 22:37 | 752 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL - CARGA TRANSFERIDA AL 1520-05 | S22080200300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-02 | 1504 | keep | 0 | Aug | 2022 | 0.0010244 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2022-08-02 22:35 | 2022-08-02 22:37 | 68 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1520-01 LLEVA LA CARGA DEL 1520-04 | S22080200300 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-02 | 136 | keep | 0 | Aug | 2022 | 9.2629e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
PONCE | 2022-08-02 22:46 | 2022-08-03 08:17 | 9 | 9:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO EN XMR | P22080200326 | New_Event | Primary Wire Break | Include | Include | Equipment | 571 | 2022-08-02 | 5139 | keep | 0 | Aug | 2022 | 0.0035001 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-08-02 23:20 | 2022-08-03 10:33 | 40 | 11:13 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y SE INSTALO ESPACEADOR | S22080200302 | New_Event | Primary Wire Break | Include | Include | Equipment | 673 | 2022-08-02 | 26920 | keep | 0 | Aug | 2022 | 0.018335 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-02 23:23 | 2022-08-02 23:24 | 171 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO - CARGA TRANSFERIDA AL 1110-05 | S22080200302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 171 | keep | 0 | Aug | 2022 | 0.00011647 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-08-02 23:23 | 2022-08-02 23:24 | 1837 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO - CARGA TRANSFERIDA AL 1110-05 | S22080200302 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 1837 | keep | 0 | Aug | 2022 | 0.0012512 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
SAN JUAN | 2022-08-02 23:23 | 2022-08-02 23:24 | 283 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO LLEVA LA CARGA DEL 1102-02 LLEVA LA CARGA DEL 1102-03 | S22080200302 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-02 | 283 | keep | 0 | Aug | 2022 | 0.00019275 | 0.00019275 | Momentary | FALSE | FALSE | Not_TMED_Event | 283
SAN JUAN | 2022-08-02 23:24 | 2022-08-03 00:48 | 243 | 1:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO MEDIANTE G.O.I. SJ-220803-01 | S22080200303 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 84 | 2022-08-02 | 20412 | keep | 0 | Aug | 2022 | 0.013903 | 0.00016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 243
MAYAGÃœEZ | 2022-08-02 23:27 | 2022-08-02 23:28 | 1818 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22080200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-02 | 1818 | keep | 0 | Aug | 2022 | 0.0012382 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
MAYAGÃœEZ | 2022-08-02 23:27 | 2022-08-02 23:29 | 4381 | 0:02 | T | CABLE SOTERRADO AVERIADO | SALIDA SOTERRADA DE INTERRUPTOR QUEMADA SE TRANSFIRIO CARGA AL 6802-05 | M22080200379 | New_Event | UG Cable Fault | Include | Include | Equipment | 2 | 2022-08-02 | 8762 | keep | 0 | Aug | 2022 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-08-02 23:28 | 2022-08-02 23:29 | 888 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 888 | keep | 0 | Aug | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-08-02 23:28 | 2022-08-02 23:29 | 393 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 393 | keep | 0 | Aug | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-08-02 23:28 | 2022-08-02 23:29 | 4 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22080200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-02 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-08-02 23:43 | 2022-08-02 23:45 | 2697 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN OFF SE NORMALIZO RECIERRE Y SE CERRO INTERRUPTOR | A22080200174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-02 | 5394 | keep | 0 | Aug | 2022 | 0.0036738 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
FAJARDO | 2022-08-03 00:31 | 2022-08-03 09:21 | 40 | 8:50 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO | R22080300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 530 | 2022-08-03 | 21200 | keep | 0 | Aug | 2022 | 0.014439 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-03 00:33 | 2022-08-03 00:35 | 598 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 3405-03 SE CERRO POR CONTROL LLEVA EL 3403-01 | C22080300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-03 | 1196 | keep | 0 | Aug | 2022 | 0.00081459 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2022-08-03 00:33 | 2022-08-03 00:35 | 1001 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL LLEVA EL 3403-01 | C22080300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-03 | 2002 | keep | 0 | Aug | 2022 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
CANOVANAS | 2022-08-03 00:36 | 2022-08-03 10:41 | 30 | 10:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REMPLAZO CAJA AVERIADA | R22080300003 | New_Event | Cutout Failure | Include | Include | Equipment | 605 | 2022-08-03 | 18150 | keep | 0 | Aug | 2022 | 0.012362 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-03 00:43 | 2022-08-03 12:58 | 6 | 12:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA POR 50 KVA | S22080300055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 735 | 2022-08-03 | 4410 | keep | 0 | Aug | 2022 | 0.0030036 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-03 00:43 | 2022-08-03 00:45 | 598 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 3405-03 SE CERRO POR CONTROL LLEVA EL 3403-01 | C22080300004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-03 | 1196 | keep | 0 | Aug | 2022 | 0.00081459 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2022-08-03 00:43 | 2022-08-03 00:45 | 1001 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL LLEVA EL 3403-01 | C22080300004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-03 | 2002 | keep | 0 | Aug | 2022 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2022-08-03 00:48 | 2022-08-03 05:03 | 171 | 4:15 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO QUE CAYO SOBRE UN AUTOMOVIL MEDIANTE G.O.I. SJ-220803-01 CARGA TRANSFERIDA AL 1110-05 | S22080200303 | New_Event | Primary Wire Break | Include | Include | Equipment | 255 | 2022-08-03 | 43605 | keep | 0 | Aug | 2022 | 0.029699 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-08-03 00:48 | 2022-08-03 05:03 | 1837 | 4:15 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO QUE CAYO SOBRE UN AUTOMOVIL MEDIANTE G.O.I. SJ-220803-01 CARGA TRANSFERIDA AL 1110-05 | S22080200303 | New_Event | Primary Wire Break | Include | Include | Equipment | 255 | 2022-08-03 | 468435 | keep | 0 | Aug | 2022 | 0.31905 | 0.0012512 | Sustained | FALSE | FALSE | Not_TMED_Event | 1837
SAN JUAN | 2022-08-03 00:48 | 2022-08-03 05:03 | 283 | 4:15 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO QUE CAYO SOBRE UN AUTOMOVIL MEDIANTE G.O.I. SJ-220803-01 LLEVA LA CARGA DEL 1102-02 LLEVA LA CARGA DEL 1102-03 | S22080200303 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 255 | 2022-08-03 | 72165 | keep | 0 | Aug | 2022 | 0.049151 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-03 00:55 | 2022-08-03 01:30 | 4381 | 0:35 | T | CABLE SOTERRADO AVERIADO | SALIDA SOTERRADA DE INTERRUPTOR QUEMADA SE TRANSFIRIO CARGA AL 6802-05 | M22080200379 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 35 | 2022-08-03 | 153335 | keep | 0 | Aug | 2022 | 0.10444 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-08-03 00:55 | 2022-08-03 00:56 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR AL HACER PRUEBA AL 6802-04 | M22080300026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 990 | keep | 0 | Aug | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2022-08-03 00:55 | 2022-08-03 02:13 | 990 | 1:18 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | VACUMM SWITCH Y PARARRAYO AVERIADO | M22080300808 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 78 | 2022-08-03 | 77220 | keep | 0 | Aug | 2022 | 0.052594 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
CANOVANAS | 2022-08-03 01:15 | 2022-08-04 09:20 | 72 | 32:05 | P | ANIMAL | 1 X 50 Y 1 X 40 EN C/L Y 1 X 15 EN XMR AVE CRUZO LINEAS | R22080300117 | New_Event | Animals | Include | Include | Wildlife | 1925 | 2022-08-03 | 138600 | keep | 0 | Aug | 2022 | 0.0944 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
MAYAGÃœEZ | 2022-08-03 01:31 | 2022-08-03 14:53 | 4381 | 13:22 | T | CABLE SOTERRADO AVERIADO | SALIDA SOTERRADA DE INTERRUPTOR QUEMADA SE TRANSFIRIO CARGA AL 6802-05 | M22080200379 | New_Event | UG Cable Fault | Include | Include | Equipment | 802 | 2022-08-03 | 3513562 | keep | 0 | Aug | 2022 | 2.3931 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
VEGA BAJA | 2022-08-03 02:29 | 2022-08-03 09:59 | 40 | 7:30 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA SE RETIRO CULEBRA QUE CRUZO FASE A TIERRA | A22080300001 | New_Event | Animals | Include | Include | Wildlife | 450 | 2022-08-03 | 18000 | keep | 0 | Aug | 2022 | 0.01226 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-03 02:32 | 2022-08-03 03:01 | 990 | 0:29 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | VACUMM SWITCH Y PARARRAYO AVERIADO | M22080600808 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 29 | 2022-08-03 | 28710 | keep | 0 | Aug | 2022 | 0.019554 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2022-08-03 03:00 | 2022-08-04 12:41 | 36 | 33:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A LINEA Y SE CERRO FUSIBLE | S22080300318 | New_Event | Primary Wire Break | Include | Include | Equipment | 2021 | 2022-08-03 | 72756 | keep | 0 | Aug | 2022 | 0.049554 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2022-08-03 03:45 | 2022-08-03 08:48 | 118 | 5:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | C22080300006 | New_Event | Cutout Failure | Include | Include | Equipment | 303 | 2022-08-03 | 35754 | keep | 0 | Aug | 2022 | 0.024352 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
BAYAMON | 2022-08-03 05:14 | 2022-08-03 07:37 | 5961 | 2:23 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO INTERRUPTOR 1713-05 SECCIONALIZANDO AVERIA DE CAJA PRIMARIA, PARARRAYO QUEMADO Y DESGANCHE. 50% DE 1713-05 EN SERVICIO Y 95% DE 1717-02 EN SERVICIO | B22080300003 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-08-03 | 852423 | keep | 0 | Aug | 2022 | 0.58058 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-03 05:14 | 2022-08-03 07:37 | 865 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO INTERRUPTOR 1713-05 SECCIONALIZANDO AVERIA DE CAJA PRIMARIA, PARARRAYO QUEMADO Y DESGANCHE. 50% DE 1713-05 EN SERVICIO Y 95% DE 1717-02 EN SERVICIO | B22080300003 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-08-03 | 123695 | keep | 0 | Aug | 2022 | 0.084248 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
MAYAGÃœEZ | 2022-08-03 05:35 | 2022-08-03 12:01 | 990 | 6:26 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO PRUEBAS VACUMM SWITCH#6 | M22080301079 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 386 | 2022-08-03 | 382140 | keep | 0 | Aug | 2022 | 0.26027 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-03 05:41 | 2022-08-03 12:22 | 80 | 6:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22080300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 401 | 2022-08-03 | 32080 | keep | 0 | Aug | 2022 | 0.02185 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-03 05:42 | 2022-08-03 09:50 | 30 | 4:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA ZAFADA | A22080300003 | New_Event | Primary Wire Break | Include | Include | Equipment | 248 | 2022-08-03 | 7440 | keep | 0 | Aug | 2022 | 0.0050674 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-08-03 05:47 | 2022-08-03 05:48 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 2379 | keep | 0 | Aug | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
ARECIBO | 2022-08-03 05:57 | 2022-08-03 14:55 | 12 | 8:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA POR 50KVA NO HABIA DISPONIBLE DE LA MISMA CAPACIDAD | A22080300004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 538 | 2022-08-03 | 6456 | keep | 0 | Aug | 2022 | 0.0043972 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-03 06:00 | 2022-08-03 11:42 | 6 | 5:42 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE DESPEJO LINEA SECUNDARIA | S22080300064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 342 | 2022-08-03 | 2052 | keep | 0 | Aug | 2022 | 0.0013976 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-08-03 06:25 | 2022-08-03 14:08 | 20 | 7:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22080200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 463 | 2022-08-03 | 9260 | keep | 0 | Aug | 2022 | 0.0063069 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-03 06:27 | 2022-08-03 10:27 | 40 | 4:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M22080300112 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 240 | 2022-08-03 | 9600 | keep | 0 | Aug | 2022 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-03 06:33 | 2022-08-03 09:40 | 60 | 3:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-1 NO REPORTO CAUSA | S22080300026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2022-08-03 | 11220 | keep | 0 | Aug | 2022 | 0.0076419 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-03 06:34 | 2022-08-03 10:35 | 8 | 4:01 | P | OTRAS CAUSAS | 1 X 100 EN C/L FUSIBLE FATIGADO | R22080300005 | New_Event | Other Causes | Include | Include | Other | 241 | 2022-08-03 | 1928 | keep | 0 | Aug | 2022 | 0.0013132 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-03 06:37 | 2022-08-03 11:22 | 10 | 4:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22080300010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-08-03 | 2850 | keep | 0 | Aug | 2022 | 0.0019411 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-03 07:07 | 2022-08-03 08:07 | 26 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR TRASPATIO PARA REPARAR SECUNDARIA | C22080200144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-08-03 | 1560 | keep | 0 | Aug | 2022 | 0.0010625 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BARRANQUITAS | 2022-08-03 07:28 | 2022-08-03 08:35 | 390 | 1:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A LINEA | C22080200124 | New_Event | Primary Wire Break | Include | Include | Equipment | 67 | 2022-08-03 | 26130 | keep | 0 | Aug | 2022 | 0.017797 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2022-08-03 07:37 | 2022-08-03 08:23 | 2981 | 0:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO AVERIA DE CAJA PRIMARIA, PARARRAYO QUEMADO Y DESGANCHE. 55% DE 1713-05 EN SERVICIO | B22080300003 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 46 | 2022-08-03 | 137126 | keep | 0 | Aug | 2022 | 0.093396 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-03 07:39 | 2022-08-03 09:40 | 300 | 2:01 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R22080300006 | New_Event | Animals | Include | Include | Wildlife | 121 | 2022-08-03 | 36300 | keep | 0 | Aug | 2022 | 0.024724 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-08-03 07:47 | 2022-08-03 16:57 | 60 | 9:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22080300167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 550 | 2022-08-03 | 33000 | keep | 0 | Aug | 2022 | 0.022476 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-03 07:52 | 2022-08-03 10:38 | 40 | 2:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 Y 1 X 80 EN CORTES DE LINEA Y 1 X 65 EN RISER MAL TIEMPO VIENTOS FUERTES | M22080300173 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 166 | 2022-08-03 | 6640 | keep | 0 | Aug | 2022 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-03 08:00 | 2022-08-03 09:12 | 25 | 1:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22080300025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-08-03 | 1800 | keep | 0 | Aug | 2022 | 0.001226 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-08-03 08:08 | 2022-08-03 08:09 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22080300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 2299 | keep | 0 | Aug | 2022 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
VEGA BAJA | 2022-08-03 08:08 | 2022-08-03 11:03 | 97 | 2:55 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN C/L SE REMPLAZO PARARRAYO | B22080300149 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 175 | 2022-08-03 | 16975 | keep | 0 | Aug | 2022 | 0.011562 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
AGUADILLA | 2022-08-03 08:09 | 2022-08-03 13:01 | 80 | 4:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080300190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2022-08-03 | 23360 | keep | 0 | Aug | 2022 | 0.01591 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-08-03 08:11 | 2022-08-03 09:54 | 73 | 1:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22080300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-08-03 | 7519 | keep | 0 | Aug | 2022 | 0.0051212 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2022-08-03 08:23 | 2022-08-03 09:45 | 2682 | 1:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO AVERIA Y SE REMPLAZO CAJA PRIMARIA, PARARRAYO QUEMADO Y DESGANCHE. 75% DE 1713-05 EN SERVICIO | B22080300003 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 82 | 2022-08-03 | 219924 | keep | 0 | Aug | 2022 | 0.14979 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-03 08:26 | 2022-08-03 14:54 | 6 | 6:28 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE RETEZO ALAMBRE PRIMARIO Y CAMBIO DE POSTE | C22080300037 | New_Event | Primary Pole Failure | Include | Include | Equipment | 388 | 2022-08-03 | 2328 | keep | 0 | Aug | 2022 | 0.0015856 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-08-03 08:29 | 2022-08-03 10:27 | 210 | 1:58 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22080300038 | New_Event | Animals | Include | Include | Wildlife | 118 | 2022-08-03 | 24780 | keep | 0 | Aug | 2022 | 0.016878 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
BARRANQUITAS | 2022-08-03 08:52 | 2022-08-03 08:54 | 598 | 0:02 | T | DESGANCHE | DISPARO INTERRUPTOR CARGA POR EL 3405-03 CERRADO POR CONTROL | C22080300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-03 | 1196 | keep | 0 | Aug | 2022 | 0.00081459 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2022-08-03 08:52 | 2022-08-03 08:54 | 1001 | 0:02 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 3403-01 CERRADO POR CONTROL | C22080300043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-03 | 2002 | keep | 0 | Aug | 2022 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
BARRANQUITAS | 2022-08-03 08:56 | 2022-08-03 09:57 | 598 | 1:01 | T | DESGANCHE | DISPARO INTERRUPTOR 3405-03 SE SECCIONALIZO CERRADO POR CONTROL LLEVA EL 3403-01 | C22080300046 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-08-03 | 36478 | keep | 0 | Aug | 2022 | 0.024845 | 0.0004073 | Sustained | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2022-08-03 08:56 | 2022-08-03 09:57 | 1001 | 1:01 | T | DESGANCHE | DISPARO INTERRUPTOR 3405-03 SE SECCIONALIZO CERRADO POR CONTROL LLEVA EL 3403-01 | C22080300046 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-08-03 | 61061 | keep | 0 | Aug | 2022 | 0.041588 | 0.00068178 | Sustained | FALSE | FALSE | Not_TMED_Event | 1001
CANOVANAS | 2022-08-03 09:08 | 2022-08-03 12:53 | 4 | 3:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRA DE PEDESTAL | R22080300024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 225 | 2022-08-03 | 900 | keep | 0 | Aug | 2022 | 0.00061299 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-08-03 09:18 | 2022-08-03 11:18 | 1 | 2:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22080300061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-08-03 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-03 09:35 | 2022-08-03 10:17 | 1 | 0:42 | P | SECUNDARIA/DESGANCHE | 2 X 5 EN XMR DESGANCHO | R22080300026 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 42 | 2022-08-03 | 42 | keep | 0 | Aug | 2022 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-03 09:40 | 2022-08-03 14:27 | 75 | 4:47 | P | DESGANCHE | 1X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22080300273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-08-03 | 21525 | keep | 0 | Aug | 2022 | 0.014661 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-08-03 09:45 | 2022-08-03 11:13 | 1490 | 1:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO AVERIA DE CAJA PRIMARIA, PARARRAYO QUEMADO Y DESGANCHE. 75% DE 1713-05 EN SERVICIO | B22080300003 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 88 | 2022-08-03 | 131120 | keep | 0 | Aug | 2022 | 0.089305 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-03 09:50 | 2022-08-03 11:25 | 1774 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PARA TRABAJAR LEVANTANDO CONDUCTOR PRIMARIO | C22080300012 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2022-08-03 | 168530 | keep | 0 | Aug | 2022 | 0.11479 | 0.0012083 | Sustained | FALSE | FALSE | Not_TMED_Event | 1774
BARRANQUITAS | 2022-08-03 09:55 | 2022-08-03 13:40 | 12 | 3:45 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE SECUNDARIO PARTIDO | C22080300064 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 225 | 2022-08-03 | 2700 | keep | 0 | Aug | 2022 | 0.001839 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-08-03 09:57 | 2022-08-03 10:17 | 200 | 0:20 | P | DESGANCHE | ALIMENTADOR SECCIONALIZADO | C22080300046 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-08-03 | 4000 | keep | 0 | Aug | 2022 | 0.0027244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-03 10:02 | 2022-08-03 13:27 | 200 | 3:25 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22080300288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2022-08-03 | 41000 | keep | 0 | Aug | 2022 | 0.027925 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-08-03 10:07 | 2022-08-03 10:48 | 3 | 0:41 | P | PROBLEMA DEL CLIENTE | SE ABRIO CAJA PRIMARIA Y SE RETIRO TOMA AVERIADA. CLIENTE TIENE QUE REPARAR | C22080300075 | New_Event | Customer-Related Interruption | Include | Include | Public | 41 | 2022-08-03 | 123 | keep | 0 | Aug | 2022 | 8.3775e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-08-03 10:14 | 2022-08-03 14:25 | 10 | 4:11 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A22080300021 | New_Event | Animals | Include | Include | Wildlife | 251 | 2022-08-03 | 2510 | keep | 0 | Aug | 2022 | 0.0017095 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-03 10:17 | 2022-08-03 16:47 | 598 | 6:30 | T | DESGANCHE | SE DESGANCHO Y SE REEMPLAZO CORNER BRACKET CARGA POR EL 3405-03 | C22080300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2022-08-03 | 233220 | keep | 0 | Aug | 2022 | 0.15885 | 0.0004073 | Sustained | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2022-08-03 10:17 | 2022-08-03 16:47 | 1001 | 6:30 | T | DESGANCHE | SE DESGANCHO Y SE REEMPLAZO CORNER BRACKET LLEVA EL 3403-01 | C22080300046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2022-08-03 | 390390 | keep | 0 | Aug | 2022 | 0.26589 | 0.00068178 | Sustained | FALSE | FALSE | Not_TMED_Event | 1001
CANOVANAS | 2022-08-03 10:25 | 2022-08-03 12:30 | 45 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR Y REMPLAZO BAJANTE SECUNDARIO | R22080300029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2022-08-03 | 5625 | keep | 0 | Aug | 2022 | 0.0038312 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-08-03 10:26 | 2022-08-03 11:55 | 12 | 1:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA Y PARARRAYO | C22080300082 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2022-08-03 | 1068 | keep | 0 | Aug | 2022 | 0.00072741 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-03 10:27 | 2022-08-03 10:28 | 4634 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22080300000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-03 | 4634 | keep | 0 | Aug | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
CAGUAS | 2022-08-03 10:28 | 2022-08-03 12:04 | 210 | 1:36 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22080300038 | 1st_after_momentary | Animals | Include | Include | Wildlife | 96 | 2022-08-03 | 20160 | keep | 0 | Aug | 2022 | 0.013731 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
SAN JUAN | 2022-08-03 10:30 | 2022-08-03 10:53 | 40 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR BAJANTE Y CONECTORES SECUNDARIOS | S22080300035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2022-08-03 | 920 | keep | 0 | Aug | 2022 | 0.00062661 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-03 10:31 | 2022-08-03 11:18 | 500 | 0:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO EN TRONCAL | B22080300188 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 47 | 2022-08-03 | 23500 | keep | 0 | Aug | 2022 | 0.016006 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2022-08-03 10:32 | 2022-08-03 12:08 | 9 | 1:36 | P | SECUNDARIA/DESGANCHE | SE RETIRO ARBOL DE LA SECUNDARIA Y SE REPARO BAJANTE SECUNDARIO | C22080300047 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 96 | 2022-08-03 | 864 | keep | 0 | Aug | 2022 | 0.00058847 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-08-03 10:46 | 2022-08-03 10:48 | 1106 | 0:02 | P | CONDUCTOR ROTO O ABIERTO | DISPARO LLEVA 60% POR 1529-15 | S22080300000 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-08-03 | 2212 | keep | 0 | Aug | 2022 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-08-03 10:46 | 2022-08-03 10:48 | 1802 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO LLEVA 60% DEL 1346-02 | S22080300072 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-08-03 | 3604 | keep | 0 | Aug | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-08-03 10:48 | 2022-08-03 13:28 | 368 | 2:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A MACHETE PARTE POR 1529-15 | S22080300072 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 160 | 2022-08-03 | 58880 | keep | 0 | Aug | 2022 | 0.040103 | 0.00025064 | Sustained | FALSE | FALSE | Not_TMED_Event | 368
SAN JUAN | 2022-08-03 10:48 | 2022-08-03 13:28 | 600 | 2:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A MACHETE | S22080300072 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 160 | 2022-08-03 | 96000 | keep | 0 | Aug | 2022 | 0.065385 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CAGUAS | 2022-08-03 10:49 | 2022-08-03 10:50 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 6197 | keep | 0 | Aug | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2022-08-03 10:50 | 2022-08-03 17:06 | 20 | 6:16 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | C22080300167 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 376 | 2022-08-03 | 7520 | keep | 0 | Aug | 2022 | 0.0051218 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-03 10:50 | 2022-08-03 12:30 | 80 | 1:40 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A22080300024 | New_Event | Animals | Include | Include | Wildlife | 100 | 2022-08-03 | 8000 | keep | 0 | Aug | 2022 | 0.0054488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-03 10:54 | 2022-08-03 15:15 | 80 | 4:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M22080300317 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-08-03 | 20880 | keep | 0 | Aug | 2022 | 0.014221 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-08-03 10:55 | 2022-08-03 15:00 | 4 | 4:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REMPLAZO CAJA QUEMADA | R22080300030 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2022-08-03 | 980 | keep | 0 | Aug | 2022 | 0.00066747 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-08-03 11:04 | 2022-08-03 14:47 | 15 | 3:43 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22080300103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-08-03 | 3345 | keep | 0 | Aug | 2022 | 0.0022783 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-03 11:13 | 2022-08-03 12:13 | 5961 | 1:00 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1713-05 LLEVANDO 95% 1717-02 SE CERRO POR SCADA. SE ENCONTRO MACHETE QUEMADO Y SE SECCIONALIZO. ENTRO 25% DE 1713-05 Y 95% 1717-02 | B22080300003 | New_Event | Switch Failure | Include | Include | Equipment | 60 | 2022-08-03 | 357660 | keep | 0 | Aug | 2022 | 0.2436 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-03 11:13 | 2022-08-03 12:13 | 865 | 1:00 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1713-05 LLEVANDO 95% 1717-02 SE CERRO POR SCADA. SE ENCONTRO MACHETE QUEMADO | B22080300003 | New_Event | Switch Failure | Include | Include | Equipment | 60 | 2022-08-03 | 51900 | keep | 0 | Aug | 2022 | 0.035349 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
CAGUAS | 2022-08-03 11:15 | 2022-08-03 15:08 | 40 | 3:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22080300108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2022-08-03 | 9320 | keep | 0 | Aug | 2022 | 0.0063478 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-03 11:21 | 2022-08-03 20:53 | 34 | 9:32 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN SU-7 SE DEJO ABIERTO T-31 A T-30 Y T-30 A T-31 HAY QUE REMPLAZAR T-30 | S22080300073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 572 | 2022-08-03 | 19448 | keep | 0 | Aug | 2022 | 0.013246 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BARRANQUITAS | 2022-08-03 11:25 | 2022-08-03 14:05 | 737 | 2:40 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LEVANTO CONDUCTOR PRIMARIO | C22080300012 | New_Event | Primary Wire Break | Include | Include | Equipment | 160 | 2022-08-03 | 117920 | keep | 0 | Aug | 2022 | 0.080315 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
BAYAMON | 2022-08-03 11:37 | 2022-08-03 17:21 | 114 | 5:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN C/L. | S22080200235 | New_Event | Cutout Failure | Include | Include | Equipment | 344 | 2022-08-03 | 39216 | keep | 0 | Aug | 2022 | 0.02671 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
SAN JUAN | 2022-08-03 11:50 | 2022-08-03 15:00 | 102 | 3:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | S22080300084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-08-03 | 19380 | keep | 0 | Aug | 2022 | 0.0132 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
SAN JUAN | 2022-08-03 11:50 | 2022-08-03 15:13 | 342 | 3:23 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE HIZO DESGANCHE | S22080300143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-08-03 | 69426 | keep | 0 | Aug | 2022 | 0.047286 | 0.00023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 342
YAUCO | 2022-08-03 12:00 | 2022-08-03 14:45 | 180 | 2:45 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | M22080300535 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-08-03 | 29700 | keep | 0 | Aug | 2022 | 0.020229 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
GUAYAMA | 2022-08-03 12:03 | 2022-08-03 12:58 | 7 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | P22080300132 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-08-03 | 385 | keep | 0 | Aug | 2022 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-03 12:13 | 2022-08-03 12:50 | 4471 | 0:37 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO. Y SE FUE REPONIENDO SERVICIO SECCIONALIZANDO ALIMENTADOR. 50% EN SERVICIO | B22080300003 | Partial_restoration | Switch Failure | Include | Include | Equipment | 37 | 2022-08-03 | 165427 | keep | 0 | Aug | 2022 | 0.11267 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-03 12:19 | 2022-08-03 17:25 | 10 | 5:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 4160 VOLT | P22080300226 | New_Event | Service Transformer Failure | Include | Include | Equipment | 306 | 2022-08-03 | 3060 | keep | 0 | Aug | 2022 | 0.0020842 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-03 12:26 | 2022-08-03 13:15 | 5 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO TRASPATIO | C22080300035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2022-08-03 | 245 | keep | 0 | Aug | 2022 | 0.00016687 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-03 12:30 | 2022-08-03 13:03 | 2 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S22080300094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2022-08-03 | 66 | keep | 0 | Aug | 2022 | 4.4952e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2022-08-03 12:38 | 2022-08-03 13:37 | 5 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22080300141 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2022-08-03 | 295 | keep | 0 | Aug | 2022 | 0.00020092 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-03 12:50 | 2022-08-03 12:55 | 2981 | 0:05 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO. Y SE FUE REPONIENDO SERVICIO SECCIONALIZANDO ALIMENTADOR. 100% EN SERVICIO | B22080300003 | Partial_restoration | Switch Failure | Include | Include | Equipment | 5 | 2022-08-03 | 14905 | keep | 0 | Aug | 2022 | 0.010152 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-03 13:00 | 2022-08-03 22:45 | 70 | 9:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22080301210 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 585 | 2022-08-03 | 40950 | keep | 0 | Aug | 2022 | 0.027891 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-08-03 13:00 | 2022-08-03 22:01 | 80 | 9:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22080301148 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 541 | 2022-08-03 | 43280 | keep | 0 | Aug | 2022 | 0.029478 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-03 13:00 | 2022-08-03 23:10 | 125 | 10:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 Y 1 X 80 EN DIFERENTES CORTES DE LINEA LLUVIA Y FUERTES VIENTOS | M22080301110 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 610 | 2022-08-03 | 76250 | keep | 0 | Aug | 2022 | 0.051934 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2022-08-03 13:02 | 2022-08-03 17:34 | 100 | 4:32 | P | ANIMAL | 1 X 140 EN CORTE DE LINEA POR AVE | M22080300688 | New_Event | Animals | Include | Include | Wildlife | 272 | 2022-08-03 | 27200 | keep | 0 | Aug | 2022 | 0.018526 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-03 13:03 | 2022-08-03 18:36 | 828 | 5:33 | T | CAUSAS EXTERNAS | TENSOR PEGANDO A LINEA | M22080300418 | New_Event | Damage From Public | Include | Include | Public | 333 | 2022-08-03 | 275724 | keep | 0 | Aug | 2022 | 0.18779 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-08-03 13:03 | 2022-08-03 18:07 | 80 | 5:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22080300417 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2022-08-03 | 24320 | keep | 0 | Aug | 2022 | 0.016564 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-08-03 13:07 | 2022-08-03 14:58 | 50 | 1:51 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L PERSONA PRIVADA DESGANCHANDO | R22080300036 | New_Event | Damage From Public | Include | Include | Public | 111 | 2022-08-03 | 5550 | keep | 0 | Aug | 2022 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-03 13:18 | 2022-08-03 18:14 | 1 | 4:56 | P | NO SE REPORTO CAUSA | 2 X 15 EN XMR | B22080300255 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 296 | 2022-08-03 | 296 | keep | 0 | Aug | 2022 | 0.0002016 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-03 13:19 | 2022-08-03 20:32 | 60 | 7:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | M22080300443 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 433 | 2022-08-03 | 25980 | keep | 0 | Aug | 2022 | 0.017695 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-03 13:19 | 2022-08-03 18:03 | 150 | 4:44 | P | ARBOL SOBRE LINEA | 2 X 100 EN CORTE DE LINEA SE REPARO NEUTRAL PRIMARIO PARTIDO POR ARBOL | M22080300444 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 284 | 2022-08-03 | 42600 | keep | 0 | Aug | 2022 | 0.029015 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-08-03 13:22 | 2022-08-03 13:23 | 462 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080300162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 462 | keep | 0 | Aug | 2022 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
AGUADILLA | 2022-08-03 13:32 | 2022-08-03 21:30 | 100 | 7:58 | P | ARBOL SOBRE LINEA | 2 X 65 EN CORTE DE LINEA SE DESGANCHO ARBOL SOBRE LINEA Y REPARANDO LINEA PARTIDA | M22080300466 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 478 | 2022-08-03 | 47800 | keep | 0 | Aug | 2022 | 0.032556 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-03 13:36 | 2022-08-03 13:39 | 95 | 0:03 | P | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR 1705-05 LLEVANDO CARGA 1705-04, 10% 1705-03 Y 85% DE SU CARGA POR 1705-02. SE CERRO POR SCADA | B22080300263 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2022-08-03 | 285 | keep | 0 | Aug | 2022 | 0.00019411 | 6.4704e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2022-08-03 13:36 | 2022-08-03 13:39 | 67 | 0:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR 1705-05 LLEVANDO CARGA 1705-04, 10% 1705-03 Y 85% DE SU CARGA POR 1705-02. SE CERRO POR SCADA | B22080300263 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2022-08-03 | 201 | keep | 0 | Aug | 2022 | 0.0001369 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-08-03 13:36 | 2022-08-03 13:39 | 96 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1705-05 LLEVANDO CARGA 1705-04, 10% 1705-03 Y 85% DE SU CARGA POR 1705-02. SE CERRO POR SCADA | B22080300263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-03 | 288 | keep | 0 | Aug | 2022 | 0.00019616 | 6.5385e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 96
MAYAGÃœEZ | 2022-08-03 13:36 | 2022-08-03 17:06 | 70 | 3:30 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M22080300472 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 210 | 2022-08-03 | 14700 | keep | 0 | Aug | 2022 | 0.010012 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-08-03 13:39 | 2022-08-03 23:23 | 141 | 9:44 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO (NO FUNDIO) | B22080300298 | New_Event | Switch Failure | Include | Include | Equipment | 584 | 2022-08-03 | 82344 | keep | 0 | Aug | 2022 | 0.056084 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 17:03 | 40 | 3:17 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR PAJARO | M22080300502 | New_Event | Animals | Include | Include | Wildlife | 197 | 2022-08-03 | 7880 | keep | 0 | Aug | 2022 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 574 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 30996 | keep | 0 | Aug | 2022 | 0.021111 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 2493 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 134622 | keep | 0 | Aug | 2022 | 0.09169 | 0.001698 | Sustained | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 1415 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 76410 | keep | 0 | Aug | 2022 | 0.052043 | 0.00096375 | Sustained | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 1428 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 77112 | keep | 0 | Aug | 2022 | 0.052521 | 0.0009726 | Sustained | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 1036 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 55944 | keep | 0 | Aug | 2022 | 0.038103 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 382 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 20628 | keep | 0 | Aug | 2022 | 0.01405 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 39 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 2106 | keep | 0 | Aug | 2022 | 0.0014344 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2022-08-03 13:46 | 2022-08-03 14:40 | 2366 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 127764 | keep | 0 | Aug | 2022 | 0.087019 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2022-08-03 13:46 | 2022-08-03 14:40 | 1337 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 72198 | keep | 0 | Aug | 2022 | 0.049174 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-03 13:46 | 2022-08-03 14:40 | 709 | 0:54 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080301118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 54 | 2022-08-03 | 38286 | keep | 0 | Aug | 2022 | 0.026076 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
AGUADILLA | 2022-08-03 13:51 | 2022-08-04 00:35 | 200 | 10:44 | P | MAL TIEMPO/RAYOS | 2 X 50 1 X 25 Y 1X 40 EN DIFERENTES CORTES DE LINEA DESCARGAS ELECTRICAS | M22080300513 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 644 | 2022-08-03 | 128800 | keep | 0 | Aug | 2022 | 0.087725 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-03 13:53 | 2022-08-03 16:08 | 2946 | 2:15 | T | CAUSAS EXTERNAS | TENSOR DE POSTE PEGANDO A LINEA | M22080300517 | New_Event | Damage From Public | Include | Include | Public | 135 | 2022-08-03 | 397710 | keep | 0 | Aug | 2022 | 0.27088 | 0.0020065 | Sustained | FALSE | FALSE | Not_TMED_Event | 2946
AGUADILLA | 2022-08-03 14:00 | 2022-08-04 02:14 | 150 | 12:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M22080301248 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 734 | 2022-08-03 | 110100 | keep | 0 | Aug | 2022 | 0.074989 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-08-03 14:10 | 2022-08-03 18:18 | 200 | 4:08 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 EN C/L SE REMPLAZO POSTE PRIMARIO PARTIDO | P22080300179 | New_Event | Primary Pole Failure | Include | Include | Equipment | 248 | 2022-08-03 | 49600 | keep | 0 | Aug | 2022 | 0.033782 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-03 14:13 | 2022-08-03 21:01 | 100 | 6:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA POR MASETILLA AVERIADA | M22080300565 | New_Event | Cutout Failure | Include | Include | Equipment | 408 | 2022-08-03 | 40800 | keep | 0 | Aug | 2022 | 0.027789 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-08-03 14:20 | 2022-08-03 17:44 | 17 | 3:24 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22080300156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-08-03 | 3468 | keep | 0 | Aug | 2022 | 0.002362 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2022-08-03 14:21 | 2022-08-05 00:42 | 1115 | 34:21 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA Y SE CERRO N/O CON 7903-07 | M22080300579 | New_Event | Primary Wire Break | Include | Include | Equipment | 2061 | 2022-08-03 | 2298015 | keep | 0 | Aug | 2022 | 1.5652 | 0.00075942 | Sustained | FALSE | FALSE | Not_TMED_Event | 1115
BAYAMON | 2022-08-03 14:31 | 2022-08-03 16:29 | 63 | 1:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22080300273 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2022-08-03 | 7434 | keep | 0 | Aug | 2022 | 0.0050633 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
BAYAMON | 2022-08-03 14:32 | 2022-08-03 15:57 | 573 | 1:25 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1704-04 LLEVANDO CARGA 1704-05 SE SECCCIONALIZO Y SE CERRO POR SCADA 100% 1704-05 EN SERVICIO Y 50% 1704-04 EN SERVICIO. | B22080300274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-03 | 48705 | keep | 0 | Aug | 2022 | 0.033173 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2022-08-03 14:32 | 2022-08-03 15:57 | 1313 | 1:25 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1704-04 LLEVANDO CARGA 1704-05 SE SECCCIONALIZO Y SE CERRO POR SCADA 100% 1704-05 EN SERVICIO Y 50% 1704-04 EN SERVICIO. | B22080300274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-03 | 111605 | keep | 0 | Aug | 2022 | 0.076014 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
SAN JUAN | 2022-08-03 14:39 | 2022-08-03 14:42 | 514 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR. PARA SECCIONALIZAR ALAMBRE EN EL PISO SU CARGA POR 1520-05 | S22080300257 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-03 | 1542 | keep | 0 | Aug | 2022 | 0.0010502 | 0.00035008 | Momentary | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-08-03 14:39 | 2022-08-03 14:42 | 752 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR. PARA SECCIONALIZAR ALAMBRE EN EL PISO SU CARGA POR 1520-05 | S22080300257 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-03 | 2256 | keep | 0 | Aug | 2022 | 0.0015366 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2022-08-03 14:39 | 2022-08-03 14:42 | 68 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR. PARA SECCIONALIZAR ALAMBRE EN EL PISO LLEVA 1520-04 Y 1520-01 | S22080300257 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-03 | 204 | keep | 0 | Aug | 2022 | 0.00013894 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-08-03 14:42 | 2022-08-03 15:57 | 42 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO PRIMARIA Y SE CERRO MACHETE 100% EN SERVICIO | S22080300257 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 75 | 2022-08-03 | 3150 | keep | 0 | Aug | 2022 | 0.0021455 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
ARECIBO | 2022-08-03 14:44 | 2022-08-03 17:06 | 80 | 2:22 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CONVERTIDOR Y 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22080300044 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 142 | 2022-08-03 | 11360 | keep | 0 | Aug | 2022 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-03 14:48 | 2022-08-03 14:52 | 1124 | 0:04 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CERRADO X CONTROL SE VERIFICO PERSONAL FUERA | R22080300044 | New_Event | Cutout Failure | Include | Include | Equipment | 4 | 2022-08-03 | 4496 | keep | 0 | Aug | 2022 | 0.0030622 | 0.00076555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1124
CANOVANAS | 2022-08-03 14:51 | 2022-08-03 17:42 | 100 | 2:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES LLUVIAS | R22080300045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 171 | 2022-08-03 | 17100 | keep | 0 | Aug | 2022 | 0.011647 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-03 14:52 | 2022-08-03 18:57 | 150 | 4:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 65 EN C/L REMPLAZO CAJA QUEMADA | R22080300052 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 245 | 2022-08-03 | 36750 | keep | 0 | Aug | 2022 | 0.02503 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-03 14:54 | 2022-08-03 16:06 | 4381 | 1:12 | T | CABLE SOTERRADO AVERIADO | SALIDA SOTERRADA DE INTERRUPTOR QUEMADA SE TRANSFIRIO CARGA AL 6802-05 | M22080200379 | New_Event | UG Cable Fault | Include | Include | Equipment | 72 | 2022-08-03 | 315432 | keep | 0 | Aug | 2022 | 0.21484 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
CANOVANAS | 2022-08-03 14:57 | 2022-08-03 19:21 | 145 | 4:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L REMPLAZO CAJA QUEMADA | R22080300046 | New_Event | Cutout Failure | Include | Include | Equipment | 264 | 2022-08-03 | 38280 | keep | 0 | Aug | 2022 | 0.026072 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
CANOVANAS | 2022-08-03 15:00 | 2022-08-03 19:30 | 42 | 4:30 | P | CRUCETA DEFECTUOSA O AVERIADA | ABRIO C/L PARA INSTALAR POSTE PARA ELIMINAR CRUCETA EN PROVICIONAL AEREO Y RELOCALIZO LOS RISER | R22080300041 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 270 | 2022-08-03 | 11340 | keep | 0 | Aug | 2022 | 0.0077236 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2022-08-03 15:01 | 2022-08-03 15:02 | 1452 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 1452 | keep | 0 | Aug | 2022 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
BAYAMON | 2022-08-03 15:01 | 2022-08-03 21:16 | 13 | 6:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B22080300288 | New_Event | Secondary Wire Break | Include | Include | Equipment | 375 | 2022-08-03 | 4875 | keep | 0 | Aug | 2022 | 0.0033203 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-08-03 15:02 | 2022-08-03 15:50 | 100 | 0:48 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA | S22080300126 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-08-03 | 4800 | keep | 0 | Aug | 2022 | 0.0032693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-08-03 15:03 | 2022-08-03 17:19 | 15 | 2:16 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22080300171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-08-03 | 2040 | keep | 0 | Aug | 2022 | 0.0013894 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-08-03 15:06 | 2022-08-03 19:36 | 92 | 4:30 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE HIZO DESGANCHE Y SE LEVANTO LINEA | S22080300119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-08-03 | 24840 | keep | 0 | Aug | 2022 | 0.016918 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 313 | 0:04 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 90% POR 1106-05 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 1252 | keep | 0 | Aug | 2022 | 0.00085273 | 0.00021318 | Momentary | FALSE | FALSE | Not_TMED_Event | 313
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 1964 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 LLEVA 60% DE 1110-03 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 7856 | keep | 0 | Aug | 2022 | 0.0053507 | 0.0013377 | Momentary | FALSE | FALSE | Not_TMED_Event | 1964
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 733 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 LLEVA 90% 1102-05 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 2932 | keep | 0 | Aug | 2022 | 0.001997 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 915 | 0:04 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600, 60% POR 1106-04 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 3660 | keep | 0 | Aug | 2022 | 0.0024928 | 0.0006232 | Momentary | FALSE | FALSE | Not_TMED_Event | 915
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 513 | 0:04 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600, 20% POR 1118-10 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 2052 | keep | 0 | Aug | 2022 | 0.0013976 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 1825 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 7300 | keep | 0 | Aug | 2022 | 0.004972 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 4398 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 17592 | keep | 0 | Aug | 2022 | 0.011982 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 2782 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 LLEVA 20% 1111-01 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 11128 | keep | 0 | Aug | 2022 | 0.0075792 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 262 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 1048 | keep | 0 | Aug | 2022 | 0.00071379 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 296 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 1184 | keep | 0 | Aug | 2022 | 0.00080642 | 0.0002016 | Momentary | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 79 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 316 | keep | 0 | Aug | 2022 | 0.00021523 | 5.3807e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 1129 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 4516 | keep | 0 | Aug | 2022 | 0.0030758 | 0.00076896 | Momentary | FALSE | FALSE | Not_TMED_Event | 1129
SAN JUAN | 2022-08-03 15:07 | 2022-08-03 15:11 | 1573 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22080300270 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-03 | 6292 | keep | 0 | Aug | 2022 | 0.0042855 | 0.0010714 | Momentary | FALSE | FALSE | Not_TMED_Event | 1573
ARECIBO | 2022-08-03 15:12 | 2022-08-03 19:40 | 150 | 4:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA RETIRAR EL PELIGRO DE LA AVERIA | A22080300055 | New_Event | Primary Wire Break | Include | Include | Equipment | 268 | 2022-08-03 | 40200 | keep | 0 | Aug | 2022 | 0.02738 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-03 15:13 | 2022-08-03 15:20 | 726 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1346-04 | S22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-08-03 | 5082 | keep | 0 | Aug | 2022 | 0.0034613 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-08-03 15:13 | 2022-08-03 15:20 | 3932 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1303-03 | S22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-08-03 | 27524 | keep | 0 | Aug | 2022 | 0.018746 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2022-08-03 15:13 | 2022-08-03 15:14 | 681 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1530-09 | S22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 681 | keep | 0 | Aug | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-08-03 15:13 | 2022-08-03 15:17 | 1860 | 0:04 | T | DESGANCHE | DISPARO SE PROBO QUEDO EN SERVICIO | S22080300000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-08-03 | 7440 | keep | 0 | Aug | 2022 | 0.0050674 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-03 15:13 | 2022-08-03 15:14 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1520-02 | S22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 1310 | keep | 0 | Aug | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-08-03 15:16 | 2022-08-03 17:08 | 40 | 1:52 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE PRIMARIO | S22080300129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-08-03 | 4480 | keep | 0 | Aug | 2022 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-03 15:17 | 2022-08-03 19:46 | 342 | 4:29 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE HIZO DESGANCHE | S22080300143 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 269 | 2022-08-03 | 91998 | keep | 0 | Aug | 2022 | 0.062659 | 0.00023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 342
BAYAMON | 2022-08-03 15:17 | 2022-08-03 15:18 | 878 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | B22080300297 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-03 | 878 | keep | 0 | Aug | 2022 | 0.000598 | 0.000598 | Momentary | FALSE | FALSE | Not_TMED_Event | 878
CANOVANAS | 2022-08-03 15:18 | 2022-08-03 17:58 | 22 | 2:40 | P | ARBOL SOBRE LINEA | 2 X 50 EN C/L RETIRO ARBOL DE LAS LINEAS | R22080300055 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 160 | 2022-08-03 | 3520 | keep | 0 | Aug | 2022 | 0.0023975 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2022-08-03 15:18 | 2022-08-03 20:00 | 127 | 4:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L SE REMPLAZO AISLADOR Y DESGANCHE | B22080300346 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 282 | 2022-08-03 | 35814 | keep | 0 | Aug | 2022 | 0.024393 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
SAN JUAN | 2022-08-03 15:19 | 2022-08-03 20:28 | 50 | 5:09 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE HIZO DESGANCHE Y SE REPARO SECUNDARIA | S22080300135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2022-08-03 | 15450 | keep | 0 | Aug | 2022 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-03 15:20 | 2022-08-04 12:03 | 20 | 20:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | S22080300137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1243 | 2022-08-03 | 24860 | keep | 0 | Aug | 2022 | 0.016932 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-08-03 15:22 | 2022-08-03 16:00 | 10 | 0:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | P22080300196 | New_Event | Secondary Wire Break | Include | Include | Equipment | 38 | 2022-08-03 | 380 | keep | 0 | Aug | 2022 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-03 15:24 | 2022-08-03 15:25 | 3432 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 80% DE SU CARGA Y LLEVA 10% DEL 1204-03 | S22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 3432 | keep | 0 | Aug | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-08-03 15:24 | 2022-08-03 15:25 | 138 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 10% POR 1204-02 | S22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 138 | keep | 0 | Aug | 2022 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2022-08-03 15:25 | 2022-08-04 12:17 | 47 | 20:52 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S22080300147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1252 | 2022-08-03 | 58844 | keep | 0 | Aug | 2022 | 0.040078 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2022-08-03 15:26 | 2022-08-03 15:27 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22080300305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 4431 | keep | 0 | Aug | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
CANOVANAS | 2022-08-03 15:31 | 2022-08-03 19:32 | 60 | 4:01 | P | EMPALME SOTERRADO AVERIADO | 1 X 40 Y 1 X 30 EN C/LS SE REMPLAZO EMPALME EN EL T - 29 | R22080300065 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 241 | 2022-08-03 | 14460 | keep | 0 | Aug | 2022 | 0.0098486 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-03 15:32 | 2022-08-03 19:37 | 76 | 4:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L LLUVIA FUERTE | B22080300307 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 245 | 2022-08-03 | 18620 | keep | 0 | Aug | 2022 | 0.012682 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CANOVANAS | 2022-08-03 15:32 | 2022-08-03 16:45 | 8 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRAS EN PEDESTAL | R22080300062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2022-08-03 | 584 | keep | 0 | Aug | 2022 | 0.00039776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-03 15:34 | 2022-08-03 17:03 | 200 | 1:29 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22080300183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-08-03 | 17800 | keep | 0 | Aug | 2022 | 0.012123 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-08-03 15:35 | 2022-08-03 17:10 | 40 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22080300310 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-08-03 | 3800 | keep | 0 | Aug | 2022 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-08-03 15:36 | 2022-08-03 19:55 | 100 | 4:19 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTES DE LINEA DIFERENTES SE REALIZO DESGANCHE | A22080300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-08-03 | 25900 | keep | 0 | Aug | 2022 | 0.01764 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-03 15:37 | 2022-08-03 17:28 | 30 | 1:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU#8 POR NO SE REPORTO CAUSA | M22080300735 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-08-03 | 3330 | keep | 0 | Aug | 2022 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-03 15:41 | 2022-08-03 17:43 | 144 | 2:02 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYOS | B22080300317 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 122 | 2022-08-03 | 17568 | keep | 0 | Aug | 2022 | 0.011965 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
AGUADILLA | 2022-08-03 15:46 | 2022-08-03 21:12 | 80 | 5:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | M22080300753 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 326 | 2022-08-03 | 26080 | keep | 0 | Aug | 2022 | 0.017763 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-03 15:46 | 2022-08-03 15:47 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22080300319 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 4027 | keep | 0 | Aug | 2022 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
PONCE | 2022-08-03 15:48 | 2022-08-03 16:10 | 50 | 0:22 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22080300047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2022-08-03 | 1100 | keep | 0 | Aug | 2022 | 0.0007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-03 15:52 | 2022-08-03 18:15 | 60 | 2:23 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22080300066 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 143 | 2022-08-03 | 8580 | keep | 0 | Aug | 2022 | 0.0058438 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-08-03 15:53 | 2022-08-03 17:20 | 4 | 1:27 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22080300067 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 87 | 2022-08-03 | 348 | keep | 0 | Aug | 2022 | 0.00023702 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-03 15:54 | 2022-08-03 18:09 | 4 | 2:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSMADOR AVERIADO DE 25 KVA | B22080300322 | New_Event | Service Transformer Failure | Include | Include | Equipment | 135 | 2022-08-03 | 540 | keep | 0 | Aug | 2022 | 0.00036779 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-03 15:54 | 2022-08-03 19:47 | 196 | 3:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22080300171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2022-08-03 | 45668 | keep | 0 | Aug | 2022 | 0.031104 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
PONCE | 2022-08-03 15:54 | 2022-08-03 18:46 | 100 | 2:52 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P22080300203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-08-03 | 17200 | keep | 0 | Aug | 2022 | 0.011715 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-03 15:54 | 2022-08-03 17:25 | 160 | 1:31 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22080300068 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 91 | 2022-08-03 | 14560 | keep | 0 | Aug | 2022 | 0.0099167 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2022-08-03 15:57 | 2022-08-03 16:45 | 286 | 0:48 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO Y SE CERRO MACHETES | B22080300274 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-08-03 | 13728 | keep | 0 | Aug | 2022 | 0.0093501 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-03 16:00 | 2022-08-04 00:44 | 25 | 8:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A22080300144 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 524 | 2022-08-03 | 13100 | keep | 0 | Aug | 2022 | 0.0089224 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-03 16:02 | 2022-08-03 16:23 | 514 | 0:21 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE ABRIO MACHETE PARA SECCIONALIZAR OTRO TRAMO EN EL PISO SU CARGA POR 1520-05 | S22080300257 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 21 | 2022-08-03 | 10794 | keep | 0 | Aug | 2022 | 0.0073517 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-08-03 16:02 | 2022-08-03 16:23 | 752 | 0:21 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE ABRIO MACHETE PARA SECCIONALIZAR OTRO TRAMO EN EL PISO SU CARGA POR 1520-05 | S22080300257 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 21 | 2022-08-03 | 15792 | keep | 0 | Aug | 2022 | 0.010756 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2022-08-03 16:02 | 2022-08-03 16:23 | 68 | 0:21 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE ABRIO MACHETE PARA SECCIONALIZAR OTRO TRAMO EN EL PISO LLEVA 1520-01 Y 1520-04 | S22080300257 | New_Event | Primary Wire Break | Include | Include | Equipment | 21 | 2022-08-03 | 1428 | keep | 0 | Aug | 2022 | 0.0009726 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
PONCE | 2022-08-03 16:05 | 2022-08-03 16:18 | 14 | 0:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES VIENTOS | P22080300071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 13 | 2022-08-03 | 182 | keep | 0 | Aug | 2022 | 0.00012396 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2022-08-03 16:08 | 2022-08-03 17:31 | 1970 | 1:23 | T | CAUSAS EXTERNAS | TENSOR DE POSTE PEGANDO A LINEA | M22080300517 | Partial_restoration | Damage From Public | Include | Include | Public | 83 | 2022-08-03 | 163510 | keep | 0 | Aug | 2022 | 0.11137 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-03 16:11 | 2022-08-03 17:55 | 10 | 1:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIA Y VIENTO | A22080300078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 104 | 2022-08-03 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-03 16:12 | 2022-08-03 17:56 | 100 | 1:44 | P | MAL TIEMPO/RAYOS | 3 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22080300079 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2022-08-03 | 10400 | keep | 0 | Aug | 2022 | 0.0070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-03 16:14 | 2022-08-03 21:41 | 25 | 5:27 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | M22080300798 | New_Event | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-08-03 | 8175 | keep | 0 | Aug | 2022 | 0.005568 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-03 16:14 | 2022-08-03 19:00 | 40 | 2:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22080300336 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-08-03 | 6640 | keep | 0 | Aug | 2022 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-03 16:21 | 2022-08-03 16:28 | 990 | 0:07 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL CERRANDO MACHETES | M22080300808 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 7 | 2022-08-03 | 6930 | keep | 0 | Aug | 2022 | 0.00472 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 34 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 510 | keep | 0 | Aug | 2022 | 0.00034736 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 19 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 285 | keep | 0 | Aug | 2022 | 0.00019411 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 534 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 8010 | keep | 0 | Aug | 2022 | 0.0054556 | 0.0003637 | Sustained | FALSE | FALSE | Not_TMED_Event | 534
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 790 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 11850 | keep | 0 | Aug | 2022 | 0.008071 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 39 | 0:15 | P | LINEA DE TRANSMISION 38KV | DISPARO L-6800 80% POR 1910-01 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 585 | keep | 0 | Aug | 2022 | 0.00039844 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 433 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 6495 | keep | 0 | Aug | 2022 | 0.0044237 | 0.00029491 | Sustained | FALSE | FALSE | Not_TMED_Event | 433
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 558 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 LLEVA 1519-01 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 8370 | keep | 0 | Aug | 2022 | 0.0057008 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 514 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 SU CARGA POR 1520-05 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 7710 | keep | 0 | Aug | 2022 | 0.0052512 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 681 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 LLEVA 1530-09 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 10215 | keep | 0 | Aug | 2022 | 0.0069574 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 752 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 SU CARGA POR 1520-05 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 11280 | keep | 0 | Aug | 2022 | 0.0076828 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 68 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 LLEVA 1520-04 Y 1520-01 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 1020 | keep | 0 | Aug | 2022 | 0.00069472 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 271 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO L-6800 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 4065 | keep | 0 | Aug | 2022 | 0.0027687 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2022-08-03 16:23 | 2022-08-03 16:38 | 1310 | 0:15 | T | LINEA DE TRANSMISION 38KV | DISPARO L-6800 SU CARGA POR 1520-02 | S22080300262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-03 | 19650 | keep | 0 | Aug | 2022 | 0.013384 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
PONCE | 2022-08-03 16:24 | 2022-08-03 16:25 | 462 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080300286 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 462 | keep | 0 | Aug | 2022 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
CAGUAS | 2022-08-03 16:31 | 2022-08-03 17:41 | 18 | 1:10 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22080300201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-08-03 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-08-03 16:33 | 2022-08-03 17:00 | 90 | 0:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L SE DESENRREDO LINEAS FUERTES VIENTOS | P22080300168 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 27 | 2022-08-03 | 2430 | keep | 0 | Aug | 2022 | 0.0016551 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-08-03 16:38 | 2022-08-03 18:30 | 42 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE 100% EN SERVICIO | S22080300257 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2022-08-03 | 4704 | keep | 0 | Aug | 2022 | 0.0032039 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
ARECIBO | 2022-08-03 16:50 | 2022-08-03 22:35 | 9 | 5:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA | A22080300088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 345 | 2022-08-03 | 3105 | keep | 0 | Aug | 2022 | 0.0021148 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-08-03 16:56 | 2022-08-03 16:57 | 2076 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1718-03 LLEVANDO 40% CARGA 1710-05 | B22080300351 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 2076 | keep | 0 | Aug | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-08-03 16:56 | 2022-08-03 16:57 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1718-03 LLEVANDO 40% CARGA 1710-05 | B22080300351 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 2605 | keep | 0 | Aug | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2022-08-03 16:56 | 2022-08-03 16:57 | 1859 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B22080300350 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-03 | 1859 | keep | 0 | Aug | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2022-08-03 16:57 | 2022-08-03 17:34 | 975 | 0:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO PORTAFUSIBLE QUE SE PRENDIO EN FUEGO | B22080300386 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 37 | 2022-08-03 | 36075 | keep | 0 | Aug | 2022 | 0.024571 | 0.00066407 | Sustained | FALSE | FALSE | Not_TMED_Event | 975
HUMACAO | 2022-08-03 17:03 | 2022-08-03 21:02 | 5 | 3:59 | P | ANIMAL | SE REPARO BAJANTE SECUNDARIO Y SE DEJO 2 CLIENTES TRIFASICOS FUERA POR FALTA DE ROTULACION DE ROTACION DE LAS FASES. CONTINUAN MAÃ‘ANA. CRUCE POR AVE | C22080300209 | New_Event | Animals | Include | Include | Wildlife | 239 | 2022-08-03 | 1195 | keep | 0 | Aug | 2022 | 0.00081391 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-03 17:03 | 2022-08-03 17:23 | 3630 | 0:20 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M22080300888 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-08-03 | 72600 | keep | 0 | Aug | 2022 | 0.049448 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
BAYAMON | 2022-08-03 17:06 | 2022-08-03 18:55 | 12 | 1:49 | P | MAL TIEMPO/RAYOS | 2 X 15 EN XMR MAL TIEMPO RAYOS | B22080300354 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 109 | 2022-08-03 | 1308 | keep | 0 | Aug | 2022 | 0.00089087 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-03 17:09 | 2022-08-03 17:10 | 638 | 0:01 | T | NO SE REPORTO CAUSA | RECIERE DE BKR | C22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 638 | keep | 0 | Aug | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CANOVANAS | 2022-08-03 17:10 | 2022-08-03 19:09 | 200 | 1:59 | P | DESGANCHE | 2 X 65 Y 1 X 100 EN C/LS DESGANCHO | R22080300085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-08-03 | 23800 | keep | 0 | Aug | 2022 | 0.01621 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-03 17:23 | 2022-08-03 17:40 | 40 | 0:17 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR PAJARO | M22080300502 | Partial_restoration | Animals | Include | Include | Wildlife | 17 | 2022-08-03 | 680 | keep | 0 | Aug | 2022 | 0.00046314 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-03 17:30 | 2022-08-03 19:21 | 1 | 1:51 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA XMR | B22080300356 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-08-03 | 111 | keep | 0 | Aug | 2022 | 7.5602e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-03 17:34 | 2022-08-03 17:35 | 2076 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1718-03 LLEVANDO 40% CARGA 1710-05 | B22080300351 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 2076 | keep | 0 | Aug | 2022 | 0.001414 | 0.001414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2076
BAYAMON | 2022-08-03 17:34 | 2022-08-03 17:35 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1718-03 LLEVANDO 40% CARGA 1710-05 | B22080300351 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-03 | 2605 | keep | 0 | Aug | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
AGUADILLA | 2022-08-03 17:34 | 2022-08-03 22:43 | 200 | 5:09 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR ALAMBRE PARTIDO | M22080300951 | New_Event | Primary Wire Break | Include | Include | Equipment | 309 | 2022-08-03 | 61800 | keep | 0 | Aug | 2022 | 0.042092 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-03 17:34 | 2022-08-03 17:35 | 1859 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B22080300350 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-03 | 1859 | keep | 0 | Aug | 2022 | 0.0012662 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-03 17:35 | 2022-08-03 18:46 | 975 | 1:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO PORTAFUSIBLE QUE SE PRENDIO EN FUEGO | B22080300386 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 71 | 2022-08-03 | 69225 | keep | 0 | Aug | 2022 | 0.047149 | 0.00066407 | Sustained | FALSE | FALSE | Not_TMED_Event | 975
AGUADILLA | 2022-08-03 17:45 | 2022-08-03 19:19 | 300 | 1:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA Y 1 X 200 EN CONVERTIDOR POR DESGANHCE DE ARBOL SOBRE LINEA | M22080300976 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-08-03 | 28200 | keep | 0 | Aug | 2022 | 0.019207 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-08-03 17:51 | 2022-08-03 23:45 | 65 | 5:54 | P | ARBOL SOBRE LINEA | 3 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | M22080300988 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 354 | 2022-08-03 | 23010 | keep | 0 | Aug | 2022 | 0.015672 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-08-03 17:53 | 2022-08-03 18:06 | 3 | 0:13 | P | ANIMAL | 1 X 30 EN MONTURA AVE CRUZO LINEAS | P22080300234 | New_Event | Animals | Include | Include | Wildlife | 13 | 2022-08-03 | 39 | keep | 0 | Aug | 2022 | 2.6563e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-08-03 17:54 | 2022-08-03 17:55 | 3718 | 0:01 | T | DESGANCHE | RECIERRE | P22080300285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-03 | 3718 | keep | 0 | Aug | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
GUAYAMA | 2022-08-03 17:55 | 2022-08-03 19:20 | 20 | 1:25 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22080300240 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-03 | 1700 | keep | 0 | Aug | 2022 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-03 17:55 | 2022-08-03 20:57 | 120 | 3:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN SW#3, 1 X 20 EN TRANSFORMADOR , 1 X 30 EN RISER Y 2 X 100 EN SW#6 POR NEUTRAL SOBRE LINEA | M22080300999 | New_Event | Primary Wire Break | Include | Include | Equipment | 182 | 2022-08-03 | 21840 | keep | 0 | Aug | 2022 | 0.014875 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-08-03 17:57 | 2022-08-03 20:49 | 100 | 2:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA EN C/L QUEMADA | P22080300236 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-08-03 | 17200 | keep | 0 | Aug | 2022 | 0.011715 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-03 18:05 | 2022-08-03 19:49 | 70 | 1:44 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CONVERTIDOR POR DESCARGAS ELECTRICAS | A22080300111 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2022-08-03 | 7280 | keep | 0 | Aug | 2022 | 0.0049584 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-08-03 18:24 | 2022-08-03 20:54 | 219 | 2:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L Y 1 X 80 EN C/L | S22080300241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 150 | 2022-08-03 | 32850 | keep | 0 | Aug | 2022 | 0.022374 | 0.00014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 219
AGUADILLA | 2022-08-03 18:36 | 2022-08-03 19:56 | 500 | 1:20 | P | CAUSAS EXTERNAS | SE RETIRO TENSOR PEGANDO A LINEA Y SE CERRO MACHETES | M22080301033 | Partial_restoration | Damage From Public | Include | Include | Public | 80 | 2022-08-03 | 40000 | keep | 0 | Aug | 2022 | 0.027244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-03 18:46 | 2022-08-03 18:47 | 1859 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR A PETICION PERSONAL DE CAMPO PARA ABRIR CAJA PRIMARIA ARQUEANDO | B22080300375 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-03 | 1859 | keep | 0 | Aug | 2022 | 0.0012662 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-03 18:47 | 2022-08-03 19:15 | 975 | 0:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO PORTAFUSIBLE QUE SE PRENDIO EN FUEGO | B22080300386 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 28 | 2022-08-03 | 27300 | keep | 0 | Aug | 2022 | 0.018594 | 0.00066407 | Sustained | FALSE | FALSE | Not_TMED_Event | 975
BAYAMON | 2022-08-03 18:57 | 2022-08-03 21:00 | 483 | 2:03 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L Y 1 X 40 EN C/L VEHICULO IMPACTO POSTE Y LINEAS SE CRUZARON | B22080300382 | New_Event | Damage From Public | Include | Include | Public | 123 | 2022-08-03 | 59409 | keep | 0 | Aug | 2022 | 0.040463 | 0.00032897 | Sustained | FALSE | FALSE | Not_TMED_Event | 483
SAN JUAN | 2022-08-03 18:59 | 2022-08-04 12:56 | 15 | 17:57 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | S22080300254 | New_Event | Primary Wire Break | Include | Include | Equipment | 1077 | 2022-08-03 | 16155 | keep | 0 | Aug | 2022 | 0.011003 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-03 19:05 | 2022-08-03 22:39 | 125 | 3:34 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S22080300255 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-08-03 | 26750 | keep | 0 | Aug | 2022 | 0.018219 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-08-03 19:05 | 2022-08-03 19:10 | 990 | 0:05 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | PERSONAL REALIZANDO PRUEBAS VACUMM SWITCH#6 | M22080301079 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 5 | 2022-08-03 | 4950 | keep | 0 | Aug | 2022 | 0.0033714 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-03 19:10 | 2022-08-03 20:05 | 7 | 0:55 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA CRUZADA Y SE ASEGURO AREA DE POSTE SECUNDARIO PARTIDO | A22080300124 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 55 | 2022-08-03 | 385 | keep | 0 | Aug | 2022 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-08-03 19:26 | 2022-08-04 09:15 | 50 | 13:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080301109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 829 | 2022-08-03 | 41450 | keep | 0 | Aug | 2022 | 0.028231 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-03 19:28 | 2022-08-04 09:39 | 50 | 14:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22080300111 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 851 | 2022-08-03 | 42550 | keep | 0 | Aug | 2022 | 0.028981 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-03 19:32 | 2022-08-03 21:16 | 40 | 1:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | M22080301114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 104 | 2022-08-03 | 4160 | keep | 0 | Aug | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-03 19:39 | 2022-08-03 21:00 | 50 | 1:21 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P22080300262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-08-03 | 4050 | keep | 0 | Aug | 2022 | 0.0027584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-03 20:01 | 2022-08-03 23:55 | 250 | 3:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | A22080300138 | New_Event | Primary Wire Break | Include | Include | Equipment | 234 | 2022-08-03 | 58500 | keep | 0 | Aug | 2022 | 0.039844 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2022-08-03 20:07 | 2022-08-03 20:55 | 20 | 0:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | R22080300108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 48 | 2022-08-03 | 960 | keep | 0 | Aug | 2022 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-08-03 20:10 | 2022-08-04 00:02 | 140 | 3:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22080301170 | New_Event | Cutout Failure | Include | Include | Equipment | 232 | 2022-08-03 | 32480 | keep | 0 | Aug | 2022 | 0.022122 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
AGUADILLA | 2022-08-03 20:11 | 2022-08-04 15:58 | 125 | 19:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA A CAUSA DE DESGANCHE MASIVO QUE CAUSO AVERIA | M22080301171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1187 | 2022-08-03 | 148375 | keep | 0 | Aug | 2022 | 0.10106 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-08-03 20:24 | 2022-08-04 14:47 | 50 | 18:23 | P | DESGANCHE | 1X50 EN C/L | S22080300268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1103 | 2022-08-03 | 55150 | keep | 0 | Aug | 2022 | 0.037562 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-03 20:40 | 2022-08-04 11:10 | 4 | 14:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080301197 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 870 | 2022-08-03 | 3480 | keep | 0 | Aug | 2022 | 0.0023702 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-08-03 20:53 | 2022-08-04 14:20 | 20 | 17:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-30 Y T-31 AVERIADOS | S22080300073 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1047 | 2022-08-03 | 20940 | keep | 0 | Aug | 2022 | 0.014262 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-03 20:54 | 2022-08-04 09:25 | 100 | 12:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22080300271 | New_Event | Cutout Failure | Include | Include | Equipment | 751 | 2022-08-03 | 75100 | keep | 0 | Aug | 2022 | 0.05115 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-03 20:54 | 2022-08-04 14:39 | 50 | 17:45 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | B22080300413 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1065 | 2022-08-03 | 53250 | keep | 0 | Aug | 2022 | 0.036268 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-03 20:55 | 2022-08-03 21:58 | 50 | 1:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | M22080301216 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 63 | 2022-08-03 | 3150 | keep | 0 | Aug | 2022 | 0.0021455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-03 21:02 | 2022-08-04 11:15 | 2 | 14:13 | P | ANIMAL | SE REPARO BAJANTE SECUNDARIO TRIFASICO CRUCE POR AVE | C22080300209 | Partial_restoration | Animals | Include | Include | Wildlife | 853 | 2022-08-03 | 1706 | keep | 0 | Aug | 2022 | 0.0011619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-03 21:05 | 2022-08-04 10:51 | 6 | 13:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M22080301223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 826 | 2022-08-03 | 4956 | keep | 0 | Aug | 2022 | 0.0033755 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-08-03 21:05 | 2022-08-04 17:49 | 15 | 20:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X15 EN XMR POR LLUVIAS | B22080300147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1244 | 2022-08-03 | 18660 | keep | 0 | Aug | 2022 | 0.012709 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-03 21:09 | 2022-08-04 10:52 | 100 | 13:43 | P | ARBOL SOBRE LINEA | 2 X 100 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LAS LINEAS | M22080301228 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 823 | 2022-08-03 | 82300 | keep | 0 | Aug | 2022 | 0.056054 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-03 21:21 | 2022-08-03 23:09 | 10 | 1:48 | P | SECUNDARIA/DESGANCHE | SE RETIRO ARBOL SOBRE LINEA SECUNDARIA Y SE REPARO SECUNDARIA | C22080300226 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 108 | 2022-08-03 | 1080 | keep | 0 | Aug | 2022 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-03 21:24 | 2022-08-04 11:48 | 45 | 14:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L PRINCIPAL Y 2 X 20 EN BANCO DE XMR EN EL COLMADO MAL TIEMPO POR LLUVIA. | B22080300423 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 864 | 2022-08-03 | 38880 | keep | 0 | Aug | 2022 | 0.026481 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-08-03 21:52 | 2022-08-04 10:42 | 30 | 12:50 | P | ARBOL SOBRE LINEA | 1 X 15 EN TRANSFORMADOR 1 X 30 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LA LINEA | M22080301259 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 770 | 2022-08-03 | 23100 | keep | 0 | Aug | 2022 | 0.015733 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-03 22:04 | 2022-08-04 13:39 | 500 | 15:35 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080301265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 935 | 2022-08-03 | 467500 | keep | 0 | Aug | 2022 | 0.31841 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2022-08-03 22:10 | 2022-08-04 19:23 | 10 | 21:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARA SECUNDARIA AVERIADA | A22080300151 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1273 | 2022-08-03 | 12730 | keep | 0 | Aug | 2022 | 0.0086703 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-03 22:23 | 2022-08-04 09:53 | 30 | 11:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y PORTAFUSIBLE 1 X 100 EN C/L | R22080300110 | New_Event | Cutout Failure | Include | Include | Equipment | 690 | 2022-08-03 | 20700 | keep | 0 | Aug | 2022 | 0.014099 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-08-03 22:29 | 2022-08-03 22:31 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22080300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-03 | 4252 | keep | 0 | Aug | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
AGUADILLA | 2022-08-03 22:37 | 2022-08-04 10:40 | 30 | 12:03 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080301273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 723 | 2022-08-03 | 21690 | keep | 0 | Aug | 2022 | 0.014773 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-03 22:43 | 2022-08-04 18:32 | 5 | 19:49 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES | M22080400232 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1189 | 2022-08-03 | 5945 | keep | 0 | Aug | 2022 | 0.0040491 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-03 23:05 | 2022-08-03 23:29 | 6 | 0:24 | P | SECUNDARIA/DESGANCHE | SE REPARO BAJANTE SECUNDARIO EN XMR Y SE REALIZO DESGANCHE SECUNDARIO | S22080300288 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 24 | 2022-08-03 | 144 | keep | 0 | Aug | 2022 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-03 23:15 | 2022-08-04 13:23 | 209 | 14:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22080300439 | New_Event | Cutout Failure | Include | Include | Equipment | 848 | 2022-08-03 | 177232 | keep | 0 | Aug | 2022 | 0.12071 | 0.00014235 | Sustained | FALSE | FALSE | Not_TMED_Event | 209
ARECIBO | 2022-08-03 23:30 | 2022-08-04 01:30 | 800 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REPARO CAJA QUEMADA | A22080300163 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2022-08-03 | 96000 | keep | 0 | Aug | 2022 | 0.065385 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
MAYAGÃœEZ | 2022-08-03 23:36 | 2022-08-04 04:51 | 65 | 5:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M22080301287 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 315 | 2022-08-03 | 20475 | keep | 0 | Aug | 2022 | 0.013945 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2022-08-04 00:01 | 2022-08-04 09:30 | 1 | 9:29 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | P22080400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 569 | 2022-08-04 | 569 | keep | 0 | Aug | 2022 | 0.00038754 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-04 00:48 | 2022-08-04 13:34 | 30 | 12:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080401296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 766 | 2022-08-04 | 22980 | keep | 0 | Aug | 2022 | 0.015652 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-04 01:21 | 2022-08-04 09:51 | 128 | 8:30 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE PRIMARIO | R22080400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 510 | 2022-08-04 | 65280 | keep | 0 | Aug | 2022 | 0.044462 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 574 | keep | 0 | Aug | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 2493 | keep | 0 | Aug | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 1415 | keep | 0 | Aug | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 1428 | keep | 0 | Aug | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 1036 | keep | 0 | Aug | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 382 | keep | 0 | Aug | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 39 | keep | 0 | Aug | 2022 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2022-08-04 01:36 | 2022-08-04 01:37 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 2366 | keep | 0 | Aug | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2022-08-04 01:36 | 2022-08-04 01:37 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 1337 | keep | 0 | Aug | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-04 01:36 | 2022-08-04 01:37 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22080400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-04 | 709 | keep | 0 | Aug | 2022 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
CAGUAS | 2022-08-04 01:48 | 2022-08-04 06:00 | 13 | 4:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22080400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2022-08-04 | 3276 | keep | 0 | Aug | 2022 | 0.0022313 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2022-08-04 02:30 | 2022-08-05 13:11 | 60 | 34:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22080400554 | New_Event | Cutout Failure | Include | Include | Equipment | 2081 | 2022-08-04 | 124860 | keep | 0 | Aug | 2022 | 0.085042 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-04 02:32 | 2022-08-04 02:33 | 2324 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B22080400003 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-04 | 2324 | keep | 0 | Aug | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
BAYAMON | 2022-08-04 02:33 | 2022-08-04 03:59 | 258 | 1:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO (RADIAL) QUE CAYO SOBRE XMR | B22080300445 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 86 | 2022-08-04 | 22188 | keep | 0 | Aug | 2022 | 0.015112 | 0.00017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 258
CAGUAS | 2022-08-04 03:07 | 2022-08-04 03:08 | 1153 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080400014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1153 | keep | 0 | Aug | 2022 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
ARECIBO | 2022-08-04 03:07 | 2022-08-05 09:25 | 100 | 30:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080400211 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1818 | 2022-08-04 | 181800 | keep | 0 | Aug | 2022 | 0.12382 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-04 03:13 | 2022-08-05 04:40 | 25 | 25:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080400058 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1527 | 2022-08-04 | 38175 | keep | 0 | Aug | 2022 | 0.026001 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-04 03:13 | 2022-08-05 10:30 | 50 | 31:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | A22080400212 | New_Event | Primary Wire Break | Include | Include | Equipment | 1877 | 2022-08-04 | 93850 | keep | 0 | Aug | 2022 | 0.063921 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-04 03:16 | 2022-08-04 03:17 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 652 | keep | 0 | Aug | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
BAYAMON | 2022-08-04 03:59 | 2022-08-04 04:00 | 2324 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO/CERRO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA PODER, A SU VEZ, ABRIR MACHETE PARA REPARAR/LEVANTAR CONDUCTOR PRIMARIO (RADIAL) QUE CAYO SOBRE XMR | B22080400005 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-04 | 2324 | keep | 0 | Aug | 2022 | 0.0015829 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-04 04:00 | 2022-08-04 05:23 | 258 | 1:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO (RADIAL) QUE CAYO SOBRE XMR | B22080300445 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 83 | 2022-08-04 | 21414 | keep | 0 | Aug | 2022 | 0.014585 | 0.00017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 258
CAGUAS | 2022-08-04 04:21 | 2022-08-04 20:25 | 14 | 16:04 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DEL T-14 AL T-13 | C22080400015 | New_Event | UG Cable Fault | Include | Include | Equipment | 964 | 2022-08-04 | 13496 | keep | 0 | Aug | 2022 | 0.0091921 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-08-04 04:43 | 2022-08-05 08:45 | 25 | 28:02 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | R22080400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1682 | 2022-08-04 | 42050 | keep | 0 | Aug | 2022 | 0.02864 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-04 04:52 | 2022-08-04 10:38 | 50 | 5:46 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22080400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 346 | 2022-08-04 | 17300 | keep | 0 | Aug | 2022 | 0.011783 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-04 04:55 | 2022-08-04 14:43 | 42 | 9:48 | P | MAL TIEMPO/RAYOS | 1X100 EN C/L POR RAYO | B22080400009 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 588 | 2022-08-04 | 24696 | keep | 0 | Aug | 2022 | 0.01682 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
AGUADILLA | 2022-08-04 05:32 | 2022-08-05 08:35 | 30 | 27:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080400560 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1623 | 2022-08-04 | 48690 | keep | 0 | Aug | 2022 | 0.033163 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-04 05:36 | 2022-08-05 09:10 | 3 | 27:34 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080400561 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1654 | 2022-08-04 | 4962 | keep | 0 | Aug | 2022 | 0.0033796 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-04 05:40 | 2022-08-05 12:10 | 25 | 30:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080400562 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1830 | 2022-08-04 | 45750 | keep | 0 | Aug | 2022 | 0.03116 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-04 05:46 | 2022-08-05 12:30 | 75 | 30:44 | P | MAL TIEMPO/RAYOS | 1 X 65 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400563 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1844 | 2022-08-04 | 138300 | keep | 0 | Aug | 2022 | 0.094196 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-08-04 05:54 | 2022-08-04 07:36 | 1979 | 1:42 | S | ANIMAL | PAJARO OCACIONO CRUCE AVERIANDO MACHETES DE AMARRE ENTRE 5018-04 Y 5018-02, Y AL MISMO TIEMPO SACA DE SERVICIO BREAKERS DE 115 KV. (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300330 | New_Event | Animals | Include | Include | Wildlife | 102 | 2022-08-04 | 201858 | keep | 0 | Aug | 2022 | 0.13748 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2022-08-04 05:54 | 2022-08-04 10:42 | 3114 | 4:48 | S | ANIMAL | PAJARO OCACIONO CRUCE AVERIANDO MACHETES DE AMARRE ENTRE 5018-04 Y 5018-02, Y AL MISMO TIEMPO SACA DE SERVICIO BREAKERS DE 115 KV (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300340 | New_Event | Animals | Include | Include | Wildlife | 288 | 2022-08-04 | 896832 | keep | 0 | Aug | 2022 | 0.61083 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-08-04 05:54 | 2022-08-04 07:36 | 5069 | 1:42 | S | ANIMAL | PAJARO OCACIONO CRUCE AVERIANDO MACHETES DE AMARRE ENTRE 5018-04 Y 5018-02, Y AL MISMO TIEMPO SACA DE SERVICIO BREAKERS DE 115 KV (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300341 | New_Event | Animals | Include | Include | Wildlife | 102 | 2022-08-04 | 517038 | keep | 0 | Aug | 2022 | 0.35215 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2022-08-04 05:54 | 2022-08-04 10:42 | 2696 | 4:48 | S | ANIMAL | PAJARO OCACIONO CRUCE AVERIANDO MACHETES DE AMARRE ENTRE 5018-04 Y 5018-02, Y AL MISMO TIEMPO SACA DE SERVICIO BREAKERS DE 115 KV (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300342 | New_Event | Animals | Include | Include | Wildlife | 288 | 2022-08-04 | 776448 | keep | 0 | Aug | 2022 | 0.52884 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2022-08-04 05:54 | 2022-08-04 07:36 | 5063 | 1:42 | S | ANIMAL | PAJARO OCACIONO CRUCE AVERIANDO MACHETES DE AMARRE ENTRE 5018-04 Y 5018-02, Y AL MISMO TIEMPO SACA DE SERVICIO BREAKERS DE 115 KV (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300330 | New_Event | Animals | Include | Include | Wildlife | 102 | 2022-08-04 | 516426 | keep | 0 | Aug | 2022 | 0.35174 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
ARECIBO | 2022-08-04 05:59 | 2022-08-05 12:00 | 1 | 30:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | A22080400220 | New_Event | Cutout Failure | Include | Include | Equipment | 1801 | 2022-08-04 | 1801 | keep | 0 | Aug | 2022 | 0.0012267 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-04 06:14 | 2022-08-04 06:15 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 4132 | keep | 0 | Aug | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-08-04 06:14 | 2022-08-04 06:15 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 4279 | keep | 0 | Aug | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-08-04 06:14 | 2022-08-04 06:15 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE (EVENTOS SALIENDO CON FECHAS ANTERIORES) | P22080300344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 464 | keep | 0 | Aug | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
BAYAMON | 2022-08-04 06:30 | 2022-08-04 06:31 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 LLEVA 1909-09 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-04 06:30 | 2022-08-04 06:31 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 LLEVA 1909-09 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 4456 | keep | 0 | Aug | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
SAN JUAN | 2022-08-04 06:37 | 2022-08-04 15:36 | 20 | 8:59 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO CAUSA | S22080400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 539 | 2022-08-04 | 10780 | keep | 0 | Aug | 2022 | 0.0073422 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-04 06:52 | 2022-08-04 11:22 | 143 | 4:30 | P | ANIMAL | 1 X 40 EN C/L CRUZE POR AVE | B22080400013 | New_Event | Animals | Include | Include | Wildlife | 270 | 2022-08-04 | 38610 | keep | 0 | Aug | 2022 | 0.026297 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
VEGA BAJA | 2022-08-04 07:02 | 2022-08-04 11:38 | 60 | 4:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIA | B22080400014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 276 | 2022-08-04 | 16560 | keep | 0 | Aug | 2022 | 0.011279 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-04 07:06 | 2022-08-04 07:07 | 1153 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22080400017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1153 | keep | 0 | Aug | 2022 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
AGUADILLA | 2022-08-04 07:13 | 2022-08-04 21:09 | 20 | 13:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REMOVIO RAMAS DE LAS LINEAS | M22080400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 836 | 2022-08-04 | 16720 | keep | 0 | Aug | 2022 | 0.011388 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-04 07:14 | 2022-08-04 09:10 | 17 | 1:56 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR IGUANA CRUZO LINEAS | M22080400003 | New_Event | Animals | Include | Include | Wildlife | 116 | 2022-08-04 | 1972 | keep | 0 | Aug | 2022 | 0.0013431 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2022-08-04 07:15 | 2022-08-05 12:50 | 20 | 29:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080400226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1775 | 2022-08-04 | 35500 | keep | 0 | Aug | 2022 | 0.024179 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-04 07:21 | 2022-08-04 07:22 | 1153 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22080400019 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1153 | keep | 0 | Aug | 2022 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
BAYAMON | 2022-08-04 07:27 | 2022-08-04 14:27 | 110 | 7:00 | P | NO SE REPORTO CAUSA | 1X30 EN C/L, 1X25 EN C/L Y 1X20 EN OTRO C/L | B22080400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 420 | 2022-08-04 | 46200 | keep | 0 | Aug | 2022 | 0.031467 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
HUMACAO | 2022-08-04 07:28 | 2022-08-04 16:51 | 9 | 9:23 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | C22080400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 563 | 2022-08-04 | 5067 | keep | 0 | Aug | 2022 | 0.0034511 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-08-04 07:36 | 2022-08-04 09:54 | 20 | 2:18 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R22080400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-08-04 | 2760 | keep | 0 | Aug | 2022 | 0.0018798 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-04 07:38 | 2022-08-04 16:25 | 100 | 8:47 | P | ARBOL SOBRE LINEA | 1 X 50 Y 1 X 65 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LAS LINEAS | M22080400004 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 527 | 2022-08-04 | 52700 | keep | 0 | Aug | 2022 | 0.035894 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-04 07:44 | 2022-08-04 15:15 | 50 | 7:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 EN C/L POR LLUVIAS | B22080400019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 451 | 2022-08-04 | 22550 | keep | 0 | Aug | 2022 | 0.015359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-04 08:06 | 2022-08-04 09:35 | 50 | 1:29 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | R22080400013 | New_Event | Animals | Include | Include | Wildlife | 89 | 2022-08-04 | 4450 | keep | 0 | Aug | 2022 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-04 08:10 | 2022-08-04 13:10 | 2 | 5:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA ROTA | M22080400035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 300 | 2022-08-04 | 600 | keep | 0 | Aug | 2022 | 0.00040866 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-04 08:13 | 2022-08-04 15:56 | 7 | 7:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | A22080400010 | New_Event | Cutout Failure | Include | Include | Equipment | 463 | 2022-08-04 | 3241 | keep | 0 | Aug | 2022 | 0.0022074 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-08-04 08:14 | 2022-08-04 08:59 | 30 | 0:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A22080400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-08-04 | 1350 | keep | 0 | Aug | 2022 | 0.00091948 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-08-04 08:18 | 2022-08-04 12:47 | 1 | 4:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CERRO PUENTE EN BAJANTE SECUNDARIO | C22080400021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 269 | 2022-08-04 | 269 | keep | 0 | Aug | 2022 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-04 08:21 | 2022-08-04 12:33 | 15 | 4:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 15 EN TRANSFORMADORES MAL TIEMPO VIENTOS FUERTES | A22080400013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 252 | 2022-08-04 | 3780 | keep | 0 | Aug | 2022 | 0.0025745 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-08-04 08:29 | 2022-08-04 10:00 | 40 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080400015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2022-08-04 | 3640 | keep | 0 | Aug | 2022 | 0.0024792 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-04 08:33 | 2022-08-04 08:34 | 50 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO PARTE POR 1345-02 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 50 | keep | 0 | Aug | 2022 | 3.4055e-05 | 3.4055e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-04 08:33 | 2022-08-04 08:34 | 291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1345-02 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 291 | keep | 0 | Aug | 2022 | 0.0001982 | 0.0001982 | Momentary | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2022-08-04 08:33 | 2022-08-04 08:34 | 435 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA PARTE 1330-04 Y LLEVA 1342-05 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 435 | keep | 0 | Aug | 2022 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
GUAYAMA | 2022-08-04 08:39 | 2022-08-04 15:51 | 300 | 7:12 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L SE REPARO ALAMBRE PRIMARIO | P22080400004 | New_Event | Primary Wire Break | Include | Include | Equipment | 432 | 2022-08-04 | 129600 | keep | 0 | Aug | 2022 | 0.08827 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-04 08:42 | 2022-08-04 08:44 | 5809 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1710-02 (SPARE) QUE LLEVA EL 1710-01 | B22080400035 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-08-04 | 11618 | keep | 0 | Aug | 2022 | 0.007913 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-08-04 08:44 | 2022-08-04 14:25 | 500 | 5:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO TRES CAJAS PRIMARIAS EN CONVERTIDOR NO FUNDIO | B22080400074 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 341 | 2022-08-04 | 170500 | keep | 0 | Aug | 2022 | 0.11613 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-08-04 08:59 | 2022-08-04 15:20 | 12 | 6:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S22080400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2022-08-04 | 4572 | keep | 0 | Aug | 2022 | 0.003114 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-04 08:59 | 2022-08-04 10:15 | 2926 | 1:16 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE ENCONTRO INTERRUPTOR DESCARGADO SE CARGO EL SPRING Y SE CERRO POR SCADA | B22080400042 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 76 | 2022-08-04 | 222376 | keep | 0 | Aug | 2022 | 0.15146 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
AGUADILLA | 2022-08-04 09:03 | 2022-08-04 13:16 | 25 | 4:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22080400076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2022-08-04 | 6325 | keep | 0 | Aug | 2022 | 0.0043079 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-04 09:03 | 2022-08-04 15:13 | 45 | 6:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22080400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 370 | 2022-08-04 | 16650 | keep | 0 | Aug | 2022 | 0.01134 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-08-04 09:11 | 2022-08-04 13:41 | 43 | 4:30 | P | NO SE REPORTO CAUSA | DISPARO 1117-07 SE ABRIO SU-3A Y SE PASO CARGA AL 1119-04 | S22080400113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2022-08-04 | 11610 | keep | 0 | Aug | 2022 | 0.0079075 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
MAYAGÃœEZ | 2022-08-04 09:14 | 2022-08-04 11:25 | 5 | 2:11 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-08-04 | 655 | keep | 0 | Aug | 2022 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-04 09:15 | 2022-08-04 13:21 | 6 | 4:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22080400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 246 | 2022-08-04 | 1476 | keep | 0 | Aug | 2022 | 0.0010053 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-04 09:21 | 2022-08-04 14:40 | 50 | 5:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE PRIMARIO | S22080400029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2022-08-04 | 15950 | keep | 0 | Aug | 2022 | 0.010863 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-04 09:30 | 2022-08-04 10:43 | 80 | 1:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080400101 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 73 | 2022-08-04 | 5840 | keep | 0 | Aug | 2022 | 0.0039776 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-08-04 09:31 | 2022-08-04 13:20 | 10 | 3:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECCIONEA EN LINEA SECUNDARIA | P22080400031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 229 | 2022-08-04 | 2290 | keep | 0 | Aug | 2022 | 0.0015597 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-04 09:33 | 2022-08-04 11:39 | 117 | 2:06 | P | DESGANCHE | 1 X 40 EN C/L | C22080400033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-04 | 14742 | keep | 0 | Aug | 2022 | 0.010041 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
CANOVANAS | 2022-08-04 09:34 | 2022-08-04 10:50 | 25 | 1:16 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE BAMBUA | R22080400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-08-04 | 1900 | keep | 0 | Aug | 2022 | 0.0012941 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-04 09:34 | 2022-08-04 19:23 | 10 | 9:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BARRAS EN PEDESTAL | B22080400060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 589 | 2022-08-04 | 5890 | keep | 0 | Aug | 2022 | 0.0040117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-04 09:37 | 2022-08-04 14:34 | 30 | 4:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA POR LLUVIAS | A22080400021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 297 | 2022-08-04 | 8910 | keep | 0 | Aug | 2022 | 0.0060686 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-04 09:43 | 2022-08-04 12:46 | 1 | 3:03 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22080400152 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2022-08-04 | 183 | keep | 0 | Aug | 2022 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-04 10:04 | 2022-08-04 12:36 | 15 | 2:32 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | M22080400123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-08-04 | 2280 | keep | 0 | Aug | 2022 | 0.0015529 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-04 10:05 | 2022-08-04 11:05 | 12 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA. | C22080400036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-08-04 | 720 | keep | 0 | Aug | 2022 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-08-04 10:10 | 2022-08-04 10:50 | 131 | 0:40 | P | CAUSAS EXTERNAS | MUNICIPIO DE SALINAS REALIZANDO DESGANCHE 1 X 65 EN CORTE DE LINEA | P22080400041 | New_Event | Damage From Public | Include | Include | Public | 40 | 2022-08-04 | 5240 | keep | 0 | Aug | 2022 | 0.0035689 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
UTUADO | 2022-08-04 10:19 | 2022-08-04 10:36 | 934 | 0:17 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A22080400052 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-04 | 15878 | keep | 0 | Aug | 2022 | 0.010814 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-08-04 10:19 | 2022-08-04 10:36 | 4 | 0:17 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A22080400052 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-04 | 68 | keep | 0 | Aug | 2022 | 4.6314e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-08-04 10:19 | 2022-08-04 10:36 | 1479 | 0:17 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A22080400052 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-04 | 25143 | keep | 0 | Aug | 2022 | 0.017125 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-08-04 10:19 | 2022-08-04 10:36 | 1841 | 0:17 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A22080400053 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-04 | 31297 | keep | 0 | Aug | 2022 | 0.021316 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-08-04 10:19 | 2022-08-04 10:36 | 1950 | 0:17 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36400 | A22080400053 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-04 | 33150 | keep | 0 | Aug | 2022 | 0.022578 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
GUAYAMA | 2022-08-04 10:22 | 2022-08-04 12:00 | 27 | 1:38 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P22080400045 | New_Event | Animals | Include | Include | Wildlife | 98 | 2022-08-04 | 2646 | keep | 0 | Aug | 2022 | 0.0018022 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2022-08-04 10:30 | 2022-08-04 11:48 | 19 | 1:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRA SECUNDARIA EN PEDESTAL | R22080400022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 78 | 2022-08-04 | 1482 | keep | 0 | Aug | 2022 | 0.0010094 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2022-08-04 10:37 | 2022-08-04 13:30 | 14 | 2:53 | P | DESGANCHE | SE RETIRARON BAMBUAS 1 X 50 EN CORTE DE LINEA | P22080400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-08-04 | 2422 | keep | 0 | Aug | 2022 | 0.0016496 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2022-08-04 10:43 | 2022-08-04 13:36 | 150 | 2:53 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A22080400073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-08-04 | 25950 | keep | 0 | Aug | 2022 | 0.017674 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-04 10:45 | 2022-08-04 18:00 | 60 | 7:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE PROVISIONAL PARA REMPLAZO POSTE Y CORREGIR DEFICIENCIAS | S22080400041 | New_Event | Primary Pole Failure | Include | Include | Equipment | 435 | 2022-08-04 | 26100 | keep | 0 | Aug | 2022 | 0.017777 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-04 10:56 | 2022-08-04 11:12 | 1 | 0:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO PORTAFUSIBLE | R22080400024 | New_Event | Cutout Failure | Include | Include | Equipment | 16 | 2022-08-04 | 16 | keep | 0 | Aug | 2022 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-04 11:00 | 2022-08-04 20:30 | 125 | 9:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22080400270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 570 | 2022-08-04 | 71250 | keep | 0 | Aug | 2022 | 0.048528 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2022-08-04 11:04 | 2022-08-04 15:15 | 40 | 4:11 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080400153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-08-04 | 10040 | keep | 0 | Aug | 2022 | 0.0068382 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-08-04 11:13 | 2022-08-04 15:50 | 4 | 4:37 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR QUEMADO 50KVA X 50KVA | A22080400088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 277 | 2022-08-04 | 1108 | keep | 0 | Aug | 2022 | 0.00075465 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-08-04 11:23 | 2022-08-04 15:37 | 1 | 4:14 | P | ANIMAL | 1 X 30 EN RISER HACIA TRANSCLOSURE CRUCE POR AVE | C22080400051 | New_Event | Animals | Include | Include | Wildlife | 254 | 2022-08-04 | 254 | keep | 0 | Aug | 2022 | 0.000173 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-04 11:23 | 2022-08-04 14:50 | 11 | 3:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | C22080400046 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2022-08-04 | 2277 | keep | 0 | Aug | 2022 | 0.0015509 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-08-04 11:23 | 2022-08-04 13:51 | 11 | 2:28 | P | DESGANCHE | 1 X 80 EN C/L Y SE DESGANCHO | C22080400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-08-04 | 1628 | keep | 0 | Aug | 2022 | 0.0011088 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-08-04 11:23 | 2022-08-04 14:54 | 11 | 3:31 | P | DESGANCHE | 2 X 65 C/L | C22080400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-08-04 | 2321 | keep | 0 | Aug | 2022 | 0.0015808 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2022-08-04 11:42 | 2022-08-04 18:30 | 8 | 6:48 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO DE T-12 A SU-01 Y SE CERRO N/O (FID: 16063301) QUEDANDO EN SERVICIO DESDE T-11 | M22080400273 | New_Event | UG Cable Fault | Include | Include | Equipment | 408 | 2022-08-04 | 3264 | keep | 0 | Aug | 2022 | 0.0022231 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-08-04 11:51 | 2022-08-04 19:33 | 60 | 7:42 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22080400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 462 | 2022-08-04 | 27720 | keep | 0 | Aug | 2022 | 0.01888 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-04 11:52 | 2022-08-04 13:51 | 40 | 1:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080400091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 119 | 2022-08-04 | 4760 | keep | 0 | Aug | 2022 | 0.003242 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-04 11:54 | 2022-08-04 14:11 | 80 | 2:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE PRIMARIO | S22080400055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-08-04 | 10960 | keep | 0 | Aug | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-04 12:00 | 2022-08-04 13:12 | 6 | 1:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22080300239 | New_Event | Secondary Wire Break | Include | Include | Equipment | 72 | 2022-08-04 | 432 | keep | 0 | Aug | 2022 | 0.00029423 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-04 12:03 | 2022-08-04 12:04 | 2286 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22080400026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 2286 | keep | 0 | Aug | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
HUMACAO | 2022-08-04 12:19 | 2022-08-04 18:01 | 196 | 5:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22080400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2022-08-04 | 67032 | keep | 0 | Aug | 2022 | 0.045655 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
BAYAMON | 2022-08-04 12:23 | 2022-08-04 12:24 | 2147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 2147 | keep | 0 | Aug | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
AGUADILLA | 2022-08-04 12:28 | 2022-08-04 15:20 | 1 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400205 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2022-08-04 | 172 | keep | 0 | Aug | 2022 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-04 12:30 | 2022-08-04 13:32 | 5 | 1:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M22080400144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 62 | 2022-08-04 | 310 | keep | 0 | Aug | 2022 | 0.00021114 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-04 12:33 | 2022-08-04 12:34 | 3005 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C22080400060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-04 | 3005 | keep | 0 | Aug | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
SAN JUAN | 2022-08-04 12:34 | 2022-08-04 12:35 | 3432 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 80% DE SU CARGA Y LLEVA 10%DEL 1204-03 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 3432 | keep | 0 | Aug | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-08-04 12:34 | 2022-08-04 12:35 | 138 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 10% POR 1204-02 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 138 | keep | 0 | Aug | 2022 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
CAGUAS | 2022-08-04 12:34 | 2022-08-04 17:16 | 160 | 4:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22080400083 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-08-04 | 45120 | keep | 0 | Aug | 2022 | 0.030731 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
ARECIBO | 2022-08-04 12:35 | 2022-08-04 17:27 | 200 | 4:52 | P | ARBOL SOBRE LINEA | 1 X 80 Y 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUAS SOBRE LINEA | A22080400100 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 292 | 2022-08-04 | 58400 | keep | 0 | Aug | 2022 | 0.039776 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-04 12:35 | 2022-08-04 12:45 | 50 | 0:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22080400117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-08-04 | 500 | keep | 0 | Aug | 2022 | 0.00034055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-04 12:38 | 2022-08-04 17:16 | 92 | 4:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22080400061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 278 | 2022-08-04 | 25576 | keep | 0 | Aug | 2022 | 0.01742 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
MAYAGÃœEZ | 2022-08-04 12:40 | 2022-08-04 15:00 | 80 | 2:20 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA | M22080400215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2022-08-04 | 11200 | keep | 0 | Aug | 2022 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-04 12:45 | 2022-08-04 13:38 | 1026 | 0:53 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE CERRO BKR 1647-08 SECCIONALIZANDO ALIMENTADOR. QUEDO EL 65% EN SERVICIO DEL 1646-02 | R22080400029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 53 | 2022-08-04 | 54378 | keep | 0 | Aug | 2022 | 0.037037 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2022-08-04 12:45 | 2022-08-04 13:07 | 1474 | 0:22 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR 1647-08 LLEVANDO CARGA 1646-02 SE CERRO POR SCADA ABRIENDO N/O ENTRE AMBOS ALIMENTADORES 100% EN SERVICIO 1647-08 Y FUERA LA CARGA 1646-02 | R22080400029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 22 | 2022-08-04 | 32428 | keep | 0 | Aug | 2022 | 0.022087 | 0.0010039 | Sustained | FALSE | FALSE | Not_TMED_Event | 1474
MAYAGÃœEZ | 2022-08-04 12:45 | 2022-08-04 12:46 | 990 | 0:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE DEL INTERRUPTOR | M22080400395 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-08-04 | 990 | keep | 0 | Aug | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
GUAYAMA | 2022-08-04 12:49 | 2022-08-04 19:00 | 2 | 6:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | P22080400077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 371 | 2022-08-04 | 742 | keep | 0 | Aug | 2022 | 0.00050537 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-04 12:51 | 2022-08-04 19:44 | 100 | 6:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22080400229 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 413 | 2022-08-04 | 41300 | keep | 0 | Aug | 2022 | 0.028129 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-04 12:51 | 2022-08-04 17:54 | 70 | 5:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIAS | B22080400124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 303 | 2022-08-04 | 21210 | keep | 0 | Aug | 2022 | 0.014446 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-08-04 12:51 | 2022-08-04 13:51 | 30 | 1:00 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA SUBIR NEUTRAL PARTIDO | B22080400034 | New_Event | Primary Wire Break | Include | Include | Equipment | 60 | 2022-08-04 | 1800 | keep | 0 | Aug | 2022 | 0.001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-04 12:52 | 2022-08-04 15:29 | 20 | 2:37 | P | NO SE REPORTO CAUSA | 1X20 EN XMR | B22080400126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-08-04 | 3140 | keep | 0 | Aug | 2022 | 0.0021386 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-08-04 12:58 | 2022-08-04 14:50 | 1 | 1:52 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A22080400193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-08-04 | 112 | keep | 0 | Aug | 2022 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-04 12:58 | 2022-08-04 14:50 | 2266 | 1:52 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A22080400193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-08-04 | 253792 | keep | 0 | Aug | 2022 | 0.17286 | 0.0015434 | Sustained | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2022-08-04 12:58 | 2022-08-04 14:50 | 1399 | 1:52 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2600 | A22080400193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-08-04 | 156688 | keep | 0 | Aug | 2022 | 0.10672 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 3428 | 0:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 LLEVA 80% DE SU CARGA Y LLEVA 10% DE 1204-03 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 10284 | keep | 0 | Aug | 2022 | 0.0070044 | 0.0023348 | Momentary | FALSE | FALSE | Not_TMED_Event | 3428
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 1381 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 4143 | keep | 0 | Aug | 2022 | 0.0028218 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 1977 | 0:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 40% POR 1206-04 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 5931 | keep | 0 | Aug | 2022 | 0.0040396 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 8679 | 0:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 85% POR 1206-03 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 26037 | keep | 0 | Aug | 2022 | 0.017734 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 641 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 LLEVA 1206-02 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 1923 | keep | 0 | Aug | 2022 | 0.0013097 | 0.00043658 | Momentary | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 733 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 SU CARGA POR 1206-01 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 2199 | keep | 0 | Aug | 2022 | 0.0014977 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 3719 | 0:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 LLEVA 90% DE SU CARGA Y LLEVA 85% 1204-05 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 11157 | keep | 0 | Aug | 2022 | 0.007599 | 0.002533 | Momentary | FALSE | FALSE | Not_TMED_Event | 3719
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 1799 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 LLEVA 20% DE 1303-02 LLEVA 40% DE 1204-04 LLEVA 60% DE 1204-03 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 5397 | keep | 0 | Aug | 2022 | 0.0036759 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-04 13:04 | 2022-08-04 13:07 | 487 | 0:03 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37900 20% POR 1206-04 | S22080400078 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-04 | 1461 | keep | 0 | Aug | 2022 | 0.00099508 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
PONCE | 2022-08-04 13:08 | 2022-08-04 15:10 | 20 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 25 EN SW NO SE REPORTO CAUSA | P22080400078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-08-04 | 2440 | keep | 0 | Aug | 2022 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-04 13:09 | 2022-08-04 19:55 | 11 | 6:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22080400171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 406 | 2022-08-04 | 4466 | keep | 0 | Aug | 2022 | 0.0030418 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-08-04 13:09 | 2022-08-04 16:33 | 131 | 3:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22080400067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-08-04 | 26724 | keep | 0 | Aug | 2022 | 0.018202 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
AGUADILLA | 2022-08-04 13:18 | 2022-08-04 17:37 | 50 | 4:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REFIRIO PARA DESGANCHE | M22080400262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-08-04 | 12950 | keep | 0 | Aug | 2022 | 0.0088202 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-04 13:20 | 2022-08-04 14:41 | 11 | 1:21 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO SECUNDARIO | B22080400142 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 81 | 2022-08-04 | 891 | keep | 0 | Aug | 2022 | 0.00060686 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-08-04 13:22 | 2022-08-04 19:45 | 100 | 6:23 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400269 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 383 | 2022-08-04 | 38300 | keep | 0 | Aug | 2022 | 0.026086 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-04 13:34 | 2022-08-04 15:26 | 177 | 1:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE PRIMARIO | R22080400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-08-04 | 19824 | keep | 0 | Aug | 2022 | 0.013502 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
CANOVANAS | 2022-08-04 13:37 | 2022-08-04 13:38 | 1474 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DEL CAMPO PARA CERRAR MACHETE N/O INCOMODO ENTRO 100% DEL 1647-08 Y 65% DEL 1646-02 | R22080400029 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-04 | 1474 | keep | 0 | Aug | 2022 | 0.0010039 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-04 13:38 | 2022-08-04 14:51 | 359 | 1:13 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PARA REEMPLAZAR AISLADOR PARTIDO ENTRO 80% EN SERVICIO CARGA POR EL 1647-08 | R22080400029 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 73 | 2022-08-04 | 26207 | keep | 0 | Aug | 2022 | 0.017849 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-04 13:41 | 2022-08-04 14:32 | 6 | 0:51 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | S22080400081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-08-04 | 306 | keep | 0 | Aug | 2022 | 0.00020842 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-08-04 13:45 | 2022-08-04 16:58 | 30 | 3:13 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22080400084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-08-04 | 5790 | keep | 0 | Aug | 2022 | 0.0039435 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-04 13:58 | 2022-08-04 14:04 | 74 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1529-11 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-08-04 | 444 | keep | 0 | Aug | 2022 | 0.00030241 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-08-04 13:58 | 2022-08-04 14:04 | 1370 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1521-02 | S22080400084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-08-04 | 8220 | keep | 0 | Aug | 2022 | 0.0055986 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
MAYAGÃœEZ | 2022-08-04 13:58 | 2022-08-04 21:00 | 60 | 7:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400303 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 422 | 2022-08-04 | 25320 | keep | 0 | Aug | 2022 | 0.017245 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-08-04 13:58 | 2022-08-04 20:41 | 200 | 6:43 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | A22080400126 | New_Event | Primary Wire Break | Include | Include | Equipment | 403 | 2022-08-04 | 80600 | keep | 0 | Aug | 2022 | 0.054896 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-08-04 13:58 | 2022-08-04 21:41 | 200 | 7:43 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | A22080400126 | New_Event | Primary Wire Break | Include | Include | Equipment | 463 | 2022-08-04 | 92600 | keep | 0 | Aug | 2022 | 0.063069 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-04 14:05 | 2022-08-04 16:47 | 147 | 2:42 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22080400156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-08-04 | 23814 | keep | 0 | Aug | 2022 | 0.01622 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
HUMACAO | 2022-08-04 14:06 | 2022-08-04 16:01 | 1 | 1:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22080400092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-08-04 | 115 | keep | 0 | Aug | 2022 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-04 14:09 | 2022-08-04 19:05 | 150 | 4:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA 1 X 50 EN SU 1 X 80 EN RISER RECIERE DE LINEA Y 1 X 30 EN TRANSFORMADOR MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22080400314 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 296 | 2022-08-04 | 44400 | keep | 0 | Aug | 2022 | 0.030241 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-04 14:09 | 2022-08-04 15:56 | 150 | 1:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 Y 1 X 80 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR | M22080400315 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 107 | 2022-08-04 | 16050 | keep | 0 | Aug | 2022 | 0.010932 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-04 14:11 | 2022-08-04 14:12 | 828 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 60% POR 1206-04 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-08-04 14:11 | 2022-08-04 14:12 | 1977 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 40% POR 1206-04 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1977 | keep | 0 | Aug | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-04 14:11 | 2022-08-04 14:12 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 40% DEL 1204-04, LLEVA 60% DEL 1204-03 Y LLEVA 20% DEL 1303-02 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1799 | keep | 0 | Aug | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-04 14:11 | 2022-08-04 14:12 | 487 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 20% POR 1206-04 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 487 | keep | 0 | Aug | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
FAJARDO | 2022-08-04 14:17 | 2022-08-04 15:32 | 13 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA | R22080400041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2022-08-04 | 975 | keep | 0 | Aug | 2022 | 0.00066407 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2022-08-04 14:19 | 2022-08-04 15:46 | 10 | 1:27 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22080400132 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 87 | 2022-08-04 | 870 | keep | 0 | Aug | 2022 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-04 14:27 | 2022-08-04 22:40 | 5 | 8:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080400343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2022-08-04 | 2465 | keep | 0 | Aug | 2022 | 0.0016789 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-04 14:27 | 2022-08-05 18:40 | 200 | 28:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO DOS LINEAS PRIMARIAS Y SE CERRO LOS PUENTES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA DEL DIA 08/04 | M22080400342 | New_Event | Primary Wire Break | Include | Include | Equipment | 1693 | 2022-08-04 | 338600 | keep | 0 | Aug | 2022 | 0.23062 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-08-04 14:27 | 2022-08-04 16:30 | 30 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | A22080400133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-08-04 | 3690 | keep | 0 | Aug | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-08-04 14:30 | 2022-08-04 18:05 | 120 | 3:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIA | A22080400135 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 215 | 2022-08-04 | 25800 | keep | 0 | Aug | 2022 | 0.017572 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-08-04 14:42 | 2022-08-04 14:43 | 3114 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080400098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 3114 | keep | 0 | Aug | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
GUAYAMA | 2022-08-04 14:47 | 2022-08-04 17:30 | 20 | 2:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN C/L MAL TIEMPO VIENTOS | P22080400100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 163 | 2022-08-04 | 3260 | keep | 0 | Aug | 2022 | 0.0022204 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-04 14:49 | 2022-08-04 18:09 | 312 | 3:20 | T | ARBOL SOBRE LINEA | SE DISPARO INTERRUPTOR SE PROBO Y QUEDO FUERA DE SERVICIO. SE PATRULLO Y SE ENCONTRO AREA CON MUCHA VEGETACION SOBRE LAS LINEAS A CAUSA DEL MAL TIEMPO. SE SECCIONALIZO Y SE CERRO INTERRUPTOR POR SCADA UN 50% | M22080400369 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 200 | 2022-08-04 | 62400 | keep | 0 | Aug | 2022 | 0.0425 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
CANOVANAS | 2022-08-04 14:51 | 2022-08-04 14:59 | 205 | 0:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO PARA REEMPLAZAR AISLADOR PARTIDO 100% EN SERVICIO CARGA POR EL 1647-08 | R22080400029 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2022-08-04 | 1640 | keep | 0 | Aug | 2022 | 0.001117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-04 14:53 | 2022-08-04 18:20 | 40 | 3:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22080400148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2022-08-04 | 8280 | keep | 0 | Aug | 2022 | 0.0056395 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-04 14:54 | 2022-08-04 18:08 | 40 | 3:14 | P | NO SE REPORTO CAUSA | 1X65 EN C/L Y 1X20 EN OTRO C/L | B22080400172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-08-04 | 7760 | keep | 0 | Aug | 2022 | 0.0052853 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-04 15:05 | 2022-08-04 17:18 | 200 | 2:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S22080400111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-08-04 | 26600 | keep | 0 | Aug | 2022 | 0.018117 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-04 15:07 | 2022-08-04 17:27 | 100 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIAS | B22080400175 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2022-08-04 | 14000 | keep | 0 | Aug | 2022 | 0.0095353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-04 15:12 | 2022-08-04 16:09 | 10 | 0:57 | P | CABLE SOTERRADO AVERIADO | SE REPARO CONDUCTOR SOTERRADO AVERIADO (EVENTOS SALIENDO CON FECHAS ANTERIORES) | M22080300691 | New_Event | UG Cable Fault | Include | Include | Equipment | 57 | 2022-08-04 | 570 | keep | 0 | Aug | 2022 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-04 15:20 | 2022-08-04 17:08 | 2565 | 1:48 | T | CRUCETA DEFECTUOSA O AVERIADA | RECERRO INTERRUPTOR CARGA POR EL 3502-02 SE SECCIONALIZO CERRADO POR CONTROL | C22080400106 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 108 | 2022-08-04 | 277020 | keep | 0 | Aug | 2022 | 0.18868 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-08-04 15:20 | 2022-08-04 17:08 | 3565 | 1:48 | T | CRUCETA DEFECTUOSA O AVERIADA | RECERRO INTERRUPTOR LLEVA LA DEL 3502-01 SE SECCIONALIZO CERRADO POR CONTROL EN SERVICIO EL 70% | C22080400106 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 108 | 2022-08-04 | 385020 | keep | 0 | Aug | 2022 | 0.26224 | 0.0024281 | Sustained | FALSE | FALSE | Not_TMED_Event | 3565
PONCE | 2022-08-04 15:20 | 2022-08-04 15:46 | 1 | 0:26 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE RPIMARIO SAFADO EN XMR | P22080400107 | New_Event | Primary Wire Break | Include | Include | Equipment | 26 | 2022-08-04 | 26 | keep | 0 | Aug | 2022 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-04 15:26 | 2022-08-04 17:08 | 2 | 1:42 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA POR RAYOS | A22080400154 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2022-08-04 | 204 | keep | 0 | Aug | 2022 | 0.00013894 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-04 15:28 | 2022-08-04 16:38 | 20 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO/CERRO XMR PARA REPARAR SECUNDARIA EN PEDESTAL | B22080400180 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-08-04 | 1400 | keep | 0 | Aug | 2022 | 0.00095353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-04 15:30 | 2022-08-04 16:53 | 70 | 1:23 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO AVERIA DE CONDUCTOR PRIMARIO ROTO Y SE REFIRIO A PERSONAL PARA QUE CONTINUE LOS TRABAJOS | M22080400351 | New_Event | Primary Wire Break | Include | Include | Equipment | 83 | 2022-08-04 | 5810 | keep | 0 | Aug | 2022 | 0.0039572 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-08-04 15:36 | 2022-08-04 15:37 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080400402 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 199 | keep | 0 | Aug | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
CANOVANAS | 2022-08-04 15:38 | 2022-08-04 17:22 | 65 | 1:44 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R22080400045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-08-04 | 6760 | keep | 0 | Aug | 2022 | 0.0046042 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-08-04 15:40 | 2022-08-04 17:07 | 15 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | S22080400118 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2022-08-04 | 1305 | keep | 0 | Aug | 2022 | 0.00088883 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-04 15:43 | 2022-08-05 12:00 | 11 | 20:17 | P | POWER TRANSFORMER AVERIADO | REMPLAZO DE XMR AVERIADO 75KVA | B22080400318 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1217 | 2022-08-04 | 13387 | keep | 0 | Aug | 2022 | 0.0091178 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2022-08-04 15:51 | 2022-08-04 18:45 | 9 | 2:54 | P | ANIMAL | 1 X 20 EN XMR AVE CRUZO LINEAS | P22080400115 | New_Event | Animals | Include | Include | Wildlife | 174 | 2022-08-04 | 1566 | keep | 0 | Aug | 2022 | 0.0010666 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2022-08-04 16:12 | 2022-08-04 17:32 | 1 | 1:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CAJA DE C/L | P22080400121 | New_Event | Primary Wire Break | Include | Include | Equipment | 80 | 2022-08-04 | 80 | keep | 0 | Aug | 2022 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-04 16:22 | 2022-08-05 05:50 | 40 | 13:28 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400426 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 808 | 2022-08-04 | 32320 | keep | 0 | Aug | 2022 | 0.022013 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-04 16:26 | 2022-08-04 18:33 | 15 | 2:07 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22080400053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-08-04 | 1905 | keep | 0 | Aug | 2022 | 0.0012975 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-08-04 16:32 | 2022-08-04 16:33 | 3432 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 80% DE SU CARGA | S22080400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 3432 | keep | 0 | Aug | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-08-04 16:38 | 2022-08-04 16:41 | 225 | 0:03 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1303-05 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-04 | 675 | keep | 0 | Aug | 2022 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-04 16:38 | 2022-08-04 16:41 | 870 | 0:03 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1303-04 | S22080400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-04 | 2610 | keep | 0 | Aug | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-08-04 16:46 | 2022-08-04 17:49 | 1859 | 1:03 | T | DESGANCHE | SE RETIRO ARBOL A VARETA (DESDE EL PISO) Y SE CERRO INTERRUPTOR | B22080400200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-08-04 | 117117 | keep | 0 | Aug | 2022 | 0.079768 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2022-08-04 16:49 | 2022-08-04 16:51 | 4028 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22080400201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-04 | 8056 | keep | 0 | Aug | 2022 | 0.0054869 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
MAYAGÃœEZ | 2022-08-04 16:51 | 2022-08-05 03:15 | 20 | 10:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | M22080400443 | New_Event | Secondary Wire Break | Include | Include | Equipment | 624 | 2022-08-04 | 12480 | keep | 0 | Aug | 2022 | 0.0085001 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-04 16:53 | 2022-08-05 12:30 | 40 | 19:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEAS PRIMARIAS SE CERRO CORTE DE LINEA | M22080400351 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1177 | 2022-08-04 | 47080 | keep | 0 | Aug | 2022 | 0.032066 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-04 16:57 | 2022-08-04 17:27 | 43 | 0:30 | P | NO SE REPORTO CAUSA | SE TRANSFIRIO CARGA DEL 1115-05 QUE ESTABA POR 1117-07 AL 1117-09 SE ABRIO EN MH-1 FTE. WALGREENS Y SE CERRO MACHETE CONTRA 1117-09 | S22080400103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-08-04 | 1290 | keep | 0 | Aug | 2022 | 0.00087861 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2022-08-04 17:08 | 2022-08-04 19:20 | 1070 | 2:12 | P | CRUCETA DEFECTUOSA O AVERIADA | SE SECCIONALIZO CRUCE PARTIDA Y SE CERRO N/O CON EL 9602-04 | C22080400106 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 132 | 2022-08-04 | 141240 | keep | 0 | Aug | 2022 | 0.096198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-04 17:11 | 2022-08-04 17:12 | 27 | 0:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA TRANSFERIR LA CARGA Y NO FUNDIERA FUSIBLES DE CAGUITAS MALL, PARTE DE LA CARGA X 3006-04 CG-220804-02 | C22080400014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-04 | 27 | keep | 0 | Aug | 2022 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
AGUADILLA | 2022-08-04 17:11 | 2022-08-05 03:00 | 70 | 9:49 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400452 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 589 | 2022-08-04 | 41230 | keep | 0 | Aug | 2022 | 0.028082 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-08-04 17:14 | 2022-08-04 18:10 | 10 | 0:56 | P | SECUNDARIA/DESGANCHE | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO Y DESGANCHE | R22080400061 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 56 | 2022-08-04 | 560 | keep | 0 | Aug | 2022 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-08-04 17:18 | 2022-08-04 18:31 | 30 | 1:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L FUERTES VIENTOS | P22080400135 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 73 | 2022-08-04 | 2190 | keep | 0 | Aug | 2022 | 0.0014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-04 17:22 | 2022-08-04 20:32 | 1382 | 3:10 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTE PARA SECCIONALIZAR AVERIA DE POSTE PARTIDO CONTINUA ALREDEDOR DE 190 CLIENTES SIN SERVICIO | A22080400165 | New_Event | Primary Pole Failure | Include | Include | Equipment | 190 | 2022-08-04 | 262580 | keep | 0 | Aug | 2022 | 0.17884 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
HUMACAO | 2022-08-04 17:25 | 2022-08-04 17:26 | 1250 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 2901-04 EN SERVICIO | C22080400152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1250 | keep | 0 | Aug | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-08-04 17:25 | 2022-08-04 17:26 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 2901-02 EN SERVICIO | C22080400152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1827 | keep | 0 | Aug | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
MAYAGÃœEZ | 2022-08-04 17:27 | 2022-08-04 22:32 | 60 | 5:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080400461 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-08-04 | 18300 | keep | 0 | Aug | 2022 | 0.012464 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-04 17:35 | 2022-08-04 19:16 | 300 | 1:41 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTE DE LINEA DESGANCHE | S22080400157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-08-04 | 30300 | keep | 0 | Aug | 2022 | 0.020637 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-04 17:39 | 2022-08-04 17:42 | 737 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 40% DE SU CARGA Y 30% 1346-03 | S22080400159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-04 | 2211 | keep | 0 | Aug | 2022 | 0.0015059 | 0.00050197 | Momentary | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2022-08-04 17:39 | 2022-08-04 17:42 | 726 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 30% POR 1346-02 | S22080400159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-04 | 2178 | keep | 0 | Aug | 2022 | 0.0014834 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
BAYAMON | 2022-08-04 17:42 | 2022-08-04 22:31 | 100 | 4:49 | P | DESGANCHE | 1X30 EN C/L | B22080400230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-08-04 | 28900 | keep | 0 | Aug | 2022 | 0.019684 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-04 17:43 | 2022-08-04 21:32 | 27 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 20 EN PROVISIONAL AEREO | R22080400065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-08-04 | 6183 | keep | 0 | Aug | 2022 | 0.0042112 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-08-04 17:46 | 2022-08-04 17:47 | 3597 | 0:01 | T | DESGANCHE | RECERRO | B22080400232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-04 | 3597 | keep | 0 | Aug | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-08-04 17:47 | 2022-08-04 20:22 | 200 | 2:35 | P | DESGANCHE | 1X140 EN C/L SE REFIRIO PARA DESGANCHE | B22080400239 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-08-04 | 31000 | keep | 0 | Aug | 2022 | 0.021114 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-04 17:51 | 2022-08-04 17:52 | 2861 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080400238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 2861 | keep | 0 | Aug | 2022 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | Not_TMED_Event | 2861
BAYAMON | 2022-08-04 17:55 | 2022-08-04 21:21 | 20 | 3:26 | P | PARARRAYOS DEFECTUOSO | 1X25 EN C/L SE RETIRO PARARRAYO QUEMADO | B22080400240 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 206 | 2022-08-04 | 4120 | keep | 0 | Aug | 2022 | 0.0028061 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-04 18:05 | 2022-08-05 12:30 | 30 | 18:25 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22080400173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1105 | 2022-08-04 | 33150 | keep | 0 | Aug | 2022 | 0.022578 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-04 18:09 | 2022-08-04 18:55 | 156 | 0:46 | P | ARBOL SOBRE LINEA | SE REMOVIO LA OTRA PARTE AFECTADA POR LA VEGETACION A CAUSA DEL MAL TIEMPO. SE CERRO MACHETES Y QUEDO EN SERVICIO 100% | M22080400369 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 46 | 2022-08-04 | 7176 | keep | 0 | Aug | 2022 | 0.0048875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-04 18:11 | 2022-08-04 19:46 | 125 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | M22080400483 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-08-04 | 11875 | keep | 0 | Aug | 2022 | 0.008088 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2022-08-04 18:25 | 2022-08-04 19:32 | 10 | 1:07 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR RAYO | M22080400487 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 67 | 2022-08-04 | 670 | keep | 0 | Aug | 2022 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-04 18:28 | 2022-08-04 20:06 | 80 | 1:38 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | A22080400182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-08-04 | 7840 | keep | 0 | Aug | 2022 | 0.0053398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-04 18:28 | 2022-08-05 15:57 | 10 | 21:29 | P | DESGANCHE | 1 X 25 Y 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | A22080400198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1289 | 2022-08-04 | 12890 | keep | 0 | Aug | 2022 | 0.0087793 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-08-04 18:31 | 2022-08-05 14:00 | 22 | 19:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50KVA A 2.4 KV AVERIADO | P22080400142 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1169 | 2022-08-04 | 25718 | keep | 0 | Aug | 2022 | 0.017516 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2022-08-04 18:36 | 2022-08-04 20:16 | 132 | 1:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22080400170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-08-04 | 13200 | keep | 0 | Aug | 2022 | 0.0089905 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
VEGA BAJA | 2022-08-04 18:43 | 2022-08-04 20:49 | 150 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA POR NO SE ENCUENTRA CAUSA | A22080400185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-08-04 | 18900 | keep | 0 | Aug | 2022 | 0.012873 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-04 18:47 | 2022-08-04 21:18 | 20 | 2:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M22080400493 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-08-04 | 3020 | keep | 0 | Aug | 2022 | 0.0020569 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-04 18:53 | 2022-08-04 23:43 | 40 | 4:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X20 EN XMR Y SE REMPLAZO CAJA PRIMARIA DE XMR | S22080400127 | New_Event | Cutout Failure | Include | Include | Equipment | 290 | 2022-08-04 | 11600 | keep | 0 | Aug | 2022 | 0.0079007 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-04 18:53 | 2022-08-04 21:14 | 100 | 2:21 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 65 EN CORTE DE LINEA NO CAUSA | S22080400182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2022-08-04 | 14100 | keep | 0 | Aug | 2022 | 0.0096034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-04 18:53 | 2022-08-04 19:58 | 1 | 1:05 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA PARTIDA | A22080400253 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-08-04 | 65 | keep | 0 | Aug | 2022 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-04 18:59 | 2022-08-04 21:43 | 5 | 2:44 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B22080400254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-08-04 | 820 | keep | 0 | Aug | 2022 | 0.0005585 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-08-04 19:20 | 2022-08-04 19:40 | 107 | 0:20 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REEMPLAZO CRUCETA PARTIDA | C22080400106 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 20 | 2022-08-04 | 2140 | keep | 0 | Aug | 2022 | 0.0014575 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-04 19:22 | 2022-08-04 19:23 | 573 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1704-05 | B22080400257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 573 | keep | 0 | Aug | 2022 | 0.00039027 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2022-08-04 19:22 | 2022-08-04 19:23 | 1313 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1704-04 | B22080400257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 1313 | keep | 0 | Aug | 2022 | 0.00089428 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
BAYAMON | 2022-08-04 19:39 | 2022-08-04 20:55 | 62 | 1:16 | P | DESGANCHE | 1X80 EN C/L SE REFIRIO PARA DESGANCHE | B22080400262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-08-04 | 4712 | keep | 0 | Aug | 2022 | 0.0032093 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
MAYAGÃœEZ | 2022-08-04 19:47 | 2022-08-04 21:00 | 80 | 1:13 | P | MAL TIEMPO/RAYOS | 1 X 100 EN SU-6 MAL TIEMPO DESCARGAS ELECTRICAS | M22080400509 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 73 | 2022-08-04 | 5840 | keep | 0 | Aug | 2022 | 0.0039776 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-04 19:49 | 2022-08-05 15:16 | 2 | 19:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO ALAMBRE SECUNDARIO EN EL SUELO | S22080400190 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1167 | 2022-08-04 | 2334 | keep | 0 | Aug | 2022 | 0.0015897 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-04 20:07 | 2022-08-04 20:10 | 922 | 0:03 | T | NO SE REPORTO CAUSA | SE DISPARO SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1401-08 | S22080400199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-04 | 2766 | keep | 0 | Aug | 2022 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-08-04 20:07 | 2022-08-04 20:10 | 135 | 0:03 | T | NO SE REPORTO CAUSA | SE DISPARO SE CERRO POR CONTROL LLEVA LA CARGA DEL 1346-05 | S22080400199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-04 | 405 | keep | 0 | Aug | 2022 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
AGUADILLA | 2022-08-04 20:10 | 2022-08-04 22:05 | 20 | 1:55 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400154 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 115 | 2022-08-04 | 2300 | keep | 0 | Aug | 2022 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-04 20:13 | 2022-08-04 23:50 | 50 | 3:37 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22080400271 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-08-04 | 10850 | keep | 0 | Aug | 2022 | 0.0073899 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-04 20:18 | 2022-08-04 22:17 | 200 | 1:59 | P | DESGANCHE | 2X140 EN C/L 30% DE SU CARGA TRANSFERIDA AL 1346-02 | S22080400202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-08-04 | 23800 | keep | 0 | Aug | 2022 | 0.01621 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-08-04 20:20 | 2022-08-04 20:50 | 321 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PARA TRABAJAR CERRANDO PUENTE DE LINEA A MACHETES CARGA DEL CONVERTIDOR 3205-07 POR EL 3201-01. SE AFECTO 20% DE LA CARGA DEL CONVERTIDOR (1608 CLIENTES) | C22080400276 | New_Event | Primary Wire Break | Include | Include | Equipment | 30 | 2022-08-04 | 9630 | keep | 0 | Aug | 2022 | 0.0065589 | 0.00021863 | Sustained | FALSE | FALSE | Not_TMED_Event | 321
UTUADO | 2022-08-04 20:32 | 2022-08-05 23:30 | 1000 | 26:58 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE Y SE REPARO LINEA PRIMARIA | A22080400201 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1618 | 2022-08-04 | 1618000 | keep | 0 | Aug | 2022 | 1.102 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-04 20:50 | 2022-08-04 23:00 | 483 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PARA TRABAJAR CERRANDO PUENTE DE LINEA A MACHETES CARGA DEL CONVERTIDOR 3205-07 POR EL 3201-01. SE AFECTO 10% ADICIONAL DE LA CARGA DEL CONVERTIDOR (1608 CLIENTES) | C22080400276 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 130 | 2022-08-04 | 62790 | keep | 0 | Aug | 2022 | 0.042766 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-04 20:59 | 2022-08-04 21:00 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA 95% DEL 1717-02 | B22080400285 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-04 20:59 | 2022-08-04 21:00 | 865 | 0:01 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL 95% DE SU CARGA TRANSFERIDA AL 1713-05 | B22080400285 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-04 | 865 | keep | 0 | Aug | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
AGUADILLA | 2022-08-04 21:06 | 2022-08-05 13:02 | 8 | 15:56 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080400524 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 956 | 2022-08-04 | 7648 | keep | 0 | Aug | 2022 | 0.005209 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-04 21:10 | 2022-08-04 22:45 | 276 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE DE LINEA A MACHETES | C22080400276 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2022-08-04 | 26220 | keep | 0 | Aug | 2022 | 0.017858 | 0.00018798 | Sustained | FALSE | FALSE | Not_TMED_Event | 276
UTUADO | 2022-08-04 21:41 | 2022-08-05 15:11 | 7 | 17:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | A22080400126 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1050 | 2022-08-04 | 7350 | keep | 0 | Aug | 2022 | 0.0050061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-04 21:47 | 2022-08-05 16:12 | 6 | 18:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | M22080400532 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1105 | 2022-08-04 | 6630 | keep | 0 | Aug | 2022 | 0.0045157 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-08-04 21:50 | 2022-08-05 10:30 | 25 | 12:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22080400535 | New_Event | Vegetation Contact | Include | Include | Vegetation | 760 | 2022-08-04 | 19000 | keep | 0 | Aug | 2022 | 0.012941 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-04 22:17 | 2022-08-04 22:21 | 737 | 0:04 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL (LUEGO DE VERIFICAR PERSONAL FUERA DE LAS LINEAS) 60% DE SU CARGA TRANSFERIDA AL 1529-15 LLEVA 30% DEL 1346-03 | S22080400225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-04 | 2948 | keep | 0 | Aug | 2022 | 0.0020079 | 0.00050197 | Momentary | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2022-08-04 22:17 | 2022-08-04 22:21 | 726 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR - SE CERRO POR CONTROL (LUEGO DE VERIFICAR PERSONAL FUERA DE LAS LINEAS) 30% DE SU CARGA TRANSFERIDA AL 1346-02 | S22080400225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-04 | 2904 | keep | 0 | Aug | 2022 | 0.0019779 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
AGUADILLA | 2022-08-04 22:17 | 2022-08-05 09:10 | 10 | 10:53 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080400540 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 653 | 2022-08-04 | 6530 | keep | 0 | Aug | 2022 | 0.0044476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-04 22:18 | 2022-08-05 11:46 | 26 | 13:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22080400290 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 808 | 2022-08-04 | 21008 | keep | 0 | Aug | 2022 | 0.014308 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-08-04 22:21 | 2022-08-04 23:46 | 200 | 1:25 | P | DESGANCHE | 2X140 EN C/L 30% DE SU CARGA TRANSFERIDA AL 1346-02 | S22080400202 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-04 | 17000 | keep | 0 | Aug | 2022 | 0.011579 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-04 22:23 | 2022-08-05 14:46 | 9 | 16:23 | P | DESGANCHE | 2X50 EN C/L | S22080400223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 983 | 2022-08-04 | 8847 | keep | 0 | Aug | 2022 | 0.0060257 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-08-04 23:44 | 2022-08-05 12:13 | 70 | 12:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22080400544 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 749 | 2022-08-04 | 52430 | keep | 0 | Aug | 2022 | 0.03571 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-08-05 00:26 | 2022-08-05 02:51 | 2276 | 2:25 | T | DESGANCHE | DISPARO DE BKR SE REALIZO DESGANCHE Y SE RETIRO AISLADOR QUE ESTABA SOBRE LA LINEA CON VARETA DESDE EL SUELO | C22080400281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-08-05 | 330020 | keep | 0 | Aug | 2022 | 0.22478 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
AGUADILLA | 2022-08-05 00:42 | 2022-08-05 13:00 | 1115 | 12:18 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA | M22080300579 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 738 | 2022-08-05 | 822870 | keep | 0 | Aug | 2022 | 0.56045 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-05 01:46 | 2022-08-05 01:48 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1303-04 | S22080500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-05 | 3362 | keep | 0 | Aug | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-08-05 01:46 | 2022-08-05 01:48 | 1598 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1303-04 | S22080500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-05 | 3196 | keep | 0 | Aug | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
MAYAGÃœEZ | 2022-08-05 01:56 | 2022-08-05 10:00 | 40 | 8:04 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080400552 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 484 | 2022-08-05 | 19360 | keep | 0 | Aug | 2022 | 0.013186 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-05 02:05 | 2022-08-05 02:06 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 3438 | keep | 0 | Aug | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
VEGA BAJA | 2022-08-05 02:06 | 2022-08-05 11:26 | 10 | 9:20 | P | NO SE REPORTO CAUSA | SE REMPLAZO XMR DE 50KVA POR 50KVA | B22080500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 560 | 2022-08-05 | 5600 | keep | 0 | Aug | 2022 | 0.0038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-05 02:13 | 2022-08-05 08:57 | 59 | 6:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22080500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 404 | 2022-08-05 | 23836 | keep | 0 | Aug | 2022 | 0.016235 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
AGUADILLA | 2022-08-05 02:22 | 2022-08-06 14:05 | 60 | 35:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 80 EN CORTE DE LINEA POR POSTE PARTIDO | M22080500392 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2143 | 2022-08-05 | 128580 | keep | 0 | Aug | 2022 | 0.087575 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-08-05 02:27 | 2022-08-06 09:03 | 300 | 30:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080500393 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1836 | 2022-08-05 | 550800 | keep | 0 | Aug | 2022 | 0.37515 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-08-05 02:55 | 2022-08-05 02:56 | 424 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 424 | keep | 0 | Aug | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
BAYAMON | 2022-08-05 04:27 | 2022-08-05 08:27 | 478 | 4:00 | T | DESGANCHE | SE RETIRO RAMAS Y SE CERRO POR SCADA EL 1705-01 QUE LLEVA 90% DEL 1705-03 | B22080500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-08-05 | 114720 | keep | 0 | Aug | 2022 | 0.078135 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-08-05 04:27 | 2022-08-05 08:27 | 854 | 4:00 | P | DESGANCHE | SE RETIRO RAMAS Y SE CERRO POR SCADA EL 1705-01 QUE LLEVA 90% DEL 1705-03 | B22080500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-08-05 | 204960 | keep | 0 | Aug | 2022 | 0.1396 | 0.00058166 | Sustained | FALSE | FALSE | Not_TMED_Event | 854
FAJARDO | 2022-08-05 04:43 | 2022-08-05 08:50 | 40 | 4:07 | P | DESGANCHE | 1 X 25 EN C/L Y SE REALIZO DESGANCHE | R22080400077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-08-05 | 9880 | keep | 0 | Aug | 2022 | 0.0067292 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-05 05:05 | 2022-08-05 10:21 | 100 | 5:16 | P | DESGANCHE | 3 X 65 EN C/L SE REALIZO DESGANCHE | B22080500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2022-08-05 | 31600 | keep | 0 | Aug | 2022 | 0.021523 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-08-05 06:43 | 2022-08-05 13:05 | 15 | 6:22 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO | C22080500113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 382 | 2022-08-05 | 5730 | keep | 0 | Aug | 2022 | 0.0039027 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-05 06:44 | 2022-08-05 11:57 | 190 | 5:13 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | B22080500020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-08-05 | 59470 | keep | 0 | Aug | 2022 | 0.040505 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BAYAMON | 2022-08-05 07:01 | 2022-08-05 14:51 | 1 | 7:50 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER | S22080500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 470 | 2022-08-05 | 470 | keep | 0 | Aug | 2022 | 0.00032011 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-05 07:11 | 2022-08-05 11:58 | 1 | 4:47 | P | ANIMAL | 1 X 65 Y 2 X 50 EN C/LS CRUCE X AVE | C22080500031 | New_Event | Animals | Include | Include | Wildlife | 287 | 2022-08-05 | 287 | keep | 0 | Aug | 2022 | 0.00019547 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-05 07:13 | 2022-08-05 07:14 | 1983 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA 1711-04 CERRADO POR SCADA | B22080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 1983 | keep | 0 | Aug | 2022 | 0.0013506 | 0.0013506 | Momentary | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-08-05 07:13 | 2022-08-05 07:14 | 500 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA PARTE DEL 1717-01 CERRADO POR SCADA | B22080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 500 | keep | 0 | Aug | 2022 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-08-05 07:13 | 2022-08-05 07:14 | 186 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1801-02 LLEVA 1711-04 Y PARTE DEL 1717-01 CERRADO POR SCADA | B22080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 186 | keep | 0 | Aug | 2022 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2022-08-05 07:14 | 2022-08-05 11:55 | 80 | 4:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22080500038 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 281 | 2022-08-05 | 22480 | keep | 0 | Aug | 2022 | 0.015311 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-05 07:21 | 2022-08-05 10:30 | 20 | 3:09 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22080500032 | New_Event | Animals | Include | Include | Wildlife | 189 | 2022-08-05 | 3780 | keep | 0 | Aug | 2022 | 0.0025745 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-05 07:23 | 2022-08-05 15:44 | 15 | 8:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR Y SE REPARO SECUNDARIA ABIERTA - TRASPATIO | S22080500013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 501 | 2022-08-05 | 7515 | keep | 0 | Aug | 2022 | 0.0051184 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-05 07:28 | 2022-08-05 08:20 | 3871 | 0:52 | T | DESGANCHE | SE RETIRO RAMAS DE PALMA Y SE CERRO POR SCADA | B22080500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-08-05 | 201292 | keep | 0 | Aug | 2022 | 0.1371 | 0.0026365 | Sustained | FALSE | FALSE | Not_TMED_Event | 3871
CANOVANAS | 2022-08-05 07:41 | 2022-08-05 10:10 | 98 | 2:29 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | R22080500003 | New_Event | Animals | Include | Include | Wildlife | 149 | 2022-08-05 | 14602 | keep | 0 | Aug | 2022 | 0.0099454 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
VEGA BAJA | 2022-08-05 08:07 | 2022-08-05 19:45 | 9 | 11:38 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE REPARARO LINEA SECUNDARIAS PARTIDAS POR ARBOL | A22080500007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 698 | 2022-08-05 | 6282 | keep | 0 | Aug | 2022 | 0.0042786 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-08-05 08:08 | 2022-08-05 08:30 | 25 | 0:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 25 EN RISER | B22080400040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2022-08-05 | 550 | keep | 0 | Aug | 2022 | 0.0003746 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-08-05 08:18 | 2022-08-05 11:57 | 2 | 3:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA EN CORTE DE LINEA QUEMADA | P22080500009 | New_Event | Cutout Failure | Include | Include | Equipment | 219 | 2022-08-05 | 438 | keep | 0 | Aug | 2022 | 0.00029832 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-05 08:50 | 2022-08-05 19:18 | 1 | 10:28 | P | NO SE REPORTO CAUSA | 3X100 EN EL SU-3 | S22080500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 628 | 2022-08-05 | 628 | keep | 0 | Aug | 2022 | 0.00042773 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-05 08:51 | 2022-08-05 10:48 | 47 | 1:57 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22080500034 | New_Event | Animals | Include | Include | Wildlife | 117 | 2022-08-05 | 5499 | keep | 0 | Aug | 2022 | 0.0037453 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CAGUAS | 2022-08-05 08:55 | 2022-08-05 14:40 | 2 | 5:45 | P | CONDUCTOR ROTO O ABIERTO | SE RELOCALIZO POSTE Y LINEA | C22080500035 | New_Event | Primary Wire Break | Include | Include | Equipment | 345 | 2022-08-05 | 690 | keep | 0 | Aug | 2022 | 0.00046996 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-08-05 08:58 | 2022-08-05 15:17 | 19 | 6:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22080500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2022-08-05 | 7201 | keep | 0 | Aug | 2022 | 0.0049046 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-08-05 09:03 | 2022-08-05 14:30 | 80 | 5:27 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS AVERIADO | M22080500030 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 327 | 2022-08-05 | 26160 | keep | 0 | Aug | 2022 | 0.017817 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-05 09:16 | 2022-08-06 08:39 | 10 | 23:23 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080500145 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1403 | 2022-08-05 | 14030 | keep | 0 | Aug | 2022 | 0.0095558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-05 09:17 | 2022-08-05 12:21 | 30 | 3:04 | P | OTRAS CAUSAS | 1 X 50 EN C/L NO CAUSA | C22080500041 | New_Event | Other Causes | Include | Include | Other | 184 | 2022-08-05 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-08-05 09:27 | 2022-08-05 09:30 | 5042 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A22080500036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-05 | 15126 | keep | 0 | Aug | 2022 | 0.010302 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
ARECIBO | 2022-08-05 09:27 | 2022-08-05 09:30 | 2720 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A22080500036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-05 | 8160 | keep | 0 | Aug | 2022 | 0.0055577 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-08-05 09:27 | 2022-08-05 09:30 | 1883 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 | A22080500036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-05 | 5649 | keep | 0 | Aug | 2022 | 0.0038475 | 0.0012825 | Momentary | FALSE | FALSE | Not_TMED_Event | 1883
VEGA BAJA | 2022-08-05 09:43 | 2022-08-05 11:00 | 50 | 1:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-08-05 | 3850 | keep | 0 | Aug | 2022 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-05 09:47 | 2022-08-05 11:40 | 63 | 1:53 | P | PARARRAYOS DEFECTUOSO | 1X 50 EN C/L Y SE REEMPLAZO PARARRAYO | R22080500012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 113 | 2022-08-05 | 7119 | keep | 0 | Aug | 2022 | 0.0048487 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
PONCE | 2022-08-05 09:50 | 2022-08-05 11:05 | 60 | 1:15 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS PRIMARIAS | P22080500018 | New_Event | Animals | Include | Include | Wildlife | 75 | 2022-08-05 | 4500 | keep | 0 | Aug | 2022 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-08-05 10:10 | 2022-08-05 14:15 | 20 | 4:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR | P22080500019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2022-08-05 | 4900 | keep | 0 | Aug | 2022 | 0.0033374 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-05 10:15 | 2022-08-05 16:56 | 2 | 6:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZA TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | A22080500045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 401 | 2022-08-05 | 802 | keep | 0 | Aug | 2022 | 0.00054624 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-05 10:21 | 2022-08-05 18:47 | 40 | 8:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22080500073 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 506 | 2022-08-05 | 20240 | keep | 0 | Aug | 2022 | 0.013785 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-05 10:23 | 2022-08-05 14:10 | 14 | 3:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L 1 X 40 EN RISER | R22080500017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-08-05 | 3178 | keep | 0 | Aug | 2022 | 0.0021645 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-08-05 10:45 | 2022-08-05 17:36 | 60 | 6:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO UNA CAJA PRIMARIA AVERIADA | M22080500081 | New_Event | Cutout Failure | Include | Include | Equipment | 411 | 2022-08-05 | 24660 | keep | 0 | Aug | 2022 | 0.016796 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-05 10:48 | 2022-08-05 13:32 | 1 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REMPLAZO PORTAFUSIBLES | B22080500067 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2022-08-05 | 164 | keep | 0 | Aug | 2022 | 0.0001117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-05 10:53 | 2022-08-05 18:42 | 90 | 7:49 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO MASIVO SE VOLVIO A CERRAR C/L (NO FUNDIO) | S22080500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 469 | 2022-08-05 | 42210 | keep | 0 | Aug | 2022 | 0.028749 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2022-08-05 11:00 | 2022-08-05 12:54 | 6 | 1:54 | P | CAUSAS EXTERNAS | ABRIO XMR PARA DESPEGAR TENSOR DEL BUSHING SECUNDARIO | C22080100104 | New_Event | Damage From Public | Include | Include | Public | 114 | 2022-08-05 | 684 | keep | 0 | Aug | 2022 | 0.00046587 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-08-05 11:05 | 2022-08-05 14:02 | 6 | 2:57 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22080500048 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 177 | 2022-08-05 | 1062 | keep | 0 | Aug | 2022 | 0.00072332 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-08-05 11:07 | 2022-08-05 12:45 | 30 | 1:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN C/L | R22080500022 | New_Event | Primary Pole Failure | Include | Include | Equipment | 98 | 2022-08-05 | 2940 | keep | 0 | Aug | 2022 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-08-05 11:22 | 2022-08-05 14:46 | 811 | 3:24 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | C22080500033 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 204 | 2022-08-05 | 165444 | keep | 0 | Aug | 2022 | 0.11268 | 0.00055237 | Sustained | FALSE | FALSE | Not_TMED_Event | 811
SAN JUAN | 2022-08-05 11:30 | 2022-08-05 17:00 | 92 | 5:30 | P | EMPALME SOTERRADO AVERIADO | SE REPARO/EMPALMO SOTERRADO AVERIADO Y SE CERRO DE RISER @ SU-1 MEDIANTE G.O.I. SJ-220805-02 | S22080500051 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 330 | 2022-08-05 | 30360 | keep | 0 | Aug | 2022 | 0.020678 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
SAN JUAN | 2022-08-05 11:51 | 2022-08-05 15:46 | 1 | 3:55 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1X40 EN SU-1 Y 1X25 EN RISER POR CONTAMINACION EN EL SU-1 | S22080500100 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 235 | 2022-08-05 | 235 | keep | 0 | Aug | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-05 12:00 | 2022-08-05 12:44 | 1 | 0:44 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B22080500076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2022-08-05 | 44 | keep | 0 | Aug | 2022 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-05 12:09 | 2022-08-05 18:06 | 2 | 5:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA EN TRANSFORMADOR PARA FIJAR BAJANTE PRIMARIO | P22080500029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 357 | 2022-08-05 | 714 | keep | 0 | Aug | 2022 | 0.0004863 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-05 12:20 | 2022-08-05 16:42 | 12 | 4:22 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE SECUNDARIO PARTIDO (NO FUNDIO) | S22080500102 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 262 | 2022-08-05 | 3144 | keep | 0 | Aug | 2022 | 0.0021414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-08-05 12:24 | 2022-08-05 18:34 | 80 | 6:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30, 1 X 40 Y 1 X 25 EN CORTE DE LINEA MAL TIEMPO | A22080500069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 370 | 2022-08-05 | 29600 | keep | 0 | Aug | 2022 | 0.02016 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-05 12:34 | 2022-08-05 15:15 | 10 | 2:41 | P | NO SE REPORTO CAUSA | 1 X 20 EN PROVISIONAL AEREO | R22080500032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-08-05 | 1610 | keep | 0 | Aug | 2022 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-05 12:45 | 2022-08-05 20:55 | 20 | 8:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO | R22080500022 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 490 | 2022-08-05 | 9800 | keep | 0 | Aug | 2022 | 0.0066747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-05 12:48 | 2022-08-05 20:08 | 4 | 7:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARA BARRA SECUNDARIA | R22080500033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 440 | 2022-08-05 | 1760 | keep | 0 | Aug | 2022 | 0.0011987 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-08-05 12:56 | 2022-08-05 16:40 | 6 | 3:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES EN BAJANTES SECUNDARIOS AJUSTAR BUSHING | P22080500034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 224 | 2022-08-05 | 1344 | keep | 0 | Aug | 2022 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-05 13:00 | 2022-08-05 13:13 | 1115 | 0:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA SE ABRIO NORMALLY OPEN Y SE CERRO CORTE DE LINEA | M22080300579 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 13 | 2022-08-05 | 14495 | keep | 0 | Aug | 2022 | 0.0098725 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-05 13:02 | 2022-08-05 17:48 | 8 | 4:46 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO 37.5KVA X 37.5KVA | A22080500081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 286 | 2022-08-05 | 2288 | keep | 0 | Aug | 2022 | 0.0015583 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-08-05 13:05 | 2022-08-05 16:13 | 60 | 3:08 | P | DESGANCHE | 2 X 65 EN CORTE DE LINE SE REALIZO DESGACHE | A22080500084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-08-05 | 11280 | keep | 0 | Aug | 2022 | 0.0076828 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-05 13:05 | 2022-08-05 13:06 | 1604 | 0:01 | T | DESGANCHE | RECIERRE | C22080500070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-05 | 1604 | keep | 0 | Aug | 2022 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2022-08-05 13:06 | 2022-08-06 09:36 | 15 | 20:30 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO | C22080500113 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1230 | 2022-08-05 | 18450 | keep | 0 | Aug | 2022 | 0.012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-05 13:15 | 2022-08-05 15:44 | 6 | 2:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES SULFATADOS | C22080500073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 149 | 2022-08-05 | 894 | keep | 0 | Aug | 2022 | 0.0006089 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-05 13:25 | 2022-08-05 13:51 | 1 | 0:26 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | R22080500037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-08-05 | 26 | keep | 0 | Aug | 2022 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-05 13:29 | 2022-08-05 16:12 | 100 | 2:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | A22080500099 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 163 | 2022-08-05 | 16300 | keep | 0 | Aug | 2022 | 0.011102 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-05 13:30 | 2022-08-06 11:52 | 90 | 22:22 | P | TERMINACION SOTERRADA AVERIADA | SE CONSTRUYO JUMPER EN SU-1 PARA ENERGIZAR DE FASE A FASE EN LO QUE SE REALIZA LA REPARACION DE LA TERMINACION AVERIADA EN UNA DE LAS FASES | M22080500121 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1342 | 2022-08-05 | 120780 | keep | 0 | Aug | 2022 | 0.082263 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-08-05 13:37 | 2022-08-05 16:44 | 40 | 3:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080500126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-08-05 | 7480 | keep | 0 | Aug | 2022 | 0.0050946 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-05 13:45 | 2022-08-05 15:30 | 150 | 1:45 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B2208050082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-08-05 | 15750 | keep | 0 | Aug | 2022 | 0.010727 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-08-05 13:45 | 2022-08-05 14:10 | 30 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTOR EN BAJANTE SECUNDARIO | P22080500036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-08-05 | 750 | keep | 0 | Aug | 2022 | 0.00051082 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-05 13:45 | 2022-08-05 16:25 | 12 | 2:40 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE MASIVO, SE REPARO BAJANTES SECUNDARIOS Y SE REPARO LINEA SECUNDARIA ROTA | M22080500025 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 160 | 2022-08-05 | 1920 | keep | 0 | Aug | 2022 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-05 13:46 | 2022-08-05 20:40 | 20 | 6:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR LA MISMA CAPACIDAD | M22080500130 | New_Event | Service Transformer Failure | Include | Include | Equipment | 414 | 2022-08-05 | 8280 | keep | 0 | Aug | 2022 | 0.0056395 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-05 13:46 | 2022-08-06 14:35 | 50 | 24:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR LLUVIAS | M22080500391 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1489 | 2022-08-05 | 74450 | keep | 0 | Aug | 2022 | 0.050708 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-05 14:00 | 2022-08-05 18:45 | 3 | 4:45 | P | NO SE REPORTO CAUSA | 2X100 EN C/L | S22080500127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2022-08-05 | 855 | keep | 0 | Aug | 2022 | 0.00058234 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-05 14:00 | 2022-08-05 15:37 | 12 | 1:37 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BUSHING SECUNDARIOS A TRANSFORMADOR | M22080500003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 97 | 2022-08-05 | 1164 | keep | 0 | Aug | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-08-05 14:12 | 2022-08-05 16:20 | 25 | 2:08 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22080500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-08-05 | 3200 | keep | 0 | Aug | 2022 | 0.0021795 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-05 14:16 | 2022-08-05 19:40 | 59 | 5:24 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE POSTE PARTIDO | C22080500078 | New_Event | Primary Pole Failure | Include | Include | Equipment | 324 | 2022-08-05 | 19116 | keep | 0 | Aug | 2022 | 0.01302 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
SAN JUAN | 2022-08-05 14:28 | 2022-08-05 16:37 | 150 | 2:09 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA @ CAJA @ LA ENTRADA HACIA EL C/L (NO FUNDIO) | S22080500132 | New_Event | Primary Wire Break | Include | Include | Equipment | 129 | 2022-08-05 | 19350 | keep | 0 | Aug | 2022 | 0.013179 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-05 14:37 | 2022-08-05 16:09 | 10 | 1:32 | P | SECUNDARIA/DESGANCHE | 1X20 EN XMR | S22080500133 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 92 | 2022-08-05 | 920 | keep | 0 | Aug | 2022 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-05 14:54 | 2022-08-05 21:09 | 19 | 6:15 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-9 | B22080400172 | New_Event | UG Cable Fault | Include | Include | Equipment | 375 | 2022-08-05 | 7125 | keep | 0 | Aug | 2022 | 0.0048528 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-08-05 15:04 | 2022-08-05 18:21 | 2999 | 3:17 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37100 | M22080500164 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 197 | 2022-08-05 | 590803 | keep | 0 | Aug | 2022 | 0.40239 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2022-08-05 15:04 | 2022-08-05 18:21 | 1597 | 3:17 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37100 | M22080500164 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 197 | 2022-08-05 | 314609 | keep | 0 | Aug | 2022 | 0.21428 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
ARECIBO | 2022-08-05 15:09 | 2022-08-05 21:27 | 150 | 6:18 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE LEVANTO LINEA PRIMARIA PARTIDA | A22080500132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 378 | 2022-08-05 | 56700 | keep | 0 | Aug | 2022 | 0.038618 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-08-05 15:15 | 2022-08-05 16:10 | 140 | 0:55 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22080500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-08-05 | 7700 | keep | 0 | Aug | 2022 | 0.0052444 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BARRANQUITAS | 2022-08-05 15:15 | 2022-08-05 16:29 | 90 | 1:14 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22080500085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-08-05 | 6660 | keep | 0 | Aug | 2022 | 0.0045361 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2022-08-05 15:16 | 2022-08-05 18:00 | 50 | 2:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO | A22080500136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-08-05 | 8200 | keep | 0 | Aug | 2022 | 0.005585 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-05 15:20 | 2022-08-05 15:21 | 527 | 0:01 | T | NO SE REPORTO CAUSA | REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22080500049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 527 | keep | 0 | Aug | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2022-08-05 15:25 | 2022-08-06 10:44 | 25 | 19:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080500180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1159 | 2022-08-05 | 28975 | keep | 0 | Aug | 2022 | 0.019735 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-05 15:35 | 2022-08-05 17:23 | 20 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BAJANTES SECUNDARIOS EN XMR | S22080500142 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2022-08-05 | 2160 | keep | 0 | Aug | 2022 | 0.0014712 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-05 15:37 | 2022-08-05 17:56 | 20 | 2:19 | P | ANIMAL | 2 X 40 EN SU-5 IGUANA | R22080500044 | New_Event | Animals | Include | Include | Wildlife | 139 | 2022-08-05 | 2780 | keep | 0 | Aug | 2022 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-08-05 15:40 | 2022-08-05 18:06 | 3973 | 2:26 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR CON CARGA 5602-03 SE REMPLAZO AISLADOR GOI #PC-220805-01A | P22080500048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2022-08-05 | 580058 | keep | 0 | Aug | 2022 | 0.39507 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-08-05 15:40 | 2022-08-05 18:06 | 2484 | 2:26 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR 5602-02 CON CARGA 5602-03 SE REMPLAZO AISLADOR EN ALIMENTADOR 5602-02 Y SE COLOCO INTERRUPTOR 5602-02 EN SERVICIO | P22080500048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 146 | 2022-08-05 | 362664 | keep | 0 | Aug | 2022 | 0.24701 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
CANOVANAS | 2022-08-05 15:51 | 2022-08-05 18:43 | 179 | 2:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER Y SE REEMPLAZO CAJA PRIMARIA | R22080500045 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2022-08-05 | 30788 | keep | 0 | Aug | 2022 | 0.02097 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
AGUADILLA | 2022-08-05 15:55 | 2022-08-05 17:02 | 1 | 1:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DOS CAJAS PRIMARIAS AVERIADAS EN RISER | M22080500657 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2022-08-05 | 67 | keep | 0 | Aug | 2022 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-05 15:58 | 2022-08-05 17:25 | 40 | 1:27 | P | DESGANCHE | 1 X 40 EN C/L DESGACNCHE | P22080500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-08-05 | 3480 | keep | 0 | Aug | 2022 | 0.0023702 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-08-05 15:59 | 2022-08-05 22:00 | 20 | 6:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | A22080500161 | New_Event | Service Transformer Failure | Include | Include | Equipment | 361 | 2022-08-05 | 7220 | keep | 0 | Aug | 2022 | 0.0049175 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-05 16:01 | 2022-08-05 16:02 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 1017 | keep | 0 | Aug | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-08-05 16:18 | 2022-08-05 19:21 | 150 | 3:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080500226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-08-05 | 27450 | keep | 0 | Aug | 2022 | 0.018696 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-08-05 16:29 | 2022-08-05 17:24 | 25 | 0:55 | P | DESGANCHE | 1 X 65 EN C/L | R22080500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-08-05 | 1375 | keep | 0 | Aug | 2022 | 0.00093651 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-05 16:29 | 2022-08-05 16:30 | 2635 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C22080500091 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 2635 | keep | 0 | Aug | 2022 | 0.0017947 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-05 16:30 | 2022-08-05 17:36 | 90 | 1:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22080500085 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-08-05 | 5940 | keep | 0 | Aug | 2022 | 0.0040457 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-08-05 16:49 | 2022-08-05 18:55 | 10 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22080500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-08-05 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-05 16:49 | 2022-08-05 18:30 | 1 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO TOMA ABIERTA HACIA CLIENTE | C22080500102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2022-08-05 | 101 | keep | 0 | Aug | 2022 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-05 17:20 | 2022-08-05 20:57 | 20 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M22080500260 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2022-08-05 | 4340 | keep | 0 | Aug | 2022 | 0.002956 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-05 17:34 | 2022-08-05 20:47 | 15 | 3:13 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B22080500091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-08-05 | 2895 | keep | 0 | Aug | 2022 | 0.0019718 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-05 17:42 | 2022-08-05 23:05 | 100 | 5:23 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080500275 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 323 | 2022-08-05 | 32300 | keep | 0 | Aug | 2022 | 0.021999 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-05 17:50 | 2022-08-06 09:00 | 25 | 15:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22080500281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 910 | 2022-08-05 | 22750 | keep | 0 | Aug | 2022 | 0.015495 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-05 18:20 | 2022-08-05 22:44 | 40 | 4:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BEJUCO Y RAMA SOBRE LINEAS | M22080500292 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-08-05 | 10560 | keep | 0 | Aug | 2022 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-05 18:23 | 2022-08-05 19:19 | 293 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P22080500089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-08-05 | 16408 | keep | 0 | Aug | 2022 | 0.011175 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
PONCE | 2022-08-05 18:23 | 2022-08-05 19:19 | 253 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P22080500089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-08-05 | 14168 | keep | 0 | Aug | 2022 | 0.0096498 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
PONCE | 2022-08-05 18:23 | 2022-08-05 19:19 | 900 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P22080500089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-08-05 | 50400 | keep | 0 | Aug | 2022 | 0.034327 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
PONCE | 2022-08-05 18:23 | 2022-08-05 19:19 | 1615 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P22080500089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-08-05 | 90440 | keep | 0 | Aug | 2022 | 0.061598 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
PONCE | 2022-08-05 18:23 | 2022-08-05 19:19 | 3 | 0:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7900 | P22080500089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 56 | 2022-08-05 | 168 | keep | 0 | Aug | 2022 | 0.00011442 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-08-05 19:16 | 2022-08-05 21:17 | 80 | 2:01 | P | NO SE REPORTO CAUSA | DESGANCHE Y 1 X 80 EN RISER | R22080500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-08-05 | 9680 | keep | 0 | Aug | 2022 | 0.006593 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-05 19:16 | 2022-08-05 20:35 | 6 | 1:19 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | R22080500062 | New_Event | Animals | Include | Include | Wildlife | 79 | 2022-08-05 | 474 | keep | 0 | Aug | 2022 | 0.00032284 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-05 19:19 | 2022-08-06 11:49 | 12 | 16:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CAJA Y SE CERRO PUENTE PRIMARIO | B22080500094 | New_Event | Primary Wire Break | Include | Include | Equipment | 990 | 2022-08-05 | 11880 | keep | 0 | Aug | 2022 | 0.0080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-05 19:24 | 2022-08-06 01:27 | 70 | 6:03 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080500310 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 363 | 2022-08-05 | 25410 | keep | 0 | Aug | 2022 | 0.017307 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-08-05 19:42 | 2022-08-05 19:44 | 1339 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22080500362 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-05 | 2678 | keep | 0 | Aug | 2022 | 0.001824 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2022-08-05 19:42 | 2022-08-05 19:44 | 470 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22080500362 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-05 | 940 | keep | 0 | Aug | 2022 | 0.00064023 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2022-08-05 19:42 | 2022-08-05 19:44 | 2483 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22080500362 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-05 | 4966 | keep | 0 | Aug | 2022 | 0.0033823 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2022-08-05 19:42 | 2022-08-05 19:44 | 2190 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22080500362 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-05 | 4380 | keep | 0 | Aug | 2022 | 0.0029832 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2022-08-05 19:42 | 2022-08-05 19:44 | 3006 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22080500363 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-05 | 6012 | keep | 0 | Aug | 2022 | 0.0040947 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2022-08-05 19:42 | 2022-08-05 19:44 | 179 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M22080500363 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-05 | 358 | keep | 0 | Aug | 2022 | 0.00024383 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-08-05 19:42 | 2022-08-05 22:52 | 1097 | 3:10 | T | LINEA DE TRANSMISION 115KV | SE RETIRO OVERHEAD DE LINEA 37100 SOBRE LINEAS PRIMARIAS SE CERRO INETERRUPTOR | M22080500319 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-08-05 | 208430 | keep | 0 | Aug | 2022 | 0.14196 | 0.00074716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1097
AGUADILLA | 2022-08-05 19:46 | 2022-08-06 05:30 | 10 | 9:44 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22080500324 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 584 | 2022-08-05 | 5840 | keep | 0 | Aug | 2022 | 0.0039776 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-05 19:55 | 2022-08-05 21:58 | 150 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES | M22080500328 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2022-08-05 | 18450 | keep | 0 | Aug | 2022 | 0.012566 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-05 20:52 | 2022-08-05 20:53 | 4176 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22080500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-05 | 4176 | keep | 0 | Aug | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-08-05 20:53 | 2022-08-05 22:11 | 60 | 1:18 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B22080500104 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-08-05 | 4680 | keep | 0 | Aug | 2022 | 0.0031875 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-05 21:04 | 2022-08-06 14:32 | 2 | 17:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REEMPLAZO SECUNDARIA AVERIADA Y CERRO TRANSFORMADOR | M22080500356 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1048 | 2022-08-05 | 2096 | keep | 0 | Aug | 2022 | 0.0014276 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-05 21:12 | 2022-08-05 22:31 | 367 | 1:19 | P | DESGANCHE | 1X100 EN C/L | S22080500159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-08-05 | 28993 | keep | 0 | Aug | 2022 | 0.019747 | 0.00024996 | Sustained | FALSE | FALSE | Not_TMED_Event | 367
ARECIBO | 2022-08-05 21:29 | 2022-08-06 18:55 | 10 | 21:26 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO Y SE ENERGIZO EL AEREO PROVISIONAL | A22080500229 | New_Event | UG Cable Fault | Include | Include | Equipment | 1286 | 2022-08-05 | 12860 | keep | 0 | Aug | 2022 | 0.0087589 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-05 22:51 | 2022-08-06 20:35 | 21 | 21:44 | P | ARBOL SOBRE LINEA | 1 X 40 EN C/L RETIRO ARBOL DE LA LINEA | C22080500126 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1304 | 2022-08-05 | 27384 | keep | 0 | Aug | 2022 | 0.018651 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
PONCE | 2022-08-05 22:56 | 2022-08-06 09:51 | 8 | 10:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P22080500127 | New_Event | Primary Wire Break | Include | Include | Equipment | 655 | 2022-08-05 | 5240 | keep | 0 | Aug | 2022 | 0.0035689 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-05 23:08 | 2022-08-06 12:55 | 12 | 13:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22080500109 | New_Event | Secondary Wire Break | Include | Include | Equipment | 827 | 2022-08-05 | 9924 | keep | 0 | Aug | 2022 | 0.0067592 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-05 23:09 | 2022-08-06 08:58 | 150 | 9:49 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080500378 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 589 | 2022-08-05 | 88350 | keep | 0 | Aug | 2022 | 0.060175 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-05 23:11 | 2022-08-06 02:16 | 275 | 3:05 | P | DESGANCHE | 1X100 EN C/L | S22080500176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-08-05 | 50875 | keep | 0 | Aug | 2022 | 0.034651 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
GUAYAMA | 2022-08-05 23:32 | 2022-08-06 12:30 | 6 | 12:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTES SECUNDARIOS EN XMR Y SE REPARO SECUNDARIA EN VARIOS PUNTOS | P22080500129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 778 | 2022-08-05 | 4668 | keep | 0 | Aug | 2022 | 0.0031794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-05 23:42 | 2022-08-05 23:45 | 5191 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22080500110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-05 | 15573 | keep | 0 | Aug | 2022 | 0.010607 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
AGUADILLA | 2022-08-05 23:55 | 2022-08-06 02:05 | 70 | 2:10 | P | SOBRECARGA | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SOBRE CARGA | M22080500385 | New_Event | Trip Due To Overload | Include | Include | Other | 130 | 2022-08-05 | 9100 | keep | 0 | Aug | 2022 | 0.006198 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-08-06 00:19 | 2022-08-06 09:00 | 80 | 8:41 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080500240 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 521 | 2022-08-06 | 41680 | keep | 0 | Aug | 2022 | 0.028388 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-08-06 00:47 | 2022-08-08 08:57 | 10 | 56:10 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T12 AL T11 | R22080600026 | New_Event | UG Cable Fault | Include | Include | Equipment | 3370 | 2022-08-06 | 33700 | keep | 0 | Aug | 2022 | 0.022953 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-06 01:17 | 2022-08-06 03:42 | 193 | 2:25 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B22080600113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-08-06 | 27985 | keep | 0 | Aug | 2022 | 0.01906 | 0.00013145 | Sustained | FALSE | FALSE | Not_TMED_Event | 193
CAGUAS | 2022-08-06 02:39 | 2022-08-06 02:41 | 125 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR SCADA | C22080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-06 | 250 | keep | 0 | Aug | 2022 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2022-08-06 02:50 | 2022-08-06 02:51 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 4533 | keep | 0 | Aug | 2022 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
BAYAMON | 2022-08-06 03:04 | 2022-08-06 11:15 | 30 | 8:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | B22080500115 | New_Event | Cutout Failure | Include | Include | Equipment | 491 | 2022-08-06 | 14730 | keep | 0 | Aug | 2022 | 0.010033 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-06 04:17 | 2022-08-06 11:05 | 100 | 6:48 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M22080500401 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 408 | 2022-08-06 | 40800 | keep | 0 | Aug | 2022 | 0.027789 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-06 04:27 | 2022-08-06 07:24 | 125 | 2:57 | P | ANIMAL | 1 X 80 Y 1 X 65 EN C/L AVE | B22080500120 | New_Event | Animals | Include | Include | Wildlife | 177 | 2022-08-06 | 22125 | keep | 0 | Aug | 2022 | 0.015069 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2022-08-06 04:48 | 2022-08-06 11:17 | 20 | 6:29 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22080600011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 389 | 2022-08-06 | 7780 | keep | 0 | Aug | 2022 | 0.0052989 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-06 04:53 | 2022-08-07 13:01 | 12 | 32:08 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR EN TRES TRANSFORMADORES UN FUSIBLE EN CADA UNO DESCARGAS ELECTRICAS | A22080600078 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1928 | 2022-08-06 | 23136 | keep | 0 | Aug | 2022 | 0.015758 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-06 05:09 | 2022-08-06 11:09 | 75 | 6:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | C22080600002 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2022-08-06 | 27000 | keep | 0 | Aug | 2022 | 0.01839 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-08-06 05:10 | 2022-08-07 09:09 | 120 | 27:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22080600081 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1679 | 2022-08-06 | 201480 | keep | 0 | Aug | 2022 | 0.13723 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-08-06 05:23 | 2022-08-06 07:07 | 40 | 1:44 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C22080600006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2022-08-06 | 4160 | keep | 0 | Aug | 2022 | 0.0028334 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-06 05:56 | 2022-08-06 09:40 | 66 | 3:44 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 Y 1 X 30 EN SU'S SE REEMPLAZO PIN HOLE QUEMADO EN TRANSFORMADOR PM | R22080600002 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 224 | 2022-08-06 | 14784 | keep | 0 | Aug | 2022 | 0.010069 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
ARECIBO | 2022-08-06 06:17 | 2022-08-07 16:48 | 15 | 34:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080600094 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2071 | 2022-08-06 | 31065 | keep | 0 | Aug | 2022 | 0.021158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-06 06:25 | 2022-08-06 13:15 | 497 | 6:50 | P | CONDUCTOR ROTO O ABIERTO | ABRIO C/L PARA LEVANTAR NEUTRAL PRIMARIO Y LINEA SECUNDARIA | C22080600007 | New_Event | Primary Wire Break | Include | Include | Equipment | 410 | 2022-08-06 | 203770 | keep | 0 | Aug | 2022 | 0.13879 | 0.0003385 | Sustained | FALSE | FALSE | Not_TMED_Event | 497
SAN JUAN | 2022-08-06 06:26 | 2022-08-06 08:23 | 150 | 1:57 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU-12 Y SE REPORTA AVERIA SOTERRADA DEL T-50 AL T-51 | S22080500183 | New_Event | UG Cable Fault | Include | Include | Equipment | 117 | 2022-08-06 | 17550 | keep | 0 | Aug | 2022 | 0.011953 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-08-06 06:28 | 2022-08-06 09:10 | 30 | 2:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22080500544 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-08-06 | 4860 | keep | 0 | Aug | 2022 | 0.0033101 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-08-06 06:34 | 2022-08-06 06:35 | 1173 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 1173 | keep | 0 | Aug | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
VEGA BAJA | 2022-08-06 06:35 | 2022-08-06 06:36 | 2107 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22080500247 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 2107 | keep | 0 | Aug | 2022 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2022-08-06 06:36 | 2022-08-06 08:17 | 20 | 1:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22080500252 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-08-06 | 2020 | keep | 0 | Aug | 2022 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-06 06:43 | 2022-08-06 08:50 | 40 | 2:07 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R22080600005 | New_Event | Animals | Include | Include | Wildlife | 127 | 2022-08-06 | 5080 | keep | 0 | Aug | 2022 | 0.00346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-06 07:14 | 2022-08-06 07:15 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22080500250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 2697 | keep | 0 | Aug | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
AGUADILLA | 2022-08-06 07:17 | 2022-08-07 13:16 | 100 | 29:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A22080600100 | New_Event | Primary Wire Break | Include | Include | Equipment | 1799 | 2022-08-06 | 179900 | keep | 0 | Aug | 2022 | 0.12253 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-08-06 07:25 | 2022-08-07 10:16 | 185 | 26:51 | P | MAL TIEMPO/RAYOS | 1 X 100 1 X 50 Y 1 X 40 EN C/LS RAYO | C22080600011 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1611 | 2022-08-06 | 298035 | keep | 0 | Aug | 2022 | 0.20299 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
VEGA BAJA | 2022-08-06 07:28 | 2022-08-06 10:00 | 45 | 2:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22080500128 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2022-08-06 | 6840 | keep | 0 | Aug | 2022 | 0.0046587 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-08-06 07:29 | 2022-08-06 07:30 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 2379 | keep | 0 | Aug | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
YAUCO | 2022-08-06 07:33 | 2022-08-06 07:34 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 179 | keep | 0 | Aug | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2022-08-06 07:36 | 2022-08-06 13:43 | 17 | 6:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B22080600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 367 | 2022-08-06 | 6239 | keep | 0 | Aug | 2022 | 0.0042494 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2022-08-06 07:36 | 2022-08-07 15:38 | 10 | 32:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22080600105 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1922 | 2022-08-06 | 19220 | keep | 0 | Aug | 2022 | 0.013091 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-08-06 07:41 | 2022-08-06 09:25 | 10 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | M22080600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-08-06 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-08-06 08:01 | 2022-08-06 08:02 | 3114 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 3114 | keep | 0 | Aug | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
CAGUAS | 2022-08-06 08:04 | 2022-08-06 10:06 | 65 | 2:02 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/L DESGANCHO | C22080600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-08-06 | 7930 | keep | 0 | Aug | 2022 | 0.0054011 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-08-06 08:08 | 2022-08-06 10:05 | 30 | 1:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-08-06 | 3510 | keep | 0 | Aug | 2022 | 0.0023906 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-06 08:09 | 2022-08-06 08:10 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 2605 | keep | 0 | Aug | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
SAN JUAN | 2022-08-06 08:23 | 2022-08-07 20:25 | 10 | 36:02 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A T 50 | S22080500183 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 2162 | 2022-08-06 | 21620 | keep | 0 | Aug | 2022 | 0.014725 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-06 08:40 | 2022-08-07 10:35 | 50 | 25:55 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080600228 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1555 | 2022-08-06 | 77750 | keep | 0 | Aug | 2022 | 0.052955 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-06 08:46 | 2022-08-06 10:40 | 6 | 1:54 | P | CONDUCTOR ROTO O ABIERTO | REPARO BAJANTE DE CAJA A XMR NO FUNDIO | C22080600023 | New_Event | Primary Wire Break | Include | Include | Equipment | 114 | 2022-08-06 | 684 | keep | 0 | Aug | 2022 | 0.00046587 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-06 08:56 | 2022-08-07 12:00 | 80 | 27:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22080600163 | New_Event | Cutout Failure | Include | Include | Equipment | 1624 | 2022-08-06 | 129920 | keep | 0 | Aug | 2022 | 0.088488 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-06 09:09 | 2022-08-06 13:22 | 1 | 4:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22080600013 | New_Event | Cutout Failure | Include | Include | Equipment | 253 | 2022-08-06 | 253 | keep | 0 | Aug | 2022 | 0.00017232 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-06 09:47 | 2022-08-06 13:30 | 75 | 3:43 | P | ARBOL SOBRE LINEA | 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22080600009 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 223 | 2022-08-06 | 16725 | keep | 0 | Aug | 2022 | 0.011391 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2022-08-06 09:53 | 2022-08-06 09:54 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR SE ESCRIBIO EVENTO EN 0 YA QUE OMS NO CREO EVENTO AL INTENTAR CREARLO | M22080600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 179 | keep | 0 | Aug | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2022-08-06 10:05 | 2022-08-06 10:06 | 4664 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 4664 | keep | 0 | Aug | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2022-08-06 10:12 | 2022-08-06 16:42 | 135 | 6:30 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | M22080600048 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 390 | 2022-08-06 | 52650 | keep | 0 | Aug | 2022 | 0.03586 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2022-08-06 10:14 | 2022-08-06 10:15 | 4664 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 4664 | keep | 0 | Aug | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
YAUCO | 2022-08-06 10:16 | 2022-08-06 10:17 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 179 | keep | 0 | Aug | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2022-08-06 10:22 | 2022-08-06 10:23 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080600000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 179 | keep | 0 | Aug | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2022-08-06 10:25 | 2022-08-06 10:26 | 179 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL INTERRUPTOR | M22080600000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-06 | 179 | keep | 0 | Aug | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2022-08-06 10:26 | 2022-08-06 14:39 | 12 | 4:13 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE PRIMARIO | M22080600059 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 253 | 2022-08-06 | 3036 | keep | 0 | Aug | 2022 | 0.0020678 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-08-06 10:29 | 2022-08-06 11:49 | 12 | 1:20 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | A22080600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2022-08-06 | 960 | keep | 0 | Aug | 2022 | 0.00065385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-06 10:34 | 2022-08-06 10:35 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 4641 | keep | 0 | Aug | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
UTUADO | 2022-08-06 10:36 | 2022-08-06 13:30 | 20 | 2:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA RAMA CRUZO FASE A TIERRA | A22080600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-08-06 | 3480 | keep | 0 | Aug | 2022 | 0.0023702 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-08-06 11:09 | 2022-08-06 12:30 | 40 | 1:21 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22080600031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-08-06 | 3240 | keep | 0 | Aug | 2022 | 0.0022067 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-06 11:14 | 2022-08-06 17:29 | 13 | 6:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PM-T-4 SE REPARO PEDESTAL SECUNDARIO | S22080600012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 375 | 2022-08-06 | 4875 | keep | 0 | Aug | 2022 | 0.0033203 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2022-08-06 11:21 | 2022-08-06 13:48 | 25 | 2:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22080600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-08-06 | 3675 | keep | 0 | Aug | 2022 | 0.002503 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-06 11:30 | 2022-08-06 11:58 | 6 | 0:28 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR SE REPARO SECUNDARIA | B22080500088 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 28 | 2022-08-06 | 168 | keep | 0 | Aug | 2022 | 0.00011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-08-06 11:33 | 2022-08-06 13:20 | 200 | 1:47 | P | CAUSAS EXTERNAS | 2 X 65 EN CORTE DE LINEA CAMION IMPACTO POSTE Y SE CRUZARON LINEAS MOMENTANEAMENTE | A22080600024 | New_Event | Damage From Public | Include | Include | Public | 107 | 2022-08-06 | 21400 | keep | 0 | Aug | 2022 | 0.014575 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-06 11:45 | 2022-08-06 15:00 | 391 | 3:15 | P | DESGANCHE | 1 X 100 EN C/L | B22080600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-08-06 | 76245 | keep | 0 | Aug | 2022 | 0.05193 | 0.00026631 | Sustained | FALSE | FALSE | Not_TMED_Event | 391
BAYAMON | 2022-08-06 11:58 | 2022-08-06 14:03 | 98 | 2:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 2 X 80 EN C/L | S22080600023 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2022-08-06 | 12250 | keep | 0 | Aug | 2022 | 0.0083434 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
BAYAMON | 2022-08-06 12:10 | 2022-08-06 13:18 | 6 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22080600040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2022-08-06 | 408 | keep | 0 | Aug | 2022 | 0.00027789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-08-06 12:12 | 2022-08-06 15:52 | 4 | 3:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRAS DE PEDESTAL | C22080600056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 220 | 2022-08-06 | 880 | keep | 0 | Aug | 2022 | 0.00059936 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-08-06 12:23 | 2022-08-06 14:58 | 1 | 2:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA EN TRANSFORMADOR PARA FIJAR BAJANTE SECUNDARIO | P22080600040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 155 | 2022-08-06 | 155 | keep | 0 | Aug | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-06 12:33 | 2022-08-06 14:17 | 35 | 1:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22080600074 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 104 | 2022-08-06 | 3640 | keep | 0 | Aug | 2022 | 0.0024792 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-08-06 12:44 | 2022-08-06 17:08 | 1 | 4:24 | P | DESGANCHE | 1 X 80 EN C/L | C22080600059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2022-08-06 | 264 | keep | 0 | Aug | 2022 | 0.00017981 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-06 12:44 | 2022-08-06 16:45 | 70 | 4:01 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L PERSONAS DESGANCHANDO | C22080600060 | New_Event | Damage From Public | Include | Include | Public | 241 | 2022-08-06 | 16870 | keep | 0 | Aug | 2022 | 0.01149 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2022-08-06 12:53 | 2022-08-06 12:54 | 449 | 0:01 | T | ANIMAL | RECIERRE | P22080600043 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-06 | 449 | keep | 0 | Aug | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
GUAYAMA | 2022-08-06 12:54 | 2022-08-06 14:25 | 20 | 1:31 | P | ANIMAL | 1 X 50 EN C/L CRUCE DE FASE PRIMARIA POR AVE | P22080600046 | 1st_after_momentary | Animals | Include | Include | Wildlife | 91 | 2022-08-06 | 1820 | keep | 0 | Aug | 2022 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-06 13:29 | 2022-08-06 13:50 | 10 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE Y TOMA | C22080600064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2022-08-06 | 210 | keep | 0 | Aug | 2022 | 0.00014303 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-06 13:48 | 2022-08-06 13:49 | 3041 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DEL INTERRUPTOR | M22080600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-06 | 3041 | keep | 0 | Aug | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-08-06 13:49 | 2022-08-06 16:08 | 10 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIAS | M22080600089 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2022-08-06 | 1390 | keep | 0 | Aug | 2022 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-06 13:54 | 2022-08-06 18:08 | 30 | 4:14 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22080600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-08-06 | 7620 | keep | 0 | Aug | 2022 | 0.0051899 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-06 13:55 | 2022-08-06 17:25 | 200 | 3:30 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | S22080600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2022-08-06 | 42000 | keep | 0 | Aug | 2022 | 0.028606 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-08-06 14:06 | 2022-08-06 17:00 | 120 | 2:54 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L NO CAUSA | C22080600073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-06 | 20880 | keep | 0 | Aug | 2022 | 0.014221 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-08-06 14:14 | 2022-08-07 09:29 | 18 | 19:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO CAJA AVERIADA | C22080600074 | New_Event | Cutout Failure | Include | Include | Equipment | 1155 | 2022-08-06 | 20790 | keep | 0 | Aug | 2022 | 0.01416 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2022-08-06 14:14 | 2022-08-06 14:15 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080600076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 1017 | keep | 0 | Aug | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CAGUAS | 2022-08-06 14:15 | 2022-08-06 17:02 | 55 | 2:47 | P | TRANSFORMADOR AVERIADO | 1 X 65 EN C/L XMR AVERIADO | C22080600074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 167 | 2022-08-06 | 9185 | keep | 0 | Aug | 2022 | 0.0062559 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2022-08-06 14:20 | 2022-08-06 18:44 | 98 | 4:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22080600072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 264 | 2022-08-06 | 25872 | keep | 0 | Aug | 2022 | 0.017621 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
BAYAMON | 2022-08-06 14:24 | 2022-08-06 15:24 | 8 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | B22080600008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-08-06 | 480 | keep | 0 | Aug | 2022 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-06 14:49 | 2022-08-06 19:06 | 50 | 4:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES LLUVIAS | C22080600084 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 257 | 2022-08-06 | 12850 | keep | 0 | Aug | 2022 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-06 14:49 | 2022-08-06 17:50 | 400 | 3:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO LLUVIAS | M22080600092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 181 | 2022-08-06 | 72400 | keep | 0 | Aug | 2022 | 0.049311 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
HUMACAO | 2022-08-06 14:59 | 2022-08-06 16:29 | 10 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22080600019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2022-08-06 | 900 | keep | 0 | Aug | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-06 15:02 | 2022-08-06 17:54 | 10 | 2:52 | P | CONDUCTOR ROTO O ABIERTO | SE AJUSTARON CONEXIONES EN LA PRIMARIA | S22080600077 | New_Event | Primary Wire Break | Include | Include | Equipment | 172 | 2022-08-06 | 1720 | keep | 0 | Aug | 2022 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-08-06 15:04 | 2022-08-06 16:57 | 8 | 1:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | P22080600039 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2022-08-06 | 904 | keep | 0 | Aug | 2022 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-06 15:05 | 2022-08-06 15:56 | 7 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA EN TRANSFORMADOR PARA FIJAR BAJANTE SECUNDARIO | P22080600049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2022-08-06 | 357 | keep | 0 | Aug | 2022 | 0.00024315 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-06 15:25 | 2022-08-06 15:54 | 18 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22080600049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2022-08-06 | 522 | keep | 0 | Aug | 2022 | 0.00035553 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-08-06 15:42 | 2022-08-06 19:12 | 124 | 3:30 | P | PROBLEMA DEL CLIENTE | 2X50 EN RISER Y SE ELIMINO PARARRAYOS PRIVADO EN SUBESTACION DEL CONDOMINIO | S22060600080 | New_Event | Customer-Related Interruption | Include | Include | Public | 210 | 2022-08-06 | 26040 | keep | 0 | Aug | 2022 | 0.017736 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
AGUADILLA | 2022-08-06 16:08 | 2022-08-06 18:00 | 40 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA POR LINEA SAFADA DE AISLADOR EVENTO SALIO AREA DE ARECIBO | A22080600032 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2022-08-06 | 4480 | keep | 0 | Aug | 2022 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-06 16:10 | 2022-08-06 16:48 | 3114 | 0:38 | T | DESGANCHE | DISPARO INTERRUPTOR SE SECCIONALIZA AVERIA ABRIENDO MACHETES FRENTE A URB MADRIGAL | P22080600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2022-08-06 | 118332 | keep | 0 | Aug | 2022 | 0.080595 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
SAN JUAN | 2022-08-06 16:17 | 2022-08-06 18:32 | 6 | 2:15 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDAIO 1 X 25 EN XMR | S22080600085 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 135 | 2022-08-06 | 810 | keep | 0 | Aug | 2022 | 0.00055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-06 16:37 | 2022-08-06 18:14 | 45 | 1:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE ABRIO PUENTES PARA AISLAR LINEAS CRUZADAS POR RAMAS | M22080600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-08-06 | 4365 | keep | 0 | Aug | 2022 | 0.002973 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2022-08-06 16:48 | 2022-08-06 17:27 | 2086 | 0:39 | P | DESGANCHE | SE SECCIONALIZA AVERIA ABRIENDO EN SU-1 AVE PONCE DE LEON INT PR-123 Y SE CIERRA MACHETES EN URB EL MADRIGAL | P22080600063 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 39 | 2022-08-06 | 81354 | keep | 0 | Aug | 2022 | 0.05541 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-06 16:51 | 2022-08-06 21:21 | 30 | 4:30 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22080600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-08-06 | 8100 | keep | 0 | Aug | 2022 | 0.0055169 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-06 17:13 | 2022-08-07 09:28 | 40 | 16:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22080600111 | New_Event | Cutout Failure | Include | Include | Equipment | 975 | 2022-08-06 | 39000 | keep | 0 | Aug | 2022 | 0.026563 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-06 17:27 | 2022-08-06 17:55 | 1680 | 0:28 | P | DESGANCHE | SE ABRE EN CALLE MARGINAL NORTE BO MAGUEYES Y SE CIERRA EN SU-1 | P22080600067 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-08-06 | 47040 | keep | 0 | Aug | 2022 | 0.032039 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-06 17:55 | 2022-08-06 18:15 | 623 | 0:20 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEA Y SE LIGO LINEA SAFADA EN AISLADOR POR RAMA Y SE CERRO MACHETES | P22080600072 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-08-06 | 12460 | keep | 0 | Aug | 2022 | 0.0084864 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-06 18:05 | 2022-08-06 18:42 | 2696 | 0:37 | T | ANIMAL | DISPARO DE INTERRUPTOR SE TERMINA DE ABRIR CORTE DE LINEA EN CALLE VILLA Y SE COLOCA INTERRUPTOR EN SERVICIO | P22080600069 | New_Event | Animals | Include | Include | Wildlife | 37 | 2022-08-06 | 99752 | keep | 0 | Aug | 2022 | 0.067941 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2022-08-06 18:08 | 2022-08-06 20:16 | 96 | 2:08 | P | DESGANCHE | 2 X 100 EN C/L | B22080600053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-08-06 | 12288 | keep | 0 | Aug | 2022 | 0.0083693 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
MAYAGÃœEZ | 2022-08-06 18:13 | 2022-08-07 11:40 | 100 | 17:27 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080600121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1047 | 2022-08-06 | 104700 | keep | 0 | Aug | 2022 | 0.071311 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-06 18:14 | 2022-08-07 11:44 | 2 | 17:30 | P | DESGANCHE | PUENTES ABIERTOS PARA AISLAR LINEAS CRUZADAS POR RAMAS | M22080600104 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1050 | 2022-08-06 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-06 18:30 | 2022-08-06 19:38 | 150 | 1:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 80 EN C/L | C22080600117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-08-06 | 10200 | keep | 0 | Aug | 2022 | 0.0069472 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-08-06 18:42 | 2022-08-06 18:53 | 623 | 0:11 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR IGUANA | P22080600079 | Partial_restoration | Animals | Include | Include | Wildlife | 11 | 2022-08-06 | 6853 | keep | 0 | Aug | 2022 | 0.0046675 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-06 19:00 | 2022-08-08 06:54 | 5 | 35:54 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYOS | C22080600121 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2154 | 2022-08-06 | 10770 | keep | 0 | Aug | 2022 | 0.0073354 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-06 19:15 | 2022-08-07 12:23 | 279 | 17:08 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | B22080600090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1028 | 2022-08-06 | 286812 | keep | 0 | Aug | 2022 | 0.19535 | 0.00019003 | Sustained | FALSE | FALSE | Not_TMED_Event | 279
BARRANQUITAS | 2022-08-06 19:16 | 2022-08-06 19:17 | 1604 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080600124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-06 | 1604 | keep | 0 | Aug | 2022 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
SAN JUAN | 2022-08-06 19:39 | 2022-08-06 22:11 | 40 | 2:32 | P | NO SE REPORTO CAUSA | 1X25 DEL SU-1 @ T-24 | S22080600095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-08-06 | 6080 | keep | 0 | Aug | 2022 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-06 19:40 | 2022-08-06 20:57 | 20 | 1:17 | P | SECUNDARIA/DESGANCHE | 1X25 EN XMR SE REALIZO DESGANCHE SECUNDARIO | S22080600096 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 77 | 2022-08-06 | 1540 | keep | 0 | Aug | 2022 | 0.0010489 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-06 19:44 | 2022-08-07 18:08 | 7 | 22:24 | P | CAUSAS EXTERNAS | REMPLAZO DE T-47 IMPACTADO POR VEHICULO 100KVA POR 75KVA | B22080600111 | New_Event | Damage From Public | Include | Include | Public | 1344 | 2022-08-06 | 9408 | keep | 0 | Aug | 2022 | 0.0064077 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-06 20:03 | 2022-08-07 08:30 | 2 | 12:27 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080600145 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 747 | 2022-08-06 | 1494 | keep | 0 | Aug | 2022 | 0.0010176 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-08-06 21:26 | 2022-08-06 23:06 | 70 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22080600062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2022-08-06 | 7000 | keep | 0 | Aug | 2022 | 0.0047677 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-08-06 22:25 | 2022-08-07 00:20 | 120 | 1:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | A22080600064 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2022-08-06 | 13800 | keep | 0 | Aug | 2022 | 0.0093991 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-08-06 22:53 | 2022-08-07 19:13 | 7 | 20:20 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 40 EN CORTE DE LINEA | B22080600137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1220 | 2022-08-06 | 8540 | keep | 0 | Aug | 2022 | 0.0058166 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-08-06 23:04 | 2022-08-06 23:05 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C22080600139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-06 | 476 | keep | 0 | Aug | 2022 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-08-06 23:04 | 2022-08-06 23:05 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C22080600139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-06 | 1655 | keep | 0 | Aug | 2022 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-08-06 23:04 | 2022-08-06 23:05 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C22080600139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-06 | 361 | keep | 0 | Aug | 2022 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-08-06 23:04 | 2022-08-06 23:05 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C22080600139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-06 | 2842 | keep | 0 | Aug | 2022 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-08-06 23:04 | 2022-08-06 23:05 | 1702 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C22080600140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-06 | 1702 | keep | 0 | Aug | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-08-06 23:04 | 2022-08-06 23:05 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C22080600140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-06 | 918 | keep | 0 | Aug | 2022 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2022-08-06 23:04 | 2022-08-06 23:05 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAX A JUNCOS | C22080600141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-06 | 1725 | keep | 0 | Aug | 2022 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
SAN JUAN | 2022-08-06 23:32 | 2022-08-07 18:50 | 8 | 19:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR SECUNDARIA Y TOMAS RESIDENCIALES | S22080600111 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1158 | 2022-08-06 | 9264 | keep | 0 | Aug | 2022 | 0.0063097 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-06 23:33 | 2022-08-07 03:50 | 150 | 4:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080600196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-08-06 | 38550 | keep | 0 | Aug | 2022 | 0.026256 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2022-08-06 23:37 | 2022-08-07 09:14 | 80 | 9:37 | P | ANIMAL | 1 X 80 Y 1 X 100 EN CORTE DE LINEA CULEBRA CRUZO LINEAS | A22080600072 | New_Event | Animals | Include | Include | Wildlife | 577 | 2022-08-06 | 46160 | keep | 0 | Aug | 2022 | 0.031439 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-07 00:07 | 2022-08-07 15:23 | 52 | 15:16 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE REALIZO DESGANCHE 1 X 30 EN C/L | B22080600143 | New_Event | Primary Wire Break | Include | Include | Equipment | 916 | 2022-08-07 | 47632 | keep | 0 | Aug | 2022 | 0.032442 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
VEGA BAJA | 2022-08-07 01:08 | 2022-08-07 01:09 | 215 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | SE CERRO POR CONTROL LLUVIAS | B22080700003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-07 | 215 | keep | 0 | Aug | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-08-07 01:09 | 2022-08-07 07:15 | 48 | 6:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 C/L MAL TIEMPO RAYOS | B22080700004 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 366 | 2022-08-07 | 17568 | keep | 0 | Aug | 2022 | 0.011965 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2022-08-07 02:25 | 2022-08-07 02:27 | 1300 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22080700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-07 | 2600 | keep | 0 | Aug | 2022 | 0.0017708 | 0.00088542 | Momentary | FALSE | FALSE | Not_TMED_Event | 1300
CANOVANAS | 2022-08-07 02:37 | 2022-08-08 08:08 | 9 | 29:31 | P | NO SE REPORTO CAUSA | 1 X15 EN XMR | R22080700041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1771 | 2022-08-07 | 15939 | keep | 0 | Aug | 2022 | 0.010856 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-08-07 03:43 | 2022-08-07 04:03 | 1000 | 0:20 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL 80% DE SU CARGA TRANSFERIDA AL 1424-08 | S22080600114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-08-07 | 20000 | keep | 0 | Aug | 2022 | 0.013622 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-08-07 03:43 | 2022-08-07 04:03 | 9 | 0:20 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA 80% DEL 1348-06 | S22080600114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-08-07 | 180 | keep | 0 | Aug | 2022 | 0.0001226 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-08-07 04:01 | 2022-08-08 15:07 | 5 | 35:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTE VIENTOS | A22080700405 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2106 | 2022-08-07 | 10530 | keep | 0 | Aug | 2022 | 0.0071719 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-08-07 05:08 | 2022-08-07 15:30 | 50 | 10:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080700079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 622 | 2022-08-07 | 31100 | keep | 0 | Aug | 2022 | 0.021182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-07 05:29 | 2022-08-07 05:30 | 1 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22080600085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 1 | keep | 0 | Aug | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-07 05:29 | 2022-08-07 05:30 | 4607 | 0:01 | T | NO SE REPORTO CAUSA | CARGA POR 7501-01 | A22080600085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 4607 | keep | 0 | Aug | 2022 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
AGUADILLA | 2022-08-07 05:35 | 2022-08-07 05:36 | 4882 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR DESCARGAS ELECTRICAS | M22080600207 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 4882 | keep | 0 | Aug | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-08-07 05:36 | 2022-08-07 08:35 | 50 | 2:59 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080600208 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 179 | 2022-08-07 | 8950 | keep | 0 | Aug | 2022 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-07 05:48 | 2022-08-07 05:49 | 4027 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECERRO | B22080700012 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-08-07 | 4027 | keep | 0 | Aug | 2022 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2022-08-07 05:49 | 2022-08-07 08:20 | 212 | 2:31 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETESO LINEA PRIMARIA | B22080600013 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 151 | 2022-08-07 | 32012 | keep | 0 | Aug | 2022 | 0.021803 | 0.00014439 | Sustained | FALSE | FALSE | Not_TMED_Event | 212
BAYAMON | 2022-08-07 05:50 | 2022-08-07 05:51 | 4622 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 4622 | keep | 0 | Aug | 2022 | 0.003148 | 0.003148 | Momentary | FALSE | FALSE | Not_TMED_Event | 4622
ARECIBO | 2022-08-07 05:57 | 2022-08-07 19:15 | 6 | 13:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 37.5KVA | A22080700089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 798 | 2022-08-07 | 4788 | keep | 0 | Aug | 2022 | 0.0032611 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-07 06:15 | 2022-08-07 10:03 | 300 | 3:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30, 1 X 40 Y 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22080600092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 228 | 2022-08-07 | 68400 | keep | 0 | Aug | 2022 | 0.046587 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2022-08-07 06:17 | 2022-08-07 06:18 | 1718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22070600210 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 1718 | keep | 0 | Aug | 2022 | 0.0011701 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
HUMACAO | 2022-08-07 06:30 | 2022-08-07 06:31 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 824 | keep | 0 | Aug | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
FAJARDO | 2022-08-07 06:41 | 2022-08-07 12:50 | 26 | 6:09 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE PRIMARIO Y SE REMPLAZO PORTAFUSIBLE | R22080600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-08-07 | 9594 | keep | 0 | Aug | 2022 | 0.0065344 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2022-08-07 06:43 | 2022-08-07 20:07 | 643 | 13:24 | P | DESGANCHE | DESGANCHE Y 1 X 25 EN C/L | B22080700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 804 | 2022-08-07 | 516972 | keep | 0 | Aug | 2022 | 0.35211 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
ARECIBO | 2022-08-07 06:45 | 2022-08-07 10:42 | 30 | 3:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22080600097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 237 | 2022-08-07 | 7110 | keep | 0 | Aug | 2022 | 0.0048426 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-08-07 06:52 | 2022-08-07 08:34 | 40 | 1:42 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22080600149 | New_Event | Animals | Include | Include | Wildlife | 102 | 2022-08-07 | 4080 | keep | 0 | Aug | 2022 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-07 07:16 | 2022-08-07 07:17 | 3941 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | B22080700024 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-07 | 3941 | keep | 0 | Aug | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
PONCE | 2022-08-07 07:17 | 2022-08-07 07:54 | 2113 | 0:37 | T | DESGANCHE | SE RETIRO RAMA SOBRE LINEAS | P22080600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2022-08-07 | 78181 | keep | 0 | Aug | 2022 | 0.053249 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
ARECIBO | 2022-08-07 07:17 | 2022-08-07 09:28 | 12 | 2:11 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080700023 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 131 | 2022-08-07 | 1572 | keep | 0 | Aug | 2022 | 0.0010707 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-07 07:26 | 2022-08-07 09:59 | 40 | 2:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L VIENTOS | C22080700004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 153 | 2022-08-07 | 6120 | keep | 0 | Aug | 2022 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-07 07:45 | 2022-08-07 12:40 | 35 | 4:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080600216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2022-08-07 | 10325 | keep | 0 | Aug | 2022 | 0.0070323 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2022-08-07 07:47 | 2022-08-07 09:10 | 30 | 1:23 | P | ANIMAL | 2 X 65 EN C/L AVE CRUZO LINEAS | P22080600103 | New_Event | Animals | Include | Include | Wildlife | 83 | 2022-08-07 | 2490 | keep | 0 | Aug | 2022 | 0.0016959 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-07 07:49 | 2022-08-07 08:36 | 3941 | 0:47 | T | CAUSAS EXTERNAS | SE ABRIO INTERRUPTOR POR POSTE IMPACTADO A PUNTO DE CAERSE, SE SECCIONALIZO Y SE CERRO POR SCADA BY-220807-01 | B22080700024 | 1st_after_momentary | Damage From Public | Include | Include | Public | 47 | 2022-08-07 | 185227 | keep | 0 | Aug | 2022 | 0.12616 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
CAGUAS | 2022-08-07 08:00 | 2022-08-07 10:33 | 85 | 2:33 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHO | C22080700010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-08-07 | 13005 | keep | 0 | Aug | 2022 | 0.0088576 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2022-08-07 08:00 | 2022-08-07 08:01 | 732 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080600107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 732 | keep | 0 | Aug | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
BARRANQUITAS | 2022-08-07 08:10 | 2022-08-07 17:38 | 237 | 9:28 | P | DESGANCHE | 2 X 40 Y 1 X 100 EN C/LS DESGANCHE | C22080700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 568 | 2022-08-07 | 134616 | keep | 0 | Aug | 2022 | 0.091686 | 0.00016142 | Sustained | FALSE | FALSE | Not_TMED_Event | 237
VEGA BAJA | 2022-08-07 08:14 | 2022-08-07 09:39 | 100 | 1:25 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN C/L SE REALIZO DESGANCHE | B22080700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-07 | 8500 | keep | 0 | Aug | 2022 | 0.0057893 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-07 08:19 | 2022-08-07 10:00 | 20 | 1:41 | P | ANIMAL | CRUCE POR AVE SE REMPLAZO AISLADOR Y 1 X 30 EN C/L | R22080600033 | New_Event | Animals | Include | Include | Wildlife | 101 | 2022-08-07 | 2020 | keep | 0 | Aug | 2022 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-07 08:35 | 2022-08-07 12:52 | 40 | 4:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L Y 1 X 10 EN XMR RAYO | C22080700015 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 257 | 2022-08-07 | 10280 | keep | 0 | Aug | 2022 | 0.0070017 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-07 08:36 | 2022-08-07 10:41 | 1182 | 2:05 | P | CAUSAS EXTERNAS | SE ABRIO PUENTES HACIA POSTE IMPACTADO Y SE CERRO MACHETES BY-220807-01 | B22080700025 | Partial_restoration | Damage From Public | Include | Include | Public | 125 | 2022-08-07 | 147750 | keep | 0 | Aug | 2022 | 0.10063 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-07 08:42 | 2022-08-07 08:43 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 2450 | keep | 0 | Aug | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
GUAYAMA | 2022-08-07 08:45 | 2022-08-07 10:34 | 5 | 1:49 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | P22080600117 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 109 | 2022-08-07 | 545 | keep | 0 | Aug | 2022 | 0.0003712 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-07 08:54 | 2022-08-08 01:04 | 75 | 16:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | S22080700023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 970 | 2022-08-07 | 72750 | keep | 0 | Aug | 2022 | 0.04955 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-08-07 08:56 | 2022-08-07 10:53 | 5 | 1:57 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080600235 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-08-07 | 585 | keep | 0 | Aug | 2022 | 0.00039844 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-07 08:57 | 2022-08-07 08:58 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 1746 | keep | 0 | Aug | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2022-08-07 08:57 | 2022-08-07 13:10 | 13 | 4:13 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | B22080700035 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 253 | 2022-08-07 | 3289 | keep | 0 | Aug | 2022 | 0.0022401 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-08-07 08:58 | 2022-08-08 04:17 | 200 | 19:19 | P | NO SE REPORTO CAUSA | 3 X 100 SMU-20 EN SU-3 NO CAUSA | B22080700062 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1159 | 2022-08-07 | 231800 | keep | 0 | Aug | 2022 | 0.15788 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-07 09:02 | 2022-08-07 10:24 | 60 | 1:22 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L MAL TIEMPO RAYOS | B22080700058 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 82 | 2022-08-07 | 4920 | keep | 0 | Aug | 2022 | 0.003351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-07 09:05 | 2022-08-07 09:07 | 2826 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO X CONTROL | C22080700000 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-08-07 | 5652 | keep | 0 | Aug | 2022 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BARRANQUITAS | 2022-08-07 09:07 | 2022-08-07 10:08 | 1130 | 1:01 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO CONDUCTOR EN EL SUELO | C22080700150 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 61 | 2022-08-07 | 68930 | keep | 0 | Aug | 2022 | 0.046948 | 0.00076964 | Sustained | FALSE | FALSE | Not_TMED_Event | 1130
BARRANQUITAS | 2022-08-07 09:08 | 2022-08-07 09:09 | 2859 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECIERRE | C22080700042 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2022-08-07 | 2859 | keep | 0 | Aug | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
AGUADILLA | 2022-08-07 09:08 | 2022-08-07 09:09 | 1 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 7505-05 | A22080700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 1 | keep | 0 | Aug | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-07 09:08 | 2022-08-07 09:09 | 4607 | 0:01 | T | NO SE REPORTO CAUSA | CARGA POR 7505-01 | M22080700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 4607 | keep | 0 | Aug | 2022 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
BARRANQUITAS | 2022-08-07 09:09 | 2022-08-07 19:44 | 85 | 10:35 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN C/L LINEAS ARRIADAS | C22080700081 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 635 | 2022-08-07 | 53975 | keep | 0 | Aug | 2022 | 0.036762 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2022-08-07 09:13 | 2022-08-07 09:15 | 1084 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22080700050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-07 | 2168 | keep | 0 | Aug | 2022 | 0.0014766 | 0.00073831 | Momentary | FALSE | FALSE | Not_TMED_Event | 1084
BARRANQUITAS | 2022-08-07 09:15 | 2022-08-07 09:46 | 40 | 0:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C22080700052 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 31 | 2022-08-07 | 1240 | keep | 0 | Aug | 2022 | 0.00084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-07 09:19 | 2022-08-07 10:30 | 60 | 1:11 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22080600121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-08-07 | 4260 | keep | 0 | Aug | 2022 | 0.0029015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-07 09:32 | 2022-08-07 10:20 | 44 | 0:48 | P | DESGANCHE | DESGANCHE 1 X 40 Y 1 X 50 EN C/L | R22080700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-08-07 | 2112 | keep | 0 | Aug | 2022 | 0.0014385 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BARRANQUITAS | 2022-08-07 09:32 | 2022-08-07 14:22 | 120 | 4:50 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHO | C22080700063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2022-08-07 | 34800 | keep | 0 | Aug | 2022 | 0.023702 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-08-07 09:41 | 2022-08-07 12:09 | 25 | 2:28 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR EN UN TRANSFORMADOR Y 1 X 15 EN TRANSFORMADOR EN OTRO TRANSFORMADOR. MAL TIEMPO DESCARGAS ELECTRICAS SE ENCONTRO UN TRANSFORMADOR QUEMADOS Y SE ESTA REALIZANDO GESTIONES PARA REALIZAR EL CAMBIO LO MAS PRONTO POSIBLE. | A22080700039 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 148 | 2022-08-07 | 3700 | keep | 0 | Aug | 2022 | 0.0025201 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-07 09:56 | 2022-08-07 10:00 | 1 | 0:04 | P | CAUSAS EXTERNAS | SE CERRO CAJAS DE TRANSFORMADOR LINEAS SECUNDARIAS AVERIADAS POR IMPACTO DE CAMION | M22080700010 | New_Event | Damage From Public | Include | Include | Public | 4 | 2022-08-07 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-07 09:58 | 2022-08-07 13:18 | 1 | 3:20 | P | PROBLEMA DEL CLIENTE | 1 X 65 EN C/L PROBLEMA INTERIOR | P22080600125 | New_Event | Customer-Related Interruption | Include | Include | Public | 200 | 2022-08-07 | 200 | keep | 0 | Aug | 2022 | 0.00013622 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-07 10:00 | 2022-08-08 09:43 | 150 | 23:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA FUERTES VIENTOS | M22080700083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1423 | 2022-08-07 | 213450 | keep | 0 | Aug | 2022 | 0.14538 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-08-07 10:03 | 2022-08-07 18:12 | 35 | 8:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L VIENTOS FUERTES | C22080700090 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 489 | 2022-08-07 | 17115 | keep | 0 | Aug | 2022 | 0.011657 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2022-08-07 10:04 | 2022-08-07 12:44 | 500 | 2:40 | P | DESGANCHE | SE REPARO PUENTE ABIERTO POR DESGANCHE | P22080600126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-08-07 | 80000 | keep | 0 | Aug | 2022 | 0.054488 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-08-07 10:05 | 2022-08-08 09:04 | 4 | 22:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22080700072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1379 | 2022-08-07 | 5516 | keep | 0 | Aug | 2022 | 0.0037569 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-08-07 10:06 | 2022-08-07 11:22 | 1 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C22080700093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2022-08-07 | 76 | keep | 0 | Aug | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-07 10:08 | 2022-08-07 11:07 | 2826 | 0:59 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR PARA SECCIONALIZAR CONDUCTOR VIVO EN EL SUELO | C22080700150 | New_Event | Primary Wire Break | Include | Include | Equipment | 59 | 2022-08-07 | 166734 | keep | 0 | Aug | 2022 | 0.11356 | 0.0019248 | Sustained | FALSE | FALSE | Not_TMED_Event | 2826
BARRANQUITAS | 2022-08-07 10:22 | 2022-08-07 11:05 | 7 | 0:43 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN XMR ELIMINO PARARRAYO | C22080700107 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 43 | 2022-08-07 | 301 | keep | 0 | Aug | 2022 | 0.00020501 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-08-07 10:23 | 2022-08-07 14:56 | 60 | 4:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PRIMARIA | M22080700022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2022-08-07 | 16380 | keep | 0 | Aug | 2022 | 0.011156 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-07 10:37 | 2022-08-07 10:38 | 817 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22080700116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 817 | keep | 0 | Aug | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2022-08-07 10:38 | 2022-08-07 15:36 | 20 | 4:58 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L NO CAUSA | C22080700133 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 298 | 2022-08-07 | 5960 | keep | 0 | Aug | 2022 | 0.0040593 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-07 10:41 | 2022-08-07 19:05 | 300 | 8:24 | P | CAUSAS EXTERNAS | POSTE IMPACTADO EN CARR. 167 FOREST HILLS EN EL CUAL CONDUCTOR MURIO EN EL ACTO SE REEMPLAZO POSTE PRIMARIO | B22080700025 | New_Event | Damage From Public | Include | Include | Public | 504 | 2022-08-07 | 151200 | keep | 0 | Aug | 2022 | 0.10298 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2022-08-07 10:42 | 2022-08-07 12:58 | 50 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C22080700118 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2022-08-07 | 6800 | keep | 0 | Aug | 2022 | 0.0046314 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-07 11:07 | 2022-08-07 11:35 | 1696 | 0:28 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR ROTO Y SE CERRO N/O CONTRA EL 9703-02 | C22080700150 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 28 | 2022-08-07 | 47488 | keep | 0 | Aug | 2022 | 0.032344 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-07 11:09 | 2022-08-07 14:35 | 60 | 3:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 30 EN RISER | S22080700047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2022-08-07 | 12360 | keep | 0 | Aug | 2022 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-07 11:09 | 2022-08-07 14:26 | 150 | 3:17 | P | ARBOL SOBRE LINEA | 3 X 65 EN C/L RETIRO ARBOL DE LAS LINEAS | C22080700138 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 197 | 2022-08-07 | 29550 | keep | 0 | Aug | 2022 | 0.020126 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-08-07 11:09 | 2022-08-07 16:58 | 40 | 5:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L CERRO PUENTE | C22080700138 | New_Event | Primary Wire Break | Include | Include | Equipment | 349 | 2022-08-07 | 13960 | keep | 0 | Aug | 2022 | 0.0095081 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-07 11:13 | 2022-08-07 15:35 | 7 | 4:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR Y DESGANCHE | P22080600138 | New_Event | Primary Wire Break | Include | Include | Equipment | 262 | 2022-08-07 | 1834 | keep | 0 | Aug | 2022 | 0.0012491 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-07 11:21 | 2022-08-07 21:41 | 1 | 10:20 | P | ANIMAL | 1 X 25 EN XMR SE RETIRO IGUANA Y SE REALIZO DESGANCHE | S22080700051 | New_Event | Animals | Include | Include | Wildlife | 620 | 2022-08-07 | 620 | keep | 0 | Aug | 2022 | 0.00042228 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-07 11:22 | 2022-08-07 12:40 | 200 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22080700034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-08-07 | 15600 | keep | 0 | Aug | 2022 | 0.010625 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-08-07 11:29 | 2022-08-07 14:19 | 315 | 2:50 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | C22080700151 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2022-08-07 | 53550 | keep | 0 | Aug | 2022 | 0.036473 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2022-08-07 11:35 | 2022-08-07 14:57 | 1130 | 3:22 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE NORMALIZARON LAS CARGAS | C22080700150 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 202 | 2022-08-07 | 228260 | keep | 0 | Aug | 2022 | 0.15547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 11:40 | 2022-08-07 13:12 | 80 | 1:32 | P | MAL TIEMPO/RAYOS | 3 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700036 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 92 | 2022-08-07 | 7360 | keep | 0 | Aug | 2022 | 0.0050129 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-07 11:44 | 2022-08-07 12:37 | 45 | 0:53 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA CERRAR PUENTES LUEGO DE RETIRAR RAMAS SOBRE LAS LINEAS | M22080600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-08-07 | 2385 | keep | 0 | Aug | 2022 | 0.0016244 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-08-07 11:50 | 2022-08-08 08:20 | 20 | 20:30 | P | DESGANCHE | DESGANCHE 1 X 40 EN C/L | C22080700163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1230 | 2022-08-07 | 24600 | keep | 0 | Aug | 2022 | 0.016755 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-07 11:54 | 2022-08-07 15:57 | 1 | 4:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080700063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 243 | 2022-08-07 | 243 | keep | 0 | Aug | 2022 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-07 12:00 | 2022-08-07 12:01 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22080700011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 2039 | keep | 0 | Aug | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
ARECIBO | 2022-08-07 12:09 | 2022-08-07 21:33 | 10 | 9:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 37.5KVA | A22080700039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 564 | 2022-08-07 | 5640 | keep | 0 | Aug | 2022 | 0.0038414 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-07 12:13 | 2022-08-07 12:14 | 2906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 2906 | keep | 0 | Aug | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
CANOVANAS | 2022-08-07 12:23 | 2022-08-07 14:00 | 100 | 1:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 Y 2 X 65 EN CORTES DE LINEA SE REEMPLAZARON DISCOS ROTOS | R22080700012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 97 | 2022-08-07 | 9700 | keep | 0 | Aug | 2022 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-07 12:25 | 2022-08-07 15:42 | 50 | 3:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080700042 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 197 | 2022-08-07 | 9850 | keep | 0 | Aug | 2022 | 0.0067088 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-07 12:27 | 2022-08-07 15:42 | 60 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | REPARO BAJANTE DE LINEA A CAJA Y ELIMINO AISLADOR NO FUNDIO | C22080700192 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2022-08-07 | 11700 | keep | 0 | Aug | 2022 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-07 12:28 | 2022-08-07 19:00 | 93 | 6:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C22080700194 | New_Event | Cutout Failure | Include | Include | Equipment | 392 | 2022-08-07 | 36456 | keep | 0 | Aug | 2022 | 0.02483 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
BAYAMON | 2022-08-07 12:32 | 2022-08-07 12:33 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22080700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 4431 | keep | 0 | Aug | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BARRANQUITAS | 2022-08-07 12:34 | 2022-08-07 12:35 | 1131 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080700199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 1131 | keep | 0 | Aug | 2022 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
BARRANQUITAS | 2022-08-07 12:43 | 2022-08-07 15:47 | 84 | 3:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES LLUVIAS | C22080700202 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 184 | 2022-08-07 | 15456 | keep | 0 | Aug | 2022 | 0.010527 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
BAYAMON | 2022-08-07 12:46 | 2022-08-07 19:13 | 3798 | 6:27 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REEMPLAZO BUS SUPPORT EN LA FASE C EN LA BARRA DE DISTRIBUCION QUE CAUSO LOCKOUT BY-220807-02 | B22080700114 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 387 | 2022-08-07 | 1469826 | keep | 0 | Aug | 2022 | 1.0011 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2022-08-07 12:46 | 2022-08-07 19:13 | 4622 | 6:27 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REEMPLAZO BUS SUPPORT EN LA FASE C EN LA BARRA DE DISTRIBUCION QUE CAUSO LOCKOUT BY-220807-02 | B22080700114 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 387 | 2022-08-07 | 1788714 | keep | 0 | Aug | 2022 | 1.2183 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2022-08-07 12:46 | 2022-08-07 19:13 | 4089 | 6:27 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REEMPLAZO BUS SUPPORT EN LA FASE C EN LA BARRA DE DISTRIBUCION QUE CAUSO LOCKOUT BY-220807-02 | B22080700114 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 387 | 2022-08-07 | 1582443 | keep | 0 | Aug | 2022 | 1.0778 | 0.002785 | Sustained | FALSE | FALSE | Not_TMED_Event | 4089
FAJARDO | 2022-08-07 12:50 | 2022-08-07 13:30 | 10 | 0:40 | P | ANIMAL | 1 X 10 EN XMR SE RETIRO AVE CRUZO LINEAS | R22080700015 | New_Event | Animals | Include | Include | Wildlife | 40 | 2022-08-07 | 400 | keep | 0 | Aug | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-08-07 12:52 | 2022-08-07 14:57 | 6 | 2:05 | P | SECUNDARIA/DESGANCHE | DESGANCHE SE REPARO SECUNDARIA QUEMADA | P22080700010 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 125 | 2022-08-07 | 750 | keep | 0 | Aug | 2022 | 0.00051082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-07 12:52 | 2022-08-07 16:45 | 2926 | 3:53 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR QUEMADO | B22080700120 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 233 | 2022-08-07 | 681758 | keep | 0 | Aug | 2022 | 0.46434 | 0.0019929 | Sustained | FALSE | FALSE | Not_TMED_Event | 2926
AGUADILLA | 2022-08-07 12:59 | 2022-08-07 14:35 | 40 | 1:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080700049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-08-07 | 3840 | keep | 0 | Aug | 2022 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-07 13:18 | 2022-08-07 15:00 | 50 | 1:42 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA Y 1 X 5 EN TRANSFORMADOR MAL TIEMPO | A22080700081 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2022-08-07 | 5100 | keep | 0 | Aug | 2022 | 0.0034736 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-07 13:18 | 2022-08-07 15:28 | 1548 | 2:10 | T | DESGANCHE | CARGA POR 8001-04 | A22080700313 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-08-07 | 201240 | keep | 0 | Aug | 2022 | 0.13706 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-08-07 13:18 | 2022-08-07 15:28 | 185 | 2:10 | T | DESGANCHE | CARGA POR 8001-04 | A22080700315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-08-07 | 24050 | keep | 0 | Aug | 2022 | 0.01638 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-08-07 13:18 | 2022-08-07 16:43 | 9 | 3:25 | T | DESGANCHE | DISPARO DE INTERRUPTOR LLEVA LAS CARGAS DEL 8001-01 Y 8001-03 SE REALIZO DESGANCHE MASIVO SE CERRO INTERRUPTOR | A22080700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2022-08-07 | 1845 | keep | 0 | Aug | 2022 | 0.0012566 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-08-07 13:19 | 2022-08-07 17:03 | 6 | 3:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22080700083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 224 | 2022-08-07 | 1344 | keep | 0 | Aug | 2022 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-07 13:25 | 2022-08-07 18:49 | 100 | 5:24 | P | CONDUCTOR ROTO O ABIERTO | SE DESGANCHO 2 X 100 EN C/L Y SE LAVANTO CONDUCTOR | B22080700178 | New_Event | Primary Wire Break | Include | Include | Equipment | 324 | 2022-08-07 | 32400 | keep | 0 | Aug | 2022 | 0.022067 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-07 13:37 | 2022-08-07 13:38 | 2713 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080700593 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 2713 | keep | 0 | Aug | 2022 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
UTUADO | 2022-08-07 13:38 | 2022-08-07 15:32 | 7 | 1:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22080700089 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 114 | 2022-08-07 | 798 | keep | 0 | Aug | 2022 | 0.00054351 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-08-07 13:40 | 2022-08-07 13:41 | 1337 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700065 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 1337 | keep | 0 | Aug | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-07 13:40 | 2022-08-07 13:42 | 1287 | 0:02 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080700066 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2 | 2022-08-07 | 2574 | keep | 0 | Aug | 2022 | 0.0017531 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
UTUADO | 2022-08-07 13:41 | 2022-08-07 15:30 | 100 | 1:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080700091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 109 | 2022-08-07 | 10900 | keep | 0 | Aug | 2022 | 0.0074239 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-07 13:47 | 2022-08-07 13:48 | 281 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 8100 | M22080700061 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 281 | keep | 0 | Aug | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-08-07 13:47 | 2022-08-07 13:48 | 1252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700601 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1252 | keep | 0 | Aug | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2022-08-07 13:47 | 2022-08-07 13:48 | 595 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700598 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 595 | keep | 0 | Aug | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2022-08-07 13:47 | 2022-08-07 13:48 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700598 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 51 | keep | 0 | Aug | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-07 13:47 | 2022-08-07 13:48 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700598 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 721 | keep | 0 | Aug | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-08-07 13:47 | 2022-08-07 13:48 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 3502 | keep | 0 | Aug | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-07 13:47 | 2022-08-07 13:48 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1241 | keep | 0 | Aug | 2022 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-07 13:47 | 2022-08-07 13:48 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 650 | keep | 0 | Aug | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-07 13:47 | 2022-08-07 13:48 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-07 13:47 | 2022-08-07 13:48 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 654 | keep | 0 | Aug | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
UTUADO | 2022-08-07 13:48 | 2022-08-07 21:41 | 25 | 7:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080700098 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 473 | 2022-08-07 | 11825 | keep | 0 | Aug | 2022 | 0.008054 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-07 13:51 | 2022-08-07 13:52 | 281 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 8100 | M22080700604 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 281 | keep | 0 | Aug | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-08-07 13:51 | 2022-08-07 13:52 | 1252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700604 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1252 | keep | 0 | Aug | 2022 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2022-08-07 13:51 | 2022-08-07 13:52 | 595 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700230 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 595 | keep | 0 | Aug | 2022 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2022-08-07 13:51 | 2022-08-07 13:52 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700230 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 51 | keep | 0 | Aug | 2022 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-07 13:51 | 2022-08-07 13:52 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 8100 | M22080700230 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 721 | keep | 0 | Aug | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-08-07 13:51 | 2022-08-07 13:52 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 3502 | keep | 0 | Aug | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-07 13:51 | 2022-08-07 13:52 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1241 | keep | 0 | Aug | 2022 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-07 13:51 | 2022-08-07 13:52 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 650 | keep | 0 | Aug | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-07 13:51 | 2022-08-07 13:52 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-07 13:51 | 2022-08-07 13:52 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700000 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 654 | keep | 0 | Aug | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2022-08-07 13:54 | 2022-08-07 14:49 | 281 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700609 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 15455 | keep | 0 | Aug | 2022 | 0.010526 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-08-07 13:54 | 2022-08-07 14:49 | 1252 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700609 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 68860 | keep | 0 | Aug | 2022 | 0.0469 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2022-08-07 13:54 | 2022-08-07 14:49 | 595 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700607 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 32725 | keep | 0 | Aug | 2022 | 0.022289 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2022-08-07 13:54 | 2022-08-07 14:49 | 51 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700607 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 2805 | keep | 0 | Aug | 2022 | 0.0019105 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-07 13:54 | 2022-08-07 14:49 | 721 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700607 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 39655 | keep | 0 | Aug | 2022 | 0.027009 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-08-07 13:54 | 2022-08-07 14:49 | 3502 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22080700172 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 192610 | keep | 0 | Aug | 2022 | 0.13119 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-07 13:54 | 2022-08-07 14:49 | 1241 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22080700172 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 68255 | keep | 0 | Aug | 2022 | 0.046488 | 0.00084524 | Sustained | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-07 13:54 | 2022-08-07 14:49 | 650 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22080700172 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 35750 | keep | 0 | Aug | 2022 | 0.024349 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-07 13:54 | 2022-08-07 14:49 | 1382 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700167 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 76010 | keep | 0 | Aug | 2022 | 0.05177 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-07 13:54 | 2022-08-07 14:49 | 654 | 0:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700167 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 55 | 2022-08-07 | 35970 | keep | 0 | Aug | 2022 | 0.024499 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
PONCE | 2022-08-07 13:58 | 2022-08-07 15:12 | 70 | 1:14 | P | DESGANCHE | 1 X 100 EN CL/ DESGANCHE | P22080700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-08-07 | 5180 | keep | 0 | Aug | 2022 | 0.0035281 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-08-07 14:00 | 2022-08-08 11:30 | 16 | 21:30 | P | MAL TIEMPO/RAYOS | 2 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS (EVENTO SALIO CON FECHA ANTERIOR) | M22080800081 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1290 | 2022-08-07 | 20640 | keep | 0 | Aug | 2022 | 0.014058 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-08-07 14:00 | 2022-08-08 12:22 | 9 | 22:22 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS EVENTO DEL DIA 7 | M22080800111 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1342 | 2022-08-07 | 12078 | keep | 0 | Aug | 2022 | 0.0082263 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2022-08-07 14:00 | 2022-08-08 11:59 | 30 | 21:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22080700322 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1319 | 2022-08-07 | 39570 | keep | 0 | Aug | 2022 | 0.026951 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-07 14:02 | 2022-08-07 17:00 | 1497 | 2:58 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO EL ALIMENTADOR Y SE CERRO EL INTERRUPTOR. SE CONTINUA PATRULLANDO. | M22080700084 | New_Event | Primary Wire Break | Include | Include | Equipment | 178 | 2022-08-07 | 266466 | keep | 0 | Aug | 2022 | 0.18149 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700710 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 574 | keep | 0 | Aug | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700710 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 2493 | keep | 0 | Aug | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700710 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1415 | keep | 0 | Aug | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700710 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1428 | keep | 0 | Aug | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700710 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1036 | keep | 0 | Aug | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700712 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 382 | keep | 0 | Aug | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700712 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 39 | keep | 0 | Aug | 2022 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2022-08-07 14:02 | 2022-08-07 14:03 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700713 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 2366 | keep | 0 | Aug | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2022-08-07 14:02 | 2022-08-07 14:03 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700713 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1337 | keep | 0 | Aug | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-07 14:02 | 2022-08-07 14:03 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700713 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 709 | keep | 0 | Aug | 2022 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
UTUADO | 2022-08-07 14:12 | 2022-08-07 14:51 | 934 | 0:39 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22080700173 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-08-07 | 36426 | keep | 0 | Aug | 2022 | 0.02481 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-08-07 14:12 | 2022-08-07 14:51 | 4 | 0:39 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22080700173 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-08-07 | 156 | keep | 0 | Aug | 2022 | 0.00010625 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-08-07 14:12 | 2022-08-07 14:51 | 1479 | 0:39 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22080700173 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-08-07 | 57681 | keep | 0 | Aug | 2022 | 0.039286 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-08-07 14:12 | 2022-08-07 14:51 | 1841 | 0:39 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22080700174 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-08-07 | 71799 | keep | 0 | Aug | 2022 | 0.048902 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-08-07 14:12 | 2022-08-07 14:51 | 1950 | 0:39 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22080700174 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 39 | 2022-08-07 | 76050 | keep | 0 | Aug | 2022 | 0.051797 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
AGUADILLA | 2022-08-07 14:15 | 2022-08-07 14:16 | 1017 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL INTERRUPTOR LINEAS PRIMARIAS PARTIDAS | M22080700529 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-07 | 1017 | keep | 0 | Aug | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-08-07 14:16 | 2022-08-07 14:19 | 406 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | LINEAS PRIMARIAS PARTIDAS ENTRO EL 40 % EN SERVICIO | M22080700529 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-07 | 1218 | keep | 0 | Aug | 2022 | 0.00082957 | 0.00027652 | Momentary | FALSE | FALSE | Not_TMED_Event | 406
UTUADO | 2022-08-07 14:16 | 2022-08-08 12:00 | 50 | 21:44 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS( EVENTOS SALIENDO CON FECHAS ANTERIORES) | A22080800140 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1304 | 2022-08-07 | 65200 | keep | 0 | Aug | 2022 | 0.044407 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-07 14:19 | 2022-08-07 17:40 | 250 | 3:21 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR | C22080700151 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 201 | 2022-08-07 | 50250 | keep | 0 | Aug | 2022 | 0.034225 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 14:19 | 2022-08-07 17:29 | 1017 | 3:10 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA DE LINEAS PRIMARIAS PARTIDAS (SISTEMA NO DEJO CREAR EVENTOS) | M22080700000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 190 | 2022-08-07 | 193230 | keep | 0 | Aug | 2022 | 0.13161 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-08-07 14:21 | 2022-08-07 14:22 | 411 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080700726 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 411 | keep | 0 | Aug | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-08-07 14:23 | 2022-08-07 14:24 | 411 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080700728 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 411 | keep | 0 | Aug | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-08-07 14:25 | 2022-08-07 14:26 | 411 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080700729 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 411 | keep | 0 | Aug | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
CAGUAS | 2022-08-07 14:26 | 2022-08-07 14:27 | 4369 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | C22080700245 | Additional_clients | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-08-07 | 4369 | keep | 0 | Aug | 2022 | 0.0029757 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-07 14:26 | 2022-08-07 14:27 | 1584 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE INTERRUPTOR DESCARGAS ELECTRICAS | M22080700113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 1584 | keep | 0 | Aug | 2022 | 0.0010789 | 0.0010789 | Momentary | FALSE | FALSE | Not_TMED_Event | 1584
CAGUAS | 2022-08-07 14:27 | 2022-08-07 16:17 | 150 | 1:50 | P | ARBOL SOBRE LINEA | 3 X 65 EN C/L RETIRO ARBOL DE LAS LINEAS | C22080700138 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 110 | 2022-08-07 | 16500 | keep | 0 | Aug | 2022 | 0.011238 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-07 14:27 | 2022-08-07 14:28 | 4664 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR DESCARGAS ELECTRICAS | M22080700116 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 4664 | keep | 0 | Aug | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2022-08-07 14:27 | 2022-08-07 14:28 | 1352 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M22080700117 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 1352 | keep | 0 | Aug | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
UTUADO | 2022-08-07 14:27 | 2022-08-07 18:34 | 3 | 4:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22080700166 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 247 | 2022-08-07 | 741 | keep | 0 | Aug | 2022 | 0.00050469 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-07 14:28 | 2022-08-07 16:49 | 100 | 2:21 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080700138 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 141 | 2022-08-07 | 14100 | keep | 0 | Aug | 2022 | 0.0096034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-07 14:30 | 2022-08-07 23:35 | 40 | 9:05 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080700387 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 545 | 2022-08-07 | 21800 | keep | 0 | Aug | 2022 | 0.014848 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-07 14:32 | 2022-08-07 14:33 | 888 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22080700721 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 888 | keep | 0 | Aug | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-08-07 14:32 | 2022-08-07 14:33 | 393 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22080700721 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 393 | keep | 0 | Aug | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-08-07 14:32 | 2022-08-07 14:33 | 4 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22080700721 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-07 14:32 | 2022-08-07 14:33 | 990 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22080700130 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 990 | keep | 0 | Aug | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
UTUADO | 2022-08-07 14:33 | 2022-08-07 16:30 | 40 | 1:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CONVERTIDOR Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22080700176 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 117 | 2022-08-07 | 4680 | keep | 0 | Aug | 2022 | 0.0031875 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-07 14:35 | 2022-08-07 14:37 | 837 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 1401-08 LLEVA 1346-05 1401-07 LLEVA 20% 1404-09 | S22080700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-07 | 1674 | keep | 0 | Aug | 2022 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-08-07 14:35 | 2022-08-07 14:37 | 908 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 1401-08 LLEVA 1346-05 1401-07 LLEVA 20% 1404-09 | S22080700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-07 | 1816 | keep | 0 | Aug | 2022 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-08-07 14:35 | 2022-08-07 14:37 | 135 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 1401-08 LLEVA 1346-05 1401-07 LLEVA 20% 1404-09 | S22080700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-07 | 270 | keep | 0 | Aug | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-08-07 14:35 | 2022-08-07 14:37 | 1 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 1401-08 LLEVA 1346-05 1401-07 LLEVA 20% 1404-09 | S22080700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-07 | 2 | keep | 0 | Aug | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-07 14:35 | 2022-08-07 14:37 | 1295 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 1401-08 LLEVA 1346-05 1401-07 LLEVA 20% 1404-09 | S22080700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-07 | 2590 | keep | 0 | Aug | 2022 | 0.001764 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 1253 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700722 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1253 | keep | 0 | Aug | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 1266 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700722 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1266 | keep | 0 | Aug | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 411 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700722 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 411 | keep | 0 | Aug | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2022-08-07 14:36 | 2022-08-07 14:37 | 1617 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700723 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1617 | keep | 0 | Aug | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-08-07 14:36 | 2022-08-07 14:37 | 828 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700723 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 863 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 863 | keep | 0 | Aug | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 309 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 309 | keep | 0 | Aug | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 176 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700724 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 176 | keep | 0 | Aug | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 974 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22080700725 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 974 | keep | 0 | Aug | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700732 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 574 | keep | 0 | Aug | 2022 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700732 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 2493 | keep | 0 | Aug | 2022 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700732 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1415 | keep | 0 | Aug | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700732 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1428 | keep | 0 | Aug | 2022 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700732 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1036 | keep | 0 | Aug | 2022 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700733 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 382 | keep | 0 | Aug | 2022 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700733 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 39 | keep | 0 | Aug | 2022 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2022-08-07 14:36 | 2022-08-07 14:37 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700734 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 2366 | keep | 0 | Aug | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2022-08-07 14:36 | 2022-08-07 14:37 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700734 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1337 | keep | 0 | Aug | 2022 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-07 14:36 | 2022-08-07 14:37 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M22080700734 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 709 | keep | 0 | Aug | 2022 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
SAN JUAN | 2022-08-07 14:37 | 2022-08-07 17:51 | 60 | 3:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 30 EN RISER | S22080700047 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-08-07 | 11640 | keep | 0 | Aug | 2022 | 0.007928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-07 14:37 | 2022-08-07 17:10 | 50 | 2:33 | P | DESGANCHE | 1 X 50 EN BOOSTER SE RETIRO RAMA SOBRE LINEA PRIMARIA | M22080700135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-08-07 | 7650 | keep | 0 | Aug | 2022 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-07 14:39 | 2022-08-08 08:47 | 70 | 18:08 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL | M22080700146 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1088 | 2022-08-07 | 76160 | keep | 0 | Aug | 2022 | 0.051872 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-08-07 14:42 | 2022-08-07 14:43 | 108 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1500 | M22080700735 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 108 | keep | 0 | Aug | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
UTUADO | 2022-08-07 14:42 | 2022-08-07 17:36 | 14 | 2:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080700184 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 174 | 2022-08-07 | 2436 | keep | 0 | Aug | 2022 | 0.0016591 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2022-08-07 14:44 | 2022-08-08 09:05 | 20 | 18:21 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080700160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1101 | 2022-08-07 | 22020 | keep | 0 | Aug | 2022 | 0.014998 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-07 14:44 | 2022-08-07 18:48 | 300 | 4:04 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700186 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 244 | 2022-08-07 | 73200 | keep | 0 | Aug | 2022 | 0.049856 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2022-08-07 14:45 | 2022-08-07 21:55 | 40 | 7:10 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080700163 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 430 | 2022-08-07 | 17200 | keep | 0 | Aug | 2022 | 0.011715 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-07 14:45 | 2022-08-07 20:30 | 100 | 5:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080700165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2022-08-07 | 34500 | keep | 0 | Aug | 2022 | 0.023498 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-07 14:46 | 2022-08-07 19:50 | 50 | 5:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080700188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 304 | 2022-08-07 | 15200 | keep | 0 | Aug | 2022 | 0.010353 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-07 14:47 | 2022-08-08 08:46 | 400 | 17:59 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M22080700173 | New_Event | Primary Wire Break | Include | Include | Equipment | 1079 | 2022-08-07 | 431600 | keep | 0 | Aug | 2022 | 0.29396 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-08-07 14:50 | 2022-08-07 14:51 | 922 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 1401-08 LLEVA 1346-05 1401-07 LLEVA 20% 1404-09 | S22080700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 922 | keep | 0 | Aug | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-08-07 14:50 | 2022-08-07 14:51 | 97 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 1401-08 LLEVA 1346-05 1401-07 LLEVA 20% 1404-09 | S22080700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 97 | keep | 0 | Aug | 2022 | 6.6066e-05 | 6.6066e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 97
AGUADILLA | 2022-08-07 14:52 | 2022-08-07 17:25 | 50 | 2:33 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080700191 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 153 | 2022-08-07 | 7650 | keep | 0 | Aug | 2022 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-07 14:56 | 2022-08-09 13:12 | 8 | 46:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO TRAMO SECUNDARIO SOTERRADO Y BARRAS DE PEDESTAL | C22080700087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 2776 | 2022-08-07 | 22208 | keep | 0 | Aug | 2022 | 0.015126 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-07 14:58 | 2022-08-08 12:50 | 12 | 21:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C22080700253 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1312 | 2022-08-07 | 15744 | keep | 0 | Aug | 2022 | 0.010723 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-07 14:58 | 2022-08-08 13:50 | 10 | 22:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | M22080700209 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1372 | 2022-08-07 | 13720 | keep | 0 | Aug | 2022 | 0.0093446 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-07 14:59 | 2022-08-07 17:48 | 125 | 2:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22080700200 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 169 | 2022-08-07 | 21125 | keep | 0 | Aug | 2022 | 0.014388 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
FAJARDO | 2022-08-07 15:00 | 2022-08-07 18:24 | 50 | 3:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22080700020 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2022-08-07 | 10200 | keep | 0 | Aug | 2022 | 0.0069472 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-07 15:00 | 2022-08-07 15:01 | 732 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080700041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 732 | keep | 0 | Aug | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
PONCE | 2022-08-07 15:03 | 2022-08-07 18:52 | 100 | 3:49 | P | DESGANCHE | 1 X 140 EN CONVERTIDOR SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22080700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2022-08-07 | 22900 | keep | 0 | Aug | 2022 | 0.015597 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-07 15:03 | 2022-08-07 20:05 | 100 | 5:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080700223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-08-07 | 30200 | keep | 0 | Aug | 2022 | 0.020569 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-07 15:08 | 2022-08-07 15:09 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 4006-05 | P22080700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 4132 | keep | 0 | Aug | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-08-07 15:08 | 2022-08-07 15:09 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR 4006-05 | P22080700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 4279 | keep | 0 | Aug | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-08-07 15:08 | 2022-08-07 15:09 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 4003-01 Y 4003-02 | P22080700045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 464 | keep | 0 | Aug | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
MAYAGÃœEZ | 2022-08-07 15:10 | 2022-08-07 19:30 | 50 | 4:20 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN DISTINTOS CORTES DE LINEA SE REALIZO DESGANCHE | M22080700247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-08-07 | 13000 | keep | 0 | Aug | 2022 | 0.0088542 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-07 15:12 | 2022-08-07 16:46 | 70 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CONVERTIDOR MAL TIEMPO VIENTOS FUERTES | A22080700214 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2022-08-07 | 6580 | keep | 0 | Aug | 2022 | 0.0044816 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-08-07 15:19 | 2022-08-07 16:18 | 8 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO LINEA SECUNDARIA DEL SUELO | R22080700021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2022-08-07 | 472 | keep | 0 | Aug | 2022 | 0.00032148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-07 15:23 | 2022-08-07 23:00 | 7 | 7:37 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080700223 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 457 | 2022-08-07 | 3199 | keep | 0 | Aug | 2022 | 0.0021788 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-08-07 15:24 | 2022-08-07 23:30 | 20 | 8:06 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080700227 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 486 | 2022-08-07 | 9720 | keep | 0 | Aug | 2022 | 0.0066202 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-07 15:27 | 2022-08-07 20:50 | 50 | 5:23 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080700228 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 323 | 2022-08-07 | 16150 | keep | 0 | Aug | 2022 | 0.011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-07 15:27 | 2022-08-07 21:30 | 60 | 6:03 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA AVERIADA | A22080700229 | New_Event | Primary Wire Break | Include | Include | Equipment | 363 | 2022-08-07 | 21780 | keep | 0 | Aug | 2022 | 0.014834 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-07 15:36 | 2022-08-07 15:37 | 1415 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22080700318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-07 | 1415 | keep | 0 | Aug | 2022 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
AGUADILLA | 2022-08-07 15:51 | 2022-08-07 18:31 | 1337 | 2:40 | T | MAL TIEMPO/RAYOS | SE VERIFICO INTERRUPTOR ABIERTO EN LA SUBESTACION ESTA TIENE EL RTU FUERA DE SERVICIO SE PATRULLO EL ALIMENTADOR Y LA UNICA CAUSA ENCONTRADA FUE DESCARGAS ELECTRICAS EN EL AREA SE CERRO EL INTERRUPTOR Y QUEDO EN SERVICO | M22080700349 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 160 | 2022-08-07 | 213920 | keep | 0 | Aug | 2022 | 0.1457 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
CANOVANAS | 2022-08-07 15:52 | 2022-08-07 18:41 | 300 | 2:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R22080700024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-08-07 | 50700 | keep | 0 | Aug | 2022 | 0.034532 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-08-07 15:59 | 2022-08-07 16:00 | 281 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22080700727 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 281 | keep | 0 | Aug | 2022 | 0.00019139 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-07 15:59 | 2022-08-07 16:00 | 1252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22080700727 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 1252 | keep | 0 | Aug | 2022 | 0.00085273 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 15:59 | 2022-08-07 16:00 | 595 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22080700730 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 595 | keep | 0 | Aug | 2022 | 0.00040525 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 15:59 | 2022-08-07 16:00 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22080700730 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 51 | keep | 0 | Aug | 2022 | 3.4736e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 15:59 | 2022-08-07 16:00 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 | M22080700730 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-07 | 721 | keep | 0 | Aug | 2022 | 0.00049107 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-07 16:02 | 2022-08-07 17:20 | 281 | 1:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700625 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2022-08-07 | 21918 | keep | 0 | Aug | 2022 | 0.014928 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-08-07 16:02 | 2022-08-07 17:20 | 1252 | 1:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700625 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2022-08-07 | 97656 | keep | 0 | Aug | 2022 | 0.066513 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2022-08-07 16:02 | 2022-08-07 17:20 | 595 | 1:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700628 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2022-08-07 | 46410 | keep | 0 | Aug | 2022 | 0.03161 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2022-08-07 16:02 | 2022-08-07 17:20 | 51 | 1:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700628 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2022-08-07 | 3978 | keep | 0 | Aug | 2022 | 0.0027094 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-07 16:02 | 2022-08-07 17:20 | 721 | 1:18 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | M22080700628 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 78 | 2022-08-07 | 56238 | keep | 0 | Aug | 2022 | 0.038303 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-08-07 16:03 | 2022-08-07 16:41 | 3502 | 0:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22080700295 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-08-07 | 133076 | keep | 0 | Aug | 2022 | 0.090637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-07 16:03 | 2022-08-07 16:41 | 1241 | 0:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22080700295 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-08-07 | 47158 | keep | 0 | Aug | 2022 | 0.032119 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-07 16:03 | 2022-08-07 16:41 | 650 | 0:38 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22080700295 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 38 | 2022-08-07 | 24700 | keep | 0 | Aug | 2022 | 0.016823 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-07 16:03 | 2022-08-07 17:20 | 1382 | 1:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700308 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 77 | 2022-08-07 | 106414 | keep | 0 | Aug | 2022 | 0.072478 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-07 16:03 | 2022-08-07 17:20 | 654 | 1:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22080700308 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 77 | 2022-08-07 | 50358 | keep | 0 | Aug | 2022 | 0.034299 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-07 16:23 | 2022-08-07 18:44 | 106 | 2:21 | P | CONDUCTOR ROTO O ABIERTO | SE MONTO 3 WIRE A CAJA | B22080700359 | New_Event | Primary Wire Break | Include | Include | Equipment | 141 | 2022-08-07 | 14946 | keep | 0 | Aug | 2022 | 0.01018 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
BAYAMON | 2022-08-07 16:31 | 2022-08-07 18:13 | 100 | 1:42 | P | ANIMAL | 1 X 80 EN RISER Y 1 X 10 EN SU-4 AVE | B22080700369 | New_Event | Animals | Include | Include | Wildlife | 102 | 2022-08-07 | 10200 | keep | 0 | Aug | 2022 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-07 16:37 | 2022-08-07 18:30 | 35 | 1:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PRIMARIA | M22080700426 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-08-07 | 3955 | keep | 0 | Aug | 2022 | 0.0026937 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-08-07 16:44 | 2022-08-07 23:19 | 100 | 6:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE PRIMARIO | B22080700384 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2022-08-07 | 39500 | keep | 0 | Aug | 2022 | 0.026903 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-07 16:49 | 2022-08-07 16:50 | 1352 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR DESCARGAS ELECTRICAS | M22080700442 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-07 | 1352 | keep | 0 | Aug | 2022 | 0.00092084 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-07 16:50 | 2022-08-07 18:24 | 100 | 1:34 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080700138 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 94 | 2022-08-07 | 9400 | keep | 0 | Aug | 2022 | 0.0064023 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-07 17:00 | 2022-08-07 17:56 | 1097 | 0:56 | P | CONDUCTOR ROTO O ABIERTO | AL CERRAR MACHETES SE DISPARO EL INTERRUPTOR | M22080700535 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 56 | 2022-08-07 | 61432 | keep | 0 | Aug | 2022 | 0.041841 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-07 17:07 | 2022-08-07 18:50 | 50 | 1:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080700294 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 103 | 2022-08-07 | 5150 | keep | 0 | Aug | 2022 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-07 17:10 | 2022-08-07 18:00 | 7 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 8 EN XMR Y SE ABRIO OTRO XMR PARA REPARAR SECUNDARIA | C22080700239 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-08-07 | 350 | keep | 0 | Aug | 2022 | 0.00023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-08-07 17:10 | 2022-08-07 18:42 | 100 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L FUERTES LLUVIAS | C22080700288 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2022-08-07 | 9200 | keep | 0 | Aug | 2022 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-07 17:11 | 2022-08-07 17:44 | 80 | 0:33 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE QUE CRUZO LINEAS | A22080700298 | New_Event | Animals | Include | Include | Wildlife | 33 | 2022-08-07 | 2640 | keep | 0 | Aug | 2022 | 0.0017981 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-08-07 17:16 | 2022-08-07 23:10 | 30 | 5:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO DE CAJA PRIMARIA | P22080700070 | New_Event | Cutout Failure | Include | Include | Equipment | 354 | 2022-08-07 | 10620 | keep | 0 | Aug | 2022 | 0.0072332 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-07 17:30 | 2022-08-08 08:28 | 20 | 14:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080700309 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 898 | 2022-08-07 | 17960 | keep | 0 | Aug | 2022 | 0.012232 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-07 17:35 | 2022-08-07 20:14 | 120 | 2:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080700510 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-08-07 | 19080 | keep | 0 | Aug | 2022 | 0.012995 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-08-07 17:45 | 2022-08-07 20:03 | 80 | 2:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R22080700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-08-07 | 11040 | keep | 0 | Aug | 2022 | 0.0075193 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-07 17:53 | 2022-08-08 09:22 | 26 | 15:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22080700441 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 929 | 2022-08-07 | 24154 | keep | 0 | Aug | 2022 | 0.016451 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
UTUADO | 2022-08-07 17:54 | 2022-08-08 17:20 | 250 | 23:26 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22080700323 | New_Event | Primary Wire Break | Include | Include | Equipment | 1406 | 2022-08-07 | 351500 | keep | 0 | Aug | 2022 | 0.23941 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
UTUADO | 2022-08-07 17:54 | 2022-08-08 17:20 | 10 | 23:26 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080700322 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1406 | 2022-08-07 | 14060 | keep | 0 | Aug | 2022 | 0.0095762 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-07 17:56 | 2022-08-07 18:35 | 1497 | 0:39 | T | CONDUCTOR ROTO O ABIERTO | SE VOLVIO A ABRIR LOS MACHETES Y SE CERRO EL INTERRUPTOR | M22080700538 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 39 | 2022-08-07 | 58383 | keep | 0 | Aug | 2022 | 0.039764 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 18:02 | 2022-08-07 22:30 | 50 | 4:28 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700542 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 268 | 2022-08-07 | 13400 | keep | 0 | Aug | 2022 | 0.0091267 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-07 18:05 | 2022-08-08 02:43 | 50 | 8:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S22080700100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 518 | 2022-08-07 | 25900 | keep | 0 | Aug | 2022 | 0.01764 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-07 18:22 | 2022-08-07 19:12 | 1 | 0:50 | P | ANIMAL | 2 X 20 EN BANCO DE XMRS CRUCE X AVE | C22080700296 | New_Event | Animals | Include | Include | Wildlife | 50 | 2022-08-07 | 50 | keep | 0 | Aug | 2022 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-07 18:28 | 2022-08-07 19:45 | 4664 | 1:17 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO Y DOS AISLADORES ROTOS EN EL TRONCAL DEL ALIMENTADOR | M22080700571 | New_Event | Switch Failure | Include | Include | Equipment | 77 | 2022-08-07 | 359128 | keep | 0 | Aug | 2022 | 0.2446 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
AGUADILLA | 2022-08-07 18:35 | 2022-08-07 20:00 | 1097 | 1:25 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA ROTA EN TERMINAL DE LINEA QUE NO LE DA SERVICIO A NADIE Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR | M22080700538 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 85 | 2022-08-07 | 93245 | keep | 0 | Aug | 2022 | 0.063509 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 18:41 | 2022-08-07 22:50 | 30 | 4:09 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M22080700584 | New_Event | Primary Wire Break | Include | Include | Equipment | 249 | 2022-08-07 | 7470 | keep | 0 | Aug | 2022 | 0.0050878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-08-07 18:56 | 2022-08-08 08:33 | 5 | 13:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR FUERTES LLUVIAS | C22080700302 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 817 | 2022-08-07 | 4085 | keep | 0 | Aug | 2022 | 0.0027823 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-08-07 19:05 | 2022-08-08 07:47 | 20 | 12:42 | P | PARARRAYOS DEFECTUOSO | REMPLAZO PARARRAYO Y BAJANTE PRIMARIO NO FUNDIO | C22080700303 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 762 | 2022-08-07 | 15240 | keep | 0 | Aug | 2022 | 0.01038 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-08-07 19:08 | 2022-08-07 20:27 | 40 | 1:19 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS ARRIADAS | P22080700083 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 79 | 2022-08-07 | 3160 | keep | 0 | Aug | 2022 | 0.0021523 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-07 19:08 | 2022-08-07 19:09 | 4381 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR BAJANTE DE MACHETE ZAFADO | M22080700603 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-07 | 4381 | keep | 0 | Aug | 2022 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2022-08-07 19:09 | 2022-08-07 22:30 | 1460 | 3:21 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE MACHETE | M22080700621 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 201 | 2022-08-07 | 293460 | keep | 0 | Aug | 2022 | 0.19987 | 0.0009944 | Sustained | FALSE | FALSE | Not_TMED_Event | 1460
GUAYAMA | 2022-08-07 19:15 | 2022-08-07 22:05 | 40 | 2:50 | P | ANIMAL | 1 X 30 EN C/L CRUCE DE FASE PRIMARIA POR AVE | P22080700084 | New_Event | Animals | Include | Include | Wildlife | 170 | 2022-08-07 | 6800 | keep | 0 | Aug | 2022 | 0.0046314 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-07 19:27 | 2022-08-08 09:41 | 30 | 14:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L FUERTES LLUVIAS | C22080700304 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 854 | 2022-08-07 | 25620 | keep | 0 | Aug | 2022 | 0.01745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-07 19:40 | 2022-08-08 05:40 | 52 | 10:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 Y 1 X 40 EN CORTE DE LINEA LLUVIA | B22080700495 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 600 | 2022-08-07 | 31200 | keep | 0 | Aug | 2022 | 0.02125 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2022-08-07 19:40 | 2022-08-08 00:36 | 60 | 4:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080700124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-08-07 | 17760 | keep | 0 | Aug | 2022 | 0.012096 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-07 19:44 | 2022-08-08 09:49 | 2 | 14:05 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080700341 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 845 | 2022-08-07 | 1690 | keep | 0 | Aug | 2022 | 0.0011511 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-07 19:45 | 2022-08-08 02:10 | 1 | 6:25 | P | MAL TIEMPO/RAYOS | 1 X 80 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22080700611 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 385 | 2022-08-07 | 385 | keep | 0 | Aug | 2022 | 0.00026222 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-07 19:50 | 2022-08-08 09:17 | 6 | 13:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22080700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 807 | 2022-08-07 | 4842 | keep | 0 | Aug | 2022 | 0.0032979 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-07 19:53 | 2022-08-08 10:34 | 300 | 14:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080700631 | New_Event | Vegetation Contact | Include | Include | Vegetation | 881 | 2022-08-07 | 264300 | keep | 0 | Aug | 2022 | 0.18001 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2022-08-07 19:58 | 2022-08-08 09:10 | 40 | 13:12 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080700346 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 792 | 2022-08-07 | 31680 | keep | 0 | Aug | 2022 | 0.021577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-07 20:00 | 2022-08-08 16:15 | 50 | 20:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON LINEAS PRIMARIAS ROTAS RELACIONADO AEVENTO M22080700084 | M22080700106 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1215 | 2022-08-07 | 60750 | keep | 0 | Aug | 2022 | 0.041377 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-07 20:06 | 2022-08-08 14:31 | 250 | 18:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M22080700641 | New_Event | Primary Wire Break | Include | Include | Equipment | 1105 | 2022-08-07 | 276250 | keep | 0 | Aug | 2022 | 0.18815 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-08-07 20:11 | 2022-08-07 21:50 | 250 | 1:39 | P | MAL TIEMPO/RAYOS | 1 X 200 Y 1 X 100 EN DISTINTOS CORTES DE LINEA DESCARGAS ELECTRICAS | M22080700648 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 99 | 2022-08-07 | 24750 | keep | 0 | Aug | 2022 | 0.016857 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
UTUADO | 2022-08-07 20:20 | 2022-08-07 22:05 | 40 | 1:45 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080700350 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 105 | 2022-08-07 | 4200 | keep | 0 | Aug | 2022 | 0.0028606 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-07 20:25 | 2022-08-07 21:20 | 40 | 0:55 | P | CABLE SOTERRADO AVERIADO | SE ABRIO CAJA PRIMARIA EN C/L PROVISIONAL PARA CONECTAR AEREO PROVISIONAL NUEVO A T50 | S22080500183 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 55 | 2022-08-07 | 2200 | keep | 0 | Aug | 2022 | 0.0014984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-07 20:55 | 2022-08-07 22:35 | 30 | 1:40 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700666 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 100 | 2022-08-07 | 3000 | keep | 0 | Aug | 2022 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-07 21:07 | 2022-08-08 12:20 | 10 | 15:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 15KVA X 25 KVA | M22080700675 | New_Event | Service Transformer Failure | Include | Include | Equipment | 913 | 2022-08-07 | 9130 | keep | 0 | Aug | 2022 | 0.0062184 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-07 21:11 | 2022-08-08 12:30 | 150 | 15:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA EVENTO DEL DIA 7 | M22080800018 | New_Event | Cutout Failure | Include | Include | Equipment | 919 | 2022-08-07 | 137850 | keep | 0 | Aug | 2022 | 0.093889 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-07 21:11 | 2022-08-08 10:00 | 6 | 12:49 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22080700677 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 769 | 2022-08-07 | 4614 | keep | 0 | Aug | 2022 | 0.0031426 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-07 21:27 | 2022-08-08 12:38 | 40 | 15:11 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080700684 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 911 | 2022-08-07 | 36440 | keep | 0 | Aug | 2022 | 0.024819 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-07 21:38 | 2022-08-08 19:34 | 7 | 21:56 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO 37.5 KVA X 37.5 KVA Y AISLADOR | C22080700316 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1316 | 2022-08-07 | 9212 | keep | 0 | Aug | 2022 | 0.0062743 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-08-07 21:41 | 2022-08-08 12:38 | 80 | 14:57 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C22080700317 | New_Event | Vegetation Contact | Include | Include | Vegetation | 897 | 2022-08-07 | 71760 | keep | 0 | Aug | 2022 | 0.048875 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-07 21:51 | 2022-08-08 05:15 | 175 | 7:24 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700695 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 444 | 2022-08-07 | 77700 | keep | 0 | Aug | 2022 | 0.052921 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2022-08-07 21:52 | 2022-08-08 04:00 | 80 | 6:08 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700697 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 368 | 2022-08-07 | 29440 | keep | 0 | Aug | 2022 | 0.020051 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-08-07 21:53 | 2022-08-08 07:17 | 40 | 9:24 | P | DESGANCHE | 1 X 30 Y 1 X 20 EN C/LS DESGANCHO | C22080700318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 564 | 2022-08-07 | 22560 | keep | 0 | Aug | 2022 | 0.015366 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-07 22:24 | 2022-08-08 10:00 | 125 | 11:36 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700705 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 696 | 2022-08-07 | 87000 | keep | 0 | Aug | 2022 | 0.059255 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-08-07 22:41 | 2022-08-08 04:19 | 2694 | 5:38 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA (GOI # AR-220808-01A) SE CERRO INTERRUPTOR | A22080700373 | New_Event | Primary Wire Break | Include | Include | Equipment | 338 | 2022-08-07 | 910572 | keep | 0 | Aug | 2022 | 0.62019 | 0.0018349 | Sustained | FALSE | FALSE | Not_TMED_Event | 2694
CAGUAS | 2022-08-07 22:47 | 2022-08-08 07:01 | 100 | 8:14 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22080700324 | New_Event | Vegetation Contact | Include | Include | Vegetation | 494 | 2022-08-07 | 49400 | keep | 0 | Aug | 2022 | 0.033646 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-07 22:54 | 2022-08-07 23:15 | 75 | 0:21 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22080700673 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 21 | 2022-08-07 | 1575 | keep | 0 | Aug | 2022 | 0.0010727 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-08-07 23:00 | 2022-08-08 10:19 | 1 | 11:19 | P | MAL TIEMPO/RAYOS | 2 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22080800051 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 679 | 2022-08-07 | 679 | keep | 0 | Aug | 2022 | 0.00046246 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-07 23:14 | 2022-08-08 11:02 | 200 | 11:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M22080700718 | New_Event | Cutout Failure | Include | Include | Equipment | 708 | 2022-08-07 | 141600 | keep | 0 | Aug | 2022 | 0.096443 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-07 23:22 | 2022-08-08 10:27 | 6 | 11:05 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B22080700519 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 665 | 2022-08-07 | 3990 | keep | 0 | Aug | 2022 | 0.0027176 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-08-08 02:00 | 2022-08-08 11:08 | 60 | 9:08 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASES | M22080800014 | New_Event | Animals | Include | Include | Wildlife | 548 | 2022-08-08 | 32880 | keep | 0 | Aug | 2022 | 0.022394 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-08 02:40 | 2022-08-08 02:41 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 4027 | keep | 0 | Aug | 2022 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
FAJARDO | 2022-08-08 03:31 | 2022-08-09 10:04 | 7 | 30:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE AJUSTO UN HOT CLAMP | R22080800066 | New_Event | Primary Wire Break | Include | Include | Equipment | 1833 | 2022-08-08 | 12831 | keep | 0 | Aug | 2022 | 0.0087391 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-08-08 04:35 | 2022-08-08 11:26 | 9 | 6:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5 KVA @ 4 KV POR UNO DE LA MISMA CAPACIDAD. | A22080700407 | New_Event | Service Transformer Failure | Include | Include | Equipment | 411 | 2022-08-08 | 3699 | keep | 0 | Aug | 2022 | 0.0025194 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-08-08 04:41 | 2022-08-08 11:15 | 18 | 6:34 | P | NO SE REPORTO CAUSA | 1X40 EN CL | R22080700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 394 | 2022-08-08 | 7092 | keep | 0 | Aug | 2022 | 0.0048303 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2022-08-08 04:41 | 2022-08-08 17:38 | 56 | 12:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | R22080800042 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 777 | 2022-08-08 | 43512 | keep | 0 | Aug | 2022 | 0.029636 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
ARECIBO | 2022-08-08 05:09 | 2022-08-08 08:38 | 20 | 3:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080700409 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-08-08 | 4180 | keep | 0 | Aug | 2022 | 0.002847 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-08 05:49 | 2022-08-08 09:45 | 100 | 3:56 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080700410 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 236 | 2022-08-08 | 23600 | keep | 0 | Aug | 2022 | 0.016074 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-08 05:50 | 2022-08-08 09:50 | 30 | 4:00 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080700411 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 240 | 2022-08-08 | 7200 | keep | 0 | Aug | 2022 | 0.0049039 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-08 05:52 | 2022-08-08 09:00 | 14 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER HACIA XMR NO CAUSA | B22080800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-08-08 | 2632 | keep | 0 | Aug | 2022 | 0.0017926 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-08-08 06:10 | 2022-08-08 10:48 | 50 | 4:38 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CORTE DE LINEA SE REPARO BAJANTE ZAFADO EN CORTE DE LINEA | M22080800019 | New_Event | Primary Wire Break | Include | Include | Equipment | 278 | 2022-08-08 | 13900 | keep | 0 | Aug | 2022 | 0.0094672 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-08 06:18 | 2022-08-08 06:20 | 1862 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-08 | 3724 | keep | 0 | Aug | 2022 | 0.0025364 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2022-08-08 06:18 | 2022-08-08 06:20 | 1613 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-08 | 3226 | keep | 0 | Aug | 2022 | 0.0021972 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2022-08-08 06:18 | 2022-08-08 06:20 | 1448 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22080800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-08 | 2896 | keep | 0 | Aug | 2022 | 0.0019725 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
CANOVANAS | 2022-08-08 06:18 | 2022-08-08 06:19 | 3699 | 0:01 | T | DESGANCHE | RECIERRE | R22080800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-08 | 3699 | keep | 0 | Aug | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2022-08-08 06:19 | 2022-08-08 12:59 | 65 | 6:40 | P | DESGANCHE | 1 X 50 EN RISER Y 1 X 80 EN C/L DESGANCHE | R22080700049 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 400 | 2022-08-08 | 26000 | keep | 0 | Aug | 2022 | 0.017708 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-08-08 06:21 | 2022-08-08 15:27 | 4 | 9:06 | P | ANIMAL | 1 X 15 EN XMR CRUCE X REPTIL | C22080700349 | New_Event | Animals | Include | Include | Wildlife | 546 | 2022-08-08 | 2184 | keep | 0 | Aug | 2022 | 0.0014875 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-08-08 06:37 | 2022-08-08 09:06 | 6 | 2:29 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25AMP NO CAUSA | C22080700352 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-08-08 | 894 | keep | 0 | Aug | 2022 | 0.0006089 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-08-08 06:45 | 2022-08-09 08:30 | 108 | 25:45 | P | ARBOL SOBRE LINEA | SE ABRE CORTE DE LINEA PARA RETIRAR ARBOL DE LINEA | P22080800179 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1545 | 2022-08-08 | 166860 | keep | 0 | Aug | 2022 | 0.11365 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
CANOVANAS | 2022-08-08 06:47 | 2022-08-08 13:48 | 9 | 7:01 | P | DESGANCHE | 1 X15 EN XMR Y DESGANCHE | R22080700046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2022-08-08 | 3789 | keep | 0 | Aug | 2022 | 0.0025807 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-08-08 06:54 | 2022-08-08 10:25 | 30 | 3:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M22080800026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 211 | 2022-08-08 | 6330 | keep | 0 | Aug | 2022 | 0.0043113 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-08 07:06 | 2022-08-08 09:55 | 10 | 2:49 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B22080800005 | New_Event | Animals | Include | Include | Wildlife | 169 | 2022-08-08 | 1690 | keep | 0 | Aug | 2022 | 0.0011511 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-08 07:21 | 2022-08-08 11:30 | 20 | 4:09 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B22080800007 | New_Event | Animals | Include | Include | Wildlife | 249 | 2022-08-08 | 4980 | keep | 0 | Aug | 2022 | 0.0033919 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-08 07:21 | 2022-08-08 10:04 | 221 | 2:43 | P | ANIMAL | 1 X 40 Y 1 X 50 EN C/LS CRUCE X AVE | C22080700356 | New_Event | Animals | Include | Include | Wildlife | 163 | 2022-08-08 | 36023 | keep | 0 | Aug | 2022 | 0.024535 | 0.00015052 | Sustained | FALSE | FALSE | Not_TMED_Event | 221
MAYAGÃœEZ | 2022-08-08 07:34 | 2022-08-08 12:02 | 2 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR FUERTES VIENTOS | M22080800039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2022-08-08 | 536 | keep | 0 | Aug | 2022 | 0.00036507 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-08-08 07:45 | 2022-08-08 07:46 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 1702 | keep | 0 | Aug | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
BARRANQUITAS | 2022-08-08 07:45 | 2022-08-08 15:06 | 12 | 7:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L FUERTES LLUVIAS | C22080700360 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 441 | 2022-08-08 | 5292 | keep | 0 | Aug | 2022 | 0.0036044 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-08 07:46 | 2022-08-08 17:15 | 2 | 9:29 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080800007 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 569 | 2022-08-08 | 1138 | keep | 0 | Aug | 2022 | 0.00077509 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-08-08 07:55 | 2022-08-08 12:05 | 40 | 4:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22080800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2022-08-08 | 10000 | keep | 0 | Aug | 2022 | 0.006811 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-08 08:11 | 2022-08-08 08:12 | 4085 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | R22080800000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-08 | 4085 | keep | 0 | Aug | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
VEGA BAJA | 2022-08-08 08:11 | 2022-08-08 12:35 | 70 | 4:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE LEVANTO CONDUCTOR Y SE REMPLAZO AISLADOR | B22080800008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 264 | 2022-08-08 | 18480 | keep | 0 | Aug | 2022 | 0.012587 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-08-08 08:12 | 2022-08-08 14:45 | 30 | 6:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE LEVANTO CONDUCTOR DEL SUELO | R22080800056 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 393 | 2022-08-08 | 11790 | keep | 0 | Aug | 2022 | 0.0080301 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-08 08:16 | 2022-08-08 15:30 | 15 | 7:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080800056 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 434 | 2022-08-08 | 6510 | keep | 0 | Aug | 2022 | 0.0044339 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-08 08:19 | 2022-08-08 11:49 | 50 | 3:30 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080800014 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 210 | 2022-08-08 | 10500 | keep | 0 | Aug | 2022 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-08 08:21 | 2022-08-08 19:15 | 6 | 10:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R22080800053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 654 | 2022-08-08 | 3924 | keep | 0 | Aug | 2022 | 0.0026726 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-08 08:26 | 2022-08-08 12:38 | 5 | 4:12 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | C22080800007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 252 | 2022-08-08 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-08 08:36 | 2022-08-08 08:37 | 1228 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 1228 | keep | 0 | Aug | 2022 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
AGUADILLA | 2022-08-08 08:38 | 2022-08-08 14:36 | 80 | 5:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080800018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 358 | 2022-08-08 | 28640 | keep | 0 | Aug | 2022 | 0.019507 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-08 08:42 | 2022-08-08 15:30 | 30 | 6:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080800073 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 408 | 2022-08-08 | 12240 | keep | 0 | Aug | 2022 | 0.0083366 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-08 08:43 | 2022-08-08 14:14 | 20 | 5:31 | P | ANIMAL | REEMPLAZO DE PORTA FUSIBLE Y 1 X 40 EN C/L AVE | S22080800008 | New_Event | Animals | Include | Include | Wildlife | 331 | 2022-08-08 | 6620 | keep | 0 | Aug | 2022 | 0.0045089 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-08 08:46 | 2022-08-08 08:47 | 411 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080800075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 411 | keep | 0 | Aug | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
HUMACAO | 2022-08-08 08:47 | 2022-08-08 08:48 | 1891 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 1891 | keep | 0 | Aug | 2022 | 0.001288 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-08-08 08:47 | 2022-08-08 08:48 | 1250 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2901-04 | C22080800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 1250 | keep | 0 | Aug | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-08-08 08:47 | 2022-08-08 08:48 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2901-02 | C22080800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 1827 | keep | 0 | Aug | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
MAYAGÃœEZ | 2022-08-08 08:47 | 2022-08-08 12:00 | 400 | 3:13 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M22080700173 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 193 | 2022-08-08 | 77200 | keep | 0 | Aug | 2022 | 0.052581 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-08 08:55 | 2022-08-08 17:35 | 15 | 8:40 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080800024 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 520 | 2022-08-08 | 7800 | keep | 0 | Aug | 2022 | 0.0053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-08-08 08:57 | 2022-08-08 15:25 | 30 | 6:28 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL T12 AL T11 SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE AL T11 | R22080600026 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 388 | 2022-08-08 | 11640 | keep | 0 | Aug | 2022 | 0.007928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-08 09:01 | 2022-08-08 12:01 | 6 | 3:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR REPARO SECUNDARIA | C22080800016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 180 | 2022-08-08 | 1080 | keep | 0 | Aug | 2022 | 0.00073558 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-08 09:05 | 2022-08-08 18:27 | 1 | 9:22 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO XMR | S22080800010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 562 | 2022-08-08 | 562 | keep | 0 | Aug | 2022 | 0.00038278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-08 09:06 | 2022-08-08 10:36 | 1 | 1:30 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C22080800017 | New_Event | Animals | Include | Include | Wildlife | 90 | 2022-08-08 | 90 | keep | 0 | Aug | 2022 | 6.1299e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-08 09:13 | 2022-08-08 11:45 | 6 | 2:32 | P | ANIMAL | 1 X 15 EN XMR CULEBRA EN PORTA FUSIBLE | P22080800002 | New_Event | Animals | Include | Include | Wildlife | 152 | 2022-08-08 | 912 | keep | 0 | Aug | 2022 | 0.00062116 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-08 09:16 | 2022-08-08 12:38 | 15 | 3:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO CAJA PRIMARIA | R22080700059 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2022-08-08 | 3030 | keep | 0 | Aug | 2022 | 0.0020637 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-08 09:32 | 2022-08-08 11:10 | 150 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 Y 1 X 40 EN DIFERENTES CORTES DE LINEA FUERTES VIENTOS | M22080800095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2022-08-08 | 14700 | keep | 0 | Aug | 2022 | 0.010012 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-08-08 09:33 | 2022-08-08 18:24 | 1 | 8:51 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR AVE | P22080800062 | New_Event | Animals | Include | Include | Wildlife | 531 | 2022-08-08 | 531 | keep | 0 | Aug | 2022 | 0.00036166 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-08 09:39 | 2022-08-08 12:15 | 1 | 2:36 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080800101 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 156 | 2022-08-08 | 156 | keep | 0 | Aug | 2022 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-08 09:45 | 2022-08-08 14:24 | 1 | 4:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | S22080800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2022-08-08 | 279 | keep | 0 | Aug | 2022 | 0.00019003 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-08 09:54 | 2022-08-08 19:49 | 10 | 9:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080800107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 595 | 2022-08-08 | 5950 | keep | 0 | Aug | 2022 | 0.0040525 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-08 09:57 | 2022-08-08 17:58 | 6 | 8:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON VARIAS CONDICIONES EN LAS LINEAS | R22080800003 | New_Event | Secondary Wire Break | Include | Include | Equipment | 481 | 2022-08-08 | 2886 | keep | 0 | Aug | 2022 | 0.0019656 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-08 10:00 | 2022-08-09 10:07 | 60 | 24:07 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO EN TRONCAL SE ABRIO EL INTERRUPTOR PARA REPARAR | M22080800114 | New_Event | Primary Wire Break | Include | Include | Equipment | 1447 | 2022-08-08 | 86820 | keep | 0 | Aug | 2022 | 0.059133 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-08 10:02 | 2022-08-08 16:21 | 40 | 6:19 | P | CONDUCTOR ROTO O ABIERTO | FIJO BAJANTE PRIMARIO NO FUNDIO | C22080800032 | New_Event | Primary Wire Break | Include | Include | Equipment | 379 | 2022-08-08 | 15160 | keep | 0 | Aug | 2022 | 0.010325 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-08 10:04 | 2022-08-08 14:09 | 1 | 4:05 | P | NO SE REPORTO CAUSA | 1 X 200 EN RISER | S22080800019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2022-08-08 | 245 | keep | 0 | Aug | 2022 | 0.00016687 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-08 10:04 | 2022-08-09 11:00 | 1 | 24:56 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080800117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1496 | 2022-08-08 | 1496 | keep | 0 | Aug | 2022 | 0.0010189 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-08 10:05 | 2022-08-08 13:56 | 4 | 3:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO LAS TRES BARRAS EN PEDESTAL | B22080800016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 231 | 2022-08-08 | 924 | keep | 0 | Aug | 2022 | 0.00062933 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-08-08 10:07 | 2022-08-08 14:57 | 1 | 4:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22080800020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 290 | 2022-08-08 | 290 | keep | 0 | Aug | 2022 | 0.00019752 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-08 10:11 | 2022-08-08 16:20 | 30 | 6:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22080800122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-08-08 | 11070 | keep | 0 | Aug | 2022 | 0.0075397 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-08 10:20 | 2022-08-08 11:35 | 50 | 1:15 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22080800125 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-08-08 | 3750 | keep | 0 | Aug | 2022 | 0.0025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-08 10:38 | 2022-08-08 13:32 | 100 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C22080800042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-08 | 17400 | keep | 0 | Aug | 2022 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-08 10:49 | 2022-08-08 13:14 | 1548 | 2:25 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SU CARGA POR EL 8001-04 | A22080800052 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 145 | 2022-08-08 | 224460 | keep | 0 | Aug | 2022 | 0.15288 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-08-08 10:49 | 2022-08-08 13:14 | 185 | 2:25 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SU CARGA POR EL 8001-04 | A22080800052 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 145 | 2022-08-08 | 26825 | keep | 0 | Aug | 2022 | 0.01827 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-08-08 10:49 | 2022-08-08 13:14 | 9 | 2:25 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE REMPLAZO FUSIBLE EN CIRCUITO DE CONTROL LLEVA LA CARGA DEL 8001-01 Y 8001-03 | A22080800052 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 145 | 2022-08-08 | 1305 | keep | 0 | Aug | 2022 | 0.00088883 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-08-08 10:54 | 2022-08-08 20:51 | 15 | 9:57 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L NO CAUSA | S22080800030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 597 | 2022-08-08 | 8955 | keep | 0 | Aug | 2022 | 0.0060992 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-08 10:56 | 2022-08-08 16:24 | 3 | 5:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22080800141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2022-08-08 | 984 | keep | 0 | Aug | 2022 | 0.0006702 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-08-08 11:17 | 2022-08-08 14:41 | 50 | 3:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | B22080800031 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 204 | 2022-08-08 | 10200 | keep | 0 | Aug | 2022 | 0.0069472 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-08 11:28 | 2022-08-08 14:37 | 20 | 3:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R22080800012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-08-08 | 3780 | keep | 0 | Aug | 2022 | 0.0025745 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-08 11:28 | 2022-08-08 14:37 | 25 | 3:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22080800025 | New_Event | Cutout Failure | Include | Include | Equipment | 189 | 2022-08-08 | 4725 | keep | 0 | Aug | 2022 | 0.0032182 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-08 11:30 | 2022-08-08 20:33 | 15 | 9:03 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22080800068 | New_Event | Primary Wire Break | Include | Include | Equipment | 543 | 2022-08-08 | 8145 | keep | 0 | Aug | 2022 | 0.0055475 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-08-08 11:47 | 2022-08-08 15:40 | 20 | 3:53 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P22080800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-08-08 | 4660 | keep | 0 | Aug | 2022 | 0.0031739 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-08 11:50 | 2022-08-08 15:30 | 50 | 3:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080800076 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 220 | 2022-08-08 | 11000 | keep | 0 | Aug | 2022 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-08 11:53 | 2022-08-08 13:20 | 11 | 1:27 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22080800165 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 87 | 2022-08-08 | 957 | keep | 0 | Aug | 2022 | 0.00065181 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2022-08-08 12:06 | 2022-08-08 15:10 | 10 | 3:04 | P | MAL TIEMPO/RAYOS | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080800078 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 184 | 2022-08-08 | 1840 | keep | 0 | Aug | 2022 | 0.0012532 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-08-08 12:08 | 2022-08-08 14:28 | 60 | 2:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22080800170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-08-08 | 8400 | keep | 0 | Aug | 2022 | 0.0057212 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-08-08 12:11 | 2022-08-08 17:16 | 40 | 5:05 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X 10 EN XMR DESGANCHO | C22080800058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-08-08 | 12200 | keep | 0 | Aug | 2022 | 0.0083094 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-08-08 12:16 | 2022-08-08 12:59 | 8 | 0:43 | P | TRANSFORMADOR AVERIADO | ABRIO XMR PARA REMPLAZAR BUSHING SECUNDARIO | C22080600136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 43 | 2022-08-08 | 344 | keep | 0 | Aug | 2022 | 0.0002343 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-08 12:19 | 2022-08-08 18:50 | 30 | 6:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | B22080800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2022-08-08 | 11730 | keep | 0 | Aug | 2022 | 0.0079892 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-08 12:25 | 2022-08-08 16:00 | 25 | 3:35 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080800081 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 215 | 2022-08-08 | 5375 | keep | 0 | Aug | 2022 | 0.0036609 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-08 12:27 | 2022-08-08 14:38 | 12 | 2:11 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR, SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | B22080700471 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 131 | 2022-08-08 | 1572 | keep | 0 | Aug | 2022 | 0.0010707 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-08 12:30 | 2022-08-08 14:41 | 11 | 2:11 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22080800020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-08-08 | 1441 | keep | 0 | Aug | 2022 | 0.00098146 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2022-08-08 12:32 | 2022-08-08 14:30 | 1 | 1:58 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080800082 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 118 | 2022-08-08 | 118 | keep | 0 | Aug | 2022 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-08 12:33 | 2022-08-08 15:30 | 1 | 2:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 3 CAJAS PRIMARIAS Y SE LEVANTO NEUTRAL PRIMARIO | B22080800038 | New_Event | Cutout Failure | Include | Include | Equipment | 177 | 2022-08-08 | 177 | keep | 0 | Aug | 2022 | 0.00012055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-08 12:38 | 2022-08-08 17:00 | 75 | 4:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE MASIVO | A22080800083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-08-08 | 19650 | keep | 0 | Aug | 2022 | 0.013384 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-08-08 12:39 | 2022-08-08 15:11 | 10 | 2:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REPARO BAJANTE SECUNDARIO | C22080800065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 152 | 2022-08-08 | 1520 | keep | 0 | Aug | 2022 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-08 12:44 | 2022-08-08 18:28 | 200 | 5:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100, 2 X 80, 2 X 30 Y 1 X 25 EN CORTES DE LINEA DISTINTOS MAL TIEMPO VIENTOS FUERTES | M22080800187 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 344 | 2022-08-08 | 68800 | keep | 0 | Aug | 2022 | 0.046859 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-08 12:46 | 2022-08-08 18:30 | 23 | 5:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES SECUNDARIO QUEMADOS | R22080800022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 344 | 2022-08-08 | 7912 | keep | 0 | Aug | 2022 | 0.0053888 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2022-08-08 12:58 | 2022-08-08 13:41 | 13 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C22080800067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2022-08-08 | 559 | keep | 0 | Aug | 2022 | 0.00038073 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
GUAYAMA | 2022-08-08 13:00 | 2022-08-08 14:25 | 3 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR CONEXIONES EN PEDESTAL | P22080800021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2022-08-08 | 255 | keep | 0 | Aug | 2022 | 0.00017368 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-08 13:01 | 2022-08-08 13:02 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 1825 | keep | 0 | Aug | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
UTUADO | 2022-08-08 13:13 | 2022-08-08 16:30 | 70 | 3:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22080800092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-08-08 | 13790 | keep | 0 | Aug | 2022 | 0.0093923 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-08-08 13:14 | 2022-08-08 15:37 | 30 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080800095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2022-08-08 | 4290 | keep | 0 | Aug | 2022 | 0.0029219 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-08 13:14 | 2022-08-08 21:04 | 1 | 7:50 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYO | B22080800040 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 470 | 2022-08-08 | 470 | keep | 0 | Aug | 2022 | 0.00032011 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-08 13:21 | 2022-08-08 13:31 | 7 | 0:10 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C22080800072 | New_Event | Animals | Include | Include | Wildlife | 10 | 2022-08-08 | 70 | keep | 0 | Aug | 2022 | 4.7677e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-08-08 13:24 | 2022-08-08 16:21 | 75 | 2:57 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22080800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-08-08 | 13275 | keep | 0 | Aug | 2022 | 0.0090415 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-08-08 13:29 | 2022-08-08 17:10 | 5 | 3:41 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | C22080800076 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 221 | 2022-08-08 | 1105 | keep | 0 | Aug | 2022 | 0.00075261 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-08-08 13:51 | 2022-08-08 16:32 | 1 | 2:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | P22080800025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 161 | 2022-08-08 | 161 | keep | 0 | Aug | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-08 14:01 | 2022-08-08 16:08 | 5 | 2:07 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN C/L Y DESGANCHE | B22080800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-08-08 | 635 | keep | 0 | Aug | 2022 | 0.0004325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-08 14:03 | 2022-08-08 19:07 | 200 | 5:04 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 Y 1 X 100 EN CORTES DE LINEA SE LEVANTARON LINEAS PRIMARIAS PARTIDAS, SE REMPLAZO AISLACION | B22080800051 | New_Event | Primary Wire Break | Include | Include | Equipment | 304 | 2022-08-08 | 60800 | keep | 0 | Aug | 2022 | 0.041411 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-08 14:10 | 2022-08-08 16:12 | 152 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 5O EN C/L NO CAUSA | B22080800056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-08-08 | 18544 | keep | 0 | Aug | 2022 | 0.01263 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
CAGUAS | 2022-08-08 14:11 | 2022-08-08 14:35 | 1 | 0:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA NO FUNDIO | C22080800080 | New_Event | Primary Wire Break | Include | Include | Equipment | 24 | 2022-08-08 | 24 | keep | 0 | Aug | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-08 14:11 | 2022-08-08 18:05 | 2 | 3:54 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080800101 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 234 | 2022-08-08 | 468 | keep | 0 | Aug | 2022 | 0.00031875 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-08 14:17 | 2022-08-08 19:25 | 85 | 5:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA EN XMR. 1 X 40 Y 1 X 50 EN C/L | B22080800062 | New_Event | Primary Wire Break | Include | Include | Equipment | 308 | 2022-08-08 | 26180 | keep | 0 | Aug | 2022 | 0.017831 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2022-08-08 14:20 | 2022-08-08 16:35 | 400 | 2:15 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080800217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-08-08 | 54000 | keep | 0 | Aug | 2022 | 0.036779 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-08-08 14:25 | 2022-08-08 14:26 | 8680 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 85% DE SU CARGA POR EL 1206-03 | S22080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 8680 | keep | 0 | Aug | 2022 | 0.0059119 | 0.0059119 | Momentary | FALSE | FALSE | Not_TMED_Event | 8680
SAN JUAN | 2022-08-08 14:25 | 2022-08-08 14:26 | 3720 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 10% DE SU CARGA POR EL 1620-02 Y LLEVA EL 85% DEL 1204-05 | S22080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 3720 | keep | 0 | Aug | 2022 | 0.0025337 | 0.0025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 3720
FAJARDO | 2022-08-08 14:25 | 2022-08-08 15:24 | 1 | 0:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22080800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-08-08 | 59 | keep | 0 | Aug | 2022 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-08 14:25 | 2022-08-09 04:35 | 45 | 14:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22080800218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2022-08-08 | 38250 | keep | 0 | Aug | 2022 | 0.026052 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-08-08 14:25 | 2022-08-08 18:50 | 1 | 4:25 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L Y 1 X 15 EN XMR ELIMINO PARARRAYO | C22080800082 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 265 | 2022-08-08 | 265 | keep | 0 | Aug | 2022 | 0.00018049 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-08 14:28 | 2022-08-09 22:36 | 2 | 32:08 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR POR RAYO | M22080800223 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1928 | 2022-08-08 | 3856 | keep | 0 | Aug | 2022 | 0.0026263 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-08-08 14:36 | 2022-08-08 18:17 | 50 | 3:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE MASIVO | A22080800109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-08-08 | 11050 | keep | 0 | Aug | 2022 | 0.0075261 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-08 14:37 | 2022-08-08 15:45 | 1 | 1:08 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22080800110 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 68 | 2022-08-08 | 68 | keep | 0 | Aug | 2022 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-08 14:43 | 2022-08-08 16:04 | 12 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR SECUNDARIA | C22080800086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2022-08-08 | 972 | keep | 0 | Aug | 2022 | 0.00066202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-08 14:45 | 2022-08-08 19:20 | 25 | 4:35 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22080800114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2022-08-08 | 6875 | keep | 0 | Aug | 2022 | 0.0046825 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-08 14:48 | 2022-08-08 17:17 | 120 | 2:29 | P | ARBOL SOBRE LINEA | 2 X 80 EN C/L SE RETIRO ARBOL DE ENCIMA DE LA LINEAS | B22080800070 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 149 | 2022-08-08 | 17880 | keep | 0 | Aug | 2022 | 0.012178 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-08-08 14:50 | 2022-08-08 20:14 | 15 | 5:24 | P | DESGANCHE | 1 X 65 EN C/L Y SE REALIZO DESGANCHE | S22080800051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-08-08 | 4860 | keep | 0 | Aug | 2022 | 0.0033101 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-08 14:58 | 2022-08-08 18:43 | 35 | 3:45 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | B22080800078 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 225 | 2022-08-08 | 7875 | keep | 0 | Aug | 2022 | 0.0053636 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2022-08-08 15:00 | 2022-08-08 19:25 | 15 | 4:25 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22080800135 | New_Event | Primary Wire Break | Include | Include | Equipment | 265 | 2022-08-08 | 3975 | keep | 0 | Aug | 2022 | 0.0027074 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-08-08 15:00 | 2022-08-09 10:00 | 30 | 19:00 | P | NO SE REPORTO CAUSA | 1 X 30 Y 1 X 40 EN DIFERENTES CORTES DE LINEA NO SE REPORTO CAUSA | A22080800173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1140 | 2022-08-08 | 34200 | keep | 0 | Aug | 2022 | 0.023293 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-08-08 15:02 | 2022-08-08 18:33 | 72 | 3:31 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE NO FUNDIO | C22080800089 | New_Event | Primary Wire Break | Include | Include | Equipment | 211 | 2022-08-08 | 15192 | keep | 0 | Aug | 2022 | 0.010347 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
CAGUAS | 2022-08-08 15:15 | 2022-08-08 17:50 | 20 | 2:35 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22080800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-08-08 | 3100 | keep | 0 | Aug | 2022 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-08 15:29 | 2022-08-08 18:45 | 80 | 3:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22080800247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-08-08 | 15680 | keep | 0 | Aug | 2022 | 0.01068 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-08 16:07 | 2022-08-08 16:10 | 651 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-08 | 1953 | keep | 0 | Aug | 2022 | 0.0013302 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2022-08-08 16:18 | 2022-08-08 16:19 | 1382 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1706-02 LLEVA 1706-03 | B22080800104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-08 16:18 | 2022-08-08 16:19 | 663 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1706-02 LLEVA 1706-03 | B22080800104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 663 | keep | 0 | Aug | 2022 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
VEGA BAJA | 2022-08-08 16:21 | 2022-08-08 19:05 | 4 | 2:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22080800141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 164 | 2022-08-08 | 656 | keep | 0 | Aug | 2022 | 0.0004468 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-08 16:25 | 2022-08-09 08:49 | 22 | 16:24 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | R22080800045 | New_Event | Primary Wire Break | Include | Include | Equipment | 984 | 2022-08-08 | 21648 | keep | 0 | Aug | 2022 | 0.014744 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
PONCE | 2022-08-08 16:34 | 2022-08-08 17:53 | 200 | 1:19 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22080800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-08-08 | 15800 | keep | 0 | Aug | 2022 | 0.010761 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-08 16:37 | 2022-08-09 08:50 | 20 | 16:13 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L Y SE RETEZO LINEA PRIMARIA | B22080800113 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 973 | 2022-08-08 | 19460 | keep | 0 | Aug | 2022 | 0.013254 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-08-08 16:45 | 2022-08-08 19:20 | 50 | 2:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA BAMBU | P22080800039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2022-08-08 | 7750 | keep | 0 | Aug | 2022 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-08 16:45 | 2022-08-08 17:43 | 70 | 0:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22080800268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-08-08 | 4060 | keep | 0 | Aug | 2022 | 0.0027652 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2022-08-08 16:50 | 2022-08-08 18:58 | 5 | 2:08 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR CRUCE DE FASE POR IGUANA | P22080800041 | New_Event | Animals | Include | Include | Wildlife | 128 | 2022-08-08 | 640 | keep | 0 | Aug | 2022 | 0.0004359 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-08 16:52 | 2022-08-08 22:55 | 50 | 6:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE MASIVO | M22080800271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2022-08-08 | 18150 | keep | 0 | Aug | 2022 | 0.012362 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-08 17:10 | 2022-08-08 17:43 | 7 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA | B22080800041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2022-08-08 | 231 | keep | 0 | Aug | 2022 | 0.00015733 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-08 17:17 | 2022-08-08 22:13 | 33 | 4:56 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR SE FIJO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S22080800058 | New_Event | Primary Wire Break | Include | Include | Equipment | 296 | 2022-08-08 | 9768 | keep | 0 | Aug | 2022 | 0.0066529 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
HUMACAO | 2022-08-08 17:23 | 2022-08-08 17:24 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
CAGUAS | 2022-08-08 17:36 | 2022-08-08 20:39 | 45 | 3:03 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L LEVANTO CONDUCTOR | C22080800114 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2022-08-08 | 8235 | keep | 0 | Aug | 2022 | 0.0056088 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-08-08 17:40 | 2022-08-08 19:42 | 13 | 2:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C22080700350 | New_Event | Secondary Wire Break | Include | Include | Equipment | 122 | 2022-08-08 | 1586 | keep | 0 | Aug | 2022 | 0.0010802 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2022-08-08 17:42 | 2022-08-08 17:43 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22080800145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 2697 | keep | 0 | Aug | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2022-08-08 17:55 | 2022-08-08 21:50 | 75 | 3:55 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA CRUZADA CON NEUTRAL | A22080800147 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 235 | 2022-08-08 | 17625 | keep | 0 | Aug | 2022 | 0.012004 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-08-08 18:11 | 2022-08-08 19:41 | 9 | 1:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA EN XMR | B22080800123 | New_Event | Primary Wire Break | Include | Include | Equipment | 90 | 2022-08-08 | 810 | keep | 0 | Aug | 2022 | 0.00055169 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2022-08-08 18:40 | 2022-08-08 19:41 | 10 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR(PM) PARA REEMPLAZAR BARRAS SECUNDARIAS | M22080800302 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2022-08-08 | 610 | keep | 0 | Aug | 2022 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-08 18:44 | 2022-08-08 22:04 | 15 | 3:20 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA GLOBO CRUZO FASE | S22080800072 | New_Event | Damage From Public | Include | Include | Public | 200 | 2022-08-08 | 3000 | keep | 0 | Aug | 2022 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-08-08 19:01 | 2022-08-08 21:16 | 1979 | 2:15 | S | PROTECCION DEFECTUOSA | DISPARO RING BUS CANAS TC AVERIA EN 5018-04 | P22080800071 | New_Event | Protection Miscoordination | Include | Include | Other | 135 | 2022-08-08 | 267165 | keep | 0 | Aug | 2022 | 0.18196 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2022-08-08 19:01 | 2022-08-08 21:16 | 3114 | 2:15 | S | PROTECCION DEFECTUOSA | DISPARO RING BUS CANAS TC AVERIA EN 5018-04 | P22080800071 | New_Event | Protection Miscoordination | Include | Include | Other | 135 | 2022-08-08 | 420390 | keep | 0 | Aug | 2022 | 0.28633 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-08-08 19:01 | 2022-08-08 21:16 | 5069 | 2:15 | S | PROTECCION DEFECTUOSA | DISPARO RING BUS CANAS TC AVERIA EN 5018-04 | P22080800071 | New_Event | Protection Miscoordination | Include | Include | Other | 135 | 2022-08-08 | 684315 | keep | 0 | Aug | 2022 | 0.46608 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2022-08-08 19:01 | 2022-08-08 21:16 | 2696 | 2:15 | S | PROTECCION DEFECTUOSA | DISPARO RING BUS CANAS TC AVERIA EN 5018-04 | P22080800071 | New_Event | Protection Miscoordination | Include | Include | Other | 135 | 2022-08-08 | 363960 | keep | 0 | Aug | 2022 | 0.24789 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2022-08-08 19:01 | 2022-08-08 21:16 | 5063 | 2:15 | S | PROTECCION DEFECTUOSA | DISPARO RING BUS CANAS TC AVERIA EN 5018-04 | P22080800071 | New_Event | Protection Miscoordination | Include | Include | Other | 135 | 2022-08-08 | 683505 | keep | 0 | Aug | 2022 | 0.46553 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
UTUADO | 2022-08-08 19:33 | 2022-08-08 20:15 | 7 | 0:42 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22080800172 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 42 | 2022-08-08 | 294 | keep | 0 | Aug | 2022 | 0.00020024 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-08 19:35 | 2022-08-09 12:55 | 15 | 17:20 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22080800308 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1040 | 2022-08-08 | 15600 | keep | 0 | Aug | 2022 | 0.010625 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-08 20:12 | 2022-08-08 21:02 | 50 | 0:50 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO | C22080800137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-08-08 | 2500 | keep | 0 | Aug | 2022 | 0.0017027 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-08 20:14 | 2022-08-09 00:33 | 300 | 4:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080800312 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 259 | 2022-08-08 | 77700 | keep | 0 | Aug | 2022 | 0.052921 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-08 20:37 | 2022-08-08 23:07 | 260 | 2:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | B22080800135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-08-08 | 39000 | keep | 0 | Aug | 2022 | 0.026563 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
PONCE | 2022-08-08 20:43 | 2022-08-08 22:58 | 300 | 2:15 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P22080800148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-08-08 | 40500 | keep | 0 | Aug | 2022 | 0.027584 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2022-08-08 20:45 | 2022-08-08 22:36 | 100 | 1:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | B22080800137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2022-08-08 | 11100 | keep | 0 | Aug | 2022 | 0.0075602 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-08-08 20:55 | 2022-08-09 07:50 | 65 | 10:55 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/LS DESGANCHO Y ENDEREZO CAJA | C22080800146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 655 | 2022-08-08 | 42575 | keep | 0 | Aug | 2022 | 0.028998 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
GUAYAMA | 2022-08-08 21:04 | 2022-08-08 21:24 | 12 | 0:20 | P | CAUSAS EXTERNAS | 1 X 20 EN TRANSFORMADOR CAMION ARRANCA TOMA SECUNDARIA | P22080800068 | New_Event | Damage From Public | Include | Include | Public | 20 | 2022-08-08 | 240 | keep | 0 | Aug | 2022 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-08 21:05 | 2022-08-09 16:00 | 8 | 18:55 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS POR TENSOR | M22080800192 | New_Event | Damage From Public | Include | Include | Public | 1135 | 2022-08-08 | 9080 | keep | 0 | Aug | 2022 | 0.0061843 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-08-08 21:16 | 2022-08-08 21:29 | 3114 | 0:13 | T | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARRAYO DE SALIDA AMARRE 5018-02 Y 5018-04 Y SE COLOCO INTERRUPTOR EN SERVICIO | P22080800065 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 13 | 2022-08-08 | 40482 | keep | 0 | Aug | 2022 | 0.027572 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2022-08-08 21:16 | 2022-08-08 21:29 | 2696 | 0:13 | T | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARRAYO DE SALIDA AMARRE 5018-02 Y 5018-04 Y SE COLOCO INTERRUPTOR EN SERVICIO | P22080800065 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 13 | 2022-08-08 | 35048 | keep | 0 | Aug | 2022 | 0.023871 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2022-08-08 21:52 | 2022-08-09 10:10 | 10 | 12:18 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 25 KVA A 7620VOLTS AVERIADO | P22080800178 | New_Event | Service Transformer Failure | Include | Include | Equipment | 738 | 2022-08-08 | 7380 | keep | 0 | Aug | 2022 | 0.0050265 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-08 22:00 | 2022-08-09 14:45 | 8 | 16:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTE PRIMARIO | M22080800289 | New_Event | Primary Wire Break | Include | Include | Equipment | 1005 | 2022-08-08 | 8040 | keep | 0 | Aug | 2022 | 0.005476 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-08 23:38 | 2022-08-09 15:30 | 5 | 15:52 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22080800338 | New_Event | Primary Wire Break | Include | Include | Equipment | 952 | 2022-08-08 | 4760 | keep | 0 | Aug | 2022 | 0.003242 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-08 23:56 | 2022-08-08 23:57 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080800156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-08 | 2234 | keep | 0 | Aug | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2022-08-09 00:16 | 2022-08-09 10:30 | 80 | 10:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22080800340 | New_Event | Cutout Failure | Include | Include | Equipment | 614 | 2022-08-09 | 49120 | keep | 0 | Aug | 2022 | 0.033455 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-09 00:44 | 2022-08-09 00:45 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 2402 | keep | 0 | Aug | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
AGUADILLA | 2022-08-09 01:13 | 2022-08-10 01:14 | 50 | 24:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA | A22080900314 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1441 | 2022-08-09 | 72050 | keep | 0 | Aug | 2022 | 0.049073 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-09 02:06 | 2022-08-09 02:07 | 1457 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22080900313 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 1457 | keep | 0 | Aug | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
BARRANQUITAS | 2022-08-09 02:10 | 2022-08-09 15:21 | 10 | 13:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REMPLAZO CAJA PARTIDA Y CERRO PUENTE | C22080700342 | New_Event | Cutout Failure | Include | Include | Equipment | 791 | 2022-08-09 | 7910 | keep | 0 | Aug | 2022 | 0.0053875 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-08-09 04:09 | 2022-08-09 11:15 | 8 | 7:06 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | R22080900009 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 426 | 2022-08-09 | 3408 | keep | 0 | Aug | 2022 | 0.0023212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-09 04:34 | 2022-08-09 10:35 | 15 | 6:01 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEAS | M22080800341 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2022-08-09 | 5415 | keep | 0 | Aug | 2022 | 0.0036881 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-08-09 04:36 | 2022-08-09 04:39 | 2126 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-09 | 6378 | keep | 0 | Aug | 2022 | 0.004344 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CAGUAS | 2022-08-09 04:42 | 2022-08-09 06:16 | 215 | 1:34 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C22080800156 | New_Event | Animals | Include | Include | Wildlife | 94 | 2022-08-09 | 20210 | keep | 0 | Aug | 2022 | 0.013765 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
BARRANQUITAS | 2022-08-09 05:02 | 2022-08-09 07:31 | 44 | 2:29 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22080800159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-08-09 | 6556 | keep | 0 | Aug | 2022 | 0.0044653 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2022-08-09 05:08 | 2022-08-10 07:43 | 50 | 26:35 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA SE RETIRO CULEBRA QUE CRUZO FASE A TIERRA | A22080900334 | New_Event | Animals | Include | Include | Wildlife | 1595 | 2022-08-09 | 79750 | keep | 0 | Aug | 2022 | 0.054317 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-09 05:37 | 2022-08-09 08:45 | 17 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | B22080900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-08-09 | 3196 | keep | 0 | Aug | 2022 | 0.0021768 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
UTUADO | 2022-08-09 06:00 | 2022-08-09 13:42 | 1 | 7:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA | A22080900030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 462 | 2022-08-09 | 462 | keep | 0 | Aug | 2022 | 0.00031467 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-09 06:22 | 2022-08-09 08:00 | 150 | 1:38 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA NO CAUSA | P22080800203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-08-09 | 14700 | keep | 0 | Aug | 2022 | 0.010012 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-09 06:27 | 2022-08-09 10:58 | 25 | 4:31 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN XMR SE REALIZO DESGANCHE Y SE RETEZO LINEA SEC | B22080900004 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 271 | 2022-08-09 | 6775 | keep | 0 | Aug | 2022 | 0.0046144 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-09 06:45 | 2022-08-09 10:21 | 40 | 3:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO VIENTO | B22080900005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 216 | 2022-08-09 | 8640 | keep | 0 | Aug | 2022 | 0.0058847 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-09 07:03 | 2022-08-09 09:34 | 25 | 2:31 | P | DESGANCHE | 1 X 50 EN C/L | C22080800171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-08-09 | 3775 | keep | 0 | Aug | 2022 | 0.0025711 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-09 07:06 | 2022-08-09 07:07 | 1818 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22080900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 1818 | keep | 0 | Aug | 2022 | 0.0012382 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
CAGUAS | 2022-08-09 07:11 | 2022-08-09 07:51 | 4 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22080800172 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2022-08-09 | 160 | keep | 0 | Aug | 2022 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-08-09 07:23 | 2022-08-09 10:23 | 80 | 3:00 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22080800174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-08-09 | 14400 | keep | 0 | Aug | 2022 | 0.0098078 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-09 07:27 | 2022-08-09 09:33 | 30 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | B22080900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-08-09 | 3780 | keep | 0 | Aug | 2022 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-09 07:56 | 2022-08-09 19:23 | 10 | 11:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA EN VARIOS PUNTOS 1 X 20 EN TRANSFORMADOR | S22080900370 | New_Event | Secondary Wire Break | Include | Include | Equipment | 687 | 2022-08-09 | 6870 | keep | 0 | Aug | 2022 | 0.0046791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-09 08:15 | 2022-08-09 09:55 | 2 | 1:40 | P | OTRAS CAUSAS | SE ABRIO RISER PARA REPARAR CONECTOR QUEMADO | A22080900013 | New_Event | Other Causes | Include | Include | Other | 100 | 2022-08-09 | 200 | keep | 0 | Aug | 2022 | 0.00013622 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-09 08:24 | 2022-08-09 11:00 | 1 | 2:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22080900013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 156 | 2022-08-09 | 156 | keep | 0 | Aug | 2022 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-09 08:30 | 2022-08-09 09:47 | 1 | 1:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO MASETILLA QUEMADA | A22080900017 | New_Event | Cutout Failure | Include | Include | Equipment | 77 | 2022-08-09 | 77 | keep | 0 | Aug | 2022 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-09 08:35 | 2022-08-09 10:27 | 12 | 1:52 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | C22080800187 | New_Event | Animals | Include | Include | Wildlife | 112 | 2022-08-09 | 1344 | keep | 0 | Aug | 2022 | 0.00091539 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-09 08:35 | 2022-08-09 14:25 | 6 | 5:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080900017 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 350 | 2022-08-09 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-08-09 08:38 | 2022-08-09 08:39 | 4085 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | R22080900077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-09 | 4085 | keep | 0 | Aug | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-08-09 08:39 | 2022-08-09 13:00 | 10 | 4:21 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22080800080 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-08-09 | 2610 | keep | 0 | Aug | 2022 | 0.0017777 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-09 08:39 | 2022-08-09 11:08 | 1 | 2:29 | P | ANIMAL | 1 X 8 CRUCE X AVE | C22080800189 | New_Event | Animals | Include | Include | Wildlife | 149 | 2022-08-09 | 149 | keep | 0 | Aug | 2022 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-09 08:41 | 2022-08-09 14:22 | 22 | 5:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22080800060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 341 | 2022-08-09 | 7502 | keep | 0 | Aug | 2022 | 0.0051096 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
UTUADO | 2022-08-09 08:53 | 2022-08-09 08:54 | 3502 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | A22080900020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 3502 | keep | 0 | Aug | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
CAGUAS | 2022-08-09 08:55 | 2022-08-09 08:57 | 125 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-09 | 250 | keep | 0 | Aug | 2022 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-08-09 08:55 | 2022-08-09 08:56 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 1342 | keep | 0 | Aug | 2022 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
BARRANQUITAS | 2022-08-09 08:58 | 2022-08-09 11:52 | 12 | 2:54 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR | C22080900006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 174 | 2022-08-09 | 2088 | keep | 0 | Aug | 2022 | 0.0014221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-08-09 09:00 | 2022-08-09 13:03 | 1 | 4:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | A22080900058 | New_Event | Primary Wire Break | Include | Include | Equipment | 243 | 2022-08-09 | 243 | keep | 0 | Aug | 2022 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-09 09:04 | 2022-08-09 13:00 | 1 | 3:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA FUERTES VIENTOS | A22080900023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 236 | 2022-08-09 | 236 | keep | 0 | Aug | 2022 | 0.00016074 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-09 09:06 | 2022-08-09 18:20 | 8 | 9:14 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22080900028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 554 | 2022-08-09 | 4432 | keep | 0 | Aug | 2022 | 0.0030186 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-09 09:08 | 2022-08-09 11:05 | 20 | 1:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FUERTES VIENTOS | M22080900030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 117 | 2022-08-09 | 2340 | keep | 0 | Aug | 2022 | 0.0015938 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-09 09:50 | 2022-08-09 11:20 | 50 | 1:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA QUEMADA | A22080900026 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2022-08-09 | 4500 | keep | 0 | Aug | 2022 | 0.0030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-09 09:53 | 2022-08-09 13:19 | 2 | 3:26 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | R22080900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2022-08-09 | 412 | keep | 0 | Aug | 2022 | 0.00028061 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-09 10:07 | 2022-08-09 11:28 | 2713 | 1:21 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO EL INTERRUPTOR 6001-03 PARA REPARAR PUENTE ABIERTO EN TRONCAL | M22080900079 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 81 | 2022-08-09 | 219753 | keep | 0 | Aug | 2022 | 0.14967 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-09 10:12 | 2022-08-09 10:14 | 2276 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 4552 | keep | 0 | Aug | 2022 | 0.0031003 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-08-09 10:12 | 2022-08-09 10:14 | 777 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 1554 | keep | 0 | Aug | 2022 | 0.0010584 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-08-09 10:12 | 2022-08-09 10:14 | 12 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 24 | keep | 0 | Aug | 2022 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-09 10:12 | 2022-08-09 10:14 | 1290 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 2580 | keep | 0 | Aug | 2022 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
ARECIBO | 2022-08-09 10:12 | 2022-08-09 13:45 | 1 | 3:33 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE | A22080900034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 213 | 2022-08-09 | 213 | keep | 0 | Aug | 2022 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-09 10:15 | 2022-08-09 10:17 | 2276 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 4552 | keep | 0 | Aug | 2022 | 0.0031003 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-08-09 10:15 | 2022-08-09 10:17 | 777 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 1554 | keep | 0 | Aug | 2022 | 0.0010584 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-08-09 10:15 | 2022-08-09 10:17 | 12 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 24 | keep | 0 | Aug | 2022 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-09 10:15 | 2022-08-09 10:17 | 1290 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-09 | 2580 | keep | 0 | Aug | 2022 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2022-08-09 10:21 | 2022-08-09 11:25 | 2276 | 1:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2022-08-09 | 145664 | keep | 0 | Aug | 2022 | 0.099211 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-08-09 10:21 | 2022-08-09 11:25 | 777 | 1:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2022-08-09 | 49728 | keep | 0 | Aug | 2022 | 0.03387 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-08-09 10:21 | 2022-08-09 11:25 | 12 | 1:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2022-08-09 | 768 | keep | 0 | Aug | 2022 | 0.00052308 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-09 10:21 | 2022-08-09 11:25 | 1290 | 1:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22080900017 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2022-08-09 | 82560 | keep | 0 | Aug | 2022 | 0.056231 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
CAGUAS | 2022-08-09 10:23 | 2022-08-09 13:12 | 6 | 2:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C22080900019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 169 | 2022-08-09 | 1014 | keep | 0 | Aug | 2022 | 0.00069063 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-08-09 10:31 | 2022-08-09 10:32 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
FAJARDO | 2022-08-09 10:45 | 2022-08-09 11:30 | 15 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | R22080800079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-08-09 | 675 | keep | 0 | Aug | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-09 10:46 | 2022-08-10 14:45 | 56 | 27:59 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO @ T-12 | B22080900022 | New_Event | UG Cable Fault | Include | Include | Equipment | 1679 | 2022-08-09 | 94024 | keep | 0 | Aug | 2022 | 0.064039 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2022-08-09 11:05 | 2022-08-09 14:38 | 1 | 3:33 | P | ANIMAL | 2 X 50 EN C/L CRUCE POR AVE | B22080900024 | New_Event | Animals | Include | Include | Wildlife | 213 | 2022-08-09 | 213 | keep | 0 | Aug | 2022 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-09 11:10 | 2022-08-09 11:11 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 3070 | keep | 0 | Aug | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
YAUCO | 2022-08-09 11:26 | 2022-08-09 14:27 | 25 | 3:01 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22080900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-08-09 | 4525 | keep | 0 | Aug | 2022 | 0.003082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-08-09 11:32 | 2022-08-09 13:12 | 1 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | REMPLAZO HOT CLAMP | C22080800035 | New_Event | Primary Wire Break | Include | Include | Equipment | 100 | 2022-08-09 | 100 | keep | 0 | Aug | 2022 | 6.811e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-09 11:34 | 2022-08-09 20:10 | 8 | 8:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080900080 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 516 | 2022-08-09 | 4128 | keep | 0 | Aug | 2022 | 0.0028116 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-09 11:44 | 2022-08-09 18:44 | 100 | 7:00 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y 2X 80 EN C/L | B22080900031 | New_Event | Primary Wire Break | Include | Include | Equipment | 420 | 2022-08-09 | 42000 | keep | 0 | Aug | 2022 | 0.028606 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-09 12:14 | 2022-08-09 17:50 | 70 | 5:36 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA POSTE PARTIDO EN LA PERILLA | A22080900055 | New_Event | Primary Pole Failure | Include | Include | Equipment | 336 | 2022-08-09 | 23520 | keep | 0 | Aug | 2022 | 0.016019 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-08-09 12:15 | 2022-08-09 13:35 | 15 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22080900054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2022-08-09 | 1200 | keep | 0 | Aug | 2022 | 0.00081731 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-09 12:26 | 2022-08-09 13:12 | 12 | 0:46 | P | NO SE REPORTO CAUSA | SE REMPLAZO 1X50 EN CL NO CAUSA | S22080900040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-08-09 | 552 | keep | 0 | Aug | 2022 | 0.00037596 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-09 12:26 | 2022-08-09 14:24 | 4 | 1:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22080900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-08-09 | 472 | keep | 0 | Aug | 2022 | 0.00032148 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-08-09 12:36 | 2022-08-09 14:00 | 10 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 40 CORTE DE LINEA NO CAUSA | S22080900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-08-09 | 840 | keep | 0 | Aug | 2022 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-09 12:39 | 2022-08-09 15:25 | 40 | 2:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22080900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-08-09 | 6640 | keep | 0 | Aug | 2022 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-08-09 12:45 | 2022-08-09 13:30 | 5 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22080900090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-08-09 | 225 | keep | 0 | Aug | 2022 | 0.00015325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-09 12:46 | 2022-08-09 19:12 | 30 | 6:26 | P | DESGANCHE | 1 X 50 EN C/ L SE RETIRO PENCA SOBRE LINEA | B22080900033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 386 | 2022-08-09 | 11580 | keep | 0 | Aug | 2022 | 0.0078871 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-08-09 12:48 | 2022-08-09 13:12 | 49 | 0:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZA AISLADO Y SE CIERRA C/L | P22080900021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 24 | 2022-08-09 | 1176 | keep | 0 | Aug | 2022 | 0.00080097 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
BAYAMON | 2022-08-09 13:00 | 2022-08-09 16:58 | 20 | 3:58 | P | CAUSAS EXTERNAS | 1 X 1O EN XMR GLOBO | B22080900037 | New_Event | Damage From Public | Include | Include | Public | 238 | 2022-08-09 | 4760 | keep | 0 | Aug | 2022 | 0.003242 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-09 13:08 | 2022-08-09 18:40 | 12 | 5:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE EN TRANSFORMADOR | M22080900093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 332 | 2022-08-09 | 3984 | keep | 0 | Aug | 2022 | 0.0027135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-09 13:12 | 2022-08-09 13:19 | 4176 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4100 | B22080900122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-09 | 29232 | keep | 0 | Aug | 2022 | 0.01991 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-08-09 13:12 | 2022-08-09 13:19 | 252 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4100 | B22080900122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-09 | 1764 | keep | 0 | Aug | 2022 | 0.0012015 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2022-08-09 13:12 | 2022-08-09 13:19 | 2147 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4100 | B22080900122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-09 | 15029 | keep | 0 | Aug | 2022 | 0.010236 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-08-09 13:12 | 2022-08-09 13:19 | 2858 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4100 | B22080900124 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-09 | 20006 | keep | 0 | Aug | 2022 | 0.013626 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
CAGUAS | 2022-08-09 13:18 | 2022-08-09 14:55 | 8 | 1:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO TRAMO SECUNDARIO SOTERRADO Y BARRAS DE PEDESTAL | C22080700087 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 97 | 2022-08-09 | 776 | keep | 0 | Aug | 2022 | 0.00052853 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-09 13:21 | 2022-08-09 13:35 | 1 | 0:14 | P | CONDUCTOR ROTO O ABIERTO | REMPLAZO HOT CLAMP | C22080800035 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 14 | 2022-08-09 | 14 | keep | 0 | Aug | 2022 | 9.5353e-06 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-09 13:23 | 2022-08-09 13:31 | 12 | 0:08 | P | NO SE REPORTO CAUSA | SE REMPLAZO 1X50 EN CL NO CAUSA | S22080900040 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-08-09 | 96 | keep | 0 | Aug | 2022 | 6.5385e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-09 13:30 | 2022-08-09 15:02 | 6 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C22080900019 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 92 | 2022-08-09 | 552 | keep | 0 | Aug | 2022 | 0.00037596 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-09 13:38 | 2022-08-09 17:18 | 12 | 3:40 | P | NO SE REPORTO CAUSA | SE REMPLAZO 1X50 EN CL NO CAUSA | S22080900040 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 220 | 2022-08-09 | 2640 | keep | 0 | Aug | 2022 | 0.0017981 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-09 13:38 | 2022-08-09 14:10 | 4 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REGULO XMR Y SE REPARO EL BAJANTE SECUNDARIO QUEDO 125/250V | C22080900021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2022-08-09 | 128 | keep | 0 | Aug | 2022 | 8.718e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-08-09 13:50 | 2022-08-09 15:05 | 49 | 1:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZA AISLADO Y SE CIERRA C/L | P22080900021 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 75 | 2022-08-09 | 3675 | keep | 0 | Aug | 2022 | 0.002503 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-09 13:55 | 2022-08-09 15:27 | 10 | 1:32 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE SE RETEZO SECUNDARIA Y SE REPARARON TRES TOMAS. | S22080900045 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 92 | 2022-08-09 | 920 | keep | 0 | Aug | 2022 | 0.00062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-09 13:56 | 2022-08-09 13:57 | 1448 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22080900058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 1448 | keep | 0 | Aug | 2022 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
ARECIBO | 2022-08-09 13:56 | 2022-08-09 15:07 | 1548 | 1:11 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 8001-04 EL CUAL ESTA LLEVANDO LA CARGA DEL 8001-01 POR FUERTES VIENTOS | A22080900091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2022-08-09 | 109908 | keep | 0 | Aug | 2022 | 0.074858 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-08-09 13:56 | 2022-08-09 15:07 | 185 | 1:11 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 8001-04 EL CUAL ESTA LLEVANDO LA CARGA DEL 8001-03 POR FUERTES VIENTOS | A22080900091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2022-08-09 | 13135 | keep | 0 | Aug | 2022 | 0.0089462 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-08-09 13:56 | 2022-08-09 15:07 | 9 | 1:11 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR POR FUERTES VIENTOS | A22080900091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2022-08-09 | 639 | keep | 0 | Aug | 2022 | 0.00043522 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-08-09 13:58 | 2022-08-09 15:00 | 6 | 1:02 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080900101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-08-09 | 372 | keep | 0 | Aug | 2022 | 0.00025337 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-09 13:59 | 2022-08-09 15:30 | 6 | 1:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R22080900059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 91 | 2022-08-09 | 546 | keep | 0 | Aug | 2022 | 0.00037188 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-09 14:02 | 2022-08-09 15:15 | 7 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R22080900064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2022-08-09 | 511 | keep | 0 | Aug | 2022 | 0.00034804 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-09 14:05 | 2022-08-09 17:22 | 100 | 3:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/.L Y SE REPARO CAJA PRIMARIA | B22080900085 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2022-08-09 | 19700 | keep | 0 | Aug | 2022 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-08-09 14:05 | 2022-08-09 15:54 | 7 | 1:49 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE XMR 50KVA X 50KVA | R22080900067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 109 | 2022-08-09 | 763 | keep | 0 | Aug | 2022 | 0.00051968 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2022-08-09 14:10 | 2022-08-09 17:48 | 65 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L LEVANTO CONDUCTOR | C22080900160 | New_Event | Primary Wire Break | Include | Include | Equipment | 218 | 2022-08-09 | 14170 | keep | 0 | Aug | 2022 | 0.0096511 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
GUAYAMA | 2022-08-09 14:28 | 2022-08-09 17:07 | 30 | 2:39 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 40 EN C/L IGUANA | P22080900107 | New_Event | Animals | Include | Include | Wildlife | 159 | 2022-08-09 | 4770 | keep | 0 | Aug | 2022 | 0.0032488 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-09 14:30 | 2022-08-09 15:14 | 1 | 0:44 | P | CONDUCTOR ROTO O ABIERTO | CERRAR PUENTE ABIERTO EN BANCO DE XMR | R22080900084 | New_Event | Primary Wire Break | Include | Include | Equipment | 44 | 2022-08-09 | 44 | keep | 0 | Aug | 2022 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-09 14:32 | 2022-08-09 15:40 | 8 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REPARO BAJANTE SECUNDARIO | C22080900193 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2022-08-09 | 544 | keep | 0 | Aug | 2022 | 0.00037052 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-09 14:54 | 2022-08-09 18:57 | 150 | 4:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | B22080900116 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 243 | 2022-08-09 | 36450 | keep | 0 | Aug | 2022 | 0.024826 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-08-09 15:05 | 2022-08-09 16:40 | 30 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | A22080900130 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2022-08-09 | 2850 | keep | 0 | Aug | 2022 | 0.0019411 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-09 15:07 | 2022-08-09 19:01 | 1 | 3:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S22080900107 | New_Event | Cutout Failure | Include | Include | Equipment | 234 | 2022-08-09 | 234 | keep | 0 | Aug | 2022 | 0.00015938 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-08-09 15:10 | 2022-08-09 15:52 | 1 | 0:42 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN C/L Y SE RETEZO NEUTRAL | R22080900112 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 42 | 2022-08-09 | 42 | keep | 0 | Aug | 2022 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-09 15:15 | 2022-08-09 15:26 | 22 | 0:11 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE CAJA A XMR | S22080900039 | New_Event | Primary Wire Break | Include | Include | Equipment | 11 | 2022-08-09 | 242 | keep | 0 | Aug | 2022 | 0.00016483 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
VEGA BAJA | 2022-08-09 15:24 | 2022-08-09 17:07 | 100 | 1:43 | P | ANIMAL | 1 X 65 Y 1X 25 EN CORTES DE LINEA POR AVE QUE CRUZO LINEAS | A22080900141 | New_Event | Animals | Include | Include | Wildlife | 103 | 2022-08-09 | 10300 | keep | 0 | Aug | 2022 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-09 15:30 | 2022-08-09 15:40 | 3 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22080900144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2022-08-09 | 30 | keep | 0 | Aug | 2022 | 2.0433e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-09 15:43 | 2022-08-09 18:53 | 150 | 3:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REMPLAZO AISLADOR | S22080900117 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 190 | 2022-08-09 | 28500 | keep | 0 | Aug | 2022 | 0.019411 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-08-09 15:46 | 2022-08-09 15:55 | 1 | 0:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER | R22080900124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-08-09 | 9 | keep | 0 | Aug | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-09 15:56 | 2022-08-09 23:16 | 3 | 7:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN CORTE DE LINEA POR FUERTES VIENTOS | M22080900117 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 440 | 2022-08-09 | 1320 | keep | 0 | Aug | 2022 | 0.00089905 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-08-09 16:04 | 2022-08-09 19:00 | 7 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA MAL TIEMPO | A22080900163 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2022-08-09 | 1232 | keep | 0 | Aug | 2022 | 0.00083911 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-08-09 16:08 | 2022-08-09 18:25 | 32 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22080900293 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-08-09 | 4384 | keep | 0 | Aug | 2022 | 0.0029859 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
VEGA BAJA | 2022-08-09 16:08 | 2022-08-09 18:57 | 30 | 2:49 | P | DESGANCHE | 1 X 30 EN C/L Y SE REALIZO DESGANCHE | B22080900148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-08-09 | 5070 | keep | 0 | Aug | 2022 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-09 16:08 | 2022-08-09 16:34 | 7 | 0:26 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | B22080900149 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 26 | 2022-08-09 | 182 | keep | 0 | Aug | 2022 | 0.00012396 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-09 16:09 | 2022-08-09 17:28 | 12 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | S22080900125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2022-08-09 | 948 | keep | 0 | Aug | 2022 | 0.00064568 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-08-09 16:09 | 2022-08-09 19:03 | 198 | 2:54 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE NO FUNDIO | C22080900294 | New_Event | Primary Wire Break | Include | Include | Equipment | 174 | 2022-08-09 | 34452 | keep | 0 | Aug | 2022 | 0.023465 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
CAGUAS | 2022-08-09 16:10 | 2022-08-09 17:54 | 57 | 1:44 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN C/L AVERIA NUEVA DEL T - 11 AL T -10 / AVERIA VIEJA DEL T - 9 AL T - 10 | C22080900295 | New_Event | UG Cable Fault | Include | Include | Equipment | 104 | 2022-08-09 | 5928 | keep | 0 | Aug | 2022 | 0.0040375 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
ARECIBO | 2022-08-09 16:39 | 2022-08-09 16:56 | 619 | 0:17 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO MANUALMENTE NO RTU | A22080900230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2022-08-09 | 10523 | keep | 0 | Aug | 2022 | 0.0071672 | 0.0004216 | Sustained | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2022-08-09 16:39 | 2022-08-09 16:56 | 243 | 0:17 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO MANUALMENTE NO RTU | A22080900231 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2022-08-09 | 4131 | keep | 0 | Aug | 2022 | 0.0028136 | 0.00016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 243
ARECIBO | 2022-08-09 16:39 | 2022-08-09 16:56 | 2703 | 0:17 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO MANUALMENTE NO RTU | A22080900232 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2022-08-09 | 45951 | keep | 0 | Aug | 2022 | 0.031297 | 0.001841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2703
BAYAMON | 2022-08-09 16:49 | 2022-08-09 18:50 | 30 | 2:01 | P | DESGANCHE | SE CERRO PUENTE ABIERTO Y DESGANCHE 1 X 50 EN C/L | B22080900159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-08-09 | 3630 | keep | 0 | Aug | 2022 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-09 16:53 | 2022-08-09 17:26 | 1 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTORES SECUNDARIO EN SALIDA DE XMR | B22080900160 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2022-08-09 | 33 | keep | 0 | Aug | 2022 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-09 17:05 | 2022-08-10 05:45 | 13 | 12:40 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22080900309 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 760 | 2022-08-09 | 9880 | keep | 0 | Aug | 2022 | 0.0067292 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2022-08-09 17:13 | 2022-08-09 18:43 | 6 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22080900313 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2022-08-09 | 540 | keep | 0 | Aug | 2022 | 0.00036779 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-08-09 17:28 | 2022-08-09 21:40 | 10 | 4:12 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 37.5KVA X 37.5KVA | R22080900132 | New_Event | Service Transformer Failure | Include | Include | Equipment | 252 | 2022-08-09 | 2520 | keep | 0 | Aug | 2022 | 0.0017164 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-09 17:36 | 2022-08-09 19:48 | 6 | 2:12 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22080900315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-08-09 | 792 | keep | 0 | Aug | 2022 | 0.00053943 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2022-08-09 17:36 | 2022-08-09 19:10 | 20 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | P22080900162 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2022-08-09 | 1880 | keep | 0 | Aug | 2022 | 0.0012805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-09 17:40 | 2022-08-09 19:29 | 3 | 1:49 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R22080900134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-08-09 | 327 | keep | 0 | Aug | 2022 | 0.00022272 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-09 17:42 | 2022-08-09 17:56 | 1 | 0:14 | P | DESGANCHE | 1 X 30 EN RISER SE REALIZO DESGANCHE PRIMARIO | S22080900130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-08-09 | 14 | keep | 0 | Aug | 2022 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-09 17:42 | 2022-08-09 18:40 | 1548 | 0:58 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 8001-04 EL CUAL ESTA LLEVANDO LA CARGA DEL 8001-01 | A22080900194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-08-09 | 89784 | keep | 0 | Aug | 2022 | 0.061151 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-08-09 17:42 | 2022-08-09 18:40 | 185 | 0:58 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 8001-04 EL CUAL ESTA LLEVANDO LA CARGA DEL 8001-03 | A22080900194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-08-09 | 10730 | keep | 0 | Aug | 2022 | 0.0073082 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-08-09 17:42 | 2022-08-09 18:40 | 9 | 0:58 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | A22080900194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-08-09 | 522 | keep | 0 | Aug | 2022 | 0.00035553 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-08-09 17:54 | 2022-08-10 15:00 | 11 | 21:06 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DEL T-10 AL T - 11 | C22080900295 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1266 | 2022-08-09 | 13926 | keep | 0 | Aug | 2022 | 0.0094849 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-09 18:11 | 2022-08-10 11:10 | 14 | 16:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22080900174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1019 | 2022-08-09 | 14266 | keep | 0 | Aug | 2022 | 0.0097165 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-08-09 18:18 | 2022-08-10 09:15 | 12 | 14:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR | B22080900169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 897 | 2022-08-09 | 10764 | keep | 0 | Aug | 2022 | 0.0073313 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-09 18:28 | 2022-08-09 20:30 | 125 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22080900147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2022-08-09 | 15250 | keep | 0 | Aug | 2022 | 0.010387 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2022-08-09 18:28 | 2022-08-10 00:57 | 15 | 6:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CORTE DE LINEA POR LLUVIAS | A22080900203 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 389 | 2022-08-09 | 5835 | keep | 0 | Aug | 2022 | 0.0039742 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-09 18:30 | 2022-08-09 23:23 | 250 | 4:53 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080900149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2022-08-09 | 73250 | keep | 0 | Aug | 2022 | 0.04989 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-08-09 18:40 | 2022-08-09 19:26 | 12 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22080900135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2022-08-09 | 552 | keep | 0 | Aug | 2022 | 0.00037596 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-08-09 18:40 | 2022-08-09 22:42 | 50 | 4:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA REPARAR LINEA PRIMARIA PARTIDA | A22080900206 | New_Event | Primary Wire Break | Include | Include | Equipment | 242 | 2022-08-09 | 12100 | keep | 0 | Aug | 2022 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-09 18:40 | 2022-08-09 18:55 | 1 | 0:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | A22080900204 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 15 | 2022-08-09 | 15 | keep | 0 | Aug | 2022 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-09 19:07 | 2022-08-09 19:55 | 75 | 0:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22080900176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-08-09 | 3600 | keep | 0 | Aug | 2022 | 0.0024519 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-08-09 19:15 | 2022-08-09 19:46 | 1 | 0:31 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y 1 X 30 EN MONTURA | B22080900192 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 31 | 2022-08-09 | 31 | keep | 0 | Aug | 2022 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-09 19:16 | 2022-08-09 19:17 | 327 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2604-01 | C22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 327 | keep | 0 | Aug | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
HUMACAO | 2022-08-09 19:16 | 2022-08-09 19:17 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2603-07 Y 65% DE SU CARGA POR 2604-03 | C22080900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-09 | 824 | keep | 0 | Aug | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-08-09 19:56 | 2022-08-10 14:03 | 30 | 18:07 | P | DESGANCHE | 1 X 50 EN C/ L SE RETIRO PENCA SOBRE LINEA | B22080900033 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1087 | 2022-08-09 | 32610 | keep | 0 | Aug | 2022 | 0.022211 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-09 19:58 | 2022-08-09 22:02 | 309 | 2:04 | T | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA | M22080900194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-08-09 | 38316 | keep | 0 | Aug | 2022 | 0.026097 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
AGUADILLA | 2022-08-09 19:58 | 2022-08-09 22:21 | 80 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | M22080900193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2022-08-09 | 11440 | keep | 0 | Aug | 2022 | 0.0077917 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-09 20:03 | 2022-08-10 17:41 | 10 | 21:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA EN VARIOS PUNTOS 1 X 20 EN TRANSFORMADOR | S22080900370 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1298 | 2022-08-09 | 12980 | keep | 0 | Aug | 2022 | 0.0088406 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-09 20:25 | 2022-08-10 16:30 | 1 | 20:05 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN TRANSFORMADOR DESGANCHE EVENTO SALIO DEL AREA DE PONCE | P22080900227 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1205 | 2022-08-09 | 1205 | keep | 0 | Aug | 2022 | 0.00082072 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-09 20:40 | 2022-08-10 14:05 | 2 | 17:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON PUENTES PRIMARIOS ABIERTOS Y SE REALIZO DESGANCHE | M22080900203 | New_Event | Primary Wire Break | Include | Include | Equipment | 1045 | 2022-08-09 | 2090 | keep | 0 | Aug | 2022 | 0.0014235 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-09 20:50 | 2022-08-09 20:51 | 492 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | B22080900000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-09 | 492 | keep | 0 | Aug | 2022 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2022-08-09 20:51 | 2022-08-09 23:04 | 300 | 2:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 150 EN SU-212 | B22080900326 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 133 | 2022-08-09 | 39900 | keep | 0 | Aug | 2022 | 0.027176 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-09 21:06 | 2022-08-09 21:38 | 8 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONEXIONES SECUNDARIAS | S22080900134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2022-08-09 | 256 | keep | 0 | Aug | 2022 | 0.00017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-09 21:07 | 2022-08-09 21:08 | 1604 | 0:01 | T | DESGANCHE | RECIERRE | C22080900363 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-09 | 1604 | keep | 0 | Aug | 2022 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2022-08-09 21:08 | 2022-08-10 07:38 | 33 | 10:30 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO | C22080900367 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 630 | 2022-08-09 | 20790 | keep | 0 | Aug | 2022 | 0.01416 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
CANOVANAS | 2022-08-09 21:53 | 2022-08-09 22:25 | 8 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 NX DE 10 AMP. EN T-47 HAY QUE REPARAR SECUNDRIA HACIA PEDESTAL | R22080900175 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2022-08-09 | 256 | keep | 0 | Aug | 2022 | 0.00017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-09 22:08 | 2022-08-10 01:36 | 347 | 3:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN CONVERTIDOR NO CAUSA | B22080900369 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-08-09 | 72176 | keep | 0 | Aug | 2022 | 0.049159 | 0.00023634 | Sustained | FALSE | FALSE | Not_TMED_Event | 347
CAGUAS | 2022-08-09 22:24 | 2022-08-10 09:40 | 400 | 11:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22080900388 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 676 | 2022-08-09 | 270400 | keep | 0 | Aug | 2022 | 0.18417 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2022-08-09 22:30 | 2022-08-10 01:11 | 50 | 2:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22080900237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-08-09 | 8050 | keep | 0 | Aug | 2022 | 0.0054828 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-09 22:39 | 2022-08-10 04:33 | 547 | 5:54 | P | NO SE REPORTO CAUSA | 1 X 40 SUM-20 1 X 25 EN CORTE DE LINEA | B22080900397 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 354 | 2022-08-09 | 193638 | keep | 0 | Aug | 2022 | 0.13189 | 0.00037256 | Sustained | FALSE | FALSE | Not_TMED_Event | 547
BAYAMON | 2022-08-09 22:40 | 2022-08-10 15:29 | 6 | 16:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN XMR MAL TIEMPO VIENTOS | B22080900401 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1009 | 2022-08-09 | 6054 | keep | 0 | Aug | 2022 | 0.0041234 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-09 23:04 | 2022-08-09 23:05 | 492 | 0:01 | T | OTRAS CAUSAS | SE ABRE INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA PODER CERRAR FUSIBLES EN SU 212 SIN VOLTAJE Y SIN CARGA. HABIA 2 FUSIBLES FUNDIDOS | B22080900417 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-08-09 | 492 | keep | 0 | Aug | 2022 | 0.0003351 | 0.0003351 | Momentary | FALSE | FALSE | Not_TMED_Event | 492
BAYAMON | 2022-08-09 23:05 | 2022-08-10 00:01 | 300 | 0:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 150 EN SU-212 | B22080900326 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 56 | 2022-08-09 | 16800 | keep | 0 | Aug | 2022 | 0.011442 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-09 23:08 | 2022-08-10 09:35 | 54 | 10:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL AEREO | B22080900419 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 627 | 2022-08-09 | 33858 | keep | 0 | Aug | 2022 | 0.023061 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BAYAMON | 2022-08-10 00:01 | 2022-08-10 00:50 | 50 | 0:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN RISER SE REMPLAZO CAJA QUEMADA | B22080900326 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2022-08-10 | 2450 | keep | 0 | Aug | 2022 | 0.0016687 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-10 00:09 | 2022-08-10 02:48 | 200 | 2:39 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE RETIRO BEJUCO DE LA LINEA | R22080900284 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-08-10 | 31800 | keep | 0 | Aug | 2022 | 0.021659 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-10 00:25 | 2022-08-10 06:05 | 40 | 5:40 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE RETEZO LINEA | M22080900244 | New_Event | Primary Wire Break | Include | Include | Equipment | 340 | 2022-08-10 | 13600 | keep | 0 | Aug | 2022 | 0.0092629 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-10 01:12 | 2022-08-10 03:25 | 2107 | 2:13 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO DISCO PARTIDO Y SE CERRO INTERRUPTOR | A22080900319 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 133 | 2022-08-10 | 280231 | keep | 0 | Aug | 2022 | 0.19086 | 0.0014351 | Sustained | FALSE | FALSE | Not_TMED_Event | 2107
AGUADILLA | 2022-08-10 03:51 | 2022-08-10 10:27 | 70 | 6:36 | P | ANIMAL | 3 X 80 EN CORTE DE LINEA IGUANA CRUZO FASE A TIERRA | A22080900331 | New_Event | Animals | Include | Include | Wildlife | 396 | 2022-08-10 | 27720 | keep | 0 | Aug | 2022 | 0.01888 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-08-10 03:55 | 2022-08-10 06:46 | 63 | 2:51 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22080900413 | New_Event | Animals | Include | Include | Wildlife | 171 | 2022-08-10 | 10773 | keep | 0 | Aug | 2022 | 0.0073374 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2022-08-10 04:35 | 2022-08-10 10:53 | 65 | 6:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO CAUSA | S22080900353 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 378 | 2022-08-10 | 24570 | keep | 0 | Aug | 2022 | 0.016735 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-08-10 05:55 | 2022-08-10 10:00 | 25 | 4:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L NO CAUSA | B22080900459 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2022-08-10 | 6125 | keep | 0 | Aug | 2022 | 0.0041717 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-08-10 06:00 | 2022-08-10 10:41 | 20 | 4:41 | P | DESGANCHE | 1X40 EN C/L | R22081000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2022-08-10 | 5620 | keep | 0 | Aug | 2022 | 0.0038278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-10 06:12 | 2022-08-10 22:11 | 300 | 15:59 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | B22080900460 | New_Event | Primary Pole Failure | Include | Include | Equipment | 959 | 2022-08-10 | 287700 | keep | 0 | Aug | 2022 | 0.19595 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-10 06:50 | 2022-08-10 09:10 | 65 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L SE REPORTAN FUERTES LLUVIAS | B22080900464 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2022-08-10 | 9100 | keep | 0 | Aug | 2022 | 0.006198 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-08-10 07:02 | 2022-08-10 10:55 | 1447 | 3:53 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1112-04 LLEVANDO CARGA 1419-12 Y 1419-09. SE SECCIONALIZO VS EN MH 38 AVERIADO Y SE DIO SERVICIO A 5% 1112-04 | S22080900360 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 233 | 2022-08-10 | 337151 | keep | 0 | Aug | 2022 | 0.22963 | 0.00098555 | Sustained | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2022-08-10 07:02 | 2022-08-10 22:34 | 266 | 15:32 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO V.S. MH-38 SU CARGA POR 1112-04 | S22080900360 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 932 | 2022-08-10 | 247912 | keep | 0 | Aug | 2022 | 0.16885 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
SAN JUAN | 2022-08-10 07:02 | 2022-08-10 08:43 | 73 | 1:41 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR 1112-04 LLEVANDO CARGA 1419-12 Y 1419-09. SE NORMALIZO CARGA DE 1419-12 EN SU INTERRUPTOR PARA SECCIONALIZAR VS AVERIADO EN MH 38 QUE PERTENECE A 1112-04 | S22080900360 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 101 | 2022-08-10 | 7373 | keep | 0 | Aug | 2022 | 0.0050217 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
UTUADO | 2022-08-10 07:15 | 2022-08-10 10:58 | 25 | 3:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22081000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-08-10 | 5575 | keep | 0 | Aug | 2022 | 0.0037971 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-08-10 07:25 | 2022-08-10 14:24 | 1 | 6:59 | P | DESGANCHE | 1 X 80 CL DESGANCHE | C22081000418 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2022-08-10 | 419 | keep | 0 | Aug | 2022 | 0.00028538 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-10 07:30 | 2022-08-10 10:15 | 30 | 2:45 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C22080900419 | New_Event | Animals | Include | Include | Wildlife | 165 | 2022-08-10 | 4950 | keep | 0 | Aug | 2022 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-10 07:36 | 2022-08-10 22:03 | 1 | 14:27 | P | DESGANCHE | SE DESGANCHO Y SE CERRO PUENTE DE LINEA A RISER | S22081000367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 867 | 2022-08-10 | 867 | keep | 0 | Aug | 2022 | 0.00059051 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-10 07:36 | 2022-08-10 11:07 | 6 | 3:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR POR FUERTES VIENTOS | M22081000005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 211 | 2022-08-10 | 1266 | keep | 0 | Aug | 2022 | 0.00086227 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-08-10 07:40 | 2022-08-10 11:43 | 127 | 4:03 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P22081000017 | New_Event | Animals | Include | Include | Wildlife | 243 | 2022-08-10 | 30861 | keep | 0 | Aug | 2022 | 0.021019 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
CAGUAS | 2022-08-10 07:55 | 2022-08-10 07:56 | 817 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22080900422 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-10 | 817 | keep | 0 | Aug | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
UTUADO | 2022-08-10 07:57 | 2022-08-10 10:20 | 2 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A22081000010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2022-08-10 | 286 | keep | 0 | Aug | 2022 | 0.00019479 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-10 08:01 | 2022-08-10 10:33 | 150 | 2:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22081000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-08-10 | 22800 | keep | 0 | Aug | 2022 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-08-10 08:03 | 2022-08-10 11:30 | 4 | 3:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE BRISA | P22081000023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 207 | 2022-08-10 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-08-10 08:23 | 2022-08-10 13:19 | 50 | 4:56 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22081000002 | New_Event | Animals | Include | Include | Wildlife | 296 | 2022-08-10 | 14800 | keep | 0 | Aug | 2022 | 0.01008 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-10 08:24 | 2022-08-11 10:47 | 15 | 26:23 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L | B22081100012 | New_Event | Primary Wire Break | Include | Include | Equipment | 1583 | 2022-08-10 | 23745 | keep | 0 | Aug | 2022 | 0.016173 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-10 08:31 | 2022-08-10 12:26 | 1 | 3:55 | P | NO SE REPORTO CAUSA | 1X15 EN C/L NO CAUSA | S22081000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-08-10 | 235 | keep | 0 | Aug | 2022 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-10 08:48 | 2022-08-10 12:06 | 11 | 3:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA - X - 37.5KVA @ 13KV | R22081000035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 198 | 2022-08-10 | 2178 | keep | 0 | Aug | 2022 | 0.0014834 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2022-08-10 08:48 | 2022-08-10 18:52 | 1 | 10:04 | P | OTRAS CAUSAS | ABRIO C/L PARA REPARAR EQUIPO DE MEDICION | C22081000005 | New_Event | Other Causes | Include | Include | Other | 604 | 2022-08-10 | 604 | keep | 0 | Aug | 2022 | 0.00041138 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-10 08:56 | 2022-08-10 14:00 | 100 | 5:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRARON PUENTES | A22081000013 | New_Event | Primary Wire Break | Include | Include | Equipment | 304 | 2022-08-10 | 30400 | keep | 0 | Aug | 2022 | 0.020705 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-10 09:00 | 2022-08-10 16:26 | 50 | 7:26 | P | ARBOL SOBRE LINEA | SE ABRIO C/L DE EMERGENCIA SE RETIRO ARBOL SOBRE LINEA PRIMARIA Y SE REPARO LA TRENZA SECUNDARIA | B22081000025 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 446 | 2022-08-10 | 22300 | keep | 0 | Aug | 2022 | 0.015188 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-10 09:00 | 2022-08-10 14:30 | 100 | 5:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARARON PUENTES PRIMARIOS ABIERTOS | M22081000028 | New_Event | Primary Wire Break | Include | Include | Equipment | 330 | 2022-08-10 | 33000 | keep | 0 | Aug | 2022 | 0.022476 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-10 09:03 | 2022-08-10 09:04 | 4132 | 0:01 | T | ANIMAL | RECIERRE | P22081000036 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-10 | 4132 | keep | 0 | Aug | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-08-10 09:03 | 2022-08-10 09:04 | 4279 | 0:01 | T | ANIMAL | RECIERRE | P22081000036 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-10 | 4279 | keep | 0 | Aug | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-08-10 09:03 | 2022-08-10 09:04 | 464 | 0:01 | T | ANIMAL | RECIERRE | P22081000036 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-10 | 464 | keep | 0 | Aug | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-08-10 09:04 | 2022-08-10 10:25 | 47 | 1:21 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P22081000037 | 1st_after_momentary | Animals | Include | Include | Wildlife | 81 | 2022-08-10 | 3807 | keep | 0 | Aug | 2022 | 0.0025929 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
VEGA BAJA | 2022-08-10 09:05 | 2022-08-10 09:06 | 776 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-10 | 776 | keep | 0 | Aug | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
ARECIBO | 2022-08-10 09:13 | 2022-08-10 11:15 | 2 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22081000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-08-10 | 244 | keep | 0 | Aug | 2022 | 0.00016619 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-08-10 09:22 | 2022-08-10 10:14 | 8 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA (SALIDA TRAMO SOTERRADO HACIA LA CARGA) | R22081000037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2022-08-10 | 416 | keep | 0 | Aug | 2022 | 0.00028334 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-10 09:30 | 2022-08-10 16:03 | 1 | 6:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN BANCO TRANSFORMADOR NO CAUSA | S22081000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 393 | 2022-08-10 | 393 | keep | 0 | Aug | 2022 | 0.00026767 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-10 09:35 | 2022-08-10 18:25 | 100 | 8:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 75KVA Y UN SU | M22081000005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 530 | 2022-08-10 | 53000 | keep | 0 | Aug | 2022 | 0.036098 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-10 09:45 | 2022-08-10 10:12 | 1 | 0:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO DE LINEA @ CAJA | R22081000039 | New_Event | Primary Wire Break | Include | Include | Equipment | 27 | 2022-08-10 | 27 | keep | 0 | Aug | 2022 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-10 09:48 | 2022-08-10 12:21 | 78 | 2:33 | P | DESGANCHE | 2X50 EN C/L POR DESGANCHE DE BAMBUAS | B22081000036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-08-10 | 11934 | keep | 0 | Aug | 2022 | 0.0081282 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
GUAYAMA | 2022-08-10 10:02 | 2022-08-10 14:11 | 297 | 4:09 | P | NO SE REPORTO CAUSA | NO SE REPOSTO CAUSA | P22081000048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2022-08-10 | 73953 | keep | 0 | Aug | 2022 | 0.050369 | 0.00020229 | Sustained | FALSE | FALSE | Not_TMED_Event | 297
BAYAMON | 2022-08-10 10:07 | 2022-08-10 14:49 | 20 | 4:42 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | B22081000041 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 282 | 2022-08-10 | 5640 | keep | 0 | Aug | 2022 | 0.0038414 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-10 10:09 | 2022-08-10 12:50 | 14 | 2:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR REEMPLAZO SECUNDARIA | C22081000013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 161 | 2022-08-10 | 2254 | keep | 0 | Aug | 2022 | 0.0015352 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2022-08-10 10:20 | 2022-08-10 16:33 | 4 | 6:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO | P22081000052 | New_Event | Primary Pole Failure | Include | Include | Equipment | 373 | 2022-08-10 | 1492 | keep | 0 | Aug | 2022 | 0.0010162 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-08-10 10:35 | 2022-08-10 12:15 | 35 | 1:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REEMPLAZO PORTAFUSIBLE QUEMADO | C22081000016 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2022-08-10 | 3500 | keep | 0 | Aug | 2022 | 0.0023838 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-08-10 10:55 | 2022-08-10 22:34 | 1347 | 11:39 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO V.S. MH-38 LLEVA 95% DE SU CARGA Y ADEMAS EL 1419-9 | S22080900360 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 699 | 2022-08-10 | 941553 | keep | 0 | Aug | 2022 | 0.64129 | 0.00091744 | Sustained | FALSE | FALSE | Not_TMED_Event | 1347
ARECIBO | 2022-08-10 11:04 | 2022-08-10 11:34 | 1548 | 0:30 | T | NO SE REPORTO CAUSA | SE LLAMO A JORGE ROMAN DE SUBESTACIONES QUE ESTA TRABAJANDO EN LA SUBESTACION Y ESTE ME INDICO QUE EL INTERRUPTOR NO CERRO POR SCADA PORQUE ELLOS TIENEN DESCONECTADO EL AC DE CARGAR EL INTERRUPTOR PROCEDIO A CARGARLO Y SE CERRO POR SCADA. | A22081000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-08-10 | 46440 | keep | 0 | Aug | 2022 | 0.03163 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-08-10 11:04 | 2022-08-10 11:34 | 185 | 0:30 | T | NO SE REPORTO CAUSA | SE LLAMO A JORGE ROMAN DE SUBESTACIONES QUE ESTA TRABAJANDO EN LA SUBESTACION Y ESTE ME INDICO QUE EL INTERRUPTOR NO CERRO POR SCADA PORQUE ELLOS TIENEN DESCONECTADO EL AC DE CARGAR EL INTERRUPTOR PROCEDIO A CARGARLO Y SE CERRO POR SCADA. | A22081000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-08-10 | 5550 | keep | 0 | Aug | 2022 | 0.0037801 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-08-10 11:04 | 2022-08-10 11:34 | 9 | 0:30 | T | NO SE REPORTO CAUSA | SE LLAMO A JORGE ROMAN DE SUBESTACIONES QUE ESTA TRABAJANDO EN LA SUBESTACION Y ESTE ME INDICO QUE EL INTERRUPTOR NO CERRO POR SCADA PORQUE ELLOS TIENEN DESCONECTADO EL AC DE CARGAR EL INTERRUPTOR PROCEDIO A CARGARLO Y SE CERRO POR SCADA. | A22081000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-08-10 | 270 | keep | 0 | Aug | 2022 | 0.0001839 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-08-10 11:12 | 2022-08-10 12:05 | 5 | 0:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 80 EN CORTE DE LINEA | P22081000057 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2022-08-10 | 265 | keep | 0 | Aug | 2022 | 0.00018049 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-10 11:17 | 2022-08-10 15:18 | 6 | 4:01 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | C22081000014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-08-10 | 1446 | keep | 0 | Aug | 2022 | 0.00098486 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-10 11:39 | 2022-08-10 11:40 | 3597 | 0:01 | T | ANIMAL | RECERRO | B22081000000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-10 | 3597 | keep | 0 | Aug | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-08-10 11:40 | 2022-08-10 13:35 | 375 | 1:55 | P | ANIMAL | 1 X 100 C/L Y 1 X 65 EN LA URB AVE CRUZO FASE | B22081000059 | 1st_after_momentary | Animals | Include | Include | Wildlife | 115 | 2022-08-10 | 43125 | keep | 0 | Aug | 2022 | 0.029372 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
HUMACAO | 2022-08-10 11:40 | 2022-08-10 16:41 | 6 | 5:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REEMPLAZAR BAJANTE Y LINEA SECUNDARIA | C22081000021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 301 | 2022-08-10 | 1806 | keep | 0 | Aug | 2022 | 0.0012301 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-10 11:45 | 2022-08-10 12:40 | 3295 | 0:55 | T | DESGANCHE | SE RETIRO RAMA DE LA LINEA | B22081000055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-08-10 | 181225 | keep | 0 | Aug | 2022 | 0.12343 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-08-10 11:52 | 2022-08-10 15:37 | 25 | 3:45 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | B22081000056 | New_Event | Animals | Include | Include | Wildlife | 225 | 2022-08-10 | 5625 | keep | 0 | Aug | 2022 | 0.0038312 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-10 12:02 | 2022-08-11 19:45 | 1 | 31:43 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1903 | 2022-08-10 | 1903 | keep | 0 | Aug | 2022 | 0.0012961 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-10 12:03 | 2022-08-10 21:05 | 10 | 9:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA INSTALAR AEREO PROVISIONAL SECUNDARIO Y SE REPARO 2 TOMAS Y EL PEDESTAL DEL T-47/P2 | R22080900175 | New_Event | Secondary Wire Break | Include | Include | Equipment | 542 | 2022-08-10 | 5420 | keep | 0 | Aug | 2022 | 0.0036915 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-10 12:12 | 2022-08-10 17:50 | 3 | 5:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22081000063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 338 | 2022-08-10 | 1014 | keep | 0 | Aug | 2022 | 0.00069063 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-08-10 12:36 | 2022-08-10 14:15 | 100 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | P22081000067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-08-10 | 9900 | keep | 0 | Aug | 2022 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-08-10 12:39 | 2022-08-10 14:15 | 5 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA HACIA BANCO DE TRANSFORMADORES | R22081000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-08-10 | 480 | keep | 0 | Aug | 2022 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-08-10 12:39 | 2022-08-10 15:04 | 125 | 2:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REEMPLAZO PORTAFUSIBLE | C22081000029 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2022-08-10 | 18125 | keep | 0 | Aug | 2022 | 0.012345 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2022-08-10 12:59 | 2022-08-10 13:26 | 2 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN BANCO DE XMRS | R22081000042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2022-08-10 | 54 | keep | 0 | Aug | 2022 | 3.6779e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2022-08-10 12:59 | 2022-08-10 16:00 | 100 | 3:01 | P | ANIMAL | 3 X 65 EN C/L AVE CRUZO LINEAS | P22081000071 | New_Event | Animals | Include | Include | Wildlife | 181 | 2022-08-10 | 18100 | keep | 0 | Aug | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-10 13:04 | 2022-08-10 14:21 | 12 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y SE BAJO TAP 3 AL 1 QUEDO 124/248 | S22081000077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2022-08-10 | 924 | keep | 0 | Aug | 2022 | 0.00062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-08-10 13:04 | 2022-08-10 15:30 | 30 | 2:26 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA LINEAS CRUZADAS | A22081000036 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 146 | 2022-08-10 | 4380 | keep | 0 | Aug | 2022 | 0.0029832 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-08-10 13:08 | 2022-08-10 15:18 | 10 | 2:10 | P | ANIMAL | 1 X 50 CORTE DE LINEA CRUCE POR AVE | C22081000033 | New_Event | Animals | Include | Include | Wildlife | 130 | 2022-08-10 | 1300 | keep | 0 | Aug | 2022 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-10 13:08 | 2022-08-10 16:57 | 1 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | M22081000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-08-10 | 229 | keep | 0 | Aug | 2022 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-10 13:10 | 2022-08-10 19:54 | 12 | 6:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA POR 75 KVA | S22081000081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 404 | 2022-08-10 | 4848 | keep | 0 | Aug | 2022 | 0.003302 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-10 13:21 | 2022-08-10 16:29 | 139 | 3:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22081000093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-08-10 | 26132 | keep | 0 | Aug | 2022 | 0.017798 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
FAJARDO | 2022-08-10 13:22 | 2022-08-10 14:56 | 8 | 1:34 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE PRIMARIO DE LINEA A CAJA DE TRANSFORMADOR | R22081000061 | New_Event | Primary Wire Break | Include | Include | Equipment | 94 | 2022-08-10 | 752 | keep | 0 | Aug | 2022 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-10 13:26 | 2022-08-10 14:32 | 1337 | 1:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO MANUALMENTE | M22081000074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2022-08-10 | 88242 | keep | 0 | Aug | 2022 | 0.060101 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
CAGUAS | 2022-08-10 13:28 | 2022-08-10 13:29 | 2448 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081000037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-10 | 2448 | keep | 0 | Aug | 2022 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
VEGA BAJA | 2022-08-10 13:31 | 2022-08-10 15:45 | 50 | 2:14 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE | A22081000042 | New_Event | Animals | Include | Include | Wildlife | 134 | 2022-08-10 | 6700 | keep | 0 | Aug | 2022 | 0.0045633 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-10 13:37 | 2022-08-10 16:12 | 100 | 2:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 Y 1 X 30 EN CORTES DE LINEA SE REPARO CONDUCTOR PRIMARIO | R22081000046 | New_Event | Primary Wire Break | Include | Include | Equipment | 155 | 2022-08-10 | 15500 | keep | 0 | Aug | 2022 | 0.010557 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-10 13:44 | 2022-08-10 15:07 | 1548 | 1:23 | T | CONDUCTOR ROTO O ABIERTO | CARGA POR 8001-04 CON LINEA PRIMARIA ROTA SE SECCIONALIZO | A22081000044 | New_Event | Primary Wire Break | Include | Include | Equipment | 83 | 2022-08-10 | 128484 | keep | 0 | Aug | 2022 | 0.08751 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2022-08-10 13:44 | 2022-08-10 15:07 | 185 | 1:23 | T | CONDUCTOR ROTO O ABIERTO | CARGA POR 8001-04 CON LINEA PRIMARIA ROTA SE SECCIONALIZO | A22081000044 | New_Event | Primary Wire Break | Include | Include | Equipment | 83 | 2022-08-10 | 15355 | keep | 0 | Aug | 2022 | 0.010458 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
ARECIBO | 2022-08-10 13:44 | 2022-08-10 18:50 | 9 | 5:06 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA ROTA Y SE CERRO MACHETES | A22081000044 | New_Event | Primary Wire Break | Include | Include | Equipment | 306 | 2022-08-10 | 2754 | keep | 0 | Aug | 2022 | 0.0018757 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-08-10 13:52 | 2022-08-10 13:53 | 651 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B22081000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-10 | 651 | keep | 0 | Aug | 2022 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
CANOVANAS | 2022-08-10 14:04 | 2022-08-10 18:21 | 197 | 4:17 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA REEMPLAZO DE POSTE PRIMARIO PARTIDO | R22081000055 | New_Event | Primary Pole Failure | Include | Include | Equipment | 257 | 2022-08-10 | 50629 | keep | 0 | Aug | 2022 | 0.034483 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
CAGUAS | 2022-08-10 14:16 | 2022-08-10 17:09 | 40 | 2:53 | P | DESGANCHE | 1 X 40 EN C/L | C22081000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-08-10 | 6920 | keep | 0 | Aug | 2022 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-10 14:16 | 2022-08-10 17:40 | 40 | 3:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON LINEAS PRIMARIAS PARTIDAS | M22081000088 | New_Event | Primary Wire Break | Include | Include | Equipment | 204 | 2022-08-10 | 8160 | keep | 0 | Aug | 2022 | 0.0055577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-10 14:22 | 2022-08-10 17:15 | 10 | 2:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22081000094 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 173 | 2022-08-10 | 1730 | keep | 0 | Aug | 2022 | 0.0011783 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-10 14:27 | 2022-08-10 15:55 | 200 | 1:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081000093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2022-08-10 | 17600 | keep | 0 | Aug | 2022 | 0.011987 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-10 14:36 | 2022-08-10 16:05 | 288 | 1:29 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO POSTE PRIMARIO PARTIDO SE TRABAJO CON GOI SJ-220810-50 SE DEJO FUERA 33 CLIENTES PARA PODER REALIZAR EL CAMBIO | R22081000047 | New_Event | Primary Pole Failure | Include | Include | Equipment | 89 | 2022-08-10 | 25632 | keep | 0 | Aug | 2022 | 0.017458 | 0.00019616 | Sustained | FALSE | FALSE | Not_TMED_Event | 288
FAJARDO | 2022-08-10 14:48 | 2022-08-10 16:15 | 1 | 1:27 | P | ANIMAL | 1 X 20 EN RISER CRUCE POR AVE | R22081000058 | New_Event | Animals | Include | Include | Wildlife | 87 | 2022-08-10 | 87 | keep | 0 | Aug | 2022 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-10 14:51 | 2022-08-10 18:23 | 2 | 3:32 | P | DESGANCHE | 2 X 25 EN C/L DESGANCHE | P22081000108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-08-10 | 424 | keep | 0 | Aug | 2022 | 0.00028878 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-08-10 14:52 | 2022-08-10 18:07 | 6 | 3:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA | R22081000060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2022-08-10 | 1170 | keep | 0 | Aug | 2022 | 0.00079688 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-08-10 14:58 | 2022-08-10 18:25 | 40 | 3:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REEMPLAZO CAJA AVERIADA | C22081000051 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2022-08-10 | 8280 | keep | 0 | Aug | 2022 | 0.0056395 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-10 15:02 | 2022-08-10 18:07 | 20 | 3:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081000162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-08-10 | 3700 | keep | 0 | Aug | 2022 | 0.0025201 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-08-10 15:05 | 2022-08-10 15:06 | 1650 | 0:01 | T | DESGANCHE | RECIERRE | P22081000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-10 | 1650 | keep | 0 | Aug | 2022 | 0.0011238 | 0.0011238 | Momentary | FALSE | FALSE | Not_TMED_Event | 1650
AGUADILLA | 2022-08-10 15:05 | 2022-08-10 19:25 | 100 | 4:20 | P | DESGANCHE | 1X 200 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22081000109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2022-08-10 | 26000 | keep | 0 | Aug | 2022 | 0.017708 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-08-10 15:06 | 2022-08-10 18:32 | 50 | 3:26 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P22081000119 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-08-10 | 10300 | keep | 0 | Aug | 2022 | 0.0070153 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-10 15:31 | 2022-08-11 02:46 | 70 | 11:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMP | M22081000120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 675 | 2022-08-10 | 47250 | keep | 0 | Aug | 2022 | 0.032182 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-08-10 15:38 | 2022-08-10 15:39 | 73 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | DISPARO AL MOMENTO QUE SE CERRO CONTRA 1419-10 SE ENCONTRO TERMINACIONA VERIADA SU-2 A MH-1 Y SE CERRO INTERRUPTOR LA CARGA DEL 1419-10 HABIA SIDO TRANSFERIDA PREVIAMENTE | S22081000178 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2022-08-10 | 73 | keep | 0 | Aug | 2022 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2022-08-10 15:38 | 2022-08-10 15:39 | 1191 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | DISPARO AL MOMENTO QUE SE CERRO CONTRA 1419-10 SE ENCONTRO TERMINACION AVERIADA SU-2 A MH-1 Y SE CERRO INTERRUPTOR CARGA DEL 1419-10 HABIA SIDO TRANSFERIDA PREVIAMENTE | S22081000178 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2022-08-10 | 1191 | keep | 0 | Aug | 2022 | 0.00081118 | 0.00081118 | Momentary | FALSE | FALSE | Not_TMED_Event | 1191
BARRANQUITAS | 2022-08-10 15:51 | 2022-08-10 18:12 | 19 | 2:21 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C22081000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2022-08-10 | 2679 | keep | 0 | Aug | 2022 | 0.0018247 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-08-10 16:02 | 2022-08-10 18:41 | 15 | 2:39 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE HIZO DESGANCHE Y SE LEVANTO SECUNDARIA | S22081000189 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 159 | 2022-08-10 | 2385 | keep | 0 | Aug | 2022 | 0.0016244 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-10 16:05 | 2022-08-10 22:51 | 33 | 6:46 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO PARTIDO SE TRABAJO CON GOI SJ-220810-50 100% EN SERVICIO | R22081000047 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 406 | 2022-08-10 | 13398 | keep | 0 | Aug | 2022 | 0.0091253 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-10 16:31 | 2022-08-10 22:10 | 1 | 5:39 | P | ANIMAL | 1 X 50 EN C/L DESGANCHE | P22081000124 | New_Event | Animals | Include | Include | Wildlife | 339 | 2022-08-10 | 339 | keep | 0 | Aug | 2022 | 0.00023089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-10 16:41 | 2022-08-10 18:34 | 102 | 1:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081000162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-08-10 | 11526 | keep | 0 | Aug | 2022 | 0.0078503 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
BAYAMON | 2022-08-10 16:42 | 2022-08-10 18:06 | 8 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR LA SECUNDARIA QUEMADA | B22081000107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2022-08-10 | 672 | keep | 0 | Aug | 2022 | 0.0004577 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-10 16:52 | 2022-08-10 19:19 | 20 | 2:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REEMPLAZAR TRAMO SECUNDARIO | C22081000069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 147 | 2022-08-10 | 2940 | keep | 0 | Aug | 2022 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-10 17:09 | 2022-08-11 11:31 | 150 | 18:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A22081000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1102 | 2022-08-10 | 165300 | keep | 0 | Aug | 2022 | 0.11259 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-10 17:30 | 2022-08-10 17:31 | 2234 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE EN SERVICIO | B22081000113 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-10 | 2234 | keep | 0 | Aug | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-08-10 17:31 | 2022-08-10 23:19 | 350 | 5:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y 1 X 140 EN CORTE DE LINEA | B22081000211 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 348 | 2022-08-10 | 121800 | keep | 0 | Aug | 2022 | 0.082957 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
VEGA BAJA | 2022-08-10 17:35 | 2022-08-10 18:30 | 2 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR REMPLAZAR CONECTORES SECUNDARIOS | A22080900177 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-08-10 | 110 | keep | 0 | Aug | 2022 | 7.492e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-10 17:43 | 2022-08-10 19:11 | 65 | 1:28 | P | CAUSAS EXTERNAS | 1 X 50 Y 1 X 65 EN C/L A CAUSA DE CAMION EXTERNO | B22081000099 | New_Event | Damage From Public | Include | Include | Public | 88 | 2022-08-10 | 5720 | keep | 0 | Aug | 2022 | 0.0038959 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-08-10 17:47 | 2022-08-10 19:57 | 30 | 2:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S22081000239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-08-10 | 3900 | keep | 0 | Aug | 2022 | 0.0026563 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-10 17:47 | 2022-08-10 18:53 | 150 | 1:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22081000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-08-10 | 9900 | keep | 0 | Aug | 2022 | 0.0067428 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-08-10 17:48 | 2022-08-11 10:05 | 50 | 16:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | A22081000076 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 977 | 2022-08-10 | 48850 | keep | 0 | Aug | 2022 | 0.033272 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-10 17:55 | 2022-08-10 18:50 | 18 | 0:55 | P | CAUSAS EXTERNAS | 1 X 30 EN C/L CAMION SACUDIO LAS LINEAS | C22081000079 | New_Event | Damage From Public | Include | Include | Public | 55 | 2022-08-10 | 990 | keep | 0 | Aug | 2022 | 0.00067428 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-08-10 17:58 | 2022-08-10 19:22 | 723 | 1:24 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR SE ABRIO N/O CONTRA EL 1711-05 Y SE CERRO BKR Y QUEDO EN SERVICIO. | B22081000130 | New_Event | Switch Failure | Include | Include | Equipment | 84 | 2022-08-10 | 60732 | keep | 0 | Aug | 2022 | 0.041364 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-10 17:58 | 2022-08-10 21:15 | 1976 | 3:17 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO PARA EL REEMPLAZO DE MACHETE QUEMADO Y SE CERRO AMARRE CONTRA EL 1711-02. 100% EN SERVICIO | B22081000130 | New_Event | Switch Failure | Include | Include | Equipment | 197 | 2022-08-10 | 389272 | keep | 0 | Aug | 2022 | 0.26513 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
MAYAGÃœEZ | 2022-08-10 18:53 | 2022-08-10 18:58 | 1444 | 0:05 | T | DESGANCHE | DISPARO DE INTERRUPTOR 6014-02 EL CUAL ESTA LLEVANDO LA CARGA DEL 6014-01 | M22081000182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-08-10 | 7220 | keep | 0 | Aug | 2022 | 0.0049175 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-08-10 18:53 | 2022-08-10 18:58 | 3630 | 0:05 | T | DESGANCHE | DISPARO DE INTERRUPTOR | M22081000182 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-08-10 | 18150 | keep | 0 | Aug | 2022 | 0.012362 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-10 18:58 | 2022-08-10 22:20 | 150 | 3:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22081000117 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-08-10 | 30300 | keep | 0 | Aug | 2022 | 0.020637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-10 19:09 | 2022-08-10 19:48 | 6 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA QUEMADA | B22081000176 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2022-08-10 | 234 | keep | 0 | Aug | 2022 | 0.00015938 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-10 19:11 | 2022-08-10 19:13 | 1403 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22081000081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-10 | 2806 | keep | 0 | Aug | 2022 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
BAYAMON | 2022-08-10 19:25 | 2022-08-10 20:39 | 200 | 1:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | B22081000188 | New_Event | Primary Wire Break | Include | Include | Equipment | 74 | 2022-08-10 | 14800 | keep | 0 | Aug | 2022 | 0.01008 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-10 19:50 | 2022-08-10 20:45 | 103 | 0:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R22081000081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-08-10 | 5665 | keep | 0 | Aug | 2022 | 0.0038584 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
SAN JUAN | 2022-08-10 19:51 | 2022-08-11 10:19 | 50 | 14:28 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU 1 | S22081000285 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 868 | 2022-08-10 | 43400 | keep | 0 | Aug | 2022 | 0.02956 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-10 19:56 | 2022-08-10 21:00 | 4 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22081000166 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2022-08-10 | 256 | keep | 0 | Aug | 2022 | 0.00017436 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-08-10 20:01 | 2022-08-10 20:32 | 1 | 0:31 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C22081000084 | New_Event | Animals | Include | Include | Wildlife | 31 | 2022-08-10 | 31 | keep | 0 | Aug | 2022 | 2.1114e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-10 20:15 | 2022-08-10 21:00 | 10 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN XMR | P22081000171 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2022-08-10 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-08-10 20:21 | 2022-08-10 21:40 | 300 | 1:19 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22081000175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-08-10 | 23700 | keep | 0 | Aug | 2022 | 0.016142 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2022-08-10 20:26 | 2022-08-11 10:30 | 30 | 14:04 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA CLIENTES DESGANCHANDO TIRARON RAMA SOBRE LINEA | A22081000085 | New_Event | Damage From Public | Include | Include | Public | 844 | 2022-08-10 | 25320 | keep | 0 | Aug | 2022 | 0.017245 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-10 20:30 | 2022-08-10 20:31 | 4188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO INTERRUPTOR EN SERVICIO | R22081000084 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-10 | 4188 | keep | 0 | Aug | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-08-10 20:53 | 2022-08-10 20:54 | 4188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO INTERRUPTOR EN SERVICIO | R22081000000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-10 | 4188 | keep | 0 | Aug | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-08-10 20:54 | 2022-08-10 22:20 | 1167 | 1:26 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE MACHETE A LINEA | R22081000101 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 86 | 2022-08-10 | 100362 | keep | 0 | Aug | 2022 | 0.068356 | 0.00079484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1167
AGUADILLA | 2022-08-10 21:14 | 2022-08-10 22:25 | 60 | 1:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M22081000184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-08-10 | 4260 | keep | 0 | Aug | 2022 | 0.0029015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-10 22:43 | 2022-08-11 09:15 | 30 | 10:32 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYO CRUZADO | A22081000092 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 632 | 2022-08-10 | 18960 | keep | 0 | Aug | 2022 | 0.012914 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-10 23:13 | 2022-08-11 09:25 | 40 | 10:12 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DE RISER A T9 Y AVERIA VIEJA DE T9 A T13 | B22081000224 | New_Event | UG Cable Fault | Include | Include | Equipment | 612 | 2022-08-10 | 24480 | keep | 0 | Aug | 2022 | 0.016673 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-08-10 23:32 | 2022-08-11 03:50 | 125 | 4:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22081000198 | New_Event | Cutout Failure | Include | Include | Equipment | 258 | 2022-08-10 | 32250 | keep | 0 | Aug | 2022 | 0.021965 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2022-08-11 01:33 | 2022-08-11 08:15 | 80 | 6:42 | P | ANIMAL | 1 X 65 EN C/L SE RETIRO AVE | R22081100003 | New_Event | Animals | Include | Include | Wildlife | 402 | 2022-08-11 | 32160 | keep | 0 | Aug | 2022 | 0.021904 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-11 02:00 | 2022-08-11 10:55 | 100 | 8:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | A22081100002 | New_Event | Primary Wire Break | Include | Include | Equipment | 535 | 2022-08-11 | 53500 | keep | 0 | Aug | 2022 | 0.036439 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-11 02:38 | 2022-08-11 02:39 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22081100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 2039 | keep | 0 | Aug | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
SAN JUAN | 2022-08-11 03:07 | 2022-08-11 03:09 | 1106 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 60% POR 1529-15 | S22081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-11 | 2212 | keep | 0 | Aug | 2022 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-08-11 03:07 | 2022-08-11 03:09 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 60% DEL 1346-02 | S22081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-11 | 3604 | keep | 0 | Aug | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-08-11 03:13 | 2022-08-11 07:21 | 2203 | 4:08 | T | DESGANCHE | SE SECCIONALIZO AVERIA POR DESGANCHE PRIMARIO @ 13KV MEDIANTE G.O.I. SJ-220811-01 | S22081100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-08-11 | 546344 | keep | 0 | Aug | 2022 | 0.37211 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-08-11 03:51 | 2022-08-11 10:10 | 158 | 6:19 | P | DESGANCHE | 2 X 80 EN C/L SE REMOVIO RAMA DE LA LINEA | S22081100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2022-08-11 | 59882 | keep | 0 | Aug | 2022 | 0.040785 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
PONCE | 2022-08-11 04:02 | 2022-08-11 06:45 | 2 | 2:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 65 EN CORTE DE LINEA | P22081100012 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2022-08-11 | 326 | keep | 0 | Aug | 2022 | 0.00022204 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-11 05:01 | 2022-08-11 05:03 | 922 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S22081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-11 | 1844 | keep | 0 | Aug | 2022 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-08-11 05:01 | 2022-08-11 05:03 | 135 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-05 | S22081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-11 | 270 | keep | 0 | Aug | 2022 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
PONCE | 2022-08-11 05:18 | 2022-08-11 05:55 | 60 | 0:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA EN C/L | P22081100010 | New_Event | Cutout Failure | Include | Include | Equipment | 37 | 2022-08-11 | 2220 | keep | 0 | Aug | 2022 | 0.001512 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-11 06:39 | 2022-08-11 11:49 | 46 | 5:10 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22081100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-08-11 | 14260 | keep | 0 | Aug | 2022 | 0.0097124 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
GUAYAMA | 2022-08-11 06:49 | 2022-08-11 10:30 | 35 | 3:41 | P | DESGANCHE | 1 X 50 EN RISER 2 X 40 EN RISER MONTURA AAA SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22081100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-08-11 | 7735 | keep | 0 | Aug | 2022 | 0.0052683 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-08-11 07:02 | 2022-08-11 17:10 | 1 | 10:08 | P | TRANSFORMADOR AVERIADO | SE ELIMINO XMR AVERIADO EN MONTURA Y SE HIZO COMBINACION NUEVA (DELTA ABIERTA) | B22081100004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 608 | 2022-08-11 | 608 | keep | 0 | Aug | 2022 | 0.00041411 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-11 07:03 | 2022-08-11 09:20 | 80 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22081100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-08-11 | 10960 | keep | 0 | Aug | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-11 07:04 | 2022-08-11 12:00 | 30 | 4:56 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22081100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-08-11 | 8880 | keep | 0 | Aug | 2022 | 0.0060481 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-08-11 07:09 | 2022-08-11 10:42 | 60 | 3:33 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22081100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-08-11 | 12780 | keep | 0 | Aug | 2022 | 0.0087044 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-11 07:11 | 2022-08-11 09:18 | 29 | 2:07 | P | ANIMAL | 1 X 15 SE RETIRO AVE | B22081100005 | New_Event | Animals | Include | Include | Wildlife | 127 | 2022-08-11 | 3683 | keep | 0 | Aug | 2022 | 0.0025085 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
YAUCO | 2022-08-11 07:19 | 2022-08-11 08:10 | 55 | 0:51 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22081100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-08-11 | 2805 | keep | 0 | Aug | 2022 | 0.0019105 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2022-08-11 07:21 | 2022-08-11 07:58 | 440 | 0:37 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO (A VARETA) DESDE EL PISO Y SE DESPEGARON LINEAS DEL 13KV (PEGADAS ENTRE SI) MEDIANTE G.O.I. SJ-220811-01 | S22081100007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 37 | 2022-08-11 | 16280 | keep | 0 | Aug | 2022 | 0.011088 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-11 07:23 | 2022-08-11 09:16 | 226 | 1:53 | P | ANIMAL | 2 X 80 EN C/L CRUCE POR AVE | R22081100009 | New_Event | Animals | Include | Include | Wildlife | 113 | 2022-08-11 | 25538 | keep | 0 | Aug | 2022 | 0.017394 | 0.00015393 | Sustained | FALSE | FALSE | Not_TMED_Event | 226
HUMACAO | 2022-08-11 07:24 | 2022-08-11 12:42 | 100 | 5:18 | P | ANIMAL | 1 X 80 EN C/L CRUCE X LAGARTIJO | C22081100013 | New_Event | Animals | Include | Include | Wildlife | 318 | 2022-08-11 | 31800 | keep | 0 | Aug | 2022 | 0.021659 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-11 07:57 | 2022-08-11 09:47 | 2 | 1:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22081100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-08-11 | 220 | keep | 0 | Aug | 2022 | 0.00014984 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-08-11 07:58 | 2022-08-11 09:09 | 3766 | 1:11 | T | NO SE REPORTO CAUSA | SE CERRO INTERRUPTOR SECCIONALIZANDO ALIMENTADOR EN SERVICIO 35% | R22081100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-08-11 | 267386 | keep | 0 | Aug | 2022 | 0.18212 | 0.002565 | Sustained | FALSE | FALSE | Not_TMED_Event | 3766
SAN JUAN | 2022-08-11 08:15 | 2022-08-11 08:56 | 150 | 0:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN PROVISIONAL NO CAUSA | S22081100057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 41 | 2022-08-11 | 6150 | keep | 0 | Aug | 2022 | 0.0041887 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-08-11 08:16 | 2022-08-11 10:33 | 2 | 2:17 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22081100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-08-11 | 274 | keep | 0 | Aug | 2022 | 0.00018662 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-11 08:33 | 2022-08-11 15:00 | 1347 | 6:27 | P | TERMINACION SOTERRADA AVERIADA | DISPARO LLEVA 1419-9 SE ENCONTRO Y SE REPARO BOLT T EN V.S.MH-38 | S22081100067 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 387 | 2022-08-11 | 521289 | keep | 0 | Aug | 2022 | 0.35505 | 0.00091744 | Sustained | FALSE | FALSE | Not_TMED_Event | 1347
SAN JUAN | 2022-08-11 08:33 | 2022-08-11 15:00 | 266 | 6:27 | T | TERMINACION SOTERRADA AVERIADA | DISPARO SU CARGA POR 1112-04 SE ENCONTRO Y SE REPARO BOLT T EN V.S.MH-38 | S22081100067 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 387 | 2022-08-11 | 102942 | keep | 0 | Aug | 2022 | 0.070113 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
YAUCO | 2022-08-11 08:42 | 2022-08-11 10:55 | 3 | 2:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22081100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-08-11 | 399 | keep | 0 | Aug | 2022 | 0.00027176 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-08-11 08:53 | 2022-08-11 08:54 | 3046 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE INTERRUPTOR 1646-03 LLEVANDO 15% 1647-09 | R22081100053 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-11 | 3046 | keep | 0 | Aug | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2022-08-11 08:53 | 2022-08-11 08:54 | 307 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE INTERRUPTOR 1646-03 LLEVANDO 15% 1647-09 | R22081100053 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-11 | 307 | keep | 0 | Aug | 2022 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
CANOVANAS | 2022-08-11 08:54 | 2022-08-11 10:20 | 30 | 1:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO PORTAFUSIBLE | R22081100063 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 86 | 2022-08-11 | 2580 | keep | 0 | Aug | 2022 | 0.0017572 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-11 09:09 | 2022-08-11 09:39 | 2448 | 0:30 | P | NO SE REPORTO CAUSA | SE CERRO MACHETESCON ALIMENTADOR SECCIONALIZADO. EN SERVICIO 40% | R22081100013 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-08-11 | 73440 | keep | 0 | Aug | 2022 | 0.05002 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-11 09:10 | 2022-08-11 14:00 | 6 | 4:50 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081100024 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 290 | 2022-08-11 | 1740 | keep | 0 | Aug | 2022 | 0.0011851 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-08-11 09:12 | 2022-08-11 13:49 | 1 | 4:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22081100025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2022-08-11 | 277 | keep | 0 | Aug | 2022 | 0.00018866 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-11 09:16 | 2022-08-11 13:14 | 100 | 3:58 | P | ANIMAL | 1 X 100 EN C/L Y 1 X 80 EN C/L AVE CRUZO LINEAS | R22081100065 | Partial_restoration | Animals | Include | Include | Wildlife | 238 | 2022-08-11 | 23800 | keep | 0 | Aug | 2022 | 0.01621 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-11 09:19 | 2022-08-11 12:00 | 15 | 2:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | B22081100019 | New_Event | Cutout Failure | Include | Include | Equipment | 161 | 2022-08-11 | 2415 | keep | 0 | Aug | 2022 | 0.0016448 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-08-11 09:22 | 2022-08-11 14:35 | 1 | 5:13 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R22081100067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 313 | 2022-08-11 | 313 | keep | 0 | Aug | 2022 | 0.00021318 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-11 09:22 | 2022-08-11 12:18 | 15 | 2:56 | P | ARBOL SOBRE LINEA | 2 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A22081100028 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 176 | 2022-08-11 | 2640 | keep | 0 | Aug | 2022 | 0.0017981 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-11 09:25 | 2022-08-11 09:26 | 5961 | 0:01 | T | CABLE SOTERRADO AVERIADO | RECERRO LLEVA 95% DEL 1717-02 | B22081000224 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-08-11 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-11 09:25 | 2022-08-11 09:26 | 865 | 0:01 | P | CABLE SOTERRADO AVERIADO | RECIERRE 95% DE SU CARGA POR 1713-05 | B22081000224 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-08-11 | 865 | keep | 0 | Aug | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2022-08-11 09:26 | 2022-08-11 10:27 | 40 | 1:01 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA DE RISER A T9 Y AVERIA VIEJA DE T9 A T13 | B22081000224 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 61 | 2022-08-11 | 2440 | keep | 0 | Aug | 2022 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-11 09:39 | 2022-08-11 09:59 | 2259 | 0:20 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES CON ALIMENTADOR SECCIONALIZADO. EN SERVICIO 75% | R22081100013 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 20 | 2022-08-11 | 45180 | keep | 0 | Aug | 2022 | 0.030772 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-11 09:51 | 2022-08-12 12:25 | 6 | 26:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LINEA | A22081100133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1594 | 2022-08-11 | 9564 | keep | 0 | Aug | 2022 | 0.006514 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-08-11 09:54 | 2022-08-11 09:55 | 2064 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22081100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 2064 | keep | 0 | Aug | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
CANOVANAS | 2022-08-11 09:59 | 2022-08-11 10:11 | 942 | 0:12 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES ALIMENTADOR EN SERVICIO 100% | R22081100013 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-08-11 | 11304 | keep | 0 | Aug | 2022 | 0.0076991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-11 10:18 | 2022-08-11 14:19 | 100 | 4:01 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L SE REPARO ALAMBRE PRIMARIO | P22081100035 | New_Event | Primary Wire Break | Include | Include | Equipment | 241 | 2022-08-11 | 24100 | keep | 0 | Aug | 2022 | 0.016414 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-11 10:25 | 2022-08-11 11:57 | 35 | 1:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 Y 1 X 65 Y SE REMPLAZO CAJA PRIMARIA Y AISLACION | R22081100087 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2022-08-11 | 3220 | keep | 0 | Aug | 2022 | 0.0021931 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2022-08-11 10:25 | 2022-08-11 15:49 | 52 | 5:24 | P | LINEA DE TRANSMISION 38KV | ABRIR C/L PARA TRABAJOS DE VIA LIBRE DE TRANSMISION PARA LEVANTAR CONDUCTOR DEL 38KV | C22081100045 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 324 | 2022-08-11 | 16848 | keep | 0 | Aug | 2022 | 0.011475 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2022-08-11 10:27 | 2022-08-11 10:28 | 5961 | 0:01 | T | CABLE SOTERRADO AVERIADO | RECERRO LLEVA 95% DEL 1717-02 | B22081100000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-08-11 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-11 10:27 | 2022-08-11 10:28 | 865 | 0:01 | P | CABLE SOTERRADO AVERIADO | RECERRO 95%POR 1713-05 | B22081100000 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-08-11 | 865 | keep | 0 | Aug | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2022-08-11 10:28 | 2022-08-11 20:22 | 40 | 9:54 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO TRAMO DE RISER @ T-9 1 X 40 EN RISER | B22081000224 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 594 | 2022-08-11 | 23760 | keep | 0 | Aug | 2022 | 0.016183 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-11 10:50 | 2022-08-11 13:53 | 50 | 3:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C22081100049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 183 | 2022-08-11 | 9150 | keep | 0 | Aug | 2022 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-11 10:55 | 2022-08-11 13:30 | 30 | 2:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 75KVA POR UNO DE 50KVA POR PROBLEMAS EN TAP CHANGER | M22081100043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 155 | 2022-08-11 | 4650 | keep | 0 | Aug | 2022 | 0.0031671 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-08-11 10:58 | 2022-08-11 10:59 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081100090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 2722 | keep | 0 | Aug | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2022-08-11 11:07 | 2022-08-11 15:52 | 10 | 4:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA 1 X 15 EN C/L | B22081100025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 285 | 2022-08-11 | 2850 | keep | 0 | Aug | 2022 | 0.0019411 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-11 11:14 | 2022-08-11 17:35 | 8 | 6:21 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA REEMPLAZAR PEDESTAL SECUNDARIO | C22081100074 | New_Event |  |  |  |  | 381 | 2022-08-11 | 3048 | keep | 0 | Aug | 2022 | 0.002076 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-11 11:16 | 2022-08-11 18:12 | 5 | 6:56 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22081100092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2022-08-11 | 2080 | keep | 0 | Aug | 2022 | 0.0014167 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-11 11:23 | 2022-08-11 11:24 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 4641 | keep | 0 | Aug | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
SAN JUAN | 2022-08-11 11:25 | 2022-08-11 13:53 | 15 | 2:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON APROX. 100' DE ALAMBRE SECUNDARIO CALIBRE 3/4 - AL (NO FUNDIO) | S22081100179 | New_Event | Secondary Wire Break | Include | Include | Equipment | 148 | 2022-08-11 | 2220 | keep | 0 | Aug | 2022 | 0.001512 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-08-11 11:27 | 2022-08-11 11:28 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22081100095 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 2722 | keep | 0 | Aug | 2022 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
AGUADILLA | 2022-08-11 11:47 | 2022-08-11 13:00 | 40 | 1:13 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA VEHICULO IMPACTO CABLE TELEFONICOS CAUSANDO MOVIMIENTO Y CRUCE DE LINEAS PRIMARIAS | M22081100052 | New_Event | Damage From Public | Include | Include | Public | 73 | 2022-08-11 | 2920 | keep | 0 | Aug | 2022 | 0.0019888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-11 11:49 | 2022-08-11 13:26 | 1 | 1:37 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22081100100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-08-11 | 97 | keep | 0 | Aug | 2022 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-11 11:57 | 2022-08-11 15:02 | 1 | 3:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA ANTENA T-MOBILE | A22081100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-08-11 | 185 | keep | 0 | Aug | 2022 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-11 12:00 | 2022-08-11 12:48 | 3 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO ROTO | M22081100046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2022-08-11 | 144 | keep | 0 | Aug | 2022 | 9.8078e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-11 12:10 | 2022-08-11 13:27 | 3 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B22081100032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2022-08-11 | 231 | keep | 0 | Aug | 2022 | 0.00015733 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-11 12:13 | 2022-08-11 15:11 | 6 | 2:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B22081100033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 178 | 2022-08-11 | 1068 | keep | 0 | Aug | 2022 | 0.00072741 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-11 12:19 | 2022-08-11 14:58 | 100 | 2:39 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEA | B22081100034 | New_Event | Animals | Include | Include | Wildlife | 159 | 2022-08-11 | 15900 | keep | 0 | Aug | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-11 12:26 | 2022-08-11 15:12 | 15 | 2:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 75KVA X 75KVA | A22081100055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 166 | 2022-08-11 | 2490 | keep | 0 | Aug | 2022 | 0.0016959 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-08-11 12:39 | 2022-08-11 16:34 | 10 | 3:55 | P | PROBLEMA DEL CLIENTE | 1 X 100 EN C/ L Y 1 X 100 EN SU AVERIA INTERNA EN EDIFICIO NORTE MANSIONES DE GARDEN HILLS | S22081100198 | New_Event | Customer-Related Interruption | Include | Include | Public | 235 | 2022-08-11 | 2350 | keep | 0 | Aug | 2022 | 0.0016006 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-11 12:44 | 2022-08-11 17:20 | 3 | 4:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO PORTAFUSIBLE | B22081100037 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2022-08-11 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2022-08-11 13:07 | 2022-08-11 17:40 | 1 | 4:33 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081100090 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 273 | 2022-08-11 | 273 | keep | 0 | Aug | 2022 | 0.00018594 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-11 13:08 | 2022-08-11 16:21 | 20 | 3:13 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22081100054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-08-11 | 3860 | keep | 0 | Aug | 2022 | 0.002629 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-08-11 13:12 | 2022-08-11 14:26 | 2 | 1:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO | P22081100062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 74 | 2022-08-11 | 148 | keep | 0 | Aug | 2022 | 0.0001008 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-11 13:14 | 2022-08-11 13:15 | 637 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | M22081100082 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-11 | 637 | keep | 0 | Aug | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-08-11 13:14 | 2022-08-11 13:15 | 1491 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR 6703-02 QUE LLEVA LA CARGA DEL 6703-03 | M22081100082 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-11 | 1491 | keep | 0 | Aug | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-08-11 13:18 | 2022-08-11 13:19 | 637 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | M22081100086 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-11 | 637 | keep | 0 | Aug | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-08-11 13:18 | 2022-08-11 13:19 | 1491 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR 6703-02 QUE LLEVA LA CARGA DEL 6703-03 | M22081100086 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-11 | 1491 | keep | 0 | Aug | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-08-11 13:19 | 2022-08-11 13:20 | 150 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS Y LLUVIAS FUERTES | M22081100084 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-11 | 150 | keep | 0 | Aug | 2022 | 0.00010216 | 0.00010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-11 13:20 | 2022-08-11 13:21 | 637 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | M22081100087 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-11 | 637 | keep | 0 | Aug | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-08-11 13:20 | 2022-08-11 13:21 | 1491 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR 6703-02 QUE LLEVA LA CARGA DEL 6703-03 | M22081100087 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-11 | 1491 | keep | 0 | Aug | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-08-11 13:21 | 2022-08-11 15:56 | 150 | 2:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS Y LLUVIAS FUERTES | M22081100084 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 155 | 2022-08-11 | 23250 | keep | 0 | Aug | 2022 | 0.015835 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-11 13:25 | 2022-08-11 17:49 | 300 | 4:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22081100092 | New_Event | Cutout Failure | Include | Include | Equipment | 264 | 2022-08-11 | 79200 | keep | 0 | Aug | 2022 | 0.053943 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-08-11 13:36 | 2022-08-11 13:51 | 1026 | 0:15 | T | FUEGO | SE ABRE BKR PARA SECCIONALIZAR FUEGO. PERSONAL DE CAMPO LLAMO PARA DISPARO. RELACCIONADO A R22081100114. | R22081100115 | New_Event | Fire | Include | Include | Public | 15 | 2022-08-11 | 15390 | keep | 0 | Aug | 2022 | 0.010482 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2022-08-11 13:37 | 2022-08-11 15:10 | 188 | 1:33 | T | FUEGO | SE ABRE BKR PARA SECCIONALIZAR FUEGO. PERSONAL DE CAMPO LLAMO PARA DISPARO. RELACIONADO A R22081100114 SE PASO 100% DE LA CARGA AL 1203-01 | R22081100115 | New_Event | Fire | Include | Include | Public | 93 | 2022-08-11 | 17484 | keep | 0 | Aug | 2022 | 0.011908 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
MAYAGÃœEZ | 2022-08-11 13:47 | 2022-08-11 13:48 | 409 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22081100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 409 | keep | 0 | Aug | 2022 | 0.00027857 | 0.00027857 | Momentary | FALSE | FALSE | Not_TMED_Event | 409
MAYAGÃœEZ | 2022-08-11 13:47 | 2022-08-11 17:41 | 150 | 3:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081100098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-08-11 | 35100 | keep | 0 | Aug | 2022 | 0.023906 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-11 13:47 | 2022-08-11 17:43 | 10 | 3:56 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M22081100092 | New_Event | Primary Wire Break | Include | Include | Equipment | 236 | 2022-08-11 | 2360 | keep | 0 | Aug | 2022 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-11 13:50 | 2022-08-11 14:51 | 10 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22081100057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2022-08-11 | 610 | keep | 0 | Aug | 2022 | 0.00041547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-11 13:51 | 2022-08-11 13:55 | 923 | 0:04 | P | FUEGO | SE PASA EL 10% DE LA CARGA AL 1647-08 CERRANDO N/O ENTRE AMBOS PARA SECCIONALIZAR AREA EN FUEGO. SE DEJO 90% DEL ALIMENTADOR EN SERVICIO | R22081100115 | Partial_restoration | Fire | Include | Include | Public | 4 | 2022-08-11 | 3692 | keep | 0 | Aug | 2022 | 0.0025146 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-11 13:55 | 2022-08-11 16:57 | 102 | 3:02 | P | FUEGO | BOMBEROS EXTINGUIO FUEGO Y SE CERRARON MACHETES QUE SECCIONALIZABAN HACIA EL FUEGO. TAMBIEN SE NORMALIZARON CARGAS | R22081100115 | 1st_after_momentary | Fire | Include | Include | Public | 182 | 2022-08-11 | 18564 | keep | 0 | Aug | 2022 | 0.012644 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
GUAYAMA | 2022-08-11 13:55 | 2022-08-11 13:56 | 836 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22081100071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 836 | keep | 0 | Aug | 2022 | 0.0005694 | 0.0005694 | Momentary | FALSE | FALSE | Not_TMED_Event | 836
PONCE | 2022-08-11 14:07 | 2022-08-11 14:08 | 860 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22081100072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 860 | keep | 0 | Aug | 2022 | 0.00058574 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
MAYAGÃœEZ | 2022-08-11 14:15 | 2022-08-11 14:16 | 3230 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22081100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 3230 | keep | 0 | Aug | 2022 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
VEGA BAJA | 2022-08-11 14:15 | 2022-08-11 15:35 | 7 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22081100061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2022-08-11 | 560 | keep | 0 | Aug | 2022 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-08-11 14:18 | 2022-08-11 15:00 | 250 | 0:42 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE CON VOLTAJE SIN CARGA EN ANCLADA ANTES DE MACHETES | C22081100052 | New_Event | Primary Wire Break | Include | Include | Equipment | 42 | 2022-08-11 | 10500 | keep | 0 | Aug | 2022 | 0.0071515 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2022-08-11 14:20 | 2022-08-11 15:20 | 10 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA SECUNDARIA EN PEDESTAL | R22081100120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-08-11 | 600 | keep | 0 | Aug | 2022 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-11 14:25 | 2022-08-11 16:26 | 30 | 2:01 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE | R22081100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-08-11 | 3630 | keep | 0 | Aug | 2022 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-11 14:26 | 2022-08-11 14:27 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22081100111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 4304 | keep | 0 | Aug | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
VEGA BAJA | 2022-08-11 14:33 | 2022-08-11 18:03 | 130 | 3:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REEMPLAZARON DOS CAJAS PRIMARIAS DE 100 AMP | A22081100066 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2022-08-11 | 27300 | keep | 0 | Aug | 2022 | 0.018594 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
MAYAGÃœEZ | 2022-08-11 14:37 | 2022-08-11 18:26 | 300 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 65 Y 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081100114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2022-08-11 | 68700 | keep | 0 | Aug | 2022 | 0.046791 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2022-08-11 14:46 | 2022-08-11 19:23 | 50 | 4:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS Y LLUVIAS FUERTES | M22081100121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 277 | 2022-08-11 | 13850 | keep | 0 | Aug | 2022 | 0.0094332 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-11 14:47 | 2022-08-11 14:48 | 1818 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22081100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 1818 | keep | 0 | Aug | 2022 | 0.0012382 | 0.0012382 | Momentary | FALSE | FALSE | Not_TMED_Event | 1818
MAYAGÃœEZ | 2022-08-11 14:49 | 2022-08-11 14:50 | 863 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22081100127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 863 | keep | 0 | Aug | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
PONCE | 2022-08-11 14:59 | 2022-08-11 17:23 | 2 | 2:24 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE | P22081100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-08-11 | 288 | keep | 0 | Aug | 2022 | 0.00019616 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-11 15:01 | 2022-08-11 15:02 | 4304 | 0:01 | T | MAL TIEMPO/RAYOS | RECERRO INTERRUPTOR QUEDO FUERA DE SERVICIO SE INTENTO CERRAR POR SCADA Y SE QUEDO | M22081100000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-11 | 4304 | keep | 0 | Aug | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2022-08-11 15:05 | 2022-08-11 17:21 | 4304 | 2:16 | T | MAL TIEMPO/RAYOS | INTERRUPTOR RECERRO TRES VECES Y QUEDO FUERA DE SERVICIO. SE PROCEDIO A ABRIR EN AMARRE PARA SECCIONALIZAR (FID: 17525022), PROBAR INTERRUPTOR Y DETERMINAR EL AREA DE LA POSIBLE AVERIA. INTERRUPTOR QUEDO EN SERVICIO CON UN 5%. | M22081100142 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 136 | 2022-08-11 | 585344 | keep | 0 | Aug | 2022 | 0.39868 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
BARRANQUITAS | 2022-08-11 15:16 | 2022-08-11 18:23 | 60 | 3:07 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22081100080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-08-11 | 11220 | keep | 0 | Aug | 2022 | 0.0076419 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-08-11 15:21 | 2022-08-11 17:42 | 60 | 2:21 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22081100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2022-08-11 | 8460 | keep | 0 | Aug | 2022 | 0.0057621 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-08-11 15:25 | 2022-08-11 22:14 | 8 | 6:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 15 EN TRANSFORMADOR POR LLUVIAS | A22081100079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 409 | 2022-08-11 | 3272 | keep | 0 | Aug | 2022 | 0.0022285 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-11 15:27 | 2022-08-11 15:28 | 2530 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR | M22081100164 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-11 | 2530 | keep | 0 | Aug | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
UTUADO | 2022-08-11 15:27 | 2022-08-11 18:09 | 60 | 2:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | A22081100080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-08-11 | 9720 | keep | 0 | Aug | 2022 | 0.0066202 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-11 15:28 | 2022-08-11 18:39 | 9 | 3:11 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081100267 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 191 | 2022-08-11 | 1719 | keep | 0 | Aug | 2022 | 0.0011708 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2022-08-11 15:28 | 2022-08-11 20:33 | 70 | 5:05 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22081100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-08-11 | 21350 | keep | 0 | Aug | 2022 | 0.014541 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-08-11 15:29 | 2022-08-11 15:30 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22081100166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 199 | keep | 0 | Aug | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2022-08-11 15:30 | 2022-08-11 16:02 | 1 | 0:32 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S22081100237 | New_Event | Primary Wire Break | Include | Include | Equipment | 32 | 2022-08-11 | 32 | keep | 0 | Aug | 2022 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-11 15:30 | 2022-08-11 19:25 | 5 | 3:55 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081100165 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 235 | 2022-08-11 | 1175 | keep | 0 | Aug | 2022 | 0.00080029 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-11 15:35 | 2022-08-11 18:45 | 10 | 3:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22081100083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 190 | 2022-08-11 | 1900 | keep | 0 | Aug | 2022 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-11 15:46 | 2022-08-11 16:16 | 1 | 0:30 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22081100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-08-11 | 30 | keep | 0 | Aug | 2022 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-11 15:49 | 2022-08-11 18:36 | 6 | 2:47 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO WORKPACK 29159 | B22081100048 | New_Event | Primary Pole Failure | Include | Include | Equipment | 167 | 2022-08-11 | 1002 | keep | 0 | Aug | 2022 | 0.00068246 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-11 15:51 | 2022-08-11 16:54 | 100 | 1:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-08-11 | 6300 | keep | 0 | Aug | 2022 | 0.0042909 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-11 15:58 | 2022-08-13 15:20 | 25 | 47:22 | P | CONDUCTOR ROTO O ABIERTO | 2 X 15 EN BACK TO BACK SE REPARO LINEA PRIMARIA | A22081100088 | New_Event | Primary Wire Break | Include | Include | Equipment | 2842 | 2022-08-11 | 71050 | keep | 0 | Aug | 2022 | 0.048392 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-08-11 16:03 | 2022-08-11 16:04 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 2302 | keep | 0 | Aug | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
VEGA BAJA | 2022-08-11 16:04 | 2022-08-11 16:05 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2208110000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 4027 | keep | 0 | Aug | 2022 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
ARECIBO | 2022-08-11 16:10 | 2022-08-11 17:37 | 50 | 1:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22081100090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-08-11 | 4350 | keep | 0 | Aug | 2022 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-11 16:13 | 2022-08-11 19:22 | 4 | 3:09 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | P22081100088 | New_Event | Animals | Include | Include | Wildlife | 189 | 2022-08-11 | 756 | keep | 0 | Aug | 2022 | 0.00051491 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-08-11 16:22 | 2022-08-12 08:30 | 37 | 16:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L Y SE REPARO NEUTRAL PRIMARIO DESGANCHE | C22081100089 | New_Event | Primary Wire Break | Include | Include | Equipment | 968 | 2022-08-11 | 35816 | keep | 0 | Aug | 2022 | 0.024394 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BARRANQUITAS | 2022-08-11 16:22 | 2022-08-12 08:04 | 120 | 15:42 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22081100089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 942 | 2022-08-11 | 113040 | keep | 0 | Aug | 2022 | 0.076991 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
UTUADO | 2022-08-11 16:35 | 2022-08-11 21:24 | 20 | 4:49 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081100093 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 289 | 2022-08-11 | 5780 | keep | 0 | Aug | 2022 | 0.0039367 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-11 16:38 | 2022-08-11 21:25 | 12 | 4:47 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081100094 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 287 | 2022-08-11 | 3444 | keep | 0 | Aug | 2022 | 0.0023457 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-11 16:41 | 2022-08-11 23:06 | 8 | 6:25 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR RAYOS | M22081100229 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 385 | 2022-08-11 | 3080 | keep | 0 | Aug | 2022 | 0.0020978 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-11 16:44 | 2022-08-11 21:48 | 45 | 5:04 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081100232 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 304 | 2022-08-11 | 13680 | keep | 0 | Aug | 2022 | 0.0093174 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-08-11 17:05 | 2022-08-11 18:30 | 12 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA EN PEDESTAL | B22081000011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2022-08-11 | 1020 | keep | 0 | Aug | 2022 | 0.00069472 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-11 17:11 | 2022-08-12 09:48 | 30 | 16:37 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081100258 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 997 | 2022-08-11 | 29910 | keep | 0 | Aug | 2022 | 0.020372 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-08-11 17:16 | 2022-08-12 09:54 | 6 | 16:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22081100093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 998 | 2022-08-11 | 5988 | keep | 0 | Aug | 2022 | 0.0040784 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-11 17:21 | 2022-08-11 18:00 | 4089 | 0:39 | P | MAL TIEMPO/RAYOS | SE ENCONTRO CAJA PRIMARIA AVERIADA POR RAYO Y TRANSFORMADOR QUEMADO. SE REFIRIO PARA ATENDER DE INMEDIATO. SE DESCONECTO BAJANTE PRIMARIO PARA AISLAR SITUACION Y SE REEMPLAZO 1 X 140 EN CORTE DE LINEA QUE SE ENCONTRABA FUNDIDO EN INTERSECCION CERCANA | M22081100142 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 39 | 2022-08-11 | 159471 | keep | 0 | Aug | 2022 | 0.10861 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-11 17:23 | 2022-08-11 18:13 | 18 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REMPLAZAR SECUNDARIA TRAS PATIO | S22081100248 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-08-11 | 900 | keep | 0 | Aug | 2022 | 0.00061299 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-08-11 17:29 | 2022-08-11 17:30 | 637 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE DEL INTERRUPTOR CONDUCTOR NO LE DA SERVICIO A NADIE LLEVA CARGA DE 6703-03 | M22081100274 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-11 | 637 | keep | 0 | Aug | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-08-11 17:29 | 2022-08-11 17:30 | 1491 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE DEL INTERRUPTOR CONDUCTOR NO LE SERVICO A NADIE CARGA POR 6703-02 | M22081100274 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-11 | 1491 | keep | 0 | Aug | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
YAUCO | 2022-08-11 17:34 | 2022-08-12 10:20 | 153 | 16:46 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA DESCARGA ELECTRICA | P22081100096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1006 | 2022-08-11 | 153918 | keep | 0 | Aug | 2022 | 0.10483 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
MAYAGÃœEZ | 2022-08-11 17:35 | 2022-08-11 19:30 | 75 | 1:55 | P | SECUNDARIA/DESGANCHE | 1 X 65 EN CORTE DE LINEA SE DESGANCHO EN LINEA SECUNDARIAS | M22081100283 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 115 | 2022-08-11 | 8625 | keep | 0 | Aug | 2022 | 0.0058744 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-08-11 17:51 | 2022-08-11 20:45 | 1 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | A22081100103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-11 | 174 | keep | 0 | Aug | 2022 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-11 17:54 | 2022-08-11 18:07 | 43 | 0:13 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO MH-1 FTE. A WALLGRENS PARA PASAR CARGA DEL 1115-05 AL 1117-07 SE REPARO AVERIA MACHETE QUEMADO | S22081100103 | New_Event | Switch Failure | Include | Include | Equipment | 13 | 2022-08-11 | 559 | keep | 0 | Aug | 2022 | 0.00038073 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
MAYAGÃœEZ | 2022-08-11 18:00 | 2022-08-11 20:50 | 2000 | 2:50 | P | MAL TIEMPO/RAYOS | SE ENCONTRO CAJA PRIMARIA AVERIADA POR RAYO Y TRANSFORMADOR QUEMADO. SE REFIRIO PARA ATENDER DE INMEDIATO. SE DESCONECTO BAJANTE PRIMARIO PARA AISLAR SITUACION Y SE REEMPLAZO 1 X 140 EN CORTE DE LINEA QUE SE ENCONTRABA FUNDIDO EN INTERSECCION CERCANA | M22081100142 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 170 | 2022-08-11 | 340000 | keep | 0 | Aug | 2022 | 0.23157 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-11 18:10 | 2022-08-11 21:31 | 60 | 3:21 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 30 EN CORTE DE LINEA NO CAUSA | S22081100253 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-08-11 | 12060 | keep | 0 | Aug | 2022 | 0.008214 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-08-11 18:10 | 2022-08-11 22:23 | 2 | 4:13 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR RAYOS | A22081100107 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 253 | 2022-08-11 | 506 | keep | 0 | Aug | 2022 | 0.00034463 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-11 18:29 | 2022-08-12 12:00 | 8 | 17:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | M22081100312 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1051 | 2022-08-11 | 8408 | keep | 0 | Aug | 2022 | 0.0057267 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-11 18:30 | 2022-08-11 22:47 | 36 | 4:17 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO SU-1 | S22081100251 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 257 | 2022-08-11 | 9252 | keep | 0 | Aug | 2022 | 0.0063015 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2022-08-11 18:32 | 2022-08-11 19:43 | 25 | 1:11 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVE QUE CRUZO LINEAS | A22081100109 | New_Event | Animals | Include | Include | Wildlife | 71 | 2022-08-11 | 1775 | keep | 0 | Aug | 2022 | 0.0012089 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-11 18:36 | 2022-08-12 15:45 | 30 | 21:09 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22081100318 | New_Event | Primary Wire Break | Include | Include | Equipment | 1269 | 2022-08-11 | 38070 | keep | 0 | Aug | 2022 | 0.025929 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-11 18:42 | 2022-08-11 22:23 | 50 | 3:41 | P | MAL TIEMPO/RAYOS | 1 X 30 Y 1 X 40 EN CORTE DE LINEA POR RAYOS | M22081100322 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 221 | 2022-08-11 | 11050 | keep | 0 | Aug | 2022 | 0.0075261 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-11 18:43 | 2022-08-12 09:15 | 4 | 14:32 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22081100324 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 872 | 2022-08-11 | 3488 | keep | 0 | Aug | 2022 | 0.0023757 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-11 18:48 | 2022-08-11 20:10 | 15 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | S22081100255 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2022-08-11 | 1230 | keep | 0 | Aug | 2022 | 0.00083775 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-08-11 18:55 | 2022-08-12 17:56 | 10 | 23:01 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO @ T-26 | C22081100102 | New_Event | UG Cable Fault | Include | Include | Equipment | 1381 | 2022-08-11 | 13810 | keep | 0 | Aug | 2022 | 0.0094059 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-11 18:57 | 2022-08-11 20:48 | 100 | 1:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REFIRIO SITUACION DE DESGANCHE | M22081100333 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-08-11 | 11100 | keep | 0 | Aug | 2022 | 0.0075602 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-11 19:03 | 2022-08-12 16:20 | 125 | 21:17 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081100337 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1277 | 2022-08-11 | 159625 | keep | 0 | Aug | 2022 | 0.10872 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-08-11 19:08 | 2022-08-11 19:11 | 637 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION DE EMANUEL MONTERO PARA RETIRAR PELIGRO YA QUE SE ENCONTRO LINEA PRIMARIA ROTA EN EL SUELO. UNA VEZ SE RETIRO PELIGRO SE PROCEDIO A CERRAR POR SCADA. ALAMBRE NO LE DA SERVICIO A NADIE LLEVA CARGA DE 6703-03 | M22081100345 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-11 | 1911 | keep | 0 | Aug | 2022 | 0.0013016 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-08-11 19:08 | 2022-08-11 19:11 | 1491 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION DE EMANUEL MONTERO PARA RETIRAR PELIGRO YA QUE SE ENCONTRO LINEA PRIMARIA ROTA EN EL SUELO. UNA VEZ SE RETIRO PELIGRO SE PROCEDIO A CERRAR POR SCADA. CARGA POR 6703-02 | M22081100345 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-08-11 | 4473 | keep | 0 | Aug | 2022 | 0.0030465 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
CANOVANAS | 2022-08-11 19:23 | 2022-08-11 20:23 | 6 | 1:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22081100129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2022-08-11 | 360 | keep | 0 | Aug | 2022 | 0.00024519 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-08-11 19:25 | 2022-08-11 19:26 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081100130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 7621 | keep | 0 | Aug | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2022-08-11 19:27 | 2022-08-12 11:42 | 70 | 16:15 | P | CABLE SOTERRADO AVERIADO | AVERIA DE RISER @T-21 SE CERRO N/O EN T-23 | S22081100258 | New_Event | UG Cable Fault | Include | Include | Equipment | 975 | 2022-08-11 | 68250 | keep | 0 | Aug | 2022 | 0.046485 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-08-11 19:27 | 2022-08-11 20:43 | 200 | 1:16 | P | CONDUCTOR ROTO O ABIERTO | 3 X 100 EN C/L SE FIJO LINEA SAFADA A AISLADOR | P22081100112 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2022-08-11 | 15200 | keep | 0 | Aug | 2022 | 0.010353 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-11 19:30 | 2022-08-12 13:50 | 125 | 18:20 | P | MAL TIEMPO/RAYOS | 1 X 65 Y 2 X 40 EN DISTINTOS CORTES DE LINEA DESCARGAS ELECTRICAS | M22081100364 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1100 | 2022-08-11 | 137500 | keep | 0 | Aug | 2022 | 0.093651 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2022-08-11 19:36 | 2022-08-12 02:15 | 24 | 6:39 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO RAMA SOBRE LINEA PRIMARIA | P22081100115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2022-08-11 | 9576 | keep | 0 | Aug | 2022 | 0.0065222 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
UTUADO | 2022-08-11 19:36 | 2022-08-12 17:00 | 30 | 21:24 | P | DESGANCHE | SE RETIRO RAMAS DE LAS LINEAS SE CERRO CORTE DE LINEA QUE SE HABIA ABIERTO PARA RETIRAR PELIGRO | A22081100117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1284 | 2022-08-11 | 38520 | keep | 0 | Aug | 2022 | 0.026236 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-08-11 19:39 | 2022-08-12 10:15 | 10 | 14:36 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22081100371 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 876 | 2022-08-11 | 8760 | keep | 0 | Aug | 2022 | 0.0059664 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-11 19:40 | 2022-08-11 22:07 | 20 | 2:27 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO TRAS PATIO | S22081100261 | New_Event | Primary Wire Break | Include | Include | Equipment | 147 | 2022-08-11 | 2940 | keep | 0 | Aug | 2022 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-11 20:01 | 2022-08-12 09:20 | 300 | 13:19 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081100388 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 799 | 2022-08-11 | 239700 | keep | 0 | Aug | 2022 | 0.16326 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2022-08-11 20:03 | 2022-08-12 08:11 | 4 | 12:08 | P | ANIMAL | 1 X 20 EN XMR CRUCE POR AVE | C22081100107 | New_Event | Animals | Include | Include | Wildlife | 728 | 2022-08-11 | 2912 | keep | 0 | Aug | 2022 | 0.0019833 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-08-11 20:28 | 2022-08-11 20:29 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22081100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 449 | keep | 0 | Aug | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
GUAYAMA | 2022-08-11 20:36 | 2022-08-12 10:35 | 10 | 13:59 | P | ANIMAL | 2 X 10 EN TRANSFORMADOR RATON CRUZO FASE | P22081100123 | New_Event | Animals | Include | Include | Wildlife | 839 | 2022-08-11 | 8390 | keep | 0 | Aug | 2022 | 0.0057144 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-11 20:37 | 2022-08-11 22:59 | 2 | 2:22 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR RAYOS | M22081100401 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 142 | 2022-08-11 | 284 | keep | 0 | Aug | 2022 | 0.00019343 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-08-11 20:55 | 2022-08-11 23:41 | 80 | 2:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | A22081100126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 166 | 2022-08-11 | 13280 | keep | 0 | Aug | 2022 | 0.0090449 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-11 21:06 | 2022-08-12 10:40 | 100 | 13:34 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REMPLAZO UN AISLADOR ROTO | M22081100413 | New_Event | Vegetation Contact | Include | Include | Vegetation | 814 | 2022-08-11 | 81400 | keep | 0 | Aug | 2022 | 0.055441 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-11 21:07 | 2022-08-12 04:06 | 5 | 6:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR POR LLUVIAS | M22081100414 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 419 | 2022-08-11 | 2095 | keep | 0 | Aug | 2022 | 0.0014269 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-11 21:26 | 2022-08-11 21:27 | 2324 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-11 | 2324 | keep | 0 | Aug | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
VEGA BAJA | 2022-08-11 21:40 | 2022-08-11 23:36 | 10 | 1:56 | P | SECUNDARIA/OTROS | SE REMPLAZO BARRA PEDESTAL Y PEDESTAL QUEDO VOLTAJE 124 X FASE | B22081100060 | New_Event |  |  |  |  | 116 | 2022-08-11 | 1160 | keep | 0 | Aug | 2022 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-11 21:51 | 2022-08-12 03:02 | 10 | 5:11 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR RAYOS | M22081100421 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 311 | 2022-08-11 | 3110 | keep | 0 | Aug | 2022 | 0.0021182 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-11 22:00 | 2022-08-12 09:34 | 8 | 11:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA @ BUSHING (A LA ENTRADA DE XMR) | S22081100273 | New_Event | Primary Wire Break | Include | Include | Equipment | 694 | 2022-08-11 | 5552 | keep | 0 | Aug | 2022 | 0.0037814 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-11 22:06 | 2022-08-12 09:00 | 8 | 10:54 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22081100422 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 654 | 2022-08-11 | 5232 | keep | 0 | Aug | 2022 | 0.0035635 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-11 22:07 | 2022-08-11 23:01 | 54 | 0:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO Y SE CERRO CORTE DE LINEA | S22081100261 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 54 | 2022-08-11 | 2916 | keep | 0 | Aug | 2022 | 0.0019861 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-11 22:16 | 2022-08-12 17:35 | 40 | 19:19 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081100423 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1159 | 2022-08-11 | 46360 | keep | 0 | Aug | 2022 | 0.031576 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-11 22:28 | 2022-08-12 09:40 | 30 | 11:12 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA SE RETIRO IGUANA | A22081100135 | New_Event | Animals | Include | Include | Wildlife | 672 | 2022-08-11 | 20160 | keep | 0 | Aug | 2022 | 0.013731 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-11 22:46 | 2022-08-12 13:52 | 100 | 15:06 | P | ARBOL SOBRE LINEA | 1 X 50 EN C/L SE RETIRO ARBOL | B22081100061 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 906 | 2022-08-11 | 90600 | keep | 0 | Aug | 2022 | 0.061707 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-08-11 23:16 | 2022-08-12 09:30 | 30 | 10:14 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22081100135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 614 | 2022-08-11 | 18420 | keep | 0 | Aug | 2022 | 0.012546 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-11 23:28 | 2022-08-12 04:09 | 1 | 4:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN RISER SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22081100428 | New_Event | Cutout Failure | Include | Include | Equipment | 281 | 2022-08-11 | 281 | keep | 0 | Aug | 2022 | 0.00019139 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-12 01:14 | 2022-08-12 03:11 | 48 | 1:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO | S22081200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-08-12 | 5616 | keep | 0 | Aug | 2022 | 0.003825 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
VEGA BAJA | 2022-08-12 01:24 | 2022-08-12 08:21 | 200 | 6:57 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B22081200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2022-08-12 | 83400 | keep | 0 | Aug | 2022 | 0.056803 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-12 04:00 | 2022-08-12 09:34 | 100 | 5:34 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081200008 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 334 | 2022-08-12 | 33400 | keep | 0 | Aug | 2022 | 0.022749 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-08-12 05:44 | 2022-08-12 05:45 | 3114 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22081200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-12 | 3114 | keep | 0 | Aug | 2022 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BARRANQUITAS | 2022-08-12 06:41 | 2022-08-12 17:58 | 120 | 11:17 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PARTIDO Y REEMPLAZO XMR 25KVA X 37.5KVA | C22081200033 | New_Event | Primary Pole Failure | Include | Include | Equipment | 677 | 2022-08-12 | 81240 | keep | 0 | Aug | 2022 | 0.055332 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2022-08-12 07:01 | 2022-08-12 08:14 | 11 | 1:13 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHE Y REPARAR SECUNDARIA | C22081100106 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 73 | 2022-08-12 | 803 | keep | 0 | Aug | 2022 | 0.00054692 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-08-12 07:05 | 2022-08-12 07:50 | 9 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22080500088 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-08-12 | 405 | keep | 0 | Aug | 2022 | 0.00027584 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-08-12 07:19 | 2022-08-12 10:56 | 8 | 3:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA DE TRANSFORMADOR PARA LEVANTAR SECUNDARIA | S22081200006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 217 | 2022-08-12 | 1736 | keep | 0 | Aug | 2022 | 0.0011824 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-12 07:29 | 2022-08-12 18:55 | 50 | 11:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22081200007 | New_Event | Cutout Failure | Include | Include | Equipment | 686 | 2022-08-12 | 34300 | keep | 0 | Aug | 2022 | 0.023362 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-12 08:01 | 2022-08-12 15:10 | 5 | 7:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22081200036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 429 | 2022-08-12 | 2145 | keep | 0 | Aug | 2022 | 0.0014609 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-12 08:02 | 2022-08-12 10:05 | 2 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTICAS | M22081200037 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-08-12 | 246 | keep | 0 | Aug | 2022 | 0.00016755 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-12 08:15 | 2022-08-12 11:50 | 50 | 3:35 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR POR DESCARGAS ELECTRICA | M22081200040 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 215 | 2022-08-12 | 10750 | keep | 0 | Aug | 2022 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-12 08:24 | 2022-08-12 08:27 | 3420 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-12 | 10260 | keep | 0 | Aug | 2022 | 0.006988 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
VEGA BAJA | 2022-08-12 08:27 | 2022-08-12 12:44 | 40 | 4:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A22081200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-08-12 | 10280 | keep | 0 | Aug | 2022 | 0.0070017 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-12 08:29 | 2022-08-12 13:48 | 1 | 5:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A22081200045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 319 | 2022-08-12 | 319 | keep | 0 | Aug | 2022 | 0.00021727 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-12 08:33 | 2022-08-12 18:45 | 1 | 10:12 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081200047 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 612 | 2022-08-12 | 612 | keep | 0 | Aug | 2022 | 0.00041683 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-12 09:00 | 2022-08-12 15:59 | 1 | 6:59 | P | DESGANCHE | SE ABRIO CORTE DE LINEA TRIFASICO QUE DA SERVICIO A BOMAS DE AGUA DE UPR PARA DESGANCHAR | C22081200018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2022-08-12 | 419 | keep | 0 | Aug | 2022 | 0.00028538 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-12 09:00 | 2022-08-12 09:50 | 8 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA AVERIADA | P22081200014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-08-12 | 400 | keep | 0 | Aug | 2022 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-12 09:00 | 2022-08-12 09:25 | 8 | 0:25 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA VERIFICAR AVERIA EN BASE DE CONTADOR MULTIPLE Y SE DEJO ABIERTA YA QUE LA MISMA ESTA AVERIADA Y SE VOLVIO A CERRAR EL TRANSFORMADOR | M22081200009 | New_Event |  |  |  |  | 25 | 2022-08-12 | 200 | keep | 0 | Aug | 2022 | 0.00013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-12 09:10 | 2022-08-12 14:52 | 6 | 5:42 | P | PROBLEMA DEL CLIENTE | SE ABRE XMR Y SE CIERRA AL SER PROBLEMA INTERNO DE CLIENTE | S22081200014 | New_Event | Customer-Related Interruption | Include | Include | Public | 342 | 2022-08-12 | 2052 | keep | 0 | Aug | 2022 | 0.0013976 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-12 09:28 | 2022-08-12 10:45 | 129 | 1:17 | P | ANIMAL | 1 X 40 Y 1 X 30 EN CORTES DE LINEA CRUCE POR AVE | R22081200008 | New_Event | Animals | Include | Include | Wildlife | 77 | 2022-08-12 | 9933 | keep | 0 | Aug | 2022 | 0.0067653 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
SAN JUAN | 2022-08-12 09:50 | 2022-08-12 11:42 | 60 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAGA Y REMPLAZO CAJA | S22081200028 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2022-08-12 | 6720 | keep | 0 | Aug | 2022 | 0.004577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-08-12 09:50 | 2022-08-12 11:02 | 154 | 1:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22081200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-08-12 | 11088 | keep | 0 | Aug | 2022 | 0.007552 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-08-12 09:59 | 2022-08-12 13:16 | 20 | 3:17 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22081200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-08-12 | 3940 | keep | 0 | Aug | 2022 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-08-12 10:00 | 2022-08-12 13:57 | 100 | 3:57 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22081200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-08-12 | 23700 | keep | 0 | Aug | 2022 | 0.016142 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-12 10:02 | 2022-08-12 18:20 | 3 | 8:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TRANSFORMADOR DE 37.5 KVA Y UNO 25 KVA POR LA MISMA CAPACIDAD | A22081200032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 498 | 2022-08-12 | 1494 | keep | 0 | Aug | 2022 | 0.0010176 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-12 10:11 | 2022-08-12 12:50 | 200 | 2:39 | P | DESGANCHE | 1 X 80 C/L DESGANCHE | S22081200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-08-12 | 31800 | keep | 0 | Aug | 2022 | 0.021659 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-08-12 10:21 | 2022-08-12 10:42 | 18 | 0:21 | P | OTRAS CAUSAS | DESCONECTE A PETICION DEL CLIENTE, POR MANTENIMIENTO A FACILIDADES PRIVADAS (WR-6187801) MEDIANTE SF SJ-220812-01 - CALLE LAS VIOLETAS/COND. CITY VIEW TOWER - SAN JUAN. SE REALIZO SIN VIA LIBRE Y SE AFECTARON OTROS CLIENTES | S22081200022 | New_Event | Other Causes | Include | Include | Other | 21 | 2022-08-12 | 378 | keep | 0 | Aug | 2022 | 0.00025745 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2022-08-12 10:24 | 2022-08-12 12:49 | 100 | 2:25 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | C22081200025 | New_Event | Animals | Include | Include | Wildlife | 145 | 2022-08-12 | 14500 | keep | 0 | Aug | 2022 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-12 10:51 | 2022-08-12 11:15 | 3 | 0:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C22081200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-08-12 | 72 | keep | 0 | Aug | 2022 | 4.9039e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-12 10:51 | 2022-08-12 13:45 | 15 | 2:54 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081200085 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 174 | 2022-08-12 | 2610 | keep | 0 | Aug | 2022 | 0.0017777 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-12 10:56 | 2022-08-12 16:45 | 30 | 5:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081200086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2022-08-12 | 10470 | keep | 0 | Aug | 2022 | 0.0071311 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-08-12 10:59 | 2022-08-12 11:51 | 8 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C22081200028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2022-08-12 | 416 | keep | 0 | Aug | 2022 | 0.00028334 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-12 11:02 | 2022-08-12 11:04 | 4132 | 0:02 | T | ERROR HUMANO | DISPARO DE ALIMENTADOR AL ABRIR CAJA PORTAFUSIBLE HACE CONTACTO CON CABLE DE GROUND | P22081200028 | New_Event | Human Error | Include | Include | Other | 2 | 2022-08-12 | 8264 | keep | 0 | Aug | 2022 | 0.0056286 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-08-12 11:02 | 2022-08-12 11:04 | 4279 | 0:02 | T | ERROR HUMANO | DISPARO DE ALIMENTADOR AL ABRIR CAJA PORTAFUSIBLE HACE CONTACTO CON CABLE DE GROUND | P22081200028 | New_Event | Human Error | Include | Include | Other | 2 | 2022-08-12 | 8558 | keep | 0 | Aug | 2022 | 0.0058288 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-08-12 11:02 | 2022-08-12 11:04 | 464 | 0:02 | T | ERROR HUMANO | DISPARO DE ALIMENTADOR AL ABRIR CAJA PORTAFUSIBLE HACE CONTACTO CON CABLE DE GROUND | P22081200028 | New_Event | Human Error | Include | Include | Other | 2 | 2022-08-12 | 928 | keep | 0 | Aug | 2022 | 0.00063206 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2022-08-12 11:04 | 2022-08-12 11:40 | 154 | 0:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22081200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-08-12 | 5544 | keep | 0 | Aug | 2022 | 0.003776 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-08-12 11:08 | 2022-08-12 17:02 | 19 | 5:54 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIR C/L PARA REMPLAZO DE POSTE PRIMARIO (RADIAL) TERMINAR DE LINEA (WR-5930731) | S22081200026 | New_Event | Primary Pole Failure | Include | Include | Equipment | 354 | 2022-08-12 | 6726 | keep | 0 | Aug | 2022 | 0.004581 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
AGUADILLA | 2022-08-12 11:27 | 2022-08-12 13:40 | 1 | 2:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | A22081200046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 133 | 2022-08-12 | 133 | keep | 0 | Aug | 2022 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-12 11:56 | 2022-08-12 13:10 | 3 | 1:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C22081200026 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-08-12 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-08-12 11:59 | 2022-08-12 12:00 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22081200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-12 | 527 | keep | 0 | Aug | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
PONCE | 2022-08-12 12:04 | 2022-08-12 15:05 | 6 | 3:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | P22081200051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 181 | 2022-08-12 | 1086 | keep | 0 | Aug | 2022 | 0.00073967 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-12 12:05 | 2022-08-12 12:59 | 1 | 0:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO CAJA PRIMARIA | C22081200111 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2022-08-12 | 54 | keep | 0 | Aug | 2022 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-12 12:49 | 2022-08-12 13:29 | 12 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE/NEUTRAL SECUNDARIO | S22081200163 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2022-08-12 | 480 | keep | 0 | Aug | 2022 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-12 13:12 | 2022-08-12 13:14 | 1 | 0:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y SE REEMPLAZO TOMA | R22081200149 | New_Event | Secondary Wire Break | Include | Include | Equipment | 2 | 2022-08-12 | 2 | keep | 0 | Aug | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-12 13:30 | 2022-08-12 14:39 | 8 | 1:09 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARARON CONEXIONES EN LINEA SECUNDARIA | P22081200090 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 69 | 2022-08-12 | 552 | keep | 0 | Aug | 2022 | 0.00037596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-12 13:54 | 2022-08-12 20:41 | 30 | 6:47 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR SECTOR REQUIERE DESGANCHE | A22081200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2022-08-12 | 12210 | keep | 0 | Aug | 2022 | 0.0083162 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-12 13:58 | 2022-08-12 18:00 | 40 | 4:02 | P | DESCONECTIVO DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | M22081200141 | New_Event | Switch Failure | Include | Include | Equipment | 242 | 2022-08-12 | 9680 | keep | 0 | Aug | 2022 | 0.006593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-12 13:59 | 2022-08-12 17:55 | 12 | 3:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN PROVISIONAL AEREO | C22081200184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 236 | 2022-08-12 | 2832 | keep | 0 | Aug | 2022 | 0.0019289 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-12 14:01 | 2022-08-12 14:03 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | CERRADO POR SCADA LUEGO DE VERIFICADO PERSONAL FUERA DISPARO 1303-04 QUE LLEVA 1303-01 Y 1346-06. PERO LA CARGA DEL 1303-04 ESTA POR 1303-05 | S22081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-12 | 3362 | keep | 0 | Aug | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-08-12 14:01 | 2022-08-12 14:03 | 1598 | 0:02 | T | NO SE REPORTO CAUSA | CERRADO POR SCADA LUEGO DE VERIFICADO PERSONAL FUERA DISPARO 1303-04 QUE LLEVA 1303-01 Y 1346-06. PERO LA CARGA DEL 1303-04 ESTA POR 1303-05 | S22081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-12 | 3196 | keep | 0 | Aug | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2022-08-12 14:11 | 2022-08-12 15:08 | 10 | 0:57 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L | B22081200135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-08-12 | 570 | keep | 0 | Aug | 2022 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-12 14:17 | 2022-08-12 16:00 | 15 | 1:43 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER @ SOTERRADO | S22081200209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-08-12 | 1545 | keep | 0 | Aug | 2022 | 0.0010523 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-08-12 14:19 | 2022-08-12 18:21 | 300 | 4:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO 3 CAJAS PRIMARIAS | C22081200187 | New_Event | Cutout Failure | Include | Include | Equipment | 242 | 2022-08-12 | 72600 | keep | 0 | Aug | 2022 | 0.049448 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-12 14:45 | 2022-08-12 14:46 | 1944 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE 1336-06 PARCIAL 30% X 1619-02 | S22081200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-12 | 1944 | keep | 0 | Aug | 2022 | 0.001324 | 0.001324 | Momentary | FALSE | FALSE | Not_TMED_Event | 1944
AGUADILLA | 2022-08-12 14:46 | 2022-08-12 17:20 | 50 | 2:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22081200157 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 154 | 2022-08-12 | 7700 | keep | 0 | Aug | 2022 | 0.0052444 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-12 14:47 | 2022-08-12 14:48 | 849 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE 1418-01 QUE LLEVA 1423-03 | S22081200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-12 | 849 | keep | 0 | Aug | 2022 | 0.00057825 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-08-12 14:47 | 2022-08-12 14:48 | 600 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE 1418-01 QUE LLEVA 1423-03 | S22081200000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-12 | 600 | keep | 0 | Aug | 2022 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-08-12 14:48 | 2022-08-12 17:05 | 100 | 2:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S22081200221 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 137 | 2022-08-12 | 13700 | keep | 0 | Aug | 2022 | 0.009331 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-12 14:57 | 2022-08-12 16:39 | 78 | 1:42 | P | PARARRAYOS DEFECTUOSO | 1 X 100 Y 1 X 40 EN C/L PARARRAYO | R22081200190 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 102 | 2022-08-12 | 7956 | keep | 0 | Aug | 2022 | 0.0054188 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
BAYAMON | 2022-08-12 14:58 | 2022-08-13 12:23 | 12 | 21:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-11 GOI BY-220813-01 | S22081200215 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1285 | 2022-08-12 | 15420 | keep | 0 | Aug | 2022 | 0.010502 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-12 15:00 | 2022-08-12 15:01 | 1835 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C22081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-12 | 1835 | keep | 0 | Aug | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
VEGA BAJA | 2022-08-12 15:04 | 2022-08-12 22:27 | 500 | 7:23 | P | DESCONECTIVO DEFECTUOSO | 2 X 140 1 X 100 EN C/L SE REMPLAZO MACHETES | B22081200139 | New_Event | Switch Failure | Include | Include | Equipment | 443 | 2022-08-12 | 221500 | keep | 0 | Aug | 2022 | 0.15086 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2022-08-12 15:05 | 2022-08-12 18:36 | 100 | 3:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22081200091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-08-12 | 21100 | keep | 0 | Aug | 2022 | 0.014371 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-12 15:05 | 2022-08-12 17:00 | 10 | 1:55 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO LINEAS | A22081200097 | New_Event | Animals | Include | Include | Wildlife | 115 | 2022-08-12 | 1150 | keep | 0 | Aug | 2022 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-12 15:15 | 2022-08-12 15:50 | 18 | 0:35 | P | OTRAS CAUSAS | SE RECONECTO CLIENTE MEDIANTE SF SJ-220812-01 | S22081200022 | New_Event | Other Causes | Include | Include | Other | 35 | 2022-08-12 | 630 | keep | 0 | Aug | 2022 | 0.00042909 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-08-12 15:17 | 2022-08-12 19:10 | 20 | 3:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2022-08-12 | 4660 | keep | 0 | Aug | 2022 | 0.0031739 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-12 15:20 | 2022-08-13 04:17 | 113 | 12:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN TRANCLOUSURE | B22081200144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 777 | 2022-08-12 | 87801 | keep | 0 | Aug | 2022 | 0.059801 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
BARRANQUITAS | 2022-08-12 15:22 | 2022-08-12 17:40 | 2 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 10 EN XMR | C22081200195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-08-12 | 276 | keep | 0 | Aug | 2022 | 0.00018798 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-12 15:32 | 2022-08-12 20:41 | 21 | 5:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA PRIMARIA | S22081200230 | New_Event | Cutout Failure | Include | Include | Equipment | 309 | 2022-08-12 | 6489 | keep | 0 | Aug | 2022 | 0.0044196 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2022-08-12 15:43 | 2022-08-13 09:07 | 7 | 17:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X20 EN XMR Y SE REMPLAZO PORTAFUSIBLE | S22081200235 | New_Event | Cutout Failure | Include | Include | Equipment | 1044 | 2022-08-12 | 7308 | keep | 0 | Aug | 2022 | 0.0049774 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-12 15:48 | 2022-08-12 18:17 | 28 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22081200239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-08-12 | 4172 | keep | 0 | Aug | 2022 | 0.0028415 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
GUAYAMA | 2022-08-12 15:58 | 2022-08-12 18:46 | 11 | 2:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO EN TRANSFORMADOR | P22081200114 | New_Event | Primary Wire Break | Include | Include | Equipment | 168 | 2022-08-12 | 1848 | keep | 0 | Aug | 2022 | 0.0012587 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-08-12 16:02 | 2022-08-12 16:03 | 3041 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22081200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-12 | 3041 | keep | 0 | Aug | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-08-12 16:03 | 2022-08-12 22:19 | 80 | 6:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M22081200199 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 376 | 2022-08-12 | 30080 | keep | 0 | Aug | 2022 | 0.020487 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-12 16:16 | 2022-08-12 20:45 | 1 | 4:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22081200175 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 269 | 2022-08-12 | 269 | keep | 0 | Aug | 2022 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-12 16:16 | 2022-08-12 20:36 | 140 | 4:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CONVERTIDOR CAJA PRIMARIA AVERIADA | A22081200100 | New_Event | Cutout Failure | Include | Include | Equipment | 260 | 2022-08-12 | 36400 | keep | 0 | Aug | 2022 | 0.024792 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2022-08-12 16:17 | 2022-08-13 10:50 | 1 | 18:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN BANCO DE XMR SE CERRO PUENTE DE LINEA A CAJA | S22081200246 | New_Event | Primary Wire Break | Include | Include | Equipment | 1113 | 2022-08-12 | 1113 | keep | 0 | Aug | 2022 | 0.00075806 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-12 16:21 | 2022-08-12 19:05 | 10 | 2:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | M22081200176 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 164 | 2022-08-12 | 1640 | keep | 0 | Aug | 2022 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-12 16:30 | 2022-08-13 09:17 | 1 | 16:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA @ CAJA EN XMR (NO FUNDIO) | S22081200249 | New_Event | Primary Wire Break | Include | Include | Equipment | 1007 | 2022-08-12 | 1007 | keep | 0 | Aug | 2022 | 0.00068586 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-12 16:36 | 2022-08-12 20:03 | 8 | 3:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | M22081200180 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 207 | 2022-08-12 | 1656 | keep | 0 | Aug | 2022 | 0.0011279 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-12 16:50 | 2022-08-12 18:25 | 25 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 25 EN PROVISIONAL AEREO | B22081200165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-08-12 | 2375 | keep | 0 | Aug | 2022 | 0.0016176 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-12 16:51 | 2022-08-12 18:23 | 65 | 1:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S22081200252 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2022-08-12 | 5980 | keep | 0 | Aug | 2022 | 0.004073 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-08-12 17:13 | 2022-08-12 18:35 | 50 | 1:22 | P | MAL TIEMPO/RAYOS | 2 X 50 N CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081200185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 82 | 2022-08-12 | 4100 | keep | 0 | Aug | 2022 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-12 17:17 | 2022-08-12 19:45 | 20 | 2:28 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081200114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 148 | 2022-08-12 | 2960 | keep | 0 | Aug | 2022 | 0.002016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-12 17:35 | 2022-08-12 17:50 | 9 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22081200094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2022-08-12 | 135 | keep | 0 | Aug | 2022 | 9.1948e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-08-12 17:48 | 2022-08-12 17:51 | 652 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22081200185 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-12 | 1956 | keep | 0 | Aug | 2022 | 0.0013322 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-12 17:48 | 2022-08-12 17:51 | 2704 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22081200185 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-12 | 8112 | keep | 0 | Aug | 2022 | 0.005525 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
BARRANQUITAS | 2022-08-12 17:58 | 2022-08-12 18:00 | 2826 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22081200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-12 | 5652 | keep | 0 | Aug | 2022 | 0.0038496 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BARRANQUITAS | 2022-08-12 18:00 | 2022-08-13 15:30 | 120 | 21:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO Y REEMPLAZO XMR 25KVA X 37.5KVA | C22081200033 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1290 | 2022-08-12 | 154800 | keep | 0 | Aug | 2022 | 0.10543 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-08-12 19:29 | 2022-08-12 19:30 | 1497 | 0:01 | T | DESGANCHE | RECIERRE INTERRUPTOR | M22081200195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-12 | 1497 | keep | 0 | Aug | 2022 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | Not_TMED_Event | 1497
AGUADILLA | 2022-08-12 19:30 | 2022-08-12 21:30 | 400 | 2:00 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081200198 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-08-12 | 48000 | keep | 0 | Aug | 2022 | 0.032693 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
YAUCO | 2022-08-12 19:40 | 2022-08-13 09:56 | 10 | 14:16 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22081200209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 856 | 2022-08-12 | 8560 | keep | 0 | Aug | 2022 | 0.0058302 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-08-12 20:07 | 2022-08-12 23:40 | 60 | 3:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P22081200137 | New_Event | Cutout Failure | Include | Include | Equipment | 213 | 2022-08-12 | 12780 | keep | 0 | Aug | 2022 | 0.0087044 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-12 20:27 | 2022-08-13 02:29 | 250 | 6:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 75 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | A22081200135 | New_Event | Cutout Failure | Include | Include | Equipment | 362 | 2022-08-12 | 90500 | keep | 0 | Aug | 2022 | 0.061639 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BARRANQUITAS | 2022-08-12 20:29 | 2022-08-13 10:53 | 25 | 14:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22081200261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 864 | 2022-08-12 | 21600 | keep | 0 | Aug | 2022 | 0.014712 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-08-12 20:39 | 2022-08-12 20:40 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22081200142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-12 | 527 | keep | 0 | Aug | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
AGUADILLA | 2022-08-12 21:01 | 2022-08-13 04:49 | 50 | 7:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M22081200244 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 468 | 2022-08-12 | 23400 | keep | 0 | Aug | 2022 | 0.015938 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-12 21:02 | 2022-08-13 08:28 | 65 | 11:26 | P | CONDUCTOR ROTO O ABIERTO | 3 X 50 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | C22081200268 | New_Event | Primary Wire Break | Include | Include | Equipment | 686 | 2022-08-12 | 44590 | keep | 0 | Aug | 2022 | 0.03037 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2022-08-12 21:38 | 2022-08-13 13:47 | 12 | 16:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C22081200276 | New_Event | Secondary Wire Break | Include | Include | Equipment | 969 | 2022-08-12 | 11628 | keep | 0 | Aug | 2022 | 0.0079198 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-08-12 21:42 | 2022-08-13 16:00 | 10 | 18:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22081200148 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1098 | 2022-08-12 | 10980 | keep | 0 | Aug | 2022 | 0.0074784 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-12 21:57 | 2022-08-13 12:55 | 80 | 14:58 | P | ARBOL SOBRE LINEA | 2 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22081200252 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 898 | 2022-08-12 | 71840 | keep | 0 | Aug | 2022 | 0.04893 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-12 21:58 | 2022-08-13 09:12 | 50 | 11:14 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | C22081200284 | New_Event | Animals | Include | Include | Wildlife | 674 | 2022-08-12 | 33700 | keep | 0 | Aug | 2022 | 0.022953 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-12 21:59 | 2022-08-13 08:28 | 20 | 10:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X20 EN RISER SE REMPLAZO CAJA PRIMARIA | B22081200023 | New_Event | Cutout Failure | Include | Include | Equipment | 629 | 2022-08-12 | 12580 | keep | 0 | Aug | 2022 | 0.0085682 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-12 22:04 | 2022-08-13 03:41 | 100 | 5:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081200235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 337 | 2022-08-12 | 33700 | keep | 0 | Aug | 2022 | 0.022953 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-12 22:26 | 2022-08-13 13:09 | 6 | 14:43 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | R22081200329 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 883 | 2022-08-12 | 5298 | keep | 0 | Aug | 2022 | 0.0036084 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-08-12 23:05 | 2022-08-13 13:05 | 80 | 14:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081200152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 840 | 2022-08-12 | 67200 | keep | 0 | Aug | 2022 | 0.04577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-13 00:09 | 2022-08-13 10:00 | 50 | 9:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22081300001 | New_Event | Cutout Failure | Include | Include | Equipment | 591 | 2022-08-13 | 29550 | keep | 0 | Aug | 2022 | 0.020126 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-13 00:37 | 2022-08-13 00:38 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1362 | keep | 0 | Aug | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2022-08-13 01:19 | 2022-08-13 08:08 | 70 | 6:49 | P | DESGANCHE | 1 X 40 EN C/L Y 1 X 30 EN OTRO C/L | B22081300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2022-08-13 | 28630 | keep | 0 | Aug | 2022 | 0.0195 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-08-13 01:19 | 2022-08-13 03:12 | 4 | 1:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | A22081300004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 113 | 2022-08-13 | 452 | keep | 0 | Aug | 2022 | 0.00030786 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-13 01:35 | 2022-08-13 01:36 | 1408 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1714-02 QUE LLEVA 1714-03 | B22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1408 | keep | 0 | Aug | 2022 | 0.00095898 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2022-08-13 01:35 | 2022-08-13 01:36 | 455 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1714-02 QUE LLEVA 1714-03 | B22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 455 | keep | 0 | Aug | 2022 | 0.0003099 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
CAGUAS | 2022-08-13 01:54 | 2022-08-13 11:44 | 12 | 9:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO PORTAFUSIBLE | C22081300009 | New_Event | Cutout Failure | Include | Include | Equipment | 590 | 2022-08-13 | 7080 | keep | 0 | Aug | 2022 | 0.0048222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-13 02:07 | 2022-08-13 12:18 | 6285 | 10:11 | S | PARARRAYOS DEFECTUOSO | DISPARO DE SUBESTACION, SE REALIZO INSPECCION Y SE ENCONTRO PARARRAYO QUEMADO EN LA ALTA DE TRANSFORMADOR. SE REEMPLAZO PARARRAYO Y SE ENERGIZO SUBESTACION. | M22081300002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 611 | 2022-08-13 | 3840135 | keep | 0 | Aug | 2022 | 2.6155 | 0.0042807 | Sustained | FALSE | FALSE | Not_TMED_Event | 6285
AGUADILLA | 2022-08-13 02:07 | 2022-08-13 12:18 | 2225 | 10:11 | S | PARARRAYOS DEFECTUOSO | DISPARO DE SUBESTACION, SE REALIZO INSPECCION Y SE ENCONTRO PARARRAYO QUEMADO EN LA ALTA DE TRANSFORMADOR. SE REEMPLAZO PARARRAYO Y SE ENERGIZO SUBESTACION. | M22081300002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 611 | 2022-08-13 | 1359475 | keep | 0 | Aug | 2022 | 0.92593 | 0.0015154 | Sustained | FALSE | FALSE | Not_TMED_Event | 2225
VEGA BAJA | 2022-08-13 02:16 | 2022-08-13 12:59 | 70 | 10:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A2208130003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 643 | 2022-08-13 | 45010 | keep | 0 | Aug | 2022 | 0.030656 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-08-13 02:33 | 2022-08-13 07:55 | 152 | 5:22 | P | ANIMAL | 1 X 65 EN C/L AVE | R22081300006 | New_Event | Animals | Include | Include | Wildlife | 322 | 2022-08-13 | 48944 | keep | 0 | Aug | 2022 | 0.033336 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
SAN JUAN | 2022-08-13 02:36 | 2022-08-13 02:37 | 602 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1418-04 | S22081400071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 602 | keep | 0 | Aug | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-08-13 02:36 | 2022-08-13 02:37 | 43 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1418-03 | S22081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 43 | keep | 0 | Aug | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2022-08-13 02:40 | 2022-08-13 13:45 | 48 | 11:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22081300013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 665 | 2022-08-13 | 31920 | keep | 0 | Aug | 2022 | 0.021741 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
SAN JUAN | 2022-08-13 03:10 | 2022-08-13 03:11 | 1483 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE 1336-08 QUE LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 CERRADO POR SCADA | S22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1483 | keep | 0 | Aug | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-08-13 03:10 | 2022-08-13 03:11 | 1500 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE 1336-08 QUE LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 CERRADO POR SCADA | S22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-08-13 03:10 | 2022-08-13 03:11 | 5290 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1336-08 QUE LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 CERRADO POR SCADA | S22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 5290 | keep | 0 | Aug | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-08-13 03:24 | 2022-08-13 03:25 | 602 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1418-04 | S22081400071 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 602 | keep | 0 | Aug | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-08-13 03:24 | 2022-08-13 03:25 | 43 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1418-03 | S22081400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 43 | keep | 0 | Aug | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2022-08-13 03:55 | 2022-08-13 10:06 | 100 | 6:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22081300016 | New_Event | Cutout Failure | Include | Include | Equipment | 371 | 2022-08-13 | 37100 | keep | 0 | Aug | 2022 | 0.025269 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-13 04:08 | 2022-08-13 11:25 | 20 | 7:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22081300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 437 | 2022-08-13 | 8740 | keep | 0 | Aug | 2022 | 0.0059528 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-13 04:51 | 2022-08-13 04:52 | 824 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 1119-04 Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05 Y 50% DEL 1119-02 | S22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 824 | keep | 0 | Aug | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
SAN JUAN | 2022-08-13 04:51 | 2022-08-13 04:52 | 422 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 1119-04 Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05 Y 50% DEL 1119-02 | S22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 422 | keep | 0 | Aug | 2022 | 0.00028742 | 0.00028742 | Momentary | FALSE | FALSE | Not_TMED_Event | 422
SAN JUAN | 2022-08-13 04:51 | 2022-08-13 04:52 | 2720 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1119-04 Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05 Y 50% DEL 1119-02 | S22081300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 2720 | keep | 0 | Aug | 2022 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
AGUADILLA | 2022-08-13 06:07 | 2022-08-13 10:56 | 80 | 4:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PORTA FUSIBLE AVERIADA | M22081300022 | New_Event | Cutout Failure | Include | Include | Equipment | 289 | 2022-08-13 | 23120 | keep | 0 | Aug | 2022 | 0.015747 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-13 06:39 | 2022-08-13 09:16 | 50 | 2:37 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | B22081300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-08-13 | 7850 | keep | 0 | Aug | 2022 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-13 06:59 | 2022-08-13 09:27 | 125 | 2:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22081300040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 148 | 2022-08-13 | 18500 | keep | 0 | Aug | 2022 | 0.0126 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
HUMACAO | 2022-08-13 07:06 | 2022-08-13 09:09 | 50 | 2:03 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C22081300038 | New_Event | Animals | Include | Include | Wildlife | 123 | 2022-08-13 | 6150 | keep | 0 | Aug | 2022 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-13 07:06 | 2022-08-13 10:20 | 90 | 3:14 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C22081300037 | New_Event | Animals | Include | Include | Wildlife | 194 | 2022-08-13 | 17460 | keep | 0 | Aug | 2022 | 0.011892 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-08-13 07:21 | 2022-08-13 07:22 | 602 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA LA CARGA DEL 1418-04 | S22081300005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 602 | keep | 0 | Aug | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-08-13 07:21 | 2022-08-13 07:22 | 43 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA TRANSFERIDA AL 1418-03 | S22081300005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 43 | keep | 0 | Aug | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
ARECIBO | 2022-08-13 07:49 | 2022-08-13 10:40 | 1 | 2:51 | P | NO SE REPORTO CAUSA | 1 EN 30 EN RISER NO SE IDENTIFICO CAUSA | A22081300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-08-13 | 171 | keep | 0 | Aug | 2022 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-13 07:54 | 2022-08-13 10:28 | 25 | 2:34 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C22081300056 | New_Event | Animals | Include | Include | Wildlife | 154 | 2022-08-13 | 3850 | keep | 0 | Aug | 2022 | 0.0026222 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-13 08:18 | 2022-08-13 12:07 | 120 | 3:49 | P | ANIMAL | 1 X 200 EN C/L CRUCE POR AVE | C22081300065 | New_Event | Animals | Include | Include | Wildlife | 229 | 2022-08-13 | 27480 | keep | 0 | Aug | 2022 | 0.018717 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-08-13 08:21 | 2022-08-13 12:24 | 10 | 4:03 | P | ARBOL SOBRE LINEA | 2 X 10 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR A CAUSA DE ARBOL QUE CAYO SOBRE LAS LINEAS SE RETIRO ARBOL SOBRE LINEA | M22081300069 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 243 | 2022-08-13 | 2430 | keep | 0 | Aug | 2022 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-13 08:59 | 2022-08-13 10:20 | 74 | 1:21 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22081300033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-08-13 | 5994 | keep | 0 | Aug | 2022 | 0.0040825 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
AGUADILLA | 2022-08-13 09:25 | 2022-08-13 10:04 | 20 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | M22081300094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2022-08-13 | 780 | keep | 0 | Aug | 2022 | 0.00053125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-13 09:30 | 2022-08-13 13:40 | 6 | 4:10 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081300098 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 250 | 2022-08-13 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-08-13 09:36 | 2022-08-13 12:30 | 50 | 2:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22081300015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2022-08-13 | 8700 | keep | 0 | Aug | 2022 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-13 09:37 | 2022-08-13 11:01 | 70 | 1:24 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081300101 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 84 | 2022-08-13 | 5880 | keep | 0 | Aug | 2022 | 0.0040048 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-08-13 09:49 | 2022-08-13 11:32 | 7 | 1:43 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | C22081300097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-08-13 | 721 | keep | 0 | Aug | 2022 | 0.00049107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-13 10:11 | 2022-08-13 12:40 | 1526 | 2:29 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR PRIMARIO GOI BY-220813-02 | B22081300060 | New_Event | Primary Wire Break | Include | Include | Equipment | 149 | 2022-08-13 | 227374 | keep | 0 | Aug | 2022 | 0.15486 | 0.0010394 | Sustained | FALSE | FALSE | Not_TMED_Event | 1526
YAUCO | 2022-08-13 10:14 | 2022-08-13 11:39 | 10 | 1:25 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | P22081300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-13 | 850 | keep | 0 | Aug | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-13 10:15 | 2022-08-13 15:00 | 5 | 4:45 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081300112 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 285 | 2022-08-13 | 1425 | keep | 0 | Aug | 2022 | 0.00097056 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-13 10:51 | 2022-08-13 12:03 | 3 | 1:12 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M22081300119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2022-08-13 | 216 | keep | 0 | Aug | 2022 | 0.00014712 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-08-13 10:53 | 2022-08-13 16:17 | 2 | 5:24 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR ANIMAL | P22081300025 | New_Event | Animals | Include | Include | Wildlife | 324 | 2022-08-13 | 648 | keep | 0 | Aug | 2022 | 0.00044135 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-13 11:03 | 2022-08-13 13:25 | 75 | 2:22 | P | DESGANCHE | 2 X 80 EN C/L SE DESGANCHO | S22081300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-08-13 | 10650 | keep | 0 | Aug | 2022 | 0.0072537 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-08-13 11:22 | 2022-08-13 12:21 | 5 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | S22081300022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2022-08-13 | 295 | keep | 0 | Aug | 2022 | 0.00020092 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-08-13 11:28 | 2022-08-13 12:40 | 3 | 1:12 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081300123 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 72 | 2022-08-13 | 216 | keep | 0 | Aug | 2022 | 0.00014712 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-13 11:39 | 2022-08-13 11:40 | 1483 | 0:01 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL 30% DE SU CARGA TRANSFERIDA AL 1336-08 | S22081300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1483 | keep | 0 | Aug | 2022 | 0.0010101 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-08-13 11:39 | 2022-08-13 11:40 | 1531 | 0:01 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL 15% DE SU CARGA TRANSFERIDA AL 1336-08 | S22081300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1531 | keep | 0 | Aug | 2022 | 0.0010428 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2022-08-13 11:39 | 2022-08-13 11:40 | 5290 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 | S22081300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 5290 | keep | 0 | Aug | 2022 | 0.003603 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2022-08-13 11:40 | 2022-08-13 12:34 | 10 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22081200265 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2022-08-13 | 540 | keep | 0 | Aug | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-13 11:49 | 2022-08-13 17:10 | 100 | 5:21 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN C/L 3 X 65 EN C/L SE LEVANTO PRIMARIA | B22081300068 | New_Event | Primary Wire Break | Include | Include | Equipment | 321 | 2022-08-13 | 32100 | keep | 0 | Aug | 2022 | 0.021863 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-13 11:57 | 2022-08-13 13:05 | 25 | 1:08 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22081300118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-08-13 | 1700 | keep | 0 | Aug | 2022 | 0.0011579 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-13 11:58 | 2022-08-13 16:28 | 36 | 4:30 | P | ANIMAL | 1 X 50 C/L AVE | B22081300026 | New_Event | Animals | Include | Include | Wildlife | 270 | 2022-08-13 | 9720 | keep | 0 | Aug | 2022 | 0.0066202 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-08-13 12:05 | 2022-08-13 17:39 | 9 | 5:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22081300029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 334 | 2022-08-13 | 3006 | keep | 0 | Aug | 2022 | 0.0020474 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-08-13 12:17 | 2022-08-13 14:00 | 138 | 1:43 | P | ANIMAL | 1 X 65 1 X 40 1 X 100 EN C/L AVE | S22081300031 | New_Event | Animals | Include | Include | Wildlife | 103 | 2022-08-13 | 14214 | keep | 0 | Aug | 2022 | 0.0096811 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
CANOVANAS | 2022-08-13 12:28 | 2022-08-13 13:08 | 10 | 0:40 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22081300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-08-13 | 400 | keep | 0 | Aug | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-13 12:31 | 2022-08-13 14:45 | 80 | 2:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-08-13 | 10720 | keep | 0 | Aug | 2022 | 0.0073013 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-13 12:38 | 2022-08-13 17:13 | 9 | 4:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22081300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2022-08-13 | 2475 | keep | 0 | Aug | 2022 | 0.0016857 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-08-13 12:51 | 2022-08-13 12:52 | 1040 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 2% DE SU CARGA TRANSFERIDA AL 1652-02 | S22081300045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 0.00070834 | Momentary | FALSE | FALSE | Not_TMED_Event | 1040
BAYAMON | 2022-08-13 12:54 | 2022-08-13 14:43 | 36 | 1:49 | P | NO SE REPORTO CAUSA | 2 X 100 SMU-20 EN SU-B | B22081300089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-08-13 | 3924 | keep | 0 | Aug | 2022 | 0.0026726 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
MAYAGÃœEZ | 2022-08-13 12:55 | 2022-08-13 13:30 | 3 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22081300127 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-08-13 | 105 | keep | 0 | Aug | 2022 | 7.1515e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-13 12:56 | 2022-08-13 13:00 | 2124 | 0:04 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 8496 | keep | 0 | Aug | 2022 | 0.0057866 | 0.0014466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2124
SAN JUAN | 2022-08-13 12:56 | 2022-08-13 12:57 | 1040 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 2% DE SU CARGA TRANSFERIDA AL 1652-02 | S22081300046 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 0.00070834 | Momentary | FALSE | FALSE | Not_TMED_Event | 1040
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 9 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 36 | keep | 0 | Aug | 2022 | 2.4519e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 6 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 24 | keep | 0 | Aug | 2022 | 1.6346e-05 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 CARGA POR EL 1615-08 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 12 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 LLEVA LA CARGA DEL 1617-04 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 48 | keep | 0 | Aug | 2022 | 3.2693e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 3 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 12 | keep | 0 | Aug | 2022 | 8.1731e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 7 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 28 | keep | 0 | Aug | 2022 | 1.9071e-05 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 4 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 16 | keep | 0 | Aug | 2022 | 1.0898e-05 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 4 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 16 | keep | 0 | Aug | 2022 | 1.0898e-05 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 331 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 1324 | keep | 0 | Aug | 2022 | 0.00090177 | 0.00022544 | Momentary | FALSE | FALSE | Not_TMED_Event | 331
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1132 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4528 | keep | 0 | Aug | 2022 | 0.003084 | 0.000771 | Momentary | FALSE | FALSE | Not_TMED_Event | 1132
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 234 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 936 | keep | 0 | Aug | 2022 | 0.00063751 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 2179 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 8716 | keep | 0 | Aug | 2022 | 0.0059364 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 2005 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 CARGA POR EL 1619-03 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 8020 | keep | 0 | Aug | 2022 | 0.0054624 | 0.0013656 | Momentary | FALSE | FALSE | Not_TMED_Event | 2005
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 5062 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 LLEVA LA CARGA DEL 1619-02 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 20248 | keep | 0 | Aug | 2022 | 0.013791 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 165 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 660 | keep | 0 | Aug | 2022 | 0.00044952 | 0.00011238 | Momentary | FALSE | FALSE | Not_TMED_Event | 165
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 437 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 1748 | keep | 0 | Aug | 2022 | 0.0011906 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 363 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 1452 | keep | 0 | Aug | 2022 | 0.00098895 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 14 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 LLEVA EL 1118-07 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 56 | keep | 0 | Aug | 2022 | 3.8141e-05 | 9.5353e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 2245 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 CARGA POR EL 1658-15 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 8980 | keep | 0 | Aug | 2022 | 0.0061162 | 0.0015291 | Momentary | FALSE | FALSE | Not_TMED_Event | 2245
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 12:56 | 2022-08-13 13:00 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 LLEVA EL 1658-13 | R22081300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-13 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-13 13:01 | 2022-08-13 14:35 | 150 | 1:34 | P | NO SE REPORTO CAUSA | 1 X 200 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22081300140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-08-13 | 14100 | keep | 0 | Aug | 2022 | 0.0096034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-13 13:06 | 2022-08-13 14:00 | 2 | 0:54 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081300143 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 54 | 2022-08-13 | 108 | keep | 0 | Aug | 2022 | 7.3558e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-13 13:25 | 2022-08-13 14:58 | 60 | 1:33 | P | ARBOL SOBRE LINEA | 2 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22081300151 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 93 | 2022-08-13 | 5580 | keep | 0 | Aug | 2022 | 0.0038005 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-13 13:27 | 2022-08-13 15:03 | 35 | 1:36 | P | ANIMAL | 1 X 50 C/L AVE | B22081300091 | New_Event | Animals | Include | Include | Wildlife | 96 | 2022-08-13 | 3360 | keep | 0 | Aug | 2022 | 0.0022885 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-08-13 14:38 | 2022-08-13 19:21 | 150 | 4:43 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L 2 X 65 EN C/L | C22081300134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2022-08-13 | 42450 | keep | 0 | Aug | 2022 | 0.028913 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-08-13 15:10 | 2022-08-13 15:11 | 1153 | 0:01 | T | DESGANCHE | RECIERRE | C22081300143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-13 | 1153 | keep | 0 | Aug | 2022 | 0.0007853 | 0.0007853 | Momentary | FALSE | FALSE | Not_TMED_Event | 1153
CAGUAS | 2022-08-13 15:11 | 2022-08-13 17:17 | 1153 | 2:06 | T | DESGANCHE | SE REALIZO DESGANCHE CON VARETA Y SE CERRO BKR | C22081300158 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-13 | 145278 | keep | 0 | Aug | 2022 | 0.098948 | 0.0007853 | Sustained | FALSE | FALSE | Not_TMED_Event | 1153
MAYAGÃœEZ | 2022-08-13 15:29 | 2022-08-13 17:48 | 40 | 2:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22081300168 | New_Event | Primary Wire Break | Include | Include | Equipment | 139 | 2022-08-13 | 5560 | keep | 0 | Aug | 2022 | 0.0037869 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-13 15:29 | 2022-08-13 17:40 | 1 | 2:11 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR BAJANTE CRUZADO | A22081300044 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 131 | 2022-08-13 | 131 | keep | 0 | Aug | 2022 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-13 15:47 | 2022-08-14 15:05 | 20 | 23:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE ABRIO PUENTE HACIA TRANSFORMADOR VACANTE PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | C22081300164 | New_Event | Primary Wire Break | Include | Include | Equipment | 1398 | 2022-08-13 | 27960 | keep | 0 | Aug | 2022 | 0.019043 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-13 15:48 | 2022-08-13 16:40 | 11 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22081300145 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2022-08-13 | 572 | keep | 0 | Aug | 2022 | 0.00038959 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-08-13 15:50 | 2022-08-13 17:25 | 175 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M22081300183 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2022-08-13 | 16625 | keep | 0 | Aug | 2022 | 0.011323 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
AGUADILLA | 2022-08-13 16:07 | 2022-08-13 16:08 | 1057 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22081300184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 1057 | keep | 0 | Aug | 2022 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
HUMACAO | 2022-08-13 16:10 | 2022-08-13 17:09 | 3 | 0:59 | P | OTRAS CAUSAS | 1 X 40 EN C/L SE ELIMINO PT DE MEDICION | C22081300174 | New_Event | Other Causes | Include | Include | Other | 59 | 2022-08-13 | 177 | keep | 0 | Aug | 2022 | 0.00012055 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-13 16:43 | 2022-08-14 02:28 | 50 | 9:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22081300019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 585 | 2022-08-13 | 29250 | keep | 0 | Aug | 2022 | 0.019922 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-13 16:46 | 2022-08-13 21:22 | 50 | 4:36 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO Y LEVANTO CONDUCTOR | R22081300142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2022-08-13 | 13800 | keep | 0 | Aug | 2022 | 0.0093991 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-13 16:57 | 2022-08-13 18:21 | 25 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 65 C/L | B22081300102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-08-13 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-13 16:57 | 2022-08-13 19:41 | 60 | 2:44 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L Y 1 X 30 RISER | B22081300109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-08-13 | 9840 | keep | 0 | Aug | 2022 | 0.006702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-13 16:59 | 2022-08-13 19:27 | 25 | 2:28 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO | R22081300145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-08-13 | 3700 | keep | 0 | Aug | 2022 | 0.0025201 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-08-13 17:02 | 2022-08-13 18:31 | 30 | 1:29 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO | R22081300146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-08-13 | 2670 | keep | 0 | Aug | 2022 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-08-13 17:04 | 2022-08-13 17:05 | 2064 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22081300197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-13 | 2064 | keep | 0 | Aug | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
VEGA BAJA | 2022-08-13 18:05 | 2022-08-13 19:45 | 50 | 1:40 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA 1 X 30 EN CORTE DE LINEA PERSONAL NO IDENTIFICO CAUSA | A22081300050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-08-13 | 5000 | keep | 0 | Aug | 2022 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-13 18:16 | 2022-08-14 12:07 | 69 | 17:51 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S22081300605 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1071 | 2022-08-13 | 73899 | keep | 0 | Aug | 2022 | 0.050332 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2022-08-13 18:41 | 2022-08-14 09:44 | 10 | 15:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22081300611 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 903 | 2022-08-13 | 9030 | keep | 0 | Aug | 2022 | 0.0061503 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-08-13 18:42 | 2022-08-13 21:34 | 50 | 2:52 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA/ DESGANCHE | P22081300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-08-13 | 8600 | keep | 0 | Aug | 2022 | 0.0058574 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-13 18:48 | 2022-08-13 21:12 | 1 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 10 EN MONTURA | B22081300117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-08-13 | 144 | keep | 0 | Aug | 2022 | 9.8078e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-13 19:24 | 2022-08-13 20:45 | 1 | 1:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22081300154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-08-13 | 81 | keep | 0 | Aug | 2022 | 5.5169e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-13 19:24 | 2022-08-14 09:57 | 45 | 14:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22081300202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 873 | 2022-08-13 | 39285 | keep | 0 | Aug | 2022 | 0.026757 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-08-13 19:48 | 2022-08-13 21:10 | 50 | 1:22 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081300192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-08-13 | 4100 | keep | 0 | Aug | 2022 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-13 19:53 | 2022-08-13 22:00 | 67 | 2:07 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22081300076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-08-13 | 8509 | keep | 0 | Aug | 2022 | 0.0057954 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 00:36 | 1106 | 4:14 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 60% DE SU CARGA ESTA POR EL 1529-15 | S22081300657 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 254 | 2022-08-13 | 280924 | keep | 0 | Aug | 2022 | 0.19134 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 00:36 | 74 | 4:14 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 CARGA POR EL 1529-11 | S22081300657 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 254 | 2022-08-13 | 18796 | keep | 0 | Aug | 2022 | 0.012802 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 08:45 | 946 | 12:23 | T | LINEA DE TRANSMISION 115KV | LINEA 38300 CRUZO 4KV 1525-05 QUE LLEVA 1525-02 SE RETIRO PARARRAYOS AVERIADOS Y SE CERRO POR SCADA | S22081300641 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 743 | 2022-08-13 | 702878 | keep | 0 | Aug | 2022 | 0.47873 | 0.00064432 | Sustained | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 08:45 | 937 | 12:23 | T | LINEA DE TRANSMISION 115KV | LINEA 38300 CRUZO 4KV 1525-05 QUE LLEVA 1525-02 SE RETIRO PARARRAYOS AVERIADOS Y SE CERRO POR SCADA | S22081300641 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 743 | 2022-08-13 | 696191 | keep | 0 | Aug | 2022 | 0.47417 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 00:36 | 1370 | 4:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 LLEVA LA CARGA DEL 1521-02 | S22081300657 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 254 | 2022-08-13 | 347980 | keep | 0 | Aug | 2022 | 0.23701 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 00:36 | 1984 | 4:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 LLEVA 75% DEL 1911-07 | S22081300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 254 | 2022-08-13 | 503936 | keep | 0 | Aug | 2022 | 0.34323 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 00:36 | 199 | 4:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 LLEVA 25% DEL 1911-07 | S22081300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 254 | 2022-08-13 | 50546 | keep | 0 | Aug | 2022 | 0.034427 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2022-08-13 20:22 | 2022-08-14 00:36 | 1802 | 4:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 LLEVA 60% DEL 1346-02 | S22081300657 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 254 | 2022-08-13 | 457708 | keep | 0 | Aug | 2022 | 0.31174 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-08-13 20:22 | 2022-08-14 00:36 | 577 | 4:14 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 75% DE SU CARGA POR EL 1529-12 Y 25% POR EL 1529-13 | S22081300657 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 254 | 2022-08-13 | 146558 | keep | 0 | Aug | 2022 | 0.09982 | 0.00039299 | Sustained | FALSE | FALSE | Not_TMED_Event | 577
ARECIBO | 2022-08-13 20:45 | 2022-08-14 09:53 | 6 | 13:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22081300057 | New_Event | Cutout Failure | Include | Include | Equipment | 788 | 2022-08-13 | 4728 | keep | 0 | Aug | 2022 | 0.0032202 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-08-13 20:58 | 2022-08-14 08:48 | 60 | 11:50 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-1 NO CAUSA | P22081300083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 710 | 2022-08-13 | 42600 | keep | 0 | Aug | 2022 | 0.029015 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-13 21:55 | 2022-08-14 09:50 | 80 | 11:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081300056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2022-08-13 | 57200 | keep | 0 | Aug | 2022 | 0.038959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-13 22:40 | 2022-08-14 08:39 | 14 | 9:59 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R22081300162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 599 | 2022-08-13 | 8386 | keep | 0 | Aug | 2022 | 0.0057117 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-08-14 01:46 | 2022-08-14 01:47 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 4188 | keep | 0 | Aug | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
AGUADILLA | 2022-08-14 02:10 | 2022-08-14 02:20 | 140 | 0:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22081400177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-08-14 | 1400 | keep | 0 | Aug | 2022 | 0.00095353 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2022-08-14 02:58 | 2022-08-14 05:27 | 222 | 2:29 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 100% 1907-03 Y 10% DEL 1909-09 | S22081400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-08-14 | 33078 | keep | 0 | Aug | 2022 | 0.022529 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-14 02:58 | 2022-08-14 05:27 | 4456 | 2:29 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 100% 1907-03 Y 10% DEL 1909-09 | S22081400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-08-14 | 663944 | keep | 0 | Aug | 2022 | 0.45221 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
SAN JUAN | 2022-08-14 04:00 | 2022-08-14 10:26 | 602 | 6:26 | T | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES ABIERTOS, SE REMPLAZO PARARRAYOS AVERIADOS EN CALLE GUAYAMA FRENTE A DEPT. DEL TRABAJO Y SE CERRO BREAKER POR CONTROL. SJ-220814-01, 1418-03 LLEVA 1418-04 | S22081400071 | New_Event | Primary Wire Break | Include | Include | Equipment | 386 | 2022-08-14 | 232372 | keep | 0 | Aug | 2022 | 0.15827 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-08-14 04:00 | 2022-08-14 10:26 | 43 | 6:26 | T | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES ABIERTOS, SE REMPLAZO PARARRAYOS AVERIADOS EN CALLE GUAYAMA FRENTE A DEPT. DEL TRABAJO Y SE CERRO BREAKER POR CONTROL. SJ-220814-01, 1418-03 LLEVA 1418-04 | S22081400071 | New_Event | Primary Wire Break | Include | Include | Equipment | 386 | 2022-08-14 | 16598 | keep | 0 | Aug | 2022 | 0.011305 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2022-08-14 04:18 | 2022-08-14 10:20 | 80 | 6:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA Y SE CERRO PUENTE TRASPATIO | C22081400005 | New_Event | Cutout Failure | Include | Include | Equipment | 362 | 2022-08-14 | 28960 | keep | 0 | Aug | 2022 | 0.019725 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-08-14 05:09 | 2022-08-14 10:15 | 80 | 5:06 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22081400012 | New_Event | Animals | Include | Include | Wildlife | 306 | 2022-08-14 | 24480 | keep | 0 | Aug | 2022 | 0.016673 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-14 05:13 | 2022-08-14 08:35 | 25 | 3:22 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN C/L SE ELIMINO PARARAYO | B22081400007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 202 | 2022-08-14 | 5050 | keep | 0 | Aug | 2022 | 0.0034395 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-14 05:27 | 2022-08-14 06:45 | 1782 | 1:18 | P | DESGANCHE | SE REALIZARON OPERACIONES Y ENTRO 40% ADICIONAL DEL ALIMENTADOR (50% EN SERVICIO) | S22081400037 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-08-14 | 138996 | keep | 0 | Aug | 2022 | 0.09467 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-14 05:55 | 2022-08-14 10:40 | 50 | 4:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22081400015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-08-14 | 14250 | keep | 0 | Aug | 2022 | 0.0097056 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-14 06:00 | 2022-08-14 18:10 | 1 | 12:10 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO SE REPORTO CAUSA | M22081400131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 730 | 2022-08-14 | 730 | keep | 0 | Aug | 2022 | 0.0004972 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-14 06:09 | 2022-08-14 06:10 | 2147 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 2147 | keep | 0 | Aug | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
CANOVANAS | 2022-08-14 06:27 | 2022-08-14 06:28 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGAS X 2402-04 | R22081400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 3699 | keep | 0 | Aug | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
BAYAMON | 2022-08-14 06:36 | 2022-08-14 08:55 | 60 | 2:19 | P | ANIMAL | 2 X 65 Y 1 X 80 EN C/L SE RETIRO AVE | B22081400011 | New_Event | Animals | Include | Include | Wildlife | 139 | 2022-08-14 | 8340 | keep | 0 | Aug | 2022 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-14 06:42 | 2022-08-14 09:00 | 642 | 2:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO RISER @ PM (SE ENCONTRO CAJA ABIERTA) | B22081400012 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2022-08-14 | 88596 | keep | 0 | Aug | 2022 | 0.060342 | 0.00043726 | Sustained | FALSE | FALSE | Not_TMED_Event | 642
BAYAMON | 2022-08-14 06:45 | 2022-08-14 07:26 | 2228 | 0:41 | P | DESGANCHE | SE REALIZO DESGANCHE DESDE EL SUELO A VARETA Y SE CERRO MACHETES 100% EN SERVICIO | S22081400037 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 41 | 2022-08-14 | 91348 | keep | 0 | Aug | 2022 | 0.062217 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-14 06:45 | 2022-08-14 06:46 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22081400017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 4304 | keep | 0 | Aug | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
FAJARDO | 2022-08-14 06:54 | 2022-08-14 06:55 | 1394 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R22081400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 1394 | keep | 0 | Aug | 2022 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2022-08-14 06:55 | 2022-08-14 12:39 | 120 | 5:44 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | R22081400005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 344 | 2022-08-14 | 41280 | keep | 0 | Aug | 2022 | 0.028116 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-08-14 07:12 | 2022-08-14 10:45 | 12 | 3:33 | P | ANIMAL | 1 X 15 EN XMR SE RETIRO AVE | B22081400014 | New_Event | Animals | Include | Include | Wildlife | 213 | 2022-08-14 | 2556 | keep | 0 | Aug | 2022 | 0.0017409 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-08-14 07:53 | 2022-08-14 12:01 | 10 | 4:08 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22081400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2022-08-14 | 2480 | keep | 0 | Aug | 2022 | 0.0016891 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-14 07:56 | 2022-08-14 10:50 | 60 | 2:54 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22081400009 | New_Event | Animals | Include | Include | Wildlife | 174 | 2022-08-14 | 10440 | keep | 0 | Aug | 2022 | 0.0071106 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-14 08:00 | 2022-08-14 22:30 | 1 | 14:30 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | M22081400166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 870 | 2022-08-14 | 870 | keep | 0 | Aug | 2022 | 0.00059255 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-14 08:11 | 2022-08-14 12:50 | 1 | 4:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22081400027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2022-08-14 | 279 | keep | 0 | Aug | 2022 | 0.00019003 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-14 08:38 | 2022-08-14 09:05 | 25 | 0:27 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO LA TIERRA DEL TRANSFORMADOR Y SE CERRO CAJA PRIMARIA | C22081400011 | New_Event | Primary Wire Break | Include | Include | Equipment | 27 | 2022-08-14 | 675 | keep | 0 | Aug | 2022 | 0.00045974 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-14 08:45 | 2022-08-14 09:50 | 15 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A22081400012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-08-14 | 975 | keep | 0 | Aug | 2022 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-14 08:50 | 2022-08-14 12:27 | 1 | 3:37 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22081400046 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 217 | 2022-08-14 | 217 | keep | 0 | Aug | 2022 | 0.0001478 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-14 08:53 | 2022-08-14 13:22 | 120 | 4:29 | P | DESGANCHE | 2 X 80 Y 1 X 100 EN C/L DESGANCHE | S22081400160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2022-08-14 | 32280 | keep | 0 | Aug | 2022 | 0.021986 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-08-14 08:59 | 2022-08-14 12:14 | 30 | 3:15 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22081400049 | New_Event | Animals | Include | Include | Wildlife | 195 | 2022-08-14 | 5850 | keep | 0 | Aug | 2022 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-14 09:15 | 2022-08-14 12:00 | 27 | 2:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22081400164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-08-14 | 4455 | keep | 0 | Aug | 2022 | 0.0030343 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2022-08-14 09:21 | 2022-08-14 09:22 | 827 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE 1620-05 QUE LLEVA 20% DEL 1206-03 SE CERRO POR SCADA | S22081400135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 827 | keep | 0 | Aug | 2022 | 0.00056327 | 0.00056327 | Momentary | FALSE | FALSE | Not_TMED_Event | 827
SAN JUAN | 2022-08-14 09:21 | 2022-08-14 09:22 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-05 QUE LLEVA 20% DEL 1206-03 SE CERRO POR SCADA | S22081400135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 1615 | keep | 0 | Aug | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
HUMACAO | 2022-08-14 09:29 | 2022-08-14 14:50 | 184 | 5:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO PIN | C22081400050 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 321 | 2022-08-14 | 59064 | keep | 0 | Aug | 2022 | 0.040228 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
VEGA BAJA | 2022-08-14 09:30 | 2022-08-14 13:30 | 15 | 4:00 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22081400021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 240 | 2022-08-14 | 3600 | keep | 0 | Aug | 2022 | 0.0024519 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-08-14 09:36 | 2022-08-14 09:37 | 3902 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO INTERRUPTOR EN SERVICIO | C22081400054 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-14 | 3902 | keep | 0 | Aug | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2022-08-14 09:42 | 2022-08-14 09:43 | 3902 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO INTERRUPTOR EN SERVICIO | C22081400057 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-14 | 3902 | keep | 0 | Aug | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2022-08-14 09:43 | 2022-08-14 11:49 | 20 | 2:06 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA DE TRANSFORMADOR | C22081400080 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 126 | 2022-08-14 | 2520 | keep | 0 | Aug | 2022 | 0.0017164 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-08-14 10:39 | 2022-08-14 13:53 | 20 | 3:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA AVERIADA | P22081400028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 194 | 2022-08-14 | 3880 | keep | 0 | Aug | 2022 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-14 11:18 | 2022-08-14 14:58 | 3147 | 3:40 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETES QUEMADOS DE BARRA Y EN TRONCAL DE ALIMENTADOR | M22081400085 | New_Event | Switch Failure | Include | Include | Equipment | 220 | 2022-08-14 | 692340 | keep | 0 | Aug | 2022 | 0.47155 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-08-14 11:19 | 2022-08-14 15:50 | 25 | 4:31 | P | CONDUCTOR ROTO O ABIERTO | 2 X 30 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR ALAMBRE PARTIDO | M22081400082 | New_Event | Primary Wire Break | Include | Include | Equipment | 271 | 2022-08-14 | 6775 | keep | 0 | Aug | 2022 | 0.0046144 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-14 11:28 | 2022-08-14 11:29 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1720-08 | S22081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 2402 | keep | 0 | Aug | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-08-14 11:28 | 2022-08-14 11:29 | 1 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1709-02 | S22081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 1 | keep | 0 | Aug | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-14 11:45 | 2022-08-14 13:59 | 15 | 2:14 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22081400084 | New_Event | Animals | Include | Include | Wildlife | 134 | 2022-08-14 | 2010 | keep | 0 | Aug | 2022 | 0.001369 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-14 11:58 | 2022-08-15 13:30 | 35 | 25:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22081400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1532 | 2022-08-14 | 53620 | keep | 0 | Aug | 2022 | 0.03652 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-08-14 12:00 | 2022-08-14 12:25 | 15 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22081400021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-08-14 | 375 | keep | 0 | Aug | 2022 | 0.00025541 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-14 12:15 | 2022-08-14 13:25 | 15 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22081400188 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-08-14 | 1050 | keep | 0 | Aug | 2022 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-14 12:17 | 2022-08-14 13:26 | 1 | 1:09 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081400097 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 69 | 2022-08-14 | 69 | keep | 0 | Aug | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-14 12:22 | 2022-08-14 12:23 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22081400093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 3458 | keep | 0 | Aug | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-08-14 12:46 | 2022-08-14 12:47 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22081400095 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 3458 | keep | 0 | Aug | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-08-14 13:00 | 2022-08-14 15:10 | 1 | 2:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REPARO AISLADOR ZAFADO DE CRUCETA VERIFCADA CON BITACORA | M22081400098 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 130 | 2022-08-14 | 130 | keep | 0 | Aug | 2022 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-08-14 13:36 | 2022-08-14 15:37 | 150 | 2:01 | P | CAUSAS EXTERNAS | 2 X 40 Y 2 X 50 EN C/LS PERSONA DESGANCHANDO | R22081400028 | New_Event | Damage From Public | Include | Include | Public | 121 | 2022-08-14 | 18150 | keep | 0 | Aug | 2022 | 0.012362 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-08-14 13:37 | 2022-08-14 14:43 | 60 | 1:06 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 140 EN RISER AVERIA DEL SU - 7A @ SU - 7B CERRO N/O EN SU - C @ SU - 7B BASE DE SMU AVERIADA EN EL SU - A | R22081400029 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 66 | 2022-08-14 | 3960 | keep | 0 | Aug | 2022 | 0.0026971 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-14 13:57 | 2022-08-14 13:58 | 2234 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B22081400033 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-14 | 2234 | keep | 0 | Aug | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-08-14 13:58 | 2022-08-14 19:31 | 125 | 5:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B22081400034 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 333 | 2022-08-14 | 41625 | keep | 0 | Aug | 2022 | 0.028351 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-08-14 14:34 | 2022-08-14 16:01 | 8 | 1:27 | P | TRANSFORMADOR AVERIADO | 1X25 EN RISER Y SE REMPLAZO BUSHING PRIMARIO | S22081400172 | New_Event | Service Transformer Failure | Include | Include | Equipment | 87 | 2022-08-14 | 696 | keep | 0 | Aug | 2022 | 0.00047404 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-08-14 14:39 | 2022-08-14 16:25 | 180 | 1:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M22081400104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 106 | 2022-08-14 | 19080 | keep | 0 | Aug | 2022 | 0.012995 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
AGUADILLA | 2022-08-14 15:33 | 2022-08-14 19:20 | 50 | 3:47 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081400116 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 227 | 2022-08-14 | 11350 | keep | 0 | Aug | 2022 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-14 15:44 | 2022-08-14 15:45 | 1444 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M22081400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 1444 | keep | 0 | Aug | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-08-14 15:44 | 2022-08-14 15:45 | 3630 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M22081400121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 3630 | keep | 0 | Aug | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
UTUADO | 2022-08-14 15:46 | 2022-08-14 15:53 | 1527 | 0:07 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR POR SCADA A PETICION DE JOSE VELEZ PARA RETIRAR LINEA PRIMARIA VIA EN EL SUELO. SE SECCIONALIZO PARA PODER TRABAJAR Y SE CERRO POR SCADA. | A22081400029 | New_Event | Primary Wire Break | Include | Include | Equipment | 7 | 2022-08-14 | 10689 | keep | 0 | Aug | 2022 | 0.0072802 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
MAYAGÃœEZ | 2022-08-14 15:50 | 2022-08-15 12:43 | 10 | 20:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22081400082 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1253 | 2022-08-14 | 12530 | keep | 0 | Aug | 2022 | 0.0085341 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-14 15:53 | 2022-08-14 18:35 | 500 | 2:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A22081400029 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 162 | 2022-08-14 | 81000 | keep | 0 | Aug | 2022 | 0.055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-14 15:53 | 2022-08-14 20:25 | 70 | 4:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CONVERTIDOR Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22081400032 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 272 | 2022-08-14 | 19040 | keep | 0 | Aug | 2022 | 0.012968 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-08-14 15:54 | 2022-08-14 16:35 | 6 | 0:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR FUSIBLE PODRIDO | R22081400049 | New_Event | Cutout Failure | Include | Include | Equipment | 41 | 2022-08-14 | 246 | keep | 0 | Aug | 2022 | 0.00016755 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-08-14 15:56 | 2022-08-14 15:57 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22081400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 4634 | keep | 0 | Aug | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
AGUADILLA | 2022-08-14 16:01 | 2022-08-14 17:43 | 15 | 1:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22081400035 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-08-14 | 1530 | keep | 0 | Aug | 2022 | 0.0010421 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-14 16:03 | 2022-08-14 16:04 | 1444 | 0:01 | T | ANIMAL | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON, CERRADO POR SCADA | M22081400123 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-14 | 1444 | keep | 0 | Aug | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-08-14 16:03 | 2022-08-14 16:04 | 3630 | 0:01 | T | ANIMAL | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON, CERRADO POR SCADA | M22081400123 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-14 | 3630 | keep | 0 | Aug | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-08-14 16:04 | 2022-08-14 20:50 | 40 | 4:46 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASES | M22081400132 | 1st_after_momentary | Animals | Include | Include | Wildlife | 286 | 2022-08-14 | 11440 | keep | 0 | Aug | 2022 | 0.0077917 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-08-14 16:32 | 2022-08-14 17:03 | 8 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXIONES SECUNDARIAS DEL TRANSFORMADOR | A22081400042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2022-08-14 | 248 | keep | 0 | Aug | 2022 | 0.00016891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-14 17:10 | 2022-08-14 17:50 | 9 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES SECUNDARIAS DEL TRANSFORMADOR | A22081400051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2022-08-14 | 360 | keep | 0 | Aug | 2022 | 0.00024519 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-08-14 17:12 | 2022-08-14 18:09 | 6 | 0:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR AJUSTO CAJA SUELTA | R22081400054 | New_Event | Cutout Failure | Include | Include | Equipment | 57 | 2022-08-14 | 342 | keep | 0 | Aug | 2022 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-08-14 17:28 | 2022-08-14 21:26 | 50 | 3:58 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA Y 1 X 40 EN RISER SE REEMPLAZO PARARRAYO QUEMADO EN AREA SOTERRADA | A22081400058 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 238 | 2022-08-14 | 11900 | keep | 0 | Aug | 2022 | 0.008105 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-14 17:31 | 2022-08-14 18:18 | 200 | 0:47 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | P22081400045 | New_Event | Animals | Include | Include | Wildlife | 47 | 2022-08-14 | 9400 | keep | 0 | Aug | 2022 | 0.0064023 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-14 17:35 | 2022-08-14 19:24 | 60 | 1:49 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASES | M22081400135 | New_Event | Animals | Include | Include | Wildlife | 109 | 2022-08-14 | 6540 | keep | 0 | Aug | 2022 | 0.0044544 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-14 17:36 | 2022-08-14 17:37 | 1570 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081400038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 1570 | keep | 0 | Aug | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
HUMACAO | 2022-08-14 17:41 | 2022-08-14 17:42 | 2450 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22081400114 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-14 | 2450 | keep | 0 | Aug | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-08-14 17:42 | 2022-08-15 06:44 | 69 | 13:02 | P | ANIMAL | 1 X 40 Y 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | C22081400116 | 1st_after_momentary | Animals | Include | Include | Wildlife | 782 | 2022-08-14 | 53958 | keep | 0 | Aug | 2022 | 0.036751 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
YAUCO | 2022-08-14 18:18 | 2022-08-14 18:19 | 3973 | 0:01 | T | ANIMAL | RECIERRE | P22081400055 | Additional_clients | Animals | Include | Include | Wildlife | 1 | 2022-08-14 | 3973 | keep | 0 | Aug | 2022 | 0.002706 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-14 18:19 | 2022-08-14 18:52 | 200 | 0:33 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | P22081400045 | 1st_after_momentary | Animals | Include | Include | Wildlife | 33 | 2022-08-14 | 6600 | keep | 0 | Aug | 2022 | 0.0044952 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-08-14 18:19 | 2022-08-15 07:49 | 15 | 13:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081400139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 810 | 2022-08-14 | 12150 | keep | 0 | Aug | 2022 | 0.0082753 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-08-14 18:35 | 2022-08-15 09:37 | 33 | 15:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA | C22081400125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 902 | 2022-08-14 | 29766 | keep | 0 | Aug | 2022 | 0.020273 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BARRANQUITAS | 2022-08-14 19:18 | 2022-08-14 19:19 | 1604 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO INTERRUPTOR EN SERVICIO | C22081400127 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-14 | 1604 | keep | 0 | Aug | 2022 | 0.0010925 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
BARRANQUITAS | 2022-08-14 19:19 | 2022-08-15 08:03 | 219 | 12:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE CORTO PEDAZO DE ALAMBRE QUE SE SALIA DE LA GRAPA | C22081400130 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 764 | 2022-08-14 | 167316 | keep | 0 | Aug | 2022 | 0.11396 | 0.00014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 219
ARECIBO | 2022-08-14 19:21 | 2022-08-14 22:00 | 50 | 2:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22081400074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2022-08-14 | 7950 | keep | 0 | Aug | 2022 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-14 19:25 | 2022-08-14 21:29 | 150 | 2:04 | P | DESGANCHE | 1 X 80 Y 1 X 50 EN DIFERENTES CORTES DE LINEA REQUIERE DESGANCHE | M22081400141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-08-14 | 18600 | keep | 0 | Aug | 2022 | 0.012668 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-08-14 19:37 | 2022-08-14 20:34 | 3046 | 0:57 | T | NO SE REPORTO CAUSA | DISPARO SE SECCIONALIZO EL BKR | R22081400196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-08-14 | 173622 | keep | 0 | Aug | 2022 | 0.11825 | 0.0020746 | Sustained | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2022-08-14 19:37 | 2022-08-15 00:04 | 308 | 4:27 | P | NO SE REPORTO CAUSA | NO ENCONTRO CAUSA 15% DE LA CARGA X 1646-03 | R22081400196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 267 | 2022-08-14 | 82236 | keep | 0 | Aug | 2022 | 0.056011 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
YAUCO | 2022-08-14 19:37 | 2022-08-15 12:46 | 7 | 17:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE CAMBIARON 3 CAJAS PRIMARIAS | P22081400060 | New_Event | Cutout Failure | Include | Include | Equipment | 1029 | 2022-08-14 | 7203 | keep | 0 | Aug | 2022 | 0.0049059 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-14 19:48 | 2022-08-14 19:49 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22081400154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 2999 | keep | 0 | Aug | 2022 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
VEGA BAJA | 2022-08-14 20:07 | 2022-08-15 00:08 | 617 | 4:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B22081400054 | New_Event | Primary Wire Break | Include | Include | Equipment | 241 | 2022-08-14 | 148697 | keep | 0 | Aug | 2022 | 0.10128 | 0.00042024 | Sustained | FALSE | FALSE | Not_TMED_Event | 617
BAYAMON | 2022-08-14 20:32 | 2022-08-15 15:51 | 7 | 19:19 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE CERRO C/L | B22081400122 | New_Event | Primary Wire Break | Include | Include | Equipment | 1159 | 2022-08-14 | 8113 | keep | 0 | Aug | 2022 | 0.0055257 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-08-14 20:34 | 2022-08-14 21:29 | 1218 | 0:55 | P | NO SE REPORTO CAUSA | NO ENCONTRO CAUSA | R22081400196 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 55 | 2022-08-14 | 66990 | keep | 0 | Aug | 2022 | 0.045627 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-14 20:41 | 2022-08-14 21:21 | 40 | 0:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22081400085 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 40 | 2022-08-14 | 1600 | keep | 0 | Aug | 2022 | 0.0010898 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-14 21:28 | 2022-08-15 00:08 | 40 | 2:40 | P | NO SE REPORTO CAUSA | SE REALIZO DESGANCHE Y DISCO QUEMADO Y 1 X 65 EN C/L | S22081400254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2022-08-14 | 6400 | keep | 0 | Aug | 2022 | 0.004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-14 21:33 | 2022-08-14 23:14 | 30 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22081400170 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2022-08-14 | 3030 | keep | 0 | Aug | 2022 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-08-14 22:17 | 2022-08-14 22:18 | 485 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22081400070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 485 | keep | 0 | Aug | 2022 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
VEGA BAJA | 2022-08-14 22:23 | 2022-08-14 22:24 | 652 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 25% DE LA CARGA POR EL 9003-06 | B22081400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-14 | 652 | keep | 0 | Aug | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-14 22:23 | 2022-08-14 22:24 | 3076 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR LLEVA 25% DE LA CARGA DEL 9003-05 | B22081400000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-14 | 3076 | keep | 0 | Aug | 2022 | 0.002095 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
YAUCO | 2022-08-14 22:24 | 2022-08-14 22:25 | 2484 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERREPTOR 5602-02 CON CARGA 5602-03 | P22081400055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 2484 | keep | 0 | Aug | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
VEGA BAJA | 2022-08-14 22:24 | 2022-08-15 00:54 | 15 | 2:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 140 EN C/L | B22081400068 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 150 | 2022-08-14 | 2250 | keep | 0 | Aug | 2022 | 0.0015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-14 22:59 | 2022-08-14 23:00 | 3565 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081400156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 3565 | keep | 0 | Aug | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
HUMACAO | 2022-08-14 23:59 | 2022-08-15 | 1117 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-14 | 1117 | keep | 0 | Aug | 2022 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
VEGA BAJA | 2022-08-15 00:14 | 2022-08-15 08:16 | 40 | 8:02 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22081500001 | New_Event | Animals | Include | Include | Wildlife | 482 | 2022-08-15 | 19280 | keep | 0 | Aug | 2022 | 0.013132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-15 02:44 | 2022-08-15 02:45 | 343 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 20% DEL DE SU CARGA POR EL 1708-03 | B22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 343 | keep | 0 | Aug | 2022 | 0.00023362 | 0.00023362 | Momentary | FALSE | FALSE | Not_TMED_Event | 343
BAYAMON | 2022-08-15 02:44 | 2022-08-15 02:45 | 1498 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA PARTE DEL 1708-02 | S22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
CAGUAS | 2022-08-15 03:46 | 2022-08-15 10:32 | 107 | 6:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA DE RISER | C22081500003 | New_Event | Primary Wire Break | Include | Include | Equipment | 406 | 2022-08-15 | 43442 | keep | 0 | Aug | 2022 | 0.029588 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
BARRANQUITAS | 2022-08-15 03:46 | 2022-08-15 10:43 | 50 | 6:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C22081500042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2022-08-15 | 20850 | keep | 0 | Aug | 2022 | 0.014201 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-15 04:20 | 2022-08-15 13:50 | 30 | 9:30 | P | SOBRECARGA | 1 X 40 EN TRANSFORMADOR Y 1 X 50 EN CORTE DE LINEA | M22081500003 | New_Event | Trip Due To Overload | Include | Include | Other | 570 | 2022-08-15 | 17100 | keep | 0 | Aug | 2022 | 0.011647 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-15 05:32 | 2022-08-15 09:00 | 50 | 3:28 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R22081500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-08-15 | 10400 | keep | 0 | Aug | 2022 | 0.0070834 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-15 05:59 | 2022-08-16 12:03 | 6 | 30:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO | A22081500004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1804 | 2022-08-15 | 10824 | keep | 0 | Aug | 2022 | 0.0073722 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-08-15 06:21 | 2022-08-15 06:22 | 1307 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22081500007 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-15 | 1307 | keep | 0 | Aug | 2022 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2022-08-15 06:22 | 2022-08-15 11:44 | 112 | 5:22 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22081500009 | 1st_after_momentary | Animals | Include | Include | Wildlife | 322 | 2022-08-15 | 36064 | keep | 0 | Aug | 2022 | 0.024563 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BARRANQUITAS | 2022-08-15 06:32 | 2022-08-15 09:40 | 4 | 3:08 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PARARRAYO | C22081500012 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 188 | 2022-08-15 | 752 | keep | 0 | Aug | 2022 | 0.00051218 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-15 06:43 | 2022-08-15 08:30 | 1 | 1:47 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 80 SMU-20 EN SU- 22A @ SU-2B (CONTAMINADO) | R22081500013 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 107 | 2022-08-15 | 107 | keep | 0 | Aug | 2022 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-15 06:43 | 2022-08-15 10:22 | 80 | 3:39 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2022-08-15 | 17520 | keep | 0 | Aug | 2022 | 0.011933 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-15 06:45 | 2022-08-15 08:59 | 3 | 2:14 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22081500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-08-15 | 402 | keep | 0 | Aug | 2022 | 0.0002738 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-15 06:46 | 2022-08-15 09:50 | 30 | 3:04 | P | ANIMAL | 1 X 15 EN XMR Y 1 X 30 C/L UN AVE CRUZO LINEA | B22081500004 | New_Event | Animals | Include | Include | Wildlife | 184 | 2022-08-15 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-08-15 06:50 | 2022-08-15 06:51 | 2286 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 3100 DE FAJARDO TC A DAGUAO | R22081500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 2286 | keep | 0 | Aug | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-08-15 06:50 | 2022-08-15 06:51 | 693 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 3100 DE FAJARDO TC A DAGUAO | R22081500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 693 | keep | 0 | Aug | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
GUAYAMA | 2022-08-15 06:56 | 2022-08-15 06:57 | 4132 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | P22081500007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-08-15 | 4132 | keep | 0 | Aug | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-08-15 06:57 | 2022-08-15 12:04 | 1 | 5:07 | P | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARRAYO 1 X 65 EN CORTE DE LINEA | P22081500009 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 307 | 2022-08-15 | 307 | keep | 0 | Aug | 2022 | 0.0002091 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-15 07:04 | 2022-08-15 07:05 | 603 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 9206-08 LLEVANDO CARGA 9206-09 | B22081500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 603 | keep | 0 | Aug | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2022-08-15 07:04 | 2022-08-15 07:05 | 6 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 9206-08 LLEVANDO CARGA 9206-09 | B22081500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 6 | keep | 0 | Aug | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-15 07:19 | 2022-08-15 07:50 | 87 | 0:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L REMPLAZO AISLADOR | R22081500020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 31 | 2022-08-15 | 2697 | keep | 0 | Aug | 2022 | 0.0018369 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
YAUCO | 2022-08-15 07:38 | 2022-08-15 12:07 | 10 | 4:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS ARRIADAS | P22081500034 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 269 | 2022-08-15 | 2690 | keep | 0 | Aug | 2022 | 0.0018321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-08-15 07:48 | 2022-08-15 12:27 | 2 | 4:39 | P | ANIMAL | 1 X 15 EN MONTURA TRIFASICA POR AVE | P22081500043 | New_Event | Animals | Include | Include | Wildlife | 279 | 2022-08-15 | 558 | keep | 0 | Aug | 2022 | 0.00038005 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-08-15 07:50 | 2022-08-15 09:56 | 2286 | 2:06 | S | NO SE REPORTO CAUSA | SUBESTACION SE FUE A LOCK OUT SE SECCIONALIZO SUBESTACION MEDIANTE SJ-220815-50 Y SE TRANSFIRIO LA CARGA DEL 2006-03 AL 2006-04 Y ESTOS A SU VEZ AL 2005-09 | R22081500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-08-15 | 288036 | keep | 0 | Aug | 2022 | 0.19618 | 0.001557 | Sustained | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-08-15 07:50 | 2022-08-15 09:56 | 693 | 2:06 | S | NO SE REPORTO CAUSA | SUBESTACION SE FUE A LOCK OUT SE SECCIONALIZO SUBESTACION MEDIANTE SJ-220815-50 Y SE TRANSFIRIO LA CARGA DEL 2006-03 AL 2006-04 Y ESTOS A SU VEZ AL 2005-09 | R22081500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-08-15 | 87318 | keep | 0 | Aug | 2022 | 0.059472 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
FAJARDO | 2022-08-15 07:51 | 2022-08-15 07:52 | 1571 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE INTERRUPTOR EN SERVICIO | R22081500000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-15 | 1571 | keep | 0 | Aug | 2022 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
FAJARDO | 2022-08-15 07:52 | 2022-08-15 12:14 | 31 | 4:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA PRIMARIA | R22081500025 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 262 | 2022-08-15 | 8122 | keep | 0 | Aug | 2022 | 0.0055319 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CAGUAS | 2022-08-15 07:53 | 2022-08-15 09:30 | 7 | 1:37 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN BANCO DE TRANSFORMADORES CRUCE POR AVE SE REEMPLAZO PARARRAYO Y SE REPARO BAJANTE PRIMARIO | C22081500020 | New_Event | Animals | Include | Include | Wildlife | 97 | 2022-08-15 | 679 | keep | 0 | Aug | 2022 | 0.00046246 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-15 07:56 | 2022-08-15 09:35 | 12 | 1:39 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-08-15 | 1188 | keep | 0 | Aug | 2022 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-08-15 08:01 | 2022-08-15 10:03 | 5 | 2:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22081500006 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2022-08-15 | 610 | keep | 0 | Aug | 2022 | 0.00041547 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-08-15 08:04 | 2022-08-15 08:20 | 33 | 0:16 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C22081500026 | New_Event | Animals | Include | Include | Wildlife | 16 | 2022-08-15 | 528 | keep | 0 | Aug | 2022 | 0.00035962 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2022-08-15 08:13 | 2022-08-15 12:05 | 1 | 3:52 | P | ANIMAL | 2 X 50 EN RISER IGUANA CRUZO LINEAS | M22081500010 | New_Event | Animals | Include | Include | Wildlife | 232 | 2022-08-15 | 232 | keep | 0 | Aug | 2022 | 0.00015801 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-15 08:19 | 2022-08-15 09:25 | 2 | 1:06 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA POR AVE | P22081500012 | New_Event | Animals | Include | Include | Wildlife | 66 | 2022-08-15 | 132 | keep | 0 | Aug | 2022 | 8.9905e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-15 08:19 | 2022-08-15 11:06 | 5 | 2:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIAS FUERTES | M22081500011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 167 | 2022-08-15 | 835 | keep | 0 | Aug | 2022 | 0.00056871 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-15 08:29 | 2022-08-15 10:50 | 184 | 2:21 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22081500027 | New_Event | Animals | Include | Include | Wildlife | 141 | 2022-08-15 | 25944 | keep | 0 | Aug | 2022 | 0.01767 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
CAGUAS | 2022-08-15 08:43 | 2022-08-16 12:42 | 10 | 27:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA X 50KVA | C22081500030 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1679 | 2022-08-15 | 16790 | keep | 0 | Aug | 2022 | 0.011436 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-15 08:48 | 2022-08-15 12:30 | 93 | 3:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22081500031 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 222 | 2022-08-15 | 20646 | keep | 0 | Aug | 2022 | 0.014062 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
AGUADILLA | 2022-08-15 08:56 | 2022-08-15 16:23 | 1 | 7:27 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA A CAUSA DE DESGANCHE | M22081200058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 447 | 2022-08-15 | 447 | keep | 0 | Aug | 2022 | 0.00030445 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-15 08:57 | 2022-08-15 09:59 | 45 | 1:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-08-15 | 2790 | keep | 0 | Aug | 2022 | 0.0019003 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-08-15 08:58 | 2022-08-16 11:21 | 12 | 26:23 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 EN TRANSFORMADOR SE CERRO PUENTE PRIMARIO | S22081500016 | New_Event | Primary Wire Break | Include | Include | Equipment | 1583 | 2022-08-15 | 18996 | keep | 0 | Aug | 2022 | 0.012938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-15 09:01 | 2022-08-15 12:25 | 60 | 3:24 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA 1 X 65 EN RISER 1X 80 EN RIER 1 X 100 EN RISER | S22081500017 | New_Event | Primary Wire Break | Include | Include | Equipment | 204 | 2022-08-15 | 12240 | keep | 0 | Aug | 2022 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-08-15 09:15 | 2022-08-15 14:57 | 6 | 5:42 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PRIMARIO IMPACTADO POR VEHICULO | C22081500037 | New_Event | Damage From Public | Include | Include | Public | 342 | 2022-08-15 | 2052 | keep | 0 | Aug | 2022 | 0.0013976 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-15 09:15 | 2022-08-15 11:20 | 6 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXIONES SECUNDARIAS | M22081500016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2022-08-15 | 750 | keep | 0 | Aug | 2022 | 0.00051082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-15 09:17 | 2022-08-15 09:50 | 15 | 0:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS EN TRANSFORMADOR | M22081500017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 33 | 2022-08-15 | 495 | keep | 0 | Aug | 2022 | 0.00033714 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-15 09:18 | 2022-08-15 11:15 | 1 | 1:57 | P | DESCONECTIVO DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | M22081500018 | New_Event | Switch Failure | Include | Include | Equipment | 117 | 2022-08-15 | 117 | keep | 0 | Aug | 2022 | 7.9688e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-15 09:18 | 2022-08-15 11:20 | 1 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22081500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-08-15 | 122 | keep | 0 | Aug | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-15 09:27 | 2022-08-15 10:35 | 7 | 1:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22081500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-08-15 | 476 | keep | 0 | Aug | 2022 | 0.0003242 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-15 09:32 | 2022-08-15 11:06 | 19 | 1:34 | P | ANIMAL | 1 X 10 EN XMR Y SE RETIRO AVE | B22081500001 | New_Event | Animals | Include | Include | Wildlife | 94 | 2022-08-15 | 1786 | keep | 0 | Aug | 2022 | 0.0012164 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-08-15 09:38 | 2022-08-15 22:19 | 16 | 12:41 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO BAJANTE SECUNDARIO | S22081500023 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 761 | 2022-08-15 | 12176 | keep | 0 | Aug | 2022 | 0.008293 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2022-08-15 09:58 | 2022-08-15 11:04 | 50 | 1:06 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P22081500022 | New_Event | Animals | Include | Include | Wildlife | 66 | 2022-08-15 | 3300 | keep | 0 | Aug | 2022 | 0.0022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-15 10:06 | 2022-08-15 12:13 | 80 | 2:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22081500023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-08-15 | 10160 | keep | 0 | Aug | 2022 | 0.0069199 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-08-15 10:24 | 2022-08-15 17:33 | 200 | 7:09 | P | NO SE REPORTO CAUSA | 2 X 100 Y 2 X 80 EN C/L | R22081500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 429 | 2022-08-15 | 85800 | keep | 0 | Aug | 2022 | 0.058438 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 873 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 62856 | keep | 0 | Aug | 2022 | 0.042811 | 0.0005946 | Sustained | FALSE | FALSE | Not_TMED_Event | 873
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 1261 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 90792 | keep | 0 | Aug | 2022 | 0.061838 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 2713 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 195336 | keep | 0 | Aug | 2022 | 0.13304 | 0.0018478 | Sustained | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 51 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 LLEVA CARGA DE 6001-05 | M22081500243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 3672 | keep | 0 | Aug | 2022 | 0.002501 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 285 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 16000 CARGA POR 6001-04 | M22081500243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 20520 | keep | 0 | Aug | 2022 | 0.013976 | 0.00019411 | Sustained | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 192 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22081500250 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 9792 | keep | 0 | Aug | 2022 | 0.0066693 | 0.00013077 | Sustained | FALSE | FALSE | Not_TMED_Event | 192
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 20 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22081500250 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 1020 | keep | 0 | Aug | 2022 | 0.00069472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 406 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22081500250 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 20706 | keep | 0 | Aug | 2022 | 0.014103 | 0.00027652 | Sustained | FALSE | FALSE | Not_TMED_Event | 406
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 793 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22081500250 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 40443 | keep | 0 | Aug | 2022 | 0.027546 | 0.00054011 | Sustained | FALSE | FALSE | Not_TMED_Event | 793
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 1509 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22081500250 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 76959 | keep | 0 | Aug | 2022 | 0.052416 | 0.0010278 | Sustained | FALSE | FALSE | Not_TMED_Event | 1509
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:35 | 824 | 2:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 CARGA POR 6003-03 | M22081500247 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 170 | 2022-08-15 | 140080 | keep | 0 | Aug | 2022 | 0.095408 | 0.00056122 | Sustained | FALSE | FALSE | Not_TMED_Event | 824
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:35 | 146 | 2:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 | M22081500247 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 170 | 2022-08-15 | 24820 | keep | 0 | Aug | 2022 | 0.016905 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:35 | 667 | 2:50 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 LLEVA CARGA DE 6003-01 | M22081500247 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 170 | 2022-08-15 | 113390 | keep | 0 | Aug | 2022 | 0.077229 | 0.00045429 | Sustained | FALSE | FALSE | Not_TMED_Event | 667
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 1142 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 58242 | keep | 0 | Aug | 2022 | 0.039668 | 0.00077781 | Sustained | FALSE | FALSE | Not_TMED_Event | 1142
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 409 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 20859 | keep | 0 | Aug | 2022 | 0.014207 | 0.00027857 | Sustained | FALSE | FALSE | Not_TMED_Event | 409
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:36 | 424 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500030 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2022-08-15 | 21624 | keep | 0 | Aug | 2022 | 0.014728 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 1145 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500246 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 82440 | keep | 0 | Aug | 2022 | 0.05615 | 0.00077985 | Sustained | FALSE | FALSE | Not_TMED_Event | 1145
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 1889 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 | M22081500246 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 136008 | keep | 0 | Aug | 2022 | 0.092634 | 0.0012866 | Sustained | FALSE | FALSE | Not_TMED_Event | 1889
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:50 | 372 | 3:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 SE CERRO POR SCADA YA QUE PERSONAL DE CCE PONCE REALIZO OPERACIONES EN SCADA PARA PODER ENERGIZAR TRAMO QUE ALIMENTA SUBESTACION. CARGA SE ENCUENTRA POR INTERRUPTOR SPARE 6008-03 | M22081500251 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 185 | 2022-08-15 | 68820 | keep | 0 | Aug | 2022 | 0.046873 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:50 | 2530 | 3:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 SE CERRO POR SCADA YA QUE PERSONAL DE CCE PONCE REALIZO OPERACIONES EN SCADA PARA PODER ENERGIZAR TRAMO QUE ALIMENTA SUBESTACION | M22081500251 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 185 | 2022-08-15 | 468050 | keep | 0 | Aug | 2022 | 0.31879 | 0.0017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:50 | 199 | 3:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 SE CERRO POR SCADA YA QUE PERSONAL DE CCE PONCE REALIZO OPERACIONES EN SCADA PARA PODER ENERGIZAR TRAMO QUE ALIMENTA SUBESTACION | M22081500251 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 185 | 2022-08-15 | 36815 | keep | 0 | Aug | 2022 | 0.025075 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:12 | 1253 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 LLEVA CARGA DE 6010-02 | M22081500238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 33831 | keep | 0 | Aug | 2022 | 0.023042 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:12 | 1266 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 CARGA POR 6010-01 | M22081500238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 34182 | keep | 0 | Aug | 2022 | 0.023281 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:12 | 411 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500238 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 11097 | keep | 0 | Aug | 2022 | 0.0075581 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 10:46 | 1352 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 FUE AFECTADO POR DISPARO DE LINEA 1600 | M22081500000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1352 | keep | 0 | Aug | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 1444 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 CARGA POR 6014-02 | M22081500236 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 103968 | keep | 0 | Aug | 2022 | 0.070812 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 10:46 | 871 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE BARRA 38KV MAYAGÃœEZ PLANTA A CAUSA DE AVERIA EN LINEA 1600 CARGA POR 6012-05 | M22081500028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 871 | keep | 0 | Aug | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:52 | 312 | 3:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 SE CERRO POR SCADA YA QUE PERSONAL DE CCE PONCE REALIZO OPERACIONES EN SCADA PARA PODER ENERGIZAR TRAMO QUE ALIMENTA SUBESTACION. | M22081500232 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2022-08-15 | 58344 | keep | 0 | Aug | 2022 | 0.039738 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 13:52 | 4641 | 3:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1600 SE CERRO POR SCADA YA QUE PERSONAL DE CCE PONCE REALIZO OPERACIONES EN SCADA PARA PODER ENERGIZAR TRAMO QUE ALIMENTA SUBESTACION. | M22081500232 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 187 | 2022-08-15 | 867867 | keep | 0 | Aug | 2022 | 0.5911 | 0.003161 | Sustained | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 10:58 | 810 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 A CAUSA DE AVERIA EN LINEA 1600 | M22081500229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2022-08-15 | 10530 | keep | 0 | Aug | 2022 | 0.0071719 | 0.00055169 | Sustained | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 10:58 | 1235 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 A CAUSA DE AVERIA EN LINEA 1600 | M22081500229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2022-08-15 | 16055 | keep | 0 | Aug | 2022 | 0.010935 | 0.00084115 | Sustained | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 10:58 | 93 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 A CAUSA DE AVERIA EN LINEA 1600 | M22081500229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2022-08-15 | 1209 | keep | 0 | Aug | 2022 | 0.00082344 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 10:58 | 1825 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 A CAUSA DE AVERIA EN LINEA 1600 | M22081500229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2022-08-15 | 23725 | keep | 0 | Aug | 2022 | 0.016159 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 10:58 | 3230 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 A CAUSA DE AVERIA EN LINEA 1600 | M22081500229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2022-08-15 | 41990 | keep | 0 | Aug | 2022 | 0.028599 | 0.0021999 | Sustained | FALSE | FALSE | Not_TMED_Event | 3230
AGUADILLA | 2022-08-15 10:45 | 2022-08-15 11:12 | 1617 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 43659 | keep | 0 | Aug | 2022 | 0.029736 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-08-15 10:45 | 2022-08-15 11:12 | 1017 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 27459 | keep | 0 | Aug | 2022 | 0.018702 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-08-15 10:45 | 2022-08-15 11:12 | 828 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500240 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 22356 | keep | 0 | Aug | 2022 | 0.015227 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:12 | 863 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500248 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 23301 | keep | 0 | Aug | 2022 | 0.01587 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:12 | 309 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500248 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 8343 | keep | 0 | Aug | 2022 | 0.0056824 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:12 | 176 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500248 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 4752 | keep | 0 | Aug | 2022 | 0.0032366 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:57 | 108 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 A CAUSA DE AVERIA EN LINEA 1600 | M22081500249 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-08-15 | 7776 | keep | 0 | Aug | 2022 | 0.0052962 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-08-15 10:45 | 2022-08-15 11:12 | 974 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 A CAUSA DE AVERIA EN LINEA 1600 | M22081500226 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-15 | 26298 | keep | 0 | Aug | 2022 | 0.017911 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
CANOVANAS | 2022-08-15 11:05 | 2022-08-15 11:06 | 1862 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 1862 | keep | 0 | Aug | 2022 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
BAYAMON | 2022-08-15 11:05 | 2022-08-15 15:35 | 2 | 4:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5KVA POR UNO DE 25KVA | B22081500029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 270 | 2022-08-15 | 540 | keep | 0 | Aug | 2022 | 0.00036779 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-15 11:09 | 2022-08-15 11:10 | 68 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECERRO POR 1106-05 | S22081500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-15 | 68 | keep | 0 | Aug | 2022 | 4.6314e-05 | 4.6314e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-08-15 11:09 | 2022-08-15 11:10 | 348 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECERRO POR 1106-05 | S22081500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-15 | 348 | keep | 0 | Aug | 2022 | 0.00023702 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-08-15 11:09 | 2022-08-15 11:10 | 348 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECERRO POR 1106-05 | S22081500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-15 | 348 | keep | 0 | Aug | 2022 | 0.00023702 | 0.00023702 | Momentary | FALSE | FALSE | Not_TMED_Event | 348
SAN JUAN | 2022-08-15 11:09 | 2022-08-15 11:10 | 733 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECERRO LLEVA 1102-01,05,04 | S22081500000 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-15 | 733 | keep | 0 | Aug | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-08-15 11:32 | 2022-08-15 11:33 | 726 | 0:01 | T | CAUSAS EXTERNAS | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-04 | S22081500000 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-15 | 726 | keep | 0 | Aug | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-08-15 11:32 | 2022-08-15 11:33 | 3932 | 0:01 | T | CAUSAS EXTERNAS | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1303-03 | S22081500000 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-15 | 3932 | keep | 0 | Aug | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
SAN JUAN | 2022-08-15 11:37 | 2022-08-15 11:38 | 1295 | 0:01 | T | DESGANCHE | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22081500050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-15 | 1295 | keep | 0 | Aug | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
BARRANQUITAS | 2022-08-15 11:51 | 2022-08-15 12:50 | 317 | 0:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22081500065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 59 | 2022-08-15 | 18703 | keep | 0 | Aug | 2022 | 0.012739 | 0.00021591 | Sustained | FALSE | FALSE | Not_TMED_Event | 317
HUMACAO | 2022-08-15 11:52 | 2022-08-15 12:00 | 8 | 0:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | EL TRANSFORMADOR ESTABA EN EL ULTIMO TAP, SE REEMPLAZO CONECTOR SULFATADO Y SE DEJO EN 118 VOLTIOS | C22081500067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 8 | 2022-08-15 | 64 | keep | 0 | Aug | 2022 | 4.359e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-15 12:12 | 2022-08-15 13:02 | 10 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES EN SECUNDARIA | B22081500035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-08-15 | 500 | keep | 0 | Aug | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-15 12:16 | 2022-08-15 15:21 | 175 | 3:05 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500018 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 185 | 2022-08-15 | 32375 | keep | 0 | Aug | 2022 | 0.02205 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BAYAMON | 2022-08-15 12:19 | 2022-08-15 16:35 | 67 | 4:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L 1 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA | B22081500037 | New_Event | Cutout Failure | Include | Include | Equipment | 256 | 2022-08-15 | 17152 | keep | 0 | Aug | 2022 | 0.011682 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BARRANQUITAS | 2022-08-15 12:26 | 2022-08-15 14:21 | 225 | 1:55 | P | MAL TIEMPO/RAYOS | 3 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C22081500078 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 115 | 2022-08-15 | 25875 | keep | 0 | Aug | 2022 | 0.017623 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
BARRANQUITAS | 2022-08-15 12:29 | 2022-08-15 13:34 | 7 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C22081500079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-08-15 | 455 | keep | 0 | Aug | 2022 | 0.0003099 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-15 12:36 | 2022-08-15 17:52 | 120 | 5:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22081500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2022-08-15 | 37920 | keep | 0 | Aug | 2022 | 0.025827 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-08-15 12:47 | 2022-08-15 15:17 | 100 | 2:30 | P | MAL TIEMPO/RAYOS | 1 X 80 Y 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081500286 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 150 | 2022-08-15 | 15000 | keep | 0 | Aug | 2022 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-15 12:47 | 2022-08-15 15:45 | 60 | 2:58 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500038 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 178 | 2022-08-15 | 10680 | keep | 0 | Aug | 2022 | 0.0072741 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-15 12:51 | 2022-08-15 16:20 | 1 | 3:29 | P | ANIMAL | 1 X 10 EN BANCO DE TRANSFORMADOR CRUCE POR AVE | C22081500103 | New_Event | Animals | Include | Include | Wildlife | 209 | 2022-08-15 | 209 | keep | 0 | Aug | 2022 | 0.00014235 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-15 12:52 | 2022-08-15 16:57 | 100 | 4:05 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 245 | 2022-08-15 | 24500 | keep | 0 | Aug | 2022 | 0.016687 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-15 12:57 | 2022-08-15 14:00 | 80 | 1:03 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500045 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 63 | 2022-08-15 | 5040 | keep | 0 | Aug | 2022 | 0.0034327 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-15 12:57 | 2022-08-15 17:44 | 15 | 4:47 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500046 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 287 | 2022-08-15 | 4305 | keep | 0 | Aug | 2022 | 0.0029321 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-15 13:01 | 2022-08-16 00:15 | 11 | 11:14 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | CON EL GOI SJ-220815-52 SE REMPLAZO POSTE PRIMARIO PARTIDO | R22081500099 | New_Event | Primary Pole Failure | Include | Include | Equipment | 674 | 2022-08-15 | 7414 | keep | 0 | Aug | 2022 | 0.0050496 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-08-15 13:06 | 2022-08-15 14:27 | 2234 | 1:21 | T | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA EN SERVICIO | B22081500040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-08-15 | 180954 | keep | 0 | Aug | 2022 | 0.12325 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
PONCE | 2022-08-15 13:07 | 2022-08-15 19:06 | 102 | 5:59 | P | CAUSAS EXTERNAS | REMPLAZO DE POSTE PRIMARIO PARTIDO POR AUTO 3 X 100 EN CORTE DE LINEA | P22081500048 | New_Event | Damage From Public | Include | Include | Public | 359 | 2022-08-15 | 36618 | keep | 0 | Aug | 2022 | 0.02494 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
VEGA BAJA | 2022-08-15 13:07 | 2022-08-16 20:55 | 10 | 31:48 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500054 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1908 | 2022-08-15 | 19080 | keep | 0 | Aug | 2022 | 0.012995 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-15 13:10 | 2022-08-15 13:11 | 1647 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 1647 | keep | 0 | Aug | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
UTUADO | 2022-08-15 13:17 | 2022-08-15 13:24 | 1633 | 0:07 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS SE CERRO MANUALMENTE | A22081500033 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 7 | 2022-08-15 | 11431 | keep | 0 | Aug | 2022 | 0.0077856 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
SAN JUAN | 2022-08-15 13:18 | 2022-08-15 13:19 | 4476 | 0:01 | T | OTRAS CAUSAS | RECIERRE DEL 1619-03 QUE LLEVA 1336-06 | R22081500000 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-08-15 | 4476 | keep | 0 | Aug | 2022 | 0.0030486 | 0.0030486 | Momentary | FALSE | FALSE | Not_TMED_Event | 4476
CANOVANAS | 2022-08-15 13:18 | 2022-08-15 13:19 | 5062 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1619-03 QUE LLEVA 1336-06 | R22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 5062 | keep | 0 | Aug | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
FAJARDO | 2022-08-15 13:18 | 2022-08-15 16:46 | 87 | 3:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L REMPLAZO AISLADOR | R22081500020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 208 | 2022-08-15 | 18096 | keep | 0 | Aug | 2022 | 0.012325 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
PONCE | 2022-08-15 13:20 | 2022-08-15 14:30 | 327 | 1:10 | P | ANIMAL | 1 X 65 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P22081500054 | New_Event | Animals | Include | Include | Wildlife | 70 | 2022-08-15 | 22890 | keep | 0 | Aug | 2022 | 0.01559 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
BAYAMON | 2022-08-15 13:21 | 2022-08-15 13:22 | 3597 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 3597 | keep | 0 | Aug | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
VEGA BAJA | 2022-08-15 13:21 | 2022-08-15 13:22 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081500049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 2704 | keep | 0 | Aug | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
AGUADILLA | 2022-08-15 13:25 | 2022-08-15 14:50 | 6 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS Y LLUVIAS FUERTES | M22081500298 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2022-08-15 | 510 | keep | 0 | Aug | 2022 | 0.00034736 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-08-15 13:25 | 2022-08-16 11:09 | 7 | 21:44 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081500059 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1304 | 2022-08-15 | 9128 | keep | 0 | Aug | 2022 | 0.006217 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-15 13:25 | 2022-08-15 20:30 | 15 | 7:05 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500060 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 425 | 2022-08-15 | 6375 | keep | 0 | Aug | 2022 | 0.004342 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-08-15 13:26 | 2022-08-15 16:40 | 40 | 3:14 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500061 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 194 | 2022-08-15 | 7760 | keep | 0 | Aug | 2022 | 0.0052853 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-15 13:27 | 2022-08-15 13:30 | 215 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA EN SERVICIO | B22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-15 | 645 | keep | 0 | Aug | 2022 | 0.00043931 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BARRANQUITAS | 2022-08-15 13:27 | 2022-08-15 14:40 | 30 | 1:13 | P | MAL TIEMPO/RAYOS | 3 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C22081500092 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 73 | 2022-08-15 | 2190 | keep | 0 | Aug | 2022 | 0.0014916 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-08-15 13:27 | 2022-08-15 20:06 | 335 | 6:39 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C22081500092 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 399 | 2022-08-15 | 133665 | keep | 0 | Aug | 2022 | 0.091039 | 0.00022817 | Sustained | FALSE | FALSE | Not_TMED_Event | 335
VEGA BAJA | 2022-08-15 13:28 | 2022-08-15 16:36 | 30 | 3:08 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22081500064 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 188 | 2022-08-15 | 5640 | keep | 0 | Aug | 2022 | 0.0038414 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-15 13:30 | 2022-08-15 16:04 | 152 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22081500075 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-08-15 | 23408 | keep | 0 | Aug | 2022 | 0.015943 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
AGUADILLA | 2022-08-15 13:33 | 2022-08-15 13:34 | 470 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 470 | keep | 0 | Aug | 2022 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
BARRANQUITAS | 2022-08-15 13:35 | 2022-08-15 15:49 | 484 | 2:14 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | C22081500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-08-15 | 64856 | keep | 0 | Aug | 2022 | 0.044173 | 0.00032965 | Sustained | FALSE | FALSE | Not_TMED_Event | 484
ARECIBO | 2022-08-15 13:36 | 2022-08-15 13:37 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2600 | A22081500074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1 | keep | 0 | Aug | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-15 13:36 | 2022-08-15 13:37 | 2266 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2600 | A22081500074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 2266 | keep | 0 | Aug | 2022 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2022-08-15 13:36 | 2022-08-15 13:37 | 1399 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2600 | A22081500074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1399 | keep | 0 | Aug | 2022 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BARRANQUITAS | 2022-08-15 13:41 | 2022-08-15 21:58 | 45 | 8:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22081500098 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 497 | 2022-08-15 | 22365 | keep | 0 | Aug | 2022 | 0.015233 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-08-15 13:44 | 2022-08-15 13:47 | 3957 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-15 | 11871 | keep | 0 | Aug | 2022 | 0.0080853 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2022-08-15 13:44 | 2022-08-15 15:12 | 12 | 1:28 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE RETIRO POSTE SECUNDARIO PARTIDO Y SE CERRO XMR (NO FUNDIO) | B22081500059 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 88 | 2022-08-15 | 1056 | keep | 0 | Aug | 2022 | 0.00071924 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-15 13:45 | 2022-08-15 13:59 | 1444 | 0:14 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR 6014-02 | M22081500308 | New_Event | Primary Wire Break | Include | Include | Equipment | 14 | 2022-08-15 | 20216 | keep | 0 | Aug | 2022 | 0.013769 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-08-15 13:45 | 2022-08-15 13:59 | 3630 | 0:14 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA CARGA DE 6014-01 | M22081500310 | New_Event | Primary Wire Break | Include | Include | Equipment | 14 | 2022-08-15 | 50820 | keep | 0 | Aug | 2022 | 0.034613 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
AGUADILLA | 2022-08-15 13:48 | 2022-08-15 13:49 | 569 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22081500309 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 569 | keep | 0 | Aug | 2022 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
UTUADO | 2022-08-15 13:49 | 2022-08-15 15:00 | 30 | 1:11 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22081500081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-08-15 | 2130 | keep | 0 | Aug | 2022 | 0.0014507 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-15 13:52 | 2022-08-15 18:44 | 7 | 4:52 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | B22081500071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 292 | 2022-08-15 | 2044 | keep | 0 | Aug | 2022 | 0.0013922 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-15 13:55 | 2022-08-15 15:06 | 6 | 1:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22081500076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 71 | 2022-08-15 | 426 | keep | 0 | Aug | 2022 | 0.00029015 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-15 13:56 | 2022-08-15 19:35 | 11 | 5:39 | P | CAUSAS EXTERNAS | ABRIR BANCO DE TRANSFORMADORES PARA REEMPLAZAR POSTE SECUNDARIO IMPACTADO POR VEHICULO | C22081500106 | New_Event | Damage From Public | Include | Include | Public | 339 | 2022-08-15 | 3729 | keep | 0 | Aug | 2022 | 0.0025398 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-08-15 13:57 | 2022-08-15 14:09 | 222 | 0:12 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 1907-03 QUE LLEVA 1909-09 SE QUEDO FUERA Y SE CERRO POR SCADA MAL TIEMPO LLUVIA | S22081500105 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 12 | 2022-08-15 | 2664 | keep | 0 | Aug | 2022 | 0.0018144 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-15 13:57 | 2022-08-15 14:09 | 4456 | 0:12 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 1907-03 QUE LLEVA 1909-09 SE QUEDO FUERA Y SE CERRO POR SCADA MAL TIEMPO LLUVIA | S22081500105 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 12 | 2022-08-15 | 53472 | keep | 0 | Aug | 2022 | 0.03642 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
BARRANQUITAS | 2022-08-15 13:58 | 2022-08-15 15:19 | 888 | 1:21 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A LINEA CON HOT CLAMP | C22081500095 | New_Event | Primary Wire Break | Include | Include | Equipment | 81 | 2022-08-15 | 71928 | keep | 0 | Aug | 2022 | 0.04899 | 0.00060481 | Sustained | FALSE | FALSE | Not_TMED_Event | 888
BAYAMON | 2022-08-15 13:59 | 2022-08-15 15:30 | 36 | 1:31 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22081500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-08-15 | 3276 | keep | 0 | Aug | 2022 | 0.0022313 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-08-15 13:59 | 2022-08-15 14:11 | 5961 | 0:12 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 1713-05 QUE LLEVA 95% DEL 1717-02 QUEDO FUERA Y SE CERRO POR SCADA - POR LLUVIA | B22081500000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 12 | 2022-08-15 | 71532 | keep | 0 | Aug | 2022 | 0.04872 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-15 13:59 | 2022-08-15 14:11 | 866 | 0:12 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 1713-05 QUE LLEVA 95% DEL 1717-02 QUEDO FUERA Y SE CERRO POR SCADA - POR LLUVIA | B22081500000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 12 | 2022-08-15 | 10392 | keep | 0 | Aug | 2022 | 0.0070779 | 0.00058983 | Sustained | FALSE | FALSE | Not_TMED_Event | 866
MAYAGÃœEZ | 2022-08-15 13:59 | 2022-08-15 19:20 | 200 | 5:21 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE PRIMARIO DE LOS MACHETES | M22081500311 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 321 | 2022-08-15 | 64200 | keep | 0 | Aug | 2022 | 0.043726 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-15 14:02 | 2022-08-16 12:00 | 30 | 21:58 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 Y 1 X 40 EN CONVERTIDOR SE REPARO LINEA PRIMARIA ROTA | A22081500091 | New_Event | Primary Wire Break | Include | Include | Equipment | 1318 | 2022-08-15 | 39540 | keep | 0 | Aug | 2022 | 0.026931 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-15 14:03 | 2022-08-16 07:39 | 8 | 17:36 | P | DESGANCHE | 3 X 80 EN C/L SE REALIZO DESGANCHE | R22081500104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1056 | 2022-08-15 | 8448 | keep | 0 | Aug | 2022 | 0.0057539 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-15 14:06 | 2022-08-15 14:07 | 1352 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6014-03 | M22081500319 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-15 | 1352 | keep | 0 | Aug | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-08-15 14:06 | 2022-08-15 14:07 | 871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6012-05 | M22081500319 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 871 | keep | 0 | Aug | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
ARECIBO | 2022-08-15 14:09 | 2022-08-15 16:45 | 25 | 2:36 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 156 | 2022-08-15 | 3900 | keep | 0 | Aug | 2022 | 0.0026563 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-15 14:10 | 2022-08-15 17:10 | 90 | 3:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMAIRA DEFECTUOSA | C22081500114 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2022-08-15 | 16200 | keep | 0 | Aug | 2022 | 0.011034 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-08-15 14:16 | 2022-08-15 15:40 | 2276 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A LA MUDA | C22081500117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-08-15 | 191184 | keep | 0 | Aug | 2022 | 0.13021 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-08-15 14:16 | 2022-08-15 15:40 | 777 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A LA MUDA | C22081500117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-08-15 | 65268 | keep | 0 | Aug | 2022 | 0.044454 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-08-15 14:16 | 2022-08-15 15:40 | 12 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A LA MUDA | C22081500117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-08-15 | 1008 | keep | 0 | Aug | 2022 | 0.00068654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-15 14:16 | 2022-08-15 15:40 | 1290 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE CAGUAS A LA MUDA | C22081500117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-08-15 | 108360 | keep | 0 | Aug | 2022 | 0.073804 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2022-08-15 14:16 | 2022-08-15 16:52 | 15 | 2:36 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B22081500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-08-15 | 2340 | keep | 0 | Aug | 2022 | 0.0015938 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-15 14:19 | 2022-08-15 18:25 | 160 | 4:06 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A22081500102 | New_Event | Primary Wire Break | Include | Include | Equipment | 246 | 2022-08-15 | 39360 | keep | 0 | Aug | 2022 | 0.026808 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2022-08-15 14:19 | 2022-08-15 18:40 | 300 | 4:21 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO C/L | B22081500099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-08-15 | 78300 | keep | 0 | Aug | 2022 | 0.05333 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-08-15 14:21 | 2022-08-15 16:36 | 1352 | 2:15 | T | CONDUCTOR ROTO O ABIERTO | INTERRUPTOR RECERRO TRES VECES Y QUEDO FUERA DE SERVICIO. SE REPARO BAJANTE PRIMARIO ZAFADO Y SE PROCEDIO A CERRAR INTERRUPTOR POR SCADA LLEVA CARGA POR 6014-03 | M22081500328 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 135 | 2022-08-15 | 182520 | keep | 0 | Aug | 2022 | 0.12431 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-08-15 14:21 | 2022-08-15 16:36 | 871 | 2:15 | T | CONDUCTOR ROTO O ABIERTO | INTERRUPTOR RECERRO TRES VECES Y QUEDO FUERA DE SERVICIO. SE REPARO BAJANTE PRIMARIO ZAFADO Y SE PROCEDIO A CERRAR INTERRUPTOR POR SCADA CARGA POR 6012-05 | M22081500328 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2022-08-15 | 117585 | keep | 0 | Aug | 2022 | 0.080087 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
CANOVANAS | 2022-08-15 14:25 | 2022-08-15 18:15 | 290 | 3:50 | P | CONDUCTOR ROTO O ABIERTO | ABRIO MACHETES PARA LEVANTAR NEUTRAL PRIMARIO | R22081500110 | New_Event | Primary Wire Break | Include | Include | Equipment | 230 | 2022-08-15 | 66700 | keep | 0 | Aug | 2022 | 0.045429 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
BAYAMON | 2022-08-15 14:27 | 2022-08-15 14:55 | 100 | 0:28 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO POR SCADA EN SERVICIO SE REPUSO 1 X 80 EN CONVERTIDOR BY-220815-01 | B22081500040 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-08-15 | 2800 | keep | 0 | Aug | 2022 | 0.0019071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-15 14:28 | 2022-08-16 09:58 | 1 | 19:30 | P | SOBRECARGA | 1 X 40 EN TRANSFORMADOR | M22081500331 | New_Event | Trip Due To Overload | Include | Include | Other | 1170 | 2022-08-15 | 1170 | keep | 0 | Aug | 2022 | 0.00079688 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-15 14:34 | 2022-08-15 17:13 | 1 | 2:39 | P | ANIMAL | 2 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22081500125 | New_Event | Animals | Include | Include | Wildlife | 159 | 2022-08-15 | 159 | keep | 0 | Aug | 2022 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-15 14:44 | 2022-08-15 18:40 | 25 | 3:56 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C22081500135 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 236 | 2022-08-15 | 5900 | keep | 0 | Aug | 2022 | 0.0040185 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-08-15 14:45 | 2022-08-15 14:46 | 4035 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22081500074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 4035 | keep | 0 | Aug | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
FAJARDO | 2022-08-15 14:48 | 2022-08-15 18:14 | 10 | 3:26 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | R22081500113 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 206 | 2022-08-15 | 2060 | keep | 0 | Aug | 2022 | 0.0014031 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-15 14:51 | 2022-08-15 17:38 | 10 | 2:47 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081500333 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 167 | 2022-08-15 | 1670 | keep | 0 | Aug | 2022 | 0.0011374 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-15 15:00 | 2022-08-15 19:35 | 94 | 4:35 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 EN C/L | B22081500121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 275 | 2022-08-15 | 25850 | keep | 0 | Aug | 2022 | 0.017606 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
ARECIBO | 2022-08-15 15:02 | 2022-08-15 17:15 | 8 | 2:13 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081500122 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 133 | 2022-08-15 | 1064 | keep | 0 | Aug | 2022 | 0.00072469 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-15 15:05 | 2022-08-16 14:15 | 100 | 23:10 | P | MAL TIEMPO/RAYOS | 1 X 65 Y 1 X 30 EN CORTES DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500207 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1390 | 2022-08-15 | 139000 | keep | 0 | Aug | 2022 | 0.094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-15 15:08 | 2022-08-15 16:55 | 15 | 1:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M22081500347 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-08-15 | 1605 | keep | 0 | Aug | 2022 | 0.0010932 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-15 15:08 | 2022-08-15 19:23 | 158 | 4:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO DOS PUENTES ABIERTOS Y SE CERRO C/L | B22081500129 | New_Event | Primary Wire Break | Include | Include | Equipment | 255 | 2022-08-15 | 40290 | keep | 0 | Aug | 2022 | 0.027441 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
SAN JUAN | 2022-08-15 15:09 | 2022-08-15 16:29 | 199 | 1:20 | T | DESGANCHE | DISPARO 1529-13 QUE LLEVA 25% DEL 1911-07, SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S22081500146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-08-15 | 15920 | keep | 0 | Aug | 2022 | 0.010843 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-08-15 15:09 | 2022-08-15 16:29 | 144 | 1:20 | P | DESGANCHE | DISPARO 1529-13 QUE LLEVA 25% DEL 1911-07, SE REALIZO DESGANCHE Y SE CERRO POR SCADA | S22081500146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-08-15 | 11520 | keep | 0 | Aug | 2022 | 0.0078462 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
PONCE | 2022-08-15 15:15 | 2022-08-15 19:10 | 90 | 3:55 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22081500078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-08-15 | 21150 | keep | 0 | Aug | 2022 | 0.014405 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
GUAYAMA | 2022-08-15 15:26 | 2022-08-15 17:15 | 10 | 1:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REEMPLAZAR CONEXIONES EN BARRA DE PEDESTAL | P22081500083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 109 | 2022-08-15 | 1090 | keep | 0 | Aug | 2022 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-15 15:28 | 2022-08-15 18:54 | 60 | 3:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081500134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2022-08-15 | 12360 | keep | 0 | Aug | 2022 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-15 15:28 | 2022-08-15 15:29 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081500133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 3699 | keep | 0 | Aug | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
BAYAMON | 2022-08-15 15:29 | 2022-08-15 15:31 | 2234 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22081500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-15 | 4468 | keep | 0 | Aug | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
HUMACAO | 2022-08-15 15:46 | 2022-08-15 16:32 | 11 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C22081500158 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2022-08-15 | 506 | keep | 0 | Aug | 2022 | 0.00034463 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-08-15 15:55 | 2022-08-15 18:50 | 50 | 2:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081500146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-08-15 | 8750 | keep | 0 | Aug | 2022 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-15 16:05 | 2022-08-15 20:28 | 50 | 4:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22081500378 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 263 | 2022-08-15 | 13150 | keep | 0 | Aug | 2022 | 0.0089564 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-15 16:23 | 2022-08-15 17:21 | 50 | 0:58 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22081500161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-08-15 | 2900 | keep | 0 | Aug | 2022 | 0.0019752 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-15 16:28 | 2022-08-15 18:08 | 45 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22081500382 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2022-08-15 | 4500 | keep | 0 | Aug | 2022 | 0.0030649 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-08-15 16:28 | 2022-08-15 18:15 | 12 | 1:47 | P | MAL TIEMPO/RAYOS | 1 X 40 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081500383 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 107 | 2022-08-15 | 1284 | keep | 0 | Aug | 2022 | 0.00087453 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-15 16:30 | 2022-08-15 20:44 | 150 | 4:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081500295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-08-15 | 38100 | keep | 0 | Aug | 2022 | 0.02595 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-08-15 16:35 | 2022-08-16 10:17 | 100 | 17:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIA FUERTE | B22081500170 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1062 | 2022-08-15 | 106200 | keep | 0 | Aug | 2022 | 0.072332 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-15 16:37 | 2022-08-16 12:58 | 8 | 20:21 | P | MAL TIEMPO/RAYOS | 1 X 80 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS EVENTO DEL DIA 8/15 CON WR 6217254 A LAS 04:37PM CREADO CON FASE FUERA EN VEZ DE COMO EVENTO | A22081600112 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1221 | 2022-08-15 | 9768 | keep | 0 | Aug | 2022 | 0.0066529 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-15 16:46 | 2022-08-15 19:58 | 25 | 3:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 10 EN TRANSFORMADOR 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22081500388 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 192 | 2022-08-15 | 4800 | keep | 0 | Aug | 2022 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-15 16:47 | 2022-08-15 17:35 | 30 | 0:48 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L 1 X 15 EN XMR MAL TIEMPO RAYOS | B22081500174 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 48 | 2022-08-15 | 1440 | keep | 0 | Aug | 2022 | 0.00098078 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-15 16:52 | 2022-08-16 07:39 | 5 | 14:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA PRIMARIA | B22081500179 | New_Event | Cutout Failure | Include | Include | Equipment | 887 | 2022-08-15 | 4435 | keep | 0 | Aug | 2022 | 0.0030207 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-15 16:54 | 2022-08-15 18:51 | 8 | 1:57 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S22081500266 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 117 | 2022-08-15 | 936 | keep | 0 | Aug | 2022 | 0.00063751 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-15 16:59 | 2022-08-16 07:16 | 20 | 14:17 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22081500178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 857 | 2022-08-15 | 17140 | keep | 0 | Aug | 2022 | 0.011674 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-15 17:00 | 2022-08-15 17:57 | 3 | 0:57 | P | ARBOL SOBRE LINEA | SE REPARO LINEA SECUNDARIA A CAUSA DE ARBOL QUE CAYO SOBRE LA LINEA | M22081500349 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 57 | 2022-08-15 | 171 | keep | 0 | Aug | 2022 | 0.00011647 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-08-15 17:03 | 2022-08-15 19:57 | 100 | 2:54 | P | MAL TIEMPO/RAYOS | 3 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081500164 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 174 | 2022-08-15 | 17400 | keep | 0 | Aug | 2022 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-15 17:07 | 2022-08-15 21:17 | 100 | 4:10 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M22081500397 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 250 | 2022-08-15 | 25000 | keep | 0 | Aug | 2022 | 0.017027 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-08-15 17:15 | 2022-08-15 17:17 | 3420 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-15 | 6840 | keep | 0 | Aug | 2022 | 0.0046587 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
MAYAGÃœEZ | 2022-08-15 17:20 | 2022-08-15 21:25 | 45 | 4:05 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081500403 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 245 | 2022-08-15 | 11025 | keep | 0 | Aug | 2022 | 0.0075091 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-08-15 17:24 | 2022-08-15 18:20 | 50 | 0:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22081500199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2022-08-15 | 2800 | keep | 0 | Aug | 2022 | 0.0019071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-15 17:24 | 2022-08-15 21:50 | 40 | 4:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22081500187 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 266 | 2022-08-15 | 10640 | keep | 0 | Aug | 2022 | 0.0072469 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-08-15 17:30 | 2022-08-16 08:53 | 3 | 15:23 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081500175 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 923 | 2022-08-15 | 2769 | keep | 0 | Aug | 2022 | 0.001886 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2022-08-15 17:34 | 2022-08-16 16:10 | 4 | 22:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15KVA | A22081500178 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1356 | 2022-08-15 | 5424 | keep | 0 | Aug | 2022 | 0.0036943 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-15 17:48 | 2022-08-15 21:52 | 85 | 4:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 Y 2 X 40 EN C/LS REMPLAZO CAJA QUEMADA | R22081500145 | New_Event | Cutout Failure | Include | Include | Equipment | 244 | 2022-08-15 | 20740 | keep | 0 | Aug | 2022 | 0.014126 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2022-08-15 17:51 | 2022-08-16 10:13 | 12 | 16:22 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | S22081500284 | New_Event | Animals | Include | Include | Wildlife | 982 | 2022-08-15 | 11784 | keep | 0 | Aug | 2022 | 0.008026 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-08-15 17:59 | 2022-08-15 22:52 | 50 | 4:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22081500194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 293 | 2022-08-15 | 14650 | keep | 0 | Aug | 2022 | 0.009978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-15 18:03 | 2022-08-15 20:18 | 3000 | 2:15 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA SECCIONALIZAR ALAMBRE EN EL SUELO Y SE CERRO POR SCADA | B22081500227 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2022-08-15 | 405000 | keep | 0 | Aug | 2022 | 0.27584 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
AGUADILLA | 2022-08-15 18:08 | 2022-08-16 09:39 | 5 | 15:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22081500422 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 931 | 2022-08-15 | 4655 | keep | 0 | Aug | 2022 | 0.0031705 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-08-15 18:12 | 2022-08-15 20:04 | 50 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | A22081500198 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2022-08-15 | 5600 | keep | 0 | Aug | 2022 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-15 18:17 | 2022-08-15 20:40 | 40 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L Y 1 X 10 EN XMR REMPLAZO CAJA AVERIADA | R22081500151 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-08-15 | 5720 | keep | 0 | Aug | 2022 | 0.0038959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-15 18:29 | 2022-08-15 20:48 | 4304 | 2:19 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE INTENTO CERRAR POR SCADA Y QUEDO FUERA DE SERVICIO. SE ENCONTRO PUENTE ABIERTO. SE SECCIONALIZO PARA PODER TRABAJAR. | M22081500430 | New_Event | Primary Wire Break | Include | Include | Equipment | 139 | 2022-08-15 | 598256 | keep | 0 | Aug | 2022 | 0.40747 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
CAGUAS | 2022-08-15 18:45 | 2022-08-16 20:24 | 15 | 25:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO DE TRANSFORMADOR DE 75KVA X 50KVA | C22081500203 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1539 | 2022-08-15 | 23085 | keep | 0 | Aug | 2022 | 0.015723 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-15 19:21 | 2022-08-16 06:49 | 50 | 11:28 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22081500205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 688 | 2022-08-15 | 34400 | keep | 0 | Aug | 2022 | 0.02343 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-15 19:27 | 2022-08-15 21:16 | 2 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22081500156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-08-15 | 218 | keep | 0 | Aug | 2022 | 0.00014848 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-15 19:27 | 2022-08-16 12:10 | 80 | 16:43 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | M22081500494 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1003 | 2022-08-15 | 80240 | keep | 0 | Aug | 2022 | 0.054651 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-15 19:28 | 2022-08-16 15:50 | 25 | 20:22 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081500216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1222 | 2022-08-15 | 30550 | keep | 0 | Aug | 2022 | 0.020807 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-15 19:30 | 2022-08-15 22:27 | 300 | 2:57 | P | DESGANCHE | 1 X65 EN C/L | B22081500291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-08-15 | 53100 | keep | 0 | Aug | 2022 | 0.036166 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2022-08-15 19:33 | 2022-08-15 21:29 | 4 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | M22081500498 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-08-15 | 464 | keep | 0 | Aug | 2022 | 0.00031603 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-15 19:39 | 2022-08-16 10:50 | 8 | 15:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | M22081500504 | New_Event | Primary Wire Break | Include | Include | Equipment | 911 | 2022-08-15 | 7288 | keep | 0 | Aug | 2022 | 0.0049638 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-15 19:43 | 2022-08-15 23:16 | 60 | 3:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081500307 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-08-15 | 12780 | keep | 0 | Aug | 2022 | 0.0087044 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-15 19:46 | 2022-08-16 08:19 | 2678 | 12:33 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO INTERRUPTOR SECCIONALIZANDO CONDUCTOR PRIMARIO PARTIDO. 25% EN SERVICIO | B22081500312 | New_Event | Primary Wire Break | Include | Include | Equipment | 753 | 2022-08-15 | 2016534 | keep | 0 | Aug | 2022 | 1.3735 | 0.001824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2678
HUMACAO | 2022-08-15 19:50 | 2022-08-15 19:51 | 1891 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500207 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1891 | keep | 0 | Aug | 2022 | 0.001288 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-08-15 19:50 | 2022-08-15 19:51 | 1250 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500207 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1250 | keep | 0 | Aug | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-08-15 19:50 | 2022-08-15 19:51 | 2141 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500207 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 2141 | keep | 0 | Aug | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-08-15 19:50 | 2022-08-15 19:51 | 1827 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500207 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1827 | keep | 0 | Aug | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 2775 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 2775 | keep | 0 | Aug | 2022 | 0.00189 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 1457 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1457 | keep | 0 | Aug | 2022 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 1086 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1086 | keep | 0 | Aug | 2022 | 0.00073967 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 2134 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 2134 | keep | 0 | Aug | 2022 | 0.0014535 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 1464 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1464 | keep | 0 | Aug | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 1833 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1833 | keep | 0 | Aug | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 1565 | keep | 0 | Aug | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-08-15 19:50 | 2022-08-15 19:51 | 977 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-15 | 977 | keep | 0 | Aug | 2022 | 0.00066543 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
ARECIBO | 2022-08-15 20:05 | 2022-08-15 21:13 | 3 | 1:08 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081500224 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 68 | 2022-08-15 | 204 | keep | 0 | Aug | 2022 | 0.00013894 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-08-15 20:09 | 2022-08-16 09:14 | 3 | 13:05 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081500227 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 785 | 2022-08-15 | 2355 | keep | 0 | Aug | 2022 | 0.001604 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-08-15 20:11 | 2022-08-15 20:13 | 1891 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 3782 | keep | 0 | Aug | 2022 | 0.0025759 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-08-15 20:11 | 2022-08-15 20:13 | 1250 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 2500 | keep | 0 | Aug | 2022 | 0.0017027 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-08-15 20:11 | 2022-08-15 20:13 | 2141 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 4282 | keep | 0 | Aug | 2022 | 0.0029165 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-08-15 20:11 | 2022-08-15 20:13 | 1827 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 DE HUMACAO A MAUNABO TC | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 3654 | keep | 0 | Aug | 2022 | 0.0024887 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 2775 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500132 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 5550 | keep | 0 | Aug | 2022 | 0.0037801 | 0.00189 | Momentary | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 1457 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500132 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 2914 | keep | 0 | Aug | 2022 | 0.0019847 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 1086 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500132 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 2172 | keep | 0 | Aug | 2022 | 0.0014793 | 0.00073967 | Momentary | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 2134 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500132 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 4268 | keep | 0 | Aug | 2022 | 0.0029069 | 0.0014535 | Momentary | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 1464 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500133 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 2928 | keep | 0 | Aug | 2022 | 0.0019942 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 1833 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500133 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 3666 | keep | 0 | Aug | 2022 | 0.0024969 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 1565 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500133 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 3130 | keep | 0 | Aug | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-08-15 20:11 | 2022-08-15 20:13 | 977 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500133 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-15 | 1954 | keep | 0 | Aug | 2022 | 0.0013309 | 0.00066543 | Momentary | FALSE | FALSE | Not_TMED_Event | 977
BAYAMON | 2022-08-15 20:15 | 2022-08-16 09:42 | 35 | 13:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22081500307 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 807 | 2022-08-15 | 28245 | keep | 0 | Aug | 2022 | 0.019238 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2022-08-15 20:16 | 2022-08-16 16:49 | 80 | 20:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081500229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1233 | 2022-08-15 | 98640 | keep | 0 | Aug | 2022 | 0.067183 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-08-15 20:18 | 2022-08-16 00:25 | 1891 | 4:07 | S | LINEA DE TRANSMISION 38KV | CERRO PUENTE EN LA LINEA 3700 | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2022-08-15 | 467077 | keep | 0 | Aug | 2022 | 0.31812 | 0.001288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2022-08-15 20:18 | 2022-08-16 00:25 | 1250 | 4:07 | S | LINEA DE TRANSMISION 38KV | CERRO PUENTE EN LA LINEA 3700 | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2022-08-15 | 308750 | keep | 0 | Aug | 2022 | 0.21029 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-08-15 20:18 | 2022-08-16 00:25 | 2141 | 4:07 | S | LINEA DE TRANSMISION 38KV | CERRO PUENTE EN LA LINEA 3700 | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2022-08-15 | 528827 | keep | 0 | Aug | 2022 | 0.36018 | 0.0014582 | Sustained | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-08-15 20:18 | 2022-08-16 00:25 | 1827 | 4:07 | S | LINEA DE TRANSMISION 38KV | CERRO PUENTE EN LA LINEA 3700 | C22081500211 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 247 | 2022-08-15 | 451269 | keep | 0 | Aug | 2022 | 0.30736 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:39 | 2775 | 1:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2022-08-15 | 224775 | keep | 0 | Aug | 2022 | 0.15309 | 0.00189 | Sustained | FALSE | FALSE | Not_TMED_Event | 2775
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:21 | 1457 | 1:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-08-15 | 91791 | keep | 0 | Aug | 2022 | 0.062518 | 0.00099236 | Sustained | FALSE | FALSE | Not_TMED_Event | 1457
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:21 | 1086 | 1:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 63 | 2022-08-15 | 68418 | keep | 0 | Aug | 2022 | 0.046599 | 0.00073967 | Sustained | FALSE | FALSE | Not_TMED_Event | 1086
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:39 | 2134 | 1:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500143 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 81 | 2022-08-15 | 172854 | keep | 0 | Aug | 2022 | 0.11773 | 0.0014535 | Sustained | FALSE | FALSE | Not_TMED_Event | 2134
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:22 | 1464 | 1:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500144 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 64 | 2022-08-15 | 93696 | keep | 0 | Aug | 2022 | 0.063816 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:40 | 1833 | 1:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500144 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 82 | 2022-08-15 | 150306 | keep | 0 | Aug | 2022 | 0.10237 | 0.0012484 | Sustained | FALSE | FALSE | Not_TMED_Event | 1833
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:40 | 1565 | 1:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500144 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 82 | 2022-08-15 | 128330 | keep | 0 | Aug | 2022 | 0.087405 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
GUAYAMA | 2022-08-15 20:18 | 2022-08-15 21:40 | 977 | 1:22 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | P22081500144 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 82 | 2022-08-15 | 80114 | keep | 0 | Aug | 2022 | 0.054565 | 0.00066543 | Sustained | FALSE | FALSE | Not_TMED_Event | 977
VEGA BAJA | 2022-08-15 20:18 | 2022-08-15 21:58 | 15 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | SE SUBIO PRIMARIA Y SE CERRO C/L | B22081500227 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 100 | 2022-08-15 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-15 20:48 | 2022-08-15 21:17 | 560 | 0:29 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M22081500430 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 29 | 2022-08-15 | 16240 | keep | 0 | Aug | 2022 | 0.011061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-15 20:58 | 2022-08-16 06:01 | 35 | 9:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU | B22081500358 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 543 | 2022-08-15 | 19005 | keep | 0 | Aug | 2022 | 0.012944 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2022-08-15 21:01 | 2022-08-16 00:26 | 150 | 3:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | M22081500550 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2022-08-15 | 30750 | keep | 0 | Aug | 2022 | 0.020944 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-08-15 21:17 | 2022-08-16 10:29 | 31 | 13:12 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | C22081500257 | New_Event | Primary Wire Break | Include | Include | Equipment | 792 | 2022-08-15 | 24552 | keep | 0 | Aug | 2022 | 0.016722 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2022-08-15 21:18 | 2022-08-16 14:56 | 20 | 17:38 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO PM-30 A PM 36 | M22081500570 | New_Event | UG Cable Fault | Include | Include | Equipment | 1058 | 2022-08-15 | 21160 | keep | 0 | Aug | 2022 | 0.014412 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-15 21:18 | 2022-08-16 15:18 | 5 | 18:00 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22081500571 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1080 | 2022-08-15 | 5400 | keep | 0 | Aug | 2022 | 0.0036779 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-08-15 21:28 | 2022-08-16 02:25 | 90 | 4:57 | P | DESGANCHE | 1 X 80 C/L DESGANCHE | P22081500168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-08-15 | 26730 | keep | 0 | Aug | 2022 | 0.018206 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-08-15 21:29 | 2022-08-15 23:09 | 65 | 1:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L INSTALO AISLADOR | R22081500173 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 100 | 2022-08-15 | 6500 | keep | 0 | Aug | 2022 | 0.0044271 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BARRANQUITAS | 2022-08-15 21:39 | 2022-08-16 07:30 | 80 | 9:51 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L | C22081500261 | New_Event | Primary Wire Break | Include | Include | Equipment | 591 | 2022-08-15 | 47280 | keep | 0 | Aug | 2022 | 0.032202 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-15 21:40 | 2022-08-15 21:41 | 637 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 6703-03 | M22081500584 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 637 | keep | 0 | Aug | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-08-15 21:40 | 2022-08-15 21:41 | 1491 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 6703-02 | M22081500584 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 1491 | keep | 0 | Aug | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-08-15 21:43 | 2022-08-16 01:12 | 140 | 3:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER MAL TIEMPO LLUVIA Y VENTOLERA | M22081500586 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 209 | 2022-08-15 | 29260 | keep | 0 | Aug | 2022 | 0.019929 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2022-08-15 21:44 | 2022-08-16 07:39 | 135 | 9:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S22081500319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 595 | 2022-08-15 | 80325 | keep | 0 | Aug | 2022 | 0.054709 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
BARRANQUITAS | 2022-08-15 22:00 | 2022-08-15 22:01 | 3565 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-15 | 3565 | keep | 0 | Aug | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
MAYAGÃœEZ | 2022-08-15 22:32 | 2022-08-16 14:17 | 15 | 15:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFOMADOR 25KVA A 4.16KV | M22081500597 | New_Event | Service Transformer Failure | Include | Include | Equipment | 945 | 2022-08-15 | 14175 | keep | 0 | Aug | 2022 | 0.0096545 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-15 22:59 | 2022-08-16 12:40 | 5 | 13:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | R22081500182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 821 | 2022-08-15 | 4105 | keep | 0 | Aug | 2022 | 0.0027959 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-16 00:04 | 2022-08-16 09:07 | 100 | 9:03 | P | DESGANCHE | 1 X 80 EN C/L SE REMPLAZO CAJA PIMARIA Y SE REALIZO DESGANCHE EN 3 PUNTOS | B22081600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 543 | 2022-08-16 | 54300 | keep | 0 | Aug | 2022 | 0.036983 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-16 00:37 | 2022-08-16 03:27 | 900 | 2:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 2 X 80 Y 1 X 100 EN CORTES DE LINEA | B22081600013 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2022-08-16 | 153000 | keep | 0 | Aug | 2022 | 0.10421 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
FAJARDO | 2022-08-16 00:51 | 2022-08-16 08:22 | 178 | 7:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R22081600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 451 | 2022-08-16 | 80278 | keep | 0 | Aug | 2022 | 0.054677 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
ARECIBO | 2022-08-16 00:53 | 2022-08-16 09:10 | 20 | 8:17 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600002 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 497 | 2022-08-16 | 9940 | keep | 0 | Aug | 2022 | 0.0067701 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-08-16 00:59 | 2022-08-16 01:00 | 1530 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 1530 | keep | 0 | Aug | 2022 | 0.0010421 | 0.0010421 | Momentary | FALSE | FALSE | Not_TMED_Event | 1530
HUMACAO | 2022-08-16 00:59 | 2022-08-16 01:00 | 1593 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 1593 | keep | 0 | Aug | 2022 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
BAYAMON | 2022-08-16 01:26 | 2022-08-16 07:39 | 40 | 6:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22081600023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 373 | 2022-08-16 | 14920 | keep | 0 | Aug | 2022 | 0.010162 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-16 01:43 | 2022-08-16 01:44 | 2565 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C22081600007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-08-16 | 2565 | keep | 0 | Aug | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-08-16 01:44 | 2022-08-16 04:43 | 2 | 2:59 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO AVERIADO | C22081600067 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 179 | 2022-08-16 | 358 | keep | 0 | Aug | 2022 | 0.00024383 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-16 03:49 | 2022-08-16 15:12 | 7 | 11:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA X 50KVA | A22081600138 | New_Event | Service Transformer Failure | Include | Include | Equipment | 683 | 2022-08-16 | 4781 | keep | 0 | Aug | 2022 | 0.0032563 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-16 03:52 | 2022-08-16 07:39 | 80 | 3:47 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L SE REMPLAZO PARARRAYO | B22081600025 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 227 | 2022-08-16 | 18160 | keep | 0 | Aug | 2022 | 0.012369 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-16 04:08 | 2022-08-16 07:39 | 50 | 3:31 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN C/L DESGANCHE PRIMARIO | B22081600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-08-16 | 10550 | keep | 0 | Aug | 2022 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-16 04:17 | 2022-08-16 07:25 | 1 | 3:08 | P | MAL TIEMPO/RAYOS | 1 X 10 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22081600047 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 188 | 2022-08-16 | 188 | keep | 0 | Aug | 2022 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-08-16 04:40 | 2022-08-16 04:41 | 1394 | 0:01 | T | DESGANCHE | RECIERRE | R22081600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-16 | 1394 | keep | 0 | Aug | 2022 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2022-08-16 04:41 | 2022-08-16 08:40 | 89 | 3:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22081600007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-08-16 | 21271 | keep | 0 | Aug | 2022 | 0.014488 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BARRANQUITAS | 2022-08-16 04:43 | 2022-08-16 04:44 | 2565 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C22081600007 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-08-16 | 2565 | keep | 0 | Aug | 2022 | 0.001747 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-16 04:43 | 2022-08-16 08:41 | 15 | 3:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22081600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2022-08-16 | 3570 | keep | 0 | Aug | 2022 | 0.0024315 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-16 04:44 | 2022-08-16 11:32 | 2 | 6:48 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO AVERIADO | C22081600067 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 408 | 2022-08-16 | 816 | keep | 0 | Aug | 2022 | 0.00055577 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-16 05:01 | 2022-08-16 05:02 | 723 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA EL 1711-05 | B22081600239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 723 | keep | 0 | Aug | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-16 05:01 | 2022-08-16 05:02 | 1976 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1700-02 | B22081600239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 1976 | keep | 0 | Aug | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CANOVANAS | 2022-08-16 05:54 | 2022-08-16 10:39 | 125 | 4:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R22081600011 | New_Event | Cutout Failure | Include | Include | Equipment | 285 | 2022-08-16 | 35625 | keep | 0 | Aug | 2022 | 0.024264 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BARRANQUITAS | 2022-08-16 06:03 | 2022-08-16 06:04 | 3565 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C22081600019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-08-16 | 3565 | keep | 0 | Aug | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BARRANQUITAS | 2022-08-16 06:04 | 2022-08-16 10:18 | 4 | 4:14 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO AVERIADO | C22081600040 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 254 | 2022-08-16 | 1016 | keep | 0 | Aug | 2022 | 0.00069199 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-16 06:08 | 2022-08-16 06:09 | 2533 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO PARCIAL PARTE POR 1801-02 | B22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 2533 | keep | 0 | Aug | 2022 | 0.0017252 | 0.0017252 | Momentary | FALSE | FALSE | Not_TMED_Event | 2533
MAYAGÃœEZ | 2022-08-16 06:10 | 2022-08-16 14:53 | 100 | 8:43 | P | MAL TIEMPO/RAYOS | 1 X 100 C/L MAL TIEMPO | M22081600006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 523 | 2022-08-16 | 52300 | keep | 0 | Aug | 2022 | 0.035621 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-16 06:27 | 2022-08-16 13:30 | 105 | 7:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2022-08-16 | 44415 | keep | 0 | Aug | 2022 | 0.030251 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2022-08-16 06:31 | 2022-08-16 06:33 | 21 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON EL 2% DE LA CARGA POR EL 1652-04 | S22081600013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-16 | 42 | keep | 0 | Aug | 2022 | 2.8606e-05 | 1.4303e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2022-08-16 06:31 | 2022-08-16 06:33 | 148 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON EL 60% DE LA CARGA POR EL 1652-05 | S22081600013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-16 | 296 | keep | 0 | Aug | 2022 | 0.0002016 | 0.0001008 | Momentary | FALSE | FALSE | Not_TMED_Event | 148
CANOVANAS | 2022-08-16 06:31 | 2022-08-16 06:33 | 614 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON | S22081600013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-16 | 1228 | keep | 0 | Aug | 2022 | 0.00083639 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
SAN JUAN | 2022-08-16 06:31 | 2022-08-16 06:33 | 770 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1000 DE SABANA LLANA A SAN ANTON | S22081600013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-16 | 1540 | keep | 0 | Aug | 2022 | 0.0010489 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2022-08-16 06:31 | 2022-08-16 06:33 | 1271 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 1000 DE SABANA LLANA A SAN ANTON LLEVA EL 2% DEL 1301-01 | S22081600013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-16 | 2542 | keep | 0 | Aug | 2022 | 0.0017313 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CANOVANAS | 2022-08-16 06:31 | 2022-08-16 06:33 | 247 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 1000 DE SABANA LLANA A SAN ANTON LLEVA EL 60% DEL 1301-04 | S22081600013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-16 | 494 | keep | 0 | Aug | 2022 | 0.00033646 | 0.00016823 | Momentary | FALSE | FALSE | Not_TMED_Event | 247
VEGA BAJA | 2022-08-16 06:32 | 2022-08-16 14:40 | 2 | 8:08 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22081600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2022-08-16 | 976 | keep | 0 | Aug | 2022 | 0.00066475 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-16 06:34 | 2022-08-16 10:20 | 2 | 3:46 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081600009 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 226 | 2022-08-16 | 452 | keep | 0 | Aug | 2022 | 0.00030786 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-16 06:37 | 2022-08-16 20:48 | 10 | 14:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 37.5KVA | A22081600259 | New_Event | Service Transformer Failure | Include | Include | Equipment | 851 | 2022-08-16 | 8510 | keep | 0 | Aug | 2022 | 0.0057961 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-16 06:44 | 2022-08-16 13:07 | 60 | 6:23 | P | CRUCETA DEFECTUOSA O AVERIADA | 2 X 50 EN CORTE DE LINEA SE REPARO CRUCETA | A22081600011 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 383 | 2022-08-16 | 22980 | keep | 0 | Aug | 2022 | 0.015652 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-08-16 06:50 | 2022-08-16 09:48 | 50 | 2:58 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22081600028 | New_Event | Animals | Include | Include | Wildlife | 178 | 2022-08-16 | 8900 | keep | 0 | Aug | 2022 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-16 07:08 | 2022-08-16 07:10 | 513 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% POR 1118-10 | S22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-16 | 1026 | keep | 0 | Aug | 2022 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-08-16 07:08 | 2022-08-16 07:10 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% DEL 1111-01 | S22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-16 | 5564 | keep | 0 | Aug | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
GUAYAMA | 2022-08-16 07:15 | 2022-08-16 10:45 | 50 | 3:30 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA POR PARARRAYOS QUEMADO Y SE REMPLAZO | P22081600018 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 210 | 2022-08-16 | 10500 | keep | 0 | Aug | 2022 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-16 07:18 | 2022-08-16 09:15 | 8 | 1:57 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-08-16 | 936 | keep | 0 | Aug | 2022 | 0.00063751 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-16 07:19 | 2022-08-16 12:50 | 40 | 5:31 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22081600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-08-16 | 13240 | keep | 0 | Aug | 2022 | 0.0090177 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-16 07:25 | 2022-08-16 07:26 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | M22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 4641 | keep | 0 | Aug | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-08-16 07:26 | 2022-08-16 09:41 | 1 | 2:15 | P | MAL TIEMPO/RAYOS | 1 X 10 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22081600047 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 135 | 2022-08-16 | 135 | keep | 0 | Aug | 2022 | 9.1948e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-16 07:30 | 2022-08-16 10:25 | 30 | 2:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO AVERIDO | C22081500261 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 175 | 2022-08-16 | 5250 | keep | 0 | Aug | 2022 | 0.0035758 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-16 07:31 | 2022-08-16 09:05 | 200 | 1:34 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | M22081600263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-08-16 | 18800 | keep | 0 | Aug | 2022 | 0.012805 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-16 07:36 | 2022-08-16 07:37 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22081600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 4085 | keep | 0 | Aug | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2022-08-16 07:37 | 2022-08-16 12:00 | 12 | 4:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO CAUSA | S22081600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2022-08-16 | 3156 | keep | 0 | Aug | 2022 | 0.0021495 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-08-16 07:40 | 2022-08-16 12:24 | 50 | 4:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | C22081600036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 284 | 2022-08-16 | 14200 | keep | 0 | Aug | 2022 | 0.0096716 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-16 07:44 | 2022-08-16 09:28 | 10 | 1:44 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA | R22081600023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2022-08-16 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-16 07:44 | 2022-08-16 08:34 | 12 | 0:50 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | C22081600022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2022-08-16 | 600 | keep | 0 | Aug | 2022 | 0.00040866 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-16 07:46 | 2022-08-16 07:47 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
SAN JUAN | 2022-08-16 07:48 | 2022-08-16 11:31 | 135 | 3:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S22081500319 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-08-16 | 30105 | keep | 0 | Aug | 2022 | 0.020504 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-16 07:49 | 2022-08-16 18:15 | 8 | 10:26 | P | DESGANCHE | 3 X 80 EN C/L SE REALIZO DESGANCHE | R22081500104 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 626 | 2022-08-16 | 5008 | keep | 0 | Aug | 2022 | 0.0034109 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 07:49 | 2022-08-16 11:38 | 5 | 3:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA PRIMARIA | B22081500179 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 229 | 2022-08-16 | 1145 | keep | 0 | Aug | 2022 | 0.00077985 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 07:49 | 2022-08-16 14:42 | 40 | 6:53 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22081600023 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 413 | 2022-08-16 | 16520 | keep | 0 | Aug | 2022 | 0.011252 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 07:49 | 2022-08-16 10:30 | 50 | 2:41 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN C/L DESGANCHE PRIMARIO | B22081600026 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-08-16 | 8050 | keep | 0 | Aug | 2022 | 0.0054828 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 07:49 | 2022-08-16 14:51 | 80 | 7:02 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L SE REMPLAZO PARARRAYO | B22081600025 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 422 | 2022-08-16 | 33760 | keep | 0 | Aug | 2022 | 0.022994 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 08:07 | 2022-08-16 15:13 | 8 | 7:06 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22081600067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 426 | 2022-08-16 | 3408 | keep | 0 | Aug | 2022 | 0.0023212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-16 08:19 | 2022-08-16 09:03 | 2009 | 0:44 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZANDO CONDUCTOR PRIMARIO PARTIDO. 30% EN SERVICIO | B22081500312 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 44 | 2022-08-16 | 88396 | keep | 0 | Aug | 2022 | 0.060206 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-16 08:34 | 2022-08-16 13:21 | 10 | 4:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081600039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-08-16 | 2870 | keep | 0 | Aug | 2022 | 0.0019547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-16 08:49 | 2022-08-16 11:12 | 1 | 2:23 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22081600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-08-16 | 143 | keep | 0 | Aug | 2022 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-16 09:03 | 2022-08-16 18:42 | 1875 | 9:39 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRO MACHETES 100% EN SERVICIO | B22081500312 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 579 | 2022-08-16 | 1085625 | keep | 0 | Aug | 2022 | 0.73941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-16 09:08 | 2022-08-16 10:28 | 770 | 1:20 | T | LINEA DE TRANSMISION 38KV | SE ABRE INTERRUPTOR PARA LEVANTAR OVERHEAD DE LINEA 1000 SOBRE 1652-03 | S22081600046 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-08-16 | 61600 | keep | 0 | Aug | 2022 | 0.041955 | 0.00052444 | Sustained | FALSE | FALSE | Not_TMED_Event | 770
CANOVANAS | 2022-08-16 09:13 | 2022-08-16 15:02 | 60 | 5:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO Y LINEA SECUNDARIA | R22081500057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 349 | 2022-08-16 | 20940 | keep | 0 | Aug | 2022 | 0.014262 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-16 09:13 | 2022-08-16 12:44 | 20 | 3:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081600046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-08-16 | 4220 | keep | 0 | Aug | 2022 | 0.0028742 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-08-16 09:26 | 2022-08-16 10:20 | 4 | 0:54 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600049 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 54 | 2022-08-16 | 216 | keep | 0 | Aug | 2022 | 0.00014712 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-08-16 09:40 | 2022-08-16 14:15 | 36 | 4:35 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L SE SUBIO CONDUCTOR ZAFADO DE ASILADOR | C22081600056 | New_Event | Primary Wire Break | Include | Include | Equipment | 275 | 2022-08-16 | 9900 | keep | 0 | Aug | 2022 | 0.0067428 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
ARECIBO | 2022-08-16 09:51 | 2022-08-16 13:25 | 6 | 3:34 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600053 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 214 | 2022-08-16 | 1284 | keep | 0 | Aug | 2022 | 0.00087453 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-08-16 09:55 | 2022-08-16 13:19 | 1 | 3:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22081600065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 204 | 2022-08-16 | 204 | keep | 0 | Aug | 2022 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-16 10:08 | 2022-08-16 15:03 | 4 | 4:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR BAJANTE SECUNDARIO | C22081600069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 295 | 2022-08-16 | 1180 | keep | 0 | Aug | 2022 | 0.00080369 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-08-16 10:12 | 2022-08-16 14:26 | 500 | 4:14 | P | DESGANCHE | 1 X 140 EN C/L SE RETIRO PALMA | B22081600118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-08-16 | 127000 | keep | 0 | Aug | 2022 | 0.086499 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
GUAYAMA | 2022-08-16 10:26 | 2022-08-16 16:49 | 25 | 6:23 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO | P22081600030 | New_Event | Primary Pole Failure | Include | Include | Equipment | 383 | 2022-08-16 | 9575 | keep | 0 | Aug | 2022 | 0.0065215 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-08-16 10:29 | 2022-08-16 17:46 | 60 | 7:17 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600063 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 437 | 2022-08-16 | 26220 | keep | 0 | Aug | 2022 | 0.017858 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-16 10:32 | 2022-08-16 19:28 | 120 | 8:56 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHO | R22081600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2022-08-16 | 64320 | keep | 0 | Aug | 2022 | 0.043808 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-08-16 10:32 | 2022-08-16 11:56 | 2 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | M22081600071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-08-16 | 168 | keep | 0 | Aug | 2022 | 0.00011442 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-08-16 10:32 | 2022-08-16 12:30 | 30 | 1:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600064 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 118 | 2022-08-16 | 3540 | keep | 0 | Aug | 2022 | 0.0024111 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-16 10:33 | 2022-08-16 16:59 | 10 | 6:26 | P | MAL TIEMPO/RAYOS | 1 X 30 C/L DESCARGAS ELECTRICAS | M22081600073 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 386 | 2022-08-16 | 3860 | keep | 0 | Aug | 2022 | 0.002629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-16 10:50 | 2022-08-16 11:35 | 1 | 0:45 | P | OTRAS CAUSAS | SE ABRIO RISER PARA QUE PERSONAL DE MEDICIONES REALIZARA PRUEBAS | A22081600070 | New_Event | Other Causes | Include | Include | Other | 45 | 2022-08-16 | 45 | keep | 0 | Aug | 2022 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-16 11:00 | 2022-08-16 16:00 | 7 | 5:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA RELOCALIZAR TRANSFORMADOR DE POSTE AVERIADO A POSTE NUEVO | A22081600055 | New_Event | Primary Pole Failure | Include | Include | Equipment | 300 | 2022-08-16 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-16 11:30 | 2022-08-16 13:00 | 25 | 1:30 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PARTIDO | M22081600078 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 90 | 2022-08-16 | 2250 | keep | 0 | Aug | 2022 | 0.0015325 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-16 11:33 | 2022-08-16 11:58 | 10 | 0:25 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | B22081500385 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 25 | 2022-08-16 | 250 | keep | 0 | Aug | 2022 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-16 11:40 | 2022-08-16 16:06 | 7 | 4:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA X 25KVA | C22081600082 | New_Event | Service Transformer Failure | Include | Include | Equipment | 266 | 2022-08-16 | 1862 | keep | 0 | Aug | 2022 | 0.0012682 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2022-08-16 11:41 | 2022-08-16 16:24 | 15 | 4:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22081600081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 283 | 2022-08-16 | 4245 | keep | 0 | Aug | 2022 | 0.0028913 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-16 11:42 | 2022-08-16 17:24 | 80 | 5:42 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO | R22081600050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2022-08-16 | 27360 | keep | 0 | Aug | 2022 | 0.018635 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-16 11:43 | 2022-08-16 14:45 | 7 | 3:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y REMPLAZO BARRA SECUNDARIA EN PM | R22081600051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 182 | 2022-08-16 | 1274 | keep | 0 | Aug | 2022 | 0.00086772 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-08-16 11:48 | 2022-08-16 13:07 | 1 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C22081600070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2022-08-16 | 79 | keep | 0 | Aug | 2022 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-16 11:50 | 2022-08-16 12:20 | 1 | 0:30 | P | OTRAS CAUSAS | SE ABRIO RISER PARA QUE PERSONAL DE MEDICIONES REALIZARA PRUEBAS | A22081600093 | New_Event | Other Causes | Include | Include | Other | 30 | 2022-08-16 | 30 | keep | 0 | Aug | 2022 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-16 11:52 | 2022-08-16 14:27 | 1 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | C22081600084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2022-08-16 | 155 | keep | 0 | Aug | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-16 12:03 | 2022-08-16 18:12 | 1479 | 6:09 | T | MAL TIEMPO/RAYOS | SE REPARO LINEAS PRIMARIAS ROTAS EN TRONCAL DEL ALIMENTADOR RAYO EN POSTE SE ESPERILLO POSTE SE FUE AL PISO | A22081600194 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 369 | 2022-08-16 | 545751 | keep | 0 | Aug | 2022 | 0.37171 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
BARRANQUITAS | 2022-08-16 12:06 | 2022-08-16 18:29 | 14 | 6:23 | P | PARARRAYOS DEFECTUOSO | REEMPLAZO DE PARARRAYO AVERIADO | C22081600086 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 383 | 2022-08-16 | 5362 | keep | 0 | Aug | 2022 | 0.003652 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-08-16 12:07 | 2022-08-16 15:10 | 30 | 3:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081600098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-08-16 | 5490 | keep | 0 | Aug | 2022 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-08-16 12:19 | 2022-08-16 15:20 | 30 | 3:01 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A22081600100 | New_Event | Animals | Include | Include | Wildlife | 181 | 2022-08-16 | 5430 | keep | 0 | Aug | 2022 | 0.0036983 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-16 12:27 | 2022-08-16 12:28 | 2179 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22081600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 2179 | keep | 0 | Aug | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
BAYAMON | 2022-08-16 12:27 | 2022-08-16 12:28 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081600159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 3871 | keep | 0 | Aug | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
FAJARDO | 2022-08-16 12:28 | 2022-08-16 13:13 | 474 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA TOTAL PARA LEVANTAR CONDUCTOR PRIMARIO | R22081600058 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2022-08-16 | 21330 | keep | 0 | Aug | 2022 | 0.014528 | 0.00032284 | Sustained | FALSE | FALSE | Not_TMED_Event | 474
MAYAGÃœEZ | 2022-08-16 12:32 | 2022-08-16 16:25 | 5 | 3:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARA LINEA SECUNDARIA | M22081600089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 233 | 2022-08-16 | 1165 | keep | 0 | Aug | 2022 | 0.00079348 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-16 12:34 | 2022-08-16 14:30 | 60 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22081600160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-08-16 | 6960 | keep | 0 | Aug | 2022 | 0.0047404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-16 12:34 | 2022-08-16 12:35 | 2770 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | C22081600090 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-08-16 | 2770 | keep | 0 | Aug | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
BARRANQUITAS | 2022-08-16 12:35 | 2022-08-16 18:40 | 30 | 6:05 | P | ARBOL SOBRE LINEA | 1 X 30, 1 X 40, 1 X 50 EN C/L ARBOL SOBRE LINEA | C22081600103 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 365 | 2022-08-16 | 10950 | keep | 0 | Aug | 2022 | 0.007458 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-16 12:37 | 2022-08-16 15:43 | 80 | 3:06 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | B22081600161 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 186 | 2022-08-16 | 14880 | keep | 0 | Aug | 2022 | 0.010135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-08-16 12:37 | 2022-08-16 13:27 | 100 | 0:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | C22081600091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 50 | 2022-08-16 | 5000 | keep | 0 | Aug | 2022 | 0.0034055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-16 13:00 | 2022-08-16 13:03 | 5809 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1710-02 LLEVANDO CARGA 1710-01 | B22081600167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-08-16 | 17427 | keep | 0 | Aug | 2022 | 0.011869 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 959 | keep | 0 | Aug | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 663 | keep | 0 | Aug | 2022 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 1000 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 PARTE DE SU CARGA POR 1707-01 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1000 | keep | 0 | Aug | 2022 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 1498 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 1221 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1221 | keep | 0 | Aug | 2022 | 0.00083162 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 1100 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1100 | keep | 0 | Aug | 2022 | 0.0007492 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1514 | keep | 0 | Aug | 2022 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-08-16 13:01 | 2022-08-16 13:02 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22081600169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1105 | keep | 0 | Aug | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-08-16 13:03 | 2022-08-16 21:03 | 10 | 8:00 | P | DESGANCHE | 2 X 15 EN XMR DESGANCHE | B22081600268 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 480 | 2022-08-16 | 4800 | keep | 0 | Aug | 2022 | 0.0032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-16 13:04 | 2022-08-16 13:08 | 3295 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B22081600171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-16 | 13180 | keep | 0 | Aug | 2022 | 0.0089768 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-08-16 13:05 | 2022-08-16 13:06 | 222 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22081600558 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-16 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-16 13:05 | 2022-08-16 13:06 | 4456 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22081600558 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-16 | 4456 | keep | 0 | Aug | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
SAN JUAN | 2022-08-16 13:06 | 2022-08-16 13:11 | 1681 | 0:05 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO LLEVA 1346-06 MAL TIEMPO LLUVIA | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-08-16 | 8405 | keep | 0 | Aug | 2022 | 0.0057246 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-08-16 13:06 | 2022-08-16 13:11 | 1598 | 0:05 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO SU CARGA POR 1303-04 | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-08-16 | 7990 | keep | 0 | Aug | 2022 | 0.005442 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-08-16 13:08 | 2022-08-16 13:11 | 842 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600174 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-08-16 | 2526 | keep | 0 | Aug | 2022 | 0.0017204 | 0.00057348 | Momentary | FALSE | FALSE | Not_TMED_Event | 842
BAYAMON | 2022-08-16 13:08 | 2022-08-16 13:09 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081600175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 2402 | keep | 0 | Aug | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
MAYAGÃœEZ | 2022-08-16 13:09 | 2022-08-16 16:30 | 20 | 3:21 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE CERRO PUENTE PRIMARIO | M22081600095 | New_Event | Primary Wire Break | Include | Include | Equipment | 201 | 2022-08-16 | 4020 | keep | 0 | Aug | 2022 | 0.002738 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-16 13:11 | 2022-08-16 13:12 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081600176 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 2402 | keep | 0 | Aug | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-08-16 13:11 | 2022-08-16 13:16 | 651 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22081600176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-16 | 3255 | keep | 0 | Aug | 2022 | 0.002217 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2022-08-16 13:11 | 2022-08-16 13:14 | 2617 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | B22081600177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-16 | 7851 | keep | 0 | Aug | 2022 | 0.0053473 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
GUAYAMA | 2022-08-16 13:11 | 2022-08-16 20:17 | 1 | 7:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22081600039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 426 | 2022-08-16 | 426 | keep | 0 | Aug | 2022 | 0.00029015 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-16 13:11 | 2022-08-16 14:01 | 40 | 0:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L Y 1 X 15 EN XMR MAL VIENTO LLUVIAS | C22081600097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 50 | 2022-08-16 | 2000 | keep | 0 | Aug | 2022 | 0.0013622 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-16 13:12 | 2022-08-16 13:48 | 1681 | 0:36 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1346-06 MAL TIEMPO LLUVIA | S22081600000 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 36 | 2022-08-16 | 60516 | keep | 0 | Aug | 2022 | 0.041217 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-16 13:12 | 2022-08-16 13:48 | 1598 | 0:36 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-04 MAL TIEMPO LLUVIA | S22081600000 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 36 | 2022-08-16 | 57528 | keep | 0 | Aug | 2022 | 0.039182 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-16 13:13 | 2022-08-16 13:47 | 1106 | 0:34 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICO MAL TIEMPO 60% POR 1529-15 | S22081600193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 34 | 2022-08-16 | 37604 | keep | 0 | Aug | 2022 | 0.025612 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-08-16 13:13 | 2022-08-16 13:47 | 1802 | 0:34 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICO MAL TIEMPO LLEVA 60% DEL 1346-02 | S22081600193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 34 | 2022-08-16 | 61268 | keep | 0 | Aug | 2022 | 0.041729 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2022-08-16 13:14 | 2022-08-16 15:34 | 300 | 2:20 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C22081600100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-08-16 | 42000 | keep | 0 | Aug | 2022 | 0.028606 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-16 13:17 | 2022-08-16 13:23 | 1 | 0:06 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 MAL TIEMPO AFECTA PORTATIL #19 | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-16 | 6 | keep | 0 | Aug | 2022 | 4.0866e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-16 13:17 | 2022-08-16 13:23 | 738 | 0:06 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 MAL TIEMPO AFECTA PORTATIL #19 LLEVA 40% DE SU CARGA | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-16 | 4428 | keep | 0 | Aug | 2022 | 0.0030159 | 0.00050265 | Sustained | FALSE | FALSE | Not_TMED_Event | 738
SAN JUAN | 2022-08-16 13:17 | 2022-08-16 13:23 | 2422 | 0:06 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 MAL TIEMPO AFECTA PORTATIL #19 | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-16 | 14532 | keep | 0 | Aug | 2022 | 0.0098977 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
GUAYAMA | 2022-08-16 13:18 | 2022-08-16 16:27 | 1 | 3:09 | P | SECUNDARIA/OTROS | SE RETIRO CONTADOR EN FUEGO | P22081600040 | New_Event |  |  |  |  | 189 | 2022-08-16 | 189 | keep | 0 | Aug | 2022 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-16 13:18 | 2022-08-16 13:19 | 974 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2000 | M22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 974 | keep | 0 | Aug | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
SAN JUAN | 2022-08-16 13:20 | 2022-08-16 13:47 | 199 | 0:27 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO LLEVA 25% DEL 1911-7 | S22081600193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 27 | 2022-08-16 | 5373 | keep | 0 | Aug | 2022 | 0.0036595 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-08-16 13:20 | 2022-08-16 13:47 | 144 | 0:27 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO 25% POR 1529-13 | S22081600193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 27 | 2022-08-16 | 3888 | keep | 0 | Aug | 2022 | 0.0026481 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2022-08-16 13:21 | 2022-08-16 13:47 | 726 | 0:26 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 1346-04 MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 26 | 2022-08-16 | 18876 | keep | 0 | Aug | 2022 | 0.012856 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-08-16 13:21 | 2022-08-16 13:47 | 726 | 0:26 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SU CARGA POR 1303-03 MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 26 | 2022-08-16 | 18876 | keep | 0 | Aug | 2022 | 0.012856 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-08-16 13:21 | 2022-08-16 14:58 | 514 | 1:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6800 MAL TIEMPO | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2022-08-16 | 49858 | keep | 0 | Aug | 2022 | 0.033958 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-08-16 13:21 | 2022-08-16 14:58 | 681 | 1:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6800 MAL TIEMPO LLEVA 1530-09 | S22081600497 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2022-08-16 | 66057 | keep | 0 | Aug | 2022 | 0.044991 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-08-16 13:21 | 2022-08-16 14:58 | 752 | 1:37 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6800 MAL TIEMPO | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2022-08-16 | 72944 | keep | 0 | Aug | 2022 | 0.049682 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2022-08-16 13:21 | 2022-08-16 14:58 | 68 | 1:37 | S | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LINEA 6800 MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2022-08-16 | 6596 | keep | 0 | Aug | 2022 | 0.0044925 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-08-16 13:21 | 2022-08-16 14:58 | 1310 | 1:37 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6800 MAL TIEMPO SU CARGA POR 1520-02 | S22081600497 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 97 | 2022-08-16 | 127070 | keep | 0 | Aug | 2022 | 0.086547 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-08-16 13:22 | 2022-08-16 13:51 | 36 | 0:29 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1620-03 MAL TIEMPO LLUVIA | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 29 | 2022-08-16 | 1044 | keep | 0 | Aug | 2022 | 0.00071106 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-08-16 13:22 | 2022-08-16 13:51 | 1073 | 0:29 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1620-01 MAL TIEMPO LLUVIA | S22081600197 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 29 | 2022-08-16 | 31117 | keep | 0 | Aug | 2022 | 0.021194 | 0.00073082 | Sustained | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2022-08-16 13:23 | 2022-08-16 13:24 | 828 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | DRECERRO 60% POR 1206-04 MAL TIEMPO LLUVIA | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-08-16 13:23 | 2022-08-16 13:24 | 1977 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 40% POR 1206-04 MAL TIEMPO LLUVIA | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 1977 | keep | 0 | Aug | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-16 13:23 | 2022-08-16 13:24 | 1799 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 40% 1204-04 MAL TIEMPO LLUVIA | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 1799 | keep | 0 | Aug | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-16 13:23 | 2022-08-16 13:24 | 487 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 20% POR 1206-04 MAL TIEMPO LLUVIA | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 487 | keep | 0 | Aug | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
CANOVANAS | 2022-08-16 13:24 | 2022-08-16 13:41 | 1615 | 0:17 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 20% 1206-03 MAL TIEMPO LLUVIA | S22081600206 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 17 | 2022-08-16 | 27455 | keep | 0 | Aug | 2022 | 0.018699 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2022-08-16 13:25 | 2022-08-16 13:26 | 4476 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 1336-10 MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 4476 | keep | 0 | Aug | 2022 | 0.0030486 | 0.0030486 | Momentary | FALSE | FALSE | Not_TMED_Event | 4476
SAN JUAN | 2022-08-16 13:25 | 2022-08-16 13:26 | 403 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO SU CARGA POR 1336-06 MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 403 | keep | 0 | Aug | 2022 | 0.00027448 | 0.00027448 | Momentary | FALSE | FALSE | Not_TMED_Event | 403
CANOVANAS | 2022-08-16 13:25 | 2022-08-16 13:26 | 437 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO SU CARGA POR 1336-06 | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 437 | keep | 0 | Aug | 2022 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2022-08-16 13:25 | 2022-08-16 13:26 | 2402 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | B22081600191 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 2402 | keep | 0 | Aug | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-08-16 13:26 | 2022-08-16 13:41 | 200 | 0:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | S22081600244 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 15 | 2022-08-16 | 3000 | keep | 0 | Aug | 2022 | 0.0020433 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-08-16 13:27 | 2022-08-16 13:28 | 8679 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO 85% POR 1206-3 MAL TIEMPO LLUVIA | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 8679 | keep | 0 | Aug | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-08-16 13:27 | 2022-08-16 13:28 | 3719 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 85% 1204-05 Y 10% DE 1206-3 POR 1620-02 MAL TIEMPO LLUVIA | S22081600206 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 3719 | keep | 0 | Aug | 2022 | 0.002533 | 0.002533 | Momentary | FALSE | FALSE | Not_TMED_Event | 3719
SAN JUAN | 2022-08-16 13:27 | 2022-08-16 13:48 | 225 | 0:21 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SU CARGA POR 1303-05 MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 21 | 2022-08-16 | 4725 | keep | 0 | Aug | 2022 | 0.0032182 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-16 13:27 | 2022-08-16 13:48 | 870 | 0:21 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 1303-4 MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 21 | 2022-08-16 | 18270 | keep | 0 | Aug | 2022 | 0.012444 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-08-16 13:27 | 2022-08-16 13:28 | 602 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 1418-04 | S22081600213 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 602 | keep | 0 | Aug | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-08-16 13:27 | 2022-08-16 13:28 | 43 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO SU CARGA POR 1418-03 | S22081600213 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 43 | keep | 0 | Aug | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2022-08-16 13:28 | 2022-08-16 13:29 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 1026 | keep | 0 | Aug | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CAGUAS | 2022-08-16 13:28 | 2022-08-16 13:29 | 718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081600107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 718 | keep | 0 | Aug | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
SAN JUAN | 2022-08-16 13:30 | 2022-08-16 14:52 | 2203 | 1:22 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600229 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 82 | 2022-08-16 | 180646 | keep | 0 | Aug | 2022 | 0.12304 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
UTUADO | 2022-08-16 13:31 | 2022-08-16 13:45 | 1841 | 0:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22081600128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2022-08-16 | 25774 | keep | 0 | Aug | 2022 | 0.017555 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-08-16 13:31 | 2022-08-16 13:45 | 1950 | 0:14 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22081600128 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 14 | 2022-08-16 | 27300 | keep | 0 | Aug | 2022 | 0.018594 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
SAN JUAN | 2022-08-16 13:32 | 2022-08-16 13:33 | 828 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 60% POR 1206-04 MAL TIEMPO | S22081600000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-08-16 13:32 | 2022-08-16 13:33 | 1977 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 40% POR 1206-04 MAL TIEMPO | S22081600000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 1977 | keep | 0 | Aug | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-16 13:32 | 2022-08-16 13:33 | 1799 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 40% 1204-04 LLEVA 60% 1204-03 Y 20% 1303-02 MAL TIEMPO | S22081600000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 1799 | keep | 0 | Aug | 2022 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-16 13:32 | 2022-08-16 13:33 | 487 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 20% POR 1206-04 MAL TIEMPO | S22081600000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 487 | keep | 0 | Aug | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-08-16 13:32 | 2022-08-16 13:46 | 74 | 0:14 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SU CARGA POR 1529-11 MAL TIEMPO | S22081600239 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 14 | 2022-08-16 | 1036 | keep | 0 | Aug | 2022 | 0.00070561 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-08-16 13:32 | 2022-08-16 13:46 | 1370 | 0:14 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 1521-02 MAL TIEMPO | S22081600239 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 14 | 2022-08-16 | 19180 | keep | 0 | Aug | 2022 | 0.013063 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-08-16 13:33 | 2022-08-16 18:33 | 74 | 5:00 | P | MAL TIEMPO/RAYOS | 2 X 140 EN C/L MAL TIEMPO RAYOS | S22081600238 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 300 | 2022-08-16 | 22200 | keep | 0 | Aug | 2022 | 0.01512 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2022-08-16 13:33 | 2022-08-16 13:35 | 3295 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22081600196 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-16 | 6590 | keep | 0 | Aug | 2022 | 0.0044884 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
SAN JUAN | 2022-08-16 13:34 | 2022-08-16 13:57 | 948 | 0:23 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600249 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 23 | 2022-08-16 | 21804 | keep | 0 | Aug | 2022 | 0.014851 | 0.00064568 | Sustained | FALSE | FALSE | Not_TMED_Event | 948
SAN JUAN | 2022-08-16 13:34 | 2022-08-16 13:46 | 1984 | 0:12 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 75% DEL 1911-07 QUEDO EN SERVICIO MAL TIEMPO | S22081600250 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 12 | 2022-08-16 | 23808 | keep | 0 | Aug | 2022 | 0.016216 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
BAYAMON | 2022-08-16 13:34 | 2022-08-16 13:35 | 222 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | S22081600558 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-16 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-16 13:34 | 2022-08-16 13:35 | 4456 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | S22081600558 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-16 | 4456 | keep | 0 | Aug | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-08-16 13:34 | 2022-08-16 13:46 | 432 | 0:12 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO 75% POR 1529-12 | S22081600250 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 12 | 2022-08-16 | 5184 | keep | 0 | Aug | 2022 | 0.0035308 | 0.00029423 | Sustained | FALSE | FALSE | Not_TMED_Event | 432
SAN JUAN | 2022-08-16 13:35 | 2022-08-16 13:58 | 1860 | 0:23 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600259 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 23 | 2022-08-16 | 42780 | keep | 0 | Aug | 2022 | 0.029137 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
SAN JUAN | 2022-08-16 13:38 | 2022-08-17 10:39 | 50 | 21:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S22081600261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1261 | 2022-08-16 | 63050 | keep | 0 | Aug | 2022 | 0.042943 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-16 13:38 | 2022-08-16 13:48 | 1287 | 0:10 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTOR SE CERRO POR SCADA | M22081600102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-08-16 | 12870 | keep | 0 | Aug | 2022 | 0.0087657 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
VEGA BAJA | 2022-08-16 13:38 | 2022-08-16 13:39 | 2366 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081600129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-16 | 2366 | keep | 0 | Aug | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
SAN JUAN | 2022-08-16 13:40 | 2022-08-16 13:41 | 849 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7200 MAL TIEMPO LLEVA 1423-03 | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 849 | keep | 0 | Aug | 2022 | 0.00057825 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-08-16 13:40 | 2022-08-16 13:41 | 893 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7200 MAL TIEMPO | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 893 | keep | 0 | Aug | 2022 | 0.00060822 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-08-16 13:40 | 2022-08-16 13:41 | 602 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7200 MAL TIEMPO | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 602 | keep | 0 | Aug | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-08-16 13:40 | 2022-08-16 13:41 | 43 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7200 MAL TIEMPO | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 43 | keep | 0 | Aug | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-08-16 13:40 | 2022-08-16 13:41 | 1389 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7200 MAL TIEMPO | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1389 | keep | 0 | Aug | 2022 | 0.00094604 | 0.00094604 | Momentary | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-08-16 13:40 | 2022-08-16 13:41 | 600 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7200 MAL TIEMPO SU CARGA POR 1418-01 | S22081600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 600 | keep | 0 | Aug | 2022 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
AGUADILLA | 2022-08-16 13:40 | 2022-08-16 13:41 | 2825 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M22081600103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-16 | 2825 | keep | 0 | Aug | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
UTUADO | 2022-08-16 13:40 | 2022-08-16 13:41 | 1527 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | A22081600130 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-16 | 1527 | keep | 0 | Aug | 2022 | 0.00104 | 0.00104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1527
CANOVANAS | 2022-08-16 13:41 | 2022-08-16 15:17 | 2005 | 1:36 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL DE LAS LINEAS, CARGAS X 1619-03 | R22081600175 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 96 | 2022-08-16 | 192480 | keep | 0 | Aug | 2022 | 0.1311 | 0.0013656 | Sustained | FALSE | FALSE | Not_TMED_Event | 2005
CANOVANAS | 2022-08-16 13:41 | 2022-08-16 14:26 | 5062 | 0:45 | T | ARBOL SOBRE LINEA | SE SECCIONALIZO EL ALIMENTADOR Y SE ABRIO EL N/O CONTRA EL 1619-02 | R22081600071 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 45 | 2022-08-16 | 227790 | keep | 0 | Aug | 2022 | 0.15515 | 0.0034477 | Sustained | FALSE | FALSE | Not_TMED_Event | 5062
BAYAMON | 2022-08-16 13:41 | 2022-08-16 13:42 | 2402 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | B22081600207 | Additional_clients | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-16 | 2402 | keep | 0 | Aug | 2022 | 0.001636 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-16 13:41 | 2022-08-16 19:38 | 25 | 5:57 | P | DESGANCHE | 1 X 40 C/L DESGANCHE | M22081600106 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 357 | 2022-08-16 | 8925 | keep | 0 | Aug | 2022 | 0.0060788 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-08-16 13:41 | 2022-08-16 16:15 | 300 | 2:34 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | A22081600239 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 154 | 2022-08-16 | 46200 | keep | 0 | Aug | 2022 | 0.031467 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-16 13:42 | 2022-08-17 01:48 | 200 | 12:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | S22081600244 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 726 | 2022-08-16 | 145200 | keep | 0 | Aug | 2022 | 0.098895 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-08-16 13:43 | 2022-08-16 13:44 | 1986 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081600156 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-16 | 1986 | keep | 0 | Aug | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
SAN JUAN | 2022-08-16 13:44 | 2022-08-16 14:00 | 271 | 0:16 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600296 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 16 | 2022-08-16 | 4336 | keep | 0 | Aug | 2022 | 0.0029532 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2022-08-16 13:44 | 2022-08-16 16:05 | 2580 | 2:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R22081600078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-08-16 | 363780 | keep | 0 | Aug | 2022 | 0.24777 | 0.0017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2022-08-16 13:44 | 2022-08-16 16:05 | 500 | 2:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R22081600078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2022-08-16 | 70500 | keep | 0 | Aug | 2022 | 0.048017 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2022-08-16 13:45 | 2022-08-16 13:46 | 2276 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 2276 | keep | 0 | Aug | 2022 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-08-16 13:45 | 2022-08-16 13:46 | 777 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 777 | keep | 0 | Aug | 2022 | 0.00052921 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-08-16 13:45 | 2022-08-16 13:46 | 12 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 12 | keep | 0 | Aug | 2022 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-16 13:45 | 2022-08-16 13:46 | 1290 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 1290 | keep | 0 | Aug | 2022 | 0.00087861 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2022-08-16 13:48 | 2022-08-16 14:00 | 6244 | 0:12 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 12 | 2022-08-16 | 74928 | keep | 0 | Aug | 2022 | 0.051033 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
VEGA BAJA | 2022-08-16 13:48 | 2022-08-16 18:15 | 80 | 4:27 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081600133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 267 | 2022-08-16 | 21360 | keep | 0 | Aug | 2022 | 0.014548 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-16 13:49 | 2022-08-16 13:50 | 1026 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | R22081600076 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-08-16 | 1026 | keep | 0 | Aug | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CAGUAS | 2022-08-16 13:49 | 2022-08-16 14:58 | 2276 | 1:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600119 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2022-08-16 | 157044 | keep | 0 | Aug | 2022 | 0.10696 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-08-16 13:49 | 2022-08-16 14:58 | 777 | 1:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600119 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2022-08-16 | 53613 | keep | 0 | Aug | 2022 | 0.036516 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-08-16 13:49 | 2022-08-16 14:58 | 12 | 1:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600119 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2022-08-16 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-08-16 13:49 | 2022-08-16 14:58 | 1290 | 1:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22081600119 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2022-08-16 | 89010 | keep | 0 | Aug | 2022 | 0.060624 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2022-08-16 13:50 | 2022-08-16 14:35 | 1384 | 0:45 | S | MAL TIEMPO/LLUVIA O VIENTO | SUBEST. CON PROBLEMA DE INDICACIONES ERRONEAS SE RETIRO CARGA SE INSPECCIONO Y CERRO BKR. 1 A LAS 14:35 Y BKR. A2 A LAS 14:38 MAL TIEMPO LLUVIA NO SE ENCONTRO CAUSA | S22081600335 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 45 | 2022-08-16 | 62280 | keep | 0 | Aug | 2022 | 0.042419 | 0.00094264 | Sustained | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2022-08-16 13:50 | 2022-08-16 14:38 | 869 | 0:48 | S | MAL TIEMPO/LLUVIA O VIENTO | SUBEST. CON PROBLEMA DE INDICACIONES ERRONEAS SE RETIRO CARGA SE INSPECCIONO Y CERRO BKR. 1 A LAS 14:35 Y BKR. A2 A LAS 14:38 MAL TIEMPO LLUVIA NO SE ENCONTRO CAUSA | S22081600334 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 48 | 2022-08-16 | 41712 | keep | 0 | Aug | 2022 | 0.02841 | 0.00059187 | Sustained | FALSE | FALSE | Not_TMED_Event | 869
CANOVANAS | 2022-08-16 13:50 | 2022-08-16 16:41 | 416 | 2:51 | P | DESCONECTIVO DEFECTUOSO | REMPLAZO MACHETE QUEMADO | R22081600076 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 171 | 2022-08-16 | 71136 | keep | 0 | Aug | 2022 | 0.04845 | 0.00028334 | Sustained | FALSE | FALSE | Not_TMED_Event | 416
BAYAMON | 2022-08-16 13:51 | 2022-08-16 13:53 | 222 | 0:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | S22081600558 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-08-16 | 444 | keep | 0 | Aug | 2022 | 0.00030241 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-16 13:51 | 2022-08-16 13:53 | 4456 | 0:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO 1909-09 | S22081600558 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-08-16 | 8912 | keep | 0 | Aug | 2022 | 0.0060699 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-08-16 13:52 | 2022-08-16 14:02 | 723 | 0:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22081600239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-08-16 | 7230 | keep | 0 | Aug | 2022 | 0.0049243 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-16 13:52 | 2022-08-16 14:02 | 1976 | 0:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22081600239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-08-16 | 19760 | keep | 0 | Aug | 2022 | 0.013458 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2022-08-16 13:53 | 2022-08-16 20:04 | 20 | 6:11 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | C22081600120 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 371 | 2022-08-16 | 7420 | keep | 0 | Aug | 2022 | 0.0050537 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-16 13:54 | 2022-08-16 14:02 | 1825 | 0:08 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 8 | 2022-08-16 | 14600 | keep | 0 | Aug | 2022 | 0.009944 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-08-16 13:54 | 2022-08-16 14:02 | 36 | 0:08 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1620-03 MAL TIEMPO LLUVIA | S22081600000 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 8 | 2022-08-16 | 288 | keep | 0 | Aug | 2022 | 0.00019616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-16 13:54 | 2022-08-16 14:02 | 1073 | 0:08 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1620-01 MAL TIEMPO LLUVIA | S22081600332 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 8 | 2022-08-16 | 8584 | keep | 0 | Aug | 2022 | 0.0058465 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 13:54 | 2022-08-16 16:38 | 222 | 2:44 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO 1907-03 LLEVA 1909-09 SE ABRIO AMARRE Y SE CERRO 1907-03 | S22081600558 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 164 | 2022-08-16 | 36408 | keep | 0 | Aug | 2022 | 0.024797 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-16 13:54 | 2022-08-16 18:21 | 4456 | 4:27 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO 1909-09 Y SE CERRO N/O CONTRA 1907-03 | S22081600558 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 267 | 2022-08-16 | 1189752 | keep | 0 | Aug | 2022 | 0.81033 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-08-16 13:55 | 2022-08-16 21:32 | 36 | 7:37 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22081600214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2022-08-16 | 16452 | keep | 0 | Aug | 2022 | 0.011205 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CANOVANAS | 2022-08-16 14:00 | 2022-08-16 15:29 | 4188 | 1:29 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO EL BKR | R22081600085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-08-16 | 372732 | keep | 0 | Aug | 2022 | 0.25387 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
SAN JUAN | 2022-08-16 14:01 | 2022-08-16 17:23 | 922 | 3:22 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO N/O CONTRA 1346-05 Y SE CERRO 1401-08 QUEDO EN SERVICIO SE REMPLAZO MACHETE DEL 1346-05 | S22081600361 | New_Event | Switch Failure | Include | Include | Equipment | 202 | 2022-08-16 | 186244 | keep | 0 | Aug | 2022 | 0.12685 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-08-16 14:01 | 2022-08-16 15:30 | 135 | 1:29 | T | DESCONECTIVO DEFECTUOSO | DISPARO SE ABRIO N/O CONTRA 1346-05 Y SE CERRO 1401-08 QUEDO EN SERVICIO SE REMPLAZO MACHETE EN 1346-05 | S22081600000 | New_Event | Switch Failure | Include | Include | Equipment | 89 | 2022-08-16 | 12015 | keep | 0 | Aug | 2022 | 0.0081834 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2022-08-16 14:02 | 2022-08-16 14:03 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081600087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 2675 | keep | 0 | Aug | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
BAYAMON | 2022-08-16 14:03 | 2022-08-16 21:01 | 50 | 6:58 | P | DESGANCHE | 1 X 65 EN C/L 1 X 50 EN C/L DESGANCHE | B22081600217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2022-08-16 | 20900 | keep | 0 | Aug | 2022 | 0.014235 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-16 14:05 | 2022-08-16 14:06 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22081600123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 179 | keep | 0 | Aug | 2022 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
SAN JUAN | 2022-08-16 14:07 | 2022-08-16 14:29 | 1208 | 0:22 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO MAL TIEMPO | S22081600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 22 | 2022-08-16 | 26576 | keep | 0 | Aug | 2022 | 0.018101 | 0.00082276 | Sustained | FALSE | FALSE | Not_TMED_Event | 1208
BARRANQUITAS | 2022-08-16 14:09 | 2022-08-16 16:23 | 35 | 2:14 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22081600123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 134 | 2022-08-16 | 4690 | keep | 0 | Aug | 2022 | 0.0031943 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-08-16 14:13 | 2022-08-16 15:19 | 723 | 1:06 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1711-02 LLEVANCDO CARGA 1711-05 BY-220816-02 SE CERRO POR TRAMOS MAL TIEMPO RAYOS | B22081600239 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 66 | 2022-08-16 | 47718 | keep | 0 | Aug | 2022 | 0.032501 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-16 14:13 | 2022-08-16 16:38 | 1976 | 2:25 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 BY-220816-02 SE CERRO AMARRE 50 % EN SERVICIO DEL 1711-05 | B22081600239 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 145 | 2022-08-16 | 286520 | keep | 0 | Aug | 2022 | 0.19515 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2022-08-16 14:13 | 2022-08-16 17:54 | 200 | 3:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65, 1 X 50, 1 X 40 EN C/L MAL TIEMPO LLUVIAS | C22081600124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 221 | 2022-08-16 | 44200 | keep | 0 | Aug | 2022 | 0.030104 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-08-16 14:13 | 2022-08-16 19:55 | 30 | 5:42 | P | ARBOL SOBRE LINEA | 2 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS PRIMARIAS | A22081600154 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 342 | 2022-08-16 | 10260 | keep | 0 | Aug | 2022 | 0.006988 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-16 14:14 | 2022-08-16 20:27 | 90 | 6:13 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L 1 X 30 EN C/L MAL TIEMPO RAYOS | B22081600233 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 373 | 2022-08-16 | 33570 | keep | 0 | Aug | 2022 | 0.022864 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-08-16 14:18 | 2022-08-16 15:27 | 4664 | 1:09 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUOPTOR SE ABRIO MACHETES EN CARR 2 INT 402 BO POZO HONDO AÃ‘ASCO Y SE COLOCO INTERRUPTOR EN SERVICIO | M22081600110 | New_Event | Primary Wire Break | Include | Include | Equipment | 69 | 2022-08-16 | 321816 | keep | 0 | Aug | 2022 | 0.21919 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
UTUADO | 2022-08-16 14:19 | 2022-08-16 16:54 | 512 | 2:35 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | A22081600160 | New_Event | Primary Wire Break | Include | Include | Equipment | 155 | 2022-08-16 | 79360 | keep | 0 | Aug | 2022 | 0.054052 | 0.00034872 | Sustained | FALSE | FALSE | Not_TMED_Event | 512
BAYAMON | 2022-08-16 14:22 | 2022-08-16 15:24 | 60 | 1:02 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L MAL TIEMPO RAYOS | B22081600238 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 62 | 2022-08-16 | 3720 | keep | 0 | Aug | 2022 | 0.0025337 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-16 14:22 | 2022-08-16 14:23 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 4634 | keep | 0 | Aug | 2022 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
MAYAGÃœEZ | 2022-08-16 14:22 | 2022-08-16 17:14 | 130 | 2:52 | P | ARBOL SOBRE LINEA | 2 X 100 C/L SE RETIRO ARBOL SOBRE LINEAS PRIMARIAS | M22081600113 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 172 | 2022-08-16 | 22360 | keep | 0 | Aug | 2022 | 0.015229 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
AGUADILLA | 2022-08-16 14:23 | 2022-08-16 17:55 | 60 | 3:32 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | M22081600114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-08-16 | 12720 | keep | 0 | Aug | 2022 | 0.0086635 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-16 14:26 | 2022-08-16 15:07 | 2025 | 0:41 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL DE LAS LINEAS | R22081600175 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 41 | 2022-08-16 | 83025 | keep | 0 | Aug | 2022 | 0.056548 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 14:26 | 2022-08-16 19:40 | 191 | 5:14 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | B22081600246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-08-16 | 59974 | keep | 0 | Aug | 2022 | 0.040848 | 0.00013009 | Sustained | FALSE | FALSE | Not_TMED_Event | 191
BAYAMON | 2022-08-16 14:27 | 2022-08-17 10:36 | 160 | 20:09 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L SE REMPLAZO PORTAFUSIBLE CAMION SE ENREDO EN CONDUCTORES | B22081600248 | New_Event | Damage From Public | Include | Include | Public | 1209 | 2022-08-16 | 193440 | keep | 0 | Aug | 2022 | 0.13175 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
AGUADILLA | 2022-08-16 14:28 | 2022-08-16 20:27 | 10 | 5:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22081600118 | New_Event | Secondary Wire Break | Include | Include | Equipment | 359 | 2022-08-16 | 3590 | keep | 0 | Aug | 2022 | 0.0024451 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-16 14:29 | 2022-08-16 19:25 | 85 | 4:56 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO | R22081600115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-08-16 | 25160 | keep | 0 | Aug | 2022 | 0.017136 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-08-16 14:30 | 2022-08-16 16:40 | 60 | 2:10 | P | DESGANCHE | 2 X 50 EN C/L, 2 X 65 EN C/L, 1 X 80 EN C/L, 1 X 100 EN C/L, 3 X 100 EN CONVERTIDOR EN LA ALTA Y 2 X 80 EN BAJA DEL CONVERTIDOR Y 2 X 50 EN TOMITO | B22081600249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-08-16 | 7800 | keep | 0 | Aug | 2022 | 0.0053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-16 14:31 | 2022-08-16 14:32 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CON CARGA 6014-03 REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22081600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 1352 | keep | 0 | Aug | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-08-16 14:31 | 2022-08-16 14:32 | 871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 CON CARGA 6014-03 | M22081600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 871 | keep | 0 | Aug | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
BARRANQUITAS | 2022-08-16 14:31 | 2022-08-16 15:16 | 10 | 0:45 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | C22081600133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-08-16 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-16 14:33 | 2022-08-16 14:35 | 1222 | 0:02 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR | A22081600175 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 2 | 2022-08-16 | 2444 | keep | 0 | Aug | 2022 | 0.0016646 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2022-08-16 14:35 | 2022-08-16 17:06 | 400 | 2:31 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | INTERRUPTOR 7601-01 CON FASE INTERNA ABIERTA SE PASO LA CARGA AL 7601-04 | A22081600190 | 1st_after_momentary | Feeder Breaker Failure | Include | Include | Equipment | 151 | 2022-08-16 | 60400 | keep | 0 | Aug | 2022 | 0.041138 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BARRANQUITAS | 2022-08-16 14:36 | 2022-08-16 17:05 | 30 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L, 1 X 15 EN XMR Y 1 X 10 EN XMR MAL TIEMPO LLUVIAS | C22081600137 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2022-08-16 | 4470 | keep | 0 | Aug | 2022 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-16 14:37 | 2022-08-16 14:38 | 528 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22081600122 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-16 | 528 | keep | 0 | Aug | 2022 | 0.00035962 | 0.00035962 | Momentary | FALSE | FALSE | Not_TMED_Event | 528
YAUCO | 2022-08-16 14:37 | 2022-08-16 17:12 | 50 | 2:35 | P | MAL TIEMPO/RAYOS | 2 X 50 EN C/L DESCARGAS ELECTRICAS | M22081600121 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 155 | 2022-08-16 | 7750 | keep | 0 | Aug | 2022 | 0.0052785 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-16 14:38 | 2022-08-16 22:46 | 200 | 8:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 4 CAJAS PRIMARIA AVERIADAS | M22081600288 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 488 | 2022-08-16 | 97600 | keep | 0 | Aug | 2022 | 0.066475 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-16 14:42 | 2022-08-16 16:30 | 300 | 1:48 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600181 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 108 | 2022-08-16 | 32400 | keep | 0 | Aug | 2022 | 0.022067 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2022-08-16 14:45 | 2022-08-16 20:54 | 8 | 6:09 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO AVERIADO | C22081600144 | New_Event | Primary Wire Break | Include | Include | Equipment | 369 | 2022-08-16 | 2952 | keep | 0 | Aug | 2022 | 0.0020106 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-16 14:46 | 2022-08-16 14:47 | 539 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 539 | keep | 0 | Aug | 2022 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
BAYAMON | 2022-08-16 14:48 | 2022-08-16 18:41 | 91 | 3:53 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYOS | B22081600275 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 233 | 2022-08-16 | 21203 | keep | 0 | Aug | 2022 | 0.014441 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
ARECIBO | 2022-08-16 14:48 | 2022-08-16 19:20 | 100 | 4:32 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600197 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 272 | 2022-08-16 | 27200 | keep | 0 | Aug | 2022 | 0.018526 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-16 14:49 | 2022-08-16 18:00 | 60 | 3:11 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L DESGARCAS ELECTRICAS | M22081600127 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 191 | 2022-08-16 | 11460 | keep | 0 | Aug | 2022 | 0.0078054 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-16 14:49 | 2022-08-16 18:45 | 30 | 3:56 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600198 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 236 | 2022-08-16 | 7080 | keep | 0 | Aug | 2022 | 0.0048222 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-16 14:51 | 2022-08-16 23:10 | 86 | 8:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE Y 1 X 65 EN C/L Y DESGANCHE | B22081600277 | New_Event | Primary Wire Break | Include | Include | Equipment | 499 | 2022-08-16 | 42914 | keep | 0 | Aug | 2022 | 0.029229 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
BARRANQUITAS | 2022-08-16 14:53 | 2022-08-16 16:48 | 120 | 1:55 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESGANCHE - COLINDANCIA CON REGION CAGUAS | C22081600154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-08-16 | 13800 | keep | 0 | Aug | 2022 | 0.0093991 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-08-16 14:54 | 2022-08-16 15:52 | 32 | 0:58 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L DESCARGAS ELECTRICAS | M22081600131 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 58 | 2022-08-16 | 1856 | keep | 0 | Aug | 2022 | 0.0012641 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
ARECIBO | 2022-08-16 14:55 | 2022-08-16 20:25 | 25 | 5:30 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS SE UTILIZO EL MIS EVENTO PARA LAS DOS INTERRUPCIONES. | A22081600205 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 330 | 2022-08-16 | 8250 | keep | 0 | Aug | 2022 | 0.005619 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-08-16 14:55 | 2022-08-17 13:01 | 6 | 22:06 | P | TRANSFORMADOR AVERIADO | REEMPLAZARA XMR DE 50KVA X 50KVA | A22081600205 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1326 | 2022-08-16 | 7956 | keep | 0 | Aug | 2022 | 0.0054188 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-16 14:56 | 2022-08-16 14:57 | 888 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22081600151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 888 | keep | 0 | Aug | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-08-16 14:56 | 2022-08-16 14:57 | 393 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22081600151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 393 | keep | 0 | Aug | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-08-16 14:56 | 2022-08-16 14:57 | 4 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1600 | M22081600151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-16 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2022-08-16 14:57 | 2022-08-16 18:20 | 10 | 3:23 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO RAYOS | P22081600056 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 203 | 2022-08-16 | 2030 | keep | 0 | Aug | 2022 | 0.0013826 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-16 14:57 | 2022-08-16 19:50 | 20 | 4:53 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO PM-30 A PM 36 | M22081500570 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 293 | 2022-08-16 | 5860 | keep | 0 | Aug | 2022 | 0.0039912 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 14:57 | 2022-08-16 18:44 | 58 | 3:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22081600283 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-08-16 | 13166 | keep | 0 | Aug | 2022 | 0.0089673 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-08-16 15:01 | 2022-08-16 20:16 | 100 | 5:15 | P | MAL TIEMPO/RAYOS | 2 X 65 EN C/L MAL TIEMPO RAYOS | B22081600291 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 315 | 2022-08-16 | 31500 | keep | 0 | Aug | 2022 | 0.021455 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-08-16 15:01 | 2022-08-16 16:23 | 80 | 1:22 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22081600059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-08-16 | 6560 | keep | 0 | Aug | 2022 | 0.004468 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-08-16 15:03 | 2022-08-16 16:37 | 30 | 1:34 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22081600168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-08-16 | 2820 | keep | 0 | Aug | 2022 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-16 15:04 | 2022-08-16 18:45 | 100 | 3:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REMPLAZO AISLADOR | M22081600140 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 221 | 2022-08-16 | 22100 | keep | 0 | Aug | 2022 | 0.015052 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-16 15:04 | 2022-08-16 19:00 | 30 | 3:56 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600211 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 236 | 2022-08-16 | 7080 | keep | 0 | Aug | 2022 | 0.0048222 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-16 15:07 | 2022-08-16 20:45 | 80 | 5:38 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | B22081600298 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 338 | 2022-08-16 | 27040 | keep | 0 | Aug | 2022 | 0.018417 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-16 15:07 | 2022-08-16 18:27 | 2 | 3:20 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22081600142 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 200 | 2022-08-16 | 400 | keep | 0 | Aug | 2022 | 0.00027244 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-08-16 15:08 | 2022-08-16 18:34 | 60 | 3:26 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L SE REPARO ALAMBRE PRIMARIO | P22081600061 | New_Event | Primary Wire Break | Include | Include | Equipment | 206 | 2022-08-16 | 12360 | keep | 0 | Aug | 2022 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-16 15:08 | 2022-08-16 17:00 | 60 | 1:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081600216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-08-16 | 6720 | keep | 0 | Aug | 2022 | 0.004577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-16 15:10 | 2022-08-16 19:30 | 200 | 4:20 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 Y 1 X 30 EN CORTES DE LINEA SE REPARO BAJANTE PRIMARIO ABIERTO | A22081600219 | New_Event | Primary Wire Break | Include | Include | Equipment | 260 | 2022-08-16 | 52000 | keep | 0 | Aug | 2022 | 0.035417 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-16 15:13 | 2022-08-16 15:14 | 770 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 7801-04 CON CARGA 7801-02 | M22081600146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 770 | keep | 0 | Aug | 2022 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
AGUADILLA | 2022-08-16 15:13 | 2022-08-16 15:14 | 1772 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22081600146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 1772 | keep | 0 | Aug | 2022 | 0.0012069 | 0.0012069 | Momentary | FALSE | FALSE | Not_TMED_Event | 1772
UTUADO | 2022-08-16 15:13 | 2022-08-16 18:30 | 7 | 3:17 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081600222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-08-16 | 1379 | keep | 0 | Aug | 2022 | 0.00093923 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-08-16 15:15 | 2022-08-16 16:00 | 2 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | R22081600162 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-08-16 | 90 | keep | 0 | Aug | 2022 | 6.1299e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-08-16 15:15 | 2022-08-16 15:55 | 4 | 0:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZO DE CAJA PRIMARA | A22081600208 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-08-16 | 160 | keep | 0 | Aug | 2022 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-08-16 15:23 | 2022-08-16 18:59 | 350 | 3:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L AISLADOR ROTO | M22081600153 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 216 | 2022-08-16 | 75600 | keep | 0 | Aug | 2022 | 0.051491 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
GUAYAMA | 2022-08-16 15:25 | 2022-08-16 17:25 | 6 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22081600072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2022-08-16 | 720 | keep | 0 | Aug | 2022 | 0.00049039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-16 15:27 | 2022-08-16 21:38 | 105 | 6:11 | P | MAL TIEMPO/RAYOS | 2 X 65 EN C/L, 2 X 40 C/L, 1 X 50 EN C/L MAL TIEMPO RAYOS | B22081600317 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 371 | 2022-08-16 | 38955 | keep | 0 | Aug | 2022 | 0.026532 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
MAYAGÃœEZ | 2022-08-16 15:27 | 2022-08-16 18:53 | 3580 | 3:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO MACHETES | M22081600165 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 206 | 2022-08-16 | 737480 | keep | 0 | Aug | 2022 | 0.50229 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-16 15:29 | 2022-08-16 15:33 | 2932 | 0:04 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES NO SE ENCONTRO CAUSA | R22081600085 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-16 | 11728 | keep | 0 | Aug | 2022 | 0.0079879 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-16 15:40 | 2022-08-17 08:30 | 20 | 16:50 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | C22081600172 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1010 | 2022-08-16 | 20200 | keep | 0 | Aug | 2022 | 0.013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-08-16 15:50 | 2022-08-16 17:43 | 5 | 1:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR Y LEVANTAR SECUNDARIA | R22081600209 | New_Event | Secondary Wire Break | Include | Include | Equipment | 113 | 2022-08-16 | 565 | keep | 0 | Aug | 2022 | 0.00038482 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-16 15:53 | 2022-08-16 17:14 | 12 | 1:21 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA X 37.5KVA | C22081600166 | New_Event | Service Transformer Failure | Include | Include | Equipment | 81 | 2022-08-16 | 972 | keep | 0 | Aug | 2022 | 0.00066202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-16 15:54 | 2022-08-16 15:55 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1909-08 QUE LLEVA 1907-05 | S22081600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 2435 | keep | 0 | Aug | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-08-16 15:54 | 2022-08-16 15:55 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1909-08 QUE LLEVA 1907-05 | S22081600704 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 2956 | keep | 0 | Aug | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-08-16 15:58 | 2022-08-16 19:42 | 64 | 3:44 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L MAL TIEMPO RAYOS | B22081600341 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 224 | 2022-08-16 | 14336 | keep | 0 | Aug | 2022 | 0.0097642 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
ARECIBO | 2022-08-16 16:05 | 2022-08-16 20:00 | 25 | 3:55 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600270 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 235 | 2022-08-16 | 5875 | keep | 0 | Aug | 2022 | 0.0040014 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-16 16:19 | 2022-08-16 17:47 | 5 | 1:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8 EN XMR MAL TIEMPO LLUVIAS | C22081600180 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 88 | 2022-08-16 | 440 | keep | 0 | Aug | 2022 | 0.00029968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-08-16 16:27 | 2022-08-16 17:49 | 100 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | R22081600227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-08-16 | 8200 | keep | 0 | Aug | 2022 | 0.005585 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-16 16:30 | 2022-08-16 17:00 | 10 | 0:30 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHO | R22081600229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-08-16 | 300 | keep | 0 | Aug | 2022 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-16 16:31 | 2022-08-16 18:37 | 40 | 2:06 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | C22081600181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-08-16 | 5040 | keep | 0 | Aug | 2022 | 0.0034327 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-16 16:38 | 2022-08-16 16:50 | 988 | 0:12 | P | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1711-02 LLEVANCDO CARGA 1711-05 BY-220816-02 SE CERRO TRAMO MAL TIEMPO 100 % EN SERVICIO DEL 1711-05 | B22081600239 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 12 | 2022-08-16 | 11856 | keep | 0 | Aug | 2022 | 0.0080751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-16 16:52 | 2022-08-16 18:41 | 100 | 1:49 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22081600187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-08-16 | 10900 | keep | 0 | Aug | 2022 | 0.0074239 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-16 16:53 | 2022-08-17 04:24 | 20 | 11:31 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22081600379 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 691 | 2022-08-16 | 13820 | keep | 0 | Aug | 2022 | 0.0094127 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-16 16:53 | 2022-08-16 22:56 | 15 | 6:03 | P | NO SE REPORTO CAUSA | 2 X 20 EN XMR | B22081600507 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2022-08-16 | 5445 | keep | 0 | Aug | 2022 | 0.0037086 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-16 16:54 | 2022-08-16 17:23 | 1054 | 0:29 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEAS CRUZADAS Y SE CERRO EL INTERRUPTOR | A22081600292 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 29 | 2022-08-16 | 30566 | keep | 0 | Aug | 2022 | 0.020818 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-16 17:00 | 2022-08-16 21:00 | 1 | 4:00 | P | MAL TIEMPO/RAYOS | 1 X 10 EN RISER, DESCARGAS ELECTRICAS | M22081600390 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 240 | 2022-08-16 | 240 | keep | 0 | Aug | 2022 | 0.00016346 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-16 17:01 | 2022-08-16 17:06 | 222 | 0:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES DISPARO 1907-03 LLEVA 1909-09 SE ABRIO AMARRE Y SE CERRO 1907-03 BY-220816-03 | S22081600558 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2022-08-16 | 1110 | keep | 0 | Aug | 2022 | 0.00075602 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-16 17:03 | 2022-08-16 17:04 | 1228 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRRE | C22081600189 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 1228 | keep | 0 | Aug | 2022 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
UTUADO | 2022-08-16 17:06 | 2022-08-16 19:30 | 25 | 2:24 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600300 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 144 | 2022-08-16 | 3600 | keep | 0 | Aug | 2022 | 0.0024519 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-08-16 17:10 | 2022-08-16 18:30 | 10 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | P22081600086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2022-08-16 | 800 | keep | 0 | Aug | 2022 | 0.00054488 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-16 17:10 | 2022-08-16 20:50 | 200 | 3:40 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | M22081600250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-08-16 | 44000 | keep | 0 | Aug | 2022 | 0.029968 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-08-16 17:10 | 2022-08-16 21:00 | 20 | 3:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS EVENTO TRANSFERIDO DE PONCE | P22081600087 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 230 | 2022-08-16 | 4600 | keep | 0 | Aug | 2022 | 0.003133 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-16 17:17 | 2022-08-16 22:04 | 7 | 4:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR FUERTES LLUVIAS | C22081600195 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 287 | 2022-08-16 | 2009 | keep | 0 | Aug | 2022 | 0.0013683 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-16 17:20 | 2022-08-16 19:54 | 30 | 2:34 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L DESCARGAS ELECTRICAS | M22081600258 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 154 | 2022-08-16 | 4620 | keep | 0 | Aug | 2022 | 0.0031467 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-16 17:22 | 2022-08-16 20:50 | 40 | 3:28 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGAS ELECTRICAS | M22081600261 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 208 | 2022-08-16 | 8320 | keep | 0 | Aug | 2022 | 0.0056667 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-16 17:23 | 2022-08-16 21:00 | 100 | 3:37 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L, DESCARGAS ELECTRICAS | M22081600262 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 217 | 2022-08-16 | 21700 | keep | 0 | Aug | 2022 | 0.01478 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-16 17:23 | 2022-08-16 21:30 | 512 | 4:07 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | A22081600160 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 247 | 2022-08-16 | 126464 | keep | 0 | Aug | 2022 | 0.086134 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-16 17:25 | 2022-08-16 20:19 | 2 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 200 EN C/L | R22081600253 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-16 | 348 | keep | 0 | Aug | 2022 | 0.00023702 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-08-16 17:27 | 2022-08-16 20:10 | 80 | 2:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L REMPLAZO AISLADOR | R22081600249 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 163 | 2022-08-16 | 13040 | keep | 0 | Aug | 2022 | 0.0088815 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-16 17:38 | 2022-08-16 19:10 | 50 | 1:32 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGAS ELECTRICAS | M22081600273 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 92 | 2022-08-16 | 4600 | keep | 0 | Aug | 2022 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-16 17:44 | 2022-08-16 22:38 | 150 | 4:54 | P | NO SE REPORTO CAUSA | 1 X 100 Y 1 X 80 CORTES DE LINEA | S22081600971 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2022-08-16 | 44100 | keep | 0 | Aug | 2022 | 0.030036 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-16 17:46 | 2022-08-16 19:40 | 60 | 1:54 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | M22081600279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-08-16 | 6840 | keep | 0 | Aug | 2022 | 0.0046587 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-16 17:49 | 2022-08-16 17:50 | 3070 | 0:01 | T | DESGANCHE | RECIERRE | B22081600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-16 | 3070 | keep | 0 | Aug | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-08-16 17:50 | 2022-08-16 21:36 | 334 | 3:46 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | B22081600419 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-08-16 | 75484 | keep | 0 | Aug | 2022 | 0.051412 | 0.00022749 | Sustained | FALSE | FALSE | Not_TMED_Event | 334
SAN JUAN | 2022-08-16 18:05 | 2022-08-17 14:22 | 38 | 20:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA PORTAFUSIBLE | S22081601004 | New_Event | Cutout Failure | Include | Include | Equipment | 1217 | 2022-08-16 | 46246 | keep | 0 | Aug | 2022 | 0.031498 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
AGUADILLA | 2022-08-16 18:10 | 2022-08-17 11:25 | 10 | 17:15 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081600295 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1035 | 2022-08-16 | 10350 | keep | 0 | Aug | 2022 | 0.0070493 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-16 18:13 | 2022-08-17 12:04 | 3 | 17:51 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR QUEMADO DE 50KVA X 25KVA | A22081600022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1071 | 2022-08-16 | 3213 | keep | 0 | Aug | 2022 | 0.0021884 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2022-08-16 18:18 | 2022-08-16 21:49 | 12 | 3:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22081600341 | New_Event | Secondary Wire Break | Include | Include | Equipment | 211 | 2022-08-16 | 2532 | keep | 0 | Aug | 2022 | 0.0017245 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-16 18:21 | 2022-08-16 18:36 | 3565 | 0:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO PARARRAYO Y SE CERRO MACHETES Y DISPARO 1907-03 QUE LLEVA 1909-09 | S22081600558 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 15 | 2022-08-16 | 53475 | keep | 0 | Aug | 2022 | 0.036422 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-16 18:25 | 2022-08-16 22:30 | 60 | 4:05 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081600305 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 245 | 2022-08-16 | 14700 | keep | 0 | Aug | 2022 | 0.010012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-16 18:25 | 2022-08-17 12:10 | 20 | 17:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081600346 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1065 | 2022-08-16 | 21300 | keep | 0 | Aug | 2022 | 0.014507 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-16 18:26 | 2022-08-16 19:37 | 67 | 1:11 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHO | R22081600267 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-08-16 | 4757 | keep | 0 | Aug | 2022 | 0.00324 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2022-08-16 18:31 | 2022-08-16 21:00 | 10 | 2:29 | P | DESCONECTIVO DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE QUEMADO | A22081600349 | New_Event | Switch Failure | Include | Include | Equipment | 149 | 2022-08-16 | 1490 | keep | 0 | Aug | 2022 | 0.0010148 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-16 18:36 | 2022-08-16 18:37 | 222 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES DISPARO 1907-03 LLEVA 1909-09 SE ABRIO MACHETES EN LOS FRAILES Y SE CERRO 1907-03 BY-220816-03 | S22081600558 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-16 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 18:36 | 2022-08-16 18:37 | 4456 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE RETIRO PARARRAYO Y SE CERRO MACHETES Y DISPARO 1907-03 QUE LLEVA 1909-09 SE ABRIO MACHETES Y SE CERRO POR SCADA 1907-03 NUVAMENTE | S22081600558 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-16 | 4456 | keep | 0 | Aug | 2022 | 0.003035 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 18:37 | 2022-08-16 19:07 | 2228 | 0:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ASLADOR PARTIDO Y SE CERRO MACHETES DE LOS FRAILES 50% EN SERVICIO DEL 1909-09 QUE ESTA POR 1907-03 | S22081600558 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 30 | 2022-08-16 | 66840 | keep | 0 | Aug | 2022 | 0.045524 | 0.0015175 | Sustained | FALSE | FALSE | Not_TMED_Event | 2228
CANOVANAS | 2022-08-16 18:39 | 2022-08-17 20:08 | 12 | 25:29 | P | ANIMAL | 1X15 EN XMR POR CRUCE DE AVE | R22081600273 | New_Event | Animals | Include | Include | Wildlife | 1529 | 2022-08-16 | 18348 | keep | 0 | Aug | 2022 | 0.012497 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-16 18:42 | 2022-08-16 20:44 | 314 | 2:02 | P | MAL TIEMPO/RAYOS | 2 X 65 EN RISER MAL TIEMPO RAYOS | S22081601065 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 122 | 2022-08-16 | 38308 | keep | 0 | Aug | 2022 | 0.026091 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
CANOVANAS | 2022-08-16 18:43 | 2022-08-16 21:26 | 50 | 2:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN C/L FUERTES LLUVIAS | R22081600274 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 163 | 2022-08-16 | 8150 | keep | 0 | Aug | 2022 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-16 18:45 | 2022-08-17 11:10 | 60 | 16:25 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22081600439 | New_Event | Vegetation Contact | Include | Include | Vegetation | 985 | 2022-08-16 | 59100 | keep | 0 | Aug | 2022 | 0.040253 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-16 18:49 | 2022-08-17 06:22 | 20 | 11:33 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | C22081600216 | New_Event | Animals | Include | Include | Wildlife | 693 | 2022-08-16 | 13860 | keep | 0 | Aug | 2022 | 0.00944 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-16 18:49 | 2022-08-17 00:58 | 118 | 6:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER Y 1 X 100 EN SU | B22081600440 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2022-08-16 | 43542 | keep | 0 | Aug | 2022 | 0.029656 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
MAYAGÃœEZ | 2022-08-16 18:50 | 2022-08-16 20:05 | 80 | 1:15 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L DESCARGAS ELECTRICAS | M22081600317 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-08-16 | 6000 | keep | 0 | Aug | 2022 | 0.0040866 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-16 19:01 | 2022-08-17 11:11 | 150 | 16:10 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTE DE LINEA DESGANCHE | S22081601098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 970 | 2022-08-16 | 145500 | keep | 0 | Aug | 2022 | 0.099099 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-08-16 19:01 | 2022-08-16 21:33 | 24 | 2:32 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO | R22081600279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-08-16 | 3648 | keep | 0 | Aug | 2022 | 0.0024846 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2022-08-16 19:07 | 2022-08-16 20:04 | 2228 | 0:57 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AILADOR SE LLEVO LINEA A AISLADOR Y SE CERRO MACHETES 100% EN SERVICIO DEL 1909-09 QUE ESTA POR 1907-03 | S22081600558 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 57 | 2022-08-16 | 126996 | keep | 0 | Aug | 2022 | 0.086496 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-16 19:08 | 2022-08-17 12:50 | 60 | 17:42 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS WR6218785 | M22081600325 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1062 | 2022-08-16 | 63720 | keep | 0 | Aug | 2022 | 0.043399 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-16 19:16 | 2022-08-17 10:29 | 50 | 15:13 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYO | A22081600373 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 913 | 2022-08-16 | 45650 | keep | 0 | Aug | 2022 | 0.031092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-16 19:23 | 2022-08-17 10:05 | 4 | 14:42 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081600340 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 882 | 2022-08-16 | 3528 | keep | 0 | Aug | 2022 | 0.0024029 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-16 19:28 | 2022-08-17 00:15 | 136 | 4:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22081601142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 287 | 2022-08-16 | 39032 | keep | 0 | Aug | 2022 | 0.026585 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
BARRANQUITAS | 2022-08-16 19:29 | 2022-08-17 02:32 | 179 | 7:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA NO FUNDIO | C22081600249 | New_Event | Cutout Failure | Include | Include | Equipment | 423 | 2022-08-16 | 75717 | keep | 0 | Aug | 2022 | 0.051571 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
PONCE | 2022-08-16 19:36 | 2022-08-17 07:06 | 8 | 11:30 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | P22081600118 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 690 | 2022-08-16 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-16 19:36 | 2022-08-16 22:00 | 6 | 2:24 | P | MAL TIEMPO/RAYOS | 1 X 15 TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081600381 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 144 | 2022-08-16 | 864 | keep | 0 | Aug | 2022 | 0.00058847 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-16 19:40 | 2022-08-17 12:03 | 120 | 16:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22081601161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 983 | 2022-08-16 | 117960 | keep | 0 | Aug | 2022 | 0.080342 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-08-16 19:45 | 2022-08-16 23:06 | 20 | 3:21 | P | DESGANCHE | 1 X 80 EN C/L Y SE REALIZO DESGANCHE | S22081601172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-08-16 | 4020 | keep | 0 | Aug | 2022 | 0.002738 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-16 19:53 | 2022-08-16 22:08 | 40 | 2:15 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/LS DESGANCHE | R22081600291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-08-16 | 5400 | keep | 0 | Aug | 2022 | 0.0036779 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-16 19:54 | 2022-08-17 08:55 | 6 | 13:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR PORTAFUSIBLE | M22081600362 | New_Event | Cutout Failure | Include | Include | Equipment | 781 | 2022-08-16 | 4686 | keep | 0 | Aug | 2022 | 0.0031916 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-16 20:02 | 2022-08-17 09:50 | 5 | 13:48 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081600367 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 828 | 2022-08-16 | 4140 | keep | 0 | Aug | 2022 | 0.0028197 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-16 20:06 | 2022-08-16 22:15 | 30 | 2:09 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | P22081600369 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 129 | 2022-08-16 | 3870 | keep | 0 | Aug | 2022 | 0.0026358 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-16 20:07 | 2022-08-17 09:00 | 10 | 12:53 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR RAYO | B22081600475 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 773 | 2022-08-16 | 7730 | keep | 0 | Aug | 2022 | 0.0052649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-16 20:15 | 2022-08-17 14:20 | 80 | 18:05 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE RETIRO PARARRAYOS AVERIADO | M22081600375 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1085 | 2022-08-16 | 86800 | keep | 0 | Aug | 2022 | 0.059119 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-16 20:18 | 2022-08-17 13:08 | 235 | 16:50 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22081601250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1010 | 2022-08-16 | 237350 | keep | 0 | Aug | 2022 | 0.16166 | 0.00016006 | Sustained | FALSE | FALSE | Not_TMED_Event | 235
MAYAGÃœEZ | 2022-08-16 20:22 | 2022-08-17 09:25 | 5 | 13:03 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081600382 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 783 | 2022-08-16 | 3915 | keep | 0 | Aug | 2022 | 0.0026665 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-08-16 20:25 | 2022-08-16 23:32 | 50 | 3:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU - 1E | R22081600297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2022-08-16 | 9350 | keep | 0 | Aug | 2022 | 0.0063682 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-16 20:26 | 2022-08-17 08:35 | 6 | 12:09 | P | MAL TIEMPO/RAYOS | 1 X 30 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081600384 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 729 | 2022-08-16 | 4374 | keep | 0 | Aug | 2022 | 0.0029791 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-16 20:40 | 2022-08-17 08:33 | 50 | 11:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S22081601290 | New_Event | Cutout Failure | Include | Include | Equipment | 713 | 2022-08-16 | 35650 | keep | 0 | Aug | 2022 | 0.024281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-16 20:43 | 2022-08-17 11:10 | 8 | 14:27 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | S22081601297 | New_Event | Vegetation Contact | Include | Include | Vegetation | 867 | 2022-08-16 | 6936 | keep | 0 | Aug | 2022 | 0.0047241 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-16 20:43 | 2022-08-17 09:15 | 2 | 12:32 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22081600404 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 752 | 2022-08-16 | 1504 | keep | 0 | Aug | 2022 | 0.0010244 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-16 20:44 | 2022-08-17 11:56 | 11 | 15:12 | P | DESGANCHE | DESGANCHE PRIMARIO Y 1 X 20 EN XMR | B22081600473 | New_Event | Vegetation Contact | Include | Include | Vegetation | 912 | 2022-08-16 | 10032 | keep | 0 | Aug | 2022 | 0.0068327 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-08-16 20:45 | 2022-08-17 11:10 | 158 | 14:25 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | S22081600303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 865 | 2022-08-16 | 136670 | keep | 0 | Aug | 2022 | 0.093085 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
MAYAGÃœEZ | 2022-08-16 20:53 | 2022-08-16 22:35 | 70 | 1:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081600398 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-08-16 | 7140 | keep | 0 | Aug | 2022 | 0.004863 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-08-16 20:56 | 2022-08-17 17:35 | 50 | 20:39 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22081600399 | New_Event | Primary Wire Break | Include | Include | Equipment | 1239 | 2022-08-16 | 61950 | keep | 0 | Aug | 2022 | 0.042194 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-16 20:58 | 2022-08-17 02:35 | 80 | 5:37 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081600400 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 337 | 2022-08-16 | 26960 | keep | 0 | Aug | 2022 | 0.018362 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-16 21:14 | 2022-08-17 12:10 | 10 | 14:56 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR QUEMADO 25KVA X 37.5 KVA | A22081600012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 896 | 2022-08-16 | 8960 | keep | 0 | Aug | 2022 | 0.0061026 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-16 21:19 | 2022-08-17 07:18 | 40 | 9:59 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C22081600244 | New_Event | Animals | Include | Include | Wildlife | 599 | 2022-08-16 | 23960 | keep | 0 | Aug | 2022 | 0.016319 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-16 21:19 | 2022-08-17 07:01 | 12 | 9:42 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22081600244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 582 | 2022-08-16 | 6984 | keep | 0 | Aug | 2022 | 0.0047568 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-16 21:34 | 2022-08-16 21:35 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081600314 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 3464 | keep | 0 | Aug | 2022 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
BAYAMON | 2022-08-16 21:34 | 2022-08-17 14:20 | 12 | 16:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22081600490 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1006 | 2022-08-16 | 12072 | keep | 0 | Aug | 2022 | 0.0082222 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-16 21:35 | 2022-08-16 22:53 | 50 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22081600319 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-08-16 | 3900 | keep | 0 | Aug | 2022 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-16 21:43 | 2022-08-17 13:12 | 60 | 15:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE LEVANTO CONDUCTOR | S22081601355 | New_Event | Primary Wire Break | Include | Include | Equipment | 929 | 2022-08-16 | 55740 | keep | 0 | Aug | 2022 | 0.037964 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-16 21:46 | 2022-08-17 11:10 | 40 | 13:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081601358 | New_Event | Vegetation Contact | Include | Include | Vegetation | 804 | 2022-08-16 | 32160 | keep | 0 | Aug | 2022 | 0.021904 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-16 21:49 | 2022-08-18 22:00 | 10 | 48:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR Y SE REPARARON CONEXIONES SECUNDARIAS | A22081600419 | New_Event | Primary Wire Break | Include | Include | Equipment | 2891 | 2022-08-16 | 28910 | keep | 0 | Aug | 2022 | 0.01969 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-16 21:52 | 2022-08-16 22:07 | 34 | 0:15 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | B22081600492 | New_Event | Vegetation Contact | Include | Include | Vegetation | 15 | 2022-08-16 | 510 | keep | 0 | Aug | 2022 | 0.00034736 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2022-08-16 22:00 | 2022-08-17 11:10 | 146 | 13:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE HIZO DESGANCHE | S22081601367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 790 | 2022-08-16 | 115340 | keep | 0 | Aug | 2022 | 0.078558 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
AGUADILLA | 2022-08-16 22:04 | 2022-08-17 09:09 | 30 | 11:05 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081600416 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 665 | 2022-08-16 | 19950 | keep | 0 | Aug | 2022 | 0.013588 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-16 22:06 | 2022-08-16 23:25 | 60 | 1:19 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081600422 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 79 | 2022-08-16 | 4740 | keep | 0 | Aug | 2022 | 0.0032284 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-08-16 22:07 | 2022-08-17 11:30 | 200 | 13:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | A22081600423 | New_Event | Cutout Failure | Include | Include | Equipment | 803 | 2022-08-16 | 160600 | keep | 0 | Aug | 2022 | 0.10938 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-16 22:10 | 2022-08-17 04:53 | 80 | 6:43 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON LINEAS PRIMARIAS PARTIDAS | M22081600419 | New_Event | Primary Wire Break | Include | Include | Equipment | 403 | 2022-08-16 | 32240 | keep | 0 | Aug | 2022 | 0.021959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-08-16 22:12 | 2022-08-17 07:48 | 50 | 9:36 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | P22081600144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 576 | 2022-08-16 | 28800 | keep | 0 | Aug | 2022 | 0.019616 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-16 22:39 | 2022-08-17 10:22 | 51 | 11:43 | P | DESGANCHE | 3 X 65 EN RISER DE ENTRADA Y 3 X 50 EN SALIDA DE RISER SE REALIZO DESGANCHE | R22081600332 | New_Event | Vegetation Contact | Include | Include | Vegetation | 703 | 2022-08-16 | 35853 | keep | 0 | Aug | 2022 | 0.024419 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
UTUADO | 2022-08-16 22:44 | 2022-08-17 15:32 | 80 | 16:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA SE CERRO CORTE DE LINEA | A22081600429 | New_Event | Primary Wire Break | Include | Include | Equipment | 1008 | 2022-08-16 | 80640 | keep | 0 | Aug | 2022 | 0.054924 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-16 22:50 | 2022-08-17 09:02 | 50 | 10:12 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA POR RAYOS | A22081600426 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 612 | 2022-08-16 | 30600 | keep | 0 | Aug | 2022 | 0.020842 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-16 22:56 | 2022-08-16 22:57 | 3597 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22081600503 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-16 | 3597 | keep | 0 | Aug | 2022 | 0.0024499 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-16 22:57 | 2022-08-17 05:21 | 15 | 6:24 | P | NO SE REPORTO CAUSA | 2 X 20 EN XMR | B22081600507 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 384 | 2022-08-16 | 5760 | keep | 0 | Aug | 2022 | 0.0039231 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-16 23:28 | 2022-08-17 19:28 | 20 | 20:00 | P | DESGANCHE | SE REALIZO DESGANCHE Y LEVANTO CONDUCTOR NO FUNDIO | C22081600273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1200 | 2022-08-16 | 24000 | keep | 0 | Aug | 2022 | 0.016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-16 23:29 | 2022-08-17 10:44 | 45 | 11:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S22081601404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 675 | 2022-08-16 | 30375 | keep | 0 | Aug | 2022 | 0.020688 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-08-17 00:42 | 2022-08-17 16:36 | 100 | 15:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE LEVANTO LINEA | S22081700011 | New_Event | Primary Wire Break | Include | Include | Equipment | 954 | 2022-08-17 | 95400 | keep | 0 | Aug | 2022 | 0.064977 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
HUMACAO | 2022-08-17 00:59 | 2022-08-17 01:00 | 1250 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 1250 | keep | 0 | Aug | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | TMED_Event | 1250
BAYAMON | 2022-08-17 01:41 | 2022-08-17 04:03 | 227 | 2:22 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | B22081700002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-08-17 | 32234 | keep | 0 | Aug | 2022 | 0.021954 | 0.00015461 | Sustained | FALSE | FALSE | TMED_Event | 227
VEGA BAJA | 2022-08-17 04:02 | 2022-08-17 09:30 | 350 | 5:28 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | A22081700010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2022-08-17 | 114800 | keep | 0 | Aug | 2022 | 0.07819 | 0.00023838 | Sustained | FALSE | FALSE | TMED_Event | 350
SAN JUAN | 2022-08-17 05:19 | 2022-08-17 08:52 | 142 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S22081700032 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2022-08-17 | 30246 | keep | 0 | Aug | 2022 | 0.0206 | 9.6716e-05 | Sustained | FALSE | FALSE | TMED_Event | 142
CAGUAS | 2022-08-17 05:37 | 2022-08-17 05:38 | 1378 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 1378 | keep | 0 | Aug | 2022 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | TMED_Event | 1378
SAN JUAN | 2022-08-17 06:00 | 2022-08-17 09:45 | 1 | 3:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S22081700120 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2022-08-17 | 225 | keep | 0 | Aug | 2022 | 0.00015325 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2022-08-17 06:07 | 2022-08-17 12:20 | 25 | 6:13 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C22081700006 | New_Event | Animals | Include | Include | Wildlife | 373 | 2022-08-17 | 9325 | keep | 0 | Aug | 2022 | 0.0063512 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BAYAMON | 2022-08-17 06:12 | 2022-08-17 06:14 | 320 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22081700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-17 | 640 | keep | 0 | Aug | 2022 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | TMED_Event | 320
ARECIBO | 2022-08-17 06:23 | 2022-08-17 09:21 | 30 | 2:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | A22081700028 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 178 | 2022-08-17 | 5340 | keep | 0 | Aug | 2022 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
MAYAGÃœEZ | 2022-08-17 06:29 | 2022-08-17 08:45 | 6 | 2:16 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700007 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 136 | 2022-08-17 | 816 | keep | 0 | Aug | 2022 | 0.00055577 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
MAYAGÃœEZ | 2022-08-17 06:40 | 2022-08-17 09:40 | 12 | 3:00 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700008 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 180 | 2022-08-17 | 2160 | keep | 0 | Aug | 2022 | 0.0014712 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CANOVANAS | 2022-08-17 06:49 | 2022-08-17 10:25 | 11 | 3:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTE | R22081700010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 216 | 2022-08-17 | 2376 | keep | 0 | Aug | 2022 | 0.0016183 | 7.492e-06 | Sustained | FALSE | FALSE | TMED_Event | 11
BAYAMON | 2022-08-17 06:52 | 2022-08-17 12:52 | 1 | 6:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA | S22081700050 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2022-08-17 | 360 | keep | 0 | Aug | 2022 | 0.00024519 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
SAN JUAN | 2022-08-17 06:59 | 2022-08-17 16:19 | 5 | 9:20 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | S22081700054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 560 | 2022-08-17 | 2800 | keep | 0 | Aug | 2022 | 0.0019071 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
MAYAGÃœEZ | 2022-08-17 06:59 | 2022-08-17 10:30 | 80 | 3:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22081700009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 211 | 2022-08-17 | 16880 | keep | 0 | Aug | 2022 | 0.011497 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
ARECIBO | 2022-08-17 07:00 | 2022-08-17 16:42 | 2 | 9:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO SECUNDARIA | A22081700034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 582 | 2022-08-17 | 1164 | keep | 0 | Aug | 2022 | 0.0007928 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BAYAMON | 2022-08-17 07:05 | 2022-08-17 07:06 | 1362 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B22081700000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-17 | 1362 | keep | 0 | Aug | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | TMED_Event | 1362
BARRANQUITAS | 2022-08-17 07:05 | 2022-08-17 09:42 | 14 | 2:37 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO AVERIADO | C22081700018 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 157 | 2022-08-17 | 2198 | keep | 0 | Aug | 2022 | 0.001497 | 9.5353e-06 | Sustained | FALSE | FALSE | TMED_Event | 14
AGUADILLA | 2022-08-17 07:05 | 2022-08-17 10:00 | 6 | 2:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22081700012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 175 | 2022-08-17 | 1050 | keep | 0 | Aug | 2022 | 0.00071515 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BAYAMON | 2022-08-17 07:10 | 2022-08-17 10:12 | 80 | 3:02 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22081700017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 182 | 2022-08-17 | 14560 | keep | 0 | Aug | 2022 | 0.0099167 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
CANOVANAS | 2022-08-17 07:26 | 2022-08-17 11:30 | 2 | 4:04 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22081700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2022-08-17 | 488 | keep | 0 | Aug | 2022 | 0.00033237 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
VEGA BAJA | 2022-08-17 07:37 | 2022-08-17 11:40 | 35 | 4:03 | P | MAL TIEMPO/RAYOS | 1 X 50, 1 X 40, 1 X 30 EN CORTES DE LINEA DISTINTOS Y 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081700043 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 243 | 2022-08-17 | 8505 | keep | 0 | Aug | 2022 | 0.0057927 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
BARRANQUITAS | 2022-08-17 07:37 | 2022-08-17 10:45 | 10 | 3:08 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L REMPLAZO 2 PARARRAYOS | C22081700022 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 188 | 2022-08-17 | 1880 | keep | 0 | Aug | 2022 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
HUMACAO | 2022-08-17 07:58 | 2022-08-17 12:25 | 15 | 4:27 | P | ANIMAL | 2 X 80 EN C/L Y 2 X 20 EN BANCO XMR SE REEMPLAZO CAJA PRIMARIA CRUCE X AVE | C22081700027 | New_Event | Animals | Include | Include | Wildlife | 267 | 2022-08-17 | 4005 | keep | 0 | Aug | 2022 | 0.0027278 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
SAN JUAN | 2022-08-17 08:00 | 2022-08-17 12:45 | 40 | 4:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081700255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-08-17 | 11400 | keep | 0 | Aug | 2022 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
BAYAMON | 2022-08-17 08:06 | 2022-08-17 12:50 | 100 | 4:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | B22081700023 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2022-08-17 | 28400 | keep | 0 | Aug | 2022 | 0.019343 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
VEGA BAJA | 2022-08-17 08:11 | 2022-08-17 11:40 | 30 | 3:29 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700052 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 209 | 2022-08-17 | 6270 | keep | 0 | Aug | 2022 | 0.0042705 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BARRANQUITAS | 2022-08-17 08:29 | 2022-08-17 09:52 | 15 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | C22081700020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2022-08-17 | 1245 | keep | 0 | Aug | 2022 | 0.00084796 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
ARECIBO | 2022-08-17 08:29 | 2022-08-17 14:21 | 1 | 5:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO CONEXIONES | A22081700059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 352 | 2022-08-17 | 352 | keep | 0 | Aug | 2022 | 0.00023975 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
AGUADILLA | 2022-08-17 08:35 | 2022-08-17 10:08 | 1 | 1:33 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2022-08-17 | 93 | keep | 0 | Aug | 2022 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
CAGUAS | 2022-08-17 08:44 | 2022-08-17 11:10 | 8 | 2:26 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR SECUNDARIA IMPACTO DE CAMION EXTERNO | C22081700032 | New_Event | Damage From Public | Include | Include | Public | 146 | 2022-08-17 | 1168 | keep | 0 | Aug | 2022 | 0.00079552 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
CAGUAS | 2022-08-17 08:47 | 2022-08-17 11:10 | 12 | 2:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CONSTRUYO PROVICIONAL AEREO SECUNDARIO | C22081500030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 143 | 2022-08-17 | 1716 | keep | 0 | Aug | 2022 | 0.0011688 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
VEGA BAJA | 2022-08-17 08:51 | 2022-08-17 18:18 | 300 | 9:27 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 567 | 2022-08-17 | 170100 | keep | 0 | Aug | 2022 | 0.11585 | 0.00020433 | Sustained | FALSE | FALSE | TMED_Event | 300
SAN JUAN | 2022-08-17 08:52 | 2022-08-17 08:53 | 5619 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 90% POR 1620-03 | S22081700109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 5619 | keep | 0 | Aug | 2022 | 0.0038271 | 0.0038271 | Momentary | FALSE | FALSE | TMED_Event | 5619
SAN JUAN | 2022-08-17 08:52 | 2022-08-17 08:53 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1620-03 | S22081700109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 36 | keep | 0 | Aug | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | TMED_Event | 36
SAN JUAN | 2022-08-17 08:52 | 2022-08-17 08:53 | 1073 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 90% DEL 1336-07 Y 1620-01 | S22081700109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 1073 | keep | 0 | Aug | 2022 | 0.00073082 | 0.00073082 | Momentary | FALSE | FALSE | TMED_Event | 1073
CANOVANAS | 2022-08-17 09:00 | 2022-08-17 16:11 | 20 | 7:11 | P | DESGANCHE | 2X80 EN C/L | R22081700025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 431 | 2022-08-17 | 8620 | keep | 0 | Aug | 2022 | 0.005871 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
BAYAMON | 2022-08-17 09:03 | 2022-08-17 11:10 | 50 | 2:07 | P | DESGANCHE | DESGANCHE PRIMARIO 1 X 15 EN XMR Y 1 X 40 EN C/L | B22081700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-08-17 | 6350 | keep | 0 | Aug | 2022 | 0.004325 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
UTUADO | 2022-08-17 09:06 | 2022-08-17 15:32 | 25 | 6:26 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR RAYOS | A22081700070 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 386 | 2022-08-17 | 9650 | keep | 0 | Aug | 2022 | 0.0065726 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
CANOVANAS | 2022-08-17 09:07 | 2022-08-17 15:12 | 8 | 6:05 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | R22081700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 365 | 2022-08-17 | 2920 | keep | 0 | Aug | 2022 | 0.0019888 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
MAYAGÃœEZ | 2022-08-17 09:13 | 2022-08-17 12:00 | 6 | 2:47 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700042 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 167 | 2022-08-17 | 1002 | keep | 0 | Aug | 2022 | 0.00068246 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BARRANQUITAS | 2022-08-17 09:14 | 2022-08-17 09:15 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081700038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 1017 | keep | 0 | Aug | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | TMED_Event | 1017
BARRANQUITAS | 2022-08-17 09:15 | 2022-08-17 12:09 | 7 | 2:54 | P | CONDUCTOR ROTO O ABIERTO | SE RELOCALIZO SECUNDARIA Y SE REPARO PUENTE PRIMARIO | C22081700037 | New_Event | Primary Wire Break | Include | Include | Equipment | 174 | 2022-08-17 | 1218 | keep | 0 | Aug | 2022 | 0.00082957 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
CANOVANAS | 2022-08-17 09:16 | 2022-08-17 11:10 | 150 | 1:54 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | R22081700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-08-17 | 17100 | keep | 0 | Aug | 2022 | 0.011647 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
VEGA BAJA | 2022-08-17 09:18 | 2022-08-17 10:35 | 10 | 1:17 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA POR RAYOS | A22081700073 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 77 | 2022-08-17 | 770 | keep | 0 | Aug | 2022 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
UTUADO | 2022-08-17 09:21 | 2022-08-17 16:19 | 70 | 6:58 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA Y 4 X 15 EN TRANSFORMADORES POR ARBOL SOBRE LINEAS | A22081700082 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 418 | 2022-08-17 | 29260 | keep | 0 | Aug | 2022 | 0.019929 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
SAN JUAN | 2022-08-17 09:22 | 2022-08-17 15:55 | 120 | 6:33 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | S22081700134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2022-08-17 | 47160 | keep | 0 | Aug | 2022 | 0.03212 | 8.1731e-05 | Sustained | FALSE | FALSE | TMED_Event | 120
MAYAGÃœEZ | 2022-08-17 09:33 | 2022-08-17 12:30 | 60 | 2:57 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700045 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 177 | 2022-08-17 | 10620 | keep | 0 | Aug | 2022 | 0.0072332 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
CANOVANAS | 2022-08-17 09:40 | 2022-08-17 13:24 | 30 | 3:44 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | R22081700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2022-08-17 | 6720 | keep | 0 | Aug | 2022 | 0.004577 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
ARECIBO | 2022-08-17 09:43 | 2022-08-17 10:43 | 80 | 1:00 | P | CAUSAS EXTERNAS | 1 X 100 EN CORTE DE LINEA POR PERSONAL DE MUNICIPIO DESGANCHANDO | A22081700087 | New_Event | Damage From Public | Include | Include | Public | 60 | 2022-08-17 | 4800 | keep | 0 | Aug | 2022 | 0.0032693 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
AGUADILLA | 2022-08-17 09:46 | 2022-08-17 14:14 | 75 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22081700049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2022-08-17 | 20100 | keep | 0 | Aug | 2022 | 0.01369 | 5.1082e-05 | Sustained | FALSE | FALSE | TMED_Event | 75
ARECIBO | 2022-08-17 09:47 | 2022-08-17 11:54 | 20 | 2:07 | P | DESGANCHE | 1 X 25 Y 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE DE PALMA | A22081700090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-08-17 | 2540 | keep | 0 | Aug | 2022 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
BAYAMON | 2022-08-17 09:50 | 2022-08-17 10:45 | 2861 | 0:55 | T | DESGANCHE | SE CERRO INTERRUPTOR SECCIONALIZANDO PARA REALIZAR DESGANCHE. EN SERVICIO 60% | B22081700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-08-17 | 157355 | keep | 0 | Aug | 2022 | 0.10717 | 0.0019486 | Sustained | FALSE | FALSE | TMED_Event | 2861
BAYAMON | 2022-08-17 10:04 | 2022-08-17 10:06 | 723 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-17 | 1446 | keep | 0 | Aug | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | TMED_Event | 723
BAYAMON | 2022-08-17 10:04 | 2022-08-17 10:06 | 1976 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 | B22081700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-17 | 3952 | keep | 0 | Aug | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | TMED_Event | 1976
AGUADILLA | 2022-08-17 10:06 | 2022-08-17 17:45 | 40 | 7:39 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700052 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 459 | 2022-08-17 | 18360 | keep | 0 | Aug | 2022 | 0.012505 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
AGUADILLA | 2022-08-17 10:09 | 2022-08-17 11:10 | 40 | 1:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE RETRIRO RAMA DE LAS LINEAS Y SE REMPLAZO UNA CAJA PRIMARIA EN CORTE DE LINEA | M22081700053 | New_Event | Cutout Failure | Include | Include | Equipment | 61 | 2022-08-17 | 2440 | keep | 0 | Aug | 2022 | 0.0016619 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
PONCE | 2022-08-17 10:10 | 2022-08-17 10:31 | 5 | 0:21 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN MONTURA TRIFASICA PROBLEMA CLIENTE | P22081700051 | New_Event | Customer-Related Interruption | Include | Include | Public | 21 | 2022-08-17 | 105 | keep | 0 | Aug | 2022 | 7.1515e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
SAN JUAN | 2022-08-17 10:11 | 2022-08-17 12:49 | 100 | 2:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | S22081700156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 158 | 2022-08-17 | 15800 | keep | 0 | Aug | 2022 | 0.010761 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
MAYAGÃœEZ | 2022-08-17 10:15 | 2022-08-17 12:40 | 8 | 2:25 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700056 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 145 | 2022-08-17 | 1160 | keep | 0 | Aug | 2022 | 0.00079007 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
MAYAGÃœEZ | 2022-08-17 10:17 | 2022-08-17 13:25 | 4 | 3:08 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700057 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 188 | 2022-08-17 | 752 | keep | 0 | Aug | 2022 | 0.00051218 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
VEGA BAJA | 2022-08-17 10:17 | 2022-08-17 11:40 | 10 | 1:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5KVA | A22081700101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 83 | 2022-08-17 | 830 | keep | 0 | Aug | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CANOVANAS | 2022-08-17 10:20 | 2022-08-17 14:45 | 22 | 4:25 | P | DESGANCHE | 1X40 EN Y 1X20 EN C/L DE OTRO TAP | R22081700038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2022-08-17 | 5830 | keep | 0 | Aug | 2022 | 0.0039708 | 1.4984e-05 | Sustained | FALSE | FALSE | TMED_Event | 22
MAYAGÃœEZ | 2022-08-17 10:23 | 2022-08-17 12:00 | 40 | 1:37 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700058 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 97 | 2022-08-17 | 3880 | keep | 0 | Aug | 2022 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
MAYAGÃœEZ | 2022-08-17 10:40 | 2022-08-17 16:55 | 20 | 6:15 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | M22081700060 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 375 | 2022-08-17 | 7500 | keep | 0 | Aug | 2022 | 0.0051082 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
BAYAMON | 2022-08-17 10:45 | 2022-08-17 12:46 | 1144 | 2:01 | P | DESGANCHE | SE REALIZO DESGANCHE EN TRONCAL Y SE CERRO MACHETES | B22081700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-08-17 | 138424 | keep | 0 | Aug | 2022 | 0.09428 | 0.00077917 | Sustained | FALSE | FALSE | TMED_Event | 1144
SAN JUAN | 2022-08-17 10:48 | 2022-08-18 10:05 | 86 | 23:17 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S22081700174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1397 | 2022-08-17 | 120142 | keep | 0 | Aug | 2022 | 0.081828 | 5.8574e-05 | Sustained | FALSE | FALSE | TMED_Event | 86
AGUADILLA | 2022-08-17 10:59 | 2022-08-17 18:30 | 80 | 7:31 | P | PARARRAYOS DEFECTUOSO | 3 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE DESCONECTO PARARRAYOS AVERIADO | M22081700061 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 451 | 2022-08-17 | 36080 | keep | 0 | Aug | 2022 | 0.024574 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
SAN JUAN | 2022-08-17 11:04 | 2022-08-17 17:00 | 15 | 5:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S22081700178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 356 | 2022-08-17 | 5340 | keep | 0 | Aug | 2022 | 0.003637 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
AGUADILLA | 2022-08-17 11:04 | 2022-08-18 10:26 | 3 | 23:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA POR UNO DE 37.5KVA | M22081700065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1402 | 2022-08-17 | 4206 | keep | 0 | Aug | 2022 | 0.0028647 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
AGUADILLA | 2022-08-17 11:11 | 2022-08-17 11:50 | 60 | 0:39 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700066 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 39 | 2022-08-17 | 2340 | keep | 0 | Aug | 2022 | 0.0015938 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
CANOVANAS | 2022-08-17 11:15 | 2022-08-17 13:04 | 3464 | 1:49 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SUB LOCK OUT. CAMARA INTERNA AVERIADA DEL 2404-05 SE TRANSFIRIO AL 2404-08 | R22081700111 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 109 | 2022-08-17 | 377576 | keep | 0 | Aug | 2022 | 0.25717 | 0.0023593 | Sustained | FALSE | FALSE | TMED_Event | 3464
CANOVANAS | 2022-08-17 11:15 | 2022-08-17 13:03 | 7621 | 1:48 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SUB LOCK OUT. CAMARA INTERNA AVERIADA DEL 2404-05 SE REMONTO LOCKOUT Y SE CERRO INTERRUPTOR | R22081700111 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 108 | 2022-08-17 | 823068 | keep | 0 | Aug | 2022 | 0.56059 | 0.0051906 | Sustained | FALSE | FALSE | TMED_Event | 7621
CANOVANAS | 2022-08-17 11:15 | 2022-08-17 13:04 | 2675 | 1:49 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SUB LOCK OUT. CAMARA INTERNA AVERIADA DEL 2404-05 SE REMONTO LOCKOUT Y SE CERRO INTERRUPTOR CON LA CARGA DEL 2404-05 A TRAVES DE LA B/I | R22081700111 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 109 | 2022-08-17 | 291575 | keep | 0 | Aug | 2022 | 0.19859 | 0.0018219 | Sustained | FALSE | FALSE | TMED_Event | 2675
CAGUAS | 2022-08-17 11:17 | 2022-08-17 15:35 | 12 | 4:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CONSTRUYO PROVICIONAL AEREO SECUNDARIO | C22081500030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 258 | 2022-08-17 | 3096 | keep | 0 | Aug | 2022 | 0.0021087 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
BAYAMON | 2022-08-17 11:18 | 2022-08-17 12:15 | 50 | 0:57 | P | DESGANCHE | DESGANCHE PRIMARIO 1 X 15 EN XMR Y 1 X 40 EN C/L | B22081700036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-08-17 | 2850 | keep | 0 | Aug | 2022 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BAYAMON | 2022-08-17 11:18 | 2022-08-17 14:40 | 60 | 3:22 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22081600439 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-08-17 | 12120 | keep | 0 | Aug | 2022 | 0.0082549 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
BAYAMON | 2022-08-17 11:19 | 2022-08-17 15:35 | 158 | 4:16 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | S22081600303 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-08-17 | 40448 | keep | 0 | Aug | 2022 | 0.027549 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-08-17 11:19 | 2022-08-17 14:33 | 8 | 3:14 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | S22081601297 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-08-17 | 1552 | keep | 0 | Aug | 2022 | 0.0010571 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-08-17 11:19 | 2022-08-17 12:38 | 150 | 1:19 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTE DE LINEA DESGANCHE | S22081601098 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-08-17 | 11850 | keep | 0 | Aug | 2022 | 0.008071 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-08-17 11:19 | 2022-08-17 14:29 | 146 | 3:10 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE HIZO DESGANCHE | S22081601367 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-08-17 | 27740 | keep | 0 | Aug | 2022 | 0.018894 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
SAN JUAN | 2022-08-17 11:19 | 2022-08-17 12:44 | 40 | 1:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081601358 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-17 | 3400 | keep | 0 | Aug | 2022 | 0.0023157 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2022-08-17 11:29 | 2022-08-17 12:08 | 8 | 0:39 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR SECUNDARIA IMPACTO DE CAMION EXTERNO | C22081700032 | New_Event | Damage From Public | Include | Include | Public | 39 | 2022-08-17 | 312 | keep | 0 | Aug | 2022 | 0.0002125 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
BARRANQUITAS | 2022-08-17 11:30 | 2022-08-17 21:05 | 1 | 9:35 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L RAYOS | C22081700097 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 575 | 2022-08-17 | 575 | keep | 0 | Aug | 2022 | 0.00039163 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:05 | 5809 | 1:25 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700120 | New_Event |  |  |  |  | 85 | 2022-08-17 | 493765 | keep | 0 | Aug | 2022 | 0.3363 | 0.0039565 | Sustained | FALSE | FALSE | TMED_Event | 5809
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:05 | 3941 | 1:25 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700120 | New_Event |  |  |  |  | 85 | 2022-08-17 | 334985 | keep | 0 | Aug | 2022 | 0.22816 | 0.0026842 | Sustained | FALSE | FALSE | TMED_Event | 3941
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:05 | 3871 | 1:25 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700120 | New_Event |  |  |  |  | 85 | 2022-08-17 | 329035 | keep | 0 | Aug | 2022 | 0.2241 | 0.0026365 | Sustained | FALSE | FALSE | TMED_Event | 3871
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:05 | 5191 | 1:25 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700120 | New_Event |  |  |  |  | 85 | 2022-08-17 | 441235 | keep | 0 | Aug | 2022 | 0.30052 | 0.0035356 | Sustained | FALSE | FALSE | TMED_Event | 5191
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:03 | 1210 | 1:23 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700123 | New_Event |  |  |  |  | 83 | 2022-08-17 | 100430 | keep | 0 | Aug | 2022 | 0.068402 | 0.00082413 | Sustained | FALSE | FALSE | TMED_Event | 1210
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:03 | 3438 | 1:23 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700123 | New_Event |  |  |  |  | 83 | 2022-08-17 | 285354 | keep | 0 | Aug | 2022 | 0.19435 | 0.0023416 | Sustained | FALSE | FALSE | TMED_Event | 3438
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:03 | 2605 | 1:23 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700123 | New_Event |  |  |  |  | 83 | 2022-08-17 | 216215 | keep | 0 | Aug | 2022 | 0.14726 | 0.0017743 | Sustained | FALSE | FALSE | TMED_Event | 2605
BAYAMON | 2022-08-17 11:40 | 2022-08-17 13:03 | 73 | 1:23 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700123 | New_Event |  |  |  |  | 83 | 2022-08-17 | 6059 | keep | 0 | Aug | 2022 | 0.0041268 | 4.972e-05 | Sustained | FALSE | FALSE | TMED_Event | 73
BAYAMON | 2022-08-17 11:40 | 2022-08-17 16:29 | 222 | 4:49 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1907-03 LLEVA CARGA 1909-09 | S22081700244 | New_Event |  |  |  |  | 289 | 2022-08-17 | 64158 | keep | 0 | Aug | 2022 | 0.043698 | 0.0001512 | Sustained | FALSE | FALSE | TMED_Event | 222
BAYAMON | 2022-08-17 11:40 | 2022-08-17 15:17 | 2466 | 3:37 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | S22081700244 | New_Event |  |  |  |  | 217 | 2022-08-17 | 535122 | keep | 0 | Aug | 2022 | 0.36447 | 0.0016796 | Sustained | FALSE | FALSE | TMED_Event | 2466
BAYAMON | 2022-08-17 11:40 | 2022-08-17 16:29 | 4456 | 4:49 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1907-03 LLEVA CARGA 1909-09 | S22081700244 | New_Event |  |  |  |  | 289 | 2022-08-17 | 1287784 | keep | 0 | Aug | 2022 | 0.8771 | 0.003035 | Sustained | FALSE | FALSE | TMED_Event | 4456
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 15:45 | 2791 | 4:05 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO LINEA 50300 | A22070100140 | New_Event |  |  |  |  | 245 | 2022-08-17 | 683795 | keep | 0 | Aug | 2022 | 0.46573 | 0.0019009 | Sustained | FALSE | FALSE | TMED_Event | 2791
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 15:45 | 1464 | 4:05 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO LINEA 50300 | A22070100140 | New_Event |  |  |  |  | 245 | 2022-08-17 | 358680 | keep | 0 | Aug | 2022 | 0.2443 | 0.00099712 | Sustained | FALSE | FALSE | TMED_Event | 1464
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 15:45 | 759 | 4:05 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO LINEA 50300 | A22070100140 | New_Event |  |  |  |  | 245 | 2022-08-17 | 185955 | keep | 0 | Aug | 2022 | 0.12665 | 0.00051695 | Sustained | FALSE | FALSE | TMED_Event | 759
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 15:45 | 1500 | 4:05 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO LINEA 50300 | A22070100140 | New_Event |  |  |  |  | 245 | 2022-08-17 | 367500 | keep | 0 | Aug | 2022 | 0.2503 | 0.0010216 | Sustained | FALSE | FALSE | TMED_Event | 1500
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 12:10 | 2132 | 0:30 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO DE LINEA 50300 | A22081700141 | New_Event |  |  |  |  | 30 | 2022-08-17 | 63960 | keep | 0 | Aug | 2022 | 0.043563 | 0.0014521 | Sustained | FALSE | FALSE | TMED_Event | 2132
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 12:10 | 2366 | 0:30 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO DE LINEA 50300 | A22081700141 | New_Event |  |  |  |  | 30 | 2022-08-17 | 70980 | keep | 0 | Aug | 2022 | 0.048344 | 0.0016115 | Sustained | FALSE | FALSE | TMED_Event | 2366
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 12:10 | 1976 | 0:30 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO DE LINEA 50300 | A22081700141 | New_Event |  |  |  |  | 30 | 2022-08-17 | 59280 | keep | 0 | Aug | 2022 | 0.040375 | 0.0013458 | Sustained | FALSE | FALSE | TMED_Event | 1976
VEGA BAJA | 2022-08-17 11:40 | 2022-08-17 12:10 | 3688 | 0:30 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | DISPARO DE LINEA 50300 | A22081700141 | New_Event |  |  |  |  | 30 | 2022-08-17 | 110640 | keep | 0 | Aug | 2022 | 0.075356 | 0.0025119 | Sustained | FALSE | FALSE | TMED_Event | 3688
BAYAMON | 2022-08-17 11:40 | 2022-08-17 15:49 | 3070 | 4:09 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700073 | New_Event |  |  |  |  | 249 | 2022-08-17 | 764430 | keep | 0 | Aug | 2022 | 0.52065 | 0.002091 | Sustained | FALSE | FALSE | TMED_Event | 3070
BAYAMON | 2022-08-17 11:40 | 2022-08-17 16:25 | 2735 | 4:45 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700073 | New_Event |  |  |  |  | 285 | 2022-08-17 | 779475 | keep | 0 | Aug | 2022 | 0.5309 | 0.0018628 | Sustained | FALSE | FALSE | TMED_Event | 2735
BAYAMON | 2022-08-17 11:40 | 2022-08-17 16:25 | 1070 | 4:45 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700073 | New_Event |  |  |  |  | 285 | 2022-08-17 | 304950 | keep | 0 | Aug | 2022 | 0.2077 | 0.00072877 | Sustained | FALSE | FALSE | TMED_Event | 1070
BAYAMON | 2022-08-17 11:40 | 2022-08-17 15:36 | 1647 | 3:56 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700075 | New_Event |  |  |  |  | 236 | 2022-08-17 | 388692 | keep | 0 | Aug | 2022 | 0.26474 | 0.0011218 | Sustained | FALSE | FALSE | TMED_Event | 1647
BAYAMON | 2022-08-17 11:40 | 2022-08-17 15:36 | 3295 | 3:56 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700075 | New_Event |  |  |  |  | 236 | 2022-08-17 | 777620 | keep | 0 | Aug | 2022 | 0.52963 | 0.0022442 | Sustained | FALSE | FALSE | TMED_Event | 3295
BAYAMON | 2022-08-17 11:40 | 2022-08-17 16:25 | 1180 | 4:45 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700075 | New_Event |  |  |  |  | 285 | 2022-08-17 | 336300 | keep | 0 | Aug | 2022 | 0.22905 | 0.00080369 | Sustained | FALSE | FALSE | TMED_Event | 1180
BAYAMON | 2022-08-17 11:40 | 2022-08-17 15:36 | 320 | 3:56 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700076 | New_Event |  |  |  |  | 236 | 2022-08-17 | 75520 | keep | 0 | Aug | 2022 | 0.051436 | 0.00021795 | Sustained | FALSE | FALSE | TMED_Event | 320
BAYAMON | 2022-08-17 11:40 | 2022-08-17 16:25 | 2234 | 4:45 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700076 | New_Event |  |  |  |  | 285 | 2022-08-17 | 636690 | keep | 0 | Aug | 2022 | 0.43365 | 0.0015216 | Sustained | FALSE | FALSE | TMED_Event | 2234
FAJARDO | 2022-08-17 11:45 | 2022-08-17 15:15 | 25 | 3:30 | P | DESGANCHE | 1X40 EN C/L Y 1X15 EN XMR | R22081700097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-08-17 | 5250 | keep | 0 | Aug | 2022 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
AGUADILLA | 2022-08-17 12:04 | 2022-08-17 14:50 | 40 | 2:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE RETRIRO RAMA DE LAS LINEAS Y SE REMPLAZO UNA CAJA PRIMARIA EN CORTE DE LINEA | M22081700053 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 166 | 2022-08-17 | 6640 | keep | 0 | Aug | 2022 | 0.0045225 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CANOVANAS | 2022-08-17 12:08 | 2022-08-17 14:24 | 60 | 2:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L SE REMPLAZO CAJA PRIMARIA | R22081700115 | New_Event | Cutout Failure | Include | Include | Equipment | 136 | 2022-08-17 | 8160 | keep | 0 | Aug | 2022 | 0.0055577 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
BAYAMON | 2022-08-17 12:14 | 2022-08-17 12:17 | 2617 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22081700128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-17 | 7851 | keep | 0 | Aug | 2022 | 0.0053473 | 0.0017824 | Momentary | FALSE | FALSE | TMED_Event | 2617
AGUADILLA | 2022-08-17 12:19 | 2022-08-17 15:34 | 5 | 3:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | M22081700095 | New_Event | Cutout Failure | Include | Include | Equipment | 195 | 2022-08-17 | 975 | keep | 0 | Aug | 2022 | 0.00066407 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
AGUADILLA | 2022-08-17 12:27 | 2022-08-17 20:00 | 15 | 7:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TRANSFORMADOR AVERIADO DE 50KVA X 75KVA | M22081700200 | New_Event | Service Transformer Failure | Include | Include | Equipment | 453 | 2022-08-17 | 6795 | keep | 0 | Aug | 2022 | 0.004628 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
ARECIBO | 2022-08-17 12:29 | 2022-08-17 17:31 | 40 | 5:02 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22081700161 | New_Event | Primary Wire Break | Include | Include | Equipment | 302 | 2022-08-17 | 12080 | keep | 0 | Aug | 2022 | 0.0082276 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
BAYAMON | 2022-08-17 12:35 | 2022-08-17 18:30 | 1715 | 5:55 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR Y SE LLEVO LINEA A AISLADOR(SE REMPLAZO LIGADURA) SE CERRO INTERRUPTOR | B22081700158 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 355 | 2022-08-17 | 608825 | keep | 0 | Aug | 2022 | 0.41467 | 0.0011681 | Sustained | FALSE | FALSE | TMED_Event | 1715
BAYAMON | 2022-08-17 12:35 | 2022-08-17 18:30 | 1498 | 5:55 | T | CONDUCTOR ARRIADO O CRUZADO | SE SECCIONALIZO ALIMENTADOR PARA LLEVAR LINEA A AISLADOR (SE REMPLAZO LIGADURA) Y SE CERRO INTERRUPTOR | B22081700158 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 355 | 2022-08-17 | 531790 | keep | 0 | Aug | 2022 | 0.3622 | 0.0010203 | Sustained | FALSE | FALSE | TMED_Event | 1498
BAYAMON | 2022-08-17 12:39 | 2022-08-17 18:41 | 2617 | 6:02 | T | DESGANCHE | SE SECCIONALZIO ALIMENTADOR | B22081700158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-08-17 | 947354 | keep | 0 | Aug | 2022 | 0.64524 | 0.0017824 | Sustained | FALSE | FALSE | TMED_Event | 2617
CAGUAS | 2022-08-17 12:41 | 2022-08-17 12:43 | 2900 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22081700137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-17 | 5800 | keep | 0 | Aug | 2022 | 0.0039504 | 0.0019752 | Momentary | FALSE | FALSE | TMED_Event | 2900
FAJARDO | 2022-08-17 12:42 | 2022-08-17 13:53 | 16 | 1:11 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR PALOMA | R22081700146 | New_Event | Animals | Include | Include | Wildlife | 71 | 2022-08-17 | 1136 | keep | 0 | Aug | 2022 | 0.00077372 | 1.0898e-05 | Sustained | FALSE | FALSE | TMED_Event | 16
CANOVANAS | 2022-08-17 13:03 | 2022-08-17 18:41 | 150 | 5:38 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | R22081700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2022-08-17 | 50700 | keep | 0 | Aug | 2022 | 0.034532 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
CAGUAS | 2022-08-17 13:05 | 2022-08-17 14:16 | 1 | 1:11 | P | MAL TIEMPO/RAYOS | 1 X 15 EN BANCO DE XMRS RAYOS | C22081700149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 71 | 2022-08-17 | 71 | keep | 0 | Aug | 2022 | 4.8358e-05 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-08-17 13:08 | 2022-08-17 17:00 | 2402 | 3:52 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 LLEVA LA CARGA DEL 1720-08 | S22081700170 | New_Event |  |  |  |  | 232 | 2022-08-17 | 557264 | keep | 0 | Aug | 2022 | 0.37955 | 0.001636 | Sustained | FALSE | FALSE | TMED_Event | 2402
BAYAMON | 2022-08-17 13:08 | 2022-08-17 15:35 | 766 | 2:27 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1709-03 LLEVA CARGA 1709-05 Y 50% DE SU CARGA POR 1909-07 | S22081700170 | New_Event |  |  |  |  | 147 | 2022-08-17 | 112602 | keep | 0 | Aug | 2022 | 0.076693 | 0.00052172 | Sustained | FALSE | FALSE | TMED_Event | 766
BAYAMON | 2022-08-17 13:08 | 2022-08-17 15:35 | 2364 | 2:27 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1709-03 LLEVA CARGA 1709-05 | S22081700170 | New_Event |  |  |  |  | 147 | 2022-08-17 | 347508 | keep | 0 | Aug | 2022 | 0.23669 | 0.0016101 | Sustained | FALSE | FALSE | TMED_Event | 2364
BAYAMON | 2022-08-17 13:08 | 2022-08-17 14:36 | 3626 | 1:28 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 20% POR EL 1801-02 | B22081700174 | New_Event |  |  |  |  | 88 | 2022-08-17 | 319088 | keep | 0 | Aug | 2022 | 0.21733 | 0.0024697 | Sustained | FALSE | FALSE | TMED_Event | 3626
BAYAMON | 2022-08-17 13:08 | 2022-08-17 18:27 | 45 | 5:19 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 95% DE LA CARGA ESTA POR EL 1713-05 | B22081700174 | New_Event |  |  |  |  | 319 | 2022-08-17 | 14355 | keep | 0 | Aug | 2022 | 0.0097771 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
BAYAMON | 2022-08-17 13:08 | 2022-08-17 14:36 | 4431 | 1:28 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700174 | New_Event |  |  |  |  | 88 | 2022-08-17 | 389928 | keep | 0 | Aug | 2022 | 0.26558 | 0.0030179 | Sustained | FALSE | FALSE | TMED_Event | 4431
BAYAMON | 2022-08-17 13:08 | 2022-08-17 14:36 | 1362 | 1:28 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700174 | New_Event |  |  |  |  | 88 | 2022-08-17 | 119856 | keep | 0 | Aug | 2022 | 0.081633 | 0.00092765 | Sustained | FALSE | FALSE | TMED_Event | 1362
BAYAMON | 2022-08-17 13:08 | 2022-08-17 18:28 | 341 | 5:20 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700174 | New_Event |  |  |  |  | 320 | 2022-08-17 | 109120 | keep | 0 | Aug | 2022 | 0.074321 | 0.00023225 | Sustained | FALSE | FALSE | TMED_Event | 341
BAYAMON | 2022-08-17 13:08 | 2022-08-17 17:00 | 1 | 3:52 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 CARGA POR EL 1709-02 | S22081700170 | New_Event |  |  |  |  | 232 | 2022-08-17 | 232 | keep | 0 | Aug | 2022 | 0.00015801 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
MAYAGÃœEZ | 2022-08-17 13:08 | 2022-08-17 14:22 | 199 | 1:14 | T | DESGANCHE | SE RETIRO RAMAS DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M22081700106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-08-17 | 14726 | keep | 0 | Aug | 2022 | 0.01003 | 0.00013554 | Sustained | FALSE | FALSE | TMED_Event | 199
BAYAMON | 2022-08-17 13:09 | 2022-08-17 15:37 | 766 | 2:28 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1909-07 LLEVA 50% 1709-03 | S22081700302 | New_Event |  |  |  |  | 148 | 2022-08-17 | 113368 | keep | 0 | Aug | 2022 | 0.077214 | 0.00052172 | Sustained | FALSE | FALSE | TMED_Event | 766
BAYAMON | 2022-08-17 13:09 | 2022-08-17 15:50 | 2435 | 2:41 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1909-08 LLEVA CARGA 1907-05 | S22081700302 | New_Event |  |  |  |  | 161 | 2022-08-17 | 392035 | keep | 0 | Aug | 2022 | 0.26701 | 0.0016585 | Sustained | FALSE | FALSE | TMED_Event | 2435
BAYAMON | 2022-08-17 13:09 | 2022-08-17 15:37 | 1139 | 2:28 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1909-07 LLEVA 50% 1709-03 | S22081700302 | New_Event |  |  |  |  | 148 | 2022-08-17 | 168572 | keep | 0 | Aug | 2022 | 0.11481 | 0.00077577 | Sustained | FALSE | FALSE | TMED_Event | 1139
BAYAMON | 2022-08-17 13:09 | 2022-08-17 15:50 | 2956 | 2:41 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 1909-08 LLEVA CARGA 1907-05 | S22081700302 | New_Event |  |  |  |  | 161 | 2022-08-17 | 475916 | keep | 0 | Aug | 2022 | 0.32414 | 0.0020133 | Sustained | FALSE | FALSE | TMED_Event | 2956
BAYAMON | 2022-08-17 13:10 | 2022-08-17 15:38 | 1526 | 2:28 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700175 | New_Event |  |  |  |  | 148 | 2022-08-17 | 225848 | keep | 0 | Aug | 2022 | 0.15382 | 0.0010394 | Sustained | FALSE | FALSE | TMED_Event | 1526
BAYAMON | 2022-08-17 13:10 | 2022-08-17 15:26 | 308 | 2:16 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 LLEVA PARTE DEL 9202-03 | B22081700175 | New_Event |  |  |  |  | 136 | 2022-08-17 | 41888 | keep | 0 | Aug | 2022 | 0.02853 | 0.00020978 | Sustained | FALSE | FALSE | TMED_Event | 308
BAYAMON | 2022-08-17 13:10 | 2022-08-17 15:26 | 1159 | 2:16 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 17% DE SU CARGA POR EL 9202-02 Y LLEVA PARTE DEL 9201-01 | B22081700175 | New_Event |  |  |  |  | 136 | 2022-08-17 | 157624 | keep | 0 | Aug | 2022 | 0.10736 | 0.00078939 | Sustained | FALSE | FALSE | TMED_Event | 1159
BAYAMON | 2022-08-17 13:10 | 2022-08-17 18:02 | 2926 | 4:52 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 LLEVA 50% DEL 9201-04 | B22081700175 | New_Event |  |  |  |  | 292 | 2022-08-17 | 854392 | keep | 0 | Aug | 2022 | 0.58192 | 0.0019929 | Sustained | FALSE | FALSE | TMED_Event | 2926
BAYAMON | 2022-08-17 13:10 | 2022-08-17 16:36 | 27 | 3:26 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 9206-08 LLEVA 9206-09 | B22081700183 | New_Event |  |  |  |  | 206 | 2022-08-17 | 5562 | keep | 0 | Aug | 2022 | 0.0037883 | 1.839e-05 | Sustained | FALSE | FALSE | TMED_Event | 27
BAYAMON | 2022-08-17 13:10 | 2022-08-17 15:38 | 603 | 2:28 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 9206-08 LLEVA 9206-09 | B22081700183 | New_Event |  |  |  |  | 148 | 2022-08-17 | 89244 | keep | 0 | Aug | 2022 | 0.060784 | 0.0004107 | Sustained | FALSE | FALSE | TMED_Event | 603
BAYAMON | 2022-08-17 13:10 | 2022-08-17 15:38 | 6 | 2:28 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 9206-08 LLEVA 9206-09 | B22081700183 | New_Event |  |  |  |  | 148 | 2022-08-17 | 888 | keep | 0 | Aug | 2022 | 0.00060481 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
BAYAMON | 2022-08-17 13:10 | 2022-08-17 16:48 | 325 | 3:38 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700183 | New_Event |  |  |  |  | 218 | 2022-08-17 | 70850 | keep | 0 | Aug | 2022 | 0.048256 | 0.00022136 | Sustained | FALSE | FALSE | TMED_Event | 325
BAYAMON | 2022-08-17 13:10 | 2022-08-17 16:49 | 172 | 3:39 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 50300 | B22081700183 | New_Event |  |  |  |  | 219 | 2022-08-17 | 37668 | keep | 0 | Aug | 2022 | 0.025656 | 0.00011715 | Sustained | FALSE | FALSE | TMED_Event | 172
SAN JUAN | 2022-08-17 13:11 | 2022-08-17 16:31 | 8679 | 3:20 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 LLEVA 85% DEL 1204-05 | S22081700000 | New_Event |  |  |  |  | 200 | 2022-08-17 | 1735800 | keep | 0 | Aug | 2022 | 1.1822 | 0.0059112 | Sustained | FALSE | FALSE | TMED_Event | 8679
SAN JUAN | 2022-08-17 13:11 | 2022-08-17 16:31 | 3719 | 3:20 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 LLEVA 85% DEL 1204-05 | S22081700000 | New_Event |  |  |  |  | 200 | 2022-08-17 | 743800 | keep | 0 | Aug | 2022 | 0.5066 | 0.002533 | Sustained | FALSE | FALSE | TMED_Event | 3719
SAN JUAN | 2022-08-17 13:11 | 2022-08-17 16:31 | 5619 | 3:20 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 90% POR 1620-03 | S22081700305 | New_Event |  |  |  |  | 200 | 2022-08-17 | 1123800 | keep | 0 | Aug | 2022 | 0.76542 | 0.0038271 | Sustained | FALSE | FALSE | TMED_Event | 5619
SAN JUAN | 2022-08-17 13:11 | 2022-08-17 16:31 | 36 | 3:20 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 SU CARGA POR 1620-03 | S22081700305 | New_Event |  |  |  |  | 200 | 2022-08-17 | 7200 | keep | 0 | Aug | 2022 | 0.0049039 | 2.4519e-05 | Sustained | FALSE | FALSE | TMED_Event | 36
SAN JUAN | 2022-08-17 13:11 | 2022-08-17 18:24 | 3718 | 5:13 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 | S22081700305 | New_Event |  |  |  |  | 313 | 2022-08-17 | 1163734 | keep | 0 | Aug | 2022 | 0.79261 | 0.0025323 | Sustained | FALSE | FALSE | TMED_Event | 3718
SAN JUAN | 2022-08-17 13:11 | 2022-08-17 16:31 | 1073 | 3:20 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 LLEVA 1620-01 Y 90% DEL 1336-07 | S22081700305 | New_Event |  |  |  |  | 200 | 2022-08-17 | 214600 | keep | 0 | Aug | 2022 | 0.14616 | 0.00073082 | Sustained | FALSE | FALSE | TMED_Event | 1073
CANOVANAS | 2022-08-17 13:11 | 2022-08-17 18:24 | 172 | 5:13 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 | S22081700305 | New_Event |  |  |  |  | 313 | 2022-08-17 | 53836 | keep | 0 | Aug | 2022 | 0.036667 | 0.00011715 | Sustained | FALSE | FALSE | TMED_Event | 172
CANOVANAS | 2022-08-17 13:11 | 2022-08-17 18:24 | 1615 | 5:13 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 | S22081700305 | New_Event |  |  |  |  | 313 | 2022-08-17 | 505495 | keep | 0 | Aug | 2022 | 0.34429 | 0.0011 | Sustained | FALSE | FALSE | TMED_Event | 1615
SAN JUAN | 2022-08-17 13:12 | 2022-08-17 18:23 | 3 | 5:11 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA EN LINEA 50300 | S22081700303 | New_Event |  |  |  |  | 311 | 2022-08-17 | 933 | keep | 0 | Aug | 2022 | 0.00063546 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
SAN JUAN | 2022-08-17 13:12 | 2022-08-17 18:23 | 3957 | 5:11 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA EN LINEA 50300 | S22081700303 | New_Event |  |  |  |  | 311 | 2022-08-17 | 1230627 | keep | 0 | Aug | 2022 | 0.83817 | 0.0026951 | Sustained | FALSE | FALSE | TMED_Event | 3957
SAN JUAN | 2022-08-17 13:12 | 2022-08-17 15:39 | 386 | 2:27 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 | S22081700303 | New_Event |  |  |  |  | 147 | 2022-08-17 | 56742 | keep | 0 | Aug | 2022 | 0.038647 | 0.0002629 | Sustained | FALSE | FALSE | TMED_Event | 386
SAN JUAN | 2022-08-17 13:13 | 2022-08-17 15:53 | 1106 | 2:40 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 60% POR 1529-15 | S22081700304 | New_Event |  |  |  |  | 160 | 2022-08-17 | 176960 | keep | 0 | Aug | 2022 | 0.12053 | 0.00075329 | Sustained | FALSE | FALSE | TMED_Event | 1106
SAN JUAN | 2022-08-17 13:13 | 2022-08-17 15:53 | 74 | 2:40 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 SU CARGA POR 1529-11 | S22081700304 | New_Event |  |  |  |  | 160 | 2022-08-17 | 11840 | keep | 0 | Aug | 2022 | 0.0080642 | 5.0401e-05 | Sustained | FALSE | FALSE | TMED_Event | 74
SAN JUAN | 2022-08-17 13:13 | 2022-08-17 15:53 | 1370 | 2:40 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 LLEVA CARGA 1521-02 | S22081700304 | New_Event |  |  |  |  | 160 | 2022-08-17 | 219200 | keep | 0 | Aug | 2022 | 0.1493 | 0.0009331 | Sustained | FALSE | FALSE | TMED_Event | 1370
SAN JUAN | 2022-08-17 13:13 | 2022-08-17 15:25 | 1984 | 2:12 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 LLEVA 75% 1911-7 | S22081700304 | New_Event |  |  |  |  | 132 | 2022-08-17 | 261888 | keep | 0 | Aug | 2022 | 0.17837 | 0.0013513 | Sustained | FALSE | FALSE | TMED_Event | 1984
SAN JUAN | 2022-08-17 13:13 | 2022-08-17 14:08 | 199 | 0:55 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RESOBRE CARGA LINEA 50300 LLEVA 25% DEL 1911-07 | S22081700304 | New_Event |  |  |  |  | 55 | 2022-08-17 | 10945 | keep | 0 | Aug | 2022 | 0.0074546 | 0.00013554 | Sustained | FALSE | FALSE | TMED_Event | 199
SAN JUAN | 2022-08-17 13:13 | 2022-08-17 15:53 | 1802 | 2:40 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 LLEVA 60% DEL 1346-02 | S22081700304 | New_Event |  |  |  |  | 160 | 2022-08-17 | 288320 | keep | 0 | Aug | 2022 | 0.19637 | 0.0012273 | Sustained | FALSE | FALSE | TMED_Event | 1802
BAYAMON | 2022-08-17 13:13 | 2022-08-17 14:08 | 144 | 0:55 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRE CARGA LINEA 50300 | S22081700304 | New_Event |  |  |  |  | 55 | 2022-08-17 | 7920 | keep | 0 | Aug | 2022 | 0.0053943 | 9.8078e-05 | Sustained | FALSE | FALSE | TMED_Event | 144
BAYAMON | 2022-08-17 13:13 | 2022-08-17 15:25 | 433 | 2:12 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 75% POR 1529-12 | S22081700304 | New_Event |  |  |  |  | 132 | 2022-08-17 | 57156 | keep | 0 | Aug | 2022 | 0.038929 | 0.00029491 | Sustained | FALSE | FALSE | TMED_Event | 433
ARECIBO | 2022-08-17 13:13 | 2022-08-17 15:19 | 10 | 2:06 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | A22081700180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-17 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-08-17 13:14 | 2022-08-17 15:39 | 3597 | 2:25 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 503000 | B22081700170 | New_Event |  |  |  |  | 145 | 2022-08-17 | 521565 | keep | 0 | Aug | 2022 | 0.35524 | 0.0024499 | Sustained | FALSE | FALSE | TMED_Event | 3597
BAYAMON | 2022-08-17 13:14 | 2022-08-17 18:23 | 492 | 5:09 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 503000 | B22081700170 | New_Event |  |  |  |  | 309 | 2022-08-17 | 152028 | keep | 0 | Aug | 2022 | 0.10355 | 0.0003351 | Sustained | FALSE | FALSE | TMED_Event | 492
BAYAMON | 2022-08-17 13:14 | 2022-08-17 18:23 | 4028 | 5:09 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 503000 | B22081700170 | New_Event |  |  |  |  | 309 | 2022-08-17 | 1244652 | keep | 0 | Aug | 2022 | 0.84773 | 0.0027435 | Sustained | FALSE | FALSE | TMED_Event | 4028
CAGUAS | 2022-08-17 13:14 | 2022-08-17 15:58 | 25 | 2:44 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO Y REMPLAZO PIN POLE TOP | C22081700152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-08-17 | 4100 | keep | 0 | Aug | 2022 | 0.0027925 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
SAN JUAN | 2022-08-17 13:16 | 2022-08-17 15:55 | 828 | 2:39 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 60% POR 1206-04 | S22081700309 | New_Event |  |  |  |  | 159 | 2022-08-17 | 131652 | keep | 0 | Aug | 2022 | 0.089668 | 0.00056395 | Sustained | FALSE | FALSE | TMED_Event | 828
SAN JUAN | 2022-08-17 13:16 | 2022-08-17 15:55 | 1977 | 2:39 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 40% POR 1206-04 | S22081700309 | New_Event |  |  |  |  | 159 | 2022-08-17 | 314343 | keep | 0 | Aug | 2022 | 0.2141 | 0.0013465 | Sustained | FALSE | FALSE | TMED_Event | 1977
SAN JUAN | 2022-08-17 13:16 | 2022-08-17 18:23 | 338 | 5:07 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 | S22081700309 | New_Event |  |  |  |  | 307 | 2022-08-17 | 103766 | keep | 0 | Aug | 2022 | 0.070675 | 0.00023021 | Sustained | FALSE | FALSE | TMED_Event | 338
SAN JUAN | 2022-08-17 13:16 | 2022-08-17 18:23 | 733 | 5:07 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 SU CARGA POR 1206-1 | S22081700309 | New_Event |  |  |  |  | 307 | 2022-08-17 | 225031 | keep | 0 | Aug | 2022 | 0.15327 | 0.00049924 | Sustained | FALSE | FALSE | TMED_Event | 733
SAN JUAN | 2022-08-17 13:16 | 2022-08-17 15:55 | 1799 | 2:39 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 LLEVA 40% DEL 1204-4 60% DEL 1204-3 Y LLEVA 20% 1303-02 | S22081700309 | New_Event |  |  |  |  | 159 | 2022-08-17 | 286041 | keep | 0 | Aug | 2022 | 0.19482 | 0.0012253 | Sustained | FALSE | FALSE | TMED_Event | 1799
SAN JUAN | 2022-08-17 13:16 | 2022-08-17 15:55 | 487 | 2:39 | P | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 20% POR 1206-04 | S22081700309 | New_Event |  |  |  |  | 159 | 2022-08-17 | 77433 | keep | 0 | Aug | 2022 | 0.052739 | 0.00033169 | Sustained | FALSE | FALSE | TMED_Event | 487
AGUADILLA | 2022-08-17 13:20 | 2022-08-17 19:30 | 4 | 6:10 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700109 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 370 | 2022-08-17 | 1480 | keep | 0 | Aug | 2022 | 0.001008 | 2.7244e-06 | Sustained | FALSE | FALSE | TMED_Event | 4
GUAYAMA | 2022-08-17 13:23 | 2022-08-17 14:36 | 14 | 1:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON CONECCIONES SECUNDARIAS EN PEDESTAL | P22081700096 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2022-08-17 | 1022 | keep | 0 | Aug | 2022 | 0.00069608 | 9.5353e-06 | Sustained | FALSE | FALSE | TMED_Event | 14
CANOVANAS | 2022-08-17 13:24 | 2022-08-17 18:23 | 2039 | 4:59 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 | R22081700161 | New_Event |  |  |  |  | 299 | 2022-08-17 | 609661 | keep | 0 | Aug | 2022 | 0.41524 | 0.0013888 | Sustained | FALSE | FALSE | TMED_Event | 2039
CANOVANAS | 2022-08-17 13:24 | 2022-08-17 15:40 | 4188 | 2:16 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 | R22081700162 | New_Event |  |  |  |  | 136 | 2022-08-17 | 569568 | keep | 0 | Aug | 2022 | 0.38793 | 0.0028524 | Sustained | FALSE | FALSE | TMED_Event | 4188
CANOVANAS | 2022-08-17 13:24 | 2022-08-17 16:28 | 4085 | 3:04 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 | R22081700163 | New_Event |  |  |  |  | 184 | 2022-08-17 | 751640 | keep | 0 | Aug | 2022 | 0.51194 | 0.0027823 | Sustained | FALSE | FALSE | TMED_Event | 4085
CANOVANAS | 2022-08-17 13:24 | 2022-08-17 18:25 | 3699 | 5:01 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 CARGA POR EL 2402-04 | R22081700164 | New_Event |  |  |  |  | 301 | 2022-08-17 | 1113399 | keep | 0 | Aug | 2022 | 0.75833 | 0.0025194 | Sustained | FALSE | FALSE | TMED_Event | 3699
FAJARDO | 2022-08-17 13:40 | 2022-08-17 14:48 | 10 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN XMR | R22081700170 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2022-08-17 | 680 | keep | 0 | Aug | 2022 | 0.00046314 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BARRANQUITAS | 2022-08-17 13:50 | 2022-08-17 19:40 | 33 | 5:50 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22081700157 | New_Event | Animals | Include | Include | Wildlife | 350 | 2022-08-17 | 11550 | keep | 0 | Aug | 2022 | 0.0078667 | 2.2476e-05 | Sustained | FALSE | FALSE | TMED_Event | 33
BARRANQUITAS | 2022-08-17 13:53 | 2022-08-17 16:14 | 254 | 2:21 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L RAYO | C22081700159 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 141 | 2022-08-17 | 35814 | keep | 0 | Aug | 2022 | 0.024393 | 0.000173 | Sustained | FALSE | FALSE | TMED_Event | 254
BARRANQUITAS | 2022-08-17 13:59 | 2022-08-17 17:32 | 15 | 3:33 | P | TRANSFORMADOR AVERIADO | REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA X 37.5KVA | C22081700016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 213 | 2022-08-17 | 3195 | keep | 0 | Aug | 2022 | 0.0021761 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
CANOVANAS | 2022-08-17 14:00 | 2022-08-17 16:31 | 32 | 2:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22081700162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-08-17 | 4832 | keep | 0 | Aug | 2022 | 0.0032911 | 2.1795e-05 | Sustained | FALSE | FALSE | TMED_Event | 32
CAGUAS | 2022-08-17 14:03 | 2022-08-17 17:43 | 10 | 3:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR FUERTES LLUVIAS | C22081700165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 220 | 2022-08-17 | 2200 | keep | 0 | Aug | 2022 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
AGUADILLA | 2022-08-17 14:03 | 2022-08-17 16:23 | 50 | 2:20 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081700189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 140 | 2022-08-17 | 7000 | keep | 0 | Aug | 2022 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BARRANQUITAS | 2022-08-17 14:07 | 2022-08-17 14:08 | 1617 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | C22081700169 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-17 | 1617 | keep | 0 | Aug | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | TMED_Event | 1617
BARRANQUITAS | 2022-08-17 14:08 | 2022-08-17 17:06 | 100 | 2:58 | P | MAL TIEMPO/RAYOS | 3 X 50 EN C/L RAYOS | C22081700239 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 178 | 2022-08-17 | 17800 | keep | 0 | Aug | 2022 | 0.012123 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
YAUCO | 2022-08-17 14:12 | 2022-08-17 14:13 | 1268 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M22081700129 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 1268 | keep | 0 | Aug | 2022 | 0.00086363 | 0.00086363 | Momentary | FALSE | FALSE | TMED_Event | 1268
YAUCO | 2022-08-17 14:12 | 2022-08-17 14:13 | 2064 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M22081700129 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 2064 | keep | 0 | Aug | 2022 | 0.0014058 | 0.0014058 | Momentary | FALSE | FALSE | TMED_Event | 2064
YAUCO | 2022-08-17 14:12 | 2022-08-17 14:13 | 3036 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M22081700129 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 3036 | keep | 0 | Aug | 2022 | 0.0020678 | 0.0020678 | Momentary | FALSE | FALSE | TMED_Event | 3036
YAUCO | 2022-08-17 14:12 | 2022-08-17 14:13 | 2952 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1200 | M22081700129 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 2952 | keep | 0 | Aug | 2022 | 0.0020106 | 0.0020106 | Momentary | FALSE | FALSE | TMED_Event | 2952
AGUADILLA | 2022-08-17 14:13 | 2022-08-17 16:16 | 70 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700193 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-08-17 | 8610 | keep | 0 | Aug | 2022 | 0.0058642 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
CANOVANAS | 2022-08-17 14:15 | 2022-08-17 15:58 | 99 | 1:43 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 | R22081700194 | New_Event |  |  |  |  | 103 | 2022-08-17 | 10197 | keep | 0 | Aug | 2022 | 0.0069451 | 6.7428e-05 | Sustained | FALSE | FALSE | TMED_Event | 99
CANOVANAS | 2022-08-17 14:15 | 2022-08-17 16:32 | 31 | 2:17 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA LINEA 50300 | R22081700195 | New_Event |  |  |  |  | 137 | 2022-08-17 | 4247 | keep | 0 | Aug | 2022 | 0.0028926 | 2.1114e-05 | Sustained | FALSE | FALSE | TMED_Event | 31
CANOVANAS | 2022-08-17 14:15 | 2022-08-17 16:32 | 1474 | 2:17 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 | R22081700196 | New_Event |  |  |  |  | 137 | 2022-08-17 | 201938 | keep | 0 | Aug | 2022 | 0.13754 | 0.0010039 | Sustained | FALSE | FALSE | TMED_Event | 1474
CANOVANAS | 2022-08-17 14:15 | 2022-08-17 18:26 | 2053 | 4:11 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 | R22081700197 | New_Event |  |  |  |  | 251 | 2022-08-17 | 515303 | keep | 0 | Aug | 2022 | 0.35097 | 0.0013983 | Sustained | FALSE | FALSE | TMED_Event | 2053
CANOVANAS | 2022-08-17 14:15 | 2022-08-17 18:26 | 61 | 4:11 | S | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SOBRECARGA L-50300 | R22081700198 | New_Event |  |  |  |  | 251 | 2022-08-17 | 15311 | keep | 0 | Aug | 2022 | 0.010428 | 4.1547e-05 | Sustained | FALSE | FALSE | TMED_Event | 61
CAGUAS | 2022-08-17 14:16 | 2022-08-17 18:23 | 3108 | 4:07 | T | NO SE REPORTO CAUSA | DISPARO, SE DEJO FUERA POR RELEVO POR CONTINGENCIA - TRANSMISION | C22081700174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 247 | 2022-08-17 | 767676 | keep | 0 | Aug | 2022 | 0.52286 | 0.0021168 | Sustained | FALSE | FALSE | TMED_Event | 3108
YAUCO | 2022-08-17 14:16 | 2022-08-17 14:17 | 2470 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22081700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 2470 | keep | 0 | Aug | 2022 | 0.0016823 | 0.0016823 | Momentary | FALSE | FALSE | TMED_Event | 2470
YAUCO | 2022-08-17 14:16 | 2022-08-17 14:17 | 1182 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22081700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 1182 | keep | 0 | Aug | 2022 | 0.00080505 | 0.00080505 | Momentary | FALSE | FALSE | TMED_Event | 1182
YAUCO | 2022-08-17 14:16 | 2022-08-17 14:17 | 2340 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22081700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 2340 | keep | 0 | Aug | 2022 | 0.0015938 | 0.0015938 | Momentary | FALSE | FALSE | TMED_Event | 2340
YAUCO | 2022-08-17 14:16 | 2022-08-17 14:17 | 1637 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22081700117 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 1637 | keep | 0 | Aug | 2022 | 0.001115 | 0.001115 | Momentary | FALSE | FALSE | TMED_Event | 1637
YAUCO | 2022-08-17 14:16 | 2022-08-17 17:24 | 1475 | 3:08 | S | LINEA DE TRANSMISION 38KV | SE DISPARARON BREAKERS 0010 EN SUBESTACION 5305-00 | P22081700111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 188 | 2022-08-17 | 277300 | keep | 0 | Aug | 2022 | 0.18887 | 0.0010046 | Sustained | FALSE | FALSE | TMED_Event | 1475
YAUCO | 2022-08-17 14:16 | 2022-08-17 17:35 | 661 | 3:19 | S | LINEA DE TRANSMISION 38KV | SE DISPARARON BREAKERS 0010 EN SUBESTACION 5305-00 | P22081700111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 199 | 2022-08-17 | 131539 | keep | 0 | Aug | 2022 | 0.089591 | 0.0004502 | Sustained | FALSE | FALSE | TMED_Event | 661
YAUCO | 2022-08-17 14:16 | 2022-08-17 14:17 | 1352 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22081700131 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 1352 | keep | 0 | Aug | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | TMED_Event | 1352
YAUCO | 2022-08-17 14:16 | 2022-08-17 14:17 | 3973 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22081700131 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 3973 | keep | 0 | Aug | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | TMED_Event | 3973
YAUCO | 2022-08-17 14:16 | 2022-08-17 14:17 | 2484 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8300 | P22081700131 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 2484 | keep | 0 | Aug | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | TMED_Event | 2484
YAUCO | 2022-08-17 14:17 | 2022-08-17 17:50 | 2340 | 3:33 | T | NO SE REPORTO CAUSA | SE ENCONTRO ALIMENTADOR FUERA DE SERVICIO SE PATRULLO LINEA NO SE ENCONTRO CAUSA NO HAY RTU | P22081700152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-08-17 | 498420 | keep | 0 | Aug | 2022 | 0.33947 | 0.0015938 | Sustained | FALSE | FALSE | TMED_Event | 2340
BARRANQUITAS | 2022-08-17 14:19 | 2022-08-17 21:52 | 25 | 7:33 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22081700178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 453 | 2022-08-17 | 11325 | keep | 0 | Aug | 2022 | 0.0077134 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
YAUCO | 2022-08-17 14:20 | 2022-08-18 15:50 | 167 | 25:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22081700225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1530 | 2022-08-17 | 255510 | keep | 0 | Aug | 2022 | 0.17403 | 0.00011374 | Sustained | FALSE | FALSE | TMED_Event | 167
BARRANQUITAS | 2022-08-17 14:21 | 2022-08-18 07:52 | 45 | 17:31 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22081700179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1051 | 2022-08-17 | 47295 | keep | 0 | Aug | 2022 | 0.032212 | 3.0649e-05 | Sustained | FALSE | FALSE | TMED_Event | 45
MAYAGÃœEZ | 2022-08-17 14:22 | 2022-08-17 16:40 | 100 | 2:18 | P | DESGANCHE | 1 X 65 Y 2 X 50 EN CORTE DE LINEAS DISTINTOS SE REALIZO DESGANCHE | M22081700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-08-17 | 13800 | keep | 0 | Aug | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
BAYAMON | 2022-08-17 14:27 | 2022-08-17 17:06 | 12 | 2:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | B22081700243 | New_Event | Secondary Wire Break | Include | Include | Equipment | 159 | 2022-08-17 | 1908 | keep | 0 | Aug | 2022 | 0.0012995 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
CAGUAS | 2022-08-17 14:28 | 2022-08-17 18:29 | 76 | 4:01 | P | PROBLEMA DEL CLIENTE | 1 X 50 EN C/L DEJO FUERA BOMBAS AAA POR PROA | C22081700182 | New_Event | Customer-Related Interruption | Include | Include | Public | 241 | 2022-08-17 | 18316 | keep | 0 | Aug | 2022 | 0.012475 | 5.1763e-05 | Sustained | FALSE | FALSE | TMED_Event | 76
BAYAMON | 2022-08-17 14:31 | 2022-08-17 18:44 | 6136 | 4:13 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | RELEVO POR CONTINGENCIA SOBRECARGA LINEA 503000 | B22081700000 | New_Event |  |  |  |  | 253 | 2022-08-17 | 1552408 | keep | 0 | Aug | 2022 | 1.0573 | 0.0041792 | Sustained | FALSE | FALSE | TMED_Event | 6136
CAGUAS | 2022-08-17 14:33 | 2022-08-17 16:05 | 48 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L FUERTES LLUVIAS | C22081700184 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2022-08-17 | 4416 | keep | 0 | Aug | 2022 | 0.0030077 | 3.2693e-05 | Sustained | FALSE | FALSE | TMED_Event | 48
BARRANQUITAS | 2022-08-17 14:36 | 2022-08-17 18:09 | 30 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES LLUVIAS | C22081700189 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2022-08-17 | 6390 | keep | 0 | Aug | 2022 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BARRANQUITAS | 2022-08-17 14:37 | 2022-08-17 18:26 | 5 | 3:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR LLUVIAS | C22081700192 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 229 | 2022-08-17 | 1145 | keep | 0 | Aug | 2022 | 0.00077985 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
MAYAGÃœEZ | 2022-08-17 14:44 | 2022-08-17 18:00 | 100 | 3:16 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE DESCONECTO PARARRAYOS AVERIADO | M22081700136 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 196 | 2022-08-17 | 19600 | keep | 0 | Aug | 2022 | 0.013349 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
SAN JUAN | 2022-08-17 14:50 | 2022-08-17 19:01 | 20 | 4:11 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081700409 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-08-17 | 5020 | keep | 0 | Aug | 2022 | 0.0034191 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
AGUADILLA | 2022-08-17 14:57 | 2022-08-18 05:29 | 3 | 14:32 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700140 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 872 | 2022-08-17 | 2616 | keep | 0 | Aug | 2022 | 0.0017817 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
BARRANQUITAS | 2022-08-17 15:00 | 2022-08-17 17:02 | 50 | 2:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L REMPLAZO AISLADOR | C22081700204 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 122 | 2022-08-17 | 6100 | keep | 0 | Aug | 2022 | 0.0041547 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
UTUADO | 2022-08-17 15:00 | 2022-08-17 16:44 | 2 | 1:44 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A22081700206 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2022-08-17 | 208 | keep | 0 | Aug | 2022 | 0.00014167 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
BARRANQUITAS | 2022-08-17 15:00 | 2022-08-18 10:38 | 15 | 19:38 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA X 37.5KVA | C22081700227 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1178 | 2022-08-17 | 17670 | keep | 0 | Aug | 2022 | 0.012035 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
BARRANQUITAS | 2022-08-17 15:01 | 2022-08-17 17:58 | 15 | 2:57 | P | DESGANCHE | 2 X 25 EN C/L DESGANCHE | C22081700205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-08-17 | 2655 | keep | 0 | Aug | 2022 | 0.0018083 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
CANOVANAS | 2022-08-17 15:04 | 2022-08-17 22:22 | 2 | 7:18 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | ABRIO XMR Y REMPLAZO 2 POSTES SECUNDARIOS | R22081700224 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 438 | 2022-08-17 | 876 | keep | 0 | Aug | 2022 | 0.00059664 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
SAN JUAN | 2022-08-17 15:07 | 2022-08-17 18:35 | 80 | 3:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA CAJA QUEMADA | S22081700438 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2022-08-17 | 16640 | keep | 0 | Aug | 2022 | 0.011333 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
AGUADILLA | 2022-08-17 15:09 | 2022-08-17 16:10 | 100 | 1:01 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22081700143 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 61 | 2022-08-17 | 6100 | keep | 0 | Aug | 2022 | 0.0041547 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
BAYAMON | 2022-08-17 15:09 | 2022-08-18 10:47 | 40 | 19:38 | P | DESGANCHE | 1X50 EN C/L | B22081700282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1178 | 2022-08-17 | 47120 | keep | 0 | Aug | 2022 | 0.032093 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
UTUADO | 2022-08-17 15:12 | 2022-08-17 18:28 | 30 | 3:16 | P | MAL TIEMPO/RAYOS | 1 X 65 Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700207 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 196 | 2022-08-17 | 5880 | keep | 0 | Aug | 2022 | 0.0040048 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
MAYAGÃœEZ | 2022-08-17 15:15 | 2022-08-17 18:45 | 25 | 3:30 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700148 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 210 | 2022-08-17 | 5250 | keep | 0 | Aug | 2022 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
UTUADO | 2022-08-17 15:18 | 2022-08-18 15:20 | 10 | 24:02 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081700210 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1442 | 2022-08-17 | 14420 | keep | 0 | Aug | 2022 | 0.0098214 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
UTUADO | 2022-08-17 15:18 | 2022-08-17 18:51 | 150 | 3:33 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA Y 3 X 15 EN TRANSFORMADORMAL TIEMPO DESCARGAS ELECTRICAS | A22081700209 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 213 | 2022-08-17 | 31950 | keep | 0 | Aug | 2022 | 0.021761 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
BARRANQUITAS | 2022-08-17 15:19 | 2022-08-17 16:53 | 229 | 1:34 | T | NO SE REPORTO CAUSA | DISPARO LLEVA LA CARGA DEL 9901-02 CERRADO X CONTROL, NO CAUSA, SE DEJO FUERA POR RELEVO DE CARGA POR CONTINGENCIA - TRANSMISION | C22081700212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-08-17 | 21526 | keep | 0 | Aug | 2022 | 0.014661 | 0.00015597 | Sustained | FALSE | FALSE | TMED_Event | 229
BARRANQUITAS | 2022-08-17 15:19 | 2022-08-17 16:53 | 1246 | 1:34 | T | NO SE REPORTO CAUSA | DISPARO DEL 9901-01 | C22081700212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2022-08-17 | 117124 | keep | 0 | Aug | 2022 | 0.079773 | 0.00084864 | Sustained | FALSE | FALSE | TMED_Event | 1246
BARRANQUITAS | 2022-08-17 15:23 | 2022-08-17 17:01 | 150 | 1:38 | P | MAL TIEMPO/RAYOS | 2 X 100 EN C/L RAYOS | C22081700218 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 98 | 2022-08-17 | 14700 | keep | 0 | Aug | 2022 | 0.010012 | 0.00010216 | Sustained | FALSE | FALSE | TMED_Event | 150
BARRANQUITAS | 2022-08-17 15:25 | 2022-08-17 18:16 | 231 | 2:51 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 65 EN C/LS RAYOS | C22081700219 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 171 | 2022-08-17 | 39501 | keep | 0 | Aug | 2022 | 0.026904 | 0.00015733 | Sustained | FALSE | FALSE | TMED_Event | 231
MAYAGÃœEZ | 2022-08-17 15:30 | 2022-08-17 18:30 | 1 | 3:00 | P | MAL TIEMPO/RAYOS | 1 X 10 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22081700171 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 180 | 2022-08-17 | 180 | keep | 0 | Aug | 2022 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-08-17 15:35 | 2022-08-17 15:57 | 235 | 0:22 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22081601250 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 22 | 2022-08-17 | 5170 | keep | 0 | Aug | 2022 | 0.0035213 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
PONCE | 2022-08-17 15:36 | 2022-08-17 18:50 | 35 | 3:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 ,1 X 65 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR | P22081700140 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 194 | 2022-08-17 | 6790 | keep | 0 | Aug | 2022 | 0.0046246 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
UTUADO | 2022-08-17 15:37 | 2022-08-17 17:10 | 5 | 1:33 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081700216 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2022-08-17 | 465 | keep | 0 | Aug | 2022 | 0.00031671 | 3.4055e-06 | Sustained | FALSE | FALSE | TMED_Event | 5
SAN JUAN | 2022-08-17 15:40 | 2022-08-17 20:01 | 8 | 4:21 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | S22081700481 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-08-17 | 2088 | keep | 0 | Aug | 2022 | 0.0014221 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
CANOVANAS | 2022-08-17 15:40 | 2022-08-17 21:01 | 30 | 5:21 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | R22081700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2022-08-17 | 9630 | keep | 0 | Aug | 2022 | 0.0065589 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
VEGA BAJA | 2022-08-17 15:42 | 2022-08-17 17:59 | 40 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22081700330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-08-17 | 5480 | keep | 0 | Aug | 2022 | 0.0037324 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
VEGA BAJA | 2022-08-17 15:45 | 2022-08-17 17:45 | 10 | 2:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA X 37.5KVA | A22081700101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 120 | 2022-08-17 | 1200 | keep | 0 | Aug | 2022 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
VEGA BAJA | 2022-08-17 15:45 | 2022-08-17 19:24 | 30 | 3:39 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS EVENTO EN TRANSMISION | A22081700052 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 219 | 2022-08-17 | 6570 | keep | 0 | Aug | 2022 | 0.0044748 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
VEGA BAJA | 2022-08-17 15:45 | 2022-08-17 20:30 | 35 | 4:45 | P | MAL TIEMPO/RAYOS | 1 X 50, 1 X 40, 1 X 30 EN CORTES DE LINEA DISTINTOS Y 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS HUBO UN EVENTO EN TRANSMISION | A22081700043 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 285 | 2022-08-17 | 9975 | keep | 0 | Aug | 2022 | 0.0067939 | 2.3838e-05 | Sustained | FALSE | FALSE | TMED_Event | 35
SAN JUAN | 2022-08-17 15:52 | 2022-08-17 20:46 | 20 | 4:54 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE CORTE DE LINEA PARA REMPLAZO POSTE PRIMARIO | S22081700775 | New_Event | Primary Pole Failure | Include | Include | Equipment | 294 | 2022-08-17 | 5880 | keep | 0 | Aug | 2022 | 0.0040048 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
PONCE | 2022-08-17 15:54 | 2022-08-17 16:50 | 21 | 0:56 | P | EXCAVACIONES | LINEA SECUNDARIA AVERIADA POR MAQUINARIA AAA | P22081700143 | New_Event | Excavation | Include | Include | Public | 56 | 2022-08-17 | 1176 | keep | 0 | Aug | 2022 | 0.00080097 | 1.4303e-05 | Sustained | FALSE | FALSE | TMED_Event | 21
MAYAGÃœEZ | 2022-08-17 16:03 | 2022-08-18 14:10 | 60 | 22:07 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M22081700168 | New_Event | Primary Wire Break | Include | Include | Equipment | 1327 | 2022-08-17 | 79620 | keep | 0 | Aug | 2022 | 0.054229 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
MAYAGÃœEZ | 2022-08-17 16:07 | 2022-08-17 18:35 | 1 | 2:28 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700173 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 148 | 2022-08-17 | 148 | keep | 0 | Aug | 2022 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
YAUCO | 2022-08-17 16:10 | 2022-08-17 20:03 | 140 | 3:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M22081700174 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 233 | 2022-08-17 | 32620 | keep | 0 | Aug | 2022 | 0.022217 | 9.5353e-05 | Sustained | FALSE | FALSE | TMED_Event | 140
UTUADO | 2022-08-17 16:14 | 2022-08-17 20:12 | 30 | 3:58 | P | MAL TIEMPO/RAYOS | 3 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081700228 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 238 | 2022-08-17 | 7140 | keep | 0 | Aug | 2022 | 0.004863 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
HUMACAO | 2022-08-17 16:23 | 2022-08-17 19:07 | 100 | 2:44 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C22081700259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2022-08-17 | 16400 | keep | 0 | Aug | 2022 | 0.01117 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
CAGUAS | 2022-08-17 16:23 | 2022-08-17 16:24 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081700268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 6197 | keep | 0 | Aug | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | TMED_Event | 6197
BARRANQUITAS | 2022-08-17 16:24 | 2022-08-17 16:25 | 1843 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081700260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 1843 | keep | 0 | Aug | 2022 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | TMED_Event | 1843
SAN JUAN | 2022-08-17 16:25 | 2022-08-17 19:28 | 50 | 3:03 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081700523 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-08-17 | 9150 | keep | 0 | Aug | 2022 | 0.006232 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BARRANQUITAS | 2022-08-17 16:25 | 2022-08-18 08:55 | 120 | 16:30 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22081700262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 990 | 2022-08-17 | 118800 | keep | 0 | Aug | 2022 | 0.080914 | 8.1731e-05 | Sustained | FALSE | FALSE | TMED_Event | 120
HUMACAO | 2022-08-17 16:41 | 2022-08-17 18:02 | 2 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA Y REGULARLO | C22081700027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2022-08-17 | 162 | keep | 0 | Aug | 2022 | 0.00011034 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
VEGA BAJA | 2022-08-17 16:43 | 2022-08-17 21:08 | 127 | 4:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN C/L SE REMPLAZO CAJA | B22081700358 | New_Event | Cutout Failure | Include | Include | Equipment | 265 | 2022-08-17 | 33655 | keep | 0 | Aug | 2022 | 0.022922 | 8.6499e-05 | Sustained | FALSE | FALSE | TMED_Event | 127
MAYAGÃœEZ | 2022-08-17 16:45 | 2022-08-17 17:00 | 10 | 0:15 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | M22081700186 | New_Event |  |  |  |  | 15 | 2022-08-17 | 150 | keep | 0 | Aug | 2022 | 0.00010216 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
AGUADILLA | 2022-08-17 16:52 | 2022-08-17 18:50 | 10 | 1:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22081700192 | New_Event | Primary Wire Break | Include | Include | Equipment | 118 | 2022-08-17 | 1180 | keep | 0 | Aug | 2022 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
CAGUAS | 2022-08-17 16:53 | 2022-08-17 19:07 | 16 | 2:14 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO | C22081700282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-08-17 | 2144 | keep | 0 | Aug | 2022 | 0.0014603 | 1.0898e-05 | Sustained | FALSE | FALSE | TMED_Event | 16
MAYAGÃœEZ | 2022-08-17 16:56 | 2022-08-17 21:42 | 25 | 4:46 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700195 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 286 | 2022-08-17 | 7150 | keep | 0 | Aug | 2022 | 0.0048698 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
BARRANQUITAS | 2022-08-17 17:03 | 2022-08-18 09:45 | 140 | 16:42 | P | TRANSFORMADOR AVERIADO | 2 X 50 EN CORTE DE LINEA TRANSFORMADOR AVERIADO | C22081700287 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1002 | 2022-08-17 | 140280 | keep | 0 | Aug | 2022 | 0.095544 | 9.5353e-05 | Sustained | FALSE | FALSE | TMED_Event | 140
VEGA BAJA | 2022-08-17 17:09 | 2022-08-17 21:32 | 100 | 4:23 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700244 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 263 | 2022-08-17 | 26300 | keep | 0 | Aug | 2022 | 0.017913 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
SAN JUAN | 2022-08-17 17:12 | 2022-08-17 20:00 | 80 | 2:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22081700574 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-08-17 | 13440 | keep | 0 | Aug | 2022 | 0.0091539 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
MAYAGÃœEZ | 2022-08-17 17:14 | 2022-08-17 18:35 | 10 | 1:21 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700197 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 81 | 2022-08-17 | 810 | keep | 0 | Aug | 2022 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-08-17 17:23 | 2022-08-18 03:36 | 60 | 10:13 | P | DESGANCHE | 1 X 80 EN RISER SE DESGANCHO | B22081700404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 613 | 2022-08-17 | 36780 | keep | 0 | Aug | 2022 | 0.025051 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
MAYAGÃœEZ | 2022-08-17 17:34 | 2022-08-17 23:00 | 100 | 5:26 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700208 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 326 | 2022-08-17 | 32600 | keep | 0 | Aug | 2022 | 0.022204 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
UTUADO | 2022-08-17 17:39 | 2022-08-18 09:50 | 40 | 16:11 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700253 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 971 | 2022-08-17 | 38840 | keep | 0 | Aug | 2022 | 0.026454 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
BARRANQUITAS | 2022-08-17 17:42 | 2022-08-18 08:25 | 15 | 14:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR MAL TIEMPO LLUVIAS | C22081700302 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 883 | 2022-08-17 | 13245 | keep | 0 | Aug | 2022 | 0.0090211 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
UTUADO | 2022-08-17 17:54 | 2022-08-17 23:10 | 200 | 5:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON LINEAS PRIMARIAS PARTIDAS Y SE REEMPLAZO CAJA PRIMARIA AVERIADA | A22081700257 | New_Event | Primary Wire Break | Include | Include | Equipment | 316 | 2022-08-17 | 63200 | keep | 0 | Aug | 2022 | 0.043045 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
PONCE | 2022-08-17 17:58 | 2022-08-17 18:35 | 32 | 0:37 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22081700185 | New_Event | Animals | Include | Include | Wildlife | 37 | 2022-08-17 | 1184 | keep | 0 | Aug | 2022 | 0.00080642 | 2.1795e-05 | Sustained | FALSE | FALSE | TMED_Event | 32
BARRANQUITAS | 2022-08-17 17:59 | 2022-08-17 20:54 | 100 | 2:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22081700310 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-08-17 | 17500 | keep | 0 | Aug | 2022 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
YAUCO | 2022-08-17 18:00 | 2022-08-17 18:43 | 177 | 0:43 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGA ELECTRICA | P22081700189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 43 | 2022-08-17 | 7611 | keep | 0 | Aug | 2022 | 0.0051838 | 0.00012055 | Sustained | FALSE | FALSE | TMED_Event | 177
YAUCO | 2022-08-17 18:00 | 2022-08-17 19:00 | 21 | 1:00 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR DESCARGA ELECTRICA | P22081700192 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 60 | 2022-08-17 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 1.4303e-05 | Sustained | FALSE | FALSE | TMED_Event | 21
UTUADO | 2022-08-17 18:15 | 2022-08-18 17:00 | 250 | 22:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO EN CONVERTIDOR DE 25 KVA POR 37.5 KVA FID-25857239 | A22081700264 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1365 | 2022-08-17 | 341250 | keep | 0 | Aug | 2022 | 0.23242 | 0.00017027 | Sustained | FALSE | FALSE | TMED_Event | 250
BAYAMON | 2022-08-17 18:21 | 2022-08-17 18:22 | 1570 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22081700463 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-17 | 1570 | keep | 0 | Aug | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | TMED_Event | 1570
UTUADO | 2022-08-17 18:27 | 2022-08-17 21:17 | 250 | 2:50 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700269 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 170 | 2022-08-17 | 42500 | keep | 0 | Aug | 2022 | 0.028947 | 0.00017027 | Sustained | FALSE | FALSE | TMED_Event | 250
SAN JUAN | 2022-08-17 18:28 | 2022-08-19 19:28 | 123 | 49:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO POSTE PRIMARIO | S22081700661 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2940 | 2022-08-17 | 361620 | keep | 0 | Aug | 2022 | 0.2463 | 8.3775e-05 | Sustained | FALSE | FALSE | TMED_Event | 123
BAYAMON | 2022-08-17 18:30 | 2022-08-17 19:10 | 500 | 0:40 | P | CONDUCTOR ARRIADO O CRUZADO | SE CERRO MACHETES 100% EN SERVICIO | B22081700158 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 40 | 2022-08-17 | 20000 | keep | 0 | Aug | 2022 | 0.013622 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-08-17 18:41 | 2022-08-17 19:06 | 523 | 0:25 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR | B22081700158 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 25 | 2022-08-17 | 13075 | keep | 0 | Aug | 2022 | 0.0089053 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
CAGUAS | 2022-08-17 18:41 | 2022-08-17 19:47 | 52 | 1:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES LLUVIAS | C22081700321 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 66 | 2022-08-17 | 3432 | keep | 0 | Aug | 2022 | 0.0023375 | 3.5417e-05 | Sustained | FALSE | FALSE | TMED_Event | 52
PONCE | 2022-08-17 18:41 | 2022-08-17 20:05 | 8 | 1:24 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR DESCARGA ELECTRICA | P22081700190 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 84 | 2022-08-17 | 672 | keep | 0 | Aug | 2022 | 0.0004577 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
BAYAMON | 2022-08-17 18:44 | 2022-08-17 23:09 | 18 | 4:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 EN XMR SE REPARO SECUNDARIA | B22081700495 | New_Event | Secondary Wire Break | Include | Include | Equipment | 265 | 2022-08-17 | 4770 | keep | 0 | Aug | 2022 | 0.0032488 | 1.226e-05 | Sustained | FALSE | FALSE | TMED_Event | 18
ARECIBO | 2022-08-17 18:45 | 2022-08-17 20:48 | 30 | 2:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA ROTA | M22081700219 | New_Event | Secondary Wire Break | Include | Include | Equipment | 123 | 2022-08-17 | 3690 | keep | 0 | Aug | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BARRANQUITAS | 2022-08-17 18:45 | 2022-08-17 22:42 | 165 | 3:57 | P | MAL TIEMPO/RAYOS | 1 X 65 2 X 50 Y 3 X 40 EN C/LS RAYOS | C22081700324 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 237 | 2022-08-17 | 39105 | keep | 0 | Aug | 2022 | 0.026634 | 0.00011238 | Sustained | FALSE | FALSE | TMED_Event | 165
MAYAGÃœEZ | 2022-08-17 18:46 | 2022-08-17 19:45 | 2 | 0:59 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22081700220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-08-17 | 118 | keep | 0 | Aug | 2022 | 8.0369e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | TMED_Event | 2
UTUADO | 2022-08-17 18:52 | 2022-08-17 22:26 | 25 | 3:34 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700221 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 214 | 2022-08-17 | 5350 | keep | 0 | Aug | 2022 | 0.0036439 | 1.7027e-05 | Sustained | FALSE | FALSE | TMED_Event | 25
AGUADILLA | 2022-08-17 18:54 | 2022-08-17 21:00 | 60 | 2:06 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700223 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 126 | 2022-08-17 | 7560 | keep | 0 | Aug | 2022 | 0.0051491 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
BAYAMON | 2022-08-17 18:58 | 2022-08-19 21:54 | 8 | 50:56 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22081700506 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3056 | 2022-08-17 | 24448 | keep | 0 | Aug | 2022 | 0.016651 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
AGUADILLA | 2022-08-17 18:58 | 2022-08-18 02:52 | 60 | 7:54 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081700225 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 474 | 2022-08-17 | 28440 | keep | 0 | Aug | 2022 | 0.01937 | 4.0866e-05 | Sustained | FALSE | FALSE | TMED_Event | 60
BAYAMON | 2022-08-17 19:02 | 2022-08-18 04:27 | 68 | 9:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22081700512 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 565 | 2022-08-17 | 38420 | keep | 0 | Aug | 2022 | 0.026168 | 4.6314e-05 | Sustained | FALSE | FALSE | TMED_Event | 68
HUMACAO | 2022-08-17 19:04 | 2022-08-17 20:04 | 7 | 1:00 | P | ANIMAL | 1 X 20 EN C/L CRUCE X AVE | C22081700342 | New_Event | Animals | Include | Include | Wildlife | 60 | 2022-08-17 | 420 | keep | 0 | Aug | 2022 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | TMED_Event | 7
BARRANQUITAS | 2022-08-17 19:06 | 2022-08-17 19:24 | 30 | 0:18 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYOS | C22081700346 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 18 | 2022-08-17 | 540 | keep | 0 | Aug | 2022 | 0.00036779 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
BAYAMON | 2022-08-17 19:09 | 2022-08-17 23:17 | 2617 | 4:08 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA | B22081700158 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-08-17 | 649016 | keep | 0 | Aug | 2022 | 0.44204 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
UTUADO | 2022-08-17 19:11 | 2022-08-18 13:10 | 40 | 17:59 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081700279 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1079 | 2022-08-17 | 43160 | keep | 0 | Aug | 2022 | 0.029396 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
BAYAMON | 2022-08-17 19:14 | 2022-08-18 13:05 | 30 | 17:51 | P | MAL TIEMPO/RAYOS | 1X30 EN C/L POR RAYO AL CAER | B22081700527 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1071 | 2022-08-17 | 32130 | keep | 0 | Aug | 2022 | 0.021884 | 2.0433e-05 | Sustained | FALSE | FALSE | TMED_Event | 30
SAN JUAN | 2022-08-17 19:22 | 2022-08-17 21:16 | 200 | 1:54 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S22081700707 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-08-17 | 22800 | keep | 0 | Aug | 2022 | 0.015529 | 0.00013622 | Sustained | FALSE | FALSE | TMED_Event | 200
UTUADO | 2022-08-17 19:24 | 2022-08-17 20:40 | 1527 | 1:16 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA AVERIADA SE CERRO INTERRUPTOR | A22081700284 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2022-08-17 | 116052 | keep | 0 | Aug | 2022 | 0.079042 | 0.00104 | Sustained | FALSE | FALSE | TMED_Event | 1527
BAYAMON | 2022-08-17 19:32 | 2022-08-18 01:42 | 122 | 6:10 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S22081700719 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 370 | 2022-08-17 | 45140 | keep | 0 | Aug | 2022 | 0.030745 | 8.3094e-05 | Sustained | FALSE | FALSE | TMED_Event | 122
SAN JUAN | 2022-08-17 19:33 | 2022-08-18 14:17 | 50 | 18:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER HACIA SU 1 | S22081700721 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1124 | 2022-08-17 | 56200 | keep | 0 | Aug | 2022 | 0.038278 | 3.4055e-05 | Sustained | FALSE | FALSE | TMED_Event | 50
BARRANQUITAS | 2022-08-17 19:34 | 2022-08-18 18:30 | 40 | 22:56 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE CERRO PUENTE DE LINEA A CAJA | C22081700362 | New_Event | Primary Wire Break | Include | Include | Equipment | 1376 | 2022-08-17 | 55040 | keep | 0 | Aug | 2022 | 0.037487 | 2.7244e-05 | Sustained | FALSE | FALSE | TMED_Event | 40
PONCE | 2022-08-17 19:38 | 2022-08-17 19:39 | 1863 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22081700212 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 1863 | keep | 0 | Aug | 2022 | 0.0012689 | 0.0012689 | Momentary | FALSE | FALSE | TMED_Event | 1863
PONCE | 2022-08-17 19:38 | 2022-08-17 19:39 | 708 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22081700212 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 708 | keep | 0 | Aug | 2022 | 0.00048222 | 0.00048222 | Momentary | FALSE | FALSE | TMED_Event | 708
YAUCO | 2022-08-17 19:38 | 2022-08-17 19:39 | 64 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22081700216 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 64 | keep | 0 | Aug | 2022 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | TMED_Event | 64
SAN JUAN | 2022-08-17 19:39 | 2022-08-18 18:00 | 10 | 22:21 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A T50 | S22081700722 | New_Event | UG Cable Fault | Include | Include | Equipment | 1341 | 2022-08-17 | 13410 | keep | 0 | Aug | 2022 | 0.0091335 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
YAUCO | 2022-08-17 19:39 | 2022-08-17 22:50 | 508 | 3:11 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTES HACIA TRAMO CON ALAMBRES PARTIDOS | P22081700203 | New_Event | Primary Wire Break | Include | Include | Equipment | 191 | 2022-08-17 | 97028 | keep | 0 | Aug | 2022 | 0.066085 | 0.000346 | Sustained | FALSE | FALSE | TMED_Event | 508
PONCE | 2022-08-17 19:44 | 2022-08-18 12:15 | 10 | 16:31 | P | MAL TIEMPO/RAYOS | 1 X 20 EN XMR MAL TIEMPO RAYOS | P22081700206 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 991 | 2022-08-17 | 9910 | keep | 0 | Aug | 2022 | 0.0067497 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
YAUCO | 2022-08-17 19:47 | 2022-08-17 20:39 | 169 | 0:52 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGA ELECTRICA | P22081700210 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 52 | 2022-08-17 | 8788 | keep | 0 | Aug | 2022 | 0.0059855 | 0.00011511 | Sustained | FALSE | FALSE | TMED_Event | 169
PONCE | 2022-08-17 19:49 | 2022-08-18 14:47 | 20 | 18:58 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO TRAMO DE LINEA PRIMARIA 2 X 30 EN CORTE DE LINEA | P22081700211 | New_Event | Primary Wire Break | Include | Include | Equipment | 1138 | 2022-08-17 | 22760 | keep | 0 | Aug | 2022 | 0.015502 | 1.3622e-05 | Sustained | FALSE | FALSE | TMED_Event | 20
YAUCO | 2022-08-17 20:11 | 2022-08-17 20:12 | 502 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22081700214 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 502 | keep | 0 | Aug | 2022 | 0.00034191 | 0.00034191 | Momentary | FALSE | FALSE | TMED_Event | 502
YAUCO | 2022-08-17 20:11 | 2022-08-17 20:12 | 2747 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22081700214 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 2747 | keep | 0 | Aug | 2022 | 0.001871 | 0.001871 | Momentary | FALSE | FALSE | TMED_Event | 2747
YAUCO | 2022-08-17 20:11 | 2022-08-17 20:12 | 1587 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22081700214 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 1587 | keep | 0 | Aug | 2022 | 0.0010809 | 0.0010809 | Momentary | FALSE | FALSE | TMED_Event | 1587
YAUCO | 2022-08-17 20:11 | 2022-08-17 20:12 | 2671 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 | P22081700214 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-17 | 2671 | keep | 0 | Aug | 2022 | 0.0018192 | 0.0018192 | Momentary | FALSE | FALSE | TMED_Event | 2671
AGUADILLA | 2022-08-17 20:11 | 2022-08-18 11:29 | 70 | 15:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M22081700239 | New_Event | Primary Wire Break | Include | Include | Equipment | 918 | 2022-08-17 | 64260 | keep | 0 | Aug | 2022 | 0.043767 | 4.7677e-05 | Sustained | FALSE | FALSE | TMED_Event | 70
MAYAGÃœEZ | 2022-08-17 20:20 | 2022-08-17 21:35 | 100 | 1:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22081700247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-08-17 | 7500 | keep | 0 | Aug | 2022 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | TMED_Event | 100
FAJARDO | 2022-08-17 20:30 | 2022-08-17 20:36 | 1 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV LLEVANDO SOLO UN SOLO CLIENTE, EL RESTO ESTABA POR EL 2003-01 | R22081700402 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-08-17 | 6 | keep | 0 | Aug | 2022 | 4.0866e-06 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
FAJARDO | 2022-08-17 20:30 | 2022-08-17 20:36 | 240 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV | R22081700402 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-08-17 | 1440 | keep | 0 | Aug | 2022 | 0.00098078 | 0.00016346 | Sustained | FALSE | FALSE | TMED_Event | 240
FAJARDO | 2022-08-17 20:30 | 2022-08-17 20:36 | 2722 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV | R22081700402 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-08-17 | 16332 | keep | 0 | Aug | 2022 | 0.011124 | 0.0018539 | Sustained | FALSE | FALSE | TMED_Event | 2722
FAJARDO | 2022-08-17 20:30 | 2022-08-17 20:36 | 1234 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV | R22081700402 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-08-17 | 7404 | keep | 0 | Aug | 2022 | 0.0050428 | 0.00084047 | Sustained | FALSE | FALSE | TMED_Event | 1234
FAJARDO | 2022-08-17 20:30 | 2022-08-17 20:36 | 76 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115KV | R22081700402 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2022-08-17 | 456 | keep | 0 | Aug | 2022 | 0.00031058 | 5.1763e-05 | Sustained | FALSE | FALSE | TMED_Event | 76
FAJARDO | 2022-08-17 20:39 | 2022-08-17 23:00 | 240 | 2:21 | T | DISPARO DE BARRA DE TRANSMISION | PT DE BARRA 115KV SE TRANSFIRIO LA CARGA AL 2003-01 | R22081700402 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 141 | 2022-08-17 | 33840 | keep | 0 | Aug | 2022 | 0.023048 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
FAJARDO | 2022-08-17 20:39 | 2022-08-17 22:48 | 2722 | 2:09 | T | DISPARO DE BARRA DE TRANSMISION | PT DE BARRA 115KV LLEVA LA CARGA DEL 2005-11 SE TRANSFIRIO LAS CARGAS AL 2006-04 | R22081700402 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 129 | 2022-08-17 | 351138 | keep | 0 | Aug | 2022 | 0.23916 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
FAJARDO | 2022-08-17 20:39 | 2022-08-17 23:05 | 1234 | 2:26 | T | DISPARO DE BARRA DE TRANSMISION | PT DE BARRA 115KV AVERIADO SE TRANSFIRIO LA CARGA AL 2305-02 | R22081700402 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 146 | 2022-08-17 | 180164 | keep | 0 | Aug | 2022 | 0.12271 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
FAJARDO | 2022-08-17 20:39 | 2022-08-17 22:48 | 76 | 2:09 | T | DISPARO DE BARRA DE TRANSMISION | PT DE BARRA 115KV AVERIADO CARGAS X 2005-09. SE TRANSFIRIO AL 2006-04 | R22081700402 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 129 | 2022-08-17 | 9804 | keep | 0 | Aug | 2022 | 0.0066775 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BARRANQUITAS | 2022-08-17 20:53 | 2022-08-18 13:42 | 10 | 16:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C22081700408 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1009 | 2022-08-17 | 10090 | keep | 0 | Aug | 2022 | 0.0068723 | 6.811e-06 | Sustained | FALSE | FALSE | TMED_Event | 10
BAYAMON | 2022-08-17 21:03 | 2022-08-17 22:33 | 12 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22081700451 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2022-08-17 | 1080 | keep | 0 | Aug | 2022 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | TMED_Event | 12
MAYAGÃœEZ | 2022-08-17 21:13 | 2022-08-18 00:38 | 8 | 3:25 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081700265 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 205 | 2022-08-17 | 1640 | keep | 0 | Aug | 2022 | 0.001117 | 5.4488e-06 | Sustained | FALSE | FALSE | TMED_Event | 8
SAN JUAN | 2022-08-17 21:24 | 2022-08-18 14:23 | 76 | 16:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE REMPLAZO CAJA PRIMARIA Y SE REPARO PUENTE PRIMARIO LINEA A CAJA | S22081700801 | New_Event | Cutout Failure | Include | Include | Equipment | 1019 | 2022-08-17 | 77444 | keep | 0 | Aug | 2022 | 0.052747 | 5.1763e-05 | Sustained | FALSE | FALSE | TMED_Event | 76
VEGA BAJA | 2022-08-17 21:50 | 2022-08-17 22:56 | 15 | 1:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22081700629 | New_Event | Secondary Wire Break | Include | Include | Equipment | 66 | 2022-08-17 | 990 | keep | 0 | Aug | 2022 | 0.00067428 | 1.0216e-05 | Sustained | FALSE | FALSE | TMED_Event | 15
AGUADILLA | 2022-08-17 21:57 | 2022-08-18 17:23 | 1 | 19:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMAODR DE 15KVA POR UNO DE 25KVA | M22081700271 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1166 | 2022-08-17 | 1166 | keep | 0 | Aug | 2022 | 0.00079416 | 6.811e-07 | Sustained | FALSE | FALSE | TMED_Event | 1
BAYAMON | 2022-08-17 22:14 | 2022-08-18 00:47 | 398 | 2:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081700684 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2022-08-17 | 60894 | keep | 0 | Aug | 2022 | 0.041475 | 0.00027108 | Sustained | FALSE | FALSE | TMED_Event | 398
BARRANQUITAS | 2022-08-17 22:22 | 2022-08-18 09:47 | 18 | 11:25 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22081700436 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 685 | 2022-08-17 | 12330 | keep | 0 | Aug | 2022 | 0.0083979 | 1.226e-05 | Sustained | FALSE | FALSE | TMED_Event | 18
UTUADO | 2022-08-17 22:40 | 2022-08-18 09:16 | 6 | 10:36 | P | MAL TIEMPO/RAYOS | 4 X 10 EN TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A22081700334 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 636 | 2022-08-17 | 3816 | keep | 0 | Aug | 2022 | 0.0025991 | 4.0866e-06 | Sustained | FALSE | FALSE | TMED_Event | 6
AGUADILLA | 2022-08-17 23:00 | 2022-08-18 10:17 | 3 | 11:17 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | M22081700274 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 677 | 2022-08-17 | 2031 | keep | 0 | Aug | 2022 | 0.0013833 | 2.0433e-06 | Sustained | FALSE | FALSE | TMED_Event | 3
BAYAMON | 2022-08-17 23:17 | 2022-08-17 23:24 | 523 | 0:07 | P | DESGANCHE | SE SECCIONALIZO ALMIENTADOR | B22081700158 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 7 | 2022-08-17 | 3661 | keep | 0 | Aug | 2022 | 0.0024935 | 0 | Sustained | FALSE | FALSE | TMED_Event | 0
BARRANQUITAS | 2022-08-17 23:17 | 2022-08-18 12:05 | 80 | 12:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO AVERIDO | P22081700248 | New_Event | Primary Wire Break | Include | Include | Equipment | 768 | 2022-08-17 | 61440 | keep | 0 | Aug | 2022 | 0.041847 | 5.4488e-05 | Sustained | FALSE | FALSE | TMED_Event | 80
BAYAMON | 2022-08-17 23:24 | 2022-08-17 23:25 | 2617 | 0:01 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR | B22081700158 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-17 | 2617 | keep | 0 | Aug | 2022 | 0.0017824 | 0 | Momentary | FALSE | FALSE | TMED_Event | 0
BAYAMON | 2022-08-17 23:25 | 2022-08-18 00:09 | 523 | 0:44 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES | B22081700158 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-08-17 | 23012 | keep | 0 | Aug | 2022 | 0.015673 | 0.00035621 | Sustained | FALSE | FALSE | TMED_Event | 523
SAN JUAN | 2022-08-18 00:06 | 2022-08-18 06:32 | 10 | 6:26 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR | S22081800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 386 | 2022-08-18 | 3860 | keep | 0 | Aug | 2022 | 0.002629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-18 00:25 | 2022-08-18 17:40 | 30 | 17:15 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081800002 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1035 | 2022-08-18 | 31050 | keep | 0 | Aug | 2022 | 0.021148 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-08-18 00:41 | 2022-08-18 06:47 | 10 | 6:06 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO RAYOS | P22081800012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 366 | 2022-08-18 | 3660 | keep | 0 | Aug | 2022 | 0.0024928 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-18 00:43 | 2022-08-18 12:42 | 15 | 11:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C22081800002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 719 | 2022-08-18 | 10785 | keep | 0 | Aug | 2022 | 0.0073456 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-08-18 01:11 | 2022-08-18 11:27 | 50 | 10:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO NO FUNDIO FUSIBLE | P22081800013 | New_Event | Primary Wire Break | Include | Include | Equipment | 616 | 2022-08-18 | 30800 | keep | 0 | Aug | 2022 | 0.020978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-18 01:16 | 2022-08-18 01:57 | 1571 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-08-18 | 64411 | keep | 0 | Aug | 2022 | 0.04387 | 0.00107 | Sustained | FALSE | FALSE | Not_TMED_Event | 1571
FAJARDO | 2022-08-18 01:16 | 2022-08-18 01:57 | 2041 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-08-18 | 83681 | keep | 0 | Aug | 2022 | 0.056995 | 0.0013901 | Sustained | FALSE | FALSE | Not_TMED_Event | 2041
FAJARDO | 2022-08-18 01:16 | 2022-08-18 01:57 | 625 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-08-18 | 25625 | keep | 0 | Aug | 2022 | 0.017453 | 0.00042568 | Sustained | FALSE | FALSE | Not_TMED_Event | 625
FAJARDO | 2022-08-18 01:16 | 2022-08-18 01:57 | 1463 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800067 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-08-18 | 59983 | keep | 0 | Aug | 2022 | 0.040854 | 0.00099644 | Sustained | FALSE | FALSE | Not_TMED_Event | 1463
FAJARDO | 2022-08-18 01:16 | 2022-08-18 02:46 | 1902 | 1:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-08-18 | 171180 | keep | 0 | Aug | 2022 | 0.11659 | 0.0012954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-08-18 01:16 | 2022-08-18 02:46 | 970 | 1:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-08-18 | 87300 | keep | 0 | Aug | 2022 | 0.05946 | 0.00066066 | Sustained | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2022-08-18 01:16 | 2022-08-18 02:46 | 3003 | 1:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-08-18 | 270270 | keep | 0 | Aug | 2022 | 0.18408 | 0.0020453 | Sustained | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-08-18 01:16 | 2022-08-18 08:51 | 1394 | 7:35 | S | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO TRAMO DE LINEA 16500 Y SE ENERGIZO 2003 LLEVA 2005-07 Y 8 | R22081800067 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 455 | 2022-08-18 | 634270 | keep | 0 | Aug | 2022 | 0.432 | 0.00094945 | Sustained | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2022-08-18 01:16 | 2022-08-18 08:51 | 412 | 7:35 | S | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO TRAMO DE LINEA 16500 Y SE ENERGIZO 2003 | R22081800067 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 455 | 2022-08-18 | 187460 | keep | 0 | Aug | 2022 | 0.12768 | 0.00028061 | Sustained | FALSE | FALSE | Not_TMED_Event | 412
FAJARDO | 2022-08-18 01:16 | 2022-08-18 08:51 | 424 | 7:35 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 16500 SE SECCIONALIZO SU CARGA POR 2003-1 | R22081800067 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 455 | 2022-08-18 | 192920 | keep | 0 | Aug | 2022 | 0.1314 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
FAJARDO | 2022-08-18 01:16 | 2022-08-18 08:51 | 240 | 7:35 | T | LINEA DE TRANSMISION 115KV | DISPARO LINEA 16500 SE SECCIONALIZO SU CARGA POR 2003-1 | R22081800067 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 455 | 2022-08-18 | 109200 | keep | 0 | Aug | 2022 | 0.074376 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
FAJARDO | 2022-08-18 01:16 | 2022-08-18 02:46 | 2343 | 1:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-08-18 | 210870 | keep | 0 | Aug | 2022 | 0.14362 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2022-08-18 01:16 | 2022-08-18 02:46 | 1830 | 1:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-08-18 | 164700 | keep | 0 | Aug | 2022 | 0.11218 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2022-08-18 01:16 | 2022-08-18 02:46 | 710 | 1:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-08-18 | 63900 | keep | 0 | Aug | 2022 | 0.043522 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2022-08-18 01:16 | 2022-08-18 02:46 | 1197 | 1:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEAS 3100 Y 16500 | R22081800076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-08-18 | 107730 | keep | 0 | Aug | 2022 | 0.073374 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
BARRANQUITAS | 2022-08-18 01:42 | 2022-08-18 01:45 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22081800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-18 | 2610 | keep | 0 | Aug | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-08-18 02:21 | 2022-08-18 05:09 | 34 | 2:48 | T | PROBLEMA DEL CLIENTE | SE SECCIONALIZO POSTE PARTIDO Y SE CERRO POR SCADA CENTRO DE CONTROL Y ADOPCION DE ANIMALES DEL MUNICIPIO DE SAN JUAN | S22081800025 | New_Event | Customer-Related Interruption | Include | Include | Public | 168 | 2022-08-18 | 5712 | keep | 0 | Aug | 2022 | 0.0038904 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-08-18 03:17 | 2022-08-18 17:18 | 120 | 14:01 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S22081800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 841 | 2022-08-18 | 100920 | keep | 0 | Aug | 2022 | 0.068736 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:09 | 1571 | 1:52 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800111 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-08-18 | 175952 | keep | 0 | Aug | 2022 | 0.11984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:09 | 2041 | 1:52 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800111 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-08-18 | 228592 | keep | 0 | Aug | 2022 | 0.15569 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:09 | 625 | 1:52 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800111 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-08-18 | 70000 | keep | 0 | Aug | 2022 | 0.047677 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:09 | 1463 | 1:52 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800111 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-08-18 | 163856 | keep | 0 | Aug | 2022 | 0.1116 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:17 | 1902 | 2:00 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800074 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-08-18 | 228240 | keep | 0 | Aug | 2022 | 0.15545 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:17 | 970 | 2:00 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800074 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-08-18 | 116400 | keep | 0 | Aug | 2022 | 0.07928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:17 | 3003 | 2:00 | S | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800074 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-08-18 | 360360 | keep | 0 | Aug | 2022 | 0.24544 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:01 | 2343 | 1:44 | T | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800076 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-08-18 | 243672 | keep | 0 | Aug | 2022 | 0.16596 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:07 | 1830 | 1:50 | T | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800076 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 110 | 2022-08-18 | 201300 | keep | 0 | Aug | 2022 | 0.1371 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:01 | 710 | 1:44 | T | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 CARGAS X 2201-04 | R22081800076 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-08-18 | 73840 | keep | 0 | Aug | 2022 | 0.050292 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 03:17 | 2022-08-18 05:01 | 1197 | 1:44 | T | LINEA DE TRANSMISION 38KV | SE CERRO PUENTE EN LA LINEA 3100 | R22081800076 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 104 | 2022-08-18 | 124488 | keep | 0 | Aug | 2022 | 0.084788 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-18 03:27 | 2022-08-18 06:45 | 30 | 3:18 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22081800012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2022-08-18 | 5940 | keep | 0 | Aug | 2022 | 0.0040457 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-08-18 04:18 | 2022-08-18 04:19 | 1250 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1250 | keep | 0 | Aug | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
CANOVANAS | 2022-08-18 04:21 | 2022-08-18 09:34 | 1 | 5:13 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN CORTE DE LINEA DESGANCHE | R22081800117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2022-08-18 | 313 | keep | 0 | Aug | 2022 | 0.00021318 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-18 04:28 | 2022-08-18 04:30 | 4476 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1336-10 Y 1657-02 | S22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-18 | 8952 | keep | 0 | Aug | 2022 | 0.0060972 | 0.0030486 | Momentary | FALSE | FALSE | Not_TMED_Event | 4476
SAN JUAN | 2022-08-18 04:28 | 2022-08-18 04:30 | 60 | 0:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | INTERRUPTOR 1336-06 DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1336-10 | S22081800000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-08-18 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-18 04:28 | 2022-08-18 04:30 | 437 | 0:02 | T | NO SE REPORTO CAUSA | INTERRUPTOR 1336-06 DISPARO Y SE CERRO POR CONTROL LLEVA LA CARGA DEL 1657-02 | S22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-18 | 874 | keep | 0 | Aug | 2022 | 0.00059528 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
VEGA BAJA | 2022-08-18 05:00 | 2022-08-18 05:01 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 3000 | keep | 0 | Aug | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
MAYAGÃœEZ | 2022-08-18 05:13 | 2022-08-18 10:50 | 180 | 5:37 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M22081800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2022-08-18 | 60660 | keep | 0 | Aug | 2022 | 0.041315 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2022-08-18 05:21 | 2022-08-18 11:32 | 30 | 6:11 | P | NO SE REPORTO CAUSA | 1X50 DE RISER @ SU-1 | B22081800050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 371 | 2022-08-18 | 11130 | keep | 0 | Aug | 2022 | 0.0075806 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-18 05:43 | 2022-08-18 08:45 | 50 | 3:02 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081800006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 182 | 2022-08-18 | 9100 | keep | 0 | Aug | 2022 | 0.006198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-18 05:44 | 2022-08-18 16:44 | 14 | 11:00 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22081800021 | New_Event | Animals | Include | Include | Wildlife | 660 | 2022-08-18 | 9240 | keep | 0 | Aug | 2022 | 0.0062933 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-08-18 05:47 | 2022-08-18 05:48 | 826 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-05 LLEVA 20% DEL 1206-03 | S22081800042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 826 | keep | 0 | Aug | 2022 | 0.00056258 | 0.00056258 | Momentary | FALSE | FALSE | Not_TMED_Event | 826
CANOVANAS | 2022-08-18 05:47 | 2022-08-18 05:48 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 20% 1206-03 | S22081800042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1615 | keep | 0 | Aug | 2022 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2022-08-18 05:51 | 2022-08-18 05:52 | 1 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1 | keep | 0 | Aug | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-18 05:52 | 2022-08-18 14:15 | 3 | 8:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 37.5KVA | A22081800007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 503 | 2022-08-18 | 1509 | keep | 0 | Aug | 2022 | 0.0010278 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-18 05:55 | 2022-08-18 17:05 | 8 | 11:10 | P | DESGANCHE | 1 X 20 EN XMR SE RETIRO ENREDADERA LADO PRIMARIO | S22081800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 670 | 2022-08-18 | 5360 | keep | 0 | Aug | 2022 | 0.0036507 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-18 06:14 | 2022-08-18 07:13 | 922 | 0:59 | T | DESGANCHE | SE CERRO N/O 1346-05/1401-08 ABRIENDO MACHETES PARA SECCIONALIZAR RAMA ENCIMA DE LINEA. 30% 1346-05 EN SERVICIO | S22081800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-08-18 | 54398 | keep | 0 | Aug | 2022 | 0.03705 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-08-18 06:14 | 2022-08-18 06:56 | 135 | 0:42 | T | DESGANCHE | SE CERRO INTERRUPTOR 1401-08 QUE LLEVA CARGA DE 1346-05 ABRIENDO MACHETES N/O POR RAMA EN LA LINEA (1346-05). 100% 1401-08 EN SERVICIO | S22081800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2022-08-18 | 5670 | keep | 0 | Aug | 2022 | 0.0038618 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2022-08-18 06:19 | 2022-08-18 11:45 | 30 | 5:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | R22081800141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-08-18 | 9780 | keep | 0 | Aug | 2022 | 0.0066611 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-18 06:21 | 2022-08-18 14:57 | 165 | 8:36 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S22081800051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2022-08-18 | 85140 | keep | 0 | Aug | 2022 | 0.057988 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
SAN JUAN | 2022-08-18 06:26 | 2022-08-18 06:29 | 1085 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22081800056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-18 | 3255 | keep | 0 | Aug | 2022 | 0.002217 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-08-18 06:30 | 2022-08-18 06:31 | 1715 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL INTERRUPTOR 1708-03 LLEVA CARGA 1708-02 | B22081800058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1715 | keep | 0 | Aug | 2022 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2022-08-18 06:30 | 2022-08-18 06:31 | 1498 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL INTERRUPTOR 1708-03 LLEVA CARGA 1708-02 | B22081800058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2022-08-18 06:35 | 2022-08-18 08:23 | 723 | 1:48 | T | DESGANCHE | LLEVA LA CARGA DEL 1711-05 SE ABRIO EL AMARRE, AUN QUEDA FUERA LA CARGA DEL 1711-05 | B22081800059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-08-18 | 78084 | keep | 0 | Aug | 2022 | 0.053183 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-18 06:35 | 2022-08-18 09:25 | 1976 | 2:50 | T | DESGANCHE | SE SECCIONALIZO AVERIA POR DESGANCHE PRIMARIO - AUN QUEDA FUERA 50% DE LA CARGA DEL 1711-05 | B22081800059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-08-18 | 335920 | keep | 0 | Aug | 2022 | 0.22879 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
SAN JUAN | 2022-08-18 06:42 | 2022-08-18 06:44 | 225 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-08-18 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-18 06:42 | 2022-08-18 06:44 | 870 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-08-18 | 1740 | keep | 0 | Aug | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-08-18 06:44 | 2022-08-18 06:46 | 100 | 0:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS DESGANCHE Y 3 X 100 EN C/L | S22081800074 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2022-08-18 | 200 | keep | 0 | Aug | 2022 | 0.00013622 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-18 06:46 | 2022-08-18 06:48 | 225 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2022-08-18 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-18 06:46 | 2022-08-18 06:48 | 870 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 2 | 2022-08-18 | 1740 | keep | 0 | Aug | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-08-18 06:48 | 2022-08-18 06:54 | 100 | 0:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS DESGANCHE Y 3 X 100 EN C/L | S22081800074 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 6 | 2022-08-18 | 600 | keep | 0 | Aug | 2022 | 0.00040866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-18 06:50 | 2022-08-18 12:58 | 25 | 6:08 | P | PARARRAYOS DEFECTUOSO | 1X30 EN C/L 1X10 EN XMR SE REMPLAZARON (2) PARARRAYOS | B22081800072 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 368 | 2022-08-18 | 9200 | keep | 0 | Aug | 2022 | 0.0062661 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-08-18 06:52 | 2022-08-18 11:32 | 40 | 4:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R22081800148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2022-08-18 | 11200 | keep | 0 | Aug | 2022 | 0.0076283 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-18 06:52 | 2022-08-18 07:50 | 7621 | 0:58 | T | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE ENERGIZO 30% EN SERVICIO | R22081800150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-08-18 | 442018 | keep | 0 | Aug | 2022 | 0.30106 | 0.0051906 | Sustained | FALSE | FALSE | Not_TMED_Event | 7621
SAN JUAN | 2022-08-18 06:54 | 2022-08-18 07:01 | 225 | 0:07 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 7 | 2022-08-18 | 1575 | keep | 0 | Aug | 2022 | 0.0010727 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-18 06:54 | 2022-08-18 07:01 | 870 | 0:07 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 7 | 2022-08-18 | 6090 | keep | 0 | Aug | 2022 | 0.0041479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-18 06:57 | 2022-08-18 14:15 | 10 | 7:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO | A22081800014 | New_Event | Primary Wire Break | Include | Include | Equipment | 438 | 2022-08-18 | 4380 | keep | 0 | Aug | 2022 | 0.0029832 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-18 07:01 | 2022-08-18 10:19 | 100 | 3:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS DESGANCHE Y 3 X 100 EN C/L | S22081800074 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 198 | 2022-08-18 | 19800 | keep | 0 | Aug | 2022 | 0.013486 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-18 07:04 | 2022-08-18 10:53 | 30 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081800015 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2022-08-18 | 6870 | keep | 0 | Aug | 2022 | 0.0046791 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-08-18 07:07 | 2022-08-18 07:09 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22081800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-18 | 3758 | keep | 0 | Aug | 2022 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
BAYAMON | 2022-08-18 07:08 | 2022-08-18 07:09 | 1570 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081800084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1570 | keep | 0 | Aug | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
SAN JUAN | 2022-08-18 07:13 | 2022-08-18 07:37 | 645 | 0:24 | P | DESGANCHE | SE REALIZO DESGANCHE CON VARETA Y SE CERRO MACHETES 100% EN SERVICIO | S22081800050 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 24 | 2022-08-18 | 15480 | keep | 0 | Aug | 2022 | 0.010543 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-18 07:16 | 2022-08-18 10:44 | 38 | 3:28 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S22081800087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 208 | 2022-08-18 | 7904 | keep | 0 | Aug | 2022 | 0.0053834 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
MAYAGÃœEZ | 2022-08-18 07:19 | 2022-08-18 10:28 | 80 | 3:09 | P | DESGANCHE | 1 X 65 Y 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M22081800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-08-18 | 15120 | keep | 0 | Aug | 2022 | 0.010298 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-08-18 07:22 | 2022-08-18 14:17 | 4 | 6:55 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA 2 X 15 Y 2 X 10 EN TRANSFORMADORES MAL TIEMPO RAYOS | C22081800036 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 415 | 2022-08-18 | 1660 | keep | 0 | Aug | 2022 | 0.0011306 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-18 07:23 | 2022-08-18 22:36 | 10 | 15:13 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZA TRANSFORMADOR QUEMADO DE 25KVA X 37.5 KVA | M22081800017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 913 | 2022-08-18 | 9130 | keep | 0 | Aug | 2022 | 0.0062184 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-18 07:40 | 2022-08-18 11:14 | 60 | 3:34 | P | NO SE REPORTO CAUSA | 2X50 EN C/L, 1X40 EN RISER Y 1X40 EN OTRO RISER | B22081800105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-08-18 | 12840 | keep | 0 | Aug | 2022 | 0.0087453 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-08-18 07:43 | 2022-08-18 10:20 | 50 | 2:37 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C22081800042 | New_Event | Animals | Include | Include | Wildlife | 157 | 2022-08-18 | 7850 | keep | 0 | Aug | 2022 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-18 07:43 | 2022-08-18 07:44 | 776 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081800108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 776 | keep | 0 | Aug | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
CANOVANAS | 2022-08-18 07:50 | 2022-08-18 08:30 | 5335 | 0:40 | P | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE ENERGIZO 45 % EN SERVICIO | R22081800150 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-08-18 | 213400 | keep | 0 | Aug | 2022 | 0.14535 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-18 07:55 | 2022-08-18 11:47 | 8 | 3:52 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | C22081800046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-08-18 | 1856 | keep | 0 | Aug | 2022 | 0.0012641 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-08-18 07:55 | 2022-08-18 13:16 | 50 | 5:21 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22081800046 | New_Event | Animals | Include | Include | Wildlife | 321 | 2022-08-18 | 16050 | keep | 0 | Aug | 2022 | 0.010932 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-18 08:00 | 2022-08-18 18:07 | 50 | 10:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22081800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 607 | 2022-08-18 | 30350 | keep | 0 | Aug | 2022 | 0.020671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-18 08:00 | 2022-08-18 17:17 | 10 | 9:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARA LINEA SECUNDARIA | M22081800141 | New_Event | Secondary Wire Break | Include | Include | Equipment | 557 | 2022-08-18 | 5570 | keep | 0 | Aug | 2022 | 0.0037937 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-18 08:01 | 2022-08-18 15:50 | 8 | 7:49 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REALIZAR DESGANCHE MASIVO SECUNDARIO Y SE REEMPLAZO 250 PIES DE SECUNDARIA | C22081700351 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 469 | 2022-08-18 | 3752 | keep | 0 | Aug | 2022 | 0.0025555 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-18 08:10 | 2022-08-18 08:29 | 1 | 0:19 | P | NO SE REPORTO CAUSA | 1X50 EN RISER DEL CLIENTE | B22081800122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2022-08-18 | 19 | keep | 0 | Aug | 2022 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-18 08:17 | 2022-08-18 14:25 | 20 | 6:08 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081800020 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 368 | 2022-08-18 | 7360 | keep | 0 | Aug | 2022 | 0.0050129 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-18 08:18 | 2022-08-18 12:49 | 7 | 4:31 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR PAJARO CRUZO FASE | R22081800251 | New_Event | Animals | Include | Include | Wildlife | 271 | 2022-08-18 | 1897 | keep | 0 | Aug | 2022 | 0.001292 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-08-18 08:23 | 2022-08-18 19:20 | 1 | 10:57 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800022 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 657 | 2022-08-18 | 657 | keep | 0 | Aug | 2022 | 0.00044748 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-18 08:28 | 2022-08-18 11:59 | 15 | 3:31 | P | NO SE REPORTO CAUSA | 3 X 10 EN MONTURA BURGER KING Y 3 X 50 EN C/L | S22081800107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-08-18 | 3165 | keep | 0 | Aug | 2022 | 0.0021557 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-18 08:30 | 2022-08-18 08:36 | 4192 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE ENERGIZO 75 % EN SERVICIO | R22081800150 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-08-18 | 25152 | keep | 0 | Aug | 2022 | 0.017131 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-18 08:30 | 2022-08-18 09:49 | 15 | 1:19 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | C22081800053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-08-18 | 1185 | keep | 0 | Aug | 2022 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-18 08:34 | 2022-08-18 11:53 | 1 | 3:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R22081800204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-08-18 | 199 | keep | 0 | Aug | 2022 | 0.00013554 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-18 08:36 | 2022-08-18 08:59 | 1905 | 0:23 | P | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE ENERGIZO 100% EN SERVICIO | R22081800150 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-08-18 | 43815 | keep | 0 | Aug | 2022 | 0.029842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-18 08:37 | 2022-08-18 10:54 | 12 | 2:17 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | P22081800113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 137 | 2022-08-18 | 1644 | keep | 0 | Aug | 2022 | 0.0011197 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-18 08:39 | 2022-08-18 13:57 | 12 | 5:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA ABIERTA (TRASPATIO) | B22081800137 | New_Event | Secondary Wire Break | Include | Include | Equipment | 318 | 2022-08-18 | 3816 | keep | 0 | Aug | 2022 | 0.0025991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-08-18 08:43 | 2022-08-18 09:45 | 30 | 1:02 | P | ANIMAL | 1 X 6 EN C/L AVE CRUZO LINEAS | P22081800116 | New_Event | Animals | Include | Include | Wildlife | 62 | 2022-08-18 | 1860 | keep | 0 | Aug | 2022 | 0.0012668 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-18 08:47 | 2022-08-19 14:30 | 6 | 29:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CERRO TRANSFORMADOR QUE SE HABIA DEJADO ABIERTO PARA REPARAR LINEA SECUNDARIA ROTA | A22081800027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1783 | 2022-08-18 | 10698 | keep | 0 | Aug | 2022 | 0.0072864 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-18 08:52 | 2022-08-18 13:50 | 1 | 4:58 | P | NO SE REPORTO CAUSA | 1X50 EN C/L Y 1X30 EN RISER | B22081800145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 298 | 2022-08-18 | 298 | keep | 0 | Aug | 2022 | 0.00020297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-18 08:52 | 2022-08-18 20:50 | 25 | 11:58 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE PRIMARIO PARTIDO | P22081800122 | New_Event | Primary Pole Failure | Include | Include | Equipment | 718 | 2022-08-18 | 17950 | keep | 0 | Aug | 2022 | 0.012226 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-18 08:54 | 2022-08-18 18:51 | 4 | 9:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA POR UNO DE 50KVA | M22081800023 | New_Event | Service Transformer Failure | Include | Include | Equipment | 597 | 2022-08-18 | 2388 | keep | 0 | Aug | 2022 | 0.0016265 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-08-18 08:59 | 2022-08-18 14:10 | 65 | 5:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE LEVANTO CONDUCTOR | R22081800218 | New_Event | Primary Wire Break | Include | Include | Equipment | 311 | 2022-08-18 | 20215 | keep | 0 | Aug | 2022 | 0.013768 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-08-18 08:59 | 2022-08-18 18:35 | 15 | 9:36 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800029 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 576 | 2022-08-18 | 8640 | keep | 0 | Aug | 2022 | 0.0058847 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-18 09:01 | 2022-08-18 18:43 | 16 | 9:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO/LEVANTO SECUNDARIA (TRASPATIO) | B22081800149 | New_Event | Secondary Wire Break | Include | Include | Equipment | 582 | 2022-08-18 | 9312 | keep | 0 | Aug | 2022 | 0.0063424 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
UTUADO | 2022-08-18 09:01 | 2022-08-18 13:10 | 3 | 4:09 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGA ELECTRICA | P22081800126 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 249 | 2022-08-18 | 747 | keep | 0 | Aug | 2022 | 0.00050878 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-08-18 09:03 | 2022-08-18 11:48 | 1 | 2:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR PORTAFUSIBLE | R22081800219 | New_Event | Cutout Failure | Include | Include | Equipment | 165 | 2022-08-18 | 165 | keep | 0 | Aug | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-18 09:06 | 2022-08-18 11:09 | 30 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | R22081800221 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2022-08-18 | 3690 | keep | 0 | Aug | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-08-18 09:12 | 2022-08-18 10:46 | 20 | 1:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR PORTAFUSIBLE | R22081800225 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2022-08-18 | 1880 | keep | 0 | Aug | 2022 | 0.0012805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-18 09:13 | 2022-08-18 14:11 | 30 | 4:58 | P | DESGANCHE | DESGANCHE Y 1 X 80 EN C/L | S22081800128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-08-18 | 8940 | keep | 0 | Aug | 2022 | 0.006089 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-18 09:14 | 2022-08-18 10:48 | 1715 | 1:34 | T | DESGANCHE | CARGA TRANSFERIDA AL 1708-03 SE ABRIO LA SALIDA DEL SOTERRADO HACIA AEREO - SE CONTINUA PATRULLANDO - FALTA 90% DEL 1708-03 POR ENTRAR EN SERVICIO | B22081800166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-08-18 | 161210 | keep | 0 | Aug | 2022 | 0.1098 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2022-08-18 09:14 | 2022-08-18 10:48 | 1498 | 1:34 | T | DESGANCHE | LLEVA LA CARGA DEL 1708-02 SE SECCIONALIZO AVERIA POR DESGANCHE PRIMARIO EN VARIOS PUNTOS - FALTA 90% DE LA CARGA DEL 1708-03 | B22081800166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-08-18 | 140812 | keep | 0 | Aug | 2022 | 0.095906 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BARRANQUITAS | 2022-08-18 09:14 | 2022-08-18 15:40 | 85 | 6:26 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | C22081800061 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 386 | 2022-08-18 | 32810 | keep | 0 | Aug | 2022 | 0.022347 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2022-08-18 09:18 | 2022-08-18 11:45 | 10 | 2:27 | P | MAL TIEMPO/RAYOS | 1X15 EN XMR POR RAYO AL CAER | B22081800167 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 147 | 2022-08-18 | 1470 | keep | 0 | Aug | 2022 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-18 09:18 | 2022-08-18 09:19 | 1570 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081800169 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1570 | keep | 0 | Aug | 2022 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
BAYAMON | 2022-08-18 09:25 | 2022-08-18 10:17 | 988 | 0:52 | P | DESGANCHE | SE REALIZO DESGANCHE A VARETA (DESDE EL PISO) EN SERVICIO EL 50% DE LA CARGA DEL 1711-05 QUE FALTABA | B22081800059 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-08-18 | 51376 | keep | 0 | Aug | 2022 | 0.034992 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-18 09:26 | 2022-08-18 15:15 | 2 | 5:49 | P | PROBLEMA DEL CLIENTE | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE DEJO SECCIONALIZADO SUBESTACION PRIVADA PARA CLIENTE REPARE | C22081800068 | New_Event | Customer-Related Interruption | Include | Include | Public | 349 | 2022-08-18 | 698 | keep | 0 | Aug | 2022 | 0.0004754 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-18 09:34 | 2022-08-18 11:17 | 50 | 1:43 | P | NO SE REPORTO CAUSA | 1X65 EN RISER, 1X50 EN OTRO RISER Y 2X50 EN OTRO RISER | B22081800187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-08-18 | 5150 | keep | 0 | Aug | 2022 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-18 09:35 | 2022-08-18 12:07 | 100 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | 1X100 EN C/L Y SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B22081800189 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2022-08-18 | 15200 | keep | 0 | Aug | 2022 | 0.010353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-08-18 09:36 | 2022-08-19 14:30 | 10 | 28:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 37.5 KVA | C22081800071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1734 | 2022-08-18 | 17340 | keep | 0 | Aug | 2022 | 0.01181 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-18 09:45 | 2022-08-18 17:08 | 10 | 7:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO 25 KVA X 37.5 KVA | C22081700287 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 443 | 2022-08-18 | 4430 | keep | 0 | Aug | 2022 | 0.0030173 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-18 09:46 | 2022-08-18 11:07 | 10 | 1:21 | P | TRANSFORMADOR AVERIADO | REEMPLAZAR TRANSFORMADOR QUEMADO DE 25KVA X 37.5KVA | A22081800017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 81 | 2022-08-18 | 810 | keep | 0 | Aug | 2022 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-18 09:50 | 2022-08-18 12:49 | 100 | 2:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R22081800234 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-08-18 | 17900 | keep | 0 | Aug | 2022 | 0.012192 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-18 09:50 | 2022-08-18 20:30 | 80 | 10:40 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22081800037 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 640 | 2022-08-18 | 51200 | keep | 0 | Aug | 2022 | 0.034872 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-18 09:51 | 2022-08-18 12:45 | 1500 | 2:54 | P | CONDUCTOR ROTO O ABIERTO | REPARAR BAJANTE PRIMARIO EN MACHETE | M22081800039 | New_Event | Primary Wire Break | Include | Include | Equipment | 174 | 2022-08-18 | 261000 | keep | 0 | Aug | 2022 | 0.17777 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2022-08-18 09:53 | 2022-08-18 09:56 | 5809 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1710-02 | B22081800205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-18 | 17427 | keep | 0 | Aug | 2022 | 0.011869 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BARRANQUITAS | 2022-08-18 09:53 | 2022-08-19 07:14 | 10 | 21:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22081800074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1281 | 2022-08-18 | 12810 | keep | 0 | Aug | 2022 | 0.0087248 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-18 09:54 | 2022-08-18 11:09 | 314 | 1:15 | T | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO CON VARETA | S22081800139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-08-18 | 23550 | keep | 0 | Aug | 2022 | 0.01604 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
ARECIBO | 2022-08-18 09:55 | 2022-08-18 13:30 | 50 | 3:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22081800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-08-18 | 10750 | keep | 0 | Aug | 2022 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-18 09:57 | 2022-08-18 15:45 | 15 | 5:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C22081800077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 348 | 2022-08-18 | 5220 | keep | 0 | Aug | 2022 | 0.0035553 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-18 09:58 | 2022-08-18 09:59 | 2203 | 0:01 | T | DESGANCHE | RECIERRE | C22081800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-18 | 2203 | keep | 0 | Aug | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-08-18 09:59 | 2022-08-18 19:29 | 1 | 9:30 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU 2 | S22081800142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 570 | 2022-08-18 | 570 | keep | 0 | Aug | 2022 | 0.00038822 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-18 09:59 | 2022-08-18 16:21 | 110 | 6:22 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA CRUCE POR RAMA | C22081800136 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 382 | 2022-08-18 | 42020 | keep | 0 | Aug | 2022 | 0.02862 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
UTUADO | 2022-08-18 09:59 | 2022-08-18 13:50 | 3 | 3:51 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800042 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 231 | 2022-08-18 | 693 | keep | 0 | Aug | 2022 | 0.000472 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-08-18 10:00 | 2022-08-18 12:42 | 7 | 2:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR PORTAFUSIBLE | R22081800258 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2022-08-18 | 1134 | keep | 0 | Aug | 2022 | 0.00077236 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-18 10:06 | 2022-08-18 10:09 | 761 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1310-04 LLEVANDO CARGA 1421-01 SE CERRO POR SCADA | S22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-18 | 2283 | keep | 0 | Aug | 2022 | 0.0015549 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-08-18 10:06 | 2022-08-18 10:09 | 1498 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1310-04 LLEVANDO CARGA 1421-01 SE CERRO POR SCADA | S22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-18 | 4494 | keep | 0 | Aug | 2022 | 0.0030608 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
MAYAGÃœEZ | 2022-08-18 10:10 | 2022-08-18 19:52 | 40 | 9:42 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 582 | 2022-08-18 | 23280 | keep | 0 | Aug | 2022 | 0.015856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-18 10:12 | 2022-08-18 13:01 | 50 | 2:49 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22081800222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-08-18 | 8450 | keep | 0 | Aug | 2022 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-18 10:13 | 2022-08-18 16:00 | 1 | 5:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN BANCO DE XMR SE REMPLAZO PORTAFUSIBLE | R22081800237 | New_Event | Cutout Failure | Include | Include | Equipment | 347 | 2022-08-18 | 347 | keep | 0 | Aug | 2022 | 0.00023634 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-18 10:16 | 2022-08-18 13:05 | 6 | 2:49 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800043 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 169 | 2022-08-18 | 1014 | keep | 0 | Aug | 2022 | 0.00069063 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-18 10:19 | 2022-08-18 10:22 | 225 | 0:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2022-08-18 | 675 | keep | 0 | Aug | 2022 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-18 10:19 | 2022-08-18 10:22 | 870 | 0:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22081800000 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2022-08-18 | 2610 | keep | 0 | Aug | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-08-18 10:22 | 2022-08-18 15:32 | 100 | 5:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON 2 CAJAS PRIMARIAS DESGANCHE Y 3 X 100 EN C/L | S22081800074 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 310 | 2022-08-18 | 31000 | keep | 0 | Aug | 2022 | 0.021114 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-18 10:26 | 2022-08-18 12:00 | 80 | 1:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M22081800057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-08-18 | 7520 | keep | 0 | Aug | 2022 | 0.0051218 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-18 10:27 | 2022-08-18 11:22 | 1 | 0:55 | P | NO SE REPORTO CAUSA | 2 X 40 EN C/L | C22081800090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 55 | 2022-08-18 | 55 | keep | 0 | Aug | 2022 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-18 10:27 | 2022-08-18 14:24 | 20 | 3:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22081800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2022-08-18 | 4740 | keep | 0 | Aug | 2022 | 0.0032284 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-18 10:31 | 2022-08-18 15:16 | 106 | 4:45 | P | DESGANCHE | 1X50 EN C/L | B22081800232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-08-18 | 30210 | keep | 0 | Aug | 2022 | 0.020576 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
BAYAMON | 2022-08-18 10:34 | 2022-08-18 18:58 | 94 | 8:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2X80 EN C/L SE REMPLAZO AISLADOR | S22081800163 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 504 | 2022-08-18 | 47376 | keep | 0 | Aug | 2022 | 0.032268 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
CANOVANAS | 2022-08-18 10:36 | 2022-08-18 15:40 | 12 | 5:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-34 CON PROBLEMAS DE VOLTAJE | R22081800297 | New_Event | Service Transformer Failure | Include | Include | Equipment | 304 | 2022-08-18 | 3648 | keep | 0 | Aug | 2022 | 0.0024846 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-18 10:42 | 2022-08-19 08:30 | 4 | 21:48 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETE PARA LEVANTAR LINEA | S22081800167 | New_Event | Primary Wire Break | Include | Include | Equipment | 1308 | 2022-08-18 | 5232 | keep | 0 | Aug | 2022 | 0.0035635 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-08-18 10:47 | 2022-08-18 15:15 | 100 | 4:28 | P | DESGANCHE | 3 X 50 Y 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22081800097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-08-18 | 26800 | keep | 0 | Aug | 2022 | 0.018253 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-18 10:47 | 2022-08-18 11:50 | 5 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | P22081800157 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2022-08-18 | 315 | keep | 0 | Aug | 2022 | 0.00021455 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-18 10:48 | 2022-08-18 11:57 | 1348 | 1:09 | P | DESGANCHE | LLEVA LA CARGA DEL 1708-02 SE SECCIONALIZO AVERIA POR DESGANCHE PRIMARIO EN VARIOS PUNTOS - FALTA 80% DEL 1708-03 | B22081800166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-08-18 | 93012 | keep | 0 | Aug | 2022 | 0.06335 | 0.00091812 | Sustained | FALSE | FALSE | Not_TMED_Event | 1348
CANOVANAS | 2022-08-18 10:50 | 2022-08-18 14:05 | 25 | 3:15 | P | DESGANCHE | 2 X 40 EN C/L SE DESGANCHO | R22081800159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-08-18 | 4875 | keep | 0 | Aug | 2022 | 0.0033203 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-18 10:51 | 2022-08-18 15:53 | 10 | 5:02 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22081800239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 302 | 2022-08-18 | 3020 | keep | 0 | Aug | 2022 | 0.0020569 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-18 10:52 | 2022-08-18 14:52 | 1 | 4:00 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22081800098 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 240 | 2022-08-18 | 240 | keep | 0 | Aug | 2022 | 0.00016346 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-18 10:55 | 2022-08-18 10:58 | 723 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1711-05 | B22081800241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-18 | 2169 | keep | 0 | Aug | 2022 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-18 10:55 | 2022-08-18 10:58 | 1976 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1711-02 | B22081800241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-18 | 5928 | keep | 0 | Aug | 2022 | 0.0040375 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 874 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 CARGA 20% POR 3604-06 | C22081800104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 874 | keep | 0 | Aug | 2022 | 0.00059528 | 0.00059528 | Momentary | FALSE | FALSE | Not_TMED_Event | 874
BARRANQUITAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22081800102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 1565 | keep | 0 | Aug | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22081800102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 976 | keep | 0 | Aug | 2022 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22081800102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 548 | keep | 0 | Aug | 2022 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22081800103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 315 | keep | 0 | Aug | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22081800103 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 870 | keep | 0 | Aug | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 LLEVA 20% DEL 3010-01 | C22081800104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 2906 | keep | 0 | Aug | 2022 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2022-08-18 10:57 | 2022-08-18 10:58 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22081800104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-18 | 2343 | keep | 0 | Aug | 2022 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
BAYAMON | 2022-08-18 10:58 | 2022-08-18 11:20 | 100 | 0:22 | P | NO SE REPORTO CAUSA | 1X50 EN RISER | B22081800242 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 22 | 2022-08-18 | 2200 | keep | 0 | Aug | 2022 | 0.0014984 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-18 11:07 | 2022-08-18 11:14 | 2132 | 0:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22081800055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-18 | 14924 | keep | 0 | Aug | 2022 | 0.010165 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-08-18 11:07 | 2022-08-18 11:14 | 2366 | 0:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22081800055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-18 | 16562 | keep | 0 | Aug | 2022 | 0.01128 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-08-18 11:07 | 2022-08-18 11:14 | 1976 | 0:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22081800055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-18 | 13832 | keep | 0 | Aug | 2022 | 0.0094209 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-08-18 11:07 | 2022-08-18 11:14 | 3688 | 0:07 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22081800055 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-18 | 25816 | keep | 0 | Aug | 2022 | 0.017583 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-08-18 11:07 | 2022-08-18 16:44 | 3070 | 5:37 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800470 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 337 | 2022-08-18 | 1034590 | keep | 0 | Aug | 2022 | 0.70465 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-08-18 11:07 | 2022-08-18 16:44 | 2735 | 5:37 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800470 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 337 | 2022-08-18 | 921695 | keep | 0 | Aug | 2022 | 0.62776 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-08-18 11:07 | 2022-08-18 16:44 | 1070 | 5:37 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800470 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 337 | 2022-08-18 | 360590 | keep | 0 | Aug | 2022 | 0.2456 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-08-18 11:07 | 2022-08-18 19:20 | 1647 | 8:13 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800471 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 493 | 2022-08-18 | 811971 | keep | 0 | Aug | 2022 | 0.55303 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-08-18 11:07 | 2022-08-18 19:20 | 3295 | 8:13 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800471 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 493 | 2022-08-18 | 1624435 | keep | 0 | Aug | 2022 | 1.1064 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-08-18 11:07 | 2022-08-18 19:20 | 1180 | 8:13 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800471 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 493 | 2022-08-18 | 581740 | keep | 0 | Aug | 2022 | 0.39622 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-08-18 11:07 | 2022-08-18 16:44 | 320 | 5:37 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800472 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 337 | 2022-08-18 | 107840 | keep | 0 | Aug | 2022 | 0.073449 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-08-18 11:07 | 2022-08-18 16:44 | 2234 | 5:37 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 SE ELIMINO OVERHEAD GROUND-WIRE PARTIDO Y SE REMPLAZARON (3) FUSIBLES DE LA ALTA MEDIANTE G.O.I. BY-220818-05 | B22081800472 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 337 | 2022-08-18 | 752858 | keep | 0 | Aug | 2022 | 0.51277 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2022-08-18 11:14 | 2022-08-19 12:07 | 10 | 24:53 | P | TRANSFORMADOR AVERIADO | REEMPLAZAR TRANSFORMADOR QUEMADO DE 25KVA X 37.5KVA | A22081800017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1493 | 2022-08-18 | 14930 | keep | 0 | Aug | 2022 | 0.010169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-18 11:20 | 2022-08-18 12:29 | 723 | 1:09 | T | AISLADOR ROTO, PARTIDO O SAFADO | LLEVA LA CARGA DEL 1711-05 SE ABRIO EL AMARRE ENTRE AMBOS INTERRUPTORES PARA REMPLAZO DE DISCO PRIMARIO PARTIDO MEDIANTE G.O.I. BY-220818-03 - FALTA POR ENTRAR LA CARGA DEL 1711-05 | B22081800263 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 69 | 2022-08-18 | 49887 | keep | 0 | Aug | 2022 | 0.033978 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-18 11:20 | 2022-08-18 14:39 | 1976 | 3:19 | T | AISLADOR ROTO, PARTIDO O SAFADO | CARGA TRANSFERIDA AL 1711-02 - SE REMPLAZO DISCO PRIMARIO PARTIDO MEDIENTE G.O.I. BY-220818-03 - EN SERVICIO TOTAL | B22081800263 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 199 | 2022-08-18 | 393224 | keep | 0 | Aug | 2022 | 0.26782 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
UTUADO | 2022-08-18 11:23 | 2022-08-18 16:45 | 2 | 5:22 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A22081800058 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 322 | 2022-08-18 | 644 | keep | 0 | Aug | 2022 | 0.00043863 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-18 11:27 | 2022-08-19 12:51 | 15 | 25:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR SE REMPLAZO 125PIES 3/2 TRAS PATIO | S22081800187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1524 | 2022-08-18 | 22860 | keep | 0 | Aug | 2022 | 0.01557 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-18 11:41 | 2022-08-18 19:08 | 198 | 7:27 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE LLEVO CONDUCTOR PRIMARIO AL AISLADOR | C22081800117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 447 | 2022-08-18 | 88506 | keep | 0 | Aug | 2022 | 0.060281 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-08-18 11:57 | 2022-08-18 12:27 | 1198 | 0:30 | P | DESGANCHE | LLEVA LA CARGA DEL 1708-02 SE SECCIONALIZO AVERIA POR DESGANCHE PRIMARIO EN VARIOS PUNTOS - FALTA 75% DEL 1708-03 | B22081800166 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-08-18 | 35940 | keep | 0 | Aug | 2022 | 0.024479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-18 12:00 | 2022-08-18 14:10 | 12 | 2:10 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE T#1 50KVA A 7620 VOLTS CON PERDIDA DE ACEITE POR TRANSFORMADOR 75KVA A 7620VOLTS | P22081800174 | New_Event | Service Transformer Failure | Include | Include | Equipment | 130 | 2022-08-18 | 1560 | keep | 0 | Aug | 2022 | 0.0010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-18 12:07 | 2022-08-18 13:55 | 12 | 1:48 | P | SECUNDARIA/DESGANCHE | 1X10 EN XMR POR DESGANCHE SECUNDARIO | B22081800311 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 108 | 2022-08-18 | 1296 | keep | 0 | Aug | 2022 | 0.0008827 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-08-18 12:09 | 2022-08-18 12:18 | 2 | 0:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO TRANSFORMADOR | R22081800251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-08-18 | 18 | keep | 0 | Aug | 2022 | 1.226e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-18 12:13 | 2022-08-18 18:04 | 370 | 5:51 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22081800316 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 351 | 2022-08-18 | 129870 | keep | 0 | Aug | 2022 | 0.088454 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
VEGA BAJA | 2022-08-18 12:16 | 2022-08-18 15:25 | 150 | 3:09 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081800076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-08-18 | 28350 | keep | 0 | Aug | 2022 | 0.019309 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-18 12:18 | 2022-08-18 14:07 | 10 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L SE REMPLAZO CAJA PRIMARIA | B22081800321 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2022-08-18 | 1090 | keep | 0 | Aug | 2022 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-18 12:20 | 2022-08-18 21:03 | 37 | 8:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 Y 1 X80 EN C/L SE REMPLAZO AISLACION Y SE REPARO PUENTE PRIMARIO | S22081800198 | New_Event | Primary Wire Break | Include | Include | Equipment | 523 | 2022-08-18 | 19351 | keep | 0 | Aug | 2022 | 0.01318 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2022-08-18 12:27 | 2022-08-18 13:12 | 1123 | 0:45 | P | DESGANCHE | LLEVA LA CARGA DEL 1708-02 SE SECCIONALIZO AVERIA POR DESGANCHE PRIMARIO EN VARIOS PUNTOS - EN SERVICIO EL 75% QUE FALTABA DEL DEL 1708-03 (TODO EN SERVICIO) | B22081800166 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-08-18 | 50535 | keep | 0 | Aug | 2022 | 0.034419 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-18 12:30 | 2022-08-18 14:50 | 65 | 2:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22081800081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-08-18 | 9100 | keep | 0 | Aug | 2022 | 0.006198 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-08-18 12:39 | 2022-08-18 14:40 | 1228 | 2:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14400 DE GAUTIER BENITEZ A VEREDA SE REPARO LA LINEA | C22081800189 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2022-08-18 | 148588 | keep | 0 | Aug | 2022 | 0.1012 | 0.00083639 | Sustained | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2022-08-18 12:39 | 2022-08-18 14:40 | 1271 | 2:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14400 DE GAUTIER BENITEZ A VEREDA SE REPARO LA LINEA | C22081800189 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2022-08-18 | 153791 | keep | 0 | Aug | 2022 | 0.10475 | 0.00086567 | Sustained | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2022-08-18 12:39 | 2022-08-18 14:40 | 1893 | 2:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14400 DE GAUTIER BENITEZ A VEREDA SE REPARO LA LINEA | C22081800189 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2022-08-18 | 229053 | keep | 0 | Aug | 2022 | 0.15601 | 0.0012893 | Sustained | FALSE | FALSE | Not_TMED_Event | 1893
CAGUAS | 2022-08-18 12:39 | 2022-08-18 14:40 | 473 | 2:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 14400 DE GAUTIER BENITEZ A VEREDA SE REPARO LA LINEA | C22081800189 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 121 | 2022-08-18 | 57233 | keep | 0 | Aug | 2022 | 0.038981 | 0.00032216 | Sustained | FALSE | FALSE | Not_TMED_Event | 473
BARRANQUITAS | 2022-08-18 12:40 | 2022-08-19 11:52 | 47 | 23:12 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22081800137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1392 | 2022-08-18 | 65424 | keep | 0 | Aug | 2022 | 0.04456 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2022-08-18 12:42 | 2022-08-18 12:43 | 1617 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1617 | keep | 0 | Aug | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
BAYAMON | 2022-08-18 12:43 | 2022-08-18 12:45 | 5809 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA LA CARGA DEL 1710-02 | B22081800357 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-18 | 11618 | keep | 0 | Aug | 2022 | 0.007913 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
CAGUAS | 2022-08-18 12:46 | 2022-08-18 12:47 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22081800146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1702 | keep | 0 | Aug | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
UTUADO | 2022-08-18 12:46 | 2022-08-18 15:05 | 15 | 2:19 | P | MAL TIEMPO/RAYOS | 3 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800085 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 139 | 2022-08-18 | 2085 | keep | 0 | Aug | 2022 | 0.0014201 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-08-18 12:47 | 2022-08-18 14:10 | 50 | 1:23 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22081800186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-08-18 | 4150 | keep | 0 | Aug | 2022 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-18 12:50 | 2022-08-18 18:21 | 26 | 5:31 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S22081800210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-08-18 | 8606 | keep | 0 | Aug | 2022 | 0.0058615 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2022-08-18 12:52 | 2022-08-19 14:12 | 1408 | 25:20 | T | CABLE SOTERRADO AVERIADO | LLEVABA LA CARGA DEL 1714-03, SALIDA DEL 1714-02 ESTA AVERIADA, SE TRANSPOSICIONARON AMBOS INTERRUPTORES MEDIANTE G.O.I. BY-220818-04 - (ACTUALMENTE EL 1714-03 QUEDO LLEVANDO LA CARGA DEL 1714-02) TODO QUEDO EN SERVICIO | B22081800195 | New_Event | UG Cable Fault | Include | Include | Equipment | 1520 | 2022-08-18 | 2140160 | keep | 0 | Aug | 2022 | 1.4577 | 0.00095898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2022-08-18 12:52 | 2022-08-19 14:12 | 455 | 25:20 | T | CABLE SOTERRADO AVERIADO | SU CARGA ESTABA TRANSFERIDA AL 1714-02, PERO LA SALIDA DEL 1714-02 ESTA AVERIADA, SE TRANSPOSICIONARON AMBOS INTERRUPTORES MEDIANTE G.O.I. BY-220818-04 - (ACTUALMENTE EL 1714-03 QUEDO LLEVANDO LA CARGA DEL 1714-02) TODO QUEDO EN SERVICIO | B22081800195 | New_Event | UG Cable Fault | Include | Include | Equipment | 1520 | 2022-08-18 | 691600 | keep | 0 | Aug | 2022 | 0.47105 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2022-08-18 12:57 | 2022-08-18 12:58 | 414 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE | S22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 414 | keep | 0 | Aug | 2022 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
BARRANQUITAS | 2022-08-18 12:57 | 2022-08-18 16:13 | 14 | 3:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | C22081800153 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 196 | 2022-08-18 | 2744 | keep | 0 | Aug | 2022 | 0.0018689 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2022-08-18 12:59 | 2022-08-18 13:00 | 327 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22081800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 327 | keep | 0 | Aug | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
FAJARDO | 2022-08-18 13:00 | 2022-08-18 15:06 | 15 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22081800269 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-08-18 | 1890 | keep | 0 | Aug | 2022 | 0.0012873 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-08-18 13:05 | 2022-08-18 13:52 | 1 | 0:47 | P | NO SE REPORTO CAUSA | 1 X 20 EN C/L Y 1 X 15 EN BANCO DE XMR | C22081800156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-08-18 | 47 | keep | 0 | Aug | 2022 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-18 13:12 | 2022-08-18 14:31 | 45 | 1:19 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22081800217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-08-18 | 3555 | keep | 0 | Aug | 2022 | 0.0024213 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
YAUCO | 2022-08-18 13:23 | 2022-08-18 16:55 | 5 | 3:32 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REMOVIO ARBUSTO DE LINEA SECUNDARIA | M22081800107 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 212 | 2022-08-18 | 1060 | keep | 0 | Aug | 2022 | 0.00072196 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-18 13:42 | 2022-08-18 16:25 | 1 | 2:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | A22081800101 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2022-08-18 | 163 | keep | 0 | Aug | 2022 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-18 13:43 | 2022-08-18 15:12 | 200 | 1:29 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | M22081800101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-08-18 | 17800 | keep | 0 | Aug | 2022 | 0.012123 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-18 13:44 | 2022-08-18 15:36 | 15 | 1:52 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA - X - 50KVA | B22081800414 | New_Event | Service Transformer Failure | Include | Include | Equipment | 112 | 2022-08-18 | 1680 | keep | 0 | Aug | 2022 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-18 13:46 | 2022-08-18 17:51 | 20 | 4:05 | P | CONDUCTOR ROTO O ABIERTO | 1X50 EN PROVISIONAL AEREO Y SE REPARO/SUBIO CONDUCTOR PRIMARIO DEL SUELO | B22081800416 | New_Event | Primary Wire Break | Include | Include | Equipment | 245 | 2022-08-18 | 4900 | keep | 0 | Aug | 2022 | 0.0033374 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-18 13:54 | 2022-08-18 17:21 | 80 | 3:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X100 EN C/L POR LLUVIA | B22081800424 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 207 | 2022-08-18 | 16560 | keep | 0 | Aug | 2022 | 0.011279 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-08-18 14:01 | 2022-08-18 17:21 | 223 | 3:20 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN EL SUELO | C22081800188 | New_Event | Primary Wire Break | Include | Include | Equipment | 200 | 2022-08-18 | 44600 | keep | 0 | Aug | 2022 | 0.030377 | 0.00015188 | Sustained | FALSE | FALSE | Not_TMED_Event | 223
MAYAGÃœEZ | 2022-08-18 14:01 | 2022-08-18 16:46 | 50 | 2:45 | P | ARBOL SOBRE LINEA | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081800115 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 165 | 2022-08-18 | 8250 | keep | 0 | Aug | 2022 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-18 14:02 | 2022-08-18 15:14 | 30 | 1:12 | P | DESGANCHE | 1X65 EN C/L | B22081800432 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-08-18 | 2160 | keep | 0 | Aug | 2022 | 0.0014712 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-18 14:06 | 2022-08-18 19:15 | 6 | 5:09 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR RAYOS | M22081800116 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 309 | 2022-08-18 | 1854 | keep | 0 | Aug | 2022 | 0.0012628 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-18 14:07 | 2022-08-18 18:20 | 10 | 4:13 | P | NO SE REPORTO CAUSA | 1X20 EN RISER | S22081800235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2022-08-18 | 2530 | keep | 0 | Aug | 2022 | 0.0017232 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-18 14:08 | 2022-08-18 17:17 | 10 | 3:09 | P | MAL TIEMPO/RAYOS | 1X15 EN XMR | B22081800436 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 189 | 2022-08-18 | 1890 | keep | 0 | Aug | 2022 | 0.0012873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-18 14:15 | 2022-08-18 15:48 | 1527 | 1:33 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTES PRIMARIOS | A22081800106 | New_Event | Primary Wire Break | Include | Include | Equipment | 93 | 2022-08-18 | 142011 | keep | 0 | Aug | 2022 | 0.096723 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
PONCE | 2022-08-18 14:18 | 2022-08-18 17:00 | 250 | 2:42 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA POR DESGANCHE | P22081800224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-08-18 | 40500 | keep | 0 | Aug | 2022 | 0.027584 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-08-18 14:19 | 2022-08-18 20:51 | 50 | 6:32 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S22081800241 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 392 | 2022-08-18 | 19600 | keep | 0 | Aug | 2022 | 0.013349 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-18 14:28 | 2022-08-18 17:38 | 3 | 3:10 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR RAYOS | M22081800118 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 190 | 2022-08-18 | 570 | keep | 0 | Aug | 2022 | 0.00038822 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-18 14:33 | 2022-08-19 09:55 | 60 | 19:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P22081800235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1162 | 2022-08-18 | 69720 | keep | 0 | Aug | 2022 | 0.047486 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-18 14:36 | 2022-08-18 16:05 | 40 | 1:29 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | R22081800266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-08-18 | 3560 | keep | 0 | Aug | 2022 | 0.0024247 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-18 14:37 | 2022-08-18 22:01 | 30 | 7:24 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | S22081800246 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 444 | 2022-08-18 | 13320 | keep | 0 | Aug | 2022 | 0.0090722 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-18 14:40 | 2022-08-18 16:49 | 6 | 2:09 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA RETIRAR SECUNDARIA PARTIDA POR CAMION. | S22081800252 | New_Event | Damage From Public | Include | Include | Public | 129 | 2022-08-18 | 774 | keep | 0 | Aug | 2022 | 0.00052717 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-18 14:50 | 2022-08-18 16:00 | 10 | 1:10 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO BAMBUS SOBRE LAS LINEAS | M22081800122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-08-18 | 700 | keep | 0 | Aug | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-18 14:56 | 2022-08-18 16:25 | 13 | 1:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C22081800126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 89 | 2022-08-18 | 1157 | keep | 0 | Aug | 2022 | 0.00078803 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2022-08-18 14:58 | 2022-08-18 18:05 | 3 | 3:07 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR POR RAYOS | M22081800128 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 187 | 2022-08-18 | 561 | keep | 0 | Aug | 2022 | 0.00038209 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-18 15:05 | 2022-08-19 12:39 | 12 | 21:34 | P | DESGANCHE | 2 X 10 EN TRANSFORMADOR DESGANCHE | S22081800255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1294 | 2022-08-18 | 15528 | keep | 0 | Aug | 2022 | 0.010576 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-08-18 15:06 | 2022-08-18 20:48 | 17 | 5:42 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZARON 2 TRANSFORMADORES DE 37.5 KVA X 37.5 KVA | C22081800217 | New_Event | Service Transformer Failure | Include | Include | Equipment | 342 | 2022-08-18 | 5814 | keep | 0 | Aug | 2022 | 0.0039599 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-08-18 15:11 | 2022-08-18 19:14 | 24 | 4:03 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO DEL SU-6A @ T-2 | B22081800481 | New_Event | UG Cable Fault | Include | Include | Equipment | 243 | 2022-08-18 | 5832 | keep | 0 | Aug | 2022 | 0.0039721 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
AGUADILLA | 2022-08-18 15:13 | 2022-08-18 17:00 | 5 | 1:47 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081800132 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 107 | 2022-08-18 | 535 | keep | 0 | Aug | 2022 | 0.00036439 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-08-18 15:17 | 2022-08-18 18:05 | 4 | 2:48 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800124 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 168 | 2022-08-18 | 672 | keep | 0 | Aug | 2022 | 0.0004577 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-08-18 15:21 | 2022-08-18 19:32 | 12 | 4:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA | C22081800225 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 251 | 2022-08-18 | 3012 | keep | 0 | Aug | 2022 | 0.0020515 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-08-18 15:28 | 2022-08-18 17:57 | 70 | 2:29 | P | DESGANCHE | 2X 80 EN CORTE DE LINEA POR DESGANCHE | M22081800129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-08-18 | 10430 | keep | 0 | Aug | 2022 | 0.0071038 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-08-18 15:28 | 2022-08-18 18:45 | 20 | 3:17 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 197 | 2022-08-18 | 3940 | keep | 0 | Aug | 2022 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-18 15:28 | 2022-08-18 19:00 | 20 | 3:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22081800127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-08-18 | 4240 | keep | 0 | Aug | 2022 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-18 15:44 | 2022-08-18 22:35 | 50 | 6:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S22081800265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 411 | 2022-08-18 | 20550 | keep | 0 | Aug | 2022 | 0.013997 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-18 15:48 | 2022-08-19 15:25 | 3 | 23:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 37.5KVA | A22081800007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1417 | 2022-08-18 | 4251 | keep | 0 | Aug | 2022 | 0.0028953 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2022-08-18 15:48 | 2022-08-19 12:32 | 10 | 20:44 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5KVA RELACIONADO A EVENTO A22081800014 | A22081800121 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1244 | 2022-08-18 | 12440 | keep | 0 | Aug | 2022 | 0.0084728 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-18 15:49 | 2022-08-18 19:10 | 1 | 3:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A22081800136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-08-18 | 201 | keep | 0 | Aug | 2022 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-18 15:55 | 2022-08-18 18:42 | 15 | 2:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | M22081800139 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 167 | 2022-08-18 | 2505 | keep | 0 | Aug | 2022 | 0.0017061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-18 16:03 | 2022-08-18 18:59 | 80 | 2:56 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA @ CAJA EN C/L | B22081800520 | New_Event | Primary Wire Break | Include | Include | Equipment | 176 | 2022-08-18 | 14080 | keep | 0 | Aug | 2022 | 0.0095898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-18 16:25 | 2022-08-20 21:06 | 8 | 52:41 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL @ T-68 | S22081800314 | New_Event | UG Cable Fault | Include | Include | Equipment | 3161 | 2022-08-18 | 25288 | keep | 0 | Aug | 2022 | 0.017224 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-08-18 16:36 | 2022-08-18 19:40 | 1 | 3:04 | P | DESGANCHE | 2 X 80 EN RISER SE RETIRO PENCA DE LA LINEA | C22081800259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-08-18 | 184 | keep | 0 | Aug | 2022 | 0.00012532 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-18 16:41 | 2022-08-18 19:23 | 60 | 2:42 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22081800541 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-08-18 | 9720 | keep | 0 | Aug | 2022 | 0.0066202 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-08-18 16:46 | 2022-08-18 20:19 | 83 | 3:33 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA SE DEJO SECCIONALIZADO POSTE PRIMARIO IMPACTADO POR VEHICULO | C22081800308 | New_Event | Damage From Public | Include | Include | Public | 213 | 2022-08-18 | 17679 | keep | 0 | Aug | 2022 | 0.012041 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
BARRANQUITAS | 2022-08-18 16:46 | 2022-08-19 09:26 | 120 | 16:40 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO PUENTE PRIMARIO AVERIDO | C22081800266 | New_Event | Primary Wire Break | Include | Include | Equipment | 1000 | 2022-08-18 | 120000 | keep | 0 | Aug | 2022 | 0.081731 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-08-18 16:49 | 2022-08-18 17:23 | 534 | 0:34 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1519-05 LLEVANDO 1519-01. SE RETIRO RAMA QUE CRUZO LINEAS Y SE CERRO POR SCADA | S22081800282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2022-08-18 | 18156 | keep | 0 | Aug | 2022 | 0.012366 | 0.0003637 | Sustained | FALSE | FALSE | Not_TMED_Event | 534
SAN JUAN | 2022-08-18 16:49 | 2022-08-18 17:23 | 558 | 0:34 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1519-05 LLEVANDO 1519-01. SE RETIRO RAMA QUE CRUZO LINEAS Y SE CERRO POR SCADA | S22081800282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2022-08-18 | 18972 | keep | 0 | Aug | 2022 | 0.012922 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
UTUADO | 2022-08-18 17:00 | 2022-08-18 21:40 | 10 | 4:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CREO EVENTO PARA ATENDER FALTA DE SERVICIO SE ABRIO TRANSFORMADOR REPARAR SECUNDARIA | A22081800145 | New_Event | Secondary Wire Break | Include | Include | Equipment | 280 | 2022-08-18 | 2800 | keep | 0 | Aug | 2022 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-18 17:05 | 2022-08-18 23:20 | 25 | 6:15 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800144 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 375 | 2022-08-18 | 9375 | keep | 0 | Aug | 2022 | 0.0063853 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-18 17:21 | 2022-08-18 20:20 | 598 | 2:59 | T | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO TRABAJADO CON GOI CG-220818-01A CARGA POR EL 3405-03 | C22081800277 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 179 | 2022-08-18 | 107042 | keep | 0 | Aug | 2022 | 0.072906 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-18 17:21 | 2022-08-18 17:23 | 1001 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA ABRIR MACHETES Y PODER SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO SE ESTA TRABAJANDO CON GOI CG-220818-01A 93% EN SERVICIO LLEVA LA CARGA DEL 3403-01 | C22081800277 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-08-18 | 2002 | keep | 0 | Aug | 2022 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
BARRANQUITAS | 2022-08-18 17:23 | 2022-08-18 20:20 | 71 | 2:57 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO TRABAJADO CON GOI CG-220818-01A | C22081800277 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 177 | 2022-08-18 | 12567 | keep | 0 | Aug | 2022 | 0.0085593 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
FAJARDO | 2022-08-18 17:30 | 2022-08-18 18:20 | 15 | 0:50 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22081800271 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2022-08-18 | 750 | keep | 0 | Aug | 2022 | 0.00051082 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-18 17:35 | 2022-08-18 23:33 | 40 | 5:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIAS FUERTES | M22081800154 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 358 | 2022-08-18 | 14320 | keep | 0 | Aug | 2022 | 0.0097533 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-08-18 17:41 | 2022-08-18 18:57 | 1 | 1:16 | P | DESGANCHE | 1 X 15 EN BANCO DE XMR SE DESGANCHO PRIMARIO | R22081800272 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-08-18 | 76 | keep | 0 | Aug | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-18 17:43 | 2022-08-18 19:15 | 5 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE LEVANTO CONDUCTOR SECUNDARIO | S22081800294 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2022-08-18 | 460 | keep | 0 | Aug | 2022 | 0.0003133 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-18 17:51 | 2022-08-19 10:00 | 30 | 16:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER Y 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22081800297 | New_Event | Cutout Failure | Include | Include | Equipment | 969 | 2022-08-18 | 29070 | keep | 0 | Aug | 2022 | 0.019799 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-18 17:51 | 2022-08-18 19:07 | 1 | 1:16 | P | NO SE REPORTO CAUSA | 1X65 EN RISER | S22081800298 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2022-08-18 | 76 | keep | 0 | Aug | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-18 18:00 | 2022-08-18 20:28 | 60 | 2:28 | P | CABLE SOTERRADO AVERIADO | SE ABRIO C/L PARA CONECTAR AEREO PROVISIONAL A T 50 Y RELOCALIZAR AEREO EXISTENTE A POSTE NUEVO | S22081700722 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 148 | 2022-08-18 | 8880 | keep | 0 | Aug | 2022 | 0.0060481 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-18 18:10 | 2022-08-18 22:18 | 7 | 4:08 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 248 | 2022-08-18 | 1736 | keep | 0 | Aug | 2022 | 0.0011824 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-18 18:20 | 2022-08-19 11:17 | 102 | 16:57 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22081800622 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1017 | 2022-08-18 | 103734 | keep | 0 | Aug | 2022 | 0.070653 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
CAGUAS | 2022-08-18 18:21 | 2022-08-18 20:40 | 127 | 2:19 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22081800295 | New_Event | Animals | Include | Include | Wildlife | 139 | 2022-08-18 | 17653 | keep | 0 | Aug | 2022 | 0.012023 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
YAUCO | 2022-08-18 18:57 | 2022-08-18 18:58 | 2011 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | BREAKER ABRIO NO CERRO SE CERRO POR CONTROL SCADA | P22081800279 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-18 | 2011 | keep | 0 | Aug | 2022 | 0.0013697 | 0.0013697 | Momentary | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2022-08-18 18:58 | 2022-08-18 21:15 | 670 | 2:17 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO EN TRONCAL DEL ALIMENTADOR | P22081800291 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 137 | 2022-08-18 | 91790 | keep | 0 | Aug | 2022 | 0.062518 | 0.00045633 | Sustained | FALSE | FALSE | Not_TMED_Event | 670
VEGA BAJA | 2022-08-18 19:01 | 2022-08-18 19:25 | 5 | 0:24 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 24 | 2022-08-18 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-18 19:14 | 2022-08-18 19:15 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22081800660 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-18 | 1362 | keep | 0 | Aug | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2022-08-18 19:15 | 2022-08-19 18:47 | 24 | 23:32 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO DEL SU-6A @ T-2 | B22081800481 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1412 | 2022-08-18 | 33888 | keep | 0 | Aug | 2022 | 0.023081 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-18 19:22 | 2022-08-19 09:05 | 96 | 13:43 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | R22081800283 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2022-08-18 | 79008 | keep | 0 | Aug | 2022 | 0.053812 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
AGUADILLA | 2022-08-18 19:24 | 2022-08-18 22:23 | 100 | 2:59 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081800161 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 179 | 2022-08-18 | 17900 | keep | 0 | Aug | 2022 | 0.012192 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-18 19:55 | 2022-08-19 12:54 | 1 | 16:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIA | A22081800165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1019 | 2022-08-18 | 1019 | keep | 0 | Aug | 2022 | 0.00069404 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-18 19:56 | 2022-08-18 22:40 | 5 | 2:44 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M22081800170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-08-18 | 820 | keep | 0 | Aug | 2022 | 0.0005585 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-18 20:01 | 2022-08-19 14:03 | 100 | 18:02 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22081800778 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1082 | 2022-08-18 | 108200 | keep | 0 | Aug | 2022 | 0.073695 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-08-18 20:19 | 2022-08-19 14:45 | 13 | 18:26 | P | CAUSAS EXTERNAS | 1 X 40 1 X 30 EN C/L SE REEMPLAZO POSTE PRIMARIO Y SE LEVANTO CONDUCTOR | C22081800308 | Partial_restoration | Damage From Public | Include | Include | Public | 1106 | 2022-08-18 | 14378 | keep | 0 | Aug | 2022 | 0.0097928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-18 20:25 | 2022-08-18 22:17 | 150 | 1:52 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081800178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-08-18 | 16800 | keep | 0 | Aug | 2022 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-08-18 20:30 | 2022-08-18 21:20 | 6 | 0:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN TRANSFORMADOR | A22081800171 | New_Event | Primary Wire Break | Include | Include | Equipment | 50 | 2022-08-18 | 300 | keep | 0 | Aug | 2022 | 0.00020433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-08-18 20:47 | 2022-08-18 21:39 | 20 | 0:52 | P | NO SE REPORTO CAUSA | 2X100 EN C/L | B22081800706 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-08-18 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-08-18 20:50 | 2022-08-18 21:26 | 508 | 0:36 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE INTERRUPTOR PARA CERRAR PUENTES Y CONCLUIR TRABAJOS DE REEMPLAZO DE POSTE PRIMARIO PARTIDO | P22081800308 | New_Event | Primary Pole Failure | Include | Include | Equipment | 36 | 2022-08-18 | 18288 | keep | 0 | Aug | 2022 | 0.012456 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
BAYAMON | 2022-08-18 20:50 | 2022-08-19 10:04 | 329 | 13:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L SE REMPLAZO CAJA PRIMARIA | B22081800709 | New_Event | Cutout Failure | Include | Include | Equipment | 794 | 2022-08-18 | 261226 | keep | 0 | Aug | 2022 | 0.17792 | 0.00022408 | Sustained | FALSE | FALSE | Not_TMED_Event | 329
ARECIBO | 2022-08-18 20:55 | 2022-08-18 21:18 | 1 | 0:23 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR REPARAR BAJANTE EN PT | A22081800169 | New_Event | Primary Wire Break | Include | Include | Equipment | 23 | 2022-08-18 | 23 | keep | 0 | Aug | 2022 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-18 21:00 | 2022-08-18 21:38 | 15 | 0:38 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22081800294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2022-08-18 | 570 | keep | 0 | Aug | 2022 | 0.00038822 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-08-18 21:05 | 2022-08-18 21:07 | 2216 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | B22081800719 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-18 | 4432 | keep | 0 | Aug | 2022 | 0.0030186 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
YAUCO | 2022-08-18 21:15 | 2022-08-18 21:44 | 2011 | 0:29 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE ALIMENTADOR PARA CERRAR PUENTE ABIERTO | P22081800316 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 29 | 2022-08-18 | 58319 | keep | 0 | Aug | 2022 | 0.039721 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-18 21:26 | 2022-08-19 07:44 | 80 | 10:18 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 80 EN C/L Y 1 X 40 EN C/L Y 1 X 25 EN XMR CRUCE LINEA PRIMARIA DEBIDO A POSTE PRIMARIO PARTIDO NO RELACIONADO | P22081800325 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 618 | 2022-08-18 | 49440 | keep | 0 | Aug | 2022 | 0.033673 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-18 21:26 | 2022-08-19 08:10 | 100 | 10:44 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN C/L CRUCE LINEA PRIMARIA DEBIDO A POSTE PRIMARIO PARTIDO RELACIONADO AL EVENTO P22081800308 | P22081900037 | New_Event | Primary Pole Failure | Include | Include | Equipment | 644 | 2022-08-18 | 64400 | keep | 0 | Aug | 2022 | 0.043863 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-18 21:27 | 2022-08-19 08:35 | 300 | 11:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | C22081800343 | New_Event | Primary Wire Break | Include | Include | Equipment | 668 | 2022-08-18 | 200400 | keep | 0 | Aug | 2022 | 0.13649 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-18 21:30 | 2022-08-18 22:20 | 723 | 0:50 | T | DESGANCHE | LLEVA LA CARGA DEL 1711-05 SE ABRIO EL AMARRE PARA REALIZAR DESGANCHE (A VARETA) DESDE EL PISO MEDIANTE G.O.I. BY-220818-05 FALTA POR ENTRAR EN SERVICIO LA CARGA DEL 1711-05 | B22081800724 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-08-18 | 36150 | keep | 0 | Aug | 2022 | 0.024622 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-18 21:30 | 2022-08-19 13:32 | 1976 | 16:02 | T | DESGANCHE | CARGA TRANSFERIDA AL 1711-02 SE ABRIO EL AMARRE Y SE REALIZO DESGANCHE (A VARETA) DESDE EL PISO Y SE VOLVIO A CERRAR AMARRE MEDIANTE G.O.I. BY-220818-05 | B22081800724 | New_Event | Vegetation Contact | Include | Include | Vegetation | 962 | 2022-08-18 | 1900912 | keep | 0 | Aug | 2022 | 1.2947 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
UTUADO | 2022-08-18 21:34 | 2022-08-19 16:10 | 18 | 18:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 37.5KVA | A22081800173 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1116 | 2022-08-18 | 20088 | keep | 0 | Aug | 2022 | 0.013682 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-08-18 21:59 | 2022-08-19 00:26 | 50 | 2:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M22081800214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-08-18 | 7350 | keep | 0 | Aug | 2022 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-18 22:23 | 2022-08-19 13:21 | 500 | 14:58 | P | NO SE REPORTO CAUSA | 2 X 100 EN CORTE DE LINEA NO CAUSA | S22081800350 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 898 | 2022-08-18 | 449000 | keep | 0 | Aug | 2022 | 0.30581 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-08-18 22:41 | 2022-08-19 13:41 | 20 | 15:00 | P | DESGANCHE | 1 X 100 EN C/L PARA DESGANCHE | B22081800797 | New_Event | Vegetation Contact | Include | Include | Vegetation | 900 | 2022-08-18 | 18000 | keep | 0 | Aug | 2022 | 0.01226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-18 22:42 | 2022-08-18 23:20 | 5 | 0:38 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081800175 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 38 | 2022-08-18 | 190 | keep | 0 | Aug | 2022 | 0.00012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-18 22:54 | 2022-08-19 14:29 | 7 | 15:35 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B22081800805 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 935 | 2022-08-18 | 6545 | keep | 0 | Aug | 2022 | 0.0044578 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-18 23:15 | 2022-08-19 04:04 | 120 | 4:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22081800220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-08-18 | 34680 | keep | 0 | Aug | 2022 | 0.02362 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
UTUADO | 2022-08-18 23:18 | 2022-08-19 13:38 | 15 | 14:20 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A22081800177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 860 | 2022-08-18 | 12900 | keep | 0 | Aug | 2022 | 0.0087861 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-08-18 23:37 | 2022-08-19 01:48 | 3000 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 VEGA BAJA @ MANATI | BB2208180000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-08-18 | 393000 | keep | 0 | Aug | 2022 | 0.26767 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2022-08-18 23:37 | 2022-08-19 01:48 | 908 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 VEGA BAJA @ MANATI | BB2208180000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-08-18 | 118948 | keep | 0 | Aug | 2022 | 0.081015 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2022-08-18 23:37 | 2022-08-19 01:48 | 3332 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 VEGA BAJA @ MANATI | BB2208180000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-08-18 | 436492 | keep | 0 | Aug | 2022 | 0.29729 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2022-08-18 23:37 | 2022-08-19 01:48 | 2610 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 VEGA BAJA @ MANATI | B22081800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-08-18 | 341910 | keep | 0 | Aug | 2022 | 0.23287 | 0.0017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2022-08-18 23:37 | 2022-08-19 01:48 | 3076 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 VEGA BAJA @ MANATI | B22081800000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-08-18 | 402956 | keep | 0 | Aug | 2022 | 0.27445 | 0.002095 | Sustained | FALSE | FALSE | Not_TMED_Event | 3076
CAGUAS | 2022-08-19 00:21 | 2022-08-19 00:22 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 3015-07 EN SERVICIO | C22081900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 2178 | keep | 0 | Aug | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2022-08-19 00:24 | 2022-08-19 13:37 | 50 | 13:13 | P | DESGANCHE | 1X50 EN C/L SE REFIRIO PARA DESGANCHE | B22081900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 793 | 2022-08-19 | 39650 | keep | 0 | Aug | 2022 | 0.027005 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-19 01:13 | 2022-08-19 10:29 | 70 | 9:16 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B22081900073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 556 | 2022-08-19 | 38920 | keep | 0 | Aug | 2022 | 0.026508 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-08-19 01:43 | 2022-08-19 13:39 | 50 | 11:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L, 2 X 30 EN OTRO C/L, 2 X 10 EN XMR Y SE REMPLAZO CAJA PRIMARIA | B22081900095 | New_Event | Cutout Failure | Include | Include | Equipment | 716 | 2022-08-19 | 35800 | keep | 0 | Aug | 2022 | 0.024383 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-19 02:10 | 2022-08-19 02:25 | 60 | 0:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | B22081900099 | New_Event | Primary Wire Break | Include | Include | Equipment | 15 | 2022-08-19 | 900 | keep | 0 | Aug | 2022 | 0.00061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-19 03:04 | 2022-08-19 10:30 | 15 | 7:26 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22081900005 | New_Event | Primary Wire Break | Include | Include | Equipment | 446 | 2022-08-19 | 6690 | keep | 0 | Aug | 2022 | 0.0045565 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-19 04:49 | 2022-08-19 04:50 | 723 | 0:01 | T | NO SE REPORTO CAUSA | SE VOLVIO A DISPARAR, LLEVA LA CARGA DEL 1711-05 PERO YA SE HABIA ABIERTO EL AMARRE PARA DESGANCHE MEDIANTE G.O.I. BY-220818-05 (1711-05 YA ESTABA FUERA) | B22081900120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 723 | keep | 0 | Aug | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
VEGA BAJA | 2022-08-19 04:53 | 2022-08-19 17:00 | 8 | 12:07 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22081900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 727 | 2022-08-19 | 5816 | keep | 0 | Aug | 2022 | 0.0039613 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-19 04:58 | 2022-08-19 14:37 | 1983 | 9:39 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CARGA TRANSFERIDA AL 1801-02 SE REALIZARON OPERACIONES DE CAMPO Y SE DEJO EN SERVICIO TOTAL G.O.I. BY-220819-01 | B22081900120 | New_Event | Cutout Failure | Include | Include | Equipment | 579 | 2022-08-19 | 1148157 | keep | 0 | Aug | 2022 | 0.782 | 0.0013506 | Sustained | FALSE | FALSE | Not_TMED_Event | 1983
BAYAMON | 2022-08-19 04:58 | 2022-08-19 14:37 | 186 | 9:39 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | LLEVA LA CARGA DEL 1711-04 SE REALIZARON OPERACIONES DE CAMPO Y SE DEJO EN SERVICIO TOTAL G.O.I. BY-220819-01 | B22081900120 | New_Event | Cutout Failure | Include | Include | Equipment | 579 | 2022-08-19 | 107694 | keep | 0 | Aug | 2022 | 0.07335 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
CAGUAS | 2022-08-19 05:03 | 2022-08-19 05:04 | 4390 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22081900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 4390 | keep | 0 | Aug | 2022 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
BARRANQUITAS | 2022-08-19 05:15 | 2022-08-19 05:16 | 2826 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22081900000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-19 | 2826 | keep | 0 | Aug | 2022 | 0.0019248 | 0.0019248 | Momentary | FALSE | FALSE | Not_TMED_Event | 2826
BARRANQUITAS | 2022-08-19 05:16 | 2022-08-19 09:15 | 1857 | 3:59 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA SECCIONALIZAR Y LEVANTAR ALAMBRE PRIMARIO | C22081900008 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 239 | 2022-08-19 | 443823 | keep | 0 | Aug | 2022 | 0.30229 | 0.0012648 | Sustained | FALSE | FALSE | Not_TMED_Event | 1857
VEGA BAJA | 2022-08-19 06:02 | 2022-08-19 10:09 | 30 | 4:07 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR RAYOS | A22081900005 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 247 | 2022-08-19 | 7410 | keep | 0 | Aug | 2022 | 0.0050469 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-19 06:16 | 2022-08-19 09:30 | 20 | 3:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22081900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-08-19 | 3880 | keep | 0 | Aug | 2022 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-19 06:39 | 2022-08-19 12:53 | 80 | 6:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA Y SE CERRO CORTE DE LINEA NO FUNDIO | S22081900020 | New_Event | Cutout Failure | Include | Include | Equipment | 374 | 2022-08-19 | 29920 | keep | 0 | Aug | 2022 | 0.020378 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-19 06:42 | 2022-08-19 06:43 | 2417 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22081900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 2417 | keep | 0 | Aug | 2022 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
BARRANQUITAS | 2022-08-19 06:46 | 2022-08-19 10:02 | 10 | 3:16 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO | C22081900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-08-19 | 1960 | keep | 0 | Aug | 2022 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-19 06:47 | 2022-08-19 10:24 | 10 | 3:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 30 EN C/L, 1 X 65 ENC/L Y REPARO BAJANTE SECUNDARIO | C22081900025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 217 | 2022-08-19 | 2170 | keep | 0 | Aug | 2022 | 0.001478 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-19 06:49 | 2022-08-19 06:51 | 3420 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 6840 | keep | 0 | Aug | 2022 | 0.0046587 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
CAGUAS | 2022-08-19 06:49 | 2022-08-19 09:56 | 65 | 3:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L SE REEMPLAZO TIGUERO | C22081900028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2022-08-19 | 12155 | keep | 0 | Aug | 2022 | 0.0082787 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-08-19 07:06 | 2022-08-19 08:30 | 7 | 1:24 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PARARRAYO | S22081900025 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 84 | 2022-08-19 | 588 | keep | 0 | Aug | 2022 | 0.00040048 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-08-19 07:06 | 2022-08-19 14:00 | 7 | 6:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 KVA | C22081900038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 414 | 2022-08-19 | 2898 | keep | 0 | Aug | 2022 | 0.0019738 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-08-19 07:14 | 2022-08-19 10:12 | 80 | 2:58 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C22081900040 | New_Event | Animals | Include | Include | Wildlife | 178 | 2022-08-19 | 14240 | keep | 0 | Aug | 2022 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-19 07:18 | 2022-08-19 10:02 | 60 | 2:44 | P | NO SE REPORTO CAUSA | 1X65 EN RISER, 1X50 EN OTRO RISER | B22081900178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2022-08-19 | 9840 | keep | 0 | Aug | 2022 | 0.006702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-19 07:20 | 2022-08-19 14:45 | 10 | 7:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA AVERIADO | C22081900043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 445 | 2022-08-19 | 4450 | keep | 0 | Aug | 2022 | 0.0030309 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-19 07:22 | 2022-08-19 10:15 | 80 | 2:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081900013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-08-19 | 13840 | keep | 0 | Aug | 2022 | 0.0094264 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-19 07:25 | 2022-08-19 07:27 | 104 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 75% DE SU CARGA POR 1014-16 | S22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 208 | keep | 0 | Aug | 2022 | 0.00014167 | 7.0834e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 104
AGUADILLA | 2022-08-19 07:25 | 2022-08-19 12:30 | 10 | 5:05 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M22081900014 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 305 | 2022-08-19 | 3050 | keep | 0 | Aug | 2022 | 0.0020773 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-08-19 07:42 | 2022-08-19 07:43 | 1571 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22081900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 1571 | keep | 0 | Aug | 2022 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
BARRANQUITAS | 2022-08-19 08:00 | 2022-08-19 13:37 | 1 | 5:37 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA X 50KVA | C22081900056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 337 | 2022-08-19 | 337 | keep | 0 | Aug | 2022 | 0.00022953 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-19 08:05 | 2022-08-19 08:07 | 1746 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22081900218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 3492 | keep | 0 | Aug | 2022 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
FAJARDO | 2022-08-19 08:05 | 2022-08-19 10:06 | 516 | 2:01 | P | ANIMAL | 2 X 80 Y 1 X 100 EN C/L AVE CRUZO LINEAS | R22081900012 | New_Event | Animals | Include | Include | Wildlife | 121 | 2022-08-19 | 62436 | keep | 0 | Aug | 2022 | 0.042525 | 0.00035145 | Sustained | FALSE | FALSE | Not_TMED_Event | 516
PONCE | 2022-08-19 08:12 | 2022-08-19 09:35 | 50 | 1:23 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22081900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-08-19 | 4150 | keep | 0 | Aug | 2022 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-19 08:17 | 2022-08-19 10:51 | 12 | 2:34 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B22081900229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-08-19 | 1848 | keep | 0 | Aug | 2022 | 0.0012587 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-08-19 08:18 | 2022-08-19 13:04 | 5 | 4:46 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR , 1X 15 EN XMR Y 1 X 30 EN C/L MAL TIEMPO RAYOS | C22081900061 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 286 | 2022-08-19 | 1430 | keep | 0 | Aug | 2022 | 0.00097397 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-19 08:30 | 2022-08-19 08:32 | 823 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 95% POR 1119-04 | S22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 1646 | keep | 0 | Aug | 2022 | 0.0011211 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
SAN JUAN | 2022-08-19 08:30 | 2022-08-19 08:32 | 800 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR PARTE POR 1119-04 | S22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 1600 | keep | 0 | Aug | 2022 | 0.0010898 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
SAN JUAN | 2022-08-19 08:30 | 2022-08-19 08:32 | 2720 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA PARTA DEL 1119-02 Y 95% DEL 1115-05 | S22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 5440 | keep | 0 | Aug | 2022 | 0.0037052 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2022-08-19 08:30 | 2022-08-19 16:05 | 151 | 7:35 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETE PARA LEVANTAR LINEA | S22081800167 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 455 | 2022-08-19 | 68705 | keep | 0 | Aug | 2022 | 0.046795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-19 08:32 | 2022-08-19 14:43 | 7 | 6:11 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PARARRAYO | S22081900025 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 371 | 2022-08-19 | 2597 | keep | 0 | Aug | 2022 | 0.0017688 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-19 08:44 | 2022-08-19 21:21 | 50 | 12:37 | P | DESGANCHE | 2X80 EN C/L DESGANCHE COLINDANCIA CON CAGUAS | C22081900068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 757 | 2022-08-19 | 37850 | keep | 0 | Aug | 2022 | 0.025779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-19 08:45 | 2022-08-20 06:10 | 30 | 21:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22082000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1285 | 2022-08-19 | 38550 | keep | 0 | Aug | 2022 | 0.026256 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-19 08:45 | 2022-08-20 09:10 | 20 | 24:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO A TRANSFORMADOR | M22081900273 | New_Event | Primary Wire Break | Include | Include | Equipment | 1465 | 2022-08-19 | 29300 | keep | 0 | Aug | 2022 | 0.019956 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-19 08:47 | 2022-08-19 12:59 | 51 | 4:12 | P | NO SE REPORTO CAUSA | 2X40 EN C/L | B22081900250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2022-08-19 | 12852 | keep | 0 | Aug | 2022 | 0.0087534 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
YAUCO | 2022-08-19 08:49 | 2022-08-19 13:20 | 2 | 4:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22081900056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-08-19 | 542 | keep | 0 | Aug | 2022 | 0.00036915 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-19 09:00 | 2022-08-19 09:40 | 18 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR VIVO Y NEUTRAL | S22081900052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2022-08-19 | 720 | keep | 0 | Aug | 2022 | 0.00049039 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-08-19 09:04 | 2022-08-19 11:26 | 100 | 2:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22081900016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-08-19 | 14200 | keep | 0 | Aug | 2022 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-19 09:05 | 2022-08-19 13:45 | 5 | 4:40 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081900018 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 280 | 2022-08-19 | 1400 | keep | 0 | Aug | 2022 | 0.00095353 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-08-19 09:11 | 2022-08-19 09:48 | 2 | 0:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO SE ENCONTRO CAUSA | P22081900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-08-19 | 74 | keep | 0 | Aug | 2022 | 5.0401e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-08-19 09:14 | 2022-08-19 11:57 | 1 | 2:43 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR LLUVIAS | A22081900019 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 163 | 2022-08-19 | 163 | keep | 0 | Aug | 2022 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-19 09:15 | 2022-08-19 16:47 | 200 | 7:32 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA SECCIONALIZAR Y LEVANTAR ALAMBRE PRIMARIO | C22081900008 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 452 | 2022-08-19 | 90400 | keep | 0 | Aug | 2022 | 0.061571 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-19 09:17 | 2022-08-19 13:50 | 8 | 4:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BAJANTE SECUNDARIO | C22081900080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 273 | 2022-08-19 | 2184 | keep | 0 | Aug | 2022 | 0.0014875 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-08-19 09:27 | 2022-08-19 10:37 | 21 | 1:10 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22081900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-08-19 | 1470 | keep | 0 | Aug | 2022 | 0.0010012 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
ARECIBO | 2022-08-19 09:27 | 2022-08-19 22:25 | 15 | 12:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 50KVA POR UNO DE 50KVA | A22081900020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 778 | 2022-08-19 | 11670 | keep | 0 | Aug | 2022 | 0.0079484 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-19 09:54 | 2022-08-19 13:07 | 1 | 3:13 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22081900023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2022-08-19 | 193 | keep | 0 | Aug | 2022 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-19 09:57 | 2022-08-19 15:10 | 12 | 5:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | A22081900023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 313 | 2022-08-19 | 3756 | keep | 0 | Aug | 2022 | 0.0025582 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-08-19 10:16 | 2022-08-19 14:04 | 3 | 3:48 | P | MAL TIEMPO/RAYOS | 1 X 20 EN XMR DESCARGAS ELECTRICAS | P22081900070 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 228 | 2022-08-19 | 684 | keep | 0 | Aug | 2022 | 0.00046587 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-19 10:24 | 2022-08-19 11:25 | 25 | 1:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22081900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-08-19 | 1525 | keep | 0 | Aug | 2022 | 0.0010387 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-08-19 10:27 | 2022-08-19 12:17 | 15 | 1:50 | P | ANIMAL | 1 X 10 EN XMR AVE | C22081900104 | New_Event | Animals | Include | Include | Wildlife | 110 | 2022-08-19 | 1650 | keep | 0 | Aug | 2022 | 0.0011238 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-08-19 10:27 | 2022-08-19 15:34 | 5 | 5:07 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P22081900071 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 307 | 2022-08-19 | 1535 | keep | 0 | Aug | 2022 | 0.0010455 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-08-19 10:36 | 2022-08-19 13:22 | 7 | 2:46 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO PUENTE PRIMARIO DE CAJA A XMR | C22081900106 | New_Event | Primary Wire Break | Include | Include | Equipment | 166 | 2022-08-19 | 1162 | keep | 0 | Aug | 2022 | 0.00079143 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-19 10:40 | 2022-08-19 10:41 | 61 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECERRO 45% POR 1342-04 | S22081900000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-19 | 61 | keep | 0 | Aug | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2022-08-19 10:40 | 2022-08-19 10:41 | 154 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECERRO 25% POR 1342-04 | S22081900000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-19 | 154 | keep | 0 | Aug | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-08-19 10:40 | 2022-08-19 10:41 | 390 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO LLEVA 45% DEL 1201-1 Y LLEVA 25% DEL 1203-03 | S22081900000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-19 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-08-19 10:41 | 2022-08-19 12:16 | 61 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO ALAMBRE EN EL PISO SE REALIZO MANIOBRAS PARA SECCIONALIZAR Y DEVOLVER NORMALIZAR CARGA | S22081900083 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 95 | 2022-08-19 | 5795 | keep | 0 | Aug | 2022 | 0.0039469 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2022-08-19 10:53 | 2022-08-19 15:25 | 1 | 4:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REMPLAZO PORTAFUSIBLE | S22081900082 | New_Event | Cutout Failure | Include | Include | Equipment | 272 | 2022-08-19 | 272 | keep | 0 | Aug | 2022 | 0.00018526 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-19 11:01 | 2022-08-19 12:02 | 20 | 1:01 | P | ANIMAL | 1 X 25 C/L Y 1 X 20 EN XMR CRUCE DE FASE POR AVE | P22081900075 | New_Event | Animals | Include | Include | Wildlife | 61 | 2022-08-19 | 1220 | keep | 0 | Aug | 2022 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-19 11:08 | 2022-08-19 14:38 | 216 | 3:30 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22081900089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-08-19 | 45360 | keep | 0 | Aug | 2022 | 0.030894 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2022-08-19 11:11 | 2022-08-19 16:42 | 40 | 5:31 | P | NO SE REPORTO CAUSA | 1X100 EN RISER | B22081900343 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 331 | 2022-08-19 | 13240 | keep | 0 | Aug | 2022 | 0.0090177 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-19 11:15 | 2022-08-19 18:00 | 15 | 6:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA | C22081900108 | New_Event | Service Transformer Failure | Include | Include | Equipment | 405 | 2022-08-19 | 6075 | keep | 0 | Aug | 2022 | 0.0041377 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-19 11:25 | 2022-08-19 13:16 | 200 | 1:51 | P | CAUSAS EXTERNAS | 2 X 65 EN C/L SE ENDEREZO POSTE VIRADO POR IMPACTO DE CAMION EXTERNO | C22081900115 | New_Event | Damage From Public | Include | Include | Public | 111 | 2022-08-19 | 22200 | keep | 0 | Aug | 2022 | 0.01512 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-19 11:27 | 2022-08-19 14:15 | 100 | 2:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22081900029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 168 | 2022-08-19 | 16800 | keep | 0 | Aug | 2022 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-19 11:28 | 2022-08-19 11:29 | 464 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22081900081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-19 | 464 | keep | 0 | Aug | 2022 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
UTUADO | 2022-08-19 11:28 | 2022-08-19 18:45 | 10 | 7:17 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CONVERTIDOR DESCARGAS ELECTRICAS | A22081900030 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 437 | 2022-08-19 | 4370 | keep | 0 | Aug | 2022 | 0.0029764 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-08-19 11:29 | 2022-08-19 13:25 | 20 | 1:56 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22081900077 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-08-19 | 2320 | keep | 0 | Aug | 2022 | 0.0015801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-19 11:30 | 2022-08-19 14:26 | 11 | 2:56 | P | ANIMAL | SE ABRIO XMR PARA RETIRAR PANAL DE ABEJAS EN PEDESTAL | R22081900039 | New_Event | Animals | Include | Include | Wildlife | 176 | 2022-08-19 | 1936 | keep | 0 | Aug | 2022 | 0.0013186 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-08-19 11:43 | 2022-08-19 17:36 | 110 | 5:53 | P | DESGANCHE | SE REPUSO 1X 65 EN CORTE DE LINEA DESGANCHE | S22081900102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2022-08-19 | 38830 | keep | 0 | Aug | 2022 | 0.026447 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BAYAMON | 2022-08-19 11:44 | 2022-08-19 12:17 | 10 | 0:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22081900357 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2022-08-19 | 330 | keep | 0 | Aug | 2022 | 0.00022476 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-19 11:46 | 2022-08-19 17:38 | 103 | 5:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIA | C22081900122 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 352 | 2022-08-19 | 36256 | keep | 0 | Aug | 2022 | 0.024694 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
CAGUAS | 2022-08-19 11:50 | 2022-08-19 17:45 | 63 | 5:55 | P | DESGANCHE | 2 X 65 EN C/L SE DESGANCHO | C22081900125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2022-08-19 | 22365 | keep | 0 | Aug | 2022 | 0.015233 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2022-08-19 11:54 | 2022-08-19 18:08 | 300 | 6:14 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 1 X 65 Y 2 X 40 EN DISTINTOS CORTES DE LINEA SE REMPLAZO PORTAFUSIBLES EN CORTE DE LINEA Y SE CERRO PUENTE PRIMARIO ABIERTO | A22081900032 | New_Event | Primary Wire Break | Include | Include | Equipment | 374 | 2022-08-19 | 112200 | keep | 0 | Aug | 2022 | 0.076419 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-19 11:56 | 2022-08-19 16:03 | 108 | 4:07 | P | DESGANCHE | 1X50 EN C/L | B22081900367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-08-19 | 26676 | keep | 0 | Aug | 2022 | 0.018169 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-08-19 12:00 | 2022-08-20 12:01 | 30 | 24:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR RAMA DE BAMBU SOBRE LINEA | M22081900288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1441 | 2022-08-19 | 43230 | keep | 0 | Aug | 2022 | 0.029444 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-19 12:07 | 2022-08-19 12:41 | 2052 | 0:34 | P | PROBLEMA DEL CLIENTE | DISPARO INTERRUPTOR AL REPONER EN RISER A CLIENTE PROBLEMA INTERNO Y ORIENTO Y SE CERRO POR CONTROL LLEVA 5% DEL 1115-05 Y 20% POR 1118-10 | S22081900000 | New_Event | Customer-Related Interruption | Include | Include | Public | 34 | 2022-08-19 | 69768 | keep | 0 | Aug | 2022 | 0.047519 | 0.0013976 | Sustained | FALSE | FALSE | Not_TMED_Event | 2052
SAN JUAN | 2022-08-19 12:07 | 2022-08-19 12:41 | 43 | 0:34 | P | PROBLEMA DEL CLIENTE | DISPARO INTERRUPTOR AL REPONER EN RISER A CLIENTE PROBLEMA INTERNO Y ORIENTO Y SE CERRO POR CONTROL 5% POR 1111-01 NO SALIO EVENTO | S22081900000 | New_Event | Customer-Related Interruption | Include | Include | Public | 34 | 2022-08-19 | 1462 | keep | 0 | Aug | 2022 | 0.00099576 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-08-19 12:11 | 2022-08-19 12:13 | 225 | 0:02 | T | DESGANCHE | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA POR 1303-05 | S22081900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-19 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-19 12:11 | 2022-08-19 12:13 | 870 | 0:02 | T | DESGANCHE | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1303-04 | S22081900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-19 | 1740 | keep | 0 | Aug | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2022-08-19 12:13 | 2022-08-19 18:38 | 60 | 6:25 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22081900166 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 385 | 2022-08-19 | 23100 | keep | 0 | Aug | 2022 | 0.015733 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-19 12:15 | 2022-08-19 12:17 | 590 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22081900114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 1180 | keep | 0 | Aug | 2022 | 0.00080369 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
BAYAMON | 2022-08-19 12:18 | 2022-08-19 12:19 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 50% DE SU CARGA TRANSFERIDA AL 1909-07 | S22081900116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 766 | keep | 0 | Aug | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-08-19 12:18 | 2022-08-19 12:19 | 1139 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 50% DEL 1709-03 | S22081900116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 1139 | keep | 0 | Aug | 2022 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
CANOVANAS | 2022-08-19 12:20 | 2022-08-19 12:44 | 1 | 0:24 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22081900043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2022-08-19 | 24 | keep | 0 | Aug | 2022 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-19 12:22 | 2022-08-19 12:34 | 2842 | 0:12 | T | DESGANCHE | DISPARO DE BKR SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL | C22081900140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 12 | 2022-08-19 | 34104 | keep | 0 | Aug | 2022 | 0.023228 | 0.0019357 | Sustained | FALSE | FALSE | Not_TMED_Event | 2842
BAYAMON | 2022-08-19 12:31 | 2022-08-19 16:03 | 130 | 3:32 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22081900384 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2022-08-19 | 27560 | keep | 0 | Aug | 2022 | 0.018771 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2022-08-19 12:32 | 2022-08-19 12:33 | 2005 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1619-03 LLEVANDO 1619-02 | R22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 2005 | keep | 0 | Aug | 2022 | 0.0013656 | 0.0013656 | Momentary | FALSE | FALSE | Not_TMED_Event | 2005
CANOVANAS | 2022-08-19 12:32 | 2022-08-19 12:33 | 5062 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1619-03 LLEVANDO 1619-02 | R22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 5062 | keep | 0 | Aug | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
BAYAMON | 2022-08-19 12:32 | 2022-08-19 15:06 | 130 | 2:34 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B22081900386 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-08-19 | 20020 | keep | 0 | Aug | 2022 | 0.013636 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2022-08-19 12:39 | 2022-08-19 14:40 | 2842 | 2:01 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL | C22081900150 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-08-19 | 343882 | keep | 0 | Aug | 2022 | 0.23422 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-19 12:39 | 2022-08-19 16:45 | 213 | 4:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA | P22081900083 | New_Event | Cutout Failure | Include | Include | Equipment | 246 | 2022-08-19 | 52398 | keep | 0 | Aug | 2022 | 0.035688 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
BAYAMON | 2022-08-19 12:41 | 2022-08-19 17:17 | 45 | 4:36 | P | CAUSAS EXTERNAS | 1X50 EN C/L, 1X40 EN OTRO C/L SE RETIRO TOLDO (CORTINA) PLASTICA DE LA LINEA | B22081900391 | New_Event | Damage From Public | Include | Include | Public | 276 | 2022-08-19 | 12420 | keep | 0 | Aug | 2022 | 0.0084592 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-08-19 12:46 | 2022-08-19 14:00 | 6 | 1:14 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA CONECTAR TOMA DE CLIENTE | C22081900151 | New_Event | Customer-Related Interruption | Include | Include | Public | 74 | 2022-08-19 | 444 | keep | 0 | Aug | 2022 | 0.00030241 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-19 12:46 | 2022-08-19 15:41 | 990 | 2:55 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEAS PRIMARIAS ROTAS SE CERRO INTERRUPTOR | M22081900035 | New_Event | Primary Wire Break | Include | Include | Equipment | 175 | 2022-08-19 | 173250 | keep | 0 | Aug | 2022 | 0.118 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
CANOVANAS | 2022-08-19 12:49 | 2022-08-19 12:51 | 1474 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22081900046 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-08-19 | 2948 | keep | 0 | Aug | 2022 | 0.0020079 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
MAYAGÃœEZ | 2022-08-19 12:50 | 2022-08-19 12:51 | 108 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1500 | M22081900036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 108 | keep | 0 | Aug | 2022 | 7.3558e-05 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
CANOVANAS | 2022-08-19 12:51 | 2022-08-19 14:31 | 10 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA EN XMR | R22081900047 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 100 | 2022-08-19 | 1000 | keep | 0 | Aug | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-08-19 12:53 | 2022-08-19 13:56 | 2 | 1:03 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE Y SE REPARO BAJANTE PRIMARIO LINEA A CAJA EN C/L | R22081900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-08-19 | 126 | keep | 0 | Aug | 2022 | 8.5818e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-08-19 12:57 | 2022-08-19 20:05 | 300 | 7:08 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO PORTE Y SE LEVANTO LINEA PRIMARIA | C22081900154 | New_Event | Primary Pole Failure | Include | Include | Equipment | 428 | 2022-08-19 | 128400 | keep | 0 | Aug | 2022 | 0.087453 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-19 13:00 | 2022-08-19 15:20 | 15 | 2:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE LEVANTO SECUNDARIO | S22081900096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 140 | 2022-08-19 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-19 13:05 | 2022-08-19 16:43 | 30 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C22081900157 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2022-08-19 | 6540 | keep | 0 | Aug | 2022 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 574 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 60844 | keep | 0 | Aug | 2022 | 0.041441 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 2493 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 264258 | keep | 0 | Aug | 2022 | 0.17998 | 0.001698 | Sustained | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 1415 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 149990 | keep | 0 | Aug | 2022 | 0.10216 | 0.00096375 | Sustained | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 1428 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 151368 | keep | 0 | Aug | 2022 | 0.1031 | 0.0009726 | Sustained | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 1036 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 109816 | keep | 0 | Aug | 2022 | 0.074795 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 382 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 40492 | keep | 0 | Aug | 2022 | 0.027579 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 39 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900042 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 4134 | keep | 0 | Aug | 2022 | 0.0028156 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2022-08-19 13:13 | 2022-08-19 14:59 | 2366 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 250796 | keep | 0 | Aug | 2022 | 0.17082 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2022-08-19 13:13 | 2022-08-19 14:59 | 1337 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 141722 | keep | 0 | Aug | 2022 | 0.096526 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-19 13:13 | 2022-08-19 14:59 | 709 | 1:46 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 | M22081900043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 106 | 2022-08-19 | 75154 | keep | 0 | Aug | 2022 | 0.051187 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
MAYAGÃœEZ | 2022-08-19 13:27 | 2022-08-19 15:41 | 100 | 2:14 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22081900053 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 134 | 2022-08-19 | 13400 | keep | 0 | Aug | 2022 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-19 13:29 | 2022-08-19 13:31 | 590 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | S22081900139 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 1180 | keep | 0 | Aug | 2022 | 0.00080369 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
CANOVANAS | 2022-08-19 13:33 | 2022-08-19 13:34 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22081900049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 2039 | keep | 0 | Aug | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
VEGA BAJA | 2022-08-19 13:33 | 2022-08-19 19:13 | 30 | 5:40 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22081900046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2022-08-19 | 10200 | keep | 0 | Aug | 2022 | 0.0069472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-08-19 13:34 | 2022-08-19 17:33 | 27 | 3:59 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO | P22081900092 | New_Event | Primary Wire Break | Include | Include | Equipment | 239 | 2022-08-19 | 6453 | keep | 0 | Aug | 2022 | 0.0043951 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
FAJARDO | 2022-08-19 13:36 | 2022-08-19 19:04 | 1 | 5:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KVA EN BANCO DE XMR | R22081900050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 328 | 2022-08-19 | 328 | keep | 0 | Aug | 2022 | 0.0002234 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-08-19 13:36 | 2022-08-19 14:18 | 65 | 0:42 | P | DESGANCHE | 1 X 80 EN C/L SE RETIRO ENREDADERA | R22081900048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2022-08-19 | 2730 | keep | 0 | Aug | 2022 | 0.0018594 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2022-08-19 13:40 | 2022-08-19 14:45 | 6 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22081900025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-08-19 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-08-19 13:41 | 2022-08-19 15:38 | 35 | 1:57 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22081900049 | New_Event | Primary Wire Break | Include | Include | Equipment | 117 | 2022-08-19 | 4095 | keep | 0 | Aug | 2022 | 0.0027891 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2022-08-19 13:41 | 2022-08-19 14:15 | 1 | 0:34 | P | MAL TIEMPO/RAYOS | 1 X 15 EN MONTURA DE XMR RAYOS | C22081900171 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 34 | 2022-08-19 | 34 | keep | 0 | Aug | 2022 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-19 13:46 | 2022-08-19 15:10 | 15 | 1:24 | P | CONDUCTOR ROTO O ABIERTO | REPARANDO PUENTE PRIMARIO ABIERTO | P22081900095 | New_Event | Primary Wire Break | Include | Include | Equipment | 84 | 2022-08-19 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-19 13:54 | 2022-08-19 15:03 | 20 | 1:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE VIENTO | A22081900053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 69 | 2022-08-19 | 1380 | keep | 0 | Aug | 2022 | 0.00093991 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-19 14:00 | 2022-08-19 16:51 | 1 | 2:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 25KVA | C22081900212 | New_Event | Service Transformer Failure | Include | Include | Equipment | 171 | 2022-08-19 | 171 | keep | 0 | Aug | 2022 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-19 14:01 | 2022-08-19 16:27 | 1 | 2:26 | P | DESGANCHE | 3 X 50 EN C/L SE DESGANCHO | C22081900177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2022-08-19 | 146 | keep | 0 | Aug | 2022 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-19 14:03 | 2022-08-19 19:03 | 5 | 5:00 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN XMR POR DESGANCHE SECUNDARIO | B22081900426 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 300 | 2022-08-19 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-08-19 14:07 | 2022-08-19 19:00 | 15 | 4:53 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA | C22081900185 | New_Event | Service Transformer Failure | Include | Include | Equipment | 293 | 2022-08-19 | 4395 | keep | 0 | Aug | 2022 | 0.0029934 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-19 14:10 | 2022-08-19 18:17 | 11 | 4:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA @ 4 KV POR UNO DE LA MISMA CAPACIDAD | M22081900168 | New_Event | Service Transformer Failure | Include | Include | Equipment | 247 | 2022-08-19 | 2717 | keep | 0 | Aug | 2022 | 0.0018505 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-08-19 14:10 | 2022-08-19 14:11 | 4664 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22081900089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 4664 | keep | 0 | Aug | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
BAYAMON | 2022-08-19 14:12 | 2022-08-19 18:31 | 25 | 4:19 | P | DESGANCHE | 1X30 EN C/L | B22081900429 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-08-19 | 6475 | keep | 0 | Aug | 2022 | 0.0044101 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-19 14:14 | 2022-08-19 15:34 | 281 | 1:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22081900098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-08-19 | 22480 | keep | 0 | Aug | 2022 | 0.015311 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-08-19 14:14 | 2022-08-19 15:34 | 1252 | 1:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22081900098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-08-19 | 100160 | keep | 0 | Aug | 2022 | 0.068219 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2022-08-19 14:14 | 2022-08-19 15:34 | 595 | 1:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22081900096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-08-19 | 47600 | keep | 0 | Aug | 2022 | 0.03242 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2022-08-19 14:14 | 2022-08-19 15:34 | 51 | 1:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22081900096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-08-19 | 4080 | keep | 0 | Aug | 2022 | 0.0027789 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-19 14:14 | 2022-08-19 15:34 | 721 | 1:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22081900096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 80 | 2022-08-19 | 57680 | keep | 0 | Aug | 2022 | 0.039286 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
BAYAMON | 2022-08-19 14:15 | 2022-08-19 16:37 | 80 | 2:22 | P | NO SE REPORTO CAUSA | 1X50 DE SU-13A @ RISER | B22081900431 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2022-08-19 | 11360 | keep | 0 | Aug | 2022 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-08-19 14:17 | 2022-08-19 16:04 | 1382 | 1:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22081900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 107 | 2022-08-19 | 147874 | keep | 0 | Aug | 2022 | 0.10072 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-19 14:17 | 2022-08-19 16:04 | 654 | 1:47 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 | A22081900061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 107 | 2022-08-19 | 69978 | keep | 0 | Aug | 2022 | 0.047662 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
PONCE | 2022-08-19 14:20 | 2022-08-19 16:44 | 38 | 2:24 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA SE RETIRO TENSOR | P22081900100 | New_Event | Damage From Public | Include | Include | Public | 144 | 2022-08-19 | 5472 | keep | 0 | Aug | 2022 | 0.003727 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2022-08-19 14:23 | 2022-08-19 18:36 | 100 | 4:13 | P | DESGANCHE | 1X40 EN C/L | B22081900436 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2022-08-19 | 25300 | keep | 0 | Aug | 2022 | 0.017232 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-19 14:28 | 2022-08-19 16:12 | 3147 | 1:44 | T | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO MACHETES PARA SECCIONALIZAR EL ALIMENTADOR SE CERRO INTERRUPTOR | M22081900119 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 104 | 2022-08-19 | 327288 | keep | 0 | Aug | 2022 | 0.22291 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
BAYAMON | 2022-08-19 14:32 | 2022-08-20 12:44 | 3 | 22:12 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B22081900438 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1332 | 2022-08-19 | 3996 | keep | 0 | Aug | 2022 | 0.0027217 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-19 14:37 | 2022-08-19 20:49 | 1 | 6:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L SE REMPLAZO PORTAFUSIBLE | B22081900474 | New_Event | Cutout Failure | Include | Include | Equipment | 372 | 2022-08-19 | 372 | keep | 0 | Aug | 2022 | 0.00025337 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-19 14:40 | 2022-08-19 16:30 | 710 | 1:50 | P | DESGANCHE | SE RETIRO ARBOL A VARETA Y SE CERRO MACHETE | C22081900150 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-08-19 | 78100 | keep | 0 | Aug | 2022 | 0.053194 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-19 14:40 | 2022-08-19 15:00 | 2 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CONECTORES AVERIADOS EN LINEA SECUNDARIA | A22081900063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-08-19 | 40 | keep | 0 | Aug | 2022 | 2.7244e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-19 14:53 | 2022-08-19 16:10 | 80 | 1:17 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | S22081900083 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2022-08-19 | 6160 | keep | 0 | Aug | 2022 | 0.0041955 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-19 15:00 | 2022-08-19 17:25 | 200 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22081900082 | New_Event | Primary Wire Break | Include | Include | Equipment | 145 | 2022-08-19 | 29000 | keep | 0 | Aug | 2022 | 0.019752 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-19 15:09 | 2022-08-19 19:28 | 30 | 4:19 | P | ANIMAL | 1X30 EN C/L POR AVE EN LA LINEA | B22081900446 | New_Event | Animals | Include | Include | Wildlife | 259 | 2022-08-19 | 7770 | keep | 0 | Aug | 2022 | 0.0052921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-19 15:16 | 2022-08-20 11:25 | 1 | 20:09 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR PARARRAYO | A22081900079 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1209 | 2022-08-19 | 1209 | keep | 0 | Aug | 2022 | 0.00082344 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-19 15:20 | 2022-08-19 18:20 | 50 | 3:00 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22081900081 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 180 | 2022-08-19 | 9000 | keep | 0 | Aug | 2022 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-19 15:22 | 2022-08-19 17:17 | 91 | 1:55 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P22081900113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-08-19 | 10465 | keep | 0 | Aug | 2022 | 0.0071277 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
SAN JUAN | 2022-08-19 15:23 | 2022-08-19 15:47 | 1 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO | S22081900163 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 24 | 2022-08-19 | 24 | keep | 0 | Aug | 2022 | 1.6346e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-19 15:24 | 2022-08-19 18:00 | 10 | 2:36 | P | DESGANCHE | 1X30 EN CORTE DE LINEA DESGANCHE | S22081900168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-08-19 | 1560 | keep | 0 | Aug | 2022 | 0.0010625 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-19 15:36 | 2022-08-19 19:47 | 10 | 4:11 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE HIZO DESGANCHE SECUNDARIO | S22081900169 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 251 | 2022-08-19 | 2510 | keep | 0 | Aug | 2022 | 0.0017095 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-19 15:41 | 2022-08-19 21:15 | 100 | 5:34 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTES Y SE SECCIONALIZO LINEA PRIMARIA PARTIDA | M22081900181 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 334 | 2022-08-19 | 33400 | keep | 0 | Aug | 2022 | 0.022749 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-19 15:44 | 2022-08-19 21:21 | 40 | 5:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22081900174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2022-08-19 | 13480 | keep | 0 | Aug | 2022 | 0.0091812 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-19 15:54 | 2022-08-19 21:20 | 75 | 5:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22081900221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 326 | 2022-08-19 | 24450 | keep | 0 | Aug | 2022 | 0.016653 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-08-19 16:00 | 2022-08-19 17:08 | 6 | 1:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO CAJA PRIMARIA EN XMR | B22081900466 | New_Event | Cutout Failure | Include | Include | Equipment | 68 | 2022-08-19 | 408 | keep | 0 | Aug | 2022 | 0.00027789 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-19 16:07 | 2022-08-19 17:11 | 50 | 1:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN C/L | R22081900064 | New_Event | Cutout Failure | Include | Include | Equipment | 64 | 2022-08-19 | 3200 | keep | 0 | Aug | 2022 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-19 16:12 | 2022-08-19 19:25 | 2747 | 3:13 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETAS PARTIDAS SE CERRO MACHETES | M22081900203 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 193 | 2022-08-19 | 530171 | keep | 0 | Aug | 2022 | 0.3611 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-19 16:18 | 2022-08-19 19:40 | 40 | 3:22 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYOS | C22081900234 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 202 | 2022-08-19 | 8080 | keep | 0 | Aug | 2022 | 0.0055033 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-19 16:19 | 2022-08-19 19:39 | 40 | 3:20 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22081900236 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2022-08-19 | 8000 | keep | 0 | Aug | 2022 | 0.0054488 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-19 16:29 | 2022-08-19 16:42 | 50 | 0:13 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S22081900176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2022-08-19 | 650 | keep | 0 | Aug | 2022 | 0.00044271 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-19 16:30 | 2022-08-19 19:00 | 300 | 2:30 | P | TERMINACION SOTERRADA AVERIADA | 2 X 150 EN SU-10 SE REMPLAZO 2 TERMINACIONES EN SU-3 Y SU-6 | S22081900041 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 150 | 2022-08-19 | 45000 | keep | 0 | Aug | 2022 | 0.030649 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2022-08-19 16:32 | 2022-08-19 18:14 | 1 | 1:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE TRONCAL A RAMAL | R22081900067 | New_Event | Primary Wire Break | Include | Include | Equipment | 102 | 2022-08-19 | 102 | keep | 0 | Aug | 2022 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-19 16:42 | 2022-08-20 05:40 | 12 | 12:58 | P | NO SE REPORTO CAUSA | 1 X 15 XMR | B22081900476 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 778 | 2022-08-19 | 9336 | keep | 0 | Aug | 2022 | 0.0063587 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-19 16:52 | 2022-08-19 16:54 | 513 | 0:02 | P | NO SE REPORTO CAUSA | SE PROBO QUEDO EN SERVICIO 20% 1118-10 | S22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 1026 | keep | 0 | Aug | 2022 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-08-19 16:52 | 2022-08-19 16:54 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | SE PROBO QUEDO EN SERVICIO LLEVA EL 20% DEL 1111-01 | S22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-19 | 5564 | keep | 0 | Aug | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BARRANQUITAS | 2022-08-19 16:53 | 2022-08-19 18:10 | 12 | 1:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22081900245 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2022-08-19 | 924 | keep | 0 | Aug | 2022 | 0.00062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-19 16:54 | 2022-08-19 18:27 | 3 | 1:33 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22081900211 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2022-08-19 | 279 | keep | 0 | Aug | 2022 | 0.00019003 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-19 16:56 | 2022-08-20 08:34 | 6 | 15:38 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | S22081900188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 938 | 2022-08-19 | 5628 | keep | 0 | Aug | 2022 | 0.0038332 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-19 17:01 | 2022-08-19 18:50 | 80 | 1:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | M22081900215 | New_Event | Primary Wire Break | Include | Include | Equipment | 109 | 2022-08-19 | 8720 | keep | 0 | Aug | 2022 | 0.0059392 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-19 17:04 | 2022-08-19 19:00 | 40 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22081900252 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-08-19 | 4640 | keep | 0 | Aug | 2022 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-19 17:05 | 2022-08-19 20:00 | 60 | 2:55 | P | ARBOL SOBRE LINEA | 1 X 100 Y 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22081900216 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 175 | 2022-08-19 | 10500 | keep | 0 | Aug | 2022 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-19 17:18 | 2022-08-20 15:00 | 50 | 21:42 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L | B22081900483 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1302 | 2022-08-19 | 65100 | keep | 0 | Aug | 2022 | 0.044339 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-19 17:20 | 2022-08-19 20:40 | 15 | 3:20 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE LAS LINEAS | M22081900223 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 200 | 2022-08-19 | 3000 | keep | 0 | Aug | 2022 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-08-19 17:33 | 2022-08-19 18:05 | 337 | 0:32 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE APRIMARIO ABIERTO | P22081900092 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 32 | 2022-08-19 | 10784 | keep | 0 | Aug | 2022 | 0.0073449 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-19 17:36 | 2022-08-20 10:15 | 10 | 16:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22081900096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 999 | 2022-08-19 | 9990 | keep | 0 | Aug | 2022 | 0.0068041 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-19 17:36 | 2022-08-19 20:15 | 42 | 2:39 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C22081900267 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 159 | 2022-08-19 | 6678 | keep | 0 | Aug | 2022 | 0.0045484 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
UTUADO | 2022-08-19 17:37 | 2022-08-19 17:38 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 3502 | keep | 0 | Aug | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-19 17:37 | 2022-08-19 17:38 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 1241 | keep | 0 | Aug | 2022 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-19 17:37 | 2022-08-19 17:38 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 650 | keep | 0 | Aug | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-19 17:37 | 2022-08-19 17:38 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900103 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-19 17:37 | 2022-08-19 17:38 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900103 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 654 | keep | 0 | Aug | 2022 | 0.00044544 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-19 17:40 | 2022-08-19 18:00 | 8 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C22081900266 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-08-19 | 160 | keep | 0 | Aug | 2022 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-19 17:49 | 2022-08-19 17:50 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22081900193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 2203 | keep | 0 | Aug | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2022-08-19 17:54 | 2022-08-20 15:05 | 50 | 21:11 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B22081900489 | New_Event | Primary Wire Break | Include | Include | Equipment | 1271 | 2022-08-19 | 63550 | keep | 0 | Aug | 2022 | 0.043284 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-19 18:03 | 2022-08-19 18:50 | 835 | 0:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22081900276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-08-19 | 39245 | keep | 0 | Aug | 2022 | 0.02673 | 0.00056871 | Sustained | FALSE | FALSE | Not_TMED_Event | 835
BAYAMON | 2022-08-19 18:24 | 2022-08-20 12:06 | 16 | 17:42 | P | DESGANCHE | 1X50 EN C/L | B22081900494 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1062 | 2022-08-19 | 16992 | keep | 0 | Aug | 2022 | 0.011573 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2022-08-19 18:29 | 2022-08-19 19:53 | 5 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22081900101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2022-08-19 | 420 | keep | 0 | Aug | 2022 | 0.00028606 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-19 18:30 | 2022-08-19 18:31 | 4476 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1336-10 | S22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 4476 | keep | 0 | Aug | 2022 | 0.0030486 | 0.0030486 | Momentary | FALSE | FALSE | Not_TMED_Event | 4476
SAN JUAN | 2022-08-19 18:30 | 2022-08-19 18:31 | 403 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO SU CARGA POR 1336-06 | S22081900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-08-19 | 403 | keep | 0 | Aug | 2022 | 0.00027448 | 0.00027448 | Momentary | FALSE | FALSE | Not_TMED_Event | 403
MAYAGÃœEZ | 2022-08-19 18:46 | 2022-08-19 22:22 | 350 | 3:36 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M22081900239 | New_Event | Primary Wire Break | Include | Include | Equipment | 216 | 2022-08-19 | 75600 | keep | 0 | Aug | 2022 | 0.051491 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
PONCE | 2022-08-19 18:47 | 2022-08-19 18:48 | 2113 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE POR DESCARGA ELECTRICA | P22081900133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-19 | 2113 | keep | 0 | Aug | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
UTUADO | 2022-08-19 18:48 | 2022-08-19 18:49 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900104 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 3502 | keep | 0 | Aug | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-19 18:48 | 2022-08-19 18:49 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900104 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 1241 | keep | 0 | Aug | 2022 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-19 18:48 | 2022-08-19 18:49 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900104 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 650 | keep | 0 | Aug | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-19 18:48 | 2022-08-19 18:49 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900105 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-19 18:48 | 2022-08-19 18:49 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900105 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 654 | keep | 0 | Aug | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
SAN JUAN | 2022-08-19 19:12 | 2022-08-20 11:21 | 5 | 16:09 | P | NO SE REPORTO CAUSA | 2X50 EN C/L | S22081900200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 969 | 2022-08-19 | 4845 | keep | 0 | Aug | 2022 | 0.0032999 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-19 19:12 | 2022-08-19 22:42 | 80 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | M22081900232 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2022-08-19 | 16800 | keep | 0 | Aug | 2022 | 0.011442 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-08-19 19:13 | 2022-08-19 19:14 | 508 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22081900137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 508 | keep | 0 | Aug | 2022 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
ARECIBO | 2022-08-19 19:13 | 2022-08-19 22:00 | 30 | 2:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | A22081900109 | New_Event | Primary Wire Break | Include | Include | Equipment | 167 | 2022-08-19 | 5010 | keep | 0 | Aug | 2022 | 0.0034123 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-19 19:14 | 2022-08-19 21:31 | 92 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN BOVEDA | R22081900078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-08-19 | 12604 | keep | 0 | Aug | 2022 | 0.0085845 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
ARECIBO | 2022-08-19 19:20 | 2022-08-19 19:47 | 458 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A22081900110 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-19 | 12366 | keep | 0 | Aug | 2022 | 0.0084224 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2022-08-19 19:20 | 2022-08-19 19:47 | 437 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A22081900110 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-19 | 11799 | keep | 0 | Aug | 2022 | 0.0080362 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2022-08-19 19:20 | 2022-08-19 19:47 | 1185 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A22081900110 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-19 | 31995 | keep | 0 | Aug | 2022 | 0.021792 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2022-08-19 19:20 | 2022-08-19 19:47 | 63 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A22081900110 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-19 | 1701 | keep | 0 | Aug | 2022 | 0.0011585 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2022-08-19 19:20 | 2022-08-19 19:47 | 232 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 | A22081900110 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-08-19 | 6264 | keep | 0 | Aug | 2022 | 0.0042664 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
UTUADO | 2022-08-19 19:22 | 2022-08-19 19:23 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900111 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 3502 | keep | 0 | Aug | 2022 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-19 19:22 | 2022-08-19 19:23 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900111 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 1241 | keep | 0 | Aug | 2022 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-19 19:22 | 2022-08-19 19:23 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900111 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 650 | keep | 0 | Aug | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-19 19:22 | 2022-08-19 19:23 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900112 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-19 19:22 | 2022-08-19 19:23 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900112 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-19 | 654 | keep | 0 | Aug | 2022 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
SAN JUAN | 2022-08-19 19:24 | 2022-08-19 21:52 | 5 | 2:28 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | S22081900203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-08-19 | 740 | keep | 0 | Aug | 2022 | 0.00050401 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-19 19:24 | 2022-08-20 07:35 | 300 | 12:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22081900308 | New_Event | Cutout Failure | Include | Include | Equipment | 731 | 2022-08-19 | 219300 | keep | 0 | Aug | 2022 | 0.14936 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2022-08-19 19:25 | 2022-08-19 21:03 | 30 | 1:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | C22081900309 | New_Event | Primary Wire Break | Include | Include | Equipment | 98 | 2022-08-19 | 2940 | keep | 0 | Aug | 2022 | 0.0020024 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-19 19:26 | 2022-08-19 19:30 | 3502 | 0:04 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900120 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-19 | 14008 | keep | 0 | Aug | 2022 | 0.0095408 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-19 19:26 | 2022-08-19 19:30 | 1241 | 0:04 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900120 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-19 | 4964 | keep | 0 | Aug | 2022 | 0.003381 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-19 19:26 | 2022-08-19 19:30 | 650 | 0:04 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900120 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-19 | 2600 | keep | 0 | Aug | 2022 | 0.0017708 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-19 19:26 | 2022-08-19 19:30 | 1382 | 0:04 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900119 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-19 | 5528 | keep | 0 | Aug | 2022 | 0.0037651 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-19 19:26 | 2022-08-19 19:30 | 654 | 0:04 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 4700 | A22081900119 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-19 | 2616 | keep | 0 | Aug | 2022 | 0.0017817 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
HUMACAO | 2022-08-19 19:28 | 2022-08-20 14:05 | 9 | 18:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22081900314 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1117 | 2022-08-19 | 10053 | keep | 0 | Aug | 2022 | 0.0068471 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2022-08-19 19:35 | 2022-08-20 13:00 | 10 | 17:25 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANHE SECUNDARIO | C22081900316 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1045 | 2022-08-19 | 10450 | keep | 0 | Aug | 2022 | 0.0071174 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-19 19:35 | 2022-08-19 19:52 | 3502 | 0:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22081900126 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-19 | 59534 | keep | 0 | Aug | 2022 | 0.040548 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-19 19:35 | 2022-08-19 19:52 | 1241 | 0:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22081900126 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-19 | 21097 | keep | 0 | Aug | 2022 | 0.014369 | 0.00084524 | Sustained | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-19 19:35 | 2022-08-19 19:52 | 650 | 0:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22081900126 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-19 | 11050 | keep | 0 | Aug | 2022 | 0.0075261 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-19 19:35 | 2022-08-19 19:52 | 1382 | 0:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22081900127 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-19 | 23494 | keep | 0 | Aug | 2022 | 0.016002 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-19 19:35 | 2022-08-19 19:52 | 654 | 0:17 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | A22081900127 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 17 | 2022-08-19 | 11118 | keep | 0 | Aug | 2022 | 0.0075724 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2022-08-19 19:48 | 2022-08-20 10:08 | 1 | 14:20 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR POR RAYOS | M22081900259 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 860 | 2022-08-19 | 860 | keep | 0 | Aug | 2022 | 0.00058574 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-19 19:54 | 2022-08-19 23:28 | 100 | 3:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES LLUVIAS | P22081900152 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 214 | 2022-08-19 | 21400 | keep | 0 | Aug | 2022 | 0.014575 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-19 19:54 | 2022-08-21 13:14 | 3 | 41:20 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR Y SE REPARA LINEA SECUNDARIA PARTIDA POR ARBOL | A22081900138 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2480 | 2022-08-19 | 7440 | keep | 0 | Aug | 2022 | 0.0050674 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-08-19 19:56 | 2022-08-19 23:30 | 400 | 3:34 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | P22081900156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2022-08-19 | 85600 | keep | 0 | Aug | 2022 | 0.058302 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
PONCE | 2022-08-19 19:58 | 2022-08-19 20:43 | 167 | 0:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | P22081900159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2022-08-19 | 7515 | keep | 0 | Aug | 2022 | 0.0051184 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
PONCE | 2022-08-19 19:58 | 2022-08-19 20:43 | 26 | 0:45 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 | P22081900159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2022-08-19 | 1170 | keep | 0 | Aug | 2022 | 0.00079688 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
UTUADO | 2022-08-19 19:58 | 2022-08-19 20:43 | 3502 | 0:45 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A22081900140 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2022-08-19 | 157590 | keep | 0 | Aug | 2022 | 0.10733 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-19 19:58 | 2022-08-19 20:43 | 1241 | 0:45 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A22081900140 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2022-08-19 | 55845 | keep | 0 | Aug | 2022 | 0.038036 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-19 19:58 | 2022-08-19 20:43 | 650 | 0:45 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 | A22081900140 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 45 | 2022-08-19 | 29250 | keep | 0 | Aug | 2022 | 0.019922 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-19 19:58 | 2022-08-20 16:34 | 1382 | 20:36 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZO LA SUBESTACION LUEGO DE REPARAR AVERIA EN LINEA 8100 | A22081900141 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1236 | 2022-08-19 | 1708152 | keep | 0 | Aug | 2022 | 1.1634 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-19 19:58 | 2022-08-20 16:34 | 654 | 20:36 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZO LA SUBESTACION LUEGO DE REPARAR AVERIA EN LINEA 8100 | A22081900141 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1236 | 2022-08-19 | 808344 | keep | 0 | Aug | 2022 | 0.55056 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-19 20:00 | 2022-08-19 22:06 | 50 | 2:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REFIRIO SITUACION DE DESGANCHE | M22081900263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-19 | 6300 | keep | 0 | Aug | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-19 20:12 | 2022-08-19 20:13 | 1617 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C22081900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 1617 | keep | 0 | Aug | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
YAUCO | 2022-08-19 20:15 | 2022-08-19 22:25 | 150 | 2:10 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22081900164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-08-19 | 19500 | keep | 0 | Aug | 2022 | 0.013281 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-08-19 20:26 | 2022-08-21 08:27 | 10 | 36:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIAS | A22081900217 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2161 | 2022-08-19 | 21610 | keep | 0 | Aug | 2022 | 0.014718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-19 20:51 | 2022-08-20 10:39 | 50 | 13:48 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | S22081900218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 828 | 2022-08-19 | 41400 | keep | 0 | Aug | 2022 | 0.028197 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-19 20:52 | 2022-08-19 22:00 | 1 | 1:08 | P | NO SE REPORTO CAUSA | 2 X 10 EN MONTURA | R22081900081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2022-08-19 | 68 | keep | 0 | Aug | 2022 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-19 21:00 | 2022-08-19 21:01 | 1722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22081900154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 1722 | keep | 0 | Aug | 2022 | 0.0011728 | 0.0011728 | Momentary | FALSE | FALSE | Not_TMED_Event | 1722
ARECIBO | 2022-08-19 21:00 | 2022-08-19 21:01 | 243 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | A22081900153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-19 | 243 | keep | 0 | Aug | 2022 | 0.00016551 | 0.00016551 | Momentary | FALSE | FALSE | Not_TMED_Event | 243
MAYAGÃœEZ | 2022-08-19 21:15 | 2022-08-22 17:05 | 1 | 67:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA SE CERRO PUENTES | M22082100414 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 4070 | 2022-08-19 | 4070 | keep | 0 | Aug | 2022 | 0.0027721 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-19 21:18 | 2022-08-19 22:54 | 1 | 1:36 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081900155 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 96 | 2022-08-19 | 96 | keep | 0 | Aug | 2022 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-19 21:42 | 2022-08-20 11:40 | 2 | 13:58 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZAR 150 PIES DE CABLE 3/4 PARTIDO POR RAMA | P22081900179 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 838 | 2022-08-19 | 1676 | keep | 0 | Aug | 2022 | 0.0011415 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-08-19 22:02 | 2022-08-20 11:35 | 60 | 13:33 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | C22081900340 | New_Event | Primary Wire Break | Include | Include | Equipment | 813 | 2022-08-19 | 48780 | keep | 0 | Aug | 2022 | 0.033224 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-19 22:23 | 2022-08-20 09:29 | 1 | 11:06 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B22081900519 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 666 | 2022-08-19 | 666 | keep | 0 | Aug | 2022 | 0.00045361 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-19 22:52 | 2022-08-20 01:00 | 100 | 2:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22081900190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2022-08-19 | 12800 | keep | 0 | Aug | 2022 | 0.008718 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-19 22:54 | 2022-08-19 22:55 | 1 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 7505-05 | A22081900027 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-19 | 1 | keep | 0 | Aug | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-19 22:54 | 2022-08-19 22:55 | 4607 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR CARGA POR 7505-01 | A22081900027 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-19 | 4607 | keep | 0 | Aug | 2022 | 0.0031378 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-19 22:55 | 2022-08-20 00:43 | 1 | 1:48 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22081900155 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 108 | 2022-08-19 | 108 | keep | 0 | Aug | 2022 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-19 22:57 | 2022-08-19 22:58 | 2201 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL INTERRUPTOR | A22081900165 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-19 | 2201 | keep | 0 | Aug | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-08-19 22:58 | 2022-08-20 00:37 | 150 | 1:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A22081900160 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 99 | 2022-08-19 | 14850 | keep | 0 | Aug | 2022 | 0.010114 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-19 23:02 | 2022-08-20 01:29 | 5 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTA FUSIBLE QUEMADO | A22081900161 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2022-08-19 | 735 | keep | 0 | Aug | 2022 | 0.00050061 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-08-20 00:15 | 2022-08-20 11:12 | 12 | 10:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | R22082000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 657 | 2022-08-20 | 7884 | keep | 0 | Aug | 2022 | 0.0053698 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-20 00:19 | 2022-08-20 02:18 | 50 | 1:59 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000001 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 119 | 2022-08-20 | 5950 | keep | 0 | Aug | 2022 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-20 00:37 | 2022-08-20 10:38 | 75 | 10:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | C22082000001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 601 | 2022-08-20 | 45075 | keep | 0 | Aug | 2022 | 0.0307 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-08-20 00:52 | 2022-08-20 09:39 | 18 | 8:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR Y 1 X 10 EN XMR | C22082000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 527 | 2022-08-20 | 9486 | keep | 0 | Aug | 2022 | 0.0064609 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-08-20 00:53 | 2022-08-20 07:32 | 15 | 6:39 | P | MAL TIEMPO/RAYOS | 1 X 140 EN C/L , DESCARGAS ELECTRICAS | M22082000005 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 399 | 2022-08-20 | 5985 | keep | 0 | Aug | 2022 | 0.0040764 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-20 00:59 | 2022-08-20 10:00 | 18 | 9:01 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A22082000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 541 | 2022-08-20 | 9738 | keep | 0 | Aug | 2022 | 0.0066325 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2022-08-20 02:28 | 2022-08-20 02:29 | 2005 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO 1619-03 Y LLEVA 1619-02 | R22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 2005 | keep | 0 | Aug | 2022 | 0.0013656 | 0.0013656 | Momentary | FALSE | FALSE | Not_TMED_Event | 2005
CANOVANAS | 2022-08-20 02:28 | 2022-08-20 02:29 | 5062 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1619-02 | R22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 5062 | keep | 0 | Aug | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
BARRANQUITAS | 2022-08-20 03:34 | 2022-08-20 08:48 | 100 | 5:14 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22082000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2022-08-20 | 31400 | keep | 0 | Aug | 2022 | 0.021386 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-08-20 03:55 | 2022-08-20 12:29 | 30 | 8:34 | P | ANIMAL | 1 SMU X 40 Y 1 X 50 RISER CRUCE POR RATA | C22082000006 | New_Event | Animals | Include | Include | Wildlife | 514 | 2022-08-20 | 15420 | keep | 0 | Aug | 2022 | 0.010502 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-08-20 04:13 | 2022-08-20 04:14 | 1617 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1617 | keep | 0 | Aug | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
HUMACAO | 2022-08-20 04:57 | 2022-08-20 04:58 | 1250 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 2901-04 | C22092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1250 | keep | 0 | Aug | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-08-20 04:57 | 2022-08-20 04:58 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO 2901-02 Y LLEVA 2901-04 | C22092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1827 | keep | 0 | Aug | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2022-08-20 05:13 | 2022-08-20 16:30 | 60 | 11:17 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 677 | 2022-08-20 | 40620 | keep | 0 | Aug | 2022 | 0.027666 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-08-20 05:32 | 2022-08-20 09:02 | 50 | 3:30 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | R22082000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-08-20 | 10500 | keep | 0 | Aug | 2022 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-20 05:40 | 2022-08-20 05:41 | 817 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | C22092000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 817 | keep | 0 | Aug | 2022 | 0.00055645 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
CAGUAS | 2022-08-20 05:41 | 2022-08-20 10:02 | 600 | 4:21 | P | NO SE REPORTO CAUSA | DISPARO DE INTELIRRUPTER 3006-04C SE CERRO INTELLIRUPTER EN EL CAMPO Y PROBO BUENO EN SERVICIO | C22082000010 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 261 | 2022-08-20 | 156600 | keep | 0 | Aug | 2022 | 0.10666 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
CAGUAS | 2022-08-20 06:10 | 2022-08-20 06:11 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082000016 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1702 | keep | 0 | Aug | 2022 | 0.0011592 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-20 06:11 | 2022-08-20 09:36 | 10 | 3:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22082000010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2022-08-20 | 2050 | keep | 0 | Aug | 2022 | 0.0013962 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-20 06:11 | 2022-08-20 08:59 | 30 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22082000027 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-08-20 | 5040 | keep | 0 | Aug | 2022 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-20 06:29 | 2022-08-20 10:26 | 959 | 3:57 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000/4000 - BAYAMON PUEBLO @ NARANJITO | B22082000018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 237 | 2022-08-20 | 227283 | keep | 0 | Aug | 2022 | 0.1548 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-08-20 06:29 | 2022-08-20 10:26 | 1382 | 3:57 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000/4000 - BAYAMON PUEBLO @ NARANJITO | B22082000018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 237 | 2022-08-20 | 327534 | keep | 0 | Aug | 2022 | 0.22308 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-20 06:29 | 2022-08-20 10:26 | 663 | 3:57 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000/4000 - BAYAMON PUEBLO @ NARANJITO | B22082000018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 237 | 2022-08-20 | 157131 | keep | 0 | Aug | 2022 | 0.10702 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-08-20 06:29 | 2022-08-20 10:30 | 1514 | 4:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000/4000 - BAYAMON PUEBLO @ NARANJITO | B22082000020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 241 | 2022-08-20 | 364874 | keep | 0 | Aug | 2022 | 0.24851 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-08-20 06:29 | 2022-08-20 10:30 | 1105 | 4:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000/4000 - BAYAMON PUEBLO @ NARANJITO | B22082000020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 241 | 2022-08-20 | 266305 | keep | 0 | Aug | 2022 | 0.18138 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2022-08-20 06:33 | 2022-08-20 16:22 | 20 | 9:49 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR SE REPARO SECUNDARIA DESGANCHE | S22082000005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 589 | 2022-08-20 | 11780 | keep | 0 | Aug | 2022 | 0.0080233 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-08-20 06:33 | 2022-08-20 08:48 | 3 | 2:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | P22082000009 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2022-08-20 | 405 | keep | 0 | Aug | 2022 | 0.00027584 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-08-20 06:34 | 2022-08-20 07:36 | 5063 | 1:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE REALIZA PRUEBA CON RR EN OFF Y QUEDA EN SERVICIO | P22082000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2022-08-20 | 313906 | keep | 0 | Aug | 2022 | 0.2138 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
UTUADO | 2022-08-20 06:55 | 2022-08-20 19:10 | 13 | 12:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS FUERTES | A22082000011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 735 | 2022-08-20 | 9555 | keep | 0 | Aug | 2022 | 0.0065079 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-08-20 06:56 | 2022-08-20 08:15 | 20 | 1:19 | P | ANIMAL | 1 X 50 EN C/L, CRUCE DE FASE POR AVE | M22082000024 | New_Event | Animals | Include | Include | Wildlife | 79 | 2022-08-20 | 1580 | keep | 0 | Aug | 2022 | 0.0010761 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-20 07:02 | 2022-08-20 12:19 | 70 | 5:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | M22082000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2022-08-20 | 22190 | keep | 0 | Aug | 2022 | 0.015114 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-08-20 07:32 | 2022-08-20 07:33 | 74 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1529-11 | S22082000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 74 | keep | 0 | Aug | 2022 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-08-20 07:32 | 2022-08-20 07:33 | 1370 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL LLEVA 1521-02 | S22082000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1370 | keep | 0 | Aug | 2022 | 0.0009331 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
BAYAMON | 2022-08-20 07:47 | 2022-08-21 17:11 | 5 | 33:24 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR SE REALIZO DESGANCHE SECUNDARIO | B22082000043 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 2004 | 2022-08-20 | 10020 | keep | 0 | Aug | 2022 | 0.0068246 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-20 07:49 | 2022-08-20 11:03 | 25 | 3:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22082000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-08-20 | 4850 | keep | 0 | Aug | 2022 | 0.0033033 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-08-20 07:50 | 2022-08-20 10:07 | 10 | 2:17 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | C22082000041 | New_Event | Animals | Include | Include | Wildlife | 137 | 2022-08-20 | 1370 | keep | 0 | Aug | 2022 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-20 07:54 | 2022-08-20 09:45 | 75 | 1:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | R22082000014 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2022-08-20 | 8325 | keep | 0 | Aug | 2022 | 0.0056701 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-08-20 08:00 | 2022-08-20 08:01 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22082000099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 4641 | keep | 0 | Aug | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
GUAYAMA | 2022-08-20 08:05 | 2022-08-20 10:10 | 50 | 2:05 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22082000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-08-20 | 6250 | keep | 0 | Aug | 2022 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-20 08:07 | 2022-08-20 12:22 | 25 | 4:15 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | R22082000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2022-08-20 | 6375 | keep | 0 | Aug | 2022 | 0.004342 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-20 08:11 | 2022-08-20 11:40 | 80 | 3:29 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082000021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2022-08-20 | 16720 | keep | 0 | Aug | 2022 | 0.011388 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-20 08:13 | 2022-08-20 11:20 | 5 | 3:07 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR RAYOS | M22082000053 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 187 | 2022-08-20 | 935 | keep | 0 | Aug | 2022 | 0.00063682 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-08-20 08:26 | 2022-08-20 10:30 | 25 | 2:04 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R22082000018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-08-20 | 3100 | keep | 0 | Aug | 2022 | 0.0021114 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-08-20 08:29 | 2022-08-20 09:45 | 144 | 1:16 | P | ANIMAL | 1 X 65 EN C/L AVE | R22082000019 | New_Event | Animals | Include | Include | Wildlife | 76 | 2022-08-20 | 10944 | keep | 0 | Aug | 2022 | 0.0074539 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
AGUADILLA | 2022-08-20 08:42 | 2022-08-20 15:05 | 10 | 6:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | M22082000059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 383 | 2022-08-20 | 3830 | keep | 0 | Aug | 2022 | 0.0026086 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-20 08:47 | 2022-08-20 10:58 | 60 | 2:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 200 SE REEMPLAZO AISLADOR | R22082000021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 131 | 2022-08-20 | 7860 | keep | 0 | Aug | 2022 | 0.0053534 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-20 09:00 | 2022-08-20 10:21 | 20 | 1:21 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C22082000057 | New_Event | Animals | Include | Include | Wildlife | 81 | 2022-08-20 | 1620 | keep | 0 | Aug | 2022 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-20 09:07 | 2022-08-20 12:40 | 30 | 3:33 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A22082000030 | New_Event | Animals | Include | Include | Wildlife | 213 | 2022-08-20 | 6390 | keep | 0 | Aug | 2022 | 0.0043522 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-20 09:17 | 2022-08-21 13:02 | 1 | 27:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIA | B22082000068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1665 | 2022-08-20 | 1665 | keep | 0 | Aug | 2022 | 0.001134 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-20 09:25 | 2022-08-20 10:10 | 200 | 0:45 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22082000027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-08-20 | 9000 | keep | 0 | Aug | 2022 | 0.0061299 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-20 09:32 | 2022-08-20 11:42 | 15 | 2:10 | P | DESGANCHE | 1 X 50 EN C/L | R22082000030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2022-08-20 | 1950 | keep | 0 | Aug | 2022 | 0.0013281 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-20 10:00 | 2022-08-20 13:06 | 2 | 3:06 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR RAYOS | M22082000106 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 186 | 2022-08-20 | 372 | keep | 0 | Aug | 2022 | 0.00025337 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-20 10:06 | 2022-08-20 14:39 | 160 | 4:33 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | S22082000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 273 | 2022-08-20 | 43680 | keep | 0 | Aug | 2022 | 0.02975 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2022-08-20 10:13 | 2022-08-20 14:20 | 1586 | 4:07 | P | PROBLEMA DEL CLIENTE | SE DESCONECTO MONTURA QUE SIRVE A FAST SIGNS Y SE CERRO INTERRUPTOR VER GOI BY-220820-01 LLEVA 90% DEL 1711-04 TRANSFERIDA AL 1801-02 | B22082000083 | New_Event | Customer-Related Interruption | Include | Include | Public | 247 | 2022-08-20 | 391742 | keep | 0 | Aug | 2022 | 0.26681 | 0.0010802 | Sustained | FALSE | FALSE | Not_TMED_Event | 1586
BAYAMON | 2022-08-20 10:13 | 2022-08-20 14:20 | 186 | 4:07 | T | PROBLEMA DEL CLIENTE | SE DESCONECTO MONTURA QUE SIRVE A FAST SIGNS Y SE CERRO INTERRUPTOR VER GOI BY-220820-01 LLEVA 90% DEL 1711-04 | B22082000083 | New_Event | Customer-Related Interruption | Include | Include | Public | 247 | 2022-08-20 | 45942 | keep | 0 | Aug | 2022 | 0.031291 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
VEGA BAJA | 2022-08-20 10:15 | 2022-08-20 14:30 | 25 | 4:15 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO POSTE SECUNDARIO PARTIDO | A22082000057 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 255 | 2022-08-20 | 6375 | keep | 0 | Aug | 2022 | 0.004342 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-20 10:23 | 2022-08-20 17:15 | 341 | 6:52 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE SIN VIA LIBRE POR MAL ESTADO WR-6221165 | S22082000038 | New_Event | Primary Pole Failure | Include | Include | Equipment | 412 | 2022-08-20 | 140492 | keep | 0 | Aug | 2022 | 0.095688 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2022-08-20 10:27 | 2022-08-20 12:52 | 480 | 2:25 | P | DESGANCHE | 1X100 EN C/L | S22082000032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-08-20 | 69600 | keep | 0 | Aug | 2022 | 0.047404 | 0.00032693 | Sustained | FALSE | FALSE | Not_TMED_Event | 480
BARRANQUITAS | 2022-08-20 10:30 | 2022-08-20 10:31 | 2770 | 0:01 | T | DESGANCHE | RECIERRE | C22082000000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-20 | 2770 | keep | 0 | Aug | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
BARRANQUITAS | 2022-08-20 10:31 | 2022-08-20 12:58 | 30 | 2:27 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22082000079 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-08-20 | 4410 | keep | 0 | Aug | 2022 | 0.0030036 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-20 10:34 | 2022-08-20 11:55 | 7 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARA BARRAS EN PEDESTAL | M22082000088 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2022-08-20 | 567 | keep | 0 | Aug | 2022 | 0.00038618 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-08-20 10:38 | 2022-08-20 10:40 | 3502 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA | A22082000059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 7004 | keep | 0 | Aug | 2022 | 0.0047704 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-20 10:38 | 2022-08-20 10:40 | 1241 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA | A22082000059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 2482 | keep | 0 | Aug | 2022 | 0.0016905 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-20 10:38 | 2022-08-20 10:40 | 650 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA | A22082000059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 1300 | keep | 0 | Aug | 2022 | 0.00088542 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
HUMACAO | 2022-08-20 11:05 | 2022-08-20 11:06 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082000080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 551 | keep | 0 | Aug | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
MAYAGÃœEZ | 2022-08-20 11:05 | 2022-08-20 13:15 | 4 | 2:10 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | M22082000093 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 130 | 2022-08-20 | 520 | keep | 0 | Aug | 2022 | 0.00035417 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-20 11:07 | 2022-08-20 12:13 | 20 | 1:06 | P | DESGANCHE | 1 X 25 EN C/L | R22082000041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-08-20 | 1320 | keep | 0 | Aug | 2022 | 0.00089905 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-08-20 11:09 | 2022-08-20 11:10 | 3973 | 0:01 | T | ERROR HUMANO | SE DISPARA INTERRUPTOR DURANTE VERIFICACION SISTEMA CONTROL CON CARGA 5602-03 | P22082000047 | New_Event | Human Error | Include | Include | Other | 1 | 2022-08-20 | 3973 | keep | 0 | Aug | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-08-20 11:09 | 2022-08-20 11:10 | 2484 | 0:01 | T | ERROR HUMANO | SE DISPARA INTERRUPTOR DURANTE VERIFICACION SISTEMA CONTROL CON CARGA 5602-03 | P22082000047 | New_Event | Human Error | Include | Include | Other | 1 | 2022-08-20 | 2484 | keep | 0 | Aug | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
CAGUAS | 2022-08-20 11:20 | 2022-08-20 14:27 | 20 | 3:07 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C22082000082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-08-20 | 3740 | keep | 0 | Aug | 2022 | 0.0025473 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-08-20 11:30 | 2022-08-22 11:40 | 2 | 48:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 37.5KVA | A22082000070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2890 | 2022-08-20 | 5780 | keep | 0 | Aug | 2022 | 0.0039367 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-08-20 11:38 | 2022-08-20 20:09 | 8 | 8:31 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22082000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 511 | 2022-08-20 | 4088 | keep | 0 | Aug | 2022 | 0.0027843 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-08-20 11:39 | 2022-08-20 14:40 | 15 | 3:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR Y DESGANCHE | R22082000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 181 | 2022-08-20 | 2715 | keep | 0 | Aug | 2022 | 0.0018492 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-20 11:46 | 2022-08-20 15:16 | 81 | 3:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | B22082000124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 210 | 2022-08-20 | 17010 | keep | 0 | Aug | 2022 | 0.011585 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
HUMACAO | 2022-08-20 11:52 | 2022-08-20 16:42 | 17 | 4:50 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22082000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2022-08-20 | 4930 | keep | 0 | Aug | 2022 | 0.0033578 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
GUAYAMA | 2022-08-20 11:55 | 2022-08-20 12:30 | 5 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | P22082000054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-08-20 | 175 | keep | 0 | Aug | 2022 | 0.00011919 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-20 11:59 | 2022-08-20 13:06 | 100 | 1:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIAS | B22082000134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 67 | 2022-08-20 | 6700 | keep | 0 | Aug | 2022 | 0.0045633 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-20 12:04 | 2022-08-20 15:18 | 12 | 3:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | R22082000047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 194 | 2022-08-20 | 2328 | keep | 0 | Aug | 2022 | 0.0015856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-08-20 12:05 | 2022-08-20 19:09 | 82 | 7:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C22082000093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 424 | 2022-08-20 | 34768 | keep | 0 | Aug | 2022 | 0.02368 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
CAGUAS | 2022-08-20 12:07 | 2022-08-22 20:44 | 1 | 56:37 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN RISER SE ELIMINO PARARRAYO CRUZADO | C22082000095 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 3397 | 2022-08-20 | 3397 | keep | 0 | Aug | 2022 | 0.0023137 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-20 12:08 | 2022-08-20 16:50 | 25 | 4:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN C/L SE REMPLAZO CAJA | B22082000141 | New_Event | Cutout Failure | Include | Include | Equipment | 282 | 2022-08-20 | 7050 | keep | 0 | Aug | 2022 | 0.0048017 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-08-20 12:14 | 2022-08-20 14:03 | 60 | 1:49 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR AVE | P22082000058 | New_Event | Animals | Include | Include | Wildlife | 109 | 2022-08-20 | 6540 | keep | 0 | Aug | 2022 | 0.0044544 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2022-08-20 12:15 | 2022-08-20 14:33 | 1 | 2:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR RAMAS SOBRE LINEA | P22082000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-08-20 | 138 | keep | 0 | Aug | 2022 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-20 12:16 | 2022-08-20 14:19 | 50 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000103 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-08-20 | 6150 | keep | 0 | Aug | 2022 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-20 12:29 | 2022-08-20 22:19 | 100 | 9:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA | B22082000154 | New_Event | Cutout Failure | Include | Include | Equipment | 590 | 2022-08-20 | 59000 | keep | 0 | Aug | 2022 | 0.040185 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-08-20 12:35 | 2022-08-20 13:32 | 1 | 0:57 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 EN MONTURA TRIFASICA SE REPARO BAJANTE PRIMARIO | P22082000062 | New_Event | Primary Wire Break | Include | Include | Equipment | 57 | 2022-08-20 | 57 | keep | 0 | Aug | 2022 | 3.8822e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-20 12:46 | 2022-08-21 15:16 | 2 | 26:30 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22082000158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1590 | 2022-08-20 | 3180 | keep | 0 | Aug | 2022 | 0.0021659 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-08-20 12:50 | 2022-08-20 14:50 | 30 | 2:00 | P | ANIMAL | 1 X 200 EN C/L CRUCE POR AVE | C22082000103 | New_Event | Animals | Include | Include | Wildlife | 120 | 2022-08-20 | 3600 | keep | 0 | Aug | 2022 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-20 12:53 | 2022-08-20 12:54 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 50% DE SU CARGA TRANSFERIDA AL 1909-07 LLEVA LA CARGA TOTAL DEL 1709-05 | S22082000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 766 | keep | 0 | Aug | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-08-20 12:53 | 2022-08-20 12:54 | 1139 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 50% DEL 1709-03 | S22082000062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1139 | keep | 0 | Aug | 2022 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
MAYAGÃœEZ | 2022-08-20 13:08 | 2022-08-20 15:05 | 100 | 1:57 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000116 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-08-20 | 11700 | keep | 0 | Aug | 2022 | 0.0079688 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-08-20 13:22 | 2022-08-20 15:19 | 332 | 1:57 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 100 Y 1 X 30 EN CORTES DE LINEA | R22082000051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-08-20 | 38844 | keep | 0 | Aug | 2022 | 0.026456 | 0.00022612 | Sustained | FALSE | FALSE | Not_TMED_Event | 332
BAYAMON | 2022-08-20 13:23 | 2022-08-20 15:40 | 80 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L 1 X 80 EN RISER | S22082000066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2022-08-20 | 10960 | keep | 0 | Aug | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-20 13:30 | 2022-08-20 14:29 | 10 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22082000071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2022-08-20 | 590 | keep | 0 | Aug | 2022 | 0.00040185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-08-20 13:39 | 2022-08-20 16:12 | 9 | 2:33 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO ZAFADO DE XMR | P22082000068 | New_Event | Primary Wire Break | Include | Include | Equipment | 153 | 2022-08-20 | 1377 | keep | 0 | Aug | 2022 | 0.00093787 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2022-08-20 13:51 | 2022-08-20 21:22 | 85 | 7:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22082000108 | New_Event | Cutout Failure | Include | Include | Equipment | 451 | 2022-08-20 | 38335 | keep | 0 | Aug | 2022 | 0.02611 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
UTUADO | 2022-08-20 13:57 | 2022-08-20 23:00 | 40 | 9:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22082000093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 543 | 2022-08-20 | 21720 | keep | 0 | Aug | 2022 | 0.014793 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-20 13:58 | 2022-08-20 16:06 | 6 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA | S22082000077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2022-08-20 | 768 | keep | 0 | Aug | 2022 | 0.00052308 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-08-20 14:06 | 2022-08-20 15:27 | 14 | 1:21 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA DESGANCHE | C22082000109 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 81 | 2022-08-20 | 1134 | keep | 0 | Aug | 2022 | 0.00077236 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2022-08-20 14:08 | 2022-08-20 14:09 | 3718 | 0:01 | T | ANIMAL | RECIERRE | P22082000075 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-20 | 3718 | keep | 0 | Aug | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
GUAYAMA | 2022-08-20 14:09 | 2022-08-20 15:18 | 80 | 1:09 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE | P22082000076 | 1st_after_momentary | Animals | Include | Include | Wildlife | 69 | 2022-08-20 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-08-20 14:13 | 2022-08-20 16:26 | 90 | 2:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA 100A EN CL CON 1 X 65 | P22082000077 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2022-08-20 | 11970 | keep | 0 | Aug | 2022 | 0.0081527 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-08-20 14:24 | 2022-08-20 14:25 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 2605 | keep | 0 | Aug | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
PONCE | 2022-08-20 14:27 | 2022-08-20 15:21 | 100 | 0:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P22082000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-08-20 | 5400 | keep | 0 | Aug | 2022 | 0.0036779 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-20 14:27 | 2022-08-20 14:28 | 2071 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR | A22082000097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 2071 | keep | 0 | Aug | 2022 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
SAN JUAN | 2022-08-20 14:28 | 2022-08-20 14:29 | 726 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-03 LLEVA 1346-04 CERRADO POR SCADA | S22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 726 | keep | 0 | Aug | 2022 | 0.00049448 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-08-20 14:28 | 2022-08-20 14:29 | 3932 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-03 LLEVA 1346-04 CERRADO POR SCADA | S22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 3932 | keep | 0 | Aug | 2022 | 0.0026781 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
YAUCO | 2022-08-20 14:28 | 2022-08-20 14:29 | 968 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082000085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 968 | keep | 0 | Aug | 2022 | 0.0006593 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-08-20 14:28 | 2022-08-20 14:29 | 680 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082000085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 680 | keep | 0 | Aug | 2022 | 0.00046314 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
MAYAGÃœEZ | 2022-08-20 14:29 | 2022-08-20 18:30 | 100 | 4:01 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000142 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 241 | 2022-08-20 | 24100 | keep | 0 | Aug | 2022 | 0.016414 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-20 14:32 | 2022-08-20 14:33 | 2071 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22082000099 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 2071 | keep | 0 | Aug | 2022 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
AGUADILLA | 2022-08-20 14:33 | 2022-08-20 16:50 | 120 | 2:17 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000144 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 137 | 2022-08-20 | 16440 | keep | 0 | Aug | 2022 | 0.011197 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BARRANQUITAS | 2022-08-20 14:41 | 2022-08-21 07:52 | 29 | 17:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C22082000112 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1031 | 2022-08-20 | 29899 | keep | 0 | Aug | 2022 | 0.020364 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BARRANQUITAS | 2022-08-20 14:44 | 2022-08-20 17:40 | 8 | 2:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25KVA X 37.5KVA | C22082000113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 176 | 2022-08-20 | 1408 | keep | 0 | Aug | 2022 | 0.00095898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-20 14:46 | 2022-08-20 17:28 | 50 | 2:42 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082000212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 162 | 2022-08-20 | 8100 | keep | 0 | Aug | 2022 | 0.0055169 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-20 15:03 | 2022-08-21 12:15 | 1 | 21:12 | P | MAL TIEMPO/RAYOS | 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082000181 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1272 | 2022-08-20 | 1272 | keep | 0 | Aug | 2022 | 0.00086635 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-20 15:05 | 2022-08-20 20:44 | 80 | 5:39 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L NEUTRAL CRUZADO CON FASE | B22082000214 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 339 | 2022-08-20 | 27120 | keep | 0 | Aug | 2022 | 0.018471 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-20 15:05 | 2022-08-20 15:08 | 3041 | 0:03 | T | MAL TIEMPO/RAYOS | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS SE CERRO INTERRUPTOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082000184 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 3 | 2022-08-20 | 9123 | keep | 0 | Aug | 2022 | 0.0062136 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 574 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 1148 | keep | 0 | Aug | 2022 | 0.0007819 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 2493 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 4986 | keep | 0 | Aug | 2022 | 0.0033959 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 1415 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 2830 | keep | 0 | Aug | 2022 | 0.0019275 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 1428 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 2856 | keep | 0 | Aug | 2022 | 0.0019452 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 1036 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 2072 | keep | 0 | Aug | 2022 | 0.0014112 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 382 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 LLEVA CARGA DE 7302-02 | M22082000197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 764 | keep | 0 | Aug | 2022 | 0.00052036 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 39 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 CARGA POR 7302-01 | M22082000197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 78 | keep | 0 | Aug | 2022 | 5.3125e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2022-08-20 15:05 | 2022-08-20 15:07 | 2366 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 4732 | keep | 0 | Aug | 2022 | 0.0032229 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2022-08-20 15:05 | 2022-08-20 15:07 | 1337 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 2674 | keep | 0 | Aug | 2022 | 0.0018212 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2022-08-20 15:05 | 2022-08-20 15:07 | 709 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 | M22082000198 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-20 | 1418 | keep | 0 | Aug | 2022 | 0.00096579 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
MAYAGÃœEZ | 2022-08-20 15:07 | 2022-08-20 16:36 | 100 | 1:29 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000116 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 89 | 2022-08-20 | 8900 | keep | 0 | Aug | 2022 | 0.0060617 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-20 15:08 | 2022-08-20 17:15 | 10 | 2:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | M22082000059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 127 | 2022-08-20 | 1270 | keep | 0 | Aug | 2022 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-20 15:11 | 2022-08-20 16:48 | 60 | 1:37 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 97 | 2022-08-20 | 5820 | keep | 0 | Aug | 2022 | 0.003964 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-20 15:14 | 2022-08-20 21:00 | 120 | 5:46 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA Y 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082000192 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 346 | 2022-08-20 | 41520 | keep | 0 | Aug | 2022 | 0.028279 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-08-20 15:20 | 2022-08-20 15:21 | 2946 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082000200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 2946 | keep | 0 | Aug | 2022 | 0.0020065 | 0.0020065 | Momentary | FALSE | FALSE | Not_TMED_Event | 2946
AGUADILLA | 2022-08-20 15:20 | 2022-08-20 15:21 | 1047 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082000201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1047 | keep | 0 | Aug | 2022 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
BAYAMON | 2022-08-20 15:22 | 2022-08-21 05:24 | 100 | 14:02 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 1 X 65 EN C/L MAL TIEMPO RAYOS | B22082000220 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 842 | 2022-08-20 | 84200 | keep | 0 | Aug | 2022 | 0.057348 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-20 15:26 | 2022-08-20 15:27 | 863 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082000209 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 863 | keep | 0 | Aug | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-08-20 15:30 | 2022-08-20 18:15 | 2366 | 2:45 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEAS SE CERRO INTERRUPTOR MANUAL ELECTRICO | M22082000422 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 165 | 2022-08-20 | 390390 | keep | 0 | Aug | 2022 | 0.26589 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
YAUCO | 2022-08-20 15:34 | 2022-08-20 17:20 | 100 | 1:46 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000215 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 106 | 2022-08-20 | 10600 | keep | 0 | Aug | 2022 | 0.0072196 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-20 15:35 | 2022-08-20 18:00 | 80 | 2:25 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000216 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 145 | 2022-08-20 | 11600 | keep | 0 | Aug | 2022 | 0.0079007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-20 15:39 | 2022-08-20 18:31 | 120 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000218 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2022-08-20 | 20640 | keep | 0 | Aug | 2022 | 0.014058 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-08-20 15:45 | 2022-08-21 01:18 | 40 | 9:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22082000228 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 573 | 2022-08-20 | 22920 | keep | 0 | Aug | 2022 | 0.015611 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-20 15:48 | 2022-08-20 15:49 | 3630 | 0:01 | T | MAL TIEMPO/RAYOS | DISPARO INTERRUPTOR 6014-02 MAL TIEMPO DESCARGAS ELECTRICAS SE CERRO INTERRUPTOR POR CONTROL SCADA | M22082000236 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-20 | 3630 | keep | 0 | Aug | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-08-20 15:49 | 2022-08-20 15:50 | 4664 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082000251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 4664 | keep | 0 | Aug | 2022 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2022-08-20 15:49 | 2022-08-20 19:55 | 100 | 4:06 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000465 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 246 | 2022-08-20 | 24600 | keep | 0 | Aug | 2022 | 0.016755 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-20 15:54 | 2022-08-21 11:20 | 50 | 19:26 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000245 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1166 | 2022-08-20 | 58300 | keep | 0 | Aug | 2022 | 0.039708 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-20 15:55 | 2022-08-20 18:30 | 200 | 2:35 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082000114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 155 | 2022-08-20 | 31000 | keep | 0 | Aug | 2022 | 0.021114 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-08-20 15:55 | 2022-08-20 15:56 | 1617 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1617 | keep | 0 | Aug | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
MAYAGÃœEZ | 2022-08-20 16:00 | 2022-08-22 18:36 | 108 | 50:36 | S | LINEA DE TRANSMISION 38KV | AVERIA LINEA 1500 | M22082000257 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3036 | 2022-08-20 | 327888 | keep | 0 | Aug | 2022 | 0.22332 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
BAYAMON | 2022-08-20 16:01 | 2022-08-21 04:22 | 60 | 12:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO VIENTOS | B22082000231 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 741 | 2022-08-20 | 44460 | keep | 0 | Aug | 2022 | 0.030282 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-20 16:04 | 2022-08-21 05:33 | 50 | 13:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22082000116 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 809 | 2022-08-20 | 40450 | keep | 0 | Aug | 2022 | 0.02755 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-20 16:04 | 2022-08-21 12:22 | 50 | 20:18 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR RAMA SOBRE LINEA | A22082000116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1218 | 2022-08-20 | 60900 | keep | 0 | Aug | 2022 | 0.041479 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-20 16:05 | 2022-08-20 18:00 | 150 | 1:55 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000376 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 115 | 2022-08-20 | 17250 | keep | 0 | Aug | 2022 | 0.011749 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-20 16:05 | 2022-08-21 12:00 | 1 | 19:55 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000264 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1195 | 2022-08-20 | 1195 | keep | 0 | Aug | 2022 | 0.00081391 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-20 16:06 | 2022-08-20 17:57 | 45 | 1:51 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000440 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 111 | 2022-08-20 | 4995 | keep | 0 | Aug | 2022 | 0.0034021 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-08-20 16:18 | 2022-08-21 01:19 | 100 | 9:01 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO DE CORTE DE LINEA | A22082000127 | New_Event | Primary Wire Break | Include | Include | Equipment | 541 | 2022-08-20 | 54100 | keep | 0 | Aug | 2022 | 0.036847 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-20 16:23 | 2022-08-20 21:54 | 30 | 5:31 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | S22082000096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-08-20 | 9930 | keep | 0 | Aug | 2022 | 0.0067633 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-20 16:23 | 2022-08-21 16:45 | 30 | 24:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRARON BAMBUAS DE LAS LINEAS | M22082000301 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1462 | 2022-08-20 | 43860 | keep | 0 | Aug | 2022 | 0.029873 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-20 16:30 | 2022-08-20 18:40 | 35 | 2:10 | P | MAL TIEMPO/RAYOS | 1 X 40 Y 1 X 30 EN CORTES DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000311 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 130 | 2022-08-20 | 4550 | keep | 0 | Aug | 2022 | 0.003099 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-08-20 16:31 | 2022-08-20 19:14 | 30 | 2:43 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082000135 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 163 | 2022-08-20 | 4890 | keep | 0 | Aug | 2022 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-20 16:34 | 2022-08-21 14:30 | 60 | 21:56 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22082000314 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1316 | 2022-08-20 | 78960 | keep | 0 | Aug | 2022 | 0.053779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-20 16:44 | 2022-08-20 18:40 | 80 | 1:56 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000328 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 116 | 2022-08-20 | 9280 | keep | 0 | Aug | 2022 | 0.0063206 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-20 16:44 | 2022-08-20 20:00 | 60 | 3:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIA | B22082000247 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 196 | 2022-08-20 | 11760 | keep | 0 | Aug | 2022 | 0.0080097 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-08-20 17:06 | 2022-08-20 18:59 | 125 | 1:53 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CONVERTIDOR DESCARGA ELECTRICA | P22082000110 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 113 | 2022-08-20 | 14125 | keep | 0 | Aug | 2022 | 0.0096205 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-08-20 17:07 | 2022-08-20 17:08 | 681 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1520-02 LLEVA 1530-09 SE CERRO POR SCADA | S22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 681 | keep | 0 | Aug | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-08-20 17:07 | 2022-08-20 17:08 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1520-02 LLEVA 1530-09 SE CERRO POR SCADA | S22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1310 | keep | 0 | Aug | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-08-20 17:10 | 2022-08-22 02:30 | 30 | 33:20 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-18 EN SERVICIO | B22082000250 | New_Event | UG Cable Fault | Include | Include | Equipment | 2000 | 2022-08-20 | 60000 | keep | 0 | Aug | 2022 | 0.040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-20 17:10 | 2022-08-20 20:00 | 300 | 2:50 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA AVERIADA | M22082000380 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2022-08-20 | 51000 | keep | 0 | Aug | 2022 | 0.034736 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-08-20 17:25 | 2022-08-20 17:26 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 95% 1717-02 | B22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-20 17:25 | 2022-08-20 17:26 | 865 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 95% DE SU CARGA TRANSFERIDO AL 1713-05 | B22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 865 | keep | 0 | Aug | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
UTUADO | 2022-08-20 17:25 | 2022-08-21 17:30 | 25 | 24:05 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082000156 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1445 | 2022-08-20 | 36125 | keep | 0 | Aug | 2022 | 0.024605 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-20 17:32 | 2022-08-21 00:23 | 188 | 6:51 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22082000255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2022-08-20 | 77268 | keep | 0 | Aug | 2022 | 0.052627 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
UTUADO | 2022-08-20 17:38 | 2022-08-21 10:43 | 15 | 17:05 | P | MAL TIEMPO/RAYOS | 3 X 15 EN TRANSFORMADORES POR RAYOS | A22082000162 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1025 | 2022-08-20 | 15375 | keep | 0 | Aug | 2022 | 0.010472 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-20 17:42 | 2022-08-21 14:00 | 40 | 20:18 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22082000241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1218 | 2022-08-20 | 48720 | keep | 0 | Aug | 2022 | 0.033183 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-20 17:51 | 2022-08-20 20:11 | 150 | 2:20 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L RAYOS | B22082000269 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 140 | 2022-08-20 | 21000 | keep | 0 | Aug | 2022 | 0.014303 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-20 17:53 | 2022-08-20 20:15 | 20 | 2:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22082000437 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-08-20 | 2840 | keep | 0 | Aug | 2022 | 0.0019343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-20 17:56 | 2022-08-21 12:27 | 30 | 18:31 | P | MAL TIEMPO/RAYOS | 2 X 65 EN RISER HACIA SU-2 RAYO | B22082000272 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1111 | 2022-08-20 | 33330 | keep | 0 | Aug | 2022 | 0.022701 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-08-20 17:56 | 2022-08-20 18:09 | 1 | 0:13 | P | CAUSAS EXTERNAS | 1 X 50 EN RISER CONTAMINACION GABINETE | P22082000124 | New_Event | Damage From Public | Include | Include | Public | 13 | 2022-08-20 | 13 | keep | 0 | Aug | 2022 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-20 17:59 | 2022-08-20 20:00 | 292 | 2:01 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L Y 2 X 65 EN RISER | R22082000064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-08-20 | 35332 | keep | 0 | Aug | 2022 | 0.024064 | 0.00019888 | Sustained | FALSE | FALSE | Not_TMED_Event | 292
GUAYAMA | 2022-08-20 18:02 | 2022-08-20 21:21 | 35 | 3:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22082000125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-08-20 | 6965 | keep | 0 | Aug | 2022 | 0.0047438 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-08-20 18:03 | 2022-08-21 14:14 | 60 | 20:11 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO (RADIAL) Y SE CERRO C/L (NO FUNDIO) | B22082000279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1211 | 2022-08-20 | 72660 | keep | 0 | Aug | 2022 | 0.049488 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-20 18:05 | 2022-08-20 22:41 | 1185 | 4:36 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTE PRIMARIO PARA SECCIONALIZAR TRAMO AVERIADO Y SE CERRO INTERRUPTOR POR SCADA | M22082000497 | New_Event | Primary Wire Break | Include | Include | Equipment | 276 | 2022-08-20 | 327060 | keep | 0 | Aug | 2022 | 0.22276 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2022-08-20 18:05 | 2022-08-20 20:38 | 20 | 2:33 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082000179 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 153 | 2022-08-20 | 3060 | keep | 0 | Aug | 2022 | 0.0020842 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-08-20 18:19 | 2022-08-20 18:20 | 508 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082000127 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 508 | keep | 0 | Aug | 2022 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
BAYAMON | 2022-08-20 18:25 | 2022-08-20 18:26 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-20 | 959 | keep | 0 | Aug | 2022 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-08-20 18:25 | 2022-08-20 18:26 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-20 | 1382 | keep | 0 | Aug | 2022 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-20 18:25 | 2022-08-20 18:26 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-20 | 663 | keep | 0 | Aug | 2022 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-08-20 18:25 | 2022-08-20 18:26 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-20 | 1514 | keep | 0 | Aug | 2022 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-08-20 18:25 | 2022-08-20 18:26 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22082000000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-20 | 1105 | keep | 0 | Aug | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
VEGA BAJA | 2022-08-20 18:33 | 2022-08-20 21:27 | 12 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22082000288 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-20 | 2088 | keep | 0 | Aug | 2022 | 0.0014221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-20 18:36 | 2022-08-22 08:56 | 25 | 38:20 | P | DESGANCHE | 2 X 40 EN C/L Y DESGANCHE | S22082000106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2300 | 2022-08-20 | 57500 | keep | 0 | Aug | 2022 | 0.039163 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-20 18:39 | 2022-08-20 18:41 | 199 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 1529-13 LLEVA 25% DEL 1911-07 CERRADO POR SCADA | S22082000108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-20 | 398 | keep | 0 | Aug | 2022 | 0.00027108 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
BAYAMON | 2022-08-20 18:39 | 2022-08-20 18:41 | 144 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 1529-13 LLEVA 25% DEL 1911-07 CERRADO POR SCADA | S22082000108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-20 | 288 | keep | 0 | Aug | 2022 | 0.00019616 | 9.8078e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 144
HUMACAO | 2022-08-20 18:48 | 2022-08-21 08:52 | 24 | 14:04 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C22082000127 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 844 | 2022-08-20 | 20256 | keep | 0 | Aug | 2022 | 0.013796 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CANOVANAS | 2022-08-20 19:00 | 2022-08-21 10:14 | 5 | 15:14 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | R22082000071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 914 | 2022-08-20 | 4570 | keep | 0 | Aug | 2022 | 0.0031126 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-20 19:04 | 2022-08-20 22:16 | 50 | 3:12 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LAS LINEAS | M22082000049 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 192 | 2022-08-20 | 9600 | keep | 0 | Aug | 2022 | 0.0065385 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-20 19:09 | 2022-08-21 10:17 | 6 | 15:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 TRANSFORMADOR POR LLUVIAS | A22082000198 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 908 | 2022-08-20 | 5448 | keep | 0 | Aug | 2022 | 0.0037106 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-20 19:11 | 2022-08-21 03:00 | 156 | 7:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082000298 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 469 | 2022-08-20 | 73164 | keep | 0 | Aug | 2022 | 0.049832 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
SAN JUAN | 2022-08-20 19:25 | 2022-08-20 19:55 | 4 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA SIN ABRIR XMR | S22082000114 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-08-20 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-20 19:25 | 2022-08-20 22:10 | 50 | 2:45 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22082000074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2022-08-20 | 8250 | keep | 0 | Aug | 2022 | 0.005619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-20 19:25 | 2022-08-21 03:50 | 102 | 8:25 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | B22082000308 | New_Event | Vegetation Contact | Include | Include | Vegetation | 505 | 2022-08-20 | 51510 | keep | 0 | Aug | 2022 | 0.035083 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
FAJARDO | 2022-08-20 19:42 | 2022-08-21 10:56 | 28 | 15:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR SE RETIRO BAMBUA | R22082000078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 914 | 2022-08-20 | 25592 | keep | 0 | Aug | 2022 | 0.017431 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CANOVANAS | 2022-08-20 19:43 | 2022-08-20 21:07 | 12 | 1:24 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R22082000079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-08-20 | 1008 | keep | 0 | Aug | 2022 | 0.00068654 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-20 19:44 | 2022-08-20 19:45 | 650 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | A22082000208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 650 | keep | 0 | Aug | 2022 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
YAUCO | 2022-08-20 19:58 | 2022-08-21 14:40 | 4 | 18:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE Y SE REPARO LINEA SECUNDARIA ROTA | M22082000546 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1122 | 2022-08-20 | 4488 | keep | 0 | Aug | 2022 | 0.0030568 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-08-20 19:59 | 2022-08-21 16:30 | 10 | 20:31 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082000212 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1231 | 2022-08-20 | 12310 | keep | 0 | Aug | 2022 | 0.0083843 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-20 20:01 | 2022-08-20 20:02 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
ARECIBO | 2022-08-20 20:04 | 2022-08-20 21:22 | 509 | 1:18 | T | CAUSAS EXTERNAS | SE RETIRO GLOBO DE CUMPLEAÃ‘OS ENREDADO EN EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | A22082000213 | New_Event | Damage From Public | Include | Include | Public | 78 | 2022-08-20 | 39702 | keep | 0 | Aug | 2022 | 0.027041 | 0.00034668 | Sustained | FALSE | FALSE | Not_TMED_Event | 509
BAYAMON | 2022-08-20 20:08 | 2022-08-20 20:09 | 3941 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 3941 | keep | 0 | Aug | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-08-20 20:21 | 2022-08-21 19:58 | 12 | 23:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA - X - 50KVA @ 13KV | B22082000332 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1417 | 2022-08-20 | 17004 | keep | 0 | Aug | 2022 | 0.011581 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-20 20:26 | 2022-08-21 13:35 | 30 | 17:09 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000564 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1029 | 2022-08-20 | 30870 | keep | 0 | Aug | 2022 | 0.021025 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-20 20:30 | 2022-08-20 20:32 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-20 | 6774 | keep | 0 | Aug | 2022 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
CAGUAS | 2022-08-20 20:32 | 2022-08-20 22:44 | 2302 | 2:12 | T | CAUSAS EXTERNAS | SE SECCIONALIZO ALIMENTADOR | C22082000141 | New_Event | Damage From Public | Include | Include | Public | 132 | 2022-08-20 | 303864 | keep | 0 | Aug | 2022 | 0.20696 | 0.0015679 | Sustained | FALSE | FALSE | Not_TMED_Event | 2302
BAYAMON | 2022-08-20 20:33 | 2022-08-22 18:39 | 40 | 46:06 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL DE EXISTENETE A T-9 | S22082000119 | New_Event | UG Cable Fault | Include | Include | Equipment | 2766 | 2022-08-20 | 110640 | keep | 0 | Aug | 2022 | 0.075356 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-20 20:34 | 2022-08-21 16:25 | 300 | 19:51 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | M22082000615 | New_Event | Primary Wire Break | Include | Include | Equipment | 1191 | 2022-08-20 | 357300 | keep | 0 | Aug | 2022 | 0.24336 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-20 20:40 | 2022-08-20 20:41 | 413 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 1620-01 Y 10% DEL 1206-03 CERRADO POR SCADA | S20220820000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 413 | keep | 0 | Aug | 2022 | 0.00028129 | 0.00028129 | Momentary | FALSE | FALSE | Not_TMED_Event | 413
SAN JUAN | 2022-08-20 20:40 | 2022-08-20 20:41 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 1620-01 Y 10% DEL 1206-03 CERRADO POR SCADA | S20220820000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 36 | keep | 0 | Aug | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-08-20 20:40 | 2022-08-20 20:41 | 1073 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 1620-01 Y 10% DEL 1206-03 CERRADO POR SCADA | S20220820000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 1073 | keep | 0 | Aug | 2022 | 0.00073082 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
MAYAGÃœEZ | 2022-08-20 21:05 | 2022-08-21 12:25 | 30 | 15:20 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000596 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 920 | 2022-08-20 | 27600 | keep | 0 | Aug | 2022 | 0.018798 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-20 21:13 | 2022-08-21 06:45 | 3 | 9:32 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22082000602 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 572 | 2022-08-20 | 1716 | keep | 0 | Aug | 2022 | 0.0011688 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-08-20 21:13 | 2022-08-21 12:20 | 200 | 15:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | M22082000601 | New_Event | Primary Wire Break | Include | Include | Equipment | 907 | 2022-08-20 | 181400 | keep | 0 | Aug | 2022 | 0.12355 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-20 21:20 | 2022-08-21 17:32 | 50 | 20:12 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082000606 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1212 | 2022-08-20 | 60600 | keep | 0 | Aug | 2022 | 0.041274 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-20 21:23 | 2022-08-21 02:11 | 25 | 4:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22082000609 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2022-08-20 | 7200 | keep | 0 | Aug | 2022 | 0.0049039 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-20 21:30 | 2022-08-21 01:30 | 80 | 4:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA | C22082000155 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 240 | 2022-08-20 | 19200 | keep | 0 | Aug | 2022 | 0.013077 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-20 21:35 | 2022-08-21 00:25 | 50 | 2:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22082000156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2022-08-20 | 8500 | keep | 0 | Aug | 2022 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-20 21:42 | 2022-08-21 18:25 | 12 | 20:43 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22082000620 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1243 | 2022-08-20 | 14916 | keep | 0 | Aug | 2022 | 0.010159 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-20 22:16 | 2022-08-20 23:15 | 40 | 0:59 | P | PARARRAYOS DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE REMPLAZO PARARRAYO QUEMADO | M22082000636 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 59 | 2022-08-20 | 2360 | keep | 0 | Aug | 2022 | 0.0016074 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-20 22:19 | 2022-08-21 00:21 | 80 | 2:02 | P | MAL TIEMPO/RAYOS | 1 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082000635 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 122 | 2022-08-20 | 9760 | keep | 0 | Aug | 2022 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-20 22:23 | 2022-08-21 17:30 | 60 | 19:07 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082000638 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1147 | 2022-08-20 | 68820 | keep | 0 | Aug | 2022 | 0.046873 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-20 22:24 | 2022-08-20 22:25 | 3433 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE 1204-02 CON 80% DE SU CARGA LLEVA 20% DEL 1303-02 Y 10% DEL 1204-03 | S22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 3433 | keep | 0 | Aug | 2022 | 0.0023382 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
SAN JUAN | 2022-08-20 22:24 | 2022-08-20 22:25 | 138 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE 1204-02 CON 80% DE SU CARGA LLEVA 20% DEL 1303-02 Y 10% DEL 1204-03 | S22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 138 | keep | 0 | Aug | 2022 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2022-08-20 22:24 | 2022-08-20 22:25 | 487 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE 1204-02 CON 80% DE SU CARGA LLEVA 20% DEL 1303-02 Y 10% DEL 1204-03 | S22082000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-20 | 487 | keep | 0 | Aug | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-08-20 22:25 | 2022-08-21 01:58 | 132 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN MACHETE | S22082000127 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2022-08-20 | 28116 | keep | 0 | Aug | 2022 | 0.01915 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
MAYAGÃœEZ | 2022-08-20 22:41 | 2022-08-21 11:15 | 30 | 12:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO PUENTES | M22082000641 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 754 | 2022-08-20 | 22620 | keep | 0 | Aug | 2022 | 0.015406 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-20 22:44 | 2022-08-20 23:00 | 1726 | 0:16 | P | CAUSAS EXTERNAS | SE RETIRO PEDAZO DE TENSOR CRUZANDO ALIMENTADOR | C22082000141 | Partial_restoration | Damage From Public | Include | Include | Public | 16 | 2022-08-20 | 27616 | keep | 0 | Aug | 2022 | 0.018809 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-20 22:56 | 2022-08-21 08:45 | 4 | 9:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22082000644 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 589 | 2022-08-20 | 2356 | keep | 0 | Aug | 2022 | 0.0016047 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-20 22:57 | 2022-08-21 09:02 | 94 | 10:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R22082000089 | New_Event | Cutout Failure | Include | Include | Equipment | 605 | 2022-08-20 | 56870 | keep | 0 | Aug | 2022 | 0.038734 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
BARRANQUITAS | 2022-08-20 22:58 | 2022-08-21 09:25 | 170 | 10:27 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHO | C22082000171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 627 | 2022-08-20 | 106590 | keep | 0 | Aug | 2022 | 0.072598 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
VEGA BAJA | 2022-08-20 23:48 | 2022-08-21 03:09 | 200 | 3:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082000240 | New_Event | Cutout Failure | Include | Include | Equipment | 201 | 2022-08-20 | 40200 | keep | 0 | Aug | 2022 | 0.02738 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-20 23:50 | 2022-08-21 01:48 | 236 | 1:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L PERO SE DEJA CAJA PENDIENTE A CAMBIAR MAS TARDE CELADOR SOLO | B22082000384 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2022-08-20 | 27848 | keep | 0 | Aug | 2022 | 0.018967 | 0.00016074 | Sustained | FALSE | FALSE | Not_TMED_Event | 236
ARECIBO | 2022-08-21 00:17 | 2022-08-21 12:17 | 7 | 12:00 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | A22082100001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 720 | 2022-08-21 | 5040 | keep | 0 | Aug | 2022 | 0.0034327 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-21 00:40 | 2022-08-21 02:10 | 50 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22082100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2022-08-21 | 4500 | keep | 0 | Aug | 2022 | 0.0030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-21 01:31 | 2022-08-21 14:00 | 2 | 12:29 | P | TRANSFORMADOR AVERIADO | SE ENCONTRO TRANSFORMADOR AVERIADO SE TRANSFIRIO LOS CLIENTES A OTRO TRANSFORMADOR CERCANO | M22082100004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 749 | 2022-08-21 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-21 01:48 | 2022-08-21 01:49 | 3941 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | B22082100000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-21 | 3941 | keep | 0 | Aug | 2022 | 0.0026842 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-21 01:49 | 2022-08-21 12:15 | 100 | 10:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO PUENTE Y REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L | B22082000384 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 626 | 2022-08-21 | 62600 | keep | 0 | Aug | 2022 | 0.042637 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-21 02:39 | 2022-08-21 08:48 | 25 | 6:09 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L DESCARGAS ELECTRICAS | P22082100009 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 369 | 2022-08-21 | 9225 | keep | 0 | Aug | 2022 | 0.0062831 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-21 02:54 | 2022-08-21 13:57 | 116 | 11:03 | P | DESGANCHE | 1X65 EN C/L | B22082100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 663 | 2022-08-21 | 76908 | keep | 0 | Aug | 2022 | 0.052382 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
CAGUAS | 2022-08-21 03:15 | 2022-08-21 07:17 | 80 | 4:02 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22082100004 | New_Event | Animals | Include | Include | Wildlife | 242 | 2022-08-21 | 19360 | keep | 0 | Aug | 2022 | 0.013186 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-21 04:59 | 2022-08-21 16:12 | 25 | 11:13 | P | DESGANCHE | 2X30 EN C/L | B22082100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2022-08-21 | 16825 | keep | 0 | Aug | 2022 | 0.011459 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-21 05:25 | 2022-08-21 06:54 | 1382 | 1:29 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES DE CAMPO NO SE ENCONTRO CAUSA SE CERRO POR SCADA 30% EN SERVICIO | B22082100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2022-08-21 | 122998 | keep | 0 | Aug | 2022 | 0.083773 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-21 05:25 | 2022-08-21 06:19 | 663 | 0:54 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES DE CAMPO NO SE ENCONTRO CAUSA SE CERRO POR SCADA | B22082100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 54 | 2022-08-21 | 35802 | keep | 0 | Aug | 2022 | 0.024385 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BARRANQUITAS | 2022-08-21 05:33 | 2022-08-21 11:50 | 120 | 6:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 Y 1 X 30 EN C/LS REMPLAZO AISLADSOR Y CAJA AVERIADA | C22082100006 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 377 | 2022-08-21 | 45240 | keep | 0 | Aug | 2022 | 0.030813 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-08-21 05:38 | 2022-08-21 12:56 | 34 | 7:18 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S22082100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 438 | 2022-08-21 | 14892 | keep | 0 | Aug | 2022 | 0.010143 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2022-08-21 05:49 | 2022-08-21 05:51 | 906 | 0:02 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO Y SE CERRO POR CONTROL | C22082100000 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 2 | 2022-08-21 | 1812 | keep | 0 | Aug | 2022 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
FAJARDO | 2022-08-21 06:13 | 2022-08-21 12:50 | 89 | 6:37 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R22082100004 | New_Event | Animals | Include | Include | Wildlife | 397 | 2022-08-21 | 35333 | keep | 0 | Aug | 2022 | 0.024065 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BARRANQUITAS | 2022-08-21 06:24 | 2022-08-21 06:25 | 3565 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C22082100013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-21 | 3565 | keep | 0 | Aug | 2022 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
BARRANQUITAS | 2022-08-21 06:25 | 2022-08-21 10:43 | 50 | 4:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES LLUVIAS | C22082100014 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 258 | 2022-08-21 | 12900 | keep | 0 | Aug | 2022 | 0.0087861 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-21 06:34 | 2022-08-21 11:20 | 75 | 4:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CAJA PRIMARIA | M22082100012 | New_Event | Cutout Failure | Include | Include | Equipment | 286 | 2022-08-21 | 21450 | keep | 0 | Aug | 2022 | 0.014609 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-08-21 06:46 | 2022-08-22 03:54 | 34 | 21:08 | P | DESGANCHE | SE REALIZO DESGANCHE Y 1 X 100 , 1 X 65 , 1 X 40 EN CORTES DE LINEA | B22082100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1268 | 2022-08-21 | 43112 | keep | 0 | Aug | 2022 | 0.029363 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-08-21 06:54 | 2022-08-21 07:24 | 829 | 0:30 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES DE CAMPO NO SE ENCONTRO CAUSA SE CERRO POR SCADA 60% EN SERVICIO | B22082100010 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 30 | 2022-08-21 | 24870 | keep | 0 | Aug | 2022 | 0.016939 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-21 06:59 | 2022-08-21 19:30 | 15 | 12:31 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082100019 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 751 | 2022-08-21 | 11265 | keep | 0 | Aug | 2022 | 0.0076725 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-08-21 07:02 | 2022-08-21 09:14 | 25 | 2:12 | P | ANIMAL | 1 X 40 EN C/L CRUCE DE FASE PRIMARIA POR AVE | P22082100014 | New_Event | Animals | Include | Include | Wildlife | 132 | 2022-08-21 | 3300 | keep | 0 | Aug | 2022 | 0.0022476 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-21 07:13 | 2022-08-21 10:39 | 2435 | 3:26 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE REEMPLAZO MACHETE QUEMADO CARGA POR EL 1909-08 | S22082100039 | New_Event | Switch Failure | Include | Include | Equipment | 206 | 2022-08-21 | 501610 | keep | 0 | Aug | 2022 | 0.34164 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-08-21 07:13 | 2022-08-21 10:39 | 2956 | 3:26 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE REEMPLAZO MACHETE QUEMADO LLEVA LA CARGA DEL 1907-05 | S22082100039 | New_Event | Switch Failure | Include | Include | Equipment | 206 | 2022-08-21 | 608936 | keep | 0 | Aug | 2022 | 0.41474 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
CAGUAS | 2022-08-21 07:14 | 2022-08-21 07:16 | 906 | 0:02 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO CERRADO X CONTROL | C22082100000 | 1st_after_momentary | Feeder Breaker Failure | Include | Include | Equipment | 2 | 2022-08-21 | 1812 | keep | 0 | Aug | 2022 | 0.0012341 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
VEGA BAJA | 2022-08-21 07:18 | 2022-08-21 10:04 | 127 | 2:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22082100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2022-08-21 | 21082 | keep | 0 | Aug | 2022 | 0.014359 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
VEGA BAJA | 2022-08-21 07:21 | 2022-08-21 09:14 | 50 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIAS | A22082100006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2022-08-21 | 5650 | keep | 0 | Aug | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-21 07:24 | 2022-08-21 07:42 | 553 | 0:18 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES DE CAMPO NO SE ENCONTRO CAUSA SE CERRO POR SCADA EN SERVICIO | B22082100010 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 18 | 2022-08-21 | 9954 | keep | 0 | Aug | 2022 | 0.0067796 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-21 07:31 | 2022-08-21 14:30 | 30 | 6:59 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082100009 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 419 | 2022-08-21 | 12570 | keep | 0 | Aug | 2022 | 0.0085614 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-21 07:33 | 2022-08-21 09:35 | 121 | 2:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | R22082100008 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2022-08-21 | 14762 | keep | 0 | Aug | 2022 | 0.010054 | 8.2413e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 121
BARRANQUITAS | 2022-08-21 07:35 | 2022-08-22 16:57 | 1 | 33:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 25 KVA X 25 KVA | C22082100022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2002 | 2022-08-21 | 2002 | keep | 0 | Aug | 2022 | 0.0013636 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-21 07:38 | 2022-08-22 17:49 | 1 | 34:11 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU HACIA GARAJE | B22082100040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2051 | 2022-08-21 | 2051 | keep | 0 | Aug | 2022 | 0.0013969 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-21 07:40 | 2022-08-21 08:26 | 139 | 0:46 | P | ANIMAL | 1 X 50 Y 1 X 30 EN RISER CRUCE POR AVE | R22082100009 | New_Event | Animals | Include | Include | Wildlife | 46 | 2022-08-21 | 6394 | keep | 0 | Aug | 2022 | 0.0043549 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
VEGA BAJA | 2022-08-21 07:46 | 2022-08-21 10:40 | 35 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22082100043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-21 | 6090 | keep | 0 | Aug | 2022 | 0.0041479 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-08-21 07:47 | 2022-08-21 07:48 | 3597 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 3597 | keep | 0 | Aug | 2022 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
CAGUAS | 2022-08-21 07:52 | 2022-08-21 07:53 | 906 | 0:01 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO CERRADO X CONTROL | C22082100000 | 1st_after_momentary | Feeder Breaker Failure | Include | Include | Equipment | 1 | 2022-08-21 | 906 | keep | 0 | Aug | 2022 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CAGUAS | 2022-08-21 07:56 | 2022-08-21 09:18 | 906 | 1:22 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE SECCIONALIZO EL ALIMENTADOR, CONTINUAN PATRULLANDO | C22082100024 | 1st_after_momentary | Feeder Breaker Failure | Include | Include | Equipment | 82 | 2022-08-21 | 74292 | keep | 0 | Aug | 2022 | 0.0506 | 0.00061707 | Sustained | FALSE | FALSE | Not_TMED_Event | 906
AGUADILLA | 2022-08-21 08:10 | 2022-08-21 09:50 | 15 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082100027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2022-08-21 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-21 08:38 | 2022-08-21 14:00 | 25 | 5:22 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | R22082100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-08-21 | 8050 | keep | 0 | Aug | 2022 | 0.0054828 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-08-21 08:45 | 2022-08-21 11:10 | 30 | 2:25 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22082100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-08-21 | 4350 | keep | 0 | Aug | 2022 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-21 08:47 | 2022-08-21 14:45 | 2402 | 5:58 | T | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZARON (2)BUS SUPPORTS DE LA BARRA DE DISTRIBUCION MEDIANTE G.O.I. BY-220821-03 | S22082100057 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 358 | 2022-08-21 | 859916 | keep | 0 | Aug | 2022 | 0.58568 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-08-21 08:47 | 2022-08-21 14:45 | 766 | 5:58 | P | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZARON (2) BUS SUPPORTS DE LA BARRA DE DISTRIBUCION MEDIANTE G.O.I. BY-220821-03 50% DE SU CARGA TRANSFERIDA AL 1909-07 LLEVA LA CARGA TOTAL DEL 1709-05 | S22082100057 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 358 | 2022-08-21 | 274228 | keep | 0 | Aug | 2022 | 0.18678 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-08-21 08:47 | 2022-08-21 14:45 | 2364 | 5:58 | T | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZARON (2) BUS SUPPORTS DE LA BARRA DE DISTRIBUCION MEDIANTE G.O.I. BY-220821-03 - CARGA TRANSFERIDA AL 1709-03 | S22082100057 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 358 | 2022-08-21 | 846312 | keep | 0 | Aug | 2022 | 0.57642 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
SAN JUAN | 2022-08-21 08:48 | 2022-08-21 12:56 | 65 | 4:08 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA PRINCIPAL 1 X 30 EN CORTE DE LINEA RAMAL Y SE CERRO PUENTE DE LINEA A PARARRAYO | S22082100109 | New_Event | Primary Wire Break | Include | Include | Equipment | 248 | 2022-08-21 | 16120 | keep | 0 | Aug | 2022 | 0.010979 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-08-21 09:02 | 2022-08-21 09:03 | 4154 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R22082100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-21 | 4154 | keep | 0 | Aug | 2022 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
UTUADO | 2022-08-21 09:02 | 2022-08-21 18:10 | 40 | 9:08 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082100016 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 548 | 2022-08-21 | 21920 | keep | 0 | Aug | 2022 | 0.01493 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-21 09:03 | 2022-08-21 10:58 | 435 | 1:55 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO ENREDADERA | R22082100026 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-08-21 | 50025 | keep | 0 | Aug | 2022 | 0.034072 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
VEGA BAJA | 2022-08-21 09:17 | 2022-08-21 11:49 | 40 | 2:32 | P | MAL TIEMPO/RAYOS | 3 X 80 EN CORTE DE LINEA POR RAYOS | A22082100018 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 152 | 2022-08-21 | 6080 | keep | 0 | Aug | 2022 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-21 09:18 | 2022-08-21 10:14 | 906 | 0:56 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA AL 3007-02, BKR 3007-04 CON RUIDOS FUERTES | C22082100024 | Partial_restoration | Feeder Breaker Failure | Include | Include | Equipment | 56 | 2022-08-21 | 50736 | keep | 0 | Aug | 2022 | 0.034556 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-21 09:26 | 2022-08-21 11:49 | 57 | 2:23 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHO | C22082100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-08-21 | 8151 | keep | 0 | Aug | 2022 | 0.0055516 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
PONCE | 2022-08-21 09:26 | 2022-08-21 10:30 | 25 | 1:04 | P | ANIMAL | 1 X 40 EN C/L CRUCE DE FASE PRIMARIA POR AVE | P22082100022 | New_Event | Animals | Include | Include | Wildlife | 64 | 2022-08-21 | 1600 | keep | 0 | Aug | 2022 | 0.0010898 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-21 09:31 | 2022-08-21 13:58 | 7 | 4:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22082100053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 267 | 2022-08-21 | 1869 | keep | 0 | Aug | 2022 | 0.001273 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-08-21 09:32 | 2022-08-21 09:33 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BARRANQUITAS | 2022-08-21 09:49 | 2022-08-21 14:50 | 40 | 5:01 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C22082100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 301 | 2022-08-21 | 12040 | keep | 0 | Aug | 2022 | 0.0082004 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-08-21 10:09 | 2022-08-22 10:00 | 25 | 23:51 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22082100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1431 | 2022-08-21 | 35775 | keep | 0 | Aug | 2022 | 0.024366 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-08-21 10:14 | 2022-08-21 12:56 | 111 | 2:42 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO | C22082100072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-08-21 | 17982 | keep | 0 | Aug | 2022 | 0.012247 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
CAGUAS | 2022-08-21 10:16 | 2022-08-21 10:17 | 2448 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082100062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 2448 | keep | 0 | Aug | 2022 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
SAN JUAN | 2022-08-21 10:21 | 2022-08-22 15:50 | 12 | 29:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 KVA POR 37.5KVA | S22082100159 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1769 | 2022-08-21 | 21228 | keep | 0 | Aug | 2022 | 0.014458 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-08-21 10:29 | 2022-08-21 11:46 | 15 | 1:17 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R22082100034 | New_Event | Animals | Include | Include | Wildlife | 77 | 2022-08-21 | 1155 | keep | 0 | Aug | 2022 | 0.00078667 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-21 10:36 | 2022-08-21 10:37 | 2448 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082100065 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 2448 | keep | 0 | Aug | 2022 | 0.0016673 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
HUMACAO | 2022-08-21 10:44 | 2022-08-21 13:15 | 82 | 2:31 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22082100066 | New_Event | Animals | Include | Include | Wildlife | 151 | 2022-08-21 | 12382 | keep | 0 | Aug | 2022 | 0.0084333 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BARRANQUITAS | 2022-08-21 10:53 | 2022-08-21 13:45 | 90 | 2:52 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN C/L CONDUCTOR EN EL SUELO | C22082100068 | New_Event | Primary Wire Break | Include | Include | Equipment | 172 | 2022-08-21 | 15480 | keep | 0 | Aug | 2022 | 0.010543 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-08-21 10:58 | 2022-08-21 10:59 | 4154 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R22082100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-21 | 4154 | keep | 0 | Aug | 2022 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
HUMACAO | 2022-08-21 11:01 | 2022-08-21 14:55 | 1 | 3:54 | P | DESGANCHE | 1 X 30 EN RISER Y 1 SMU 20 DE 20AMP EN TRANSCLOSURE DESGANCHO | C22082100069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2022-08-21 | 234 | keep | 0 | Aug | 2022 | 0.00015938 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-21 11:03 | 2022-08-21 21:35 | 100 | 10:32 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082100028 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 632 | 2022-08-21 | 63200 | keep | 0 | Aug | 2022 | 0.043045 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-21 11:09 | 2022-08-21 12:18 | 25 | 1:09 | P | DESGANCHE | 1 X 50 C/L DESGANCHE | P22082100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-08-21 | 1725 | keep | 0 | Aug | 2022 | 0.0011749 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-21 11:15 | 2022-08-21 11:58 | 1185 | 0:43 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR REPARAR BAJANTE EN MACHETE | M22082100111 | New_Event | Primary Wire Break | Include | Include | Equipment | 43 | 2022-08-21 | 50955 | keep | 0 | Aug | 2022 | 0.034705 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
MAYAGÃœEZ | 2022-08-21 11:20 | 2022-08-21 11:35 | 200 | 0:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | PERSONAL NO TIENE ACCESO A LA SUBESTACION INDICA QUE NECESITA ABRIR CORTE DE LINEA ANTERIOR PARA REMPLAZAR CAJA PRIMARIA | M22082100103 | New_Event | Cutout Failure | Include | Include | Equipment | 15 | 2022-08-21 | 3000 | keep | 0 | Aug | 2022 | 0.0020433 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-08-21 11:23 | 2022-08-21 14:44 | 16 | 3:21 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR | S22082100184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-08-21 | 3216 | keep | 0 | Aug | 2022 | 0.0021904 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2022-08-21 11:24 | 2022-08-21 18:05 | 30 | 6:41 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L NO CAUSA | C22082100076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 401 | 2022-08-21 | 12030 | keep | 0 | Aug | 2022 | 0.0081936 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-21 11:27 | 2022-08-21 13:11 | 10 | 1:44 | P | EXCAVACIONES | 1 X 10 EN RISER DE AEREO PROVICIONAL EXCAVACION | B22082100094 | New_Event | Excavation | Include | Include | Public | 104 | 2022-08-21 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-21 11:27 | 2022-08-22 03:56 | 80 | 16:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082100093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 989 | 2022-08-21 | 79120 | keep | 0 | Aug | 2022 | 0.053888 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-08-21 11:28 | 2022-08-21 15:35 | 18 | 4:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L REMPLAZO AISLADOR | C22082100077 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 247 | 2022-08-21 | 4446 | keep | 0 | Aug | 2022 | 0.0030282 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2022-08-21 11:31 | 2022-08-21 15:28 | 150 | 3:57 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082100118 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 237 | 2022-08-21 | 35550 | keep | 0 | Aug | 2022 | 0.024213 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-08-21 11:45 | 2022-08-21 14:05 | 30 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN C/L LLUVIA | R22082100045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2022-08-21 | 4200 | keep | 0 | Aug | 2022 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-21 11:58 | 2022-08-21 13:55 | 400 | 1:57 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO | M22082000641 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 117 | 2022-08-21 | 46800 | keep | 0 | Aug | 2022 | 0.031875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-21 12:01 | 2022-08-22 20:15 | 40 | 32:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A22082100029 | New_Event | Primary Wire Break | Include | Include | Equipment | 1934 | 2022-08-21 | 77360 | keep | 0 | Aug | 2022 | 0.05269 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-21 12:06 | 2022-08-21 13:09 | 3041 | 1:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA SECCIONALIZAR LINEA PRIMARIA ROTA | M22082100130 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2022-08-21 | 191583 | keep | 0 | Aug | 2022 | 0.13049 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2022-08-21 12:09 | 2022-08-21 18:27 | 50 | 6:18 | P | DESGANCHE | 1X65 EN C/L SE REFIRIO PARA DESGANCHE | B22082100108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 378 | 2022-08-21 | 18900 | keep | 0 | Aug | 2022 | 0.012873 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-21 12:24 | 2022-08-21 13:50 | 18 | 1:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA CONECTAR SECUNDARIA PROVISIONAL | R22081900062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 86 | 2022-08-21 | 1548 | keep | 0 | Aug | 2022 | 0.0010543 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2022-08-21 12:27 | 2022-08-21 19:10 | 5 | 6:43 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082100032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 403 | 2022-08-21 | 2015 | keep | 0 | Aug | 2022 | 0.0013724 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-08-21 12:36 | 2022-08-21 17:15 | 70 | 4:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22082100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-08-21 | 19530 | keep | 0 | Aug | 2022 | 0.013302 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2022-08-21 12:39 | 2022-08-21 13:05 | 1295 | 0:26 | T | MAL TIEMPO/RAYOS | 1 X 80 EN C/L DESCARGAS ELECTRICAS | P22082100036 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 26 | 2022-08-21 | 33670 | keep | 0 | Aug | 2022 | 0.022932 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2022-08-21 12:42 | 2022-08-21 14:48 | 50 | 2:06 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22082100207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-21 | 6300 | keep | 0 | Aug | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-21 12:56 | 2022-08-21 21:15 | 1106 | 8:19 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 PUENTE ABIERTO REPARADO. 1529-15 LLEVA 60% DEL 1346-02 | S22082100327 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 499 | 2022-08-21 | 551894 | keep | 0 | Aug | 2022 | 0.37589 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-08-21 12:56 | 2022-08-21 21:15 | 74 | 8:19 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 PUENTE ABIERTO REPARADO. 1529-11 LLEVA 1521-02 | S22082100327 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 499 | 2022-08-21 | 36926 | keep | 0 | Aug | 2022 | 0.02515 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-08-21 12:56 | 2022-08-21 21:15 | 1370 | 8:19 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 PUENTE ABIERTO REPARADO. 2529-11 LLEVA 1521-02 | S22082100327 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 499 | 2022-08-21 | 683630 | keep | 0 | Aug | 2022 | 0.46562 | 0.0009331 | Sustained | FALSE | FALSE | Not_TMED_Event | 1370
SAN JUAN | 2022-08-21 12:56 | 2022-08-21 21:15 | 1984 | 8:19 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 PUENTE ABIERTO REPARADO. 1529-12 LLEVA 75% DEL 1911-07 | S22082100327 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 499 | 2022-08-21 | 990016 | keep | 0 | Aug | 2022 | 0.6743 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
SAN JUAN | 2022-08-21 12:56 | 2022-08-21 21:15 | 199 | 8:19 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 PUENTE ABIERTO REPARADO. 1529-13 LLEVA 25% DEL 1911-07 | S22082100327 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 499 | 2022-08-21 | 99301 | keep | 0 | Aug | 2022 | 0.067633 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2022-08-21 12:56 | 2022-08-21 21:15 | 1802 | 8:19 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 PUENTE ABIERTO REPARADO. 1529-15 LLEVA 60% DEL 1346-02 | S22082100327 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 499 | 2022-08-21 | 899198 | keep | 0 | Aug | 2022 | 0.61244 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2022-08-21 12:56 | 2022-08-21 21:15 | 433 | 8:19 | T | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 38300 PUENTE ABIERTO REPARADO. 1529-12 LLEVA 75% DEL 1911-07 | S22082100327 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 499 | 2022-08-21 | 216067 | keep | 0 | Aug | 2022 | 0.14716 | 0.00029491 | Sustained | FALSE | FALSE | Not_TMED_Event | 433
SAN JUAN | 2022-08-21 13:07 | 2022-08-21 14:26 | 34 | 1:19 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S22082100022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-08-21 | 2686 | keep | 0 | Aug | 2022 | 0.0018294 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2022-08-21 13:08 | 2022-08-21 14:09 | 111 | 1:01 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHO | C22082100072 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-08-21 | 6771 | keep | 0 | Aug | 2022 | 0.0046117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-21 13:09 | 2022-08-21 15:34 | 1520 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | M22082100162 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 145 | 2022-08-21 | 220400 | keep | 0 | Aug | 2022 | 0.15011 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-21 13:24 | 2022-08-22 08:43 | 1 | 19:19 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA | R22082100064 | New_Event | Primary Wire Break | Include | Include | Equipment | 1159 | 2022-08-21 | 1159 | keep | 0 | Aug | 2022 | 0.00078939 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-21 13:30 | 2022-08-21 17:01 | 10 | 3:31 | P | DESGANCHE | DESGANCHE MASIVO Y SE LEVANTO NEUTRAL PRIMARIO DEL SUELO 1 X 15 EN XMR | P22082100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-08-21 | 2110 | keep | 0 | Aug | 2022 | 0.0014371 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-21 13:33 | 2022-08-21 18:20 | 100 | 4:47 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082100052 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 287 | 2022-08-21 | 28700 | keep | 0 | Aug | 2022 | 0.019547 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-08-21 13:34 | 2022-08-21 15:15 | 30 | 1:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL AEREO | R22082100068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-08-21 | 3030 | keep | 0 | Aug | 2022 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-21 13:35 | 2022-08-22 10:07 | 15 | 20:32 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22082100318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1232 | 2022-08-21 | 18480 | keep | 0 | Aug | 2022 | 0.012587 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-21 13:35 | 2022-08-21 23:16 | 500 | 9:41 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZO AMARRE DE 7805-13 CON 7903-06 YA QUE SE HA PATRULLADO Y NO SE HA ENCONTRADO SITUACION. SE ESTARA PATRULLANDO DE DIA | M22082100183 | New_Event | Primary Wire Break | Include | Include | Equipment | 581 | 2022-08-21 | 290500 | keep | 0 | Aug | 2022 | 0.19786 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
GUAYAMA | 2022-08-21 13:36 | 2022-08-21 15:45 | 5 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO DE XMR | P22082100063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2022-08-21 | 645 | keep | 0 | Aug | 2022 | 0.00043931 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-21 13:38 | 2022-08-22 10:24 | 6 | 20:46 | P | DESGANCHE | 1 X 10 EN XMR Y DESGANCHE | B22082100153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1246 | 2022-08-21 | 7476 | keep | 0 | Aug | 2022 | 0.0050919 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-08-21 13:39 | 2022-08-22 12:36 | 12 | 22:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082100055 | New_Event | Cutout Failure | Include | Include | Equipment | 1377 | 2022-08-21 | 16524 | keep | 0 | Aug | 2022 | 0.011254 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-21 13:49 | 2022-08-21 18:11 | 5 | 4:22 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA / DESCARGAS ELECTRICAS | M22082100186 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 262 | 2022-08-21 | 1310 | keep | 0 | Aug | 2022 | 0.00089224 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-08-21 13:54 | 2022-08-21 16:27 | 30 | 2:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22082100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-08-21 | 4590 | keep | 0 | Aug | 2022 | 0.0031262 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-21 13:55 | 2022-08-21 14:15 | 1185 | 0:20 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO Y SE CERRO EL INTERRUPTOR | M22082100013 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 20 | 2022-08-21 | 23700 | keep | 0 | Aug | 2022 | 0.016142 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-21 13:58 | 2022-08-21 15:37 | 125 | 1:39 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082100062 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 99 | 2022-08-21 | 12375 | keep | 0 | Aug | 2022 | 0.0084286 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
MAYAGÃœEZ | 2022-08-21 14:12 | 2022-08-21 18:15 | 9 | 4:03 | P | MAL TIEMPO/RAYOS | 1 X 10 Y 2 X 5 EN DISTINTOS TRANSFORMADORES / DESCARGAS ELECTRICAS | M22082100203 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 243 | 2022-08-21 | 2187 | keep | 0 | Aug | 2022 | 0.0014896 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-08-21 14:19 | 2022-08-21 15:55 | 12 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22082100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-08-21 | 1152 | keep | 0 | Aug | 2022 | 0.00078462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-21 14:20 | 2022-08-21 15:21 | 1681 | 1:01 | T | NO SE REPORTO CAUSA | DISPARO Y PROBO MALO 1303-04 TRANSFERIDO AL 1303-05. EL 1303-04 LLEVA 1303-01 Y 1346-06. SE PATRULLO NO SE VIO CONDICION Y SE CERRO POR SCADA | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-08-21 | 102541 | keep | 0 | Aug | 2022 | 0.06984 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-08-21 14:20 | 2022-08-21 15:21 | 1598 | 1:01 | T | NO SE REPORTO CAUSA | DISPARO Y PROBO MALO 1303-04 TRANSFERIDO AL 1303-05. EL 1303-04 LLEVA 1303-01 Y 1346-06. SE PATRULLO NO SE VIO CONDICION Y SE CERRO POR SCADA. | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-08-21 | 97478 | keep | 0 | Aug | 2022 | 0.066392 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
VEGA BAJA | 2022-08-21 14:23 | 2022-08-21 14:24 | 2132 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A22082100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-21 | 2132 | keep | 0 | Aug | 2022 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-08-21 14:23 | 2022-08-21 14:24 | 2366 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A22082100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-21 | 2366 | keep | 0 | Aug | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-08-21 14:23 | 2022-08-21 14:24 | 1976 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A22082100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-21 | 1976 | keep | 0 | Aug | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-08-21 14:23 | 2022-08-21 14:24 | 3688 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | A22082100000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-21 | 3688 | keep | 0 | Aug | 2022 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
CANOVANAS | 2022-08-21 14:24 | 2022-08-21 21:51 | 30 | 7:27 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L SE LEVANTO LINEA PRIMARIA | R22082100086 | New_Event | Primary Wire Break | Include | Include | Equipment | 447 | 2022-08-21 | 13410 | keep | 0 | Aug | 2022 | 0.0091335 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-21 14:29 | 2022-08-21 17:15 | 150 | 2:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22082100217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-08-21 | 24900 | keep | 0 | Aug | 2022 | 0.016959 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-08-21 14:38 | 2022-08-21 16:08 | 40 | 1:30 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22082100195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-08-21 | 3600 | keep | 0 | Aug | 2022 | 0.0024519 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-21 14:40 | 2022-08-21 18:02 | 354 | 3:22 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE CERRO POR SCADA 1335-01 QUE LLEVA 1301-01 SJ-220821-02 | S22082100378 | New_Event | Primary Wire Break | Include | Include | Equipment | 202 | 2022-08-21 | 71508 | keep | 0 | Aug | 2022 | 0.048704 | 0.00024111 | Sustained | FALSE | FALSE | Not_TMED_Event | 354
SAN JUAN | 2022-08-21 14:40 | 2022-08-21 18:02 | 402 | 3:22 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE CERRO POR SCADA LLEVA 1301-01 SJ-220821-02 | S22082100378 | New_Event | Primary Wire Break | Include | Include | Equipment | 202 | 2022-08-21 | 81204 | keep | 0 | Aug | 2022 | 0.055308 | 0.0002738 | Sustained | FALSE | FALSE | Not_TMED_Event | 402
SAN JUAN | 2022-08-21 14:44 | 2022-08-21 14:45 | 829 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02, LLEVA 40% DEL 1204-04 Y LLEVA 60% DEL 1204-03 | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 829 | keep | 0 | Aug | 2022 | 0.00056463 | 0.00056463 | Momentary | FALSE | FALSE | Not_TMED_Event | 829
SAN JUAN | 2022-08-21 14:44 | 2022-08-21 14:45 | 1978 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02, LLEVA 40% DEL 1204-04 Y LLEVA 60% DEL 1204-03 | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 1978 | keep | 0 | Aug | 2022 | 0.0013472 | 0.0013472 | Momentary | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2022-08-21 14:44 | 2022-08-21 14:45 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02, LLEVA 40% DEL 1204-04 Y LLEVA 60% DEL 1204-03 | S22082100000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 1799 | keep | 0 | Aug | 2022 | 0.0012253 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-21 14:44 | 2022-08-21 14:45 | 487 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1206-04 QUE LLEVA 20% DEL 1303-02, LLEVA 40% DEL 1204-04 Y LLEVA 60% DEL 1204-03 | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 487 | keep | 0 | Aug | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
BARRANQUITAS | 2022-08-21 14:44 | 2022-08-21 18:36 | 30 | 3:52 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22082100169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2022-08-21 | 6960 | keep | 0 | Aug | 2022 | 0.0047404 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-21 14:45 | 2022-08-21 15:17 | 16 | 0:32 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR | S22082100184 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 32 | 2022-08-21 | 512 | keep | 0 | Aug | 2022 | 0.00034872 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-08-21 14:48 | 2022-08-21 14:49 | 4291 | 0:01 | T | DESGANCHE | RECIERRE 1204-02 LLEVA 20% DEL 1303-02 Y 10% DEL 1204-03 | S22082100000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-21 | 4291 | keep | 0 | Aug | 2022 | 0.0029226 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-21 14:48 | 2022-08-21 14:49 | 138 | 0:01 | P | DESGANCHE | RECIERRE 1204-02 LLEVA 20% DEL 1303-02 Y 10% DEL 1204-03 | S22082100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-21 | 138 | keep | 0 | Aug | 2022 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2022-08-21 14:48 | 2022-08-21 14:49 | 487 | 0:01 | P | DESGANCHE | RECIERRE 1204-02 LLEVA 20% DEL 1303-02 Y 10% DEL 1204-03 | S22082100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-21 | 487 | keep | 0 | Aug | 2022 | 0.00033169 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-08-21 14:49 | 2022-08-21 17:18 | 50 | 2:29 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22082100207 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-08-21 | 7450 | keep | 0 | Aug | 2022 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-21 14:49 | 2022-08-21 14:50 | 1827 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | M22082100231 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-21 | 1827 | keep | 0 | Aug | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2022-08-21 14:50 | 2022-08-21 19:01 | 200 | 4:11 | P | ANIMAL | 3 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA Y SE REMPLAZO DOS AISLADORES | M22082100232 | 1st_after_momentary | Animals | Include | Include | Wildlife | 251 | 2022-08-21 | 50200 | keep | 0 | Aug | 2022 | 0.034191 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-21 15:04 | 2022-08-22 13:50 | 6 | 22:46 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082100238 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1366 | 2022-08-21 | 8196 | keep | 0 | Aug | 2022 | 0.0055823 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2022-08-21 15:05 | 2022-08-21 15:06 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22082100086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 3431 | keep | 0 | Aug | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
MAYAGÃœEZ | 2022-08-21 15:15 | 2022-08-21 16:11 | 3 | 0:56 | P | MAL TIEMPO/RAYOS | 1 X 30 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22082100225 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 56 | 2022-08-21 | 168 | keep | 0 | Aug | 2022 | 0.00011442 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-08-21 15:19 | 2022-08-21 15:20 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22082100091 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 3431 | keep | 0 | Aug | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
YAUCO | 2022-08-21 15:20 | 2022-08-21 18:50 | 40 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | M22082100244 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2022-08-21 | 8400 | keep | 0 | Aug | 2022 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-21 15:24 | 2022-08-22 12:14 | 10 | 20:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMLAZO CAJA PRIMARIA 1 X 15 EN XMR | B22082100175 | New_Event | Cutout Failure | Include | Include | Equipment | 1250 | 2022-08-21 | 12500 | keep | 0 | Aug | 2022 | 0.0085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-21 15:29 | 2022-08-21 15:30 | 225 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 QUE LLEVA 1303-04 CERRADO POR SCADA | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 225 | keep | 0 | Aug | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-21 15:29 | 2022-08-21 15:30 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 QUE LLEVA 1303-04 CERRADO POR SCADA | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 870 | keep | 0 | Aug | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-08-21 15:43 | 2022-08-21 17:58 | 90 | 2:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA @ CAJA EN C/L | B22082100181 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2022-08-21 | 12150 | keep | 0 | Aug | 2022 | 0.0082753 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-08-21 15:53 | 2022-08-22 10:45 | 4 | 18:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C22082100210 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1132 | 2022-08-21 | 4528 | keep | 0 | Aug | 2022 | 0.003084 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-08-21 16:02 | 2022-08-21 18:40 | 50 | 2:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22082100103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-08-21 | 7900 | keep | 0 | Aug | 2022 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-21 16:06 | 2022-08-21 19:00 | 90 | 2:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 Y 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22082100105 | New_Event | Primary Wire Break | Include | Include | Equipment | 174 | 2022-08-21 | 15660 | keep | 0 | Aug | 2022 | 0.010666 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BARRANQUITAS | 2022-08-21 16:08 | 2022-08-22 11:28 | 50 | 19:20 | P | MAL TIEMPO/RAYOS | 3 X 40 EN C/L 1 X 10 Y 1 X 15 EN XMRS RAYOS | C22082100211 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1160 | 2022-08-21 | 58000 | keep | 0 | Aug | 2022 | 0.039504 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-21 16:13 | 2022-08-22 22:15 | 19 | 30:02 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S22082100456 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1802 | 2022-08-21 | 34238 | keep | 0 | Aug | 2022 | 0.023319 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-08-21 16:19 | 2022-08-21 20:26 | 60 | 4:07 | P | ARBOL SOBRE LINEA | 1X40 EN C/L SE RETIRO ARBOL (COMPLETO) DE PRIMARIA | S22082100199 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 247 | 2022-08-21 | 14820 | keep | 0 | Aug | 2022 | 0.010094 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-21 16:25 | 2022-08-21 19:10 | 10 | 2:45 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082100112 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 165 | 2022-08-21 | 1650 | keep | 0 | Aug | 2022 | 0.0011238 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-21 16:35 | 2022-08-21 16:36 | 4882 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | M22082100272 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-21 | 4882 | keep | 0 | Aug | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-08-21 16:36 | 2022-08-21 23:18 | 150 | 6:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M22082100275 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 402 | 2022-08-21 | 60300 | keep | 0 | Aug | 2022 | 0.04107 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-08-21 16:40 | 2022-08-22 13:45 | 1 | 21:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS EN MONTURA | P22082100103 | New_Event | Cutout Failure | Include | Include | Equipment | 1265 | 2022-08-21 | 1265 | keep | 0 | Aug | 2022 | 0.00086159 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-21 16:44 | 2022-08-21 16:45 | 225 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1303-05 QUE LLEVA 1303-04 SE CERRO POR SCADA | S22082100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 225 | keep | 0 | Aug | 2022 | 0.00015325 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-21 16:44 | 2022-08-21 16:45 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1303-05 QUE LLEVA 1303-04 SE CERRO POR SCADA | S22082100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 870 | keep | 0 | Aug | 2022 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2022-08-21 16:52 | 2022-08-21 19:28 | 170 | 2:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22082100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-08-21 | 26520 | keep | 0 | Aug | 2022 | 0.018063 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
SAN JUAN | 2022-08-21 17:01 | 2022-08-21 21:12 | 250 | 4:11 | P | DESCONECTIVO DEFECTUOSO | SJ-220821-03 REMPLAZO DE MACHETE QUEMADO Y SE CERRO BKR DE PORTATIL #8 QUE LLEVA 20% DEL 1348-06 | S22082100491 | New_Event | Switch Failure | Include | Include | Equipment | 251 | 2022-08-21 | 62750 | keep | 0 | Aug | 2022 | 0.042739 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-08-21 17:01 | 2022-08-21 21:12 | 1290 | 4:11 | T | DESCONECTIVO DEFECTUOSO | SJ-220821-03 REMPLAZO DE MACHETE QUEMADO Y SE CERRO BKR DE PORTATIL #8 | S22082100491 | New_Event | Switch Failure | Include | Include | Equipment | 251 | 2022-08-21 | 323790 | keep | 0 | Aug | 2022 | 0.22053 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2022-08-21 17:05 | 2022-08-22 15:10 | 60 | 22:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22082100498 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1325 | 2022-08-21 | 79500 | keep | 0 | Aug | 2022 | 0.054147 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-21 17:08 | 2022-08-21 19:49 | 70 | 2:41 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082100131 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 161 | 2022-08-21 | 11270 | keep | 0 | Aug | 2022 | 0.0076759 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-08-21 17:12 | 2022-08-21 19:01 | 2 | 1:49 | P | MAL TIEMPO/RAYOS | 1X10 EN XMR POR RAYO AL CAER | B22082100213 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 109 | 2022-08-21 | 218 | keep | 0 | Aug | 2022 | 0.00014848 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-08-21 17:17 | 2022-08-21 17:18 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082100216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 181 | keep | 0 | Aug | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
AGUADILLA | 2022-08-21 17:19 | 2022-08-21 20:50 | 8 | 3:31 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 37.5KVA | M22082100292 | New_Event | Service Transformer Failure | Include | Include | Equipment | 211 | 2022-08-21 | 1688 | keep | 0 | Aug | 2022 | 0.0011497 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-08-21 17:22 | 2022-08-21 17:23 | 2126 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO X CONTROL | C22082100218 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-21 | 2126 | keep | 0 | Aug | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-08-21 17:23 | 2022-08-21 21:56 | 145 | 4:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE EN ENTRADA DE MACHETE | C22082100219 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 273 | 2022-08-21 | 39585 | keep | 0 | Aug | 2022 | 0.026961 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
BAYAMON | 2022-08-21 17:30 | 2022-08-21 21:19 | 1 | 3:49 | P | NO SE REPORTO CAUSA | 2X100 EN SU-11 | B22082100215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-08-21 | 229 | keep | 0 | Aug | 2022 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-21 17:36 | 2022-08-22 09:50 | 80 | 16:14 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082100294 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 974 | 2022-08-21 | 77920 | keep | 0 | Aug | 2022 | 0.053071 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-21 17:50 | 2022-08-21 20:36 | 25 | 2:46 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082100149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 166 | 2022-08-21 | 4150 | keep | 0 | Aug | 2022 | 0.0028265 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-21 18:02 | 2022-08-21 19:12 | 1061 | 1:10 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE CERRO POR SCADA 1335-01 QUE LLEVA 1301-01 SJ-220821-02 | S22082100378 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 70 | 2022-08-21 | 74270 | keep | 0 | Aug | 2022 | 0.050585 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-21 18:02 | 2022-08-21 19:12 | 1208 | 1:10 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE CERRO POR SCADA 1335-01 QUE LLEVA 1301-01 SJ-220821-02 | S22082100378 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 70 | 2022-08-21 | 84560 | keep | 0 | Aug | 2022 | 0.057593 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-21 18:18 | 2022-08-21 18:19 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 824 | keep | 0 | Aug | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
PONCE | 2022-08-21 18:23 | 2022-08-22 06:56 | 20 | 12:33 | P | ANIMAL | 1 X 20 EN XMR CRUCE DE FASE POR AVE | P22082100119 | New_Event | Animals | Include | Include | Wildlife | 753 | 2022-08-21 | 15060 | keep | 0 | Aug | 2022 | 0.010257 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-21 18:23 | 2022-08-22 08:08 | 12 | 13:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22082100249 | New_Event | Secondary Wire Break | Include | Include | Equipment | 825 | 2022-08-21 | 9900 | keep | 0 | Aug | 2022 | 0.0067428 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-08-21 18:26 | 2022-08-21 19:29 | 1883 | 1:03 | T | DESGANCHE | DISPARO DEL INTERRUPTOR SE RETIRO RAMAS SOBRE LAS LINEAS | A22082100162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-08-21 | 118629 | keep | 0 | Aug | 2022 | 0.080798 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
AGUADILLA | 2022-08-21 19:01 | 2022-08-21 19:02 | 1827 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | M22082100323 | Additional_clients | Animals | Include | Include | Wildlife | 1 | 2022-08-21 | 1827 | keep | 0 | Aug | 2022 | 0.0012444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-21 19:02 | 2022-08-21 19:45 | 200 | 0:43 | P | ANIMAL | 3 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA Y SE REMPLAZO DOS AISLADORES | M22082100232 | 1st_after_momentary | Animals | Include | Include | Wildlife | 43 | 2022-08-21 | 8600 | keep | 0 | Aug | 2022 | 0.0058574 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-08-21 19:12 | 2022-08-21 21:38 | 354 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO 1335-01 PARA REMPLAZO DE MACHETE QUE LLEVA 1301-01 SJ-220821-02 | S22082100378 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 146 | 2022-08-21 | 51684 | keep | 0 | Aug | 2022 | 0.035202 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-21 19:12 | 2022-08-21 21:38 | 402 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR 1335-01 PARA REMPLAZO DE MACHETE Y SE CERRO POR SCADA LLEVA 1301-01 SJ-220821-02 | S22082100378 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 146 | 2022-08-21 | 58692 | keep | 0 | Aug | 2022 | 0.039975 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-21 19:12 | 2022-08-21 22:32 | 10 | 3:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22082100325 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 200 | 2022-08-21 | 2000 | keep | 0 | Aug | 2022 | 0.0013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-21 19:33 | 2022-08-22 01:40 | 1681 | 6:07 | T | DESGANCHE | SE SECCIONALIZO HACIA CAMINO LOS GUANOS SE CERRO BKR 1303-04 QUE ESTA TRANSFERIDO AL 1303-05 PERO LLEVA 1303-01 QUE ENTRO EN 98% Y SE CERRO AMARRE QUE ENERGIZA EL 1346-06 Y ENTRO EL 100% DE ESTE | S22082100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2022-08-21 | 616927 | keep | 0 | Aug | 2022 | 0.42019 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-08-21 19:33 | 2022-08-22 01:40 | 1598 | 6:07 | T | DESGANCHE | SE SECCIONALIZO HACIA CAMINO LOS GUANOS SE CERRO BKR 1303-04 QUE ESTA TRANSFERIDO AL 1303-05 PERO LLEVA 1303-01 QUE ENTRO EN 98% Y SE CERRO AMARRE QUE ENERGIZA EL 1346-06 Y ENTRO EL 100% DE ESTE | S22082100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2022-08-21 | 586466 | keep | 0 | Aug | 2022 | 0.39944 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
HUMACAO | 2022-08-21 19:38 | 2022-08-21 19:39 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082100219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2022-08-21 19:42 | 2022-08-22 12:11 | 30 | 16:29 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B22082100229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 989 | 2022-08-21 | 29670 | keep | 0 | Aug | 2022 | 0.020208 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-08-21 19:43 | 2022-08-21 22:13 | 2722 | 2:30 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR | R22082100101 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 150 | 2022-08-21 | 408300 | keep | 0 | Aug | 2022 | 0.27809 | 0.0018539 | Sustained | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2022-08-21 19:56 | 2022-08-22 10:03 | 300 | 14:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIA | B22082100233 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 847 | 2022-08-21 | 254100 | keep | 0 | Aug | 2022 | 0.17307 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-21 20:05 | 2022-08-21 21:11 | 150 | 1:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN PROVISIONAL SE REMPLAZO CAJA Y SE REPARO PUENTE ABIERTO Y 1 X 80 SUM-20 | S22082100733 | New_Event | Cutout Failure | Include | Include | Equipment | 66 | 2022-08-21 | 9900 | keep | 0 | Aug | 2022 | 0.0067428 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-08-21 20:14 | 2022-08-21 21:50 | 2106 | 1:36 | T | PROBLEMA DEL CLIENTE | SE SECCIONALIZO ALIMENTADOR 30% EN SERVICIO | R22082100000 | New_Event | Customer-Related Interruption | Include | Include | Public | 96 | 2022-08-21 | 202176 | keep | 0 | Aug | 2022 | 0.1377 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
YAUCO | 2022-08-21 20:17 | 2022-08-22 07:35 | 8 | 11:18 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | M22082100348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 678 | 2022-08-21 | 5424 | keep | 0 | Aug | 2022 | 0.0036943 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-21 20:25 | 2022-08-22 16:00 | 12 | 19:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO SECUNDARIA DE RISER A PM | R22082100113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1175 | 2022-08-21 | 14100 | keep | 0 | Aug | 2022 | 0.0096034 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-21 20:36 | 2022-08-21 20:37 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
AGUADILLA | 2022-08-21 20:42 | 2022-08-21 23:41 | 12 | 2:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 75 KVA X 75 KVA | M22082100353 | New_Event | Service Transformer Failure | Include | Include | Equipment | 179 | 2022-08-21 | 2148 | keep | 0 | Aug | 2022 | 0.001463 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-21 20:43 | 2022-08-21 21:45 | 200 | 1:02 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082100354 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 62 | 2022-08-21 | 12400 | keep | 0 | Aug | 2022 | 0.0084456 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-08-21 20:53 | 2022-08-21 20:58 | 137 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22082100797 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-21 | 685 | keep | 0 | Aug | 2022 | 0.00046655 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-08-21 20:53 | 2022-08-21 20:58 | 760 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22082100797 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-21 | 3800 | keep | 0 | Aug | 2022 | 0.0025882 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2022-08-21 21:11 | 2022-08-22 09:24 | 150 | 12:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN PROVISIONAL SE REMPLAZO CAJA Y SE REPARO PUENTE ABIERTO Y 1 X 80 SUM-20 | S22082100733 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 733 | 2022-08-21 | 109950 | keep | 0 | Aug | 2022 | 0.074886 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-21 21:12 | 2022-08-22 10:35 | 10 | 13:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082100185 | New_Event | Cutout Failure | Include | Include | Equipment | 803 | 2022-08-21 | 8030 | keep | 0 | Aug | 2022 | 0.0054692 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-21 21:15 | 2022-08-22 13:57 | 65 | 16:42 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA PRINCIPAL 1 X 30 EN CORTE DE LINEA RAMAL Y SE CERRO PUENTE DE LINEA A PARARRAYO | S22082100109 | New_Event | Primary Wire Break | Include | Include | Equipment | 1002 | 2022-08-21 | 65130 | keep | 0 | Aug | 2022 | 0.04436 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
FAJARDO | 2022-08-21 21:19 | 2022-08-22 11:15 | 200 | 13:56 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | R22082100140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 836 | 2022-08-21 | 167200 | keep | 0 | Aug | 2022 | 0.11388 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-08-21 21:22 | 2022-08-22 09:45 | 1 | 12:23 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | R22082100141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 743 | 2022-08-21 | 743 | keep | 0 | Aug | 2022 | 0.00050605 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-21 21:25 | 2022-08-21 22:52 | 250 | 1:27 | P | DESCONECTIVO DEFECTUOSO | DISPARO PORTATIL SJ-220821-03 REMPLAZO DE MACHETE QUEMADO Y SE CERRO BKR DE PORTATIL #8 QUE LLEVA 20% DEL 1348-06 | S22082100491 | Partial_restoration | Switch Failure | Include | Include | Equipment | 87 | 2022-08-21 | 21750 | keep | 0 | Aug | 2022 | 0.014814 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-21 21:25 | 2022-08-21 22:52 | 1290 | 1:27 | T | DESCONECTIVO DEFECTUOSO | DISPARO PORTATIL #8 SJ-220821-03 REMPLAZO DE MACHETE QUEMADO Y SE CERRO BKR DE PORTATIL #8 | S22082100491 | Partial_restoration | Switch Failure | Include | Include | Equipment | 87 | 2022-08-21 | 112230 | keep | 0 | Aug | 2022 | 0.076439 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-21 21:38 | 2022-08-21 23:13 | 1061 | 1:35 | T | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO MACHETE Y SE CERRO POR SCADA 1335-01 QUE LLEVA 1301-01 SJ-220821-02 | S22082100378 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 95 | 2022-08-21 | 100795 | keep | 0 | Aug | 2022 | 0.068651 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-21 21:38 | 2022-08-21 23:13 | 1208 | 1:35 | T | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO MACHETE Y SE CERRO POR SCADA 1335-01 QUE LLEVA 1301-01 SJ-220821-02 | S22082100378 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 95 | 2022-08-21 | 114760 | keep | 0 | Aug | 2022 | 0.078163 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-21 21:44 | 2022-08-22 11:25 | 12 | 13:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50 KVA | A22082100186 | New_Event | Service Transformer Failure | Include | Include | Equipment | 821 | 2022-08-21 | 9852 | keep | 0 | Aug | 2022 | 0.0067102 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-21 21:50 | 2022-08-21 22:54 | 1474 | 1:04 | P | PROBLEMA DEL CLIENTE | ALIMENTADOR SECCIONALIZADO | R22082100000 | Partial_restoration | Customer-Related Interruption | Include | Include | Public | 64 | 2022-08-21 | 94336 | keep | 0 | Aug | 2022 | 0.064252 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-21 21:50 | 2022-08-21 22:05 | 1253 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 LLEVA CARGA DE 6010-02 | M22082100375 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 18795 | keep | 0 | Aug | 2022 | 0.012801 | 0.00085341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-08-21 21:50 | 2022-08-21 22:05 | 1266 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 CARGA POR 6010-01 | M22082100375 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 18990 | keep | 0 | Aug | 2022 | 0.012934 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-08-21 21:50 | 2022-08-21 22:05 | 411 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100375 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 6165 | keep | 0 | Aug | 2022 | 0.004199 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2022-08-21 21:50 | 2022-08-21 22:05 | 1617 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100379 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 24255 | keep | 0 | Aug | 2022 | 0.01652 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-08-21 21:50 | 2022-08-21 22:05 | 1017 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100379 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 15255 | keep | 0 | Aug | 2022 | 0.01039 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-08-21 21:50 | 2022-08-21 22:05 | 828 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100379 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 12420 | keep | 0 | Aug | 2022 | 0.0084592 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-08-21 21:50 | 2022-08-21 22:05 | 863 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100376 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 12945 | keep | 0 | Aug | 2022 | 0.0088168 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-08-21 21:50 | 2022-08-21 22:05 | 309 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100376 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 4635 | keep | 0 | Aug | 2022 | 0.0031569 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-08-21 21:50 | 2022-08-21 22:05 | 176 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100376 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 2640 | keep | 0 | Aug | 2022 | 0.0017981 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-08-21 21:50 | 2022-08-21 22:05 | 974 | 0:15 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22082100377 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 15 | 2022-08-21 | 14610 | keep | 0 | Aug | 2022 | 0.0099508 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
BAYAMON | 2022-08-21 21:51 | 2022-08-22 03:10 | 40 | 5:19 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22082100261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2022-08-21 | 12760 | keep | 0 | Aug | 2022 | 0.0086908 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-08-21 21:53 | 2022-08-21 22:40 | 25 | 0:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22082100153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2022-08-21 | 1175 | keep | 0 | Aug | 2022 | 0.00080029 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-21 22:05 | 2022-08-21 22:06 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1907-03 QUE LLEVA 98% 1909-09 | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-21 22:05 | 2022-08-21 22:06 | 4367 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 99% POR 1907-03 | S22082100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 4367 | keep | 0 | Aug | 2022 | 0.0029743 | 0.0029743 | Momentary | FALSE | FALSE | Not_TMED_Event | 4367
FAJARDO | 2022-08-21 22:13 | 2022-08-21 22:59 | 1633 | 0:46 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR EN SERVICIO 60 ADICIONAL | R22082100101 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 46 | 2022-08-21 | 75118 | keep | 0 | Aug | 2022 | 0.051163 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-21 22:22 | 2022-08-22 09:22 | 76 | 11:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 X 50 EN SU-1 | B22082100266 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 660 | 2022-08-21 | 50160 | keep | 0 | Aug | 2022 | 0.034164 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
GUAYAMA | 2022-08-21 22:28 | 2022-08-22 11:20 | 15 | 12:52 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE CAJA PRIMARIA A TRANSFORMADOR | P22082100163 | New_Event | Primary Wire Break | Include | Include | Equipment | 772 | 2022-08-21 | 11580 | keep | 0 | Aug | 2022 | 0.0078871 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-21 22:37 | 2022-08-22 14:55 | 67 | 16:18 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/LS DESGANCHE | C22082100344 | New_Event | Vegetation Contact | Include | Include | Vegetation | 978 | 2022-08-21 | 65526 | keep | 0 | Aug | 2022 | 0.044629 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2022-08-21 22:41 | 2022-08-22 21:43 | 319 | 23:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S22082101012 | New_Event | Cutout Failure | Include | Include | Equipment | 1382 | 2022-08-21 | 440858 | keep | 0 | Aug | 2022 | 0.30027 | 0.00021727 | Sustained | FALSE | FALSE | Not_TMED_Event | 319
BAYAMON | 2022-08-21 22:46 | 2022-08-22 11:12 | 26 | 12:26 | P | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO Y 1 X 40 Y 1 X 65 EN CORTES DE LINE | S22082100026 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 746 | 2022-08-21 | 19396 | keep | 0 | Aug | 2022 | 0.013211 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CANOVANAS | 2022-08-21 22:54 | 2022-08-21 22:55 | 2106 | 0:01 | T | PROBLEMA DEL CLIENTE | SE SECCIONALIZO ALIMENTADOR AVERIA SU-28 A HOTEL RIO MAR | R22082100000 | Additional_clients | Customer-Related Interruption | Include | Include | Public | 1 | 2022-08-21 | 2106 | keep | 0 | Aug | 2022 | 0.0014344 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-21 22:59 | 2022-08-22 00:12 | 272 | 1:13 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DEJO ABIERTO DE SU-4 @ MH7 PARA INSPECCION EN MH7 | R22082100101 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 73 | 2022-08-21 | 19856 | keep | 0 | Aug | 2022 | 0.013524 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-21 23:04 | 2022-08-22 10:40 | 200 | 11:36 | P | MAL TIEMPO/RAYOS | 2 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082100396 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 696 | 2022-08-21 | 139200 | keep | 0 | Aug | 2022 | 0.094808 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-21 23:16 | 2022-08-22 17:20 | 400 | 18:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA LINEA PARTIDA SE CERRO CONVERTIDOR RELACIONADO A EVENTO M22082100183 | M22082100309 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1084 | 2022-08-21 | 433600 | keep | 0 | Aug | 2022 | 0.29532 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-21 23:22 | 2022-08-22 00:52 | 1297 | 1:30 | T | DESGANCHE | DISPARO DE 1904-06 BKR SPARE QUE LLEVA 1901-02 Y 1901-03 SE DESGANCHO EN PARKVILLE CALLE MADISON Y SE CERRO POR SCADA | S22082101063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-08-21 | 116730 | keep | 0 | Aug | 2022 | 0.079504 | 0.00088338 | Sustained | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2022-08-21 23:22 | 2022-08-22 00:52 | 451 | 1:30 | T | DESGANCHE | DISPARO DE 1904-06 BKR SPARE QUE LLEVA 1901-02 Y 1901-03 SE DESGANCHO EN PARKVILLE CALLE MADISON Y SE CERRO POR SCADA | S22082101063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-08-21 | 40590 | keep | 0 | Aug | 2022 | 0.027646 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
YAUCO | 2022-08-21 23:25 | 2022-08-22 07:00 | 200 | 7:35 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082100411 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 455 | 2022-08-21 | 91000 | keep | 0 | Aug | 2022 | 0.06198 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-21 23:25 | 2022-08-22 10:15 | 600 | 10:50 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082100413 | New_Event | Vegetation Contact | Include | Include | Vegetation | 650 | 2022-08-21 | 390000 | keep | 0 | Aug | 2022 | 0.26563 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
HUMACAO | 2022-08-21 23:32 | 2022-08-22 06:37 | 41 | 7:05 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO | C22082100350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2022-08-21 | 17425 | keep | 0 | Aug | 2022 | 0.011868 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
AGUADILLA | 2022-08-21 23:41 | 2022-08-21 23:42 | 4882 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22082100416 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-21 | 4882 | keep | 0 | Aug | 2022 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
AGUADILLA | 2022-08-21 23:42 | 2022-08-22 10:20 | 12 | 10:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 75 KVA X 75 KVA | M22082100353 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 638 | 2022-08-21 | 7656 | keep | 0 | Aug | 2022 | 0.0052145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-22 00:10 | 2022-08-22 04:20 | 130 | 4:10 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO AVERIADO DE LINEA PRIMARIA EN EL SUELO PARA PODER TRABAJAR. | M22082200002 | New_Event | Primary Wire Break | Include | Include | Equipment | 250 | 2022-08-22 | 32500 | keep | 0 | Aug | 2022 | 0.022136 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
GUAYAMA | 2022-08-22 00:11 | 2022-08-22 03:00 | 25 | 2:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO SE REPORTO CAUSA | P22082200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-08-22 | 4225 | keep | 0 | Aug | 2022 | 0.0028776 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-08-22 00:12 | 2022-08-22 23:25 | 13 | 23:13 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO VS AVERIADO MEDIANTE SJ-220821-50 | R22082100101 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 1393 | 2022-08-22 | 18109 | keep | 0 | Aug | 2022 | 0.012334 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-22 00:14 | 2022-08-22 09:49 | 1 | 9:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE AVERIADO | A22082200001 | New_Event | Cutout Failure | Include | Include | Equipment | 575 | 2022-08-22 | 575 | keep | 0 | Aug | 2022 | 0.00039163 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-22 00:17 | 2022-08-22 12:44 | 40 | 12:27 | P | CRUCETA DEFECTUOSA O AVERIADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | M22082200121 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 747 | 2022-08-22 | 29880 | keep | 0 | Aug | 2022 | 0.020351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-08-22 00:50 | 2022-08-22 09:26 | 100 | 8:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22082200004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 516 | 2022-08-22 | 51600 | keep | 0 | Aug | 2022 | 0.035145 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-22 01:19 | 2022-08-22 14:27 | 125 | 13:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA NO FUNDIO | C22082200002 | New_Event | Cutout Failure | Include | Include | Equipment | 788 | 2022-08-22 | 98500 | keep | 0 | Aug | 2022 | 0.067088 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-08-22 01:40 | 2022-08-22 17:49 | 40 | 16:09 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE 100% EN SERVICIO | S22082200036 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 969 | 2022-08-22 | 38760 | keep | 0 | Aug | 2022 | 0.026399 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-22 02:55 | 2022-08-22 14:37 | 50 | 11:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082200003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 702 | 2022-08-22 | 35100 | keep | 0 | Aug | 2022 | 0.023906 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-22 02:56 | 2022-08-22 15:43 | 45 | 12:47 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22082200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 767 | 2022-08-22 | 34515 | keep | 0 | Aug | 2022 | 0.023508 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-08-22 03:01 | 2022-08-22 16:15 | 3 | 13:14 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE SECUNDARIO | R22082200006 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 794 | 2022-08-22 | 2382 | keep | 0 | Aug | 2022 | 0.0016224 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-22 03:54 | 2022-08-22 03:55 | 1812 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | B22082200000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-22 | 1812 | keep | 0 | Aug | 2022 | 0.0012341 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-22 03:55 | 2022-08-22 11:16 | 34 | 7:21 | P | DESGANCHE | SE REALIZO DESGANCHE Y 1 X 100 , 1 X 65 , 1 X 40 EN CORTES DE LINEA | B22082100024 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 441 | 2022-08-22 | 14994 | keep | 0 | Aug | 2022 | 0.010212 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
VEGA BAJA | 2022-08-22 03:57 | 2022-08-22 08:30 | 77 | 4:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22082200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 273 | 2022-08-22 | 21021 | keep | 0 | Aug | 2022 | 0.014317 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
ARECIBO | 2022-08-22 04:00 | 2022-08-22 11:47 | 50 | 7:47 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082200012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 467 | 2022-08-22 | 23350 | keep | 0 | Aug | 2022 | 0.015904 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-08-22 04:09 | 2022-08-22 10:00 | 125 | 5:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R22082200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2022-08-22 | 43875 | keep | 0 | Aug | 2022 | 0.029883 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2022-08-22 04:20 | 2022-08-22 12:10 | 126 | 7:50 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22082200002 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 470 | 2022-08-22 | 59220 | keep | 0 | Aug | 2022 | 0.040334 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-22 04:31 | 2022-08-22 10:30 | 40 | 5:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA | A22082200014 | New_Event | Primary Wire Break | Include | Include | Equipment | 359 | 2022-08-22 | 14360 | keep | 0 | Aug | 2022 | 0.0097805 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-22 05:00 | 2022-08-22 08:44 | 50 | 3:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C22082200007 | New_Event | Cutout Failure | Include | Include | Equipment | 224 | 2022-08-22 | 11200 | keep | 0 | Aug | 2022 | 0.0076283 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-22 05:16 | 2022-08-22 15:51 | 5 | 10:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA | A22082200013 | New_Event | Service Transformer Failure | Include | Include | Equipment | 635 | 2022-08-22 | 3175 | keep | 0 | Aug | 2022 | 0.0021625 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-22 05:36 | 2022-08-22 09:50 | 10 | 4:14 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22082200024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-08-22 | 2540 | keep | 0 | Aug | 2022 | 0.00173 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-22 05:38 | 2022-08-23 05:20 | 126 | 23:42 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22082200187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1422 | 2022-08-22 | 179172 | keep | 0 | Aug | 2022 | 0.12203 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
BAYAMON | 2022-08-22 05:47 | 2022-08-22 05:48 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 2402 | keep | 0 | Aug | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
HUMACAO | 2022-08-22 06:23 | 2022-08-22 06:24 | 824 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 65% DE SU CARGA POR 2604-03 | C22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 824 | keep | 0 | Aug | 2022 | 0.00056122 | 0.00056122 | Momentary | FALSE | FALSE | Not_TMED_Event | 824
BAYAMON | 2022-08-22 06:27 | 2022-08-22 14:18 | 1 | 7:51 | P | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLE NX 20 AMP | B22082200019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 471 | 2022-08-22 | 471 | keep | 0 | Aug | 2022 | 0.0003208 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-22 06:34 | 2022-08-22 11:22 | 1 | 4:48 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082200016 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 288 | 2022-08-22 | 288 | keep | 0 | Aug | 2022 | 0.00019616 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-22 06:57 | 2022-08-22 09:24 | 200 | 2:27 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082200020 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 147 | 2022-08-22 | 29400 | keep | 0 | Aug | 2022 | 0.020024 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-08-22 07:00 | 2022-08-22 07:01 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CON CARGA 5602-03 REALIZA UNA OPERACION Y QUEDA Y SERVICIO | P22082200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 3973 | keep | 0 | Aug | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-08-22 07:00 | 2022-08-22 07:01 | 2484 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CON CARGA 5602-03 REALIZA UNA OPERACION Y QUEDA Y SERVICIO | P22082200042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 2484 | keep | 0 | Aug | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
CANOVANAS | 2022-08-22 07:05 | 2022-08-22 13:56 | 160 | 6:51 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO RAYOS | R22082200021 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 411 | 2022-08-22 | 65760 | keep | 0 | Aug | 2022 | 0.044789 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
VEGA BAJA | 2022-08-22 07:11 | 2022-08-22 16:05 | 2 | 8:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22082200021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 534 | 2022-08-22 | 1068 | keep | 0 | Aug | 2022 | 0.00072741 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-08-22 07:20 | 2022-08-22 18:15 | 18 | 10:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22082200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 655 | 2022-08-22 | 11790 | keep | 0 | Aug | 2022 | 0.0080301 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-08-22 07:31 | 2022-08-22 13:13 | 5 | 5:42 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFROMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082200024 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 342 | 2022-08-22 | 1710 | keep | 0 | Aug | 2022 | 0.0011647 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-08-22 07:37 | 2022-08-22 07:38 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P22082200048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 2039 | keep | 0 | Aug | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CAGUAS | 2022-08-22 07:56 | 2022-08-22 07:57 | 2417 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | C22082200027 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-22 | 2417 | keep | 0 | Aug | 2022 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
BAYAMON | 2022-08-22 07:57 | 2022-08-22 07:58 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1909-08 | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 2435 | keep | 0 | Aug | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-08-22 07:57 | 2022-08-22 07:58 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1907-05 | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 2956 | keep | 0 | Aug | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CAGUAS | 2022-08-22 07:57 | 2022-08-22 16:09 | 100 | 8:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO PORTAFUSIBLE | C22082200100 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 492 | 2022-08-22 | 49200 | keep | 0 | Aug | 2022 | 0.03351 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-22 07:58 | 2022-08-22 07:59 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 95% DE LA CARGA DEL 1717-02 | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
MAYAGÃœEZ | 2022-08-22 08:00 | 2022-08-22 08:01 | 1444 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 6014-02 CON CARGA 6014-01 SE REALIZO PRUEBA Y QUEDA EN SERVICIO | M22082200065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 1444 | keep | 0 | Aug | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-08-22 08:00 | 2022-08-22 08:01 | 3630 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CON CARGA 6014-01 SE REALIZO PRUEBA Y QUEDA EN SERVICIO | M22082200065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 3630 | keep | 0 | Aug | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
AGUADILLA | 2022-08-22 08:07 | 2022-08-22 11:23 | 50 | 3:16 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22082200070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-08-22 | 9800 | keep | 0 | Aug | 2022 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-22 08:11 | 2022-08-22 12:12 | 1 | 4:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE REEMPLAZO PORTAFUSIBLE | R22082200034 | New_Event | Cutout Failure | Include | Include | Equipment | 241 | 2022-08-22 | 241 | keep | 0 | Aug | 2022 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-22 08:14 | 2022-08-22 20:47 | 100 | 12:33 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | B22082200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 753 | 2022-08-22 | 75300 | keep | 0 | Aug | 2022 | 0.051286 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-22 08:18 | 2022-08-22 14:27 | 30 | 6:09 | P | MAL TIEMPO/RAYOS | 4 X 10 EN TRANSFORMADORES Y 2 X 15 EN TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A22082200042 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 369 | 2022-08-22 | 11070 | keep | 0 | Aug | 2022 | 0.0075397 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-22 08:21 | 2022-08-22 15:13 | 3 | 6:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA EN C/L | B22082200038 | New_Event | Primary Wire Break | Include | Include | Equipment | 412 | 2022-08-22 | 1236 | keep | 0 | Aug | 2022 | 0.00084183 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-08-22 08:21 | 2022-08-22 12:22 | 5 | 4:01 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C22082200032 | New_Event | Animals | Include | Include | Wildlife | 241 | 2022-08-22 | 1205 | keep | 0 | Aug | 2022 | 0.00082072 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-08-22 08:25 | 2022-08-22 08:26 | 2039 | 0:01 | T | MAL TIEMPO/RAYOS | RECERRO | R22082200039 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-22 | 2039 | keep | 0 | Aug | 2022 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CANOVANAS | 2022-08-22 08:26 | 2022-08-22 17:45 | 1 | 9:19 | P | MAL TIEMPO/RAYOS | 1 X 80 Y 1 X 100 EN CORTE DE LINEA MAL TIEMPO RAYOS | R22082200046 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 559 | 2022-08-22 | 559 | keep | 0 | Aug | 2022 | 0.00038073 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-22 08:29 | 2022-08-22 17:02 | 200 | 8:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S22082200261 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 513 | 2022-08-22 | 102600 | keep | 0 | Aug | 2022 | 0.06988 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-22 08:41 | 2022-08-22 14:32 | 10 | 5:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA DE TRANSFORMADOR | M22082200088 | New_Event | Cutout Failure | Include | Include | Equipment | 351 | 2022-08-22 | 3510 | keep | 0 | Aug | 2022 | 0.0023906 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-22 08:41 | 2022-08-22 15:22 | 8 | 6:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22082200044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 401 | 2022-08-22 | 3208 | keep | 0 | Aug | 2022 | 0.002185 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-22 08:52 | 2022-08-22 13:44 | 1 | 4:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C22082200041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2022-08-22 | 292 | keep | 0 | Aug | 2022 | 0.00019888 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-22 08:59 | 2022-08-22 14:00 | 8 | 5:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE TRANSFORMADOR | M22082200101 | New_Event | Cutout Failure | Include | Include | Equipment | 301 | 2022-08-22 | 2408 | keep | 0 | Aug | 2022 | 0.0016401 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-22 08:59 | 2022-08-22 13:05 | 30 | 4:06 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082200049 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 246 | 2022-08-22 | 7380 | keep | 0 | Aug | 2022 | 0.0050265 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-22 09:07 | 2022-08-22 09:42 | 15 | 0:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082200052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2022-08-22 | 525 | keep | 0 | Aug | 2022 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-22 09:11 | 2022-08-22 13:30 | 1 | 4:19 | P | MAL TIEMPO/RAYOS | 1 X 25 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22082200107 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 259 | 2022-08-22 | 259 | keep | 0 | Aug | 2022 | 0.0001764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-22 09:19 | 2022-08-23 09:41 | 1 | 24:22 | P | DESGANCHE | SE REALIZO DESGANCHE Y 2 X 100 EN C/L | B22082200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1462 | 2022-08-22 | 1462 | keep | 0 | Aug | 2022 | 0.00099576 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-22 09:24 | 2022-08-22 11:00 | 150 | 1:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN PROVISIONAL SE REMPLAZO CAJA Y SE REPARO PUENTE ABIERTO Y 1 X 80 SUM-20 | S22082100733 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2022-08-22 | 14400 | keep | 0 | Aug | 2022 | 0.0098078 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-22 09:32 | 2022-08-22 15:15 | 80 | 5:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082200060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2022-08-22 | 27440 | keep | 0 | Aug | 2022 | 0.018689 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-22 09:36 | 2022-08-22 16:13 | 6 | 6:37 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B22082200062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 397 | 2022-08-22 | 2382 | keep | 0 | Aug | 2022 | 0.0016224 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-22 09:45 | 2022-08-22 12:25 | 120 | 2:40 | P | CAUSAS EXTERNAS | 2 X 100 EN C/L MAQUINA PREPARANDO TERRENO SACUDIO LAS LINEAS | C22082200053 | New_Event | Damage From Public | Include | Include | Public | 160 | 2022-08-22 | 19200 | keep | 0 | Aug | 2022 | 0.013077 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2022-08-22 09:53 | 2022-08-23 01:41 | 65 | 15:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A22082200060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 948 | 2022-08-22 | 61620 | keep | 0 | Aug | 2022 | 0.041969 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-08-22 09:55 | 2022-08-22 15:59 | 50 | 6:04 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | S22082200347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 364 | 2022-08-22 | 18200 | keep | 0 | Aug | 2022 | 0.012396 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-22 10:00 | 2022-08-22 13:42 | 20 | 3:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 50 EN C/L | B22082200070 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2022-08-22 | 4440 | keep | 0 | Aug | 2022 | 0.0030241 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-08-22 10:03 | 2022-08-22 13:55 | 12 | 3:52 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR AVE CRUZO LINEAS | M22082200122 | New_Event | Animals | Include | Include | Wildlife | 232 | 2022-08-22 | 2784 | keep | 0 | Aug | 2022 | 0.0018962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-22 10:04 | 2022-08-22 10:05 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 3871 | keep | 0 | Aug | 2022 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
MAYAGÃœEZ | 2022-08-22 10:05 | 2022-08-22 16:50 | 1 | 6:45 | P | DESGANCHE | 2 X 10 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082200125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2022-08-22 | 405 | keep | 0 | Aug | 2022 | 0.00027584 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-22 10:32 | 2022-08-22 20:45 | 38 | 10:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22082200066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 613 | 2022-08-22 | 23294 | keep | 0 | Aug | 2022 | 0.015865 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
SAN JUAN | 2022-08-22 10:34 | 2022-08-22 13:53 | 15 | 3:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S22082200374 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2022-08-22 | 2985 | keep | 0 | Aug | 2022 | 0.0020331 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-22 10:43 | 2022-08-23 11:41 | 25 | 24:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R22082200067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1498 | 2022-08-22 | 37450 | keep | 0 | Aug | 2022 | 0.025507 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-22 10:53 | 2022-08-22 16:00 | 9 | 5:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN BOMBAS AAA Y 1X 50 EN C/L | B22082200075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 307 | 2022-08-22 | 2763 | keep | 0 | Aug | 2022 | 0.0018819 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2022-08-22 11:00 | 2022-08-22 11:40 | 10 | 0:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082200072 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2022-08-22 | 400 | keep | 0 | Aug | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-22 11:04 | 2022-08-22 14:41 | 60 | 3:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA AVERIADA | C22082200073 | New_Event | Cutout Failure | Include | Include | Equipment | 217 | 2022-08-22 | 13020 | keep | 0 | Aug | 2022 | 0.0088679 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-22 11:05 | 2022-08-22 12:21 | 100 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 50 EN C/L | B22082200077 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2022-08-22 | 7600 | keep | 0 | Aug | 2022 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-22 11:06 | 2022-08-22 18:05 | 100 | 6:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 65 EN CORTE DE LINEA MAL TIEMPO | S22082200396 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 419 | 2022-08-22 | 41900 | keep | 0 | Aug | 2022 | 0.028538 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-22 11:16 | 2022-08-22 11:17 | 2073 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22082200143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 2073 | keep | 0 | Aug | 2022 | 0.0014119 | 0.0014119 | Momentary | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2022-08-22 11:16 | 2022-08-22 11:17 | 637 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22082200143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 637 | keep | 0 | Aug | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-08-22 11:16 | 2022-08-22 11:17 | 1491 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22082200143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 1491 | keep | 0 | Aug | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-08-22 11:16 | 2022-08-22 11:17 | 4892 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22082200144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 4892 | keep | 0 | Aug | 2022 | 0.0033319 | 0.0033319 | Momentary | FALSE | FALSE | Not_TMED_Event | 4892
MAYAGÃœEZ | 2022-08-22 11:16 | 2022-08-22 11:17 | 160 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13500 | M22082200144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 160 | keep | 0 | Aug | 2022 | 0.00010898 | 0.00010898 | Momentary | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2022-08-22 11:23 | 2022-08-22 11:24 | 2147 | 0:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR POR BAMBUA EN LA LINEA CERCA DE SUBESTACION HIZO QUE SE FUNDIERA FUSIBLE EN ALTA DE XMR | B22082200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-22 | 2147 | keep | 0 | Aug | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-08-22 11:24 | 2022-08-22 15:08 | 4176 | 3:44 | S | DESGANCHE | SE REMPLAZO FUSIBLE 150SE EN XMR SUBESTACION. ESTE FUNDIO CUANDO HUBO OPERACION DE INTERRUPTOR 9801-03 POR BAMBUA EN LA LINEA | B22082200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-08-22 | 935424 | keep | 0 | Aug | 2022 | 0.63711 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-08-22 11:24 | 2022-08-22 15:08 | 252 | 3:44 | S | DESGANCHE | SE REMPLAZO FUSIBLE 150SE EN XMR SUBESTACION. ESTE FUNDIO CUANDO HUBO OPERACION DE INTERRUPTOR 9801-03 POR BAMBUA EN LA LINEA | B22082200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-08-22 | 56448 | keep | 0 | Aug | 2022 | 0.038446 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2022-08-22 11:24 | 2022-08-22 15:08 | 2147 | 3:44 | S | DESGANCHE | SE REMPLAZO FUSIBLE 150SE EN XMR SUBESTACION. ESTE FUNDIO CUANDO HUBO OPERACION DE INTERRUPTOR 9801-03 POR BAMBUA EN LA LINEA | B22082200090 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-08-22 | 480928 | keep | 0 | Aug | 2022 | 0.32756 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
VEGA BAJA | 2022-08-22 11:27 | 2022-08-23 14:23 | 6 | 26:56 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | B22082200071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1616 | 2022-08-22 | 9696 | keep | 0 | Aug | 2022 | 0.0066039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-08-22 11:31 | 2022-08-22 13:37 | 75 | 2:06 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22082200086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-22 | 9450 | keep | 0 | Aug | 2022 | 0.0064364 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2022-08-22 11:50 | 2022-08-22 11:51 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 15% DEL 1647-09 | R22082200077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 3046 | keep | 0 | Aug | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2022-08-22 11:50 | 2022-08-22 11:51 | 307 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 15% POR 1646-03 | R22082200077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 307 | keep | 0 | Aug | 2022 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
MAYAGÃœEZ | 2022-08-22 11:52 | 2022-08-22 13:50 | 150 | 1:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22082200155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-08-22 | 17700 | keep | 0 | Aug | 2022 | 0.012055 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-22 11:54 | 2022-08-22 14:58 | 30 | 3:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082200093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2022-08-22 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-22 11:54 | 2022-08-22 14:10 | 8 | 2:16 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082200157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 136 | 2022-08-22 | 1088 | keep | 0 | Aug | 2022 | 0.00074103 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-22 11:55 | 2022-08-22 11:56 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 15% DEL 1647-09 | R22082200077 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 3046 | keep | 0 | Aug | 2022 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2022-08-22 11:55 | 2022-08-22 11:56 | 307 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 15% POR 1646-03 | R22082200077 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 307 | keep | 0 | Aug | 2022 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
CANOVANAS | 2022-08-22 11:57 | 2022-08-22 11:58 | 2179 | 0:01 | T | MAL TIEMPO/RAYOS | DISPARO Y SE CERRO POR SCADA | R22082200079 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-22 | 2179 | keep | 0 | Aug | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2022-08-22 11:58 | 2022-08-22 13:40 | 700 | 1:42 | P | MAL TIEMPO/RAYOS | 3 X 140 EN CORTE DE LINEA MAL TIEMPO RAYOS | R22082200083 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2022-08-22 | 71400 | keep | 0 | Aug | 2022 | 0.04863 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
SAN JUAN | 2022-08-22 12:00 | 2022-08-22 16:41 | 150 | 4:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN PROVISIONAL SE REMPLAZO CAJA Y SE REPARO PUENTE ABIERTO Y 1 X 80 SUM-20 | S22082100733 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 281 | 2022-08-22 | 42150 | keep | 0 | Aug | 2022 | 0.028708 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:20 | 2022-08-22 14:45 | 12 | 2:25 | P | MAL TIEMPO/RAYOS | 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082200161 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 145 | 2022-08-22 | 1740 | keep | 0 | Aug | 2022 | 0.0011851 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-22 12:21 | 2022-08-22 15:45 | 1 | 3:24 | P | MAL TIEMPO/RAYOS | 3 X 25 EN RISER HACIA TRANSCLOSURE MAL TIEMPO RAYOS | R22082200087 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 204 | 2022-08-22 | 204 | keep | 0 | Aug | 2022 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-22 12:21 | 2022-08-22 13:23 | 88 | 1:02 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR SECCIONALIZAR TRAMO LINEA PRIMARIA EN EL PISO SE REMPLAZO 2 CAJAS 1 X 65 EN CORTE DE LINEA Y SE REPARO SECUNDARIA Y TOMAS | S22082200487 | New_Event | Primary Wire Break | Include | Include | Equipment | 62 | 2022-08-22 | 5456 | keep | 0 | Aug | 2022 | 0.0037161 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
CANOVANAS | 2022-08-22 12:37 | 2022-08-22 17:07 | 158 | 4:30 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR GUARAGUAO | R22082200091 | New_Event | Animals | Include | Include | Wildlife | 270 | 2022-08-22 | 42660 | keep | 0 | Aug | 2022 | 0.029056 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
BARRANQUITAS | 2022-08-22 12:43 | 2022-08-22 12:45 | 3296 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA CERRADO X CONTROL | C22082200090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-22 | 6592 | keep | 0 | Aug | 2022 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
MAYAGÃœEZ | 2022-08-22 12:44 | 2022-08-22 12:49 | 1253 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 6265 | keep | 0 | Aug | 2022 | 0.0042671 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-08-22 12:44 | 2022-08-22 12:49 | 1266 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 6330 | keep | 0 | Aug | 2022 | 0.0043113 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-08-22 12:44 | 2022-08-22 12:49 | 411 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200116 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 2055 | keep | 0 | Aug | 2022 | 0.0013997 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2022-08-22 12:44 | 2022-08-22 12:49 | 1617 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 8085 | keep | 0 | Aug | 2022 | 0.0055067 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-08-22 12:44 | 2022-08-22 12:49 | 1017 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 5085 | keep | 0 | Aug | 2022 | 0.0034634 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-08-22 12:44 | 2022-08-22 12:49 | 828 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 4140 | keep | 0 | Aug | 2022 | 0.0028197 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-08-22 12:44 | 2022-08-22 12:49 | 863 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 4315 | keep | 0 | Aug | 2022 | 0.0029389 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-08-22 12:44 | 2022-08-22 12:49 | 309 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 1545 | keep | 0 | Aug | 2022 | 0.0010523 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-08-22 12:44 | 2022-08-22 12:49 | 176 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 880 | keep | 0 | Aug | 2022 | 0.00059936 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-08-22 12:44 | 2022-08-22 12:49 | 974 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200169 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-22 | 4870 | keep | 0 | Aug | 2022 | 0.0033169 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
FAJARDO | 2022-08-22 12:48 | 2022-08-22 14:20 | 135 | 1:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R22082200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-08-22 | 12420 | keep | 0 | Aug | 2022 | 0.0084592 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2022-08-22 12:49 | 2022-08-22 12:51 | 40 | 0:02 | P | CRUCETA DEFECTUOSA O AVERIADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | M22082200121 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 2 | 2022-08-22 | 80 | keep | 0 | Aug | 2022 | 5.4488e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:51 | 2022-08-22 15:45 | 1253 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200173 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 218022 | keep | 0 | Aug | 2022 | 0.14849 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:51 | 2022-08-22 15:45 | 1266 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200173 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 220284 | keep | 0 | Aug | 2022 | 0.15003 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:51 | 2022-08-22 15:45 | 411 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200173 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 71514 | keep | 0 | Aug | 2022 | 0.048708 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-22 12:51 | 2022-08-22 15:45 | 1617 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200174 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 281358 | keep | 0 | Aug | 2022 | 0.19163 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-22 12:51 | 2022-08-22 15:45 | 1017 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200174 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 176958 | keep | 0 | Aug | 2022 | 0.12053 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-22 12:51 | 2022-08-22 15:45 | 828 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200174 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 144072 | keep | 0 | Aug | 2022 | 0.098127 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:51 | 2022-08-22 15:45 | 863 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200176 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 150162 | keep | 0 | Aug | 2022 | 0.10227 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:51 | 2022-08-22 15:45 | 309 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200176 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 53766 | keep | 0 | Aug | 2022 | 0.03662 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:51 | 2022-08-22 15:45 | 176 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200176 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 30624 | keep | 0 | Aug | 2022 | 0.020858 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-22 12:51 | 2022-08-22 15:45 | 974 | 2:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 | M22082200177 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 174 | 2022-08-22 | 169476 | keep | 0 | Aug | 2022 | 0.11543 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-22 12:55 | 2022-08-23 00:14 | 25 | 11:19 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | A22082200156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 679 | 2022-08-22 | 16975 | keep | 0 | Aug | 2022 | 0.011562 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-22 13:01 | 2022-08-22 13:04 | 1718 | 0:03 | T | DESCONECTIVO DEFECTUOSO | DISPARO DEL INTERRUPTOR NO RECERRO SE CERO POR CONTROL SCADA MACHETE AVERIADO EN AUXILIAR DE LINEA DEL INTERRUPTOR | M22082200175 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2022-08-22 | 5154 | keep | 0 | Aug | 2022 | 0.0035104 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
AGUADILLA | 2022-08-22 13:04 | 2022-08-22 20:54 | 575 | 7:50 | P | DESCONECTIVO DEFECTUOSO | MACHETE AVERIADO EN AUXILIAR DE LINEA DEL INTERRUPTOR 7104-06 SE ABRIO INTERRUPTOR PARA TRANSFERIR CARA AL 7104-05 | M22082200202 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 470 | 2022-08-22 | 270250 | keep | 0 | Aug | 2022 | 0.18407 | 0.00039163 | Sustained | FALSE | FALSE | Not_TMED_Event | 575
PONCE | 2022-08-22 13:13 | 2022-08-22 14:29 | 100 | 1:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE MASIVO | P22082200110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-08-22 | 7600 | keep | 0 | Aug | 2022 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-22 13:26 | 2022-08-22 20:52 | 88 | 7:26 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR SECCIONALIZAR TRAMO LINEA PRIMARIA EN EL PISO SE REMPLAZO 2 CAJAS 1 X 65 EN CORTE DE LINEA Y SE REPARO SECUNDARIA Y TOMAS | S22082200487 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 446 | 2022-08-22 | 39248 | keep | 0 | Aug | 2022 | 0.026732 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-22 13:27 | 2022-08-22 17:03 | 90 | 3:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A22082200095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 216 | 2022-08-22 | 19440 | keep | 0 | Aug | 2022 | 0.01324 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-08-22 13:30 | 2022-08-22 16:20 | 70 | 2:50 | P | ARBOL SOBRE LINEA | 2 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22082200194 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 170 | 2022-08-22 | 11900 | keep | 0 | Aug | 2022 | 0.008105 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-08-22 13:39 | 2022-08-22 15:38 | 30 | 1:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22082200098 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 119 | 2022-08-22 | 3570 | keep | 0 | Aug | 2022 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-22 13:55 | 2022-08-22 16:02 | 5 | 2:07 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 65 EN C/L | B22082200013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 127 | 2022-08-22 | 635 | keep | 0 | Aug | 2022 | 0.0004325 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-08-22 14:01 | 2022-08-22 19:00 | 35 | 4:59 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082200106 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 299 | 2022-08-22 | 10465 | keep | 0 | Aug | 2022 | 0.0071277 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2022-08-22 14:05 | 2022-08-22 17:28 | 2 | 3:23 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M22082200215 | New_Event | Animals | Include | Include | Wildlife | 203 | 2022-08-22 | 406 | keep | 0 | Aug | 2022 | 0.00027652 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-22 14:08 | 2022-08-22 22:21 | 25 | 8:13 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO DESPACHO LE ASIGNO EL MISMO EVENTO | A22082200109 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 493 | 2022-08-22 | 12325 | keep | 0 | Aug | 2022 | 0.0083945 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-22 14:08 | 2022-08-22 22:21 | 20 | 8:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZA POSTE PRIMARIO Y SE CIERRA C/L DESPACHO LE ASIGNO EL MISMO EVENTO. | A22082200109 | New_Event | Primary Pole Failure | Include | Include | Equipment | 493 | 2022-08-22 | 9860 | keep | 0 | Aug | 2022 | 0.0067156 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-22 14:10 | 2022-08-22 14:55 | 13 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIAS | M22082200164 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-08-22 | 585 | keep | 0 | Aug | 2022 | 0.00039844 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2022-08-22 14:11 | 2022-08-22 16:27 | 3 | 2:16 | P | MAL TIEMPO/RAYOS | 2 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082200111 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 136 | 2022-08-22 | 408 | keep | 0 | Aug | 2022 | 0.00027789 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 3070 | keep | 0 | Aug | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 2735 | keep | 0 | Aug | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 1070 | keep | 0 | Aug | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 1647 | keep | 0 | Aug | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 3295 | keep | 0 | Aug | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 1180 | keep | 0 | Aug | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 320 | keep | 0 | Aug | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-08-22 14:23 | 2022-08-22 14:24 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22082200144 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 2234 | keep | 0 | Aug | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2022-08-22 14:24 | 2022-08-22 17:05 | 200 | 2:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22082200125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-08-22 | 32200 | keep | 0 | Aug | 2022 | 0.021931 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-08-22 14:27 | 2022-08-22 18:39 | 80 | 4:12 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 40 EN C/L RAYOS | C22082200113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 252 | 2022-08-22 | 20160 | keep | 0 | Aug | 2022 | 0.013731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-08-22 14:28 | 2022-08-22 21:26 | 7 | 6:58 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082200129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 418 | 2022-08-22 | 2926 | keep | 0 | Aug | 2022 | 0.0019929 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-08-22 14:31 | 2022-08-22 19:00 | 85 | 4:29 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082200227 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 269 | 2022-08-22 | 22865 | keep | 0 | Aug | 2022 | 0.015573 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
UTUADO | 2022-08-22 14:33 | 2022-08-22 18:30 | 5 | 3:57 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082200130 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 237 | 2022-08-22 | 1185 | keep | 0 | Aug | 2022 | 0.0008071 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-22 14:34 | 2022-08-22 16:00 | 10 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22082200133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2022-08-22 | 860 | keep | 0 | Aug | 2022 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-22 14:35 | 2022-08-22 14:48 | 1 | 0:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22082200132 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 13 | 2022-08-22 | 13 | keep | 0 | Aug | 2022 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-22 14:40 | 2022-08-22 14:43 | 215 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9105-07 SE CERRO POR SCADA | B22082200147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-22 | 645 | keep | 0 | Aug | 2022 | 0.00043931 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-08-22 14:43 | 2022-08-22 21:04 | 60 | 6:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22082200165 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 381 | 2022-08-22 | 22860 | keep | 0 | Aug | 2022 | 0.01557 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-22 14:44 | 2022-08-22 20:00 | 150 | 5:16 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082200143 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 316 | 2022-08-22 | 47400 | keep | 0 | Aug | 2022 | 0.032284 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-08-22 14:44 | 2022-08-22 14:45 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 3000 | keep | 0 | Aug | 2022 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2022-08-22 14:51 | 2022-08-22 14:52 | 652 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082200167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 652 | keep | 0 | Aug | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-22 14:51 | 2022-08-22 14:52 | 2704 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082200167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-22 | 2704 | keep | 0 | Aug | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2022-08-22 14:53 | 2022-08-22 18:10 | 2704 | 3:17 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO EN TRONCAL | B22082200151 | New_Event | Switch Failure | Include | Include | Equipment | 197 | 2022-08-22 | 532688 | keep | 0 | Aug | 2022 | 0.36281 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2022-08-22 14:55 | 2022-08-22 22:21 | 70 | 7:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR PRIMARIO ROTO | A22082200109 | New_Event | Primary Wire Break | Include | Include | Equipment | 446 | 2022-08-22 | 31220 | keep | 0 | Aug | 2022 | 0.021264 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-08-22 14:59 | 2022-08-22 18:50 | 4 | 3:51 | P | PROBLEMA DEL CLIENTE | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE HACIA EL SU-1, SE DEJO ABIERTO HACIA EL CHURCHS CHICKEN PARA QUE REPAREN | R22082200120 | New_Event | Customer-Related Interruption | Include | Include | Public | 231 | 2022-08-22 | 924 | keep | 0 | Aug | 2022 | 0.00062933 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-08-22 15:00 | 2022-08-22 16:50 | 15 | 1:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22082200102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 110 | 2022-08-22 | 1650 | keep | 0 | Aug | 2022 | 0.0011238 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-22 15:02 | 2022-08-22 15:03 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE 9202-03 | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 308 | keep | 0 | Aug | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-08-22 15:02 | 2022-08-22 15:03 | 1397 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE 9202-03 | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 1397 | keep | 0 | Aug | 2022 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
SAN JUAN | 2022-08-22 15:03 | 2022-08-22 15:06 | 437 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIOSU CARGA POR 1530-07 MAL TIEMPO LLUVIA | S22082200551 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-08-22 | 1311 | keep | 0 | Aug | 2022 | 0.00089292 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2022-08-22 15:03 | 2022-08-22 15:06 | 643 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1530-6 MAL TIEMPO LLUVIA | S22082200551 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-08-22 | 1929 | keep | 0 | Aug | 2022 | 0.0013138 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
AGUADILLA | 2022-08-22 15:07 | 2022-08-22 16:41 | 8 | 1:34 | P | MAL TIEMPO/RAYOS | 1 X 6 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082200244 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 94 | 2022-08-22 | 752 | keep | 0 | Aug | 2022 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-22 15:08 | 2022-08-22 19:10 | 60 | 4:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 150 EN SU-6 MAL TIEMPO LLUVIA | S22082200556 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 242 | 2022-08-22 | 14520 | keep | 0 | Aug | 2022 | 0.0098895 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-22 15:08 | 2022-08-22 18:04 | 29 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA FUERTE | B20822000160 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2022-08-22 | 5104 | keep | 0 | Aug | 2022 | 0.0034763 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2022-08-22 15:09 | 2022-08-22 19:31 | 150 | 4:22 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA DESGANCHE | S22082200558 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-08-22 | 39300 | keep | 0 | Aug | 2022 | 0.026767 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2022-08-22 15:10 | 2022-08-23 13:13 | 25 | 22:03 | P | DESGANCHE | 1 X 25 EN C/L Y DESGANCHE | B22082200163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1323 | 2022-08-22 | 33075 | keep | 0 | Aug | 2022 | 0.022527 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-22 15:11 | 2022-08-22 15:12 | 8679 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 85% POR 1206-03 MAL TIEMPO LLUVIA 10% DEL 1206-3 X 1620-02 | S22082200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-22 | 8679 | keep | 0 | Aug | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-08-22 15:11 | 2022-08-22 15:12 | 3719 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 85% DEL 1204-05 10% DEL 1206-3 X 1620-02 | S22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 3719 | keep | 0 | Aug | 2022 | 0.002533 | 0.002533 | Momentary | FALSE | FALSE | Not_TMED_Event | 3719
FAJARDO | 2022-08-22 15:11 | 2022-08-22 17:18 | 4 | 2:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R22082200122 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2022-08-22 | 508 | keep | 0 | Aug | 2022 | 0.000346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-22 15:15 | 2022-08-22 15:16 | 5961 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B22082200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-22 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-22 15:15 | 2022-08-22 15:16 | 865 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 95% DE LA CARGA POR EL 1713-05 | B22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 865 | keep | 0 | Aug | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
AGUADILLA | 2022-08-22 15:15 | 2022-08-22 18:40 | 50 | 3:25 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082200250 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 205 | 2022-08-22 | 10250 | keep | 0 | Aug | 2022 | 0.0069812 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-22 15:18 | 2022-08-22 17:20 | 1 | 2:02 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO PISTOLA 1 X 50 EN RISER | S22082200573 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 122 | 2022-08-22 | 122 | keep | 0 | Aug | 2022 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-22 15:21 | 2022-08-22 16:45 | 84 | 1:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22082200126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2022-08-22 | 7056 | keep | 0 | Aug | 2022 | 0.0048058 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
CAGUAS | 2022-08-22 15:26 | 2022-08-22 16:42 | 25 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C22082200121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2022-08-22 | 1900 | keep | 0 | Aug | 2022 | 0.0012941 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-22 15:27 | 2022-08-23 09:56 | 7 | 18:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22082200177 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1109 | 2022-08-22 | 7763 | keep | 0 | Aug | 2022 | 0.0052873 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-22 15:30 | 2022-08-22 18:44 | 1085 | 3:14 | T | DESGANCHE | DISPARO SE PATRULLO MAL TIEMPO SE RETIRO RAMA SOBRE FASE A VARETA DE PISO Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S22082200583 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-08-22 | 210490 | keep | 0 | Aug | 2022 | 0.14336 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-08-22 15:35 | 2022-08-22 19:35 | 20 | 4:00 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | S22082100428 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-08-22 | 4800 | keep | 0 | Aug | 2022 | 0.0032693 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-22 15:35 | 2022-08-22 17:30 | 10 | 1:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIA FUERTE | B22082200179 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 115 | 2022-08-22 | 1150 | keep | 0 | Aug | 2022 | 0.00078326 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-22 15:41 | 2022-08-22 15:46 | 1784 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y PARTE 1717-01 SE CERRO POR SCADA | B22082200182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-22 | 8920 | keep | 0 | Aug | 2022 | 0.0060754 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2022-08-22 15:41 | 2022-08-22 15:46 | 2000 | 0:05 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y PARTE 1717-01 SE CERRO POR SCADA | B22082200182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-22 | 10000 | keep | 0 | Aug | 2022 | 0.006811 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2022-08-22 15:41 | 2022-08-22 15:46 | 186 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y PARTE 1717-01 SE CERRO POR SCADA | B22082200182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-22 | 930 | keep | 0 | Aug | 2022 | 0.00063342 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2022-08-22 15:46 | 2022-08-22 17:07 | 3 | 1:21 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1707-02 LLEVANDO CARGA 1707-03. SE ABRIO MACHETES N/O Y SE CERRO POR CONTROL. 1707-02 100% EN SERVICIO | B22082200147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-08-22 | 243 | keep | 0 | Aug | 2022 | 0.00016551 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-22 15:46 | 2022-08-22 17:34 | 61 | 1:48 | T | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA CERRO MACHETES N/O CON 1707-02 100% EN SERVICIO | B22082200147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-08-22 | 6588 | keep | 0 | Aug | 2022 | 0.0044871 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
MAYAGÃœEZ | 2022-08-22 15:46 | 2022-08-22 18:15 | 50 | 2:29 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082200284 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 149 | 2022-08-22 | 7450 | keep | 0 | Aug | 2022 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-22 15:47 | 2022-08-22 15:48 | 437 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO SU CARGA POR 1530-07 MAL TIEMPO LLUVIA | S22082200000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-22 | 437 | keep | 0 | Aug | 2022 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2022-08-22 15:47 | 2022-08-22 15:48 | 437 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 1530-06 MAL TIEMPO LLUVIA | S22082200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-22 | 437 | keep | 0 | Aug | 2022 | 0.00029764 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
UTUADO | 2022-08-22 15:47 | 2022-08-23 14:10 | 8 | 22:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082200199 | New_Event | Cutout Failure | Include | Include | Equipment | 1343 | 2022-08-22 | 10744 | keep | 0 | Aug | 2022 | 0.0073177 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-22 15:54 | 2022-08-22 17:44 | 74 | 1:50 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PATRULLO MAL TIEMPO SE CERRO POR CONTROL QUEDO EN SERVICIO 10% POR 1437-04 | S22082200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 110 | 2022-08-22 | 8140 | keep | 0 | Aug | 2022 | 0.0055441 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-08-22 15:54 | 2022-08-22 17:44 | 892 | 1:50 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PATRULLO M,AL TIEMPO SE CERRO POR CONTROL QUEDO EN SERVICIO LLEVA 10% DEL 1301-02 | S22082200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 110 | 2022-08-22 | 98120 | keep | 0 | Aug | 2022 | 0.066829 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
UTUADO | 2022-08-22 15:54 | 2022-08-22 17:30 | 8 | 1:36 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082200205 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 96 | 2022-08-22 | 768 | keep | 0 | Aug | 2022 | 0.00052308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-22 15:56 | 2022-08-22 19:33 | 5961 | 3:37 | T | DESGANCHE | SE REMPLAZO AISLADOR PARTIDO Y SE CERRO INTERRUPTOR SECCIONALIZADO. ENTRO 25% 1713-05 QUEDO FUERA EL 95% 1717-02 | B22082200195 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-08-22 | 1293537 | keep | 0 | Aug | 2022 | 0.88102 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
AGUADILLA | 2022-08-22 15:57 | 2022-08-22 15:58 | 828 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082200291 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 828 | keep | 0 | Aug | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
BAYAMON | 2022-08-22 16:02 | 2022-08-22 19:15 | 222 | 3:13 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE REPARO NEUTRAL EN MECANISMO DEL MOTOR DE INTERRUPTOR LO QUE IMPEDIA QUE CERRARA POR CONTROL. INTERRUPTOR 1907-03 LLEVA CARGA 1909-08 | S22082200634 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 193 | 2022-08-22 | 42846 | keep | 0 | Aug | 2022 | 0.029182 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-22 16:02 | 2022-08-22 19:15 | 4367 | 3:13 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | SE REPARO NEUTRAL EN MECANISMO DEL MOTOR DE INTERRUPTOR LO QUE IMPEDIA QUE CERRARA POR CONTROL. INTERRUPTOR 1907-03 LLEVA 99% DE 1909-09 | S22082200634 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 193 | 2022-08-22 | 842831 | keep | 0 | Aug | 2022 | 0.57405 | 0.0029743 | Sustained | FALSE | FALSE | Not_TMED_Event | 4367
PONCE | 2022-08-22 16:08 | 2022-08-22 17:55 | 80 | 1:47 | P | CONDUCTOR ARRIADO O CRUZADO | SE AISLO LINEA PEGADA A POSTE MADERA 1 X 100 Y DESGANCHE | P22082200150 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 107 | 2022-08-22 | 8560 | keep | 0 | Aug | 2022 | 0.0058302 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-22 16:12 | 2022-08-22 18:41 | 147 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22082200132 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2022-08-22 | 21903 | keep | 0 | Aug | 2022 | 0.014918 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
SAN JUAN | 2022-08-22 16:13 | 2022-08-23 05:48 | 39 | 13:35 | P | DESGANCHE | SE REALIZO DESGANCHE DE RAMA, SE LEVANTO CONDUCTOR PRIMARIO Y SECUNDARIO | S22082200646 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2022-08-22 | 31785 | keep | 0 | Aug | 2022 | 0.021649 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2022-08-22 16:14 | 2022-08-22 20:38 | 27 | 4:24 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | B22082200209 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 264 | 2022-08-22 | 7128 | keep | 0 | Aug | 2022 | 0.0048548 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
SAN JUAN | 2022-08-22 16:16 | 2022-08-22 16:25 | 826 | 0:09 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO 20% POR 1620-05 SE PROBO QUEDO EN SERVICIO MAL TIEMPO LLUVIA | S22082200652 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 9 | 2022-08-22 | 7434 | keep | 0 | Aug | 2022 | 0.0050633 | 0.00056258 | Sustained | FALSE | FALSE | Not_TMED_Event | 826
CANOVANAS | 2022-08-22 16:16 | 2022-08-22 16:25 | 1615 | 0:09 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 20% DEL 1206-03 SE PROBO QUEDO EN SERVICIO MAL TIEMPO LLUVIA | S22082200652 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 9 | 2022-08-22 | 14535 | keep | 0 | Aug | 2022 | 0.0098997 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2022-08-22 16:16 | 2022-08-22 16:17 | 5668 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22082200135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 5668 | keep | 0 | Aug | 2022 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2022-08-22 16:18 | 2022-08-22 16:29 | 828 | 0:11 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO LLUVIA 40% POR 1206-04 | S22082200655 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2022-08-22 | 9108 | keep | 0 | Aug | 2022 | 0.0062034 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-08-22 16:18 | 2022-08-22 16:29 | 1977 | 0:11 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO LLUVIA 40% POR 1206-04 | S22082200655 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2022-08-22 | 21747 | keep | 0 | Aug | 2022 | 0.014812 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-22 16:18 | 2022-08-22 16:29 | 1799 | 0:11 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO LLUVIA LLEVA 60% DEL 1204-03 LLEVA 20% DEL 1303-02 Y 40% DEL 1204-04 | S22082200655 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2022-08-22 | 19789 | keep | 0 | Aug | 2022 | 0.013478 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-22 16:18 | 2022-08-22 16:29 | 487 | 0:11 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO 20% POR 1206-04 LLUVIA FUERTE | S22082200655 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2022-08-22 | 5357 | keep | 0 | Aug | 2022 | 0.0036486 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
VEGA BAJA | 2022-08-22 16:18 | 2022-08-22 21:57 | 26 | 5:39 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22082200211 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 339 | 2022-08-22 | 8814 | keep | 0 | Aug | 2022 | 0.0060032 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CANOVANAS | 2022-08-22 16:25 | 2022-08-22 23:34 | 26 | 7:09 | P | DESGANCHE | 1 X 20 EN C/L Y 1 X 8 EN XMR DESGANCHE | R22082200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2022-08-22 | 11154 | keep | 0 | Aug | 2022 | 0.0075969 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2022-08-22 16:29 | 2022-08-22 20:18 | 50 | 3:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE LEVANTO CONDUCTOR | B22082200220 | New_Event | Primary Wire Break | Include | Include | Equipment | 229 | 2022-08-22 | 11450 | keep | 0 | Aug | 2022 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-22 16:33 | 2022-08-22 18:58 | 20 | 2:25 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO RAYOS | C22082200131 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 145 | 2022-08-22 | 2900 | keep | 0 | Aug | 2022 | 0.0019752 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-22 16:34 | 2022-08-22 18:34 | 437 | 2:00 | T | MAL TIEMPO/LLUVIA O VIENTO | SE PATRULLO MAL TIEMPO Y SE CERRO N/O CONTRA 1530-7 100% EN SERVICIO | S22082200696 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2022-08-22 | 52440 | keep | 0 | Aug | 2022 | 0.035717 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2022-08-22 16:34 | 2022-08-22 17:52 | 643 | 1:18 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PATRULLO SE ABRIO N/O AVE. DE DIEGO Y SE CERRO 1530-7 Y CONTINUAN PATRULLANDO 1530-06 | S22082200696 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 78 | 2022-08-22 | 50154 | keep | 0 | Aug | 2022 | 0.03416 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
CAGUAS | 2022-08-22 16:34 | 2022-08-22 16:35 | 1709 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | C22082200132 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-22 | 1709 | keep | 0 | Aug | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
YAUCO | 2022-08-22 16:36 | 2022-08-23 11:05 | 12 | 18:29 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO LINEA PRIMARIA 1 X 40 EN CORTE DE LINEA | P22082200158 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1109 | 2022-08-22 | 13308 | keep | 0 | Aug | 2022 | 0.009064 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-22 16:41 | 2022-08-22 16:43 | 1483 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO 30% POR 1336-08 | S22082200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-08-22 | 2966 | keep | 0 | Aug | 2022 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-08-22 16:41 | 2022-08-22 16:43 | 1531 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO 15% POR 1336-08 | S22082200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-08-22 | 3062 | keep | 0 | Aug | 2022 | 0.0020855 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2022-08-22 16:41 | 2022-08-22 16:43 | 4000 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO LLEVA 30% 1204-04 Y 15% DEL 1204-5 PARTE POR 1424-08 | S22082200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-08-22 | 8000 | keep | 0 | Aug | 2022 | 0.0054488 | 0.0027244 | Momentary | FALSE | FALSE | Not_TMED_Event | 4000
AGUADILLA | 2022-08-22 16:42 | 2022-08-22 20:15 | 70 | 3:33 | P | SOBRECARGA | 1 X 80 EN CORTE DE LINEA POR SOBRECARGA | M22082200311 | New_Event | Trip Due To Overload | Include | Include | Other | 213 | 2022-08-22 | 14910 | keep | 0 | Aug | 2022 | 0.010155 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-08-22 16:45 | 2022-08-22 18:41 | 150 | 1:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN PROVISIONAL SE REMPLAZO CAJA Y SE REPARO PUENTE ABIERTO Y 1 X 80 SUM-20 | S22082100733 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 116 | 2022-08-22 | 17400 | keep | 0 | Aug | 2022 | 0.011851 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-22 16:45 | 2022-08-22 16:46 | 3046 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR LLEVANDO 15% DEL 1647-09 EN SERVICIO | R22082200143 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-22 | 3046 | keep | 0 | Aug | 2022 | 0.0020746 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-22 16:45 | 2022-08-22 16:46 | 307 | 0:01 | P | DESGANCHE | RECERRO INTERRUPTOR 15% DE LA CARGA POR 1646-03 EN SERVICIO | R22082200143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-22 | 307 | keep | 0 | Aug | 2022 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
CANOVANAS | 2022-08-22 16:46 | 2022-08-22 17:15 | 84 | 0:29 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22082200126 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 29 | 2022-08-22 | 2436 | keep | 0 | Aug | 2022 | 0.0016591 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
CAGUAS | 2022-08-22 16:47 | 2022-08-22 16:48 | 1709 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | C22082200132 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-22 | 1709 | keep | 0 | Aug | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-08-22 16:48 | 2022-08-22 18:56 | 200 | 2:08 | P | MAL TIEMPO/RAYOS | 2 X 200 EN C/L RAYOS | C22082200135 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 128 | 2022-08-22 | 25600 | keep | 0 | Aug | 2022 | 0.017436 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-22 16:49 | 2022-08-22 16:50 | 766 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 1909-07 ESTA LLEVADO 50%DE LA CARGA 1709-03 | S22082200724 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 766 | keep | 0 | Aug | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-08-22 16:49 | 2022-08-22 16:50 | 1139 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1909-07 ESTA LLEVADO 50%DE LA CARGA 1709-03 | S22082200724 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 1139 | keep | 0 | Aug | 2022 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
FAJARDO | 2022-08-22 16:49 | 2022-08-22 19:45 | 4 | 2:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 37.5 KVA | R22082200145 | New_Event | Service Transformer Failure | Include | Include | Equipment | 176 | 2022-08-22 | 704 | keep | 0 | Aug | 2022 | 0.00047949 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-08-22 16:52 | 2022-08-23 10:20 | 187 | 17:28 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22082200136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2022-08-22 | 195976 | keep | 0 | Aug | 2022 | 0.13348 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
AGUADILLA | 2022-08-22 16:55 | 2022-08-22 22:13 | 100 | 5:18 | P | ARBOL SOBRE LINEA | 1 X 65 Y 2 X 80 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LINEAS | M22082200313 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 318 | 2022-08-22 | 31800 | keep | 0 | Aug | 2022 | 0.021659 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-22 16:55 | 2022-08-22 18:33 | 100 | 1:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO LINEAS PRIMARIAS ROTAS | M22082200268 | New_Event | Primary Wire Break | Include | Include | Equipment | 98 | 2022-08-22 | 9800 | keep | 0 | Aug | 2022 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-08-22 16:57 | 2022-08-22 17:48 | 1 | 0:51 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22082200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2022-08-22 | 51 | keep | 0 | Aug | 2022 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-08-22 17:04 | 2022-08-22 21:45 | 5 | 4:41 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO RAYOS | R22082200147 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 281 | 2022-08-22 | 1405 | keep | 0 | Aug | 2022 | 0.00095694 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-22 17:07 | 2022-08-22 20:12 | 80 | 3:05 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082200320 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 185 | 2022-08-22 | 14800 | keep | 0 | Aug | 2022 | 0.01008 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-22 17:15 | 2022-08-22 23:05 | 12 | 5:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5KVA POR 37.5KVA | M22082200323 | New_Event | Service Transformer Failure | Include | Include | Equipment | 350 | 2022-08-22 | 4200 | keep | 0 | Aug | 2022 | 0.0028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-22 17:17 | 2022-08-22 19:35 | 35 | 2:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082200248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-08-22 | 4830 | keep | 0 | Aug | 2022 | 0.0032897 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-08-22 17:20 | 2022-08-22 21:54 | 1825 | 4:34 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO INTERRUPTOR PERSONAL CONSERVACION INPECCION SE REEMPLAZO BOBINA DE TRIP Y SE ENCONTRO PROTECCION DEFECTUOSA FALTA DC EN ALIMENTADOR SE PASO CARGA AL 1118-09 CERRADO N/O CALLE LOIZA FTE. LLORENS TORRES | S22082201131 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 274 | 2022-08-22 | 500050 | keep | 0 | Aug | 2022 | 0.34058 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
VEGA BAJA | 2022-08-22 17:24 | 2022-08-23 20:41 | 60 | 27:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082200252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1637 | 2022-08-22 | 98220 | keep | 0 | Aug | 2022 | 0.066897 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-08-22 17:34 | 2022-08-22 21:18 | 50 | 3:44 | P | SECUNDARIA/DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REPARO SECUNDARIA POR DESGANCHE | P22082200191 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 224 | 2022-08-22 | 11200 | keep | 0 | Aug | 2022 | 0.0076283 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-22 17:37 | 2022-08-23 03:13 | 45 | 9:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22082200329 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 576 | 2022-08-22 | 25920 | keep | 0 | Aug | 2022 | 0.017654 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-08-22 17:37 | 2022-08-22 19:35 | 8 | 1:58 | P | DESGANCHE | SE REPARO BAJANTE DE LINEA A CAJA EN XMR Y SE DESGANCHO BAMBUA | B22082200267 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-08-22 | 944 | keep | 0 | Aug | 2022 | 0.00064295 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-22 17:38 | 2022-08-22 19:04 | 50 | 1:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P22082200171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-08-22 | 4300 | keep | 0 | Aug | 2022 | 0.0029287 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-22 17:39 | 2022-08-22 20:11 | 200 | 2:32 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA POR PUENTE PEGADO A POSTE | P22082200172 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 152 | 2022-08-22 | 30400 | keep | 0 | Aug | 2022 | 0.020705 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-22 17:52 | 2022-08-22 19:18 | 1142 | 1:26 | T | ARBOL SOBRE LINEA | SE SECCIONALIZO ARBOL SOBRE LINEAS SE CERRO INTERRUPTOR | M22082200340 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 86 | 2022-08-22 | 98212 | keep | 0 | Aug | 2022 | 0.066892 | 0.00077781 | Sustained | FALSE | FALSE | Not_TMED_Event | 1142
MAYAGÃœEZ | 2022-08-22 17:52 | 2022-08-22 17:53 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082200342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 312 | keep | 0 | Aug | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
AGUADILLA | 2022-08-22 17:54 | 2022-08-23 20:00 | 2 | 26:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082200206 | New_Event | Cutout Failure | Include | Include | Equipment | 1566 | 2022-08-22 | 3132 | keep | 0 | Aug | 2022 | 0.0021332 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-08-22 18:04 | 2022-08-22 21:09 | 58 | 3:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN AEREO PROVISIONAL MAL TIEMPO LLUVIA | R22082200157 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2022-08-22 | 10730 | keep | 0 | Aug | 2022 | 0.0073082 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-08-22 18:17 | 2022-08-23 10:15 | 280 | 15:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22082200888 | New_Event | Vegetation Contact | Include | Include | Vegetation | 958 | 2022-08-22 | 268240 | keep | 0 | Aug | 2022 | 0.1827 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
FAJARDO | 2022-08-22 18:18 | 2022-08-22 22:22 | 30 | 4:04 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22082200159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2022-08-22 | 7320 | keep | 0 | Aug | 2022 | 0.0049856 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-22 18:22 | 2022-08-23 14:00 | 6 | 19:38 | P | SECUNDARIA/DESGANCHE | SE HIZO DESGANCHE Y SE REPARO SECUNDARIA | S22082200898 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1178 | 2022-08-22 | 7068 | keep | 0 | Aug | 2022 | 0.004814 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-22 18:28 | 2022-08-23 13:48 | 30 | 19:20 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA Y SE LEVANTO PRIMARIA | S22082200907 | New_Event | Primary Wire Break | Include | Include | Equipment | 1160 | 2022-08-22 | 34800 | keep | 0 | Aug | 2022 | 0.023702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-22 18:33 | 2022-08-23 17:35 | 4 | 23:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 C/L SE REPARO LINEA PRIMARIA | M22082200382 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1382 | 2022-08-22 | 5528 | keep | 0 | Aug | 2022 | 0.0037651 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-22 18:37 | 2022-08-23 02:40 | 382 | 8:03 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO PUENTE PRIMARIO | S22082200930 | New_Event | Primary Wire Break | Include | Include | Equipment | 483 | 2022-08-22 | 184506 | keep | 0 | Aug | 2022 | 0.12567 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
BAYAMON | 2022-08-22 18:38 | 2022-08-22 18:54 | 12 | 0:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE IDENTIFICO SECUNDARIA QUEMADA Y SE VOLVIO A ENERGIZAR. SE TRABAJARA MANANA | B22082000089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 16 | 2022-08-22 | 192 | keep | 0 | Aug | 2022 | 0.00013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-22 18:41 | 2022-08-23 15:05 | 12 | 20:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PM DE 100KVA | S22082200925 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1224 | 2022-08-22 | 14688 | keep | 0 | Aug | 2022 | 0.010004 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-22 18:44 | 2022-08-23 11:14 | 41 | 16:30 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | S22082200928 | New_Event | Primary Wire Break | Include | Include | Equipment | 990 | 2022-08-22 | 40590 | keep | 0 | Aug | 2022 | 0.027646 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
SAN JUAN | 2022-08-22 18:55 | 2022-08-23 12:00 | 20 | 17:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR CAJA QUEMADA | S22082200949 | New_Event | Cutout Failure | Include | Include | Equipment | 1025 | 2022-08-22 | 20500 | keep | 0 | Aug | 2022 | 0.013962 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-22 19:05 | 2022-08-23 14:19 | 20 | 19:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA | S22082200962 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1154 | 2022-08-22 | 23080 | keep | 0 | Aug | 2022 | 0.01572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-08-22 19:07 | 2022-08-22 20:11 | 12 | 1:04 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082200285 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 64 | 2022-08-22 | 768 | keep | 0 | Aug | 2022 | 0.00052308 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-22 19:18 | 2022-08-22 20:25 | 500 | 1:07 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEAS PRIMARIAS SE CERRO MACHETES | M22082200397 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 67 | 2022-08-22 | 33500 | keep | 0 | Aug | 2022 | 0.022817 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-22 19:23 | 2022-08-23 09:57 | 50 | 14:34 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B22082200333 | New_Event | Vegetation Contact | Include | Include | Vegetation | 874 | 2022-08-22 | 43700 | keep | 0 | Aug | 2022 | 0.029764 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-22 19:28 | 2022-08-23 09:38 | 5 | 14:10 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR AVE CRUZO FASE | R22082200165 | New_Event | Animals | Include | Include | Wildlife | 850 | 2022-08-22 | 4250 | keep | 0 | Aug | 2022 | 0.0028947 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-08-22 19:29 | 2022-08-22 21:20 | 2 | 1:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22082200293 | New_Event | Primary Wire Break | Include | Include | Equipment | 111 | 2022-08-22 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-22 19:33 | 2022-08-22 19:53 | 4471 | 0:20 | P | DESGANCHE | DISPARO DE INTERRUPTOR AL CERRAR MACHETES POR RAMA DE ARBOL METIDA EN LA LINEA | B22082200195 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-08-22 | 89420 | keep | 0 | Aug | 2022 | 0.060904 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-22 19:45 | 2022-08-22 22:17 | 206 | 2:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE FASE POR APARENTE PUENTE ABIERTO EN LA LINEA. | S22082200999 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2022-08-22 | 31312 | keep | 0 | Aug | 2022 | 0.021326 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
AGUADILLA | 2022-08-22 19:46 | 2022-08-22 22:37 | 300 | 2:51 | P | TRANSFORMADOR AVERIADO | SE REALIZO AMARRE CON 7503-02 YA QUE CONVERTIDOR 13KV/4KV SE QUEMO. CARR 472 KM 1.0 EN AVENIDA ESTACION, ISABELA | A22082200297 | New_Event | Service Transformer Failure | Include | Include | Equipment | 171 | 2022-08-22 | 51300 | keep | 0 | Aug | 2022 | 0.03494 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2022-08-22 19:52 | 2022-08-22 22:05 | 35 | 2:13 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22082200170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-08-22 | 4655 | keep | 0 | Aug | 2022 | 0.0031705 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-08-22 19:53 | 2022-08-22 20:52 | 5961 | 0:59 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1713-05 POR RAMA ENCIMA DE LA LINEA SE CERRO POR SCADA SECCIONALIZANDO AVERIA. ENTRO EL 95% 1717-02 Y 50% 1713-05 | B22082200195 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-08-22 | 351699 | keep | 0 | Aug | 2022 | 0.23954 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-22 19:53 | 2022-08-22 20:52 | 865 | 0:59 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1713-05 POR RAMA ENCIMA DE LA LINEA SE CERRO POR SCADA SECCIONALIZANDO AVERIA. ENTRO EL 95% 1717-02 Y 50% 1713-05 | B22082200195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-08-22 | 51035 | keep | 0 | Aug | 2022 | 0.03476 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
SAN JUAN | 2022-08-22 20:00 | 2022-08-23 00:31 | 200 | 4:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22082201009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2022-08-22 | 54200 | keep | 0 | Aug | 2022 | 0.036915 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2022-08-22 20:07 | 2022-08-23 13:00 | 20 | 16:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22082200305 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1013 | 2022-08-22 | 20260 | keep | 0 | Aug | 2022 | 0.013799 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-08-22 20:08 | 2022-08-22 20:09 | 5069 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO INTERRUPTOR. SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P22082200200 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-22 | 5069 | keep | 0 | Aug | 2022 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
SAN JUAN | 2022-08-22 20:09 | 2022-08-23 19:06 | 14 | 22:57 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REMPLAZO 2 POSTE SECUNDARIO Y SE HIZO DESGANCHE SECUNDARIO | S22082201018 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 1377 | 2022-08-22 | 19278 | keep | 0 | Aug | 2022 | 0.01313 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2022-08-22 20:10 | 2022-08-22 20:56 | 30 | 0:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P22082200201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2022-08-22 | 1380 | keep | 0 | Aug | 2022 | 0.00093991 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-22 20:14 | 2022-08-23 17:07 | 40 | 20:53 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y 1 X 65 EN C/L | B22082200357 | New_Event | Primary Wire Break | Include | Include | Equipment | 1253 | 2022-08-22 | 50120 | keep | 0 | Aug | 2022 | 0.034137 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-22 20:19 | 2022-08-22 21:15 | 2 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO Y 2 TOMAS | S22082200146 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2022-08-22 | 112 | keep | 0 | Aug | 2022 | 7.6283e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-08-22 20:33 | 2022-08-23 19:50 | 30 | 23:17 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22082200313 | New_Event | Primary Wire Break | Include | Include | Equipment | 1397 | 2022-08-22 | 41910 | keep | 0 | Aug | 2022 | 0.028545 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-08-22 20:44 | 2022-08-22 20:45 | 1342 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE | C22082200167 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-08-22 | 1342 | keep | 0 | Aug | 2022 | 0.00091403 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-22 20:45 | 2022-08-22 21:02 | 1 | 0:17 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN RISER SE ELIMINO PARARRAYO CRUZADO | C22082000095 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 17 | 2022-08-22 | 17 | keep | 0 | Aug | 2022 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-22 20:46 | 2022-08-23 02:13 | 18 | 5:27 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | B22082200373 | New_Event | Animals | Include | Include | Wildlife | 327 | 2022-08-22 | 5886 | keep | 0 | Aug | 2022 | 0.0040089 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-08-22 20:49 | 2022-08-22 21:12 | 513 | 0:23 | P | PROTECCION DEFECTUOSA | SE RETIRA CARGA A PETICION CARLOS TORRES Y RADY RIVERA PROTECCION DEFECTUOSA NINGUN BKR. TENIA DC 20% POR 1118-10 | S22082200000 | New_Event | Protection Miscoordination | Include | Include | Other | 23 | 2022-08-22 | 11799 | keep | 0 | Aug | 2022 | 0.0080362 | 0.0003494 | Sustained | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-08-22 20:49 | 2022-08-22 21:12 | 4398 | 0:23 | T | PROTECCION DEFECTUOSA | SE RETIRA CARGA A PETICION CARLOS TORRES Y RADY RIVERA PROTECCION DEFECTUOSA NINGUN BKR. TENIA DC | S22082200000 | New_Event | Protection Miscoordination | Include | Include | Other | 23 | 2022-08-22 | 101154 | keep | 0 | Aug | 2022 | 0.068896 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2022-08-22 20:49 | 2022-08-22 21:12 | 2782 | 0:23 | T | PROTECCION DEFECTUOSA | SE RETIRA CARGA A PETICION CARLOS TORRES Y RADY RIVERA PROTECCION DEFECTUOSA NINGUN BKR. TENIA DC LLEVA 20% DEL 1111-01 | S22082200000 | New_Event | Protection Miscoordination | Include | Include | Other | 23 | 2022-08-22 | 63986 | keep | 0 | Aug | 2022 | 0.043581 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2022-08-22 20:52 | 2022-08-22 21:45 | 2980 | 0:53 | P | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS Y SE CERRO MACHETES. 100% | B22082200195 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-08-22 | 157940 | keep | 0 | Aug | 2022 | 0.10757 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-22 20:54 | 2022-08-22 20:59 | 3315 | 0:05 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR CERRAR AMARRE CON 7104-06 POR MACHETE AVERIADO EN AUXILIAR DE LINEA DEL INTERRUPTOR 7104-06 | M22082200432 | New_Event | Switch Failure | Include | Include | Equipment | 5 | 2022-08-22 | 16575 | keep | 0 | Aug | 2022 | 0.011289 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2022-08-22 20:54 | 2022-08-22 20:59 | 1718 | 0:05 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR Y SE PASO LA CARGA AL 7104-05 POR MACHETE AVERIADO EN AUXILIAR DE LINEA DEL INTERRUPTOR | M22082200433 | Additional_clients | Switch Failure | Include | Include | Equipment | 5 | 2022-08-22 | 8590 | keep | 0 | Aug | 2022 | 0.0058506 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-22 20:58 | 2022-08-23 08:50 | 4 | 11:52 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082200435 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 712 | 2022-08-22 | 2848 | keep | 0 | Aug | 2022 | 0.0019398 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-22 21:07 | 2022-08-22 23:07 | 20 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO NEUTRAL SEC | B22082200018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2022-08-22 | 2400 | keep | 0 | Aug | 2022 | 0.0016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-22 21:14 | 2022-08-23 12:13 | 74 | 14:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA FUERTE | B22082200384 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 899 | 2022-08-22 | 66526 | keep | 0 | Aug | 2022 | 0.045311 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
MAYAGÃœEZ | 2022-08-22 21:16 | 2022-08-23 11:15 | 400 | 13:59 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | M22082200440 | New_Event | Primary Wire Break | Include | Include | Equipment | 839 | 2022-08-22 | 335600 | keep | 0 | Aug | 2022 | 0.22858 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2022-08-22 21:54 | 2022-08-23 17:08 | 1 | 19:14 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO PISTOLA 1 X 50 EN RISER | S22082200573 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1154 | 2022-08-22 | 1154 | keep | 0 | Aug | 2022 | 0.00078598 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-22 22:08 | 2022-08-22 22:09 | 3699 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | R22082200000 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-08-22 | 3699 | keep | 0 | Aug | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
VEGA BAJA | 2022-08-22 22:21 | 2022-08-22 22:22 | 2791 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL INTERRUPTOR | A22082200000 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-22 | 2791 | keep | 0 | Aug | 2022 | 0.0019009 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-22 22:22 | 2022-08-22 23:22 | 25 | 1:00 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A22082200109 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 60 | 2022-08-22 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-22 22:22 | 2022-08-22 23:22 | 20 | 1:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZA POSTE PRIMARIO Y SE CIERRA C/L | A22082200109 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 60 | 2022-08-22 | 1200 | keep | 0 | Aug | 2022 | 0.00081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-22 22:23 | 2022-08-23 00:32 | 83 | 2:09 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22082200397 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-08-22 | 10707 | keep | 0 | Aug | 2022 | 0.0072925 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
UTUADO | 2022-08-22 22:47 | 2022-08-23 21:55 | 12 | 23:08 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS SI SERVCIO DEL DIA 8/22 | A22082300238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1388 | 2022-08-22 | 16656 | keep | 0 | Aug | 2022 | 0.011344 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-22 23:10 | 2022-08-22 23:11 | 3699 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | R22082200000 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-08-22 | 3699 | keep | 0 | Aug | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2022-08-22 23:11 | 2022-08-23 04:00 | 154 | 4:49 | P | ARBOL SOBRE LINEA | 2 X 100 EN C/L SE RETIRO ARBOL SOBRE LAS LINEAS | R22082200201 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 289 | 2022-08-22 | 44506 | keep | 0 | Aug | 2022 | 0.030313 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
CANOVANAS | 2022-08-22 23:18 | 2022-08-23 04:00 | 58 | 4:42 | P | DESGANCHE | SE ABRIO C/L SE RETIRO ARBOL Y 2 X 100 EN C/L | R22082200201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2022-08-22 | 16356 | keep | 0 | Aug | 2022 | 0.01114 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
AGUADILLA | 2022-08-22 23:19 | 2022-08-22 23:20 | 1417 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22082200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 1417 | keep | 0 | Aug | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
VEGA BAJA | 2022-08-22 23:22 | 2022-08-22 23:23 | 2791 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | SE DISPARO INTERRUPTOR PARA SECCIONALIZAR TRAMO AVERIADO POR LINEA PRIMARIA EN EL SUELO. SE CERRO POR SCADA | A22082200000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-22 | 2791 | keep | 0 | Aug | 2022 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2022-08-22 23:23 | 2022-08-23 00:31 | 70 | 1:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR PRIMARIO ROTO | A22082200109 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 68 | 2022-08-22 | 4760 | keep | 0 | Aug | 2022 | 0.003242 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-08-22 23:23 | 2022-08-23 13:25 | 25 | 14:02 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A22082200109 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 842 | 2022-08-22 | 21050 | keep | 0 | Aug | 2022 | 0.014337 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-22 23:23 | 2022-08-23 16:18 | 20 | 16:55 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZA POSTE PRIMARIO Y SE CIERRA C/L | A22082200109 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1015 | 2022-08-22 | 20300 | keep | 0 | Aug | 2022 | 0.013826 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-22 23:29 | 2022-08-23 00:42 | 80 | 1:13 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | S22082201153 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2022-08-22 | 5840 | keep | 0 | Aug | 2022 | 0.0039776 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-08-22 23:29 | 2022-08-22 23:30 | 653 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082200230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-22 | 653 | keep | 0 | Aug | 2022 | 0.00044476 | 0.00044476 | Momentary | FALSE | FALSE | Not_TMED_Event | 653
CAGUAS | 2022-08-23 00:03 | 2022-08-23 10:25 | 122 | 10:22 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C22082300001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 622 | 2022-08-23 | 75884 | keep | 0 | Aug | 2022 | 0.051684 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
AGUADILLA | 2022-08-23 00:12 | 2022-08-23 00:17 | 595 | 0:05 | T | NO SE REPORTO CAUSA | SE DISPARO DE INTERRUPTOR Y CERRO SOLO POR SCADA LLEVA CARGA DE 7902-02 | M22082300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-23 | 2975 | keep | 0 | Aug | 2022 | 0.0020263 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2022-08-23 00:12 | 2022-08-23 00:17 | 51 | 0:05 | T | NO SE REPORTO CAUSA | SE DISPARO DE INTERRUPTOR Y CERRO SOLO POR SCADA CARGA POR 7902-01 | M22082300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-23 | 255 | keep | 0 | Aug | 2022 | 0.00017368 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-23 00:12 | 2022-08-23 00:17 | 721 | 0:05 | T | NO SE REPORTO CAUSA | SE DISPARO INTERRUPTO Y CERRO SOLO POR SCADA EN SCADA APARECE LA OPERACION | M22082300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-23 | 3605 | keep | 0 | Aug | 2022 | 0.0024553 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
CAGUAS | 2022-08-23 00:22 | 2022-08-23 06:18 | 188 | 5:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22082300007 | New_Event | Cutout Failure | Include | Include | Equipment | 356 | 2022-08-23 | 66928 | keep | 0 | Aug | 2022 | 0.045584 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
BAYAMON | 2022-08-23 00:46 | 2022-08-23 01:27 | 60 | 0:41 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU 5 | B22082300004 | New_Event | UG Cable Fault | Include | Include | Equipment | 41 | 2022-08-23 | 2460 | keep | 0 | Aug | 2022 | 0.0016755 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-23 00:53 | 2022-08-23 01:14 | 595 | 0:21 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO SOLO POR SCADA LLEVA CARGA DE 7902-02 NO RTU | M22082300005 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-08-23 | 12495 | keep | 0 | Aug | 2022 | 0.0085103 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-23 00:53 | 2022-08-23 01:14 | 51 | 0:21 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO SOLO POR SCADA CARGA POR 7902-01 | M22082300005 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-08-23 | 1071 | keep | 0 | Aug | 2022 | 0.00072945 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-23 00:53 | 2022-08-23 01:14 | 721 | 0:21 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO SOLO SCADA APARACE LA OPERACION | M22082300005 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-08-23 | 15141 | keep | 0 | Aug | 2022 | 0.010312 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-23 01:07 | 2022-08-23 11:02 | 83 | 9:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CONVERTIDOR MAL TIEMPO LLUVIA | B22082300005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 595 | 2022-08-23 | 49385 | keep | 0 | Aug | 2022 | 0.033636 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
BARRANQUITAS | 2022-08-23 01:23 | 2022-08-23 01:24 | 2565 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | C22082300013 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-08-23 | 2565 | keep | 0 | Aug | 2022 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2022-08-23 01:24 | 2022-08-23 09:35 | 38 | 8:11 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL DE LA LINEA Y REPARAR NEUTRAL PRIMARIO Y SECUNDARIO. NO FUNDIO | C22082300047 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 491 | 2022-08-23 | 18658 | keep | 0 | Aug | 2022 | 0.012708 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CANOVANAS | 2022-08-23 01:25 | 2022-08-23 01:26 | 2708 | 0:01 | T | DESGANCHE | RECIERRE | R22082300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-23 | 2708 | keep | 0 | Aug | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-08-23 01:26 | 2022-08-23 09:34 | 50 | 8:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R22082300006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 488 | 2022-08-23 | 24400 | keep | 0 | Aug | 2022 | 0.016619 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-23 01:27 | 2022-08-23 14:34 | 25 | 13:07 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN AEREO PROVISIONAL HACIA T-33 AVERIA NUEVA T-33 HACIA T32 | B22082300020 | New_Event | UG Cable Fault | Include | Include | Equipment | 787 | 2022-08-23 | 19675 | keep | 0 | Aug | 2022 | 0.013401 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-08-23 02:07 | 2022-08-23 08:57 | 40 | 6:50 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300005 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 410 | 2022-08-23 | 16400 | keep | 0 | Aug | 2022 | 0.01117 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-23 03:06 | 2022-08-23 06:40 | 45 | 3:34 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | C22082300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2022-08-23 | 9630 | keep | 0 | Aug | 2022 | 0.0065589 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-08-23 03:33 | 2022-08-23 10:55 | 99 | 7:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22082300017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2022-08-23 | 43758 | keep | 0 | Aug | 2022 | 0.029803 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
FAJARDO | 2022-08-23 03:56 | 2022-08-23 03:57 | 1571 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22082300008 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-23 | 1571 | keep | 0 | Aug | 2022 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
FAJARDO | 2022-08-23 03:57 | 2022-08-23 09:25 | 30 | 5:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | R22082300010 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 328 | 2022-08-23 | 9840 | keep | 0 | Aug | 2022 | 0.006702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-08-23 04:05 | 2022-08-23 06:50 | 38 | 2:45 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22082300019 | New_Event | Animals | Include | Include | Wildlife | 165 | 2022-08-23 | 6270 | keep | 0 | Aug | 2022 | 0.0042705 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CAGUAS | 2022-08-23 04:42 | 2022-08-23 09:00 | 295 | 4:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHO | C22082300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2022-08-23 | 76110 | keep | 0 | Aug | 2022 | 0.051838 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
VEGA BAJA | 2022-08-23 04:55 | 2022-08-23 07:15 | 80 | 2:20 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300008 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 140 | 2022-08-23 | 11200 | keep | 0 | Aug | 2022 | 0.0076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-23 05:23 | 2022-08-23 09:21 | 50 | 3:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082300012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 238 | 2022-08-23 | 11900 | keep | 0 | Aug | 2022 | 0.008105 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-23 05:55 | 2022-08-23 13:30 | 25 | 7:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2022-08-23 | 11375 | keep | 0 | Aug | 2022 | 0.0077475 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-08-23 06:11 | 2022-08-23 09:15 | 6 | 3:04 | P | MAL TIEMPO/RAYOS | 1 X 20 EN RISER Y 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300038 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 184 | 2022-08-23 | 1104 | keep | 0 | Aug | 2022 | 0.00075193 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-08-23 06:29 | 2022-08-23 06:30 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082300033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 1352 | keep | 0 | Aug | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
VEGA BAJA | 2022-08-23 06:29 | 2022-08-23 19:40 | 50 | 13:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO PORTAFUSIBLE | B22082300021 | New_Event | Cutout Failure | Include | Include | Equipment | 791 | 2022-08-23 | 39550 | keep | 0 | Aug | 2022 | 0.026937 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-23 06:31 | 2022-08-23 11:00 | 5 | 4:29 | P | ARBOL SOBRE LINEA | 1 X 30 EN CORTE DE LINEA SE REMOVIO ARBOL DE LA LINEA | C22082300035 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 269 | 2022-08-23 | 1345 | keep | 0 | Aug | 2022 | 0.00091607 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-23 06:31 | 2022-08-23 18:10 | 4 | 11:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A22082300012 | New_Event | Primary Wire Break | Include | Include | Equipment | 699 | 2022-08-23 | 2796 | keep | 0 | Aug | 2022 | 0.0019043 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-23 06:42 | 2022-08-23 10:45 | 26 | 4:03 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA Y PISTOLA BUSHING DE TRANSFORMADOR | R22082300017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 243 | 2022-08-23 | 6318 | keep | 0 | Aug | 2022 | 0.0043032 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-08-23 06:45 | 2022-08-23 15:25 | 40 | 8:40 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | S22082300033 | New_Event | Animals | Include | Include | Wildlife | 520 | 2022-08-23 | 20800 | keep | 0 | Aug | 2022 | 0.014167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-23 06:49 | 2022-08-23 09:25 | 91 | 2:36 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA POR SOBRECARGA | P22082300037 | New_Event | Trip Due To Overload | Include | Include | Other | 156 | 2022-08-23 | 14196 | keep | 0 | Aug | 2022 | 0.0096688 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
CAGUAS | 2022-08-23 06:50 | 2022-08-23 06:51 | 1879 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22082300040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 1879 | keep | 0 | Aug | 2022 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
BARRANQUITAS | 2022-08-23 06:50 | 2022-08-23 07:19 | 14 | 0:29 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO HOT CLAMP EN PUENTE PRIMARIO A CAJA DE TRANSFORMADOR | C22082300039 | New_Event | Primary Wire Break | Include | Include | Equipment | 29 | 2022-08-23 | 406 | keep | 0 | Aug | 2022 | 0.00027652 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2022-08-23 06:53 | 2022-08-23 11:25 | 50 | 4:32 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300014 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 272 | 2022-08-23 | 13600 | keep | 0 | Aug | 2022 | 0.0092629 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-23 06:58 | 2022-08-23 10:45 | 25 | 3:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082300016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-08-23 | 5675 | keep | 0 | Aug | 2022 | 0.0038652 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-08-23 07:11 | 2022-08-23 07:12 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22082300045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 676 | keep | 0 | Aug | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
BARRANQUITAS | 2022-08-23 07:13 | 2022-08-23 13:02 | 15 | 5:49 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B22082300024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2022-08-23 | 5235 | keep | 0 | Aug | 2022 | 0.0035655 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-23 07:29 | 2022-08-23 10:42 | 1 | 3:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R22082300020 | New_Event | Cutout Failure | Include | Include | Equipment | 193 | 2022-08-23 | 193 | keep | 0 | Aug | 2022 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-23 07:31 | 2022-08-23 10:53 | 20 | 3:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22082300029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-08-23 | 4040 | keep | 0 | Aug | 2022 | 0.0027516 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-08-23 07:38 | 2022-08-23 10:45 | 8 | 3:07 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082300020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-08-23 | 1496 | keep | 0 | Aug | 2022 | 0.0010189 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-23 07:40 | 2022-08-23 08:55 | 100 | 1:15 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300002 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-08-23 | 7500 | keep | 0 | Aug | 2022 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-23 07:48 | 2022-08-23 13:00 | 1 | 5:12 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082300032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 312 | 2022-08-23 | 312 | keep | 0 | Aug | 2022 | 0.0002125 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-23 07:50 | 2022-08-23 15:00 | 60 | 7:10 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE RETIRO ARBOL SOBRE LINEAS | A22082300024 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 430 | 2022-08-23 | 25800 | keep | 0 | Aug | 2022 | 0.017572 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-23 07:53 | 2022-08-23 11:43 | 122 | 3:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO CAUSA | R22082300025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2022-08-23 | 28060 | keep | 0 | Aug | 2022 | 0.019112 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
AGUADILLA | 2022-08-23 08:01 | 2022-08-23 17:35 | 8 | 9:34 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 25 KVA X 37.5 KVA | M22082300038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 574 | 2022-08-23 | 4592 | keep | 0 | Aug | 2022 | 0.0031276 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-23 08:09 | 2022-08-23 08:10 | 2092 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22082300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 2092 | keep | 0 | Aug | 2022 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
VEGA BAJA | 2022-08-23 08:11 | 2022-08-23 09:55 | 8 | 1:44 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300029 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2022-08-23 | 832 | keep | 0 | Aug | 2022 | 0.00056667 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-23 08:17 | 2022-08-23 08:18 | 4641 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | M22082300045 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2022-08-23 | 4641 | keep | 0 | Aug | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2022-08-23 08:18 | 2022-08-23 14:40 | 1 | 6:22 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 3 X 25 SMU EN SU CONTAMINACION | M22082300076 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 382 | 2022-08-23 | 382 | keep | 0 | Aug | 2022 | 0.00026018 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-23 08:22 | 2022-08-23 11:18 | 24 | 2:56 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22082300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-08-23 | 4224 | keep | 0 | Aug | 2022 | 0.0028769 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
AGUADILLA | 2022-08-23 08:37 | 2022-08-23 10:43 | 6 | 2:06 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082300053 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 126 | 2022-08-23 | 756 | keep | 0 | Aug | 2022 | 0.00051491 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-23 09:00 | 2022-08-23 09:35 | 5 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22082200443 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-08-23 | 175 | keep | 0 | Aug | 2022 | 0.00011919 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-08-23 09:01 | 2022-08-23 13:00 | 8 | 3:59 | P | SECUNDARIA/OTROS | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR Y SE REEMPLAZO 2 PEDESTALES Y SE REPARO SECUNDARIA | C22082300071 | New_Event |  |  |  |  | 239 | 2022-08-23 | 1912 | keep | 0 | Aug | 2022 | 0.0013023 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-23 09:01 | 2022-08-23 17:10 | 14 | 8:09 | P | MAL TIEMPO/RAYOS | 1 X 20 EN XMR DESCARGAS ELECTRICAS | M22082300059 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 489 | 2022-08-23 | 6846 | keep | 0 | Aug | 2022 | 0.0046628 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-08-23 09:15 | 2022-08-23 17:45 | 1 | 8:30 | P | NO SE REPORTO CAUSA | 1 X 25 EN SU 2 HACIA BOMBAS AAA | B22082300049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 510 | 2022-08-23 | 510 | keep | 0 | Aug | 2022 | 0.00034736 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-23 09:22 | 2022-08-23 11:17 | 1 | 1:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22082300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-08-23 | 115 | keep | 0 | Aug | 2022 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-23 09:33 | 2022-08-23 20:20 | 10 | 10:47 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082300055 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 647 | 2022-08-23 | 6470 | keep | 0 | Aug | 2022 | 0.0044067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-23 09:43 | 2022-08-23 16:20 | 35 | 6:37 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | S22082300033 | New_Event | Animals | Include | Include | Wildlife | 397 | 2022-08-23 | 13895 | keep | 0 | Aug | 2022 | 0.0094638 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-08-23 09:44 | 2022-08-23 20:00 | 50 | 10:16 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300058 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 616 | 2022-08-23 | 30800 | keep | 0 | Aug | 2022 | 0.020978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-23 09:50 | 2022-08-23 14:33 | 1 | 4:43 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22082300053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2022-08-23 | 283 | keep | 0 | Aug | 2022 | 0.00019275 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-23 10:00 | 2022-08-23 11:18 | 23 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-30 NO CAUSA | R22082300042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-08-23 | 1794 | keep | 0 | Aug | 2022 | 0.0012219 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-08-23 10:01 | 2022-08-23 16:00 | 10 | 5:59 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REALIZO DESGANCHE SECUNDARIO Y SE REMPLAZO SECUNDARIA | B22081900512 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 359 | 2022-08-23 | 3590 | keep | 0 | Aug | 2022 | 0.0024451 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-23 10:07 | 2022-08-24 16:38 | 10 | 30:31 | P | CAUSAS EXTERNAS | SE REPARO SECUNDARIA CAMION EXTERNO TUMBO SECUNDARIA | B22082300055 | New_Event | Damage From Public | Include | Include | Public | 1831 | 2022-08-23 | 18310 | keep | 0 | Aug | 2022 | 0.012471 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-23 10:08 | 2022-08-23 17:45 | 8 | 7:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | M22082300078 | New_Event | Cutout Failure | Include | Include | Equipment | 457 | 2022-08-23 | 3656 | keep | 0 | Aug | 2022 | 0.0024901 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-23 10:09 | 2022-08-23 13:23 | 53 | 3:14 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | P22082300053 | New_Event | Animals | Include | Include | Wildlife | 194 | 2022-08-23 | 10282 | keep | 0 | Aug | 2022 | 0.007003 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
CANOVANAS | 2022-08-23 10:16 | 2022-08-23 12:29 | 25 | 2:13 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R22082300036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2022-08-23 | 3325 | keep | 0 | Aug | 2022 | 0.0022646 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-23 10:23 | 2022-08-23 14:44 | 80 | 4:21 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | M22082300082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2022-08-23 | 20880 | keep | 0 | Aug | 2022 | 0.014221 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-08-23 10:29 | 2022-08-23 17:18 | 4 | 6:49 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO POSTE SECUNDARIO | C22082300080 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 409 | 2022-08-23 | 1636 | keep | 0 | Aug | 2022 | 0.0011143 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-08-23 10:35 | 2022-08-23 16:50 | 9 | 6:15 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300064 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 375 | 2022-08-23 | 3375 | keep | 0 | Aug | 2022 | 0.0022987 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-08-23 10:37 | 2022-08-23 13:46 | 50 | 3:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22082300065 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 189 | 2022-08-23 | 9450 | keep | 0 | Aug | 2022 | 0.0064364 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-23 10:42 | 2022-08-23 10:43 | 7621 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | R22082300000 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-23 | 7621 | keep | 0 | Aug | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2022-08-23 10:43 | 2022-08-23 14:17 | 1 | 3:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R22082300020 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 214 | 2022-08-23 | 214 | keep | 0 | Aug | 2022 | 0.00014575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-23 10:45 | 2022-08-23 16:35 | 15 | 5:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DE TRANSFORMADOR SE CAMBIO TRANSFORMADOR A POSTE NUEVO EXISTENTE Y SE REEMPLAZO 20 PIES DE SECUNDARIA | C22082300083 | New_Event | Primary Pole Failure | Include | Include | Equipment | 350 | 2022-08-23 | 5250 | keep | 0 | Aug | 2022 | 0.0035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-08-23 10:45 | 2022-08-23 12:10 | 5 | 1:25 | P | DESGANCHE | 2 X 20 EN MONTURA TRIFASICA POR DESGANCHE | P22082300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-23 | 425 | keep | 0 | Aug | 2022 | 0.00028947 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-08-23 10:59 | 2022-08-23 13:42 | 1 | 2:43 | P | NO SE REPORTO CAUSA | 1 X 15 SUM-20 | R22082300043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2022-08-23 | 163 | keep | 0 | Aug | 2022 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-23 11:01 | 2022-08-23 14:01 | 30 | 3:00 | P | NO SE REPORTO CAUSA | 1 X 100 SUM-20 NO CAUSA | S22082300138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-08-23 | 5400 | keep | 0 | Aug | 2022 | 0.0036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-23 11:03 | 2022-08-23 15:20 | 30 | 4:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L Y 1 X 10 EN XMR DESCARGAS ELECTRICAS | M22082300088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 257 | 2022-08-23 | 7710 | keep | 0 | Aug | 2022 | 0.0052512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-23 11:10 | 2022-08-23 14:48 | 80 | 3:38 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22082300140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2022-08-23 | 17440 | keep | 0 | Aug | 2022 | 0.011878 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-23 11:22 | 2022-08-23 14:49 | 8 | 3:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA EN PEDESTAL | R22082300045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 207 | 2022-08-23 | 1656 | keep | 0 | Aug | 2022 | 0.0011279 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-23 11:22 | 2022-08-23 17:18 | 2 | 5:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P22082300064 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 356 | 2022-08-23 | 712 | keep | 0 | Aug | 2022 | 0.00048494 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-23 11:28 | 2022-08-23 12:37 | 25 | 1:09 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S22082300072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-08-23 | 1725 | keep | 0 | Aug | 2022 | 0.0011749 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-23 11:37 | 2022-08-24 09:30 | 15 | 21:53 | P | ANIMAL | 1 X 15 EN CORTE DE LINEA SE RETIRO IGUANA | A22082300249 | New_Event | Animals | Include | Include | Wildlife | 1313 | 2022-08-23 | 19695 | keep | 0 | Aug | 2022 | 0.013414 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-23 11:39 | 2022-08-23 16:43 | 20 | 5:04 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO POSTE IMPACTADO POR CAMION Y SE REEMPLAZO 40 PIES DE SECUNDARIA | C22082300091 | New_Event | Damage From Public | Include | Include | Public | 304 | 2022-08-23 | 6080 | keep | 0 | Aug | 2022 | 0.0041411 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-23 11:42 | 2022-08-23 13:46 | 50 | 2:04 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B22082300075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-08-23 | 6200 | keep | 0 | Aug | 2022 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-23 11:45 | 2022-08-23 13:40 | 1879 | 1:55 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE RESETIO BANDERA EN EL DPU Y SE CERRO POR CONTROL | C22082300096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-08-23 | 216085 | keep | 0 | Aug | 2022 | 0.14717 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
PONCE | 2022-08-23 11:45 | 2022-08-23 12:10 | 12 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON CONEXIONES SECUNDARIAS EN PEDESTAL | P22082300051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-08-23 | 300 | keep | 0 | Aug | 2022 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-23 11:50 | 2022-08-23 16:10 | 1 | 4:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C22082300097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 260 | 2022-08-23 | 260 | keep | 0 | Aug | 2022 | 0.00017708 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-23 11:50 | 2022-08-23 17:50 | 1 | 6:00 | P | ANIMAL | 1 X 30 EN RISER Y 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C22082300146 | New_Event | Animals | Include | Include | Wildlife | 360 | 2022-08-23 | 360 | keep | 0 | Aug | 2022 | 0.00024519 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-23 12:00 | 2022-08-23 12:20 | 12 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL Y LA TAPA | C22082300101 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-08-23 | 240 | keep | 0 | Aug | 2022 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-23 12:15 | 2022-08-23 15:33 | 10 | 3:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR PORTAFUSIBLE | S22082300160 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2022-08-23 | 1980 | keep | 0 | Aug | 2022 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-23 12:16 | 2022-08-23 18:09 | 5 | 5:53 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B22082300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2022-08-23 | 1765 | keep | 0 | Aug | 2022 | 0.0012021 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-08-23 12:17 | 2022-08-23 14:00 | 100 | 1:43 | P | SOBRECARGA | 1 X 200 EN CORTE DE LINEA POR CARGA | P22082300067 | New_Event | Trip Due To Overload | Include | Include | Other | 103 | 2022-08-23 | 10300 | keep | 0 | Aug | 2022 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-23 12:27 | 2022-08-23 12:28 | 2201 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6900 | A22082300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 2201 | keep | 0 | Aug | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-08-23 12:27 | 2022-08-23 12:28 | 1986 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6900 | A22082300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 1986 | keep | 0 | Aug | 2022 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2022-08-23 12:27 | 2022-08-23 12:28 | 199 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6900 | A22082300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 199 | keep | 0 | Aug | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2022-08-23 12:27 | 2022-08-23 12:28 | 24 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 6900 | A22082300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 24 | keep | 0 | Aug | 2022 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2022-08-23 12:28 | 2022-08-23 12:29 | 2201 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR EN OPERACION LINEA 6900 | A22082300095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 2201 | keep | 0 | Aug | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
AGUADILLA | 2022-08-23 12:31 | 2022-08-23 12:32 | 1827 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR LINEA PRIMARIA PARTIDA | M22082300111 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-23 | 1827 | keep | 0 | Aug | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
VEGA BAJA | 2022-08-23 12:39 | 2022-08-23 14:12 | 82 | 1:33 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | B22082300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-08-23 | 7626 | keep | 0 | Aug | 2022 | 0.005194 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
CANOVANAS | 2022-08-23 12:40 | 2022-08-23 13:24 | 2106 | 0:44 | T | NO SE REPORTO CAUSA | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR SE CERRO INTERRUPTOR 70% EN SERVICIO | R22082300058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2022-08-23 | 92664 | keep | 0 | Aug | 2022 | 0.063113 | 0.0014344 | Sustained | FALSE | FALSE | Not_TMED_Event | 2106
BARRANQUITAS | 2022-08-23 12:40 | 2022-08-23 12:41 | 2192 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22082300113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 2192 | keep | 0 | Aug | 2022 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
AGUADILLA | 2022-08-23 12:49 | 2022-08-23 15:40 | 60 | 2:51 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082300117 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 171 | 2022-08-23 | 10260 | keep | 0 | Aug | 2022 | 0.006988 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-23 12:50 | 2022-08-23 13:15 | 1 | 0:25 | P | MAL TIEMPO/RAYOS | 2 X 40 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | A22082300114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 25 | 2022-08-23 | 25 | keep | 0 | Aug | 2022 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-23 12:51 | 2022-08-23 15:00 | 11 | 2:09 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR NO SE PUDO REGULAR EL VOLTAJE, REQUIERE REEMPLAZO DE XMR | C22082300114 | New_Event | Service Transformer Failure | Include | Include | Equipment | 129 | 2022-08-23 | 1419 | keep | 0 | Aug | 2022 | 0.00096647 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2022-08-23 12:54 | 2022-08-23 14:30 | 10 | 1:36 | P | MAL TIEMPO/RAYOS | 1 X 30 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300105 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 96 | 2022-08-23 | 960 | keep | 0 | Aug | 2022 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-23 12:57 | 2022-08-23 16:58 | 4 | 4:01 | P | TRANSFORMADOR AVERIADO | ABRIR CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA, PERO ESTA DEFECTUOSO TRASPATIO Y SE RELOCALIZO SECUNDARIA | C22082300160 | New_Event | Service Transformer Failure | Include | Include | Equipment | 241 | 2022-08-23 | 964 | keep | 0 | Aug | 2022 | 0.00065658 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-08-23 12:57 | 2022-08-23 15:00 | 15 | 2:03 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | M22082300121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-08-23 | 1845 | keep | 0 | Aug | 2022 | 0.0012566 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-23 13:00 | 2022-08-23 14:00 | 5 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22082300074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-08-23 | 300 | keep | 0 | Aug | 2022 | 0.00020433 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-08-23 13:01 | 2022-08-23 16:20 | 50 | 3:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-08-23 | 9950 | keep | 0 | Aug | 2022 | 0.0067769 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-08-23 13:03 | 2022-08-23 14:22 | 442 | 1:19 | P | CAUSAS EXTERNAS | 2 X 100 EN CORTE DE LINEA VEHICULO IMPACTO POSTE Y CRUZO LOS ALAMBRE | C22082300116 | New_Event | Damage From Public | Include | Include | Public | 79 | 2022-08-23 | 34918 | keep | 0 | Aug | 2022 | 0.023782 | 0.00030104 | Sustained | FALSE | FALSE | Not_TMED_Event | 442
UTUADO | 2022-08-23 13:09 | 2022-08-23 18:55 | 1 | 5:46 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300116 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 346 | 2022-08-23 | 346 | keep | 0 | Aug | 2022 | 0.00023566 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-23 13:10 | 2022-08-23 18:54 | 5 | 5:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C22082300121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 344 | 2022-08-23 | 1720 | keep | 0 | Aug | 2022 | 0.0011715 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-23 13:12 | 2022-08-23 14:03 | 1827 | 0:51 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | M22082300124 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 51 | 2022-08-23 | 93177 | keep | 0 | Aug | 2022 | 0.063462 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2022-08-23 13:13 | 2022-08-23 18:44 | 82 | 5:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C22082300122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2022-08-23 | 27142 | keep | 0 | Aug | 2022 | 0.018486 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
SAN JUAN | 2022-08-23 13:20 | 2022-08-23 14:21 | 250 | 1:01 | P | NO SE REPORTO CAUSA | SE ENCONTRO SECUNDARIO PORTATIL 8 FUERA SE VERIFICO BANDERA Y SE PROBO QUEDO EN SERVICIO INTERRUPTOR LLEVA 20% DE SU CARGA | S22082300185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-08-23 | 15250 | keep | 0 | Aug | 2022 | 0.010387 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-08-23 13:20 | 2022-08-23 14:21 | 1290 | 1:01 | S | NO SE REPORTO CAUSA | SE ENCONTRO SECUNDARIO PORTATIL 8 FUERA SE VERIFICO BANDERA Y SE PROBO QUEDO EN SERVICIO | S22082300185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2022-08-23 | 78690 | keep | 0 | Aug | 2022 | 0.053595 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
ARECIBO | 2022-08-23 13:21 | 2022-08-23 13:22 | 1883 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22082300118 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-23 | 1883 | keep | 0 | Aug | 2022 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | Not_TMED_Event | 1883
ARECIBO | 2022-08-23 13:21 | 2022-08-23 13:22 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22082300119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 3431 | keep | 0 | Aug | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-08-23 13:22 | 2022-08-23 16:05 | 18 | 2:43 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300162 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 163 | 2022-08-23 | 2934 | keep | 0 | Aug | 2022 | 0.0019983 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-08-23 13:23 | 2022-08-23 15:00 | 100 | 1:37 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300120 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 97 | 2022-08-23 | 9700 | keep | 0 | Aug | 2022 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-23 13:24 | 2022-08-23 13:46 | 2000 | 0:22 | P | NO SE REPORTO CAUSA | SE ABRIO SU-A2A Y SE CERRO MACHETE 90% EN SERVICIO | R22082300058 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 22 | 2022-08-23 | 44000 | keep | 0 | Aug | 2022 | 0.029968 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-23 13:27 | 2022-08-23 14:33 | 12 | 1:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA 1 X 10 EN TRANSFORMADOR | P22082300078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 66 | 2022-08-23 | 792 | keep | 0 | Aug | 2022 | 0.00053943 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-23 13:33 | 2022-08-23 16:10 | 60 | 2:37 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B22082300098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-08-23 | 9420 | keep | 0 | Aug | 2022 | 0.0064159 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-23 13:34 | 2022-08-23 14:45 | 867 | 1:11 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR NO HAY RTU SE COLOCO INTERRUPTOR EN SERVICIO | M22082300129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 71 | 2022-08-23 | 61557 | keep | 0 | Aug | 2022 | 0.041926 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
UTUADO | 2022-08-23 13:34 | 2022-08-23 21:30 | 7 | 7:56 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300123 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 476 | 2022-08-23 | 3332 | keep | 0 | Aug | 2022 | 0.0022694 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-08-23 13:38 | 2022-08-23 15:22 | 60 | 1:44 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300117 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2022-08-23 | 6240 | keep | 0 | Aug | 2022 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-23 13:38 | 2022-08-23 15:15 | 4 | 1:37 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300125 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 97 | 2022-08-23 | 388 | keep | 0 | Aug | 2022 | 0.00026427 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-08-23 13:44 | 2022-08-23 18:00 | 80 | 4:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | P22082300129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-08-23 | 20480 | keep | 0 | Aug | 2022 | 0.013949 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-23 13:46 | 2022-08-23 14:39 | 106 | 0:53 | P | NO SE REPORTO CAUSA | SE CORRIO EL LAZO, CERRO EN SU -A2A, NO SE ENCONTRO CAUSA | R22082300058 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 53 | 2022-08-23 | 5618 | keep | 0 | Aug | 2022 | 0.0038264 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-23 13:46 | 2022-08-23 15:02 | 8 | 1:16 | P | CAUSAS EXTERNAS | 2 X 15 EN MONTURA TRIFASICA Y SE REPARO SECUNDARIA AVERIADA POR CAMION | P22082300083 | New_Event | Damage From Public | Include | Include | Public | 76 | 2022-08-23 | 608 | keep | 0 | Aug | 2022 | 0.00041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-23 13:48 | 2022-08-23 14:08 | 2 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22082300130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-08-23 | 40 | keep | 0 | Aug | 2022 | 2.7244e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-08-23 13:50 | 2022-08-23 15:35 | 60 | 1:45 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300131 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 105 | 2022-08-23 | 6300 | keep | 0 | Aug | 2022 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-23 13:58 | 2022-08-23 15:53 | 1 | 1:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN C/L LLUVIAS FUERTES | R22082300068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 115 | 2022-08-23 | 115 | keep | 0 | Aug | 2022 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-23 14:03 | 2022-08-23 17:40 | 486 | 3:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | M22082300148 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 217 | 2022-08-23 | 105462 | keep | 0 | Aug | 2022 | 0.07183 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-23 14:03 | 2022-08-23 18:45 | 40 | 4:42 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082300144 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 282 | 2022-08-23 | 11280 | keep | 0 | Aug | 2022 | 0.0076828 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-23 14:05 | 2022-08-23 18:25 | 11 | 4:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REEMPALZO AISLADOR | C22082300134 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 260 | 2022-08-23 | 2860 | keep | 0 | Aug | 2022 | 0.0019479 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-08-23 14:06 | 2022-08-24 10:10 | 150 | 20:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR | A22082300137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1204 | 2022-08-23 | 180600 | keep | 0 | Aug | 2022 | 0.12301 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-23 14:13 | 2022-08-23 14:14 | 390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | M22082300155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-08-23 14:19 | 2022-08-23 14:20 | 681 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1530-09 | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 681 | keep | 0 | Aug | 2022 | 0.00046383 | 0.00046383 | Momentary | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-08-23 14:19 | 2022-08-23 14:20 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1520-02 | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 1310 | keep | 0 | Aug | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-08-23 14:20 | 2022-08-23 18:38 | 20 | 4:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50 KVA | S22082200962 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 258 | 2022-08-23 | 5160 | keep | 0 | Aug | 2022 | 0.0035145 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-23 14:29 | 2022-08-23 14:30 | 2178 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22082300000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-23 | 2178 | keep | 0 | Aug | 2022 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
MAYAGÃœEZ | 2022-08-23 14:29 | 2022-08-23 17:30 | 10 | 3:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22082300168 | New_Event | Secondary Wire Break | Include | Include | Equipment | 181 | 2022-08-23 | 1810 | keep | 0 | Aug | 2022 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-23 14:30 | 2022-08-23 18:09 | 384 | 3:39 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22082300143 | 1st_after_momentary | Animals | Include | Include | Wildlife | 219 | 2022-08-23 | 84096 | keep | 0 | Aug | 2022 | 0.057277 | 0.00026154 | Sustained | FALSE | FALSE | Not_TMED_Event | 384
SAN JUAN | 2022-08-23 14:33 | 2022-08-23 14:34 | 414 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO LLEVA 30% DE SU CARGA SE PROBO QUEDO EN SERVICIO | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 414 | keep | 0 | Aug | 2022 | 0.00028197 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
BAYAMON | 2022-08-23 14:34 | 2022-08-24 00:38 | 8 | 10:04 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL HACIA T-32 POR TRAMO AVERIADO | B22082300020 | New_Event | UG Cable Fault | Include | Include | Equipment | 604 | 2022-08-23 | 4832 | keep | 0 | Aug | 2022 | 0.0032911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-23 14:42 | 2022-08-23 18:38 | 79 | 3:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C22082300141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-08-23 | 18644 | keep | 0 | Aug | 2022 | 0.012698 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2022-08-23 14:44 | 2022-08-23 19:37 | 403 | 4:53 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO 6 MACHETES QUEMADOS SU CARGA POR 1336-06 LA CARGA DEL 1336-6 NO SE AFECTO POR QUE SE TRANSFIRIO AL 1657-02 | S22082300000 | New_Event | Switch Failure | Include | Include | Equipment | 293 | 2022-08-23 | 118079 | keep | 0 | Aug | 2022 | 0.080423 | 0.00027448 | Sustained | FALSE | FALSE | Not_TMED_Event | 403
AGUADILLA | 2022-08-23 14:45 | 2022-08-23 16:36 | 15 | 1:51 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082300164 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 111 | 2022-08-23 | 1665 | keep | 0 | Aug | 2022 | 0.001134 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-23 14:46 | 2022-08-23 17:58 | 150 | 3:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO PORTAFUSIBLE | B22082300106 | New_Event | Cutout Failure | Include | Include | Equipment | 192 | 2022-08-23 | 28800 | keep | 0 | Aug | 2022 | 0.019616 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-23 15:01 | 2022-08-23 16:54 | 40 | 1:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | S22082300228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2022-08-23 | 4520 | keep | 0 | Aug | 2022 | 0.0030786 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-23 15:02 | 2022-08-23 15:03 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22082300170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 3458 | keep | 0 | Aug | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
BAYAMON | 2022-08-23 15:05 | 2022-08-23 16:42 | 1 | 1:37 | P | MAL TIEMPO/RAYOS | 2 X 40 EN C/L MAL TIEMPO RAYOS | S22082300230 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 97 | 2022-08-23 | 97 | keep | 0 | Aug | 2022 | 6.6066e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-23 15:11 | 2022-08-23 19:00 | 25 | 3:49 | P | ARBOL SOBRE LINEA | SE ABRIO C/L PARA RETIRAR ARBOL SOBRE PRIMARIA | B22082300113 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 229 | 2022-08-23 | 5725 | keep | 0 | Aug | 2022 | 0.0038993 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-08-23 15:13 | 2022-08-23 15:39 | 1 | 0:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R22082300084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 26 | 2022-08-23 | 26 | keep | 0 | Aug | 2022 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-23 15:14 | 2022-08-23 18:10 | 20 | 2:56 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | A22082300170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-08-23 | 3520 | keep | 0 | Aug | 2022 | 0.0023975 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-23 15:17 | 2022-08-23 16:32 | 8679 | 1:15 | P | DESGANCHE | DISPARO SE RETIRO RAMA SOBRE LINEA CON VARETA DE PISO Y SE CERRO INTERRUPTOR 85% POR 1206-03 | S22082300234 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-08-23 | 650925 | keep | 0 | Aug | 2022 | 0.44334 | 0.0059112 | Sustained | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-08-23 15:17 | 2022-08-23 16:32 | 2893 | 1:15 | P | DESGANCHE | DISPARO SE RETIRO RAMA SOBRE LINEA CON VARETA DE PISO Y SE CERRO INTERRUPTOR LLEVA 85% DEL 1204-05 Y 10% DE SU CARGA POR 1620-02 | S22082300234 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2022-08-23 | 216975 | keep | 0 | Aug | 2022 | 0.14778 | 0.0019704 | Sustained | FALSE | FALSE | Not_TMED_Event | 2893
VEGA BAJA | 2022-08-23 15:17 | 2022-08-23 17:16 | 60 | 1:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082300166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-08-23 | 7140 | keep | 0 | Aug | 2022 | 0.004863 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-23 15:17 | 2022-08-23 16:48 | 12 | 1:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON CONEXIONES SULFATADAS Y SE REMPLAZO SECUNDARIA ROTA | B22082300110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 91 | 2022-08-23 | 1092 | keep | 0 | Aug | 2022 | 0.00074376 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-23 15:24 | 2022-08-23 17:08 | 25 | 1:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22082300236 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-08-23 | 2600 | keep | 0 | Aug | 2022 | 0.0017708 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-23 15:31 | 2022-08-23 15:34 | 1403 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22082300150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-23 | 4209 | keep | 0 | Aug | 2022 | 0.0028667 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
BAYAMON | 2022-08-23 15:33 | 2022-08-23 16:22 | 2 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE LEVANTO SECUNDARIA Y TOMA | B22082300103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2022-08-23 | 98 | keep | 0 | Aug | 2022 | 6.6747e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-08-23 15:41 | 2022-08-23 18:25 | 163 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | C22082300155 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2022-08-23 | 26732 | keep | 0 | Aug | 2022 | 0.018207 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
CANOVANAS | 2022-08-23 15:47 | 2022-08-23 17:03 | 1 | 1:16 | P | DESGANCHE | 1 X 20 EN RISER DESGANCHO Y REMPLAZO CAJA QUEMADA | R22082300086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-08-23 | 76 | keep | 0 | Aug | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-23 15:54 | 2022-08-23 17:01 | 2 | 1:07 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE REMPLAZO SECUNDARIA ABIERTA CRUZADA | B22082300116 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 67 | 2022-08-23 | 134 | keep | 0 | Aug | 2022 | 9.1267e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-08-23 15:54 | 2022-08-23 17:13 | 10 | 1:19 | P | CRUCETA DEFECTUOSA O AVERIADA | SE CONSTRUYO EN VERTICAL Y SE LLEVO ALAMBRE A AISLADOR | P22082300096 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 79 | 2022-08-23 | 790 | keep | 0 | Aug | 2022 | 0.00053807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-23 15:55 | 2022-08-23 16:00 | 1483 | 0:05 | P | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA SE PROBO QUEDO EN SERVICIO 30% POR 1336-08 | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-23 | 7415 | keep | 0 | Aug | 2022 | 0.0050503 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-08-23 15:55 | 2022-08-23 16:00 | 1531 | 0:05 | P | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA SE PROBO QUEDO EN SERVICIO 15% POR 1336-08 | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-23 | 7655 | keep | 0 | Aug | 2022 | 0.0052138 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2022-08-23 15:55 | 2022-08-23 16:00 | 4496 | 0:05 | P | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL FUERA SE PROBO QUEDO EN SERVICIO LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 Y PARTE DE SU CARGA POR 1424-08 | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-23 | 22480 | keep | 0 | Aug | 2022 | 0.015311 | 0.0030622 | Momentary | FALSE | FALSE | Not_TMED_Event | 4496
SAN JUAN | 2022-08-23 15:56 | 2022-08-23 20:50 | 8 | 4:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S22082300241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-08-23 | 2352 | keep | 0 | Aug | 2022 | 0.0016019 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-23 15:56 | 2022-08-24 09:38 | 25 | 17:42 | P | ANIMAL | 1 X 10 EN XMR Y 1 X 20 EN C/L AVE | B22082300117 | New_Event | Animals | Include | Include | Wildlife | 1062 | 2022-08-23 | 26550 | keep | 0 | Aug | 2022 | 0.018083 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-23 15:58 | 2022-08-24 08:00 | 65 | 16:02 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C22082300157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 962 | 2022-08-23 | 62530 | keep | 0 | Aug | 2022 | 0.042589 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
FAJARDO | 2022-08-23 15:59 | 2022-08-23 17:12 | 6 | 1:13 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR CLIENTE DESGANCHANDO | R22082300087 | New_Event | Damage From Public | Include | Include | Public | 73 | 2022-08-23 | 438 | keep | 0 | Aug | 2022 | 0.00029832 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-23 16:00 | 2022-08-23 17:40 | 12 | 1:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PM DE 100KVA | S22082200925 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 100 | 2022-08-23 | 1200 | keep | 0 | Aug | 2022 | 0.00081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-23 16:12 | 2022-08-23 20:25 | 10 | 4:13 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300182 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 253 | 2022-08-23 | 2530 | keep | 0 | Aug | 2022 | 0.0017232 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-23 16:14 | 2022-08-23 17:44 | 1106 | 1:30 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEA CON VARETA DE PISO Y SE CERRO MACHETE 60% POR 1529-15 | S22082300260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-08-23 | 99540 | keep | 0 | Aug | 2022 | 0.067796 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
GUAYAMA | 2022-08-23 16:14 | 2022-08-23 18:00 | 30 | 1:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22082300101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-08-23 | 3180 | keep | 0 | Aug | 2022 | 0.0021659 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-08-23 16:19 | 2022-08-23 18:50 | 145 | 2:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA DEFECTUOSA A ESPUELA, SE DEJO EN SERVICIO. SE REEMPLAZARA MAÃ‘ANA | C22082300163 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2022-08-23 | 21895 | keep | 0 | Aug | 2022 | 0.014913 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
BAYAMON | 2022-08-23 16:19 | 2022-08-23 18:31 | 10 | 2:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES EN BAJANTE SECUNDARIO | B22082300121 | New_Event | Secondary Wire Break | Include | Include | Equipment | 132 | 2022-08-23 | 1320 | keep | 0 | Aug | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-23 16:25 | 2022-08-23 18:00 | 4 | 1:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 37.5 POR 37.5KVA | S22082300259 | New_Event | Service Transformer Failure | Include | Include | Equipment | 95 | 2022-08-23 | 380 | keep | 0 | Aug | 2022 | 0.00025882 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-08-23 16:25 | 2022-08-23 18:57 | 3 | 2:32 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300183 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 152 | 2022-08-23 | 456 | keep | 0 | Aug | 2022 | 0.00031058 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-23 16:43 | 2022-08-24 19:54 | 8 | 27:11 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE SECUNDARIO | B22082300126 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 1631 | 2022-08-23 | 13048 | keep | 0 | Aug | 2022 | 0.0088869 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-23 17:09 | 2022-08-23 18:08 | 20 | 0:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082300190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2022-08-23 | 1180 | keep | 0 | Aug | 2022 | 0.00080369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-23 17:13 | 2022-08-23 17:44 | 1292 | 0:31 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEA CON VARETA DE PISO Y SE CERRO MACHETE | S22082300260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2022-08-23 | 40052 | keep | 0 | Aug | 2022 | 0.027279 | 0.00087998 | Sustained | FALSE | FALSE | Not_TMED_Event | 1292
SAN JUAN | 2022-08-23 17:14 | 2022-08-23 17:18 | 5619 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO 90% POR 1620-03 | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-23 | 22476 | keep | 0 | Aug | 2022 | 0.015308 | 0.0038271 | Momentary | FALSE | FALSE | Not_TMED_Event | 5619
SAN JUAN | 2022-08-23 17:14 | 2022-08-23 17:18 | 36 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1620-03 | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-23 | 144 | keep | 0 | Aug | 2022 | 9.8078e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-08-23 17:14 | 2022-08-23 17:18 | 1073 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO LLAVE 1620-01 Y 90% DEL 1336-07 SE PROBO QUEDO EN SERVICIO | S22082300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-23 | 4292 | keep | 0 | Aug | 2022 | 0.0029233 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
BAYAMON | 2022-08-23 17:22 | 2022-08-23 19:37 | 10 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22082300131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2022-08-23 | 1350 | keep | 0 | Aug | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-23 17:27 | 2022-08-24 09:35 | 30 | 16:08 | P | CABLE SOTERRADO AVERIADO | AVERIA DEL RISER A SW 1 SE LE CONECTO UN JUMPER Y QUEDARON TODOS EN SERVICIO | M22082300191 | New_Event | UG Cable Fault | Include | Include | Equipment | 968 | 2022-08-23 | 29040 | keep | 0 | Aug | 2022 | 0.019779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-23 17:44 | 2022-08-24 09:40 | 30 | 15:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22082300201 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 956 | 2022-08-23 | 28680 | keep | 0 | Aug | 2022 | 0.019534 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-08-23 17:58 | 2022-08-23 21:05 | 60 | 3:07 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300209 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 187 | 2022-08-23 | 11220 | keep | 0 | Aug | 2022 | 0.0076419 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-23 18:03 | 2022-08-23 21:42 | 89 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L Y SE CERRO N/O PARA TERMINAR DE ENERGIZAR LAZO DE XMR | B22082300136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-08-23 | 19491 | keep | 0 | Aug | 2022 | 0.013275 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BAYAMON | 2022-08-23 18:10 | 2022-08-24 01:54 | 65 | 7:44 | P | CAUSAS EXTERNAS | 1 X 80 EN C/L SE RETIRO GLOBO | B22082300138 | New_Event | Damage From Public | Include | Include | Public | 464 | 2022-08-23 | 30160 | keep | 0 | Aug | 2022 | 0.020542 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-08-23 18:22 | 2022-08-24 01:35 | 100 | 7:13 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082300198 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 433 | 2022-08-23 | 43300 | keep | 0 | Aug | 2022 | 0.029491 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-23 18:27 | 2022-08-23 20:45 | 40 | 2:18 | P | DESGANCHE | 1 X 20 EN RISER DESGANCHE | R22082300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2022-08-23 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-08-23 18:29 | 2022-08-23 19:39 | 15 | 1:10 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L DESCARGAS ELECTRICAS | A22082300213 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 70 | 2022-08-23 | 1050 | keep | 0 | Aug | 2022 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-23 18:33 | 2022-08-23 18:35 | 2891 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R22082300099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-23 | 5782 | keep | 0 | Aug | 2022 | 0.0039381 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
CAGUAS | 2022-08-23 18:33 | 2022-08-23 18:34 | 638 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 3007-04 | C22082300195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 638 | keep | 0 | Aug | 2022 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
CAGUAS | 2022-08-23 18:33 | 2022-08-23 18:34 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 3007-02 | C22082300195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 906 | keep | 0 | Aug | 2022 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
AGUADILLA | 2022-08-23 18:40 | 2022-08-23 20:00 | 20 | 1:20 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082300201 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 80 | 2022-08-23 | 1600 | keep | 0 | Aug | 2022 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-23 18:51 | 2022-08-24 08:54 | 282 | 14:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22082300198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 843 | 2022-08-23 | 237726 | keep | 0 | Aug | 2022 | 0.16191 | 0.00019207 | Sustained | FALSE | FALSE | Not_TMED_Event | 282
SAN JUAN | 2022-08-23 19:00 | 2022-08-23 19:31 | 437 | 0:31 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE INTERRUPTOR SE ABRIO PUENTE PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO Y CONDUCTOR EN EL SUELO 100% EN SERVICIO SU CARGA POR 1530-07 | S22082300236 | New_Event | Primary Pole Failure | Include | Include | Equipment | 31 | 2022-08-23 | 13547 | keep | 0 | Aug | 2022 | 0.0092268 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2022-08-23 19:00 | 2022-08-23 19:31 | 643 | 0:31 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE INTERRUPTOR LLEVA 1530-6 POR POSTE PARTIDO Y CONDUCTOR EN EL PISO SE VA A SECCIONALIZAR Y SE CERRO INTERRPTOR 1530-07 75% EN SERVICIO Y 100% 1530-06 | S22082300236 | New_Event | Primary Pole Failure | Include | Include | Equipment | 31 | 2022-08-23 | 19933 | keep | 0 | Aug | 2022 | 0.013576 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
ARECIBO | 2022-08-23 19:18 | 2022-08-23 21:46 | 60 | 2:28 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300220 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 148 | 2022-08-23 | 8880 | keep | 0 | Aug | 2022 | 0.0060481 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-23 19:19 | 2022-08-24 14:25 | 8 | 19:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082300290 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1146 | 2022-08-23 | 9168 | keep | 0 | Aug | 2022 | 0.0062443 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-23 19:24 | 2022-08-24 13:27 | 1 | 18:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S22082300344 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1083 | 2022-08-23 | 1083 | keep | 0 | Aug | 2022 | 0.00073763 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-23 19:31 | 2022-08-24 08:09 | 161 | 12:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE Y SE LEVANTO PRIMARIA GOI SJ-220823-04 | S22082300326 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 758 | 2022-08-23 | 122038 | keep | 0 | Aug | 2022 | 0.08312 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-23 19:33 | 2022-08-23 19:34 | 2446 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082300116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 2446 | keep | 0 | Aug | 2022 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
BAYAMON | 2022-08-23 19:37 | 2022-08-23 21:10 | 206 | 1:33 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S22082300349 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-08-23 | 19158 | keep | 0 | Aug | 2022 | 0.013048 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
ARECIBO | 2022-08-23 19:46 | 2022-08-23 21:00 | 45 | 1:14 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300252 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 74 | 2022-08-23 | 3330 | keep | 0 | Aug | 2022 | 0.002268 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2022-08-23 19:48 | 2022-08-23 22:15 | 10 | 2:27 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300227 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 147 | 2022-08-23 | 1470 | keep | 0 | Aug | 2022 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-23 19:53 | 2022-08-24 06:59 | 87 | 11:06 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C22082300215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 666 | 2022-08-23 | 57942 | keep | 0 | Aug | 2022 | 0.039464 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
MAYAGÃœEZ | 2022-08-23 19:54 | 2022-08-24 09:54 | 2 | 14:00 | P | DESGANCHE | 1 X 30 C/L SE RETIRO RAMA | M22082300218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 840 | 2022-08-23 | 1680 | keep | 0 | Aug | 2022 | 0.0011442 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-08-23 19:57 | 2022-08-23 19:58 | 1839 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22082300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 1839 | keep | 0 | Aug | 2022 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2022-08-23 19:57 | 2022-08-23 19:58 | 1778 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22082300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 1778 | keep | 0 | Aug | 2022 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2022-08-23 19:57 | 2022-08-23 19:58 | 1376 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22082300105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 1376 | keep | 0 | Aug | 2022 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2022-08-23 19:57 | 2022-08-23 19:58 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22082300106 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 293 | keep | 0 | Aug | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-08-23 19:57 | 2022-08-23 19:58 | 1215 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 | R22082300106 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-23 | 1215 | keep | 0 | Aug | 2022 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
VEGA BAJA | 2022-08-23 19:59 | 2022-08-23 22:30 | 100 | 2:31 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082300232 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 151 | 2022-08-23 | 15100 | keep | 0 | Aug | 2022 | 0.010285 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-23 20:16 | 2022-08-24 03:10 | 12 | 6:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA | B22082300154 | New_Event | Cutout Failure | Include | Include | Equipment | 414 | 2022-08-23 | 4968 | keep | 0 | Aug | 2022 | 0.0033837 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-23 20:22 | 2022-08-24 12:48 | 20 | 16:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | B22082300156 | New_Event | Secondary Wire Break | Include | Include | Equipment | 986 | 2022-08-23 | 19720 | keep | 0 | Aug | 2022 | 0.013431 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-23 20:42 | 2022-08-24 00:58 | 180 | 4:16 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22082300167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-08-23 | 46080 | keep | 0 | Aug | 2022 | 0.031385 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2022-08-23 20:48 | 2022-08-24 05:00 | 95 | 8:12 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE LLEVO LINEA A AISLADOR | B22082300197 | New_Event | Primary Wire Break | Include | Include | Equipment | 492 | 2022-08-23 | 46740 | keep | 0 | Aug | 2022 | 0.031834 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
VEGA BAJA | 2022-08-23 20:53 | 2022-08-23 21:09 | 14 | 0:16 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082300237 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 16 | 2022-08-23 | 224 | keep | 0 | Aug | 2022 | 0.00015257 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2022-08-23 21:08 | 2022-08-24 12:51 | 2 | 15:43 | P | DESGANCHE | 1 X 20 EN C/L | B22082200380 | New_Event | Vegetation Contact | Include | Include | Vegetation | 943 | 2022-08-23 | 1886 | keep | 0 | Aug | 2022 | 0.0012845 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-08-23 21:35 | 2022-08-24 06:12 | 131 | 8:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22082300233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2022-08-23 | 67727 | keep | 0 | Aug | 2022 | 0.046129 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
GUAYAMA | 2022-08-23 21:36 | 2022-08-24 07:48 | 12 | 10:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR POR PORTAFUSIBLE QUEMADO | P22082300127 | New_Event | Cutout Failure | Include | Include | Equipment | 612 | 2022-08-23 | 7344 | keep | 0 | Aug | 2022 | 0.005002 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-23 21:49 | 2022-08-23 22:35 | 50 | 0:46 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M22082300208 | New_Event | Animals | Include | Include | Wildlife | 46 | 2022-08-23 | 2300 | keep | 0 | Aug | 2022 | 0.0015665 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-23 22:19 | 2022-08-23 22:35 | 716 | 0:16 | P | DESCONECTIVO DEFECTUOSO | SE ABRE 1709-03 QUE LLEVA SOLO SU 50% EL RESTO TRANSFERIDO, PERO A SU VEZ LLEVA 1709-05 BY-220823-01 SE REMPLAZO MACHETE EN FUEGO | B22082300184 | New_Event | Switch Failure | Include | Include | Equipment | 16 | 2022-08-23 | 11456 | keep | 0 | Aug | 2022 | 0.0078026 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
BAYAMON | 2022-08-23 22:19 | 2022-08-23 22:35 | 2364 | 0:16 | T | DESCONECTIVO DEFECTUOSO | SE ABRE 1709-03 QUE LLEVA SOLO SU 50% EL RESTO TRANSFERIDO, PERO A SU VEZ LLEVA 1709-05 BY-220823-01 SE REMPLAZO MACHETE EN FUEGO | B22082300184 | New_Event | Switch Failure | Include | Include | Equipment | 16 | 2022-08-23 | 37824 | keep | 0 | Aug | 2022 | 0.025762 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
AGUADILLA | 2022-08-23 22:49 | 2022-08-23 22:50 | 390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22082300230 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-23 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
GUAYAMA | 2022-08-23 23:05 | 2022-08-24 06:48 | 75 | 7:43 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22082300133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2022-08-23 | 34725 | keep | 0 | Aug | 2022 | 0.023651 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-08-23 23:08 | 2022-08-24 13:53 | 15 | 14:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | S22082300398 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 885 | 2022-08-23 | 13275 | keep | 0 | Aug | 2022 | 0.0090415 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-24 00:51 | 2022-08-24 10:20 | 40 | 9:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22082400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 569 | 2022-08-24 | 22760 | keep | 0 | Aug | 2022 | 0.015502 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-24 01:48 | 2022-08-24 01:49 | 3041 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M22082400001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-24 | 3041 | keep | 0 | Aug | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2022-08-24 01:49 | 2022-08-24 06:20 | 80 | 4:31 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | M22082400002 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-08-24 | 21680 | keep | 0 | Aug | 2022 | 0.014766 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-08-24 02:28 | 2022-08-24 07:39 | 438 | 5:11 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C22082400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-08-24 | 136218 | keep | 0 | Aug | 2022 | 0.092777 | 0.00029832 | Sustained | FALSE | FALSE | Not_TMED_Event | 438
SAN JUAN | 2022-08-24 02:30 | 2022-08-24 02:31 | 5 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1116-05 Y SE CERRO POR SCADA LLEVA 1117-08 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 5 | keep | 0 | Aug | 2022 | 3.4055e-06 | 3.4055e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-24 02:30 | 2022-08-24 02:31 | 466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1116-05 Y SE CERRO POR SCADA LLEVA 1117-08 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 466 | keep | 0 | Aug | 2022 | 0.00031739 | 0.00031739 | Momentary | FALSE | FALSE | Not_TMED_Event | 466
MAYAGÃœEZ | 2022-08-24 02:50 | 2022-08-24 05:10 | 40 | 2:20 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082400005 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 140 | 2022-08-24 | 5600 | keep | 0 | Aug | 2022 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-24 03:41 | 2022-08-24 06:38 | 250 | 2:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C22082400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-08-24 | 44250 | keep | 0 | Aug | 2022 | 0.030138 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BARRANQUITAS | 2022-08-24 04:33 | 2022-08-24 18:00 | 10 | 13:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO CAJA DEL TRANSFORMADOR PARA REPARAR BAJANTE Y LINEA SECUNDARIA | C22082400021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 807 | 2022-08-24 | 8070 | keep | 0 | Aug | 2022 | 0.0054964 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-24 04:54 | 2022-08-24 04:55 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1203-01 QUE LLEVA EL 1203-03 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 1225 | keep | 0 | Aug | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-08-24 04:54 | 2022-08-24 04:55 | 616 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1203-01 QUE LLEVA EL 1203-03 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 616 | keep | 0 | Aug | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
AGUADILLA | 2022-08-24 04:57 | 2022-08-24 09:01 | 4 | 4:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082400007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 244 | 2022-08-24 | 976 | keep | 0 | Aug | 2022 | 0.00066475 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-08-24 05:11 | 2022-08-24 05:12 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 3973 | keep | 0 | Aug | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2022-08-24 05:11 | 2022-08-24 05:12 | 2484 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 2484 | keep | 0 | Aug | 2022 | 0.0016918 | 0.0016918 | Momentary | FALSE | FALSE | Not_TMED_Event | 2484
CAGUAS | 2022-08-24 05:38 | 2022-08-24 06:43 | 1 | 1:05 | P | ANIMAL | 1 X 40 EN RISER CRUCE POR AVE | C22082400032 | New_Event | Animals | Include | Include | Wildlife | 65 | 2022-08-24 | 65 | keep | 0 | Aug | 2022 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-24 05:38 | 2022-08-24 09:15 | 60 | 3:37 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22082400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-08-24 | 13020 | keep | 0 | Aug | 2022 | 0.0088679 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-24 06:17 | 2022-08-24 10:55 | 3 | 4:38 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082400007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-08-24 | 834 | keep | 0 | Aug | 2022 | 0.00056803 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-08-24 06:30 | 2022-08-24 11:04 | 5 | 4:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22082400009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2022-08-24 | 1370 | keep | 0 | Aug | 2022 | 0.0009331 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-24 06:44 | 2022-08-24 16:30 | 50 | 9:46 | P | CONDUCTOR ROTO O ABIERTO | 2 X 25 EN C/L SE LEVANTO CONDUCTOR | S22082400015 | New_Event | Primary Wire Break | Include | Include | Equipment | 586 | 2022-08-24 | 29300 | keep | 0 | Aug | 2022 | 0.019956 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-24 07:07 | 2022-08-24 11:55 | 1 | 4:48 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSCLOSER | B22082400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2022-08-24 | 288 | keep | 0 | Aug | 2022 | 0.00019616 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-24 07:11 | 2022-08-24 07:12 | 5630 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22082400057 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-24 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-08-24 07:12 | 2022-08-24 12:40 | 147 | 5:28 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22082400063 | 1st_after_momentary | Animals | Include | Include | Wildlife | 328 | 2022-08-24 | 48216 | keep | 0 | Aug | 2022 | 0.03284 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
BAYAMON | 2022-08-24 07:15 | 2022-08-24 07:16 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 95% DEL 1717-02 | B22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-24 07:15 | 2022-08-24 07:16 | 865 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 95 DE SU CARGA POR EL 1713-05 | B22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 865 | keep | 0 | Aug | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BARRANQUITAS | 2022-08-24 07:17 | 2022-08-24 07:52 | 2 | 0:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22082400064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2022-08-24 | 70 | keep | 0 | Aug | 2022 | 4.7677e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-24 07:20 | 2022-08-24 17:00 | 1 | 9:40 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082400015 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 580 | 2022-08-24 | 580 | keep | 0 | Aug | 2022 | 0.00039504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-24 07:20 | 2022-08-25 15:59 | 3 | 32:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 15KVA | A22082400015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1959 | 2022-08-24 | 5877 | keep | 0 | Aug | 2022 | 0.0040028 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-08-24 07:37 | 2022-08-24 11:16 | 2 | 3:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA DE TRANSFORMADOR | C22082400060 | New_Event | Primary Wire Break | Include | Include | Equipment | 219 | 2022-08-24 | 438 | keep | 0 | Aug | 2022 | 0.00029832 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-08-24 07:40 | 2022-08-24 11:29 | 50 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO REPORTO CAUSA | A22082400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-08-24 | 11450 | keep | 0 | Aug | 2022 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-24 07:44 | 2022-08-24 10:35 | 75 | 2:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22082400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-08-24 | 12825 | keep | 0 | Aug | 2022 | 0.008735 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-08-24 07:54 | 2022-08-24 09:35 | 4 | 1:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A22082400023 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2022-08-24 | 404 | keep | 0 | Aug | 2022 | 0.00027516 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-24 07:57 | 2022-08-24 12:38 | 100 | 4:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M22082400018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 281 | 2022-08-24 | 28100 | keep | 0 | Aug | 2022 | 0.019139 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-24 08:04 | 2022-08-24 10:09 | 87 | 2:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C22082400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-08-24 | 10875 | keep | 0 | Aug | 2022 | 0.0074069 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
CAGUAS | 2022-08-24 08:04 | 2022-08-24 13:30 | 12 | 5:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 25 KVA X 25 KVA DEFECTUOSO | C22082400065 | New_Event | Service Transformer Failure | Include | Include | Equipment | 326 | 2022-08-24 | 3912 | keep | 0 | Aug | 2022 | 0.0026644 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-08-24 08:13 | 2022-08-24 13:23 | 1 | 5:10 | P | OTRAS CAUSAS | 1 X 65 EN SUBESTACION DE ELLOS SE PUSO EQUIPO DE MEDICION DIRECTO | P22082400027 | New_Event | Other Causes | Include | Include | Other | 310 | 2022-08-24 | 310 | keep | 0 | Aug | 2022 | 0.00021114 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-24 08:22 | 2022-08-24 14:58 | 75 | 6:36 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA Y 1 X 15 TRANSFORMADOR POR RAYOS | M22082400024 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 396 | 2022-08-24 | 29700 | keep | 0 | Aug | 2022 | 0.020229 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-08-24 08:32 | 2022-08-24 08:33 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22082400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 4641 | keep | 0 | Aug | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
BARRANQUITAS | 2022-08-24 08:47 | 2022-08-24 11:00 | 54 | 2:13 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR PALOMA, SE REEMPLAZO AISLADOR Y SE REALIZO DESGANCHE | C22082400076 | New_Event | Animals | Include | Include | Wildlife | 133 | 2022-08-24 | 7182 | keep | 0 | Aug | 2022 | 0.0048916 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
YAUCO | 2022-08-24 08:48 | 2022-08-24 10:19 | 16 | 1:31 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | P22082400029 | New_Event | Animals | Include | Include | Wildlife | 91 | 2022-08-24 | 1456 | keep | 0 | Aug | 2022 | 0.00099167 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-08-24 08:58 | 2022-08-24 12:27 | 8 | 3:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | C22082400079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 209 | 2022-08-24 | 1672 | keep | 0 | Aug | 2022 | 0.0011388 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-08-24 08:59 | 2022-08-24 11:10 | 50 | 2:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A22082400030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 131 | 2022-08-24 | 6550 | keep | 0 | Aug | 2022 | 0.0044612 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-24 09:07 | 2022-08-24 12:56 | 4 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-08-24 | 916 | keep | 0 | Aug | 2022 | 0.00062388 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-08-24 09:36 | 2022-08-24 13:24 | 1 | 3:48 | P | ANIMAL | 1 X 40 EN RISER Y 1 SMU DE 20 AMP EN EL SU-20 CRUCE POR RATA | C22082400087 | New_Event | Animals | Include | Include | Wildlife | 228 | 2022-08-24 | 228 | keep | 0 | Aug | 2022 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-24 09:46 | 2022-08-24 09:47 | 1261 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22082400050 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-24 | 1261 | keep | 0 | Aug | 2022 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2022-08-24 09:47 | 2022-08-24 13:30 | 60 | 3:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22082400052 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 223 | 2022-08-24 | 13380 | keep | 0 | Aug | 2022 | 0.0091131 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-08-24 09:56 | 2022-08-24 19:30 | 7 | 9:34 | P | CONDUCTOR ROTO O ABIERTO | 2 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A22082400043 | New_Event | Primary Wire Break | Include | Include | Equipment | 574 | 2022-08-24 | 4018 | keep | 0 | Aug | 2022 | 0.0027366 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-08-24 10:00 | 2022-08-24 11:09 | 1 | 1:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA RPIMARIA 2 X 30 EN CORTE DE LINEA 2 X 10 EN RISER SE REPARO CABLE MEDICION | R22082400007 | New_Event | Cutout Failure | Include | Include | Equipment | 69 | 2022-08-24 | 69 | keep | 0 | Aug | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-24 10:04 | 2022-08-24 12:09 | 1 | 2:05 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | S22082400049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2022-08-24 | 125 | keep | 0 | Aug | 2022 | 8.5137e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-24 10:05 | 2022-08-24 15:14 | 20 | 5:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO BAJANTES SECUNDARIOS NO FUNDIO | C22082400096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 309 | 2022-08-24 | 6180 | keep | 0 | Aug | 2022 | 0.0042092 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-24 10:09 | 2022-08-24 15:30 | 54 | 5:21 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO, RETEZO LINEAS Y REMPLAZO PARARRAYO | C22082400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-08-24 | 17334 | keep | 0 | Aug | 2022 | 0.011806 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2022-08-24 10:39 | 2022-08-24 14:00 | 18 | 3:21 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA REPARAR BUSHING SECUNDARIO | S22082300320 | New_Event | Service Transformer Failure | Include | Include | Equipment | 201 | 2022-08-24 | 3618 | keep | 0 | Aug | 2022 | 0.0024642 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-08-24 10:55 | 2022-08-24 13:22 | 4 | 2:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA A 15KVA | M22082400064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 147 | 2022-08-24 | 588 | keep | 0 | Aug | 2022 | 0.00040048 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-08-24 10:56 | 2022-08-24 13:35 | 51 | 2:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | C22082400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2022-08-24 | 8109 | keep | 0 | Aug | 2022 | 0.005523 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
SAN JUAN | 2022-08-24 11:00 | 2022-08-24 13:54 | 10 | 2:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | S22082400056 | New_Event | Primary Wire Break | Include | Include | Equipment | 174 | 2022-08-24 | 1740 | keep | 0 | Aug | 2022 | 0.0011851 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-24 11:07 | 2022-08-24 12:00 | 10 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE SECUNDARIO Y DESGANCHE | B22082400025 | New_Event | Primary Wire Break | Include | Include | Equipment | 53 | 2022-08-24 | 530 | keep | 0 | Aug | 2022 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-24 11:12 | 2022-08-24 12:20 | 5 | 1:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA X 37.5KVA | M22082400067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 68 | 2022-08-24 | 340 | keep | 0 | Aug | 2022 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-24 11:13 | 2022-08-24 15:01 | 120 | 3:48 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE REALIZO DESGANCHE | B22082400028 | New_Event | Primary Wire Break | Include | Include | Equipment | 228 | 2022-08-24 | 27360 | keep | 0 | Aug | 2022 | 0.018635 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
UTUADO | 2022-08-24 11:13 | 2022-08-24 15:25 | 1 | 4:12 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | A22082400053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 252 | 2022-08-24 | 252 | keep | 0 | Aug | 2022 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-24 11:15 | 2022-08-24 11:16 | 188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | R22082400000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-24 | 188 | keep | 0 | Aug | 2022 | 0.00012805 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
CANOVANAS | 2022-08-24 11:16 | 2022-08-24 14:20 | 62 | 3:04 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR EN EL SUELO SE ABRIO MACHETE PARA SECCIONALIZAR | R22082400044 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 184 | 2022-08-24 | 11408 | keep | 0 | Aug | 2022 | 0.0077699 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BARRANQUITAS | 2022-08-24 11:16 | 2022-08-24 15:38 | 11 | 4:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA LEVANTAR SECUNDARIA | C22082400107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 262 | 2022-08-24 | 2882 | keep | 0 | Aug | 2022 | 0.0019629 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-08-24 11:17 | 2022-08-24 15:15 | 40 | 3:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2022-08-24 | 9520 | keep | 0 | Aug | 2022 | 0.006484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-24 11:19 | 2022-08-24 14:00 | 18 | 2:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22082400062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 161 | 2022-08-24 | 2898 | keep | 0 | Aug | 2022 | 0.0019738 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2022-08-24 11:22 | 2022-08-24 13:42 | 1 | 2:20 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN TRANSFORMADOR DESGANCHE SECUNDARIO | R22082400014 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 140 | 2022-08-24 | 140 | keep | 0 | Aug | 2022 | 9.5353e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-24 11:34 | 2022-08-24 20:41 | 100 | 9:07 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN C/L DESGANCHO, REMPLAZO CAJA QUEMADA Y REPARO SECUNDARIA | C22082400077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 547 | 2022-08-24 | 54700 | keep | 0 | Aug | 2022 | 0.037256 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-08-24 11:45 | 2022-08-24 12:15 | 4 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REEMPLAZAR CONECTORES BAJANTE SEUNDARIO | R22082400015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-08-24 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-24 12:03 | 2022-08-24 12:07 | 30 | 0:04 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L NO SE REPORTO CAUSA | M22082400076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-24 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-24 12:03 | 2022-08-24 18:23 | 70 | 6:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | M22082400077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2022-08-24 | 26600 | keep | 0 | Aug | 2022 | 0.018117 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-08-24 12:04 | 2022-08-24 13:45 | 15 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN XMR SE REPARO SECUNDARIA | S22082400068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2022-08-24 | 1515 | keep | 0 | Aug | 2022 | 0.0010319 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-24 12:10 | 2022-08-24 14:03 | 15 | 1:53 | P | ANIMAL | 1 X 15 EN XMR AVE | B22082400035 | New_Event | Animals | Include | Include | Wildlife | 113 | 2022-08-24 | 1695 | keep | 0 | Aug | 2022 | 0.0011545 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-24 12:11 | 2022-08-24 17:09 | 100 | 4:58 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22082400113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2022-08-24 | 29800 | keep | 0 | Aug | 2022 | 0.020297 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-24 12:12 | 2022-08-24 13:39 | 10 | 1:27 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | B22082400037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-08-24 | 870 | keep | 0 | Aug | 2022 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-24 12:20 | 2022-08-24 16:41 | 5 | 4:21 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO, REMPLAZO BAJANTE PRIMARIO CAJA Y PARARRAYO | C22082400114 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 261 | 2022-08-24 | 1305 | keep | 0 | Aug | 2022 | 0.00088883 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-24 12:27 | 2022-08-24 15:27 | 10 | 3:00 | P | DESGANCHE | DESGANCHE 1 X 20 EN C/L | B22082400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-08-24 | 1800 | keep | 0 | Aug | 2022 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-24 12:36 | 2022-08-24 15:50 | 12 | 3:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22082900000 | New_Event | Secondary Wire Break | Include | Include | Equipment | 194 | 2022-08-24 | 2328 | keep | 0 | Aug | 2022 | 0.0015856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-24 12:50 | 2022-08-24 14:00 | 8 | 1:10 | P | ANIMAL | 1 X 25 EN TRANSFORMADOR AVE CRUZO FASE | R22082400025 | New_Event | Animals | Include | Include | Wildlife | 70 | 2022-08-24 | 560 | keep | 0 | Aug | 2022 | 0.00038141 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-24 12:55 | 2022-08-24 14:00 | 25 | 1:05 | P | ARBOL SOBRE LINEA | 1 X 50 EN C/L RETIRO ARBOL DE LAS LINEAS | C22082400103 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 65 | 2022-08-24 | 1625 | keep | 0 | Aug | 2022 | 0.0011068 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-24 13:01 | 2022-08-24 17:00 | 50 | 3:59 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 C/L SE LIGA LINEA PRIMARIA SAFADA A PIN POLE TOP | M22082400093 | New_Event | Primary Wire Break | Include | Include | Equipment | 239 | 2022-08-24 | 11950 | keep | 0 | Aug | 2022 | 0.0081391 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-24 13:13 | 2022-08-24 15:45 | 100 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE PRIMARIO EN C/L | M22082400101 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2022-08-24 | 15200 | keep | 0 | Aug | 2022 | 0.010353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-24 13:18 | 2022-08-24 16:27 | 15 | 3:09 | P | SECUNDARIA/OTROS | SE REPARO VARIOS PEDESTALES SECUNDARIOS VARIAS BARRAS | P22082400045 | New_Event |  |  |  |  | 189 | 2022-08-24 | 2835 | keep | 0 | Aug | 2022 | 0.0019309 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-24 13:22 | 2022-08-24 15:14 | 30 | 1:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN AEREO PROVICIONAL | B22082400046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-08-24 | 3360 | keep | 0 | Aug | 2022 | 0.0022885 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-24 13:36 | 2022-08-24 17:38 | 50 | 4:02 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22082400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2022-08-24 | 12100 | keep | 0 | Aug | 2022 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-24 13:42 | 2022-08-24 13:43 | 2368 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CARGA POR EL 9103-02 | B22082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-24 | 2368 | keep | 0 | Aug | 2022 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2022-08-24 13:42 | 2022-08-24 13:43 | 538 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 LLEVA LA CARGA DEL 9103-01 | B22082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-24 | 538 | keep | 0 | Aug | 2022 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2022-08-24 13:42 | 2022-08-24 13:43 | 1284 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B22082400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-24 | 1284 | keep | 0 | Aug | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
AGUADILLA | 2022-08-24 13:46 | 2022-08-24 19:17 | 1 | 5:31 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR POR DESGANCHE | M22082400108 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 331 | 2022-08-24 | 331 | keep | 0 | Aug | 2022 | 0.00022544 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-24 13:46 | 2022-08-24 13:50 | 15 | 0:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22082400056 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 4 | 2022-08-24 | 60 | keep | 0 | Aug | 2022 | 4.0866e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-08-24 13:50 | 2022-08-24 14:10 | 6 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR SECUNDARIA | R22082400016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2022-08-24 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-24 13:50 | 2022-08-24 16:44 | 1 | 2:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M22082400114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-08-24 | 174 | keep | 0 | Aug | 2022 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-24 13:55 | 2022-08-24 14:56 | 20 | 1:01 | P | ANIMAL | 1 X 30 EN C/L AVE | S22082400051 | New_Event | Animals | Include | Include | Wildlife | 61 | 2022-08-24 | 1220 | keep | 0 | Aug | 2022 | 0.00083094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-24 14:07 | 2022-08-24 18:09 | 60 | 4:02 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN C/L REMPLAZO PARARRAYO | C22082400134 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 242 | 2022-08-24 | 14520 | keep | 0 | Aug | 2022 | 0.0098895 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-24 14:08 | 2022-08-24 16:17 | 50 | 2:09 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22082400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-08-24 | 6450 | keep | 0 | Aug | 2022 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-24 14:15 | 2022-08-24 15:56 | 11 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO BARRA EN PEDESTAL | R22082400031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2022-08-24 | 1111 | keep | 0 | Aug | 2022 | 0.0007567 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-08-24 14:20 | 2022-08-24 14:31 | 178 | 0:11 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR EN EL SUELO SE ABRIO MACHETE Y SE PASO CARGA 95% AL 1203-01 | R22082400044 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 11 | 2022-08-24 | 1958 | keep | 0 | Aug | 2022 | 0.0013336 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-24 14:20 | 2022-08-24 16:10 | 30 | 1:50 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22082400138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2022-08-24 | 3300 | keep | 0 | Aug | 2022 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-24 14:24 | 2022-08-24 14:25 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 652 | keep | 0 | Aug | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
CANOVANAS | 2022-08-24 14:31 | 2022-08-24 16:38 | 7 | 2:07 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE NORMALIZARON CARGAS | R22082400044 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 127 | 2022-08-24 | 889 | keep | 0 | Aug | 2022 | 0.00060549 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-24 14:50 | 2022-08-24 19:20 | 10 | 4:30 | P | DESGANCHE | 1 X 25 EN C/L SE DESGANCHO | R22082400051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-08-24 | 2700 | keep | 0 | Aug | 2022 | 0.001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-24 15:02 | 2022-08-24 17:33 | 60 | 2:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE DESGANCHO | R22082400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-08-24 | 9060 | keep | 0 | Aug | 2022 | 0.0061707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-24 15:14 | 2022-08-24 19:30 | 200 | 4:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X140 EN CORTE DE LINEA SE REMPLAZARON CAJAS PRIMARIAS | P22082400092 | New_Event | Cutout Failure | Include | Include | Equipment | 256 | 2022-08-24 | 51200 | keep | 0 | Aug | 2022 | 0.034872 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-08-24 15:19 | 2022-08-24 17:35 | 70 | 2:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082400084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2022-08-24 | 9520 | keep | 0 | Aug | 2022 | 0.006484 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-08-24 15:24 | 2022-08-24 22:00 | 150 | 6:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR | A22082400087 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 396 | 2022-08-24 | 59400 | keep | 0 | Aug | 2022 | 0.040457 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-24 15:32 | 2022-08-24 15:33 | 5619 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL 90% TRANSFERIDO AL 1620-03 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 5619 | keep | 0 | Aug | 2022 | 0.0038271 | 0.0038271 | Momentary | FALSE | FALSE | Not_TMED_Event | 5619
SAN JUAN | 2022-08-24 15:32 | 2022-08-24 15:33 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1620-03 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 36 | keep | 0 | Aug | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-08-24 15:32 | 2022-08-24 15:33 | 1073 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 90% 1336-07 Y 1620-01 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 1073 | keep | 0 | Aug | 2022 | 0.00073082 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
BAYAMON | 2022-08-24 15:33 | 2022-08-24 16:58 | 10 | 1:25 | P | ANIMAL | 1 X 15 EN XMR LAGARTO | P22082400112 | New_Event | Animals | Include | Include | Wildlife | 85 | 2022-08-24 | 850 | keep | 0 | Aug | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-24 15:42 | 2022-08-24 19:50 | 50 | 4:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22082400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-08-24 | 12400 | keep | 0 | Aug | 2022 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-24 15:45 | 2022-08-24 16:54 | 50 | 1:09 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | S22082400096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-08-24 | 3450 | keep | 0 | Aug | 2022 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-24 15:47 | 2022-08-24 22:00 | 15 | 6:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PARTIDA | A22082400092 | New_Event | Primary Wire Break | Include | Include | Equipment | 373 | 2022-08-24 | 5595 | keep | 0 | Aug | 2022 | 0.0038107 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-08-24 16:02 | 2022-08-24 17:36 | 2 | 1:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | R22082400154 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 94 | 2022-08-24 | 188 | keep | 0 | Aug | 2022 | 0.00012805 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2022-08-24 16:05 | 2022-08-24 17:08 | 5 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CAMBIARON CONECTORES EN LA SECUNDARIA | P22082400205 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2022-08-24 | 315 | keep | 0 | Aug | 2022 | 0.00021455 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-08-24 16:18 | 2022-08-24 18:17 | 25 | 1:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA QUEMADA | P22082400170 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2022-08-24 | 2975 | keep | 0 | Aug | 2022 | 0.0020263 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-08-24 16:21 | 2022-08-24 20:20 | 60 | 3:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA 2 X 40 EN CORTES DE LINEA DIFERENTES MAL TIEMPO VIENTOS FUERTE EVENTO TRANSFERIDO DE PC A AR/UTUD | P22082400175 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2022-08-24 | 14340 | keep | 0 | Aug | 2022 | 0.0097669 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-08-24 16:29 | 2022-08-24 17:45 | 7 | 1:16 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR CON LIQUEO ACEITE DE 37.5 KVA X 37.5 KVA | C22082400153 | New_Event | Service Transformer Failure | Include | Include | Equipment | 76 | 2022-08-24 | 532 | keep | 0 | Aug | 2022 | 0.00036234 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-08-24 16:31 | 2022-08-24 19:53 | 12 | 3:22 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22082400130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-08-24 | 2424 | keep | 0 | Aug | 2022 | 0.001651 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-24 16:32 | 2022-08-24 20:00 | 30 | 3:28 | P | CONDUCTOR ROTO O ABIERTO | SE DESGANCHO Y SE CERRO PUENTE | S22082400106 | New_Event | Primary Wire Break | Include | Include | Equipment | 208 | 2022-08-24 | 6240 | keep | 0 | Aug | 2022 | 0.00425 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-24 16:33 | 2022-08-25 17:13 | 10 | 24:40 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DE EXISTENTE A T21 | P22082400191 | New_Event | UG Cable Fault | Include | Include | Equipment | 1480 | 2022-08-24 | 14800 | keep | 0 | Aug | 2022 | 0.01008 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-08-24 16:43 | 2022-08-24 18:46 | 6 | 2:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO CONECTORES EN BAJANTE SECUNDARIO | C22082300168 | New_Event | Secondary Wire Break | Include | Include | Equipment | 123 | 2022-08-24 | 738 | keep | 0 | Aug | 2022 | 0.00050265 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-24 16:57 | 2022-08-24 20:03 | 30 | 3:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | M22082400214 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 186 | 2022-08-24 | 5580 | keep | 0 | Aug | 2022 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-24 16:58 | 2022-08-24 21:00 | 18 | 4:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR REPARAR BAJANTE SECUNDARIO | P22082400216 | New_Event | Secondary Wire Break | Include | Include | Equipment | 242 | 2022-08-24 | 4356 | keep | 0 | Aug | 2022 | 0.0029669 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
FAJARDO | 2022-08-24 17:29 | 2022-08-24 18:05 | 10 | 0:36 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO | R22082400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-08-24 | 360 | keep | 0 | Aug | 2022 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-24 17:31 | 2022-08-24 21:35 | 20 | 4:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22082400111 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 244 | 2022-08-24 | 4880 | keep | 0 | Aug | 2022 | 0.0033237 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-24 17:32 | 2022-08-24 20:06 | 8 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 10 XMR | P22082400250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2022-08-24 | 1232 | keep | 0 | Aug | 2022 | 0.00083911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-24 17:36 | 2022-08-24 19:20 | 1 | 1:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | P22082400254 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 104 | 2022-08-24 | 104 | keep | 0 | Aug | 2022 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-24 17:40 | 2022-08-24 18:42 | 40 | 1:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C22082400256 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2022-08-24 | 2480 | keep | 0 | Aug | 2022 | 0.0016891 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-24 17:40 | 2022-08-24 21:30 | 2 | 3:50 | P | SECUNDARIA/DESGANCHE | 2 X 8 EN TRANSFORMADOR REQUIERE DESGANCHE | M22082400152 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 230 | 2022-08-24 | 460 | keep | 0 | Aug | 2022 | 0.0003133 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-08-24 17:51 | 2022-08-24 17:52 | 3902 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | C22082400165 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-24 | 3902 | keep | 0 | Aug | 2022 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
HUMACAO | 2022-08-24 17:52 | 2022-08-24 20:14 | 45 | 2:22 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L CAMION SACUDIO LAS LINEAS | C22082400167 | 1st_after_momentary | Damage From Public | Include | Include | Public | 142 | 2022-08-24 | 6390 | keep | 0 | Aug | 2022 | 0.0043522 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-08-24 18:10 | 2022-08-24 19:43 | 150 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN COERTE DE LINEA POR LLUVIAS | M22082400156 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2022-08-24 | 13950 | keep | 0 | Aug | 2022 | 0.0095013 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-08-24 18:16 | 2022-08-25 15:35 | 1 | 21:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA DE TRANSFORMADOR | P22082400319 | New_Event | Primary Wire Break | Include | Include | Equipment | 1279 | 2022-08-24 | 1279 | keep | 0 | Aug | 2022 | 0.00087112 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-24 18:24 | 2022-08-24 22:05 | 100 | 3:41 | P | DESGANCHE | 1 X 140 EN C/L 2 X 80 RBA EN SU - 3A DESGANCHO Y REMPLAZO BAJANTE PRIMARIO DE MACHETE A LINEA | R22082400169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-08-24 | 22100 | keep | 0 | Aug | 2022 | 0.015052 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-24 18:34 | 2022-08-24 19:30 | 15 | 0:56 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE REALIZO DESGANCHE | S22082400121 | New_Event | Primary Wire Break | Include | Include | Equipment | 56 | 2022-08-24 | 840 | keep | 0 | Aug | 2022 | 0.00057212 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-08-24 18:34 | 2022-08-24 20:38 | 75 | 2:04 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE EN MACHETE | S22082400121 | New_Event | Primary Wire Break | Include | Include | Equipment | 124 | 2022-08-24 | 9300 | keep | 0 | Aug | 2022 | 0.0063342 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-08-24 18:35 | 2022-08-25 10:35 | 6 | 16:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA AVERIADA | M22082400159 | New_Event | Secondary Wire Break | Include | Include | Equipment | 960 | 2022-08-24 | 5760 | keep | 0 | Aug | 2022 | 0.0039231 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-24 18:36 | 2022-08-24 19:22 | 25 | 0:46 | P | ANIMAL | 1 X 50 EN C/L SE RETIRO AVE | R22082400064 | New_Event | Animals | Include | Include | Wildlife | 46 | 2022-08-24 | 1150 | keep | 0 | Aug | 2022 | 0.00078326 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-08-24 18:55 | 2022-08-25 11:06 | 18 | 16:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5KVA | P22082400413 | New_Event | Service Transformer Failure | Include | Include | Equipment | 971 | 2022-08-24 | 17478 | keep | 0 | Aug | 2022 | 0.011904 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-08-24 18:57 | 2022-08-24 20:47 | 40 | 1:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082400070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-08-24 | 4400 | keep | 0 | Aug | 2022 | 0.0029968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-24 19:04 | 2022-08-24 21:33 | 60 | 2:29 | P | PROBLEMA DEL CLIENTE | 2 X 100 EN CORTE DE LINEA SE DEJO RISER A SUBEST. PRIVADA PROA | R22082400070 | New_Event | Customer-Related Interruption | Include | Include | Public | 149 | 2022-08-24 | 8940 | keep | 0 | Aug | 2022 | 0.006089 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-08-24 19:05 | 2022-08-25 06:20 | 20 | 11:15 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO PUENTE EN TRANSFORMADOR | P22082400430 | New_Event | Primary Wire Break | Include | Include | Equipment | 675 | 2022-08-24 | 13500 | keep | 0 | Aug | 2022 | 0.0091948 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-24 19:10 | 2022-08-24 20:24 | 100 | 1:14 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | M22082400161 | New_Event | Animals | Include | Include | Wildlife | 74 | 2022-08-24 | 7400 | keep | 0 | Aug | 2022 | 0.0050401 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-24 20:00 | 2022-08-24 21:10 | 30 | 1:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22082400132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2022-08-24 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-24 20:46 | 2022-08-24 22:30 | 20 | 1:44 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRNSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | M22082400227 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 104 | 2022-08-24 | 2080 | keep | 0 | Aug | 2022 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-24 21:09 | 2022-08-25 00:31 | 269 | 3:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L PORTAFUSIBLE | S22082400198 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2022-08-24 | 54338 | keep | 0 | Aug | 2022 | 0.037009 | 0.00018321 | Sustained | FALSE | FALSE | Not_TMED_Event | 269
YAUCO | 2022-08-24 21:09 | 2022-08-25 10:05 | 200 | 12:56 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 140 EN CORTE DE LINEA SE RETEZO LINEA ARRIADA HACIENDO CONTACTO CON BRAZO DE ALUMBRADO | M22082400238 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 776 | 2022-08-24 | 155200 | keep | 0 | Aug | 2022 | 0.10571 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-08-24 21:13 | 2022-08-25 00:40 | 31 | 3:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR FUSIBLE CORROIDO | P22082400537 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2022-08-24 | 6417 | keep | 0 | Aug | 2022 | 0.0043706 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
PONCE | 2022-08-24 21:15 | 2022-08-24 23:55 | 144 | 2:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22082400538 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-08-24 | 23040 | keep | 0 | Aug | 2022 | 0.015692 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2022-08-24 21:26 | 2022-08-25 02:10 | 94 | 4:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA | S22082400199 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2022-08-24 | 26696 | keep | 0 | Aug | 2022 | 0.018183 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
BAYAMON | 2022-08-24 21:33 | 2022-08-24 21:34 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1909-09 | B22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-24 21:33 | 2022-08-24 21:34 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CARGA POR EL 1907-03 | B22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 4456 | keep | 0 | Aug | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
HUMACAO | 2022-08-24 21:35 | 2022-08-24 21:36 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082400200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
CAGUAS | 2022-08-24 21:35 | 2022-08-25 06:08 | 420 | 8:33 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C22082400197 | New_Event | Animals | Include | Include | Wildlife | 513 | 2022-08-24 | 215460 | keep | 0 | Aug | 2022 | 0.14675 | 0.00028606 | Sustained | FALSE | FALSE | Not_TMED_Event | 420
BAYAMON | 2022-08-24 21:35 | 2022-08-24 21:36 | 2324 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 2324 | keep | 0 | Aug | 2022 | 0.0015829 | 0.0015829 | Momentary | FALSE | FALSE | Not_TMED_Event | 2324
CAGUAS | 2022-08-24 21:37 | 2022-08-25 18:30 | 6 | 20:53 | P | EXCAVACIONES | SECUNDARIA AVERIADA POR PERSONAL DE AAA, SE REEMPLAZARON 3 BARRAS DE PEDESTAL | C22082400199 | New_Event | Excavation | Include | Include | Public | 1253 | 2022-08-24 | 7518 | keep | 0 | Aug | 2022 | 0.0051205 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-24 22:02 | 2022-08-24 22:03 | 837 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO 1401-07 LLEVA LA CARGA DEL 1401-06 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 837 | keep | 0 | Aug | 2022 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-08-24 22:02 | 2022-08-24 22:03 | 908 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1401-06 | S22082400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-24 | 908 | keep | 0 | Aug | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-08-24 22:03 | 2022-08-25 10:30 | 5 | 12:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO CAUSA | S22082400203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 747 | 2022-08-24 | 3735 | keep | 0 | Aug | 2022 | 0.0025439 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-08-24 22:45 | 2022-08-25 14:46 | 9 | 16:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 37.5 KV | C22082400207 | New_Event | Service Transformer Failure | Include | Include | Equipment | 961 | 2022-08-24 | 8649 | keep | 0 | Aug | 2022 | 0.0058908 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-08-24 23:11 | 2022-08-25 07:59 | 80 | 8:48 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | A22082400156 | New_Event | Animals | Include | Include | Wildlife | 528 | 2022-08-24 | 42240 | keep | 0 | Aug | 2022 | 0.028769 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-24 23:54 | 2022-08-25 08:10 | 10 | 8:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082400159 | New_Event | Cutout Failure | Include | Include | Equipment | 496 | 2022-08-24 | 4960 | keep | 0 | Aug | 2022 | 0.0033782 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-25 01:13 | 2022-08-25 01:14 | 1812 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 1812 | keep | 0 | Aug | 2022 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
HUMACAO | 2022-08-25 01:22 | 2022-08-25 01:23 | 776 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 776 | keep | 0 | Aug | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
MAYAGÃœEZ | 2022-08-25 02:04 | 2022-08-25 05:10 | 735 | 3:06 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA | M22082500008 | New_Event | Primary Wire Break | Include | Include | Equipment | 186 | 2022-08-25 | 136710 | keep | 0 | Aug | 2022 | 0.093113 | 0.00050061 | Sustained | FALSE | FALSE | Not_TMED_Event | 735
CAGUAS | 2022-08-25 02:18 | 2022-08-25 02:20 | 853 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA CERRADO X CONTROL | C22082500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-25 | 1706 | keep | 0 | Aug | 2022 | 0.0011619 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
MAYAGÃœEZ | 2022-08-25 03:07 | 2022-08-25 10:24 | 40 | 7:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | M22082500013 | New_Event | Cutout Failure | Include | Include | Equipment | 437 | 2022-08-25 | 17480 | keep | 0 | Aug | 2022 | 0.011906 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-25 03:44 | 2022-08-25 03:45 | 1498 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
HUMACAO | 2022-08-25 04:49 | 2022-08-25 04:50 | 1467 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 1467 | keep | 0 | Aug | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
CAGUAS | 2022-08-25 05:09 | 2022-08-25 08:15 | 1 | 3:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN RISER | C22082500008 | New_Event | Cutout Failure | Include | Include | Equipment | 186 | 2022-08-25 | 186 | keep | 0 | Aug | 2022 | 0.00012668 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-25 05:33 | 2022-08-25 09:19 | 59 | 3:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22082500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2022-08-25 | 13334 | keep | 0 | Aug | 2022 | 0.0090817 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
FAJARDO | 2022-08-25 05:43 | 2022-08-25 09:02 | 32 | 3:19 | P | DESGANCHE | 1X30 EN C/L Y 1X10 EN XMR | R22082500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-08-25 | 6368 | keep | 0 | Aug | 2022 | 0.0043372 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
MAYAGÃœEZ | 2022-08-25 06:00 | 2022-08-25 11:25 | 4 | 5:25 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR AVE CRUZO BUSHING | M22082500114 | New_Event | Animals | Include | Include | Wildlife | 325 | 2022-08-25 | 1300 | keep | 0 | Aug | 2022 | 0.00088542 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-08-25 06:25 | 2022-08-25 10:25 | 44 | 4:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | S22082500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2022-08-25 | 10560 | keep | 0 | Aug | 2022 | 0.0071924 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2022-08-25 06:48 | 2022-08-25 10:24 | 20 | 3:36 | P | DESGANCHE | 1X30 EN C/L | B22082500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-08-25 | 4320 | keep | 0 | Aug | 2022 | 0.0029423 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-25 06:55 | 2022-08-25 19:35 | 20 | 12:40 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA CORTE DE LINEA | S22082500008 | New_Event | Primary Wire Break | Include | Include | Equipment | 760 | 2022-08-25 | 15200 | keep | 0 | Aug | 2022 | 0.010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-25 07:09 | 2022-08-25 10:52 | 10 | 3:43 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | R22082500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-08-25 | 2230 | keep | 0 | Aug | 2022 | 0.0015188 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-25 07:27 | 2022-08-25 12:52 | 44 | 5:25 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | B22082500006 | New_Event | Animals | Include | Include | Wildlife | 325 | 2022-08-25 | 14300 | keep | 0 | Aug | 2022 | 0.0097397 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
HUMACAO | 2022-08-25 07:47 | 2022-08-25 12:30 | 130 | 4:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 Y 1 X 80 EN RISER Y 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22082500014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 283 | 2022-08-25 | 36790 | keep | 0 | Aug | 2022 | 0.025058 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2022-08-25 08:06 | 2022-08-25 10:20 | 3 | 2:14 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C22082500017 | New_Event | Animals | Include | Include | Wildlife | 134 | 2022-08-25 | 402 | keep | 0 | Aug | 2022 | 0.0002738 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-08-25 08:06 | 2022-08-25 11:20 | 118 | 3:14 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN CORTES DE LINEA SE RETIRO ENREDADERA | C22082500016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2022-08-25 | 22892 | keep | 0 | Aug | 2022 | 0.015592 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
BARRANQUITAS | 2022-08-25 08:20 | 2022-08-25 11:03 | 1 | 2:43 | P | CAUSAS EXTERNAS | 2 SMU 20 DE 20 AMP. EN TRANSCLOSURE Y 2 X 25 EN RISER CLIENTE PEGANDO MANGA DE PRECION | C22082500020 | New_Event | Damage From Public | Include | Include | Public | 163 | 2022-08-25 | 163 | keep | 0 | Aug | 2022 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-25 08:20 | 2022-08-25 13:35 | 7 | 5:15 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR PRIMARIO | M22082500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2022-08-25 | 2205 | keep | 0 | Aug | 2022 | 0.0015018 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-08-25 08:26 | 2022-08-25 14:44 | 50 | 6:18 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE RETIRARON DOS ARBOLES DE LA LINEA Y ENREDADERAS | A22082500011 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 378 | 2022-08-25 | 18900 | keep | 0 | Aug | 2022 | 0.012873 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-25 08:28 | 2022-08-25 14:20 | 5 | 5:52 | P | PROBLEMA DEL CLIENTE | 2 X 100 EN CORTE DE LINEA SE DEJO CLIENTE FUERA (PROA) | S22082500014 | New_Event | Customer-Related Interruption | Include | Include | Public | 352 | 2022-08-25 | 1760 | keep | 0 | Aug | 2022 | 0.0011987 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-25 08:28 | 2022-08-25 08:55 | 1 | 0:27 | P | MAL TIEMPO/RAYOS | 1 X 40 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22082500064 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 27 | 2022-08-25 | 27 | keep | 0 | Aug | 2022 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-25 08:32 | 2022-08-25 16:52 | 48 | 8:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22082500022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 500 | 2022-08-25 | 24000 | keep | 0 | Aug | 2022 | 0.016346 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CANOVANAS | 2022-08-25 08:41 | 2022-08-25 13:07 | 1 | 4:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIAS | R22082500011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 266 | 2022-08-25 | 266 | keep | 0 | Aug | 2022 | 0.00018117 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-25 08:55 | 2022-08-25 09:55 | 12 | 1:00 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A22082500017 | New_Event | Animals | Include | Include | Wildlife | 60 | 2022-08-25 | 720 | keep | 0 | Aug | 2022 | 0.00049039 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-08-25 09:03 | 2022-08-25 10:39 | 40 | 1:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN C/L Y SE REMPLAZO CAJA PRIMARIA | R22082500013 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2022-08-25 | 3840 | keep | 0 | Aug | 2022 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-25 09:10 | 2022-08-25 19:02 | 13 | 9:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR Y SE REPARO VARIOS PUNTOS DE SECUNDARIA | C22082500026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 592 | 2022-08-25 | 7696 | keep | 0 | Aug | 2022 | 0.0052417 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2022-08-25 09:24 | 2022-08-25 16:30 | 12 | 7:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y SE REEMPLAZO CONECTORES | C22082500028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 426 | 2022-08-25 | 5112 | keep | 0 | Aug | 2022 | 0.0034818 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-08-25 09:28 | 2022-08-25 10:12 | 7 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | LINEA SECUNDARIA SOTERRADA AVERIADA | P22082500022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2022-08-25 | 308 | keep | 0 | Aug | 2022 | 0.00020978 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-08-25 09:31 | 2022-08-25 09:50 | 1 | 0:19 | P | ANIMAL | 1 X 30 EN RISER CRUCE POR PALOMA | C22082500029 | New_Event | Animals | Include | Include | Wildlife | 19 | 2022-08-25 | 19 | keep | 0 | Aug | 2022 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-25 09:32 | 2022-08-25 13:51 | 14 | 4:19 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22802500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-08-25 | 3626 | keep | 0 | Aug | 2022 | 0.0024697 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2022-08-25 09:32 | 2022-08-25 15:32 | 11 | 6:00 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | C22082500030 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 360 | 2022-08-25 | 3960 | keep | 0 | Aug | 2022 | 0.0026971 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2022-08-25 09:34 | 2022-08-25 11:45 | 1 | 2:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 3 EN TRANSFORMADOR SE REPLAZO CAJA QUEMADA EN TRANSFORMADOR | M22082500087 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2022-08-25 | 131 | keep | 0 | Aug | 2022 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-25 09:34 | 2022-08-25 17:50 | 50 | 8:16 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082500086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 496 | 2022-08-25 | 24800 | keep | 0 | Aug | 2022 | 0.016891 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-25 09:36 | 2022-08-25 09:38 | 1785 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% CARGA 1711-04 Y PARTE 1717-01 SE CERRO POR SCADA | B22082500021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-25 | 3570 | keep | 0 | Aug | 2022 | 0.0024315 | 0.0012158 | Momentary | FALSE | FALSE | Not_TMED_Event | 1785
BAYAMON | 2022-08-25 09:36 | 2022-08-25 09:38 | 2000 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% CARGA 1711-04 Y PARTE 1717-01 SE CERRO POR SCADA | B22082500021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-25 | 4000 | keep | 0 | Aug | 2022 | 0.0027244 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2022-08-25 09:36 | 2022-08-25 09:38 | 186 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% CARGA 1711-04 Y PARTE 1717-01 SE CERRO POR SCADA | B22082500021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-25 | 372 | keep | 0 | Aug | 2022 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
HUMACAO | 2022-08-25 09:50 | 2022-08-25 09:51 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | C22082500034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-08-25 09:51 | 2022-08-25 11:44 | 1 | 1:53 | P | ANIMAL | 1 X 30 EN RISER CRUCE POR PALOMA | C22082500029 | Partial_restoration | Animals | Include | Include | Wildlife | 113 | 2022-08-25 | 113 | keep | 0 | Aug | 2022 | 7.6964e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-25 10:20 | 2022-08-25 13:33 | 10 | 3:13 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22082500028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-08-25 | 1930 | keep | 0 | Aug | 2022 | 0.0013145 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-08-25 10:21 | 2022-08-25 11:08 | 150 | 0:47 | P | OTRAS CAUSAS | CLIENTES SE QUEDAN SIN SERVICIO AL RODAR UN N/O | P22082500034 | New_Event | Other Causes | Include | Include | Other | 47 | 2022-08-25 | 7050 | keep | 0 | Aug | 2022 | 0.0048017 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-08-25 10:25 | 2022-08-25 14:15 | 5 | 3:50 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE ABRIO PUENTE HACIA RAMAL POR ARBOL SOBRE LINEAS SE DEJA SIN SERVICIO 2 CLIENTES CASAS DE VERANEO. ESTA PENDIENTE | P22082500036 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 230 | 2022-08-25 | 1150 | keep | 0 | Aug | 2022 | 0.00078326 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-25 10:30 | 2022-08-25 10:52 | 10 | 0:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE PODRIDO | A22082500029 | New_Event | Cutout Failure | Include | Include | Equipment | 22 | 2022-08-25 | 220 | keep | 0 | Aug | 2022 | 0.00014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-25 10:52 | 2022-08-25 14:19 | 40 | 3:27 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082500031 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 207 | 2022-08-25 | 8280 | keep | 0 | Aug | 2022 | 0.0056395 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-25 10:59 | 2022-08-25 11:00 | 7621 | 0:01 | T | ANIMAL | RECERRO | R22082500034 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-25 | 7621 | keep | 0 | Aug | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2022-08-25 11:00 | 2022-08-25 18:50 | 80 | 7:50 | P | ANIMAL | 1 X 80 Y 1 SMU 20 DE 40AMP EN SU - 22A CRUCE X GATO | R22082500080 | 1st_after_momentary | Animals | Include | Include | Wildlife | 470 | 2022-08-25 | 37600 | keep | 0 | Aug | 2022 | 0.025609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-25 11:09 | 2022-08-25 13:08 | 73 | 1:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22082500042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-08-25 | 8687 | keep | 0 | Aug | 2022 | 0.0059167 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
AGUADILLA | 2022-08-25 11:11 | 2022-08-25 11:12 | 80 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082500113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 80 | keep | 0 | Aug | 2022 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-08-25 11:15 | 2022-08-25 12:00 | 11 | 0:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C22082500044 | New_Event | Cutout Failure | Include | Include | Equipment | 45 | 2022-08-25 | 495 | keep | 0 | Aug | 2022 | 0.00033714 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2022-08-25 11:22 | 2022-08-25 13:15 | 30 | 1:53 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22082500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-08-25 | 3390 | keep | 0 | Aug | 2022 | 0.0023089 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-25 11:25 | 2022-08-25 13:36 | 2 | 2:11 | P | DESGANCHE | 1 X 15 EN RISER DESGANCHE DE ENREDADERA | B22082500034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-08-25 | 262 | keep | 0 | Aug | 2022 | 0.00017845 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-08-25 11:27 | 2022-08-25 11:30 | 437 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | R22082500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-25 | 1311 | keep | 0 | Aug | 2022 | 0.00089292 | 0.00029764 | Momentary | FALSE | FALSE | Not_TMED_Event | 437
CANOVANAS | 2022-08-25 11:31 | 2022-08-25 16:10 | 200 | 4:39 | P | DESGANCHE | 2 X 65 1 X 100 Y 2 X 140 DESGANCHE | R22082500036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-08-25 | 55800 | keep | 0 | Aug | 2022 | 0.038005 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-08-25 11:31 | 2022-08-25 13:48 | 44 | 2:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN RISER MAL TIEMPO LLUVIA | C22082500047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 137 | 2022-08-25 | 6028 | keep | 0 | Aug | 2022 | 0.0041056 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
SAN JUAN | 2022-08-25 11:36 | 2022-08-25 11:44 | 34 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5900 PT DE 38KV EN FUEGO | S22082500040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-08-25 | 272 | keep | 0 | Aug | 2022 | 0.00018526 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2022-08-25 11:36 | 2022-08-25 11:44 | 19 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5900 LLEVA 1910-01 PT DE 38KV EN FUEGO | S22082500040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-08-25 | 152 | keep | 0 | Aug | 2022 | 0.00010353 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-08-25 11:36 | 2022-08-25 11:44 | 37 | 0:08 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5900 SU CARGA POR 1512-05 PT DE 38KV EN FUEGO | S22082500040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-08-25 | 296 | keep | 0 | Aug | 2022 | 0.0002016 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2022-08-25 11:37 | 2022-08-25 14:04 | 3597 | 2:27 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO INTERRUPTOR SECCIONALIZANDO ALIMENTADOR. 15% EN SERVICIO | B22082500037 | New_Event | Primary Wire Break | Include | Include | Equipment | 147 | 2022-08-25 | 528759 | keep | 0 | Aug | 2022 | 0.36014 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
PONCE | 2022-08-25 11:39 | 2022-08-25 13:34 | 62 | 1:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN RISER 1 X 65 EN CORTE DE LINEA | P22082500046 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2022-08-25 | 7130 | keep | 0 | Aug | 2022 | 0.0048562 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BARRANQUITAS | 2022-08-25 11:40 | 2022-08-25 15:04 | 60 | 3:24 | P | PARARRAYOS DEFECTUOSO | 1 X 40 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO PARARRAYO | C22082500050 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 204 | 2022-08-25 | 12240 | keep | 0 | Aug | 2022 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-08-25 11:44 | 2022-08-25 15:45 | 85 | 4:01 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22082500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-08-25 | 20485 | keep | 0 | Aug | 2022 | 0.013952 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
UTUADO | 2022-08-25 11:46 | 2022-08-25 17:30 | 3 | 5:44 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR QUEMADO. SE REGO LINEA SECUNDARIA A TRANSFORMADOR CERCA EXISTENTE Y SE CONECTARON LOS TRES CLIENTES. TODOS CON SERVICIO | A22082500041 | New_Event | Service Transformer Failure | Include | Include | Equipment | 344 | 2022-08-25 | 1032 | keep | 0 | Aug | 2022 | 0.00070289 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-25 11:49 | 2022-08-25 17:01 | 200 | 5:12 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1X 50 EN C/L SE REEMPLAZARON 2 PARARRAYOS | B22082500046 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 312 | 2022-08-25 | 62400 | keep | 0 | Aug | 2022 | 0.0425 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-08-25 11:56 | 2022-08-25 11:59 | 5630 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | C22082500054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-25 | 16890 | keep | 0 | Aug | 2022 | 0.011504 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
AGUADILLA | 2022-08-25 12:04 | 2022-08-25 12:05 | 1417 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22082500123 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-08-25 | 1417 | keep | 0 | Aug | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
AGUADILLA | 2022-08-25 12:05 | 2022-08-25 20:00 | 100 | 7:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | M22082500147 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 475 | 2022-08-25 | 47500 | keep | 0 | Aug | 2022 | 0.032352 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-25 12:06 | 2022-08-25 17:31 | 34 | 5:25 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 5900 PT DE 38KV EN FUEGO SE ELIMINO Y LIMPIO AREA Y SE ENERGIZO | S22082500045 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 325 | 2022-08-25 | 11050 | keep | 0 | Aug | 2022 | 0.0075261 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-25 12:06 | 2022-08-25 17:31 | 19 | 5:25 | S | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 5900 PT DE 38KV EN FUEGO SE ELIMINO Y LIMPIO AREA Y SE ENERGIZO LLEVA 1910-01 | S22082500045 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 325 | 2022-08-25 | 6175 | keep | 0 | Aug | 2022 | 0.0042058 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-25 12:06 | 2022-08-25 17:31 | 37 | 5:25 | T | LINEA DE TRANSMISION 38KV | SE ABRE LINEA 5900 PT DE 38KV EN FUEGO SE ELIMINO Y LIMPIO AREA Y SE ENERGIZO SU CARGA POR 1512-05 | S22082500045 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 325 | 2022-08-25 | 12025 | keep | 0 | Aug | 2022 | 0.0081902 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-25 12:07 | 2022-08-25 21:45 | 200 | 9:38 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZARON CRUCETAS | M22082500125 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 578 | 2022-08-25 | 115600 | keep | 0 | Aug | 2022 | 0.078735 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-25 12:14 | 2022-08-25 12:45 | 635 | 0:31 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE CERRO INTERRUPTOR MECANICAMENTE EN LA SUBESTACION - CARGA TRANSFERIDA AL 2306-02 | R22082500048 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 31 | 2022-08-25 | 19685 | keep | 0 | Aug | 2022 | 0.013407 | 0.0004325 | Sustained | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2022-08-25 12:14 | 2022-08-25 12:45 | 1380 | 0:31 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE CERRO INTERRUPTOR MECANICAMENTE EN LA SUBESTACION - LLEVA LA CARGA DEL 2305-04 | R22082500048 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 31 | 2022-08-25 | 42780 | keep | 0 | Aug | 2022 | 0.029137 | 0.00093991 | Sustained | FALSE | FALSE | Not_TMED_Event | 1380
BARRANQUITAS | 2022-08-25 12:19 | 2022-08-25 14:18 | 89 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C22082500063 | New_Event | Primary Wire Break | Include | Include | Equipment | 119 | 2022-08-25 | 10591 | keep | 0 | Aug | 2022 | 0.0072135 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
SAN JUAN | 2022-08-25 12:21 | 2022-08-25 16:20 | 25 | 3:59 | P | DESGANCHE | 2 X 50 EN RISER DESGANCHE | S22082500046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-08-25 | 5975 | keep | 0 | Aug | 2022 | 0.0040695 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-08-25 12:21 | 2022-08-25 18:10 | 200 | 5:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22082500130 | New_Event | Primary Wire Break | Include | Include | Equipment | 349 | 2022-08-25 | 69800 | keep | 0 | Aug | 2022 | 0.04754 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-08-25 12:29 | 2022-08-25 13:40 | 19 | 1:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR SE REPARO SECUNDARIA EN PEDESTAL | C22082500070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 71 | 2022-08-25 | 1349 | keep | 0 | Aug | 2022 | 0.0009188 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-08-25 12:29 | 2022-08-26 02:40 | 1 | 14:11 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR / SE RETIRO IGUANA DE BUSHING DE TRANSFORMADOR | M22082500132 | New_Event | Animals | Include | Include | Wildlife | 851 | 2022-08-25 | 851 | keep | 0 | Aug | 2022 | 0.00057961 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-25 12:44 | 2022-08-25 13:45 | 2 | 1:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | C22082500072 | New_Event | Primary Wire Break | Include | Include | Equipment | 61 | 2022-08-25 | 122 | keep | 0 | Aug | 2022 | 8.3094e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-08-25 12:52 | 2022-08-25 15:52 | 75 | 3:00 | P | DESGANCHE | DESGANCHE 1 X 50 EN CORTE DE LINEA | P22082500053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-08-25 | 13500 | keep | 0 | Aug | 2022 | 0.0091948 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-08-25 12:54 | 2022-08-25 13:40 | 7 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA DEL TRANSFORMADOR PARA REPARAR SECUNDARIA | C22082500074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2022-08-25 | 322 | keep | 0 | Aug | 2022 | 0.00021931 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-08-25 12:57 | 2022-08-25 12:58 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 2126 | keep | 0 | Aug | 2022 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2022-08-25 13:00 | 2022-08-25 13:36 | 12 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXIONES QUEMADAS EN BAJANTE XMR | B22082400055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2022-08-25 | 432 | keep | 0 | Aug | 2022 | 0.00029423 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-25 13:03 | 2022-08-25 13:19 | 4882 | 0:16 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR POSTE PRIMARIO PARTIDO | M22082500266 | New_Event | Primary Pole Failure | Include | Include | Equipment | 16 | 2022-08-25 | 78112 | keep | 0 | Aug | 2022 | 0.053202 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
VEGA BAJA | 2022-08-25 13:04 | 2022-08-25 21:11 | 10 | 8:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37KVA AVERIADO Y 1 X 15 EN XMR | B22082500088 | New_Event | Service Transformer Failure | Include | Include | Equipment | 487 | 2022-08-25 | 4870 | keep | 0 | Aug | 2022 | 0.0033169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-25 13:13 | 2022-08-25 16:40 | 10 | 3:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | M22082500152 | New_Event | Secondary Wire Break | Include | Include | Equipment | 207 | 2022-08-25 | 2070 | keep | 0 | Aug | 2022 | 0.0014099 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-25 13:17 | 2022-08-25 18:12 | 20 | 4:55 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | REMPLAZO EL SU-4 | R22082500059 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 295 | 2022-08-25 | 5900 | keep | 0 | Aug | 2022 | 0.0040185 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-25 13:19 | 2022-08-25 17:09 | 350 | 3:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | GOI # MY-220825-01A REMPLAZO DE POSTE PARTIDO | M22082500161 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 230 | 2022-08-25 | 80500 | keep | 0 | Aug | 2022 | 0.054828 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-25 13:30 | 2022-08-25 23:30 | 300 | 10:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO Y CRUCETAS PARTIDAS EN OTRO POSTE | M22082500163 | New_Event | Primary Pole Failure | Include | Include | Equipment | 600 | 2022-08-25 | 180000 | keep | 0 | Aug | 2022 | 0.1226 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
ARECIBO | 2022-08-25 13:30 | 2022-08-25 15:18 | 7 | 1:48 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50KVA X 50KVA | A22082500044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 108 | 2022-08-25 | 756 | keep | 0 | Aug | 2022 | 0.00051491 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-25 13:32 | 2022-08-25 15:26 | 10 | 1:54 | P | SECUNDARIA/DESGANCHE | DESGANCHE DE ENREDADERA Y 1 X 10 EN XMR | B22082500097 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 114 | 2022-08-25 | 1140 | keep | 0 | Aug | 2022 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-25 13:32 | 2022-08-25 19:40 | 50 | 6:08 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082500133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 368 | 2022-08-25 | 18400 | keep | 0 | Aug | 2022 | 0.012532 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-25 13:34 | 2022-08-25 16:48 | 5 | 3:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082500046 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2022-08-25 | 970 | keep | 0 | Aug | 2022 | 0.00066066 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-25 13:36 | 2022-08-25 13:40 | 652 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082500101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-25 | 2608 | keep | 0 | Aug | 2022 | 0.0017763 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-25 13:36 | 2022-08-25 13:40 | 2704 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082500101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-08-25 | 10816 | keep | 0 | Aug | 2022 | 0.0073667 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2022-08-25 13:40 | 2022-08-25 19:39 | 2 | 5:59 | P | DESGANCHE | 1 X 15 EN RISER DESGANCHE DE ENREDADERA | B22082500034 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 359 | 2022-08-25 | 718 | keep | 0 | Aug | 2022 | 0.00048903 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-25 13:49 | 2022-08-25 13:50 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-25 13:49 | 2022-08-25 13:50 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 4456 | keep | 0 | Aug | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
SAN JUAN | 2022-08-25 13:57 | 2022-08-25 16:54 | 200 | 2:57 | P | DESGANCHE | SUM20 DE 150 AMP. DESGANCHE | S22082500068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-08-25 | 35400 | keep | 0 | Aug | 2022 | 0.024111 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-25 14:04 | 2022-08-25 14:41 | 3057 | 0:37 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR AL CERRAR MACHETES EN OPERACIONES PARA SECCIONALIZAR ALIMENTADOR | B22082500037 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 37 | 2022-08-25 | 113109 | keep | 0 | Aug | 2022 | 0.077038 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-25 14:05 | 2022-08-25 17:43 | 180 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | C22082500094 | New_Event | Primary Wire Break | Include | Include | Equipment | 218 | 2022-08-25 | 39240 | keep | 0 | Aug | 2022 | 0.026726 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
VEGA BAJA | 2022-08-25 14:05 | 2022-08-25 14:06 | 1284 | 0:01 | T | DESGANCHE | RECIERRE | B22082500113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-25 | 1284 | keep | 0 | Aug | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2022-08-25 14:06 | 2022-08-25 20:00 | 351 | 5:54 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B22082500120 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 354 | 2022-08-25 | 124254 | keep | 0 | Aug | 2022 | 0.084629 | 0.00023906 | Sustained | FALSE | FALSE | Not_TMED_Event | 351
SAN JUAN | 2022-08-25 14:09 | 2022-08-25 15:38 | 25 | 1:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22082500075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-08-25 | 2225 | keep | 0 | Aug | 2022 | 0.0015154 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-25 14:11 | 2022-08-25 15:03 | 15 | 0:52 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE REPARO SECUNDARIA CRUZADA | B22082500116 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 52 | 2022-08-25 | 780 | keep | 0 | Aug | 2022 | 0.00053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-08-25 14:14 | 2022-08-25 17:06 | 7 | 2:52 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A22082500053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 172 | 2022-08-25 | 1204 | keep | 0 | Aug | 2022 | 0.00082004 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-08-25 14:20 | 2022-08-25 17:08 | 1950 | 2:48 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REMPLAZO AISLADORES ROTOS | A22082500059 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 168 | 2022-08-25 | 327600 | keep | 0 | Aug | 2022 | 0.22313 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
SAN JUAN | 2022-08-25 14:21 | 2022-08-25 18:00 | 1 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO CAUSA | S22082500079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-08-25 | 219 | keep | 0 | Aug | 2022 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-25 14:22 | 2022-08-25 16:25 | 30 | 2:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO CAJA PRIMARIA DEL TRANSFORMADOR SE REPARO SECUNDARIA Y REEMPLAZO BAJANTE | C22082500098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 123 | 2022-08-25 | 3690 | keep | 0 | Aug | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-25 14:23 | 2022-08-26 17:05 | 10 | 26:42 | P | TRANSFORMADOR AVERIADO | REMPLAZAR TRANSFORMADOR AVERIADO DE 25KVA POR 25 KVA | M22082500179 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1602 | 2022-08-25 | 16020 | keep | 0 | Aug | 2022 | 0.010911 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-25 14:23 | 2022-08-25 14:58 | 1 | 0:35 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA RETIRAR TOMA VACANTE Y REALIZAR DESGANCHE | B22082500125 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 35 | 2022-08-25 | 35 | keep | 0 | Aug | 2022 | 2.3838e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-25 14:30 | 2022-08-25 15:22 | 8 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | S22082500071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2022-08-25 | 416 | keep | 0 | Aug | 2022 | 0.00028334 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-25 14:34 | 2022-08-25 21:50 | 15 | 7:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082500183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 436 | 2022-08-25 | 6540 | keep | 0 | Aug | 2022 | 0.0044544 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-25 14:35 | 2022-08-25 14:36 | 5961 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1713-05 LLEVANDO 95% CARGA 1717-02 | B22082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 5961 | keep | 0 | Aug | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-08-25 14:35 | 2022-08-25 14:36 | 865 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1713-05 LLEVANDO 95% CARGA 1717-02 | B22082500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 865 | keep | 0 | Aug | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
CANOVANAS | 2022-08-25 14:35 | 2022-08-25 14:58 | 1 | 0:23 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN BANCO DE XMR FALTA DE MANTENIMIENTO EN SUB DE AAA | R22082500063 | New_Event | Customer-Related Interruption | Include | Include | Public | 23 | 2022-08-25 | 23 | keep | 0 | Aug | 2022 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-25 14:37 | 2022-08-25 20:10 | 1 | 5:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | C22082500102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2022-08-25 | 333 | keep | 0 | Aug | 2022 | 0.0002268 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-25 14:41 | 2022-08-25 15:34 | 3597 | 0:53 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO INTERRUPTOR SECCIONALIZANDO ALIMENTADOR POR PUENTE ABIERTO DE LINEA A MACHETE EN RISER. 15% EN SERVICIO | B22082500037 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 53 | 2022-08-25 | 190641 | keep | 0 | Aug | 2022 | 0.12984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-25 14:43 | 2022-08-25 18:30 | 17 | 3:47 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | B22082500143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2022-08-25 | 3859 | keep | 0 | Aug | 2022 | 0.0026283 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2022-08-25 14:45 | 2022-08-25 15:53 | 80 | 1:08 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082500186 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 68 | 2022-08-25 | 5440 | keep | 0 | Aug | 2022 | 0.0037052 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-08-25 14:52 | 2022-08-25 16:05 | 12 | 1:13 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR DE DE 50KVA A 2400 VOLTIOS POR UNO DE LA MISMA CAPACIDAD | P22082500079 | New_Event | Service Transformer Failure | Include | Include | Equipment | 73 | 2022-08-25 | 876 | keep | 0 | Aug | 2022 | 0.00059664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-25 14:55 | 2022-08-26 01:16 | 50 | 10:21 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082500189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 621 | 2022-08-25 | 31050 | keep | 0 | Aug | 2022 | 0.021148 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-25 14:58 | 2022-08-25 14:59 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082500081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 527 | keep | 0 | Aug | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
CANOVANAS | 2022-08-25 14:59 | 2022-08-25 15:51 | 91 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | R22082500064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-08-25 | 4732 | keep | 0 | Aug | 2022 | 0.0032229 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
SAN JUAN | 2022-08-25 15:05 | 2022-08-26 08:41 | 30 | 17:36 | P | NO SE REPORTO CAUSA | 2 X 100 EN RISER | S22082500099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1056 | 2022-08-25 | 31680 | keep | 0 | Aug | 2022 | 0.021577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-08-25 15:11 | 2022-08-25 18:51 | 20 | 3:40 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082500070 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 220 | 2022-08-25 | 4400 | keep | 0 | Aug | 2022 | 0.0029968 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-25 15:13 | 2022-08-25 19:00 | 8 | 3:47 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | A22082500071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-08-25 | 1816 | keep | 0 | Aug | 2022 | 0.0012369 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-25 15:19 | 2022-08-25 17:58 | 1 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22082500108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2022-08-25 | 159 | keep | 0 | Aug | 2022 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-25 15:22 | 2022-08-25 15:23 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S22082500108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 2203 | keep | 0 | Aug | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
CANOVANAS | 2022-08-25 15:29 | 2022-08-25 17:41 | 8 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R22082500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-08-25 | 1056 | keep | 0 | Aug | 2022 | 0.00071924 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-25 15:34 | 2022-08-25 16:51 | 3057 | 1:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO LINEA A MACHETE EN RISER Y SE REEMPLAZARON 2 MACHETES. 95% DE ALIMENTADOR EN SERVICIO | B22082500037 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 77 | 2022-08-25 | 235389 | keep | 0 | Aug | 2022 | 0.16032 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-25 15:41 | 2022-08-25 19:28 | 1 | 3:47 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS | A22082500076 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 227 | 2022-08-25 | 227 | keep | 0 | Aug | 2022 | 0.00015461 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-25 15:48 | 2022-08-25 18:14 | 50 | 2:26 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082500077 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 146 | 2022-08-25 | 7300 | keep | 0 | Aug | 2022 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-25 15:55 | 2022-08-25 16:49 | 90 | 0:54 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R22082500077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2022-08-25 | 4860 | keep | 0 | Aug | 2022 | 0.0033101 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2022-08-25 16:06 | 2022-08-25 17:24 | 40 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S22082500124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-08-25 | 3120 | keep | 0 | Aug | 2022 | 0.002125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-25 16:15 | 2022-08-26 11:36 | 80 | 19:21 | P | DESGANCHE | 1 X 80 EN CL DSGANCHE | S22082500127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1161 | 2022-08-25 | 92880 | keep | 0 | Aug | 2022 | 0.06326 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-25 16:16 | 2022-08-26 10:46 | 18 | 18:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA PORTAFUSIBLE 1 X 40 EN RISER | S22082500128 | New_Event | Cutout Failure | Include | Include | Equipment | 1110 | 2022-08-25 | 19980 | keep | 0 | Aug | 2022 | 0.013608 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2022-08-25 16:32 | 2022-08-25 16:34 | 826 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 20% POR 1620-05 SE PROBO QUEDO EN SERVICIO | S22082500134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-25 | 1652 | keep | 0 | Aug | 2022 | 0.0011252 | 0.00056258 | Momentary | FALSE | FALSE | Not_TMED_Event | 826
CANOVANAS | 2022-08-25 16:32 | 2022-08-25 16:34 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 20% DEL 1206-03 SE PROBO QUEDO EN SERVICIO | R22082500134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-25 | 3230 | keep | 0 | Aug | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2022-08-25 16:44 | 2022-08-25 20:22 | 20 | 3:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE Y LINEA SECUNDARIA | R22082500083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 218 | 2022-08-25 | 4360 | keep | 0 | Aug | 2022 | 0.0029696 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-25 16:48 | 2022-08-25 18:44 | 2366 | 1:56 | T | CONDUCTOR ROTO O ABIERTO | INTERRUPTOR ABIERTO SE ABRIO MACHETES SECCIONALIZAR LINEA PRIMARIA ROTA HAY PARCIAL | M22082500276 | New_Event | Primary Wire Break | Include | Include | Equipment | 116 | 2022-08-25 | 274456 | keep | 0 | Aug | 2022 | 0.18693 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
BAYAMON | 2022-08-25 16:51 | 2022-08-25 16:58 | 180 | 0:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO CAJAS PRIMARIAS HACIA URBANIZACION VALLE DE CERRO GORDO. 100% EN SERVICIO | B22082500037 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 7 | 2022-08-25 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-08-25 16:51 | 2022-08-25 16:52 | 1833 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082500100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 1833 | keep | 0 | Aug | 2022 | 0.0012484 | 0.0012484 | Momentary | FALSE | FALSE | Not_TMED_Event | 1833
SAN JUAN | 2022-08-25 16:55 | 2022-08-25 16:58 | 5619 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1620-03 | S22082500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-25 | 16857 | keep | 0 | Aug | 2022 | 0.011481 | 0.0038271 | Momentary | FALSE | FALSE | Not_TMED_Event | 5619
SAN JUAN | 2022-08-25 16:55 | 2022-08-25 16:58 | 36 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1620-03 | S22082500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-25 | 108 | keep | 0 | Aug | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-08-25 16:55 | 2022-08-25 16:58 | 1073 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1620-1 Y 90% DEL 1336-07 | S22082500139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-25 | 3219 | keep | 0 | Aug | 2022 | 0.0021924 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
HUMACAO | 2022-08-25 17:01 | 2022-08-25 21:24 | 19 | 4:23 | P | TERMINACION SOTERRADA AVERIADA | 1 X 40 EN AEREO PROVISIONAL SE REPARO STRESS CONE Y 1 NX DE 18 AMP. | C22082500117 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 263 | 2022-08-25 | 4997 | keep | 0 | Aug | 2022 | 0.0034034 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-08-25 17:02 | 2022-08-25 19:38 | 15 | 2:36 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | S22082500146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-08-25 | 2340 | keep | 0 | Aug | 2022 | 0.0015938 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-25 17:09 | 2022-08-25 17:32 | 4882 | 0:23 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO INTERRUPTOR PARA CERRAR PUENTES PRIMARIOS EN TRONCAL LUEGO DE REMPLAZO DE POSTE | M22082500266 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 23 | 2022-08-25 | 112286 | keep | 0 | Aug | 2022 | 0.076477 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-25 17:11 | 2022-08-25 22:15 | 50 | 5:04 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | S22082500151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2022-08-25 | 15200 | keep | 0 | Aug | 2022 | 0.010353 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-25 17:19 | 2022-08-25 19:45 | 10 | 2:26 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22082500273 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 146 | 2022-08-25 | 1460 | keep | 0 | Aug | 2022 | 0.0009944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-25 17:19 | 2022-08-25 19:53 | 20 | 2:34 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082500084 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 154 | 2022-08-25 | 3080 | keep | 0 | Aug | 2022 | 0.0020978 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-25 17:30 | 2022-08-25 19:00 | 9 | 1:30 | P | CAUSAS EXTERNAS | SE VERIFICO CAJA PRIMARIA DEL TRANSFORMADOR ABIERTA POR IMPACTO DE CAMION A LA SECUNDARIA, SE REEMPLAZO 150 PIES DE SECUNDARIA | C22082500121 | New_Event | Damage From Public | Include | Include | Public | 90 | 2022-08-25 | 810 | keep | 0 | Aug | 2022 | 0.00055169 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2022-08-25 17:34 | 2022-08-25 19:38 | 175 | 2:04 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIAMARIO IMPACTADO POR CAMION | C22082500123 | New_Event | Damage From Public | Include | Include | Public | 124 | 2022-08-25 | 21700 | keep | 0 | Aug | 2022 | 0.01478 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BAYAMON | 2022-08-25 17:50 | 2022-08-25 18:39 | 70 | 0:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 40 EN CORTE DE LINEA LLUVIA FUERTE | B22082500238 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 49 | 2022-08-25 | 3430 | keep | 0 | Aug | 2022 | 0.0023362 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-08-25 17:56 | 2022-08-25 19:42 | 12 | 1:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C22082500126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 106 | 2022-08-25 | 1272 | keep | 0 | Aug | 2022 | 0.00086635 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-25 17:57 | 2022-08-25 22:29 | 81 | 4:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN C/L SE REMPLAZO AISLADOR | B22082500241 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 272 | 2022-08-25 | 22032 | keep | 0 | Aug | 2022 | 0.015006 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
UTUADO | 2022-08-25 17:58 | 2022-08-25 20:30 | 150 | 2:32 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082500090 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 152 | 2022-08-25 | 22800 | keep | 0 | Aug | 2022 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-25 18:02 | 2022-08-25 18:03 | 2435 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S22082500163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 2435 | keep | 0 | Aug | 2022 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2022-08-25 18:02 | 2022-08-25 18:03 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-08 LLEVANDO CARGA 1907-05 | S22082500163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 2956 | keep | 0 | Aug | 2022 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2022-08-25 18:22 | 2022-08-25 18:24 | 723 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA | B22082500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-25 | 1446 | keep | 0 | Aug | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-25 18:22 | 2022-08-25 18:24 | 198 | 0:02 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA | B22082500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-25 | 396 | keep | 0 | Aug | 2022 | 0.00026971 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-08-25 18:22 | 2022-08-25 18:24 | 1976 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA | B22082500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-25 | 3952 | keep | 0 | Aug | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CAGUAS | 2022-08-25 18:30 | 2022-08-26 14:15 | 3 | 19:45 | P | EXCAVACIONES | SE CONSTRUYO AEREO PROVISIONAL SECUNDARIO | C22082400199 | Partial_restoration | Excavation | Include | Include | Public | 1185 | 2022-08-25 | 3555 | keep | 0 | Aug | 2022 | 0.0024213 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-25 18:30 | 2022-08-26 07:31 | 25 | 13:01 | P | DESGANCHE | 1X40 EN C/L | C22082500128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 781 | 2022-08-25 | 19525 | keep | 0 | Aug | 2022 | 0.013298 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-25 18:33 | 2022-08-25 18:43 | 723 | 0:10 | T | DESGANCHE | SE ABRIO INTERRUPTOR A PETICION DE PERSONAL DE CAMPO TRABAJANDO CERCA QUE VIERON RAMA QUEMANDOSE EN LA LINEA. SE RETIRO RAMA CON VARETA | B22082500260 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-08-25 | 7230 | keep | 0 | Aug | 2022 | 0.0049243 | 0.00049243 | Sustained | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-25 18:33 | 2022-08-25 18:43 | 198 | 0:10 | P | DESGANCHE | SE ABRIO INTERRUPTOR A PETICION DE PERSONAL DE CAMPO TRABAJANDO CERCA QUE VIERON RAMA QUEMANDOSE EN LA LINEA. SE RETIRO RAMA CON VARETA | B22082500260 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-08-25 | 1980 | keep | 0 | Aug | 2022 | 0.0013486 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-08-25 18:33 | 2022-08-25 18:43 | 1976 | 0:10 | T | DESGANCHE | SE ABRIO INTERRUPTOR A PETICION DE PERSONAL DE CAMPO TRABAJANDO CERCA QUE VIERON RAMA QUEMANDOSE EN LA LINEA. SE RETIRO RAMA CON VARETA | B22082500260 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 10 | 2022-08-25 | 19760 | keep | 0 | Aug | 2022 | 0.013458 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-08-25 18:41 | 2022-08-25 19:57 | 8 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22082500276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2022-08-25 | 608 | keep | 0 | Aug | 2022 | 0.00041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-08-25 18:41 | 2022-08-25 21:01 | 15 | 2:20 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR PROBO MALO, SE AÃ‘ADIO CARGA A TRANSFORMADOR CERCANO | C22082500129 | New_Event | Service Transformer Failure | Include | Include | Equipment | 140 | 2022-08-25 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-08-25 18:44 | 2022-08-25 21:00 | 150 | 2:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO MACHETES | M22082500233 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 136 | 2022-08-25 | 20400 | keep | 0 | Aug | 2022 | 0.013894 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-25 18:45 | 2022-08-25 20:33 | 60 | 1:48 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082500098 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 108 | 2022-08-25 | 6480 | keep | 0 | Aug | 2022 | 0.0044135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-25 18:54 | 2022-08-25 19:35 | 107 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22082500449 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-08-25 | 4387 | keep | 0 | Aug | 2022 | 0.002988 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2022-08-25 18:54 | 2022-08-25 19:35 | 1666 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22082500449 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-08-25 | 68306 | keep | 0 | Aug | 2022 | 0.046523 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2022-08-25 18:54 | 2022-08-25 19:35 | 4387 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M22082500449 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2022-08-25 | 179867 | keep | 0 | Aug | 2022 | 0.12251 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2022-08-25 18:54 | 2022-08-25 23:30 | 3147 | 4:36 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LA LINEA 15700 | M22082500454 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 276 | 2022-08-25 | 868572 | keep | 0 | Aug | 2022 | 0.59158 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2022-08-25 18:54 | 2022-08-25 23:30 | 4304 | 4:36 | S | LINEA DE TRANSMISION 38KV | EN SERVICIO LA LINEA 15700 | M22082500454 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 276 | 2022-08-25 | 1187904 | keep | 0 | Aug | 2022 | 0.80908 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2022-08-25 19:05 | 2022-08-25 19:07 | 2617 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1719-19 SE CERRO POR SCADA | B22082500291 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-25 | 5234 | keep | 0 | Aug | 2022 | 0.0035649 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2022-08-25 19:17 | 2022-08-25 20:24 | 15 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN AEREO PROVISIONAL | B22082500295 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-08-25 | 1005 | keep | 0 | Aug | 2022 | 0.0006845 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-25 19:20 | 2022-08-26 12:40 | 10 | 17:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | B22082500296 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1040 | 2022-08-25 | 10400 | keep | 0 | Aug | 2022 | 0.0070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-25 19:35 | 2022-08-25 19:36 | 13 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22082500299 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 13 | keep | 0 | Aug | 2022 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2022-08-25 19:37 | 2022-08-25 21:15 | 20 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22082500540 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-08-25 | 1960 | keep | 0 | Aug | 2022 | 0.0013349 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-25 19:37 | 2022-08-25 22:54 | 40 | 3:17 | P | ANIMAL | 1 X 40 EN C/L CRUCE X CULEBRA Y REMPLAZO PARARRAYO | C22082500135 | New_Event | Animals | Include | Include | Wildlife | 197 | 2022-08-25 | 7880 | keep | 0 | Aug | 2022 | 0.005367 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-08-25 19:44 | 2022-08-26 12:50 | 5 | 17:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22082500106 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1026 | 2022-08-25 | 5130 | keep | 0 | Aug | 2022 | 0.003494 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-25 19:46 | 2022-08-25 21:20 | 105 | 1:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN C/L 1 X 65 EN C/L | B22082500303 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2022-08-25 | 9870 | keep | 0 | Aug | 2022 | 0.0067224 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
CANOVANAS | 2022-08-25 19:48 | 2022-08-25 21:09 | 22 | 1:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | R22082500105 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2022-08-25 | 1782 | keep | 0 | Aug | 2022 | 0.0012137 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
PONCE | 2022-08-25 19:48 | 2022-08-25 19:49 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082500133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 2379 | keep | 0 | Aug | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2022-08-25 19:50 | 2022-08-26 12:40 | 15 | 16:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA EN VARIOS PUNTOS | B22082500304 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1010 | 2022-08-25 | 15150 | keep | 0 | Aug | 2022 | 0.010319 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-08-25 19:52 | 2022-08-25 22:15 | 14 | 2:23 | P | TRANSFORMADOR AVERIADO | 1 X 25 EN C/L XMR QUEMADO | B22082500306 | New_Event | Service Transformer Failure | Include | Include | Equipment | 143 | 2022-08-25 | 2002 | keep | 0 | Aug | 2022 | 0.0013636 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-08-25 20:00 | 2022-08-26 10:45 | 16 | 14:45 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRE CORTE DE LINEA PARA DESENREDAR FASE | S22082500185 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 885 | 2022-08-25 | 14160 | keep | 0 | Aug | 2022 | 0.0096443 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2022-08-25 20:06 | 2022-08-25 22:53 | 100 | 2:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C22082500142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2022-08-25 | 16700 | keep | 0 | Aug | 2022 | 0.011374 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-25 20:20 | 2022-08-25 23:21 | 4 | 3:01 | P | TRANSFORMADOR AVERIADO | ABRIO XMR PARA REPARAR BUSHING SECUNDARIO | R22082500107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2022-08-25 | 724 | keep | 0 | Aug | 2022 | 0.00049311 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-25 20:26 | 2022-08-25 21:30 | 60 | 1:04 | P | DESGANCHE | 1 X 30 Y 1 X 50 EN C/L DESGANCHO | R22082500108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-08-25 | 3840 | keep | 0 | Aug | 2022 | 0.0026154 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-25 20:28 | 2022-08-25 23:54 | 20 | 3:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REMPLAZO PORTAFUSIBLE QUEMADO | C22082500158 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2022-08-25 | 4120 | keep | 0 | Aug | 2022 | 0.0028061 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-08-25 20:37 | 2022-08-26 00:18 | 15 | 3:41 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22082500600 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 221 | 2022-08-25 | 3315 | keep | 0 | Aug | 2022 | 0.0022578 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-08-25 20:48 | 2022-08-26 09:32 | 8 | 12:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22082500112 | New_Event | Secondary Wire Break | Include | Include | Equipment | 764 | 2022-08-25 | 6112 | keep | 0 | Aug | 2022 | 0.0041629 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-08-25 20:54 | 2022-08-26 05:08 | 1 | 8:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X20 EN BANCO DE XMRS Y SE REMPLAZO CAJA PRIMARIA | C22082500165 | New_Event | Cutout Failure | Include | Include | Equipment | 494 | 2022-08-25 | 494 | keep | 0 | Aug | 2022 | 0.00033646 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-25 21:00 | 2022-08-25 22:05 | 411 | 1:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO VER GOI SJ-220825-03 | S22082500189 | New_Event | Primary Wire Break | Include | Include | Equipment | 65 | 2022-08-25 | 26715 | keep | 0 | Aug | 2022 | 0.018195 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
UTUADO | 2022-08-25 21:20 | 2022-08-26 20:58 | 250 | 23:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO | A22082500114 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1418 | 2022-08-25 | 354500 | keep | 0 | Aug | 2022 | 0.24145 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
GUAYAMA | 2022-08-25 21:36 | 2022-08-26 10:14 | 1 | 12:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CAJA DE MONTURA | P22082500160 | New_Event | Primary Wire Break | Include | Include | Equipment | 758 | 2022-08-25 | 758 | keep | 0 | Aug | 2022 | 0.00051627 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-25 21:38 | 2022-08-26 07:18 | 50 | 9:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO SE REPORTO CAUSA | P22082500136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 580 | 2022-08-25 | 29000 | keep | 0 | Aug | 2022 | 0.019752 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-25 21:43 | 2022-08-26 19:23 | 10 | 21:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO VIVO/NEUTRAL EN SECUNDARIA | B22082500323 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1300 | 2022-08-25 | 13000 | keep | 0 | Aug | 2022 | 0.0088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-25 22:05 | 2022-08-25 22:40 | 25 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA ROTA | M22082500601 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-08-25 | 875 | keep | 0 | Aug | 2022 | 0.00059596 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-08-25 22:07 | 2022-08-25 22:08 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082500173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 3744 | keep | 0 | Aug | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
FAJARDO | 2022-08-25 22:12 | 2022-08-26 00:09 | 100 | 1:57 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | R22082500118 | New_Event | Animals | Include | Include | Wildlife | 117 | 2022-08-25 | 11700 | keep | 0 | Aug | 2022 | 0.0079688 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-25 22:22 | 2022-08-26 10:50 | 12 | 12:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5 KVA | B22082500306 | New_Event | Service Transformer Failure | Include | Include | Equipment | 748 | 2022-08-25 | 8976 | keep | 0 | Aug | 2022 | 0.0061135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-25 22:30 | 2022-08-26 10:45 | 42 | 12:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE CERRO PUENTE DE LINEA A CAJA | B22082500329 | New_Event | Primary Wire Break | Include | Include | Equipment | 735 | 2022-08-25 | 30870 | keep | 0 | Aug | 2022 | 0.021025 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
AGUADILLA | 2022-08-25 22:41 | 2022-08-26 12:00 | 10 | 13:19 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 50KV POR 37.5 KVA | M22082500649 | New_Event | Service Transformer Failure | Include | Include | Equipment | 799 | 2022-08-25 | 7990 | keep | 0 | Aug | 2022 | 0.005442 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-25 23:12 | 2022-08-25 23:13 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2404-08 | R22082500135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 3464 | keep | 0 | Aug | 2022 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2022-08-25 23:12 | 2022-08-25 23:13 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2404-05 | R22082500135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-25 | 2675 | keep | 0 | Aug | 2022 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
BARRANQUITAS | 2022-08-25 23:15 | 2022-08-26 06:36 | 23 | 7:21 | P | DESGANCHE | 1X65 EN C/L | C22082500184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 441 | 2022-08-25 | 10143 | keep | 0 | Aug | 2022 | 0.0069084 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
FAJARDO | 2022-08-25 23:20 | 2022-08-26 01:20 | 100 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22082500137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-08-25 | 12000 | keep | 0 | Aug | 2022 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-08-26 | 2022-08-26 09:58 | 12 | 9:58 | P | ANIMAL | 1X25 EN C/L CRUCE POR AVE | C22082600001 | New_Event | Animals | Include | Include | Wildlife | 598 | 2022-08-26 | 7176 | keep | 0 | Aug | 2022 | 0.0048875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-08-26 01:00 | 2022-08-26 08:45 | 15 | 7:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A22082600002 | New_Event | Primary Wire Break | Include | Include | Equipment | 465 | 2022-08-26 | 6975 | keep | 0 | Aug | 2022 | 0.0047506 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-26 01:40 | 2022-08-26 14:38 | 150 | 12:58 | P | DESGANCHE | 2X65 EN C/L | B22082600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 778 | 2022-08-26 | 116700 | keep | 0 | Aug | 2022 | 0.079484 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-26 01:43 | 2022-08-26 13:09 | 100 | 11:26 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S22082600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 686 | 2022-08-26 | 68600 | keep | 0 | Aug | 2022 | 0.046723 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-26 02:45 | 2022-08-26 02:46 | 1883 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22082600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-26 | 1883 | keep | 0 | Aug | 2022 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | Not_TMED_Event | 1883
PONCE | 2022-08-26 04:38 | 2022-08-26 04:39 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082600032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-26 | 2379 | keep | 0 | Aug | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
HUMACAO | 2022-08-26 05:08 | 2022-08-26 05:10 | 2126 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CERRADO X CONTROL | C22082600007 | Additional_clients | Cutout Failure | Include | Include | Equipment | 2 | 2022-08-26 | 4252 | keep | 0 | Aug | 2022 | 0.002896 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-08-26 05:10 | 2022-08-26 07:42 | 1 | 2:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X20 EN BANCO DE XMRS Y SE REMPLAZO CAJA PRIMARIA | C22082500165 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 152 | 2022-08-26 | 152 | keep | 0 | Aug | 2022 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-26 05:14 | 2022-08-26 05:19 | 2368 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22082600016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-26 | 11840 | keep | 0 | Aug | 2022 | 0.0080642 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2022-08-26 05:14 | 2022-08-26 05:19 | 538 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22082600016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-26 | 2690 | keep | 0 | Aug | 2022 | 0.0018321 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2022-08-26 05:14 | 2022-08-26 05:19 | 1284 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22082600016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-26 | 6420 | keep | 0 | Aug | 2022 | 0.0043726 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2022-08-26 05:14 | 2022-08-26 05:27 | 652 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2022-08-26 | 8476 | keep | 0 | Aug | 2022 | 0.005773 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-26 05:14 | 2022-08-26 05:27 | 2704 | 0:13 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 13 | 2022-08-26 | 35152 | keep | 0 | Aug | 2022 | 0.023942 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
ARECIBO | 2022-08-26 05:30 | 2022-08-26 09:01 | 5 | 3:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22082600005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 211 | 2022-08-26 | 1055 | keep | 0 | Aug | 2022 | 0.00071856 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-26 05:39 | 2022-08-26 10:30 | 100 | 4:51 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2022-08-26 | 29100 | keep | 0 | Aug | 2022 | 0.01982 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-26 05:59 | 2022-08-26 09:29 | 65 | 3:30 | P | DESGANCHE | 2X65 EN C/L | C22082600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-08-26 | 13650 | keep | 0 | Aug | 2022 | 0.009297 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-08-26 06:06 | 2022-08-26 10:40 | 61 | 4:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22082600007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2022-08-26 | 16714 | keep | 0 | Aug | 2022 | 0.011384 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
AGUADILLA | 2022-08-26 06:51 | 2022-08-26 17:08 | 20 | 10:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA POR 75 KVA | M22082600012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 617 | 2022-08-26 | 12340 | keep | 0 | Aug | 2022 | 0.0084047 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-26 07:06 | 2022-08-26 09:30 | 30 | 2:24 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | B22082600031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-08-26 | 4320 | keep | 0 | Aug | 2022 | 0.0029423 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-26 07:08 | 2022-08-26 18:20 | 25 | 11:12 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE MASIVO | S22082600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 672 | 2022-08-26 | 16800 | keep | 0 | Aug | 2022 | 0.011442 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-08-26 07:20 | 2022-08-26 10:52 | 7 | 3:32 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR | C22082600019 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 212 | 2022-08-26 | 1484 | keep | 0 | Aug | 2022 | 0.0010107 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-08-26 07:22 | 2022-08-26 08:59 | 50 | 1:37 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMA | P22082600040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-08-26 | 4850 | keep | 0 | Aug | 2022 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-26 07:41 | 2022-08-26 07:42 | 5809 | 0:01 | T | ANIMAL | RECERRO | B22082600000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-26 | 5809 | keep | 0 | Aug | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-08-26 07:42 | 2022-08-26 12:06 | 25 | 4:24 | P | ANIMAL | 1 X 30 EN C/L AVE | B22082600050 | 1st_after_momentary | Animals | Include | Include | Wildlife | 264 | 2022-08-26 | 6600 | keep | 0 | Aug | 2022 | 0.0044952 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-26 07:43 | 2022-08-26 11:10 | 8 | 3:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22082600009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 207 | 2022-08-26 | 1656 | keep | 0 | Aug | 2022 | 0.0011279 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-26 07:44 | 2022-08-26 09:00 | 20 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082600018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2022-08-26 | 1520 | keep | 0 | Aug | 2022 | 0.0010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-08-26 07:49 | 2022-08-26 13:02 | 35 | 5:13 | P | DESGANCHE | 1X30 EN C/L | C22082600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2022-08-26 | 10955 | keep | 0 | Aug | 2022 | 0.0074614 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-08-26 07:57 | 2022-08-26 10:35 | 20 | 2:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22082600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-08-26 | 3160 | keep | 0 | Aug | 2022 | 0.0021523 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-26 08:02 | 2022-08-26 18:09 | 8 | 10:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X10 EN XMR SE REMPLAZO PORTAFUSIBLE | B22082600042 | New_Event | Cutout Failure | Include | Include | Equipment | 607 | 2022-08-26 | 4856 | keep | 0 | Aug | 2022 | 0.0033074 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-26 08:05 | 2022-08-26 16:09 | 1 | 8:04 | P | OTRAS CAUSAS | SE BYPASEO EQUIPO MEDICION 2 X 25 EN TRANSCLOUSURE 2 X 30 EN RISER | S22082600014 | New_Event | Other Causes | Include | Include | Other | 484 | 2022-08-26 | 484 | keep | 0 | Aug | 2022 | 0.00032965 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-26 08:10 | 2022-08-26 09:29 | 50 | 1:19 | P | CONDUCTOR ROTO O ABIERTO | 1X80 EN C/L SE REPARO/SUBIO CONDUCTOR PRIMARIO | C22082600028 | New_Event | Primary Wire Break | Include | Include | Equipment | 79 | 2022-08-26 | 3950 | keep | 0 | Aug | 2022 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-26 08:22 | 2022-08-26 12:00 | 100 | 3:38 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | R22082600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-08-26 | 21800 | keep | 0 | Aug | 2022 | 0.014848 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-08-26 08:22 | 2022-08-26 09:11 | 1 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA ABIERTA | C22082600031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2022-08-26 | 49 | keep | 0 | Aug | 2022 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-26 08:23 | 2022-08-26 09:44 | 100 | 1:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22082600024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-08-26 | 8100 | keep | 0 | Aug | 2022 | 0.0055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-26 08:26 | 2022-08-26 10:30 | 5 | 2:04 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082600021 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 124 | 2022-08-26 | 620 | keep | 0 | Aug | 2022 | 0.00042228 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-26 08:32 | 2022-08-26 08:34 | 1746 | 0:02 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B22082600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-26 | 3492 | keep | 0 | Aug | 2022 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2022-08-26 08:34 | 2022-08-26 14:43 | 100 | 6:09 | P | DESGANCHE | 1X125 DE SU-13A @ RISER | B22082600081 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 369 | 2022-08-26 | 36900 | keep | 0 | Aug | 2022 | 0.025132 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-26 08:40 | 2022-08-26 08:42 | 723 | 0:02 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTRO LLEVA 1711-05 & 10% 1711-04 | B22082600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-26 | 1446 | keep | 0 | Aug | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-26 08:40 | 2022-08-26 08:42 | 198 | 0:02 | P | DESGANCHE | DISPARO Y SE CERRO POR CONTROL 10% DE LA CARGA TRANSFERIDA AL 1711-02 | B22082600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-26 | 396 | keep | 0 | Aug | 2022 | 0.00026971 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-08-26 08:40 | 2022-08-26 08:42 | 1976 | 0:02 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL CARGA TRANSFERIDA AL 1711-02 | B22082600000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-26 | 3952 | keep | 0 | Aug | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-08-26 08:42 | 2022-08-26 10:05 | 100 | 1:23 | P | DESGANCHE | 1 X 100 EN C/L SE RETIRO RAMA | B22082600029 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-08-26 | 8300 | keep | 0 | Aug | 2022 | 0.0056531 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-26 08:46 | 2022-08-26 10:13 | 8 | 1:27 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REEMPLAZARON BAJANTES SECUNDARIOS Y LINEA SECUNDARIA SE REALIZO DESGANCHE SECUNDARIO | R22082500138 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 87 | 2022-08-26 | 696 | keep | 0 | Aug | 2022 | 0.00047404 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-26 08:47 | 2022-08-26 10:50 | 30 | 2:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082600016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-08-26 | 3690 | keep | 0 | Aug | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-26 08:49 | 2022-08-26 08:50 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-26 | 1362 | keep | 0 | Aug | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
PONCE | 2022-08-26 09:09 | 2022-08-26 11:35 | 1 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE EN MONTURA | P22082600046 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2022-08-26 | 146 | keep | 0 | Aug | 2022 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-26 09:16 | 2022-08-27 11:39 | 12 | 26:23 | P | SECUNDARIA/OTROS | SE REMPLAZO PEDESTAL TIPO MOLE | C22082600050 | New_Event |  |  |  |  | 1583 | 2022-08-26 | 18996 | keep | 0 | Aug | 2022 | 0.012938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-26 09:16 | 2022-08-26 16:41 | 60 | 7:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 C/L FUERTES LLUVIAS | C22082500111 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 445 | 2022-08-26 | 26700 | keep | 0 | Aug | 2022 | 0.018185 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-08-26 09:20 | 2022-08-26 13:18 | 15 | 3:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA X 37.5KVA | C22082600052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 238 | 2022-08-26 | 3570 | keep | 0 | Aug | 2022 | 0.0024315 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-26 09:27 | 2022-08-26 11:36 | 400 | 2:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | M22082600028 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2022-08-26 | 51600 | keep | 0 | Aug | 2022 | 0.035145 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BARRANQUITAS | 2022-08-26 09:44 | 2022-08-26 11:17 | 100 | 1:33 | P | DESGANCHE | 1X140 EN C/L | C22082600056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-08-26 | 9300 | keep | 0 | Aug | 2022 | 0.0063342 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-08-26 09:47 | 2022-08-26 14:57 | 24 | 5:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA EN C/L | R22082600017 | New_Event | Primary Wire Break | Include | Include | Equipment | 310 | 2022-08-26 | 7440 | keep | 0 | Aug | 2022 | 0.0050674 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2022-08-26 09:49 | 2022-08-26 09:50 | 652 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082600094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-26 | 652 | keep | 0 | Aug | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-26 09:49 | 2022-08-26 09:50 | 2704 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082600094 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-26 | 2704 | keep | 0 | Aug | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
GUAYAMA | 2022-08-26 09:56 | 2022-08-26 11:50 | 5 | 1:54 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | P22082600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-08-26 | 570 | keep | 0 | Aug | 2022 | 0.00038822 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-26 10:00 | 2022-08-26 12:19 | 30 | 2:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER SE AJUSTA CAJA PRIMARIA | S22082600060 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2022-08-26 | 4170 | keep | 0 | Aug | 2022 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-26 10:02 | 2022-08-26 13:45 | 10 | 3:43 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO CAUSA | S22082600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-08-26 | 2230 | keep | 0 | Aug | 2022 | 0.0015188 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-26 10:24 | 2022-08-27 10:55 | 1 | 24:31 | P | ANIMAL | 1 X 10 Y 1 X 25 EN MONTURA SE RETIRO IGUANA | B22082600106 | New_Event | Animals | Include | Include | Wildlife | 1471 | 2022-08-26 | 1471 | keep | 0 | Aug | 2022 | 0.0010019 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-26 10:30 | 2022-08-26 11:45 | 18 | 1:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA CON PROBLEMAS DE VOLTAJE | B22082600093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 75 | 2022-08-26 | 1350 | keep | 0 | Aug | 2022 | 0.00091948 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-08-26 10:30 | 2022-08-26 11:15 | 10 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR REMPLAZAR BARRAS SECUNDARIAS | M22082600044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-08-26 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-26 10:43 | 2022-08-26 10:46 | 652 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082600114 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-26 | 1956 | keep | 0 | Aug | 2022 | 0.0013322 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-26 10:43 | 2022-08-26 10:46 | 2704 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22082600114 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-08-26 | 8112 | keep | 0 | Aug | 2022 | 0.005525 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2022-08-26 10:45 | 2022-08-26 11:11 | 50 | 0:26 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA DE DESENREDO LINEA | S22082500185 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 26 | 2022-08-26 | 1300 | keep | 0 | Aug | 2022 | 0.00088542 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-26 10:48 | 2022-08-26 11:31 | 20 | 0:43 | P | DESGANCHE | 1X 30 EN C/L DESGANCHE | R22082600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-08-26 | 860 | keep | 0 | Aug | 2022 | 0.00058574 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-26 10:56 | 2022-08-26 10:57 | 154 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO 25% POR 1342-04 MAL TIEMPO LLUVIA | S22082600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-26 | 154 | keep | 0 | Aug | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-08-26 10:56 | 2022-08-26 10:57 | 390 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 25% DEL 1203-03 MAL TIEMPO LLUVIA | S22082600000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-26 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-08-26 10:57 | 2022-08-26 14:44 | 5 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA FUERTE | S22082600056 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2022-08-26 | 1135 | keep | 0 | Aug | 2022 | 0.00077304 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-26 11:08 | 2022-08-26 11:10 | 3798 | 0:02 | T | NO SE REPORTO CAUSA | CERRADO POR CONTROL | B22082600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-26 | 7596 | keep | 0 | Aug | 2022 | 0.0051736 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
CAGUAS | 2022-08-26 11:28 | 2022-08-26 12:37 | 15 | 1:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 37.5KVA - X - 25KVA (POR DISPONIBILIDAD) | C22082600087 | New_Event | Service Transformer Failure | Include | Include | Equipment | 69 | 2022-08-26 | 1035 | keep | 0 | Aug | 2022 | 0.00070493 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-08-26 11:31 | 2022-08-26 11:42 | 1894 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22082600039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-08-26 | 20834 | keep | 0 | Aug | 2022 | 0.01419 | 0.00129 | Sustained | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2022-08-26 11:31 | 2022-08-26 11:42 | 4154 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22082600039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-08-26 | 45694 | keep | 0 | Aug | 2022 | 0.031122 | 0.0028293 | Sustained | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2022-08-26 11:31 | 2022-08-26 11:42 | 424 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22082600039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-08-26 | 4664 | keep | 0 | Aug | 2022 | 0.0031766 | 0.00028878 | Sustained | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-08-26 11:31 | 2022-08-26 11:42 | 2708 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22082600043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-08-26 | 29788 | keep | 0 | Aug | 2022 | 0.020288 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-08-26 11:31 | 2022-08-26 11:42 | 2524 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22082600043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-08-26 | 27764 | keep | 0 | Aug | 2022 | 0.01891 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-08-26 11:31 | 2022-08-26 11:42 | 1648 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22082600043 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-08-26 | 18128 | keep | 0 | Aug | 2022 | 0.012347 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2022-08-26 11:42 | 2022-08-26 15:18 | 20 | 3:36 | P | DESGANCHE | 1X 30 EN C/L DESGANCHE | R22082600026 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-08-26 | 4320 | keep | 0 | Aug | 2022 | 0.0029423 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-26 11:50 | 2022-08-26 12:51 | 1 | 1:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO EN RISER | R22082600052 | New_Event | Primary Wire Break | Include | Include | Equipment | 61 | 2022-08-26 | 61 | keep | 0 | Aug | 2022 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-26 11:51 | 2022-08-26 16:45 | 12 | 4:54 | P | NO SE REPORTO CAUSA | 2 X 10 EN XMR | C22082600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 294 | 2022-08-26 | 3528 | keep | 0 | Aug | 2022 | 0.0024029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-08-26 11:57 | 2022-08-26 12:55 | 140 | 0:58 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22082600061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-08-26 | 8120 | keep | 0 | Aug | 2022 | 0.0055305 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
SAN JUAN | 2022-08-26 12:00 | 2022-08-26 20:10 | 20 | 8:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | S22082600055 | New_Event | Primary Pole Failure | Include | Include | Equipment | 490 | 2022-08-26 | 9800 | keep | 0 | Aug | 2022 | 0.0066747 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-08-26 12:11 | 2022-08-26 14:02 | 30 | 1:51 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22082600060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-08-26 | 3330 | keep | 0 | Aug | 2022 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-26 12:15 | 2022-08-26 19:54 | 25 | 7:39 | P | ARBOL SOBRE LINEA | 1X15 EN XMR SE RETIRO ARBOL (COMPLETO) DE LA SECUNDARIA | B22082600127 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 459 | 2022-08-26 | 11475 | keep | 0 | Aug | 2022 | 0.0078156 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-26 12:23 | 2022-08-26 13:34 | 40 | 1:11 | P | DESGANCHE | 1X40 EN C/L | C22082600093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-08-26 | 2840 | keep | 0 | Aug | 2022 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-26 12:43 | 2022-08-26 14:24 | 10 | 1:41 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS | M22082600064 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 101 | 2022-08-26 | 1010 | keep | 0 | Aug | 2022 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-26 13:06 | 2022-08-26 13:50 | 15 | 0:44 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE RETIRO TOMA CLIENTE CRUZADA Y SE CERRO XMR | R22082600031 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 44 | 2022-08-26 | 660 | keep | 0 | Aug | 2022 | 0.00044952 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-26 13:27 | 2022-08-26 14:39 | 100 | 1:12 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B22082600142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2022-08-26 | 7200 | keep | 0 | Aug | 2022 | 0.0049039 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-08-26 13:28 | 2022-08-26 14:11 | 10 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONECTORES EN BAJANTE SECUNDARIO | R22082600069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2022-08-26 | 430 | keep | 0 | Aug | 2022 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-26 13:30 | 2022-08-26 15:44 | 1 | 2:14 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22082600045 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 134 | 2022-08-26 | 134 | keep | 0 | Aug | 2022 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-26 13:36 | 2022-08-26 14:24 | 3 | 0:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 37.5KVA X 37.5KVA | C22082600100 | New_Event | Service Transformer Failure | Include | Include | Equipment | 48 | 2022-08-26 | 144 | keep | 0 | Aug | 2022 | 9.8078e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 1225 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 8575 | keep | 0 | Aug | 2022 | 0.0058404 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 1452 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 10164 | keep | 0 | Aug | 2022 | 0.0069227 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 154 | 0:07 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 25% DE SU CARGA POR 1342-04 | S22082600088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 1078 | keep | 0 | Aug | 2022 | 0.00073422 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 211 | 0:07 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 PARTE POR 1345-02 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 1477 | keep | 0 | Aug | 2022 | 0.001006 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 790 | 0:07 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 SU CARGA POR 1345-03 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 5530 | keep | 0 | Aug | 2022 | 0.0037665 | 0.00053807 | Sustained | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 291 | 0:07 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 CARGA POR 1345-02 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 2037 | keep | 0 | Aug | 2022 | 0.0013874 | 0.0001982 | Sustained | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 660 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 4620 | keep | 0 | Aug | 2022 | 0.0031467 | 0.00044952 | Sustained | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 435 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 LLEVA CARGA 1342-05 Y PARTE DEL 1330-04 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 3045 | keep | 0 | Aug | 2022 | 0.0020739 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 259 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 LLEVA 1342-02 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 1813 | keep | 0 | Aug | 2022 | 0.0012348 | 0.0001764 | Sustained | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 686 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 4802 | keep | 0 | Aug | 2022 | 0.0032706 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2022-08-26 13:45 | 2022-08-26 13:52 | 953 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-26 | 6671 | keep | 0 | Aug | 2022 | 0.0045436 | 0.00064908 | Sustained | FALSE | FALSE | Not_TMED_Event | 953
AGUADILLA | 2022-08-26 13:46 | 2022-08-26 18:00 | 165 | 4:14 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082600071 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 254 | 2022-08-26 | 41910 | keep | 0 | Aug | 2022 | 0.028545 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
SAN JUAN | 2022-08-26 13:52 | 2022-08-26 14:00 | 10 | 0:08 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO CAUSA | S22082600044 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 8 | 2022-08-26 | 80 | keep | 0 | Aug | 2022 | 5.4488e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-26 13:55 | 2022-08-26 17:44 | 1 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO XMR | R22082600072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-08-26 | 229 | keep | 0 | Aug | 2022 | 0.00015597 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-26 13:57 | 2022-08-26 20:13 | 95 | 6:16 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 40 EN C/L SE REMPLAZO POSTE PRIMARIO | P22082600091 | New_Event | Primary Pole Failure | Include | Include | Equipment | 376 | 2022-08-26 | 35720 | keep | 0 | Aug | 2022 | 0.024329 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2022-08-26 13:58 | 2022-08-26 15:08 | 3957 | 1:10 | T | DESGANCHE | DISPARO SE RETIRA RAMA SOBRE FASE DE PISO CON VARETA Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S22082600098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2022-08-26 | 276990 | keep | 0 | Aug | 2022 | 0.18866 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2022-08-26 14:00 | 2022-08-26 16:22 | 55 | 2:22 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L Y SE REPARO PUENTE LINEA A CAJA EN C/L | S22082600010 | New_Event | Primary Wire Break | Include | Include | Equipment | 142 | 2022-08-26 | 7810 | keep | 0 | Aug | 2022 | 0.0053194 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
FAJARDO | 2022-08-26 14:16 | 2022-08-26 15:12 | 1 | 0:56 | P | DESGANCHE | 1X 30 EN C/L DESGANCHE | R22082600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-08-26 | 56 | keep | 0 | Aug | 2022 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-26 14:17 | 2022-08-26 17:38 | 30 | 3:21 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | P22082600075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2022-08-26 | 6030 | keep | 0 | Aug | 2022 | 0.004107 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-26 14:23 | 2022-08-26 15:35 | 5 | 1:12 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082600077 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 72 | 2022-08-26 | 360 | keep | 0 | Aug | 2022 | 0.00024519 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-08-26 14:29 | 2022-08-26 15:24 | 10 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22082600077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-08-26 | 550 | keep | 0 | Aug | 2022 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-26 14:36 | 2022-08-26 17:00 | 150 | 2:24 | P | DESCONECTIVO DEFECTUOSO | EN SERVICIO SE CAMBIO MACHETE | S22082600146 | New_Event | Switch Failure | Include | Include | Equipment | 144 | 2022-08-26 | 21600 | keep | 0 | Aug | 2022 | 0.014712 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-08-26 14:52 | 2022-08-26 15:15 | 1 | 0:23 | P | NO SE REPORTO CAUSA | 3 X 25 SMU20 EN SU | R22082600077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-08-26 | 23 | keep | 0 | Aug | 2022 | 1.5665e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-08-26 14:57 | 2022-08-26 15:48 | 48 | 0:51 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R22082600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2022-08-26 | 2448 | keep | 0 | Aug | 2022 | 0.0016673 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
FAJARDO | 2022-08-26 14:57 | 2022-08-26 15:22 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONECTOR SECUNDARIO EN BAJANTE DE RISER | R22082600074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-08-26 | 250 | keep | 0 | Aug | 2022 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-26 14:57 | 2022-08-26 15:58 | 3 | 1:01 | P | DESGANCHE | SE REPARO NEUTRAL EN SECUNDARIO Y SE DESGANCHO | C22082600110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2022-08-26 | 183 | keep | 0 | Aug | 2022 | 0.00012464 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-26 15:08 | 2022-08-26 16:34 | 1500 | 1:26 | P | DESGANCHE | SE CERRO INTELIRRUPTER CARR. 1 FTE. PANADERIA FRANCAIS NO DITALIZADO | S22082600196 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-08-26 | 129000 | keep | 0 | Aug | 2022 | 0.087861 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-26 15:09 | 2022-08-26 18:33 | 40 | 3:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A22082600059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-08-26 | 8160 | keep | 0 | Aug | 2022 | 0.0055577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-26 15:14 | 2022-08-26 18:31 | 50 | 3:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22082600061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-08-26 | 9850 | keep | 0 | Aug | 2022 | 0.0067088 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-26 15:31 | 2022-08-26 16:59 | 2052 | 1:28 | P | CABLE SOTERRADO AVERIADO | DISPARO SE ABRIO SU-14 A SU-12 Y SE CERRO BKR. QUEDO EN SERVICIO 40%, 20% DE SU CARGA POR 1118-10 | S22082600254 | New_Event | UG Cable Fault | Include | Include | Equipment | 88 | 2022-08-26 | 180576 | keep | 0 | Aug | 2022 | 0.12299 | 0.0013976 | Sustained | FALSE | FALSE | Not_TMED_Event | 2052
BAYAMON | 2022-08-26 15:38 | 2022-08-26 15:39 | 3295 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22082600164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-26 | 3295 | keep | 0 | Aug | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
UTUADO | 2022-08-26 15:41 | 2022-08-26 17:11 | 100 | 1:30 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA POR RAYOS | A22082600067 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 90 | 2022-08-26 | 9000 | keep | 0 | Aug | 2022 | 0.0061299 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:07 | 1225 | 0:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-08-26 | 24500 | keep | 0 | Aug | 2022 | 0.016687 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:07 | 1452 | 0:20 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-08-26 | 29040 | keep | 0 | Aug | 2022 | 0.019779 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:07 | 154 | 0:20 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 25% DE SU CARGA POR 1203-01 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 20 | 2022-08-26 | 3080 | keep | 0 | Aug | 2022 | 0.0020978 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 15:53 | 828 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO LLEVA 40% DEL 1204-04 LLEVA 60% DEL 1204-03 LLEVA 20% DEL 1303-02 | S22082600254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-08-26 | 4968 | keep | 0 | Aug | 2022 | 0.0033837 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 15:53 | 1978 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO 40% POR 1206-04 LLEVA 60% DEL 1204-03 LLEVA 20% DEL 1303-02 | S22082600254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-08-26 | 11868 | keep | 0 | Aug | 2022 | 0.0080832 | 0.0013472 | Sustained | FALSE | FALSE | Not_TMED_Event | 1978
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 15:53 | 1799 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 40% DEL 1204-04 LLEVA 60% DEL 1204-03 LLEVA 20% DEL 1303-02 | S22082600254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-08-26 | 10794 | keep | 0 | Aug | 2022 | 0.0073517 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 15:53 | 487 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO LLEVA 40% DEL 1204-04 LLEVA 60% DEL 1204-03 LLEVA 20% DEL 1303-02 | S22082600254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-08-26 | 2922 | keep | 0 | Aug | 2022 | 0.0019902 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:31 | 660 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2022-08-26 | 29040 | keep | 0 | Aug | 2022 | 0.019779 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:31 | 435 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2022-08-26 | 19140 | keep | 0 | Aug | 2022 | 0.013036 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:31 | 259 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2022-08-26 | 11396 | keep | 0 | Aug | 2022 | 0.0077618 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:31 | 686 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2022-08-26 | 30184 | keep | 0 | Aug | 2022 | 0.020558 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:47 | 2022-08-26 16:31 | 953 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | S22082600299 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2022-08-26 | 41932 | keep | 0 | Aug | 2022 | 0.02856 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 15:55 | 2022-08-26 17:23 | 828 | 1:28 | P | LINEA DE TRANSMISION 38KV | TRAMO LINEA 3100 ENCIMA TRAMO DEL 1303-2 SE ABRIO MACHETE PARA SECCIONALIZAR 60% POR 1206-04 | S22082600254 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-08-26 | 72864 | keep | 0 | Aug | 2022 | 0.049627 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-08-26 15:55 | 2022-08-26 17:23 | 1977 | 1:28 | P | LINEA DE TRANSMISION 38KV | TRAMO LINEA 3100 ENCIMA TRAMO DEL 1303-2 SE ABRIO MACHETE PARA SECCIONALIZAR 40% POR 1206-04 | S22082600254 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-08-26 | 173976 | keep | 0 | Aug | 2022 | 0.11849 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-26 15:55 | 2022-08-26 17:23 | 1799 | 1:28 | T | LINEA DE TRANSMISION 38KV | TRAMO LINEA 3100 ENCIMA TRAMO DEL 1303-2 SE ABRIO MACHETE PARA SECCIONALIZAR 100% DEL 1206-04 40% 1204-04 60% 1204-03 Y 10% DEL 1303-02 | S22082600254 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 88 | 2022-08-26 | 158312 | keep | 0 | Aug | 2022 | 0.10783 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-08-26 15:55 | 2022-08-27 14:18 | 20 | 22:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE XMR Y SE REPARO SECUNDARIA | S22082600246 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1343 | 2022-08-26 | 26860 | keep | 0 | Aug | 2022 | 0.018294 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-26 15:57 | 2022-08-26 19:20 | 50 | 3:23 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR 1 X 15 EN TRANSFORMADOR 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082600094 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 203 | 2022-08-26 | 10150 | keep | 0 | Aug | 2022 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-26 15:58 | 2022-08-26 19:07 | 30 | 3:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X30 EN C/L SE REMPLAZO DISCO PRIMARIO | B22082600170 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 189 | 2022-08-26 | 5670 | keep | 0 | Aug | 2022 | 0.0038618 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-26 15:58 | 2022-08-26 17:43 | 1 | 1:45 | P | NO SE REPORTO CAUSA | 2X10 EN XMR | B22082600170 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-08-26 | 105 | keep | 0 | Aug | 2022 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-26 16:05 | 2022-08-27 09:00 | 1 | 16:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M22082600098 | New_Event | Primary Wire Break | Include | Include | Equipment | 1015 | 2022-08-26 | 1015 | keep | 0 | Aug | 2022 | 0.00069131 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-26 16:13 | 2022-08-26 17:50 | 6 | 1:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | M22082600100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 97 | 2022-08-26 | 582 | keep | 0 | Aug | 2022 | 0.0003964 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-26 16:21 | 2022-08-26 17:30 | 80 | 1:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-08-26 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-26 16:29 | 2022-08-27 11:30 | 150 | 19:01 | P | MAL TIEMPO/RAYOS | 1 X 100, 1 X 50, 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082600111 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1141 | 2022-08-26 | 171150 | keep | 0 | Aug | 2022 | 0.11657 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-08-26 16:36 | 2022-08-27 12:32 | 65 | 19:56 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22082600404 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1196 | 2022-08-26 | 77740 | keep | 0 | Aug | 2022 | 0.052948 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2022-08-26 16:38 | 2022-08-26 16:43 | 3957 | 0:05 | T | DESGANCHE | DISPARO AL CERRAR INTELLIRUPTER CARR.1 FTE FRANCAIS | S22082600196 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-08-26 | 19785 | keep | 0 | Aug | 2022 | 0.013475 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 16:43 | 2022-08-26 18:05 | 3957 | 1:22 | T | DESGANCHE | DISPARO AL CERRAR MACHETE CARR.1 | S22082600196 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-08-26 | 324474 | keep | 0 | Aug | 2022 | 0.221 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-26 16:48 | 2022-08-27 15:34 | 60 | 22:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 2 X 40 EN CORTE DE LINEA POR LLUVIAS | M22082600121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1366 | 2022-08-26 | 81960 | keep | 0 | Aug | 2022 | 0.055823 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-26 16:55 | 2022-08-26 18:07 | 100 | 1:12 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE DE RAMA CRUZANDO LINEAS | S22082600466 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-08-26 | 7200 | keep | 0 | Aug | 2022 | 0.0049039 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-26 16:59 | 2022-08-26 17:39 | 1231 | 0:40 | P | CABLE SOTERRADO AVERIADO | SE CERRO SU-14 A SU-12 70% ENSERVICIO | S22082600254 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 40 | 2022-08-26 | 49240 | keep | 0 | Aug | 2022 | 0.033537 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 17:03 | 2022-08-26 17:07 | 74 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-11 LLEVANDO CARGA 1521-02 SE CERRO POR SCADA | S22082600496 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-26 | 296 | keep | 0 | Aug | 2022 | 0.0002016 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2022-08-26 17:03 | 2022-08-26 17:07 | 1370 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-11 LLEVANDO CARGA 1521-02 SE CERRO POR SCADA | S22082600496 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-08-26 | 5480 | keep | 0 | Aug | 2022 | 0.0037324 | 0.0009331 | Momentary | FALSE | FALSE | Not_TMED_Event | 1370
CAGUAS | 2022-08-26 17:16 | 2022-08-26 18:45 | 6 | 1:29 | P | ANIMAL | 2 X 65 Y 2 X 140 EN CORTES DE LINEA CRUCE CON AVE | C22082600116 | New_Event | Animals | Include | Include | Wildlife | 89 | 2022-08-26 | 534 | keep | 0 | Aug | 2022 | 0.0003637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-26 17:23 | 2022-08-26 19:02 | 48 | 1:39 | P | LINEA DE TRANSMISION 38KV | TRAMO LINEA 3100 ENCIMA TRAMO SE CERRO MACHETE EN SERVICIO 1303-02 POR 1206-04 | S22082600254 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 99 | 2022-08-26 | 4752 | keep | 0 | Aug | 2022 | 0.0032366 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
HUMACAO | 2022-08-26 17:25 | 2022-08-26 18:19 | 60 | 0:54 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C22082600118 | New_Event | Animals | Include | Include | Wildlife | 54 | 2022-08-26 | 3240 | keep | 0 | Aug | 2022 | 0.0022067 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-26 17:29 | 2022-08-26 17:52 | 12 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON BAJANTES SECUNDARIOS EN XMR | R22082600081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2022-08-26 | 276 | keep | 0 | Aug | 2022 | 0.00018798 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-26 17:38 | 2022-08-26 21:15 | 100 | 3:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082600131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-08-26 | 21700 | keep | 0 | Aug | 2022 | 0.01478 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-26 17:39 | 2022-08-26 17:59 | 615 | 0:20 | P | CABLE SOTERRADO AVERIADO | SE CERRO MH-5 A MH-11B 99% EN SERVICIO Y LA CARGA 5% DEL 1115-5 | S22082600254 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 20 | 2022-08-26 | 12300 | keep | 0 | Aug | 2022 | 0.0083775 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-26 17:50 | 2022-08-26 22:30 | 20 | 4:40 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO FASE A TIERRA | M22082600139 | New_Event | Animals | Include | Include | Wildlife | 280 | 2022-08-26 | 5600 | keep | 0 | Aug | 2022 | 0.0038141 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-26 17:50 | 2022-08-26 21:56 | 50 | 4:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2022-08-26 | 12300 | keep | 0 | Aug | 2022 | 0.0083775 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-26 17:53 | 2022-08-26 17:54 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-26 | 551 | keep | 0 | Aug | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
BAYAMON | 2022-08-26 17:57 | 2022-08-26 17:59 | 172 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22082600185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-26 | 344 | keep | 0 | Aug | 2022 | 0.0002343 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-08-26 17:59 | 2022-08-26 18:49 | 1 | 0:50 | P | CABLE SOTERRADO AVERIADO | SE CERRO RISER A HOSPITAL SAN JORGE Y SE DEJO FUERA CARGA APARTAMENTOS SAN JORGE CABLE AVERIADO Y STRES CONE SE ORIENTO A CLIENTE | S22082600254 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 50 | 2022-08-26 | 50 | keep | 0 | Aug | 2022 | 3.4055e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 18:02 | 2022-08-26 22:27 | 56 | 4:25 | P | DESGANCHE | 1 X 100 Y 1 X 50 EN C/L SE DESGANCHO | S22082600564 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2022-08-26 | 14840 | keep | 0 | Aug | 2022 | 0.010107 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
SAN JUAN | 2022-08-26 18:05 | 2022-08-26 18:07 | 3957 | 0:02 | T | DESGANCHE | SE ABRIO MACHETE Y SE CERRO INTELIRRUPTER 80% EN SERVICIO | S22082600196 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-08-26 | 7914 | keep | 0 | Aug | 2022 | 0.0053902 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-26 18:07 | 2022-08-26 19:04 | 2500 | 0:57 | T | DESGANCHE | SE SECCIONALIZO TRAMO ARBOL SOBRE LINEA | S22082600196 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 57 | 2022-08-26 | 142500 | keep | 0 | Aug | 2022 | 0.097056 | 0.0017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 2500
BARRANQUITAS | 2022-08-26 18:07 | 2022-08-26 20:22 | 10 | 2:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA QUEMADA | C22082600120 | New_Event | Cutout Failure | Include | Include | Equipment | 135 | 2022-08-26 | 1350 | keep | 0 | Aug | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-26 18:12 | 2022-08-26 23:13 | 40 | 5:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22082600145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2022-08-26 | 12040 | keep | 0 | Aug | 2022 | 0.0082004 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-26 18:14 | 2022-08-26 19:34 | 40 | 1:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO DESGANCHE Y 1 X 80 EN C/L | R22082600088 | New_Event | Primary Wire Break | Include | Include | Equipment | 80 | 2022-08-26 | 3200 | keep | 0 | Aug | 2022 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-26 18:58 | 2022-08-26 19:03 | 225 | 0:05 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1303-05 | S22082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-26 | 1125 | keep | 0 | Aug | 2022 | 0.00076623 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-26 18:58 | 2022-08-26 19:03 | 870 | 0:05 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1303-04 | S22082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-08-26 | 4350 | keep | 0 | Aug | 2022 | 0.0029628 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
UTUADO | 2022-08-26 18:58 | 2022-08-26 20:11 | 8 | 1:13 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR POR RAYOS | A22082600098 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 73 | 2022-08-26 | 584 | keep | 0 | Aug | 2022 | 0.00039776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-26 19:01 | 2022-08-26 21:21 | 300 | 2:20 | P | DESGANCHE | 1X100 EN C/L SE REFIRIO PARA DESGANCHE | S22082600598 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-08-26 | 42000 | keep | 0 | Aug | 2022 | 0.028606 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-26 19:03 | 2022-08-26 21:12 | 12 | 2:09 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE | S22082600603 | New_Event | Primary Wire Break | Include | Include | Equipment | 129 | 2022-08-26 | 1548 | keep | 0 | Aug | 2022 | 0.0010543 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-26 19:04 | 2022-08-26 19:56 | 1500 | 0:52 | P | DESGANCHE | SE REALIZO DEGANCHE Y SE CERRO MACHETE 100% EN SERVICIO | S22082600196 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-08-26 | 78000 | keep | 0 | Aug | 2022 | 0.053125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-08-26 19:12 | 2022-08-26 21:24 | 300 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R22082600099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2022-08-26 | 39600 | keep | 0 | Aug | 2022 | 0.026971 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-08-26 19:37 | 2022-08-27 11:30 | 50 | 15:53 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L PARARAYO EN XMR | S22082600623 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 953 | 2022-08-26 | 47650 | keep | 0 | Aug | 2022 | 0.032454 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-26 19:41 | 2022-08-27 14:55 | 50 | 19:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA Y SE REPUSO 1 X 50 EN CORTE DE LINEA | M22082600168 | New_Event | Cutout Failure | Include | Include | Equipment | 1154 | 2022-08-26 | 57700 | keep | 0 | Aug | 2022 | 0.039299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-26 19:46 | 2022-08-26 20:50 | 6 | 1:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082600170 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 64 | 2022-08-26 | 384 | keep | 0 | Aug | 2022 | 0.00026154 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-08-26 19:58 | 2022-08-27 13:26 | 65 | 17:28 | P | DESGANCHE | 1 X 80 C/L DESGANCHE | S22082600631 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2022-08-26 | 68120 | keep | 0 | Aug | 2022 | 0.046396 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-08-26 20:02 | 2022-08-26 22:30 | 4 | 2:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A22082600105 | New_Event | Primary Wire Break | Include | Include | Equipment | 148 | 2022-08-26 | 592 | keep | 0 | Aug | 2022 | 0.00040321 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-08-26 20:15 | 2022-08-27 09:25 | 8 | 13:10 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA REQUIERE DESGANCHE | A22082600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 790 | 2022-08-26 | 6320 | keep | 0 | Aug | 2022 | 0.0043045 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-26 20:21 | 2022-08-27 03:55 | 48 | 7:34 | P | NO SE REPORTO CAUSA | 3X80 EN C/L | C22082600132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 454 | 2022-08-26 | 21792 | keep | 0 | Aug | 2022 | 0.014842 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
MAYAGÃœEZ | 2022-08-26 20:42 | 2022-08-27 14:08 | 10 | 17:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 25KVA | M22082600182 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 1046 | 2022-08-26 | 10460 | keep | 0 | Aug | 2022 | 0.0071243 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-26 20:50 | 2022-08-26 21:42 | 10 | 0:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO PORTAFUSIBLE | R22082600107 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2022-08-26 | 520 | keep | 0 | Aug | 2022 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-26 21:00 | 2022-08-27 02:26 | 50 | 5:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S22082600650 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 326 | 2022-08-26 | 16300 | keep | 0 | Aug | 2022 | 0.011102 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-26 21:12 | 2022-08-26 21:52 | 30 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y SE CERRO PUENTE PRIMARIO | S22082600603 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 40 | 2022-08-26 | 1200 | keep | 0 | Aug | 2022 | 0.00081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-26 21:20 | 2022-08-27 10:27 | 40 | 13:07 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | C22082600169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 787 | 2022-08-26 | 31480 | keep | 0 | Aug | 2022 | 0.021441 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-26 21:20 | 2022-08-27 12:50 | 30 | 15:30 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082600185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 930 | 2022-08-26 | 27900 | keep | 0 | Aug | 2022 | 0.019003 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-26 21:44 | 2022-08-26 23:00 | 4 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22082600188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2022-08-26 | 304 | keep | 0 | Aug | 2022 | 0.00020705 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-08-26 21:55 | 2022-08-26 21:56 | 763 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22082600108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-26 | 763 | keep | 0 | Aug | 2022 | 0.00051968 | 0.00051968 | Momentary | FALSE | FALSE | Not_TMED_Event | 763
CAGUAS | 2022-08-26 21:57 | 2022-08-27 13:31 | 22 | 15:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE XMR | C22082600174 | New_Event | Secondary Wire Break | Include | Include | Equipment | 934 | 2022-08-26 | 20548 | keep | 0 | Aug | 2022 | 0.013995 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
YAUCO | 2022-08-26 22:11 | 2022-08-27 00:20 | 200 | 2:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22082600198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-08-26 | 25800 | keep | 0 | Aug | 2022 | 0.017572 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-08-26 22:17 | 2022-08-26 22:18 | 3005 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-26 | 3005 | keep | 0 | Aug | 2022 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
FAJARDO | 2022-08-26 22:55 | 2022-08-27 08:43 | 34 | 9:48 | P | DESGANCHE | DESGANCHE Y 1 X 30 EN C/L | R22082600110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2022-08-26 | 19992 | keep | 0 | Aug | 2022 | 0.013616 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2022-08-26 23:35 | 2022-08-27 13:45 | 8 | 14:10 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REPARO EN PEDESTAL | S22082600673 | New_Event |  |  |  |  | 850 | 2022-08-26 | 6800 | keep | 0 | Aug | 2022 | 0.0046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-27 00:45 | 2022-08-27 09:35 | 5 | 8:50 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22082700006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 530 | 2022-08-27 | 2650 | keep | 0 | Aug | 2022 | 0.0018049 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-08-27 00:48 | 2022-08-27 10:40 | 30 | 9:52 | P | ANIMAL | 1X65 EN C/L POR CRUCE DE AVE | C22082700004 | New_Event | Animals | Include | Include | Wildlife | 592 | 2022-08-27 | 17760 | keep | 0 | Aug | 2022 | 0.012096 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-08-27 01:02 | 2022-08-27 01:03 | 1606 | 0:01 | T | DESGANCHE | RECIERRE | C22082700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-27 | 1606 | keep | 0 | Aug | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2022-08-27 01:03 | 2022-08-27 03:06 | 30 | 2:03 | P | DESGANCHE | 1X50 EN C/L | C22082700006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-08-27 | 3690 | keep | 0 | Aug | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-27 01:28 | 2022-08-27 09:00 | 60 | 7:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22082700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 452 | 2022-08-27 | 27120 | keep | 0 | Aug | 2022 | 0.018471 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-27 02:52 | 2022-08-27 02:53 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22082700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 308 | keep | 0 | Aug | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CAGUAS | 2022-08-27 03:06 | 2022-08-27 03:07 | 1606 | 0:01 | T | DESGANCHE | RECIERRE | C22082700008 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-27 | 1606 | keep | 0 | Aug | 2022 | 0.0010938 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-27 03:07 | 2022-08-27 06:38 | 30 | 3:31 | P | DESGANCHE | 1X50 EN C/L | C22082700006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 211 | 2022-08-27 | 6330 | keep | 0 | Aug | 2022 | 0.0043113 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-08-27 03:12 | 2022-08-27 10:46 | 75 | 7:34 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22082700018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 454 | 2022-08-27 | 34050 | keep | 0 | Aug | 2022 | 0.023191 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2022-08-27 03:23 | 2022-08-27 03:24 | 5630 | 0:01 | T | DESGANCHE | RECIERRE | C22082700000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-27 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-08-27 03:24 | 2022-08-27 08:45 | 50 | 5:21 | P | DESGANCHE | 2X40 EN C/L | C22082700022 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-08-27 | 16050 | keep | 0 | Aug | 2022 | 0.010932 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-27 03:54 | 2022-08-27 06:16 | 1262 | 2:22 | T | MAL TIEMPO/RAYOS | SE CERRO BREAKER LUEGO DE PATRULLARSE NO SE ENCONTRO NADA ANORMAL MAL TIEMPO Y RAYOS | P22082700021 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 142 | 2022-08-27 | 179204 | keep | 0 | Aug | 2022 | 0.12206 | 0.00085954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1262
BARRANQUITAS | 2022-08-27 03:55 | 2022-08-27 03:56 | 1131 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22082700000 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 1131 | keep | 0 | Aug | 2022 | 0.00077032 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-27 03:56 | 2022-08-27 08:32 | 48 | 4:36 | P | NO SE REPORTO CAUSA | 3X80 EN C/L | C22082600132 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 276 | 2022-08-27 | 13248 | keep | 0 | Aug | 2022 | 0.0090232 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
VEGA BAJA | 2022-08-27 04:04 | 2022-08-27 04:05 | 3387 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 3387 | keep | 0 | Aug | 2022 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
PONCE | 2022-08-27 04:59 | 2022-08-27 05:00 | 2113 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEBIDO A DESCARGA ELECTRICA | P22082700039 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-27 | 2113 | keep | 0 | Aug | 2022 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
YAUCO | 2022-08-27 05:01 | 2022-08-27 06:40 | 508 | 1:39 | T | DESGANCHE | DESGANCHE | P22082700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-08-27 | 50292 | keep | 0 | Aug | 2022 | 0.034254 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
VEGA BAJA | 2022-08-27 05:34 | 2022-08-27 13:20 | 11 | 7:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22082700004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 466 | 2022-08-27 | 5126 | keep | 0 | Aug | 2022 | 0.0034913 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-08-27 05:38 | 2022-08-27 08:54 | 520 | 3:16 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | R22082700003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-08-27 | 101920 | keep | 0 | Aug | 2022 | 0.069417 | 0.00035417 | Sustained | FALSE | FALSE | Not_TMED_Event | 520
GUAYAMA | 2022-08-27 05:45 | 2022-08-27 07:11 | 1093 | 1:26 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO PARTIDO | P22082700011 | New_Event | Primary Wire Break | Include | Include | Equipment | 86 | 2022-08-27 | 93998 | keep | 0 | Aug | 2022 | 0.064022 | 0.00074444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1093
CAGUAS | 2022-08-27 05:56 | 2022-08-27 10:28 | 25 | 4:32 | P | NO SE REPORTO CAUSA | 1X20 DE RISER @ XMR (AEREO) | C22082700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 272 | 2022-08-27 | 6800 | keep | 0 | Aug | 2022 | 0.0046314 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-08-27 05:58 | 2022-08-27 08:00 | 5069 | 2:02 | T | DESGANCHE | SE DESGANCHO Y SE REMPLAZO MACHETE QUE SE ESTABA QUEMANDO | P22082700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2022-08-27 | 618418 | keep | 0 | Aug | 2022 | 0.4212 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
VEGA BAJA | 2022-08-27 06:05 | 2022-08-27 10:30 | 1 | 4:25 | P | TRANSFORMADOR AVERIADO | SE REALAMBRO MONTURA Y SE ELIMINO XMR QUEMADO EN MONTURA | B22082700006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 265 | 2022-08-27 | 265 | keep | 0 | Aug | 2022 | 0.00018049 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-27 06:18 | 2022-08-27 07:13 | 1323 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 | S22082700008 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2022-08-27 | 72765 | keep | 0 | Aug | 2022 | 0.04956 | 0.00090109 | Sustained | FALSE | FALSE | Not_TMED_Event | 1323
SAN JUAN | 2022-08-27 06:18 | 2022-08-27 07:13 | 1532 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 | S22082700008 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2022-08-27 | 84260 | keep | 0 | Aug | 2022 | 0.057389 | 0.0010434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1532
SAN JUAN | 2022-08-27 06:18 | 2022-08-27 07:13 | 5290 | 0:55 | T | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 | S22082700008 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2022-08-27 | 290950 | keep | 0 | Aug | 2022 | 0.19816 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
HUMACAO | 2022-08-27 06:26 | 2022-08-27 11:34 | 15 | 5:08 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | C22082700023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 308 | 2022-08-27 | 4620 | keep | 0 | Aug | 2022 | 0.0031467 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-08-27 06:59 | 2022-08-27 14:42 | 8 | 7:43 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22082700065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2022-08-27 | 3704 | keep | 0 | Aug | 2022 | 0.0025228 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-08-27 07:13 | 2022-08-27 07:38 | 247 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 SE VERIFICO CON PERSONAL TRABAJANDO EN AREA NO REPORTARON CAUSA Y SE CERRO POR CONTROL | S22082700008 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 25 | 2022-08-27 | 6175 | keep | 0 | Aug | 2022 | 0.0042058 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-27 07:20 | 2022-08-27 11:58 | 40 | 4:38 | P | NO SE REPORTO CAUSA | 1X50 DEL SU-5 @ PROVISIONAL AEREO | C22082700031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 278 | 2022-08-27 | 11120 | keep | 0 | Aug | 2022 | 0.0075738 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-27 07:24 | 2022-08-27 18:15 | 2 | 10:51 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR LINEAS CRUZADAS | A22082700004 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 651 | 2022-08-27 | 1302 | keep | 0 | Aug | 2022 | 0.00088679 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-08-27 07:29 | 2022-08-27 10:39 | 373 | 3:10 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER 1 X 80 EN C/L | S22082700134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2022-08-27 | 70870 | keep | 0 | Aug | 2022 | 0.048269 | 0.00025405 | Sustained | FALSE | FALSE | Not_TMED_Event | 373
SAN JUAN | 2022-08-27 07:38 | 2022-08-27 07:39 | 1323 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 | S22082700008 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-27 | 1323 | keep | 0 | Aug | 2022 | 0.00090109 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-27 07:38 | 2022-08-27 07:39 | 1532 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 | S22082700008 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-27 | 1532 | keep | 0 | Aug | 2022 | 0.0010434 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-27 07:38 | 2022-08-27 07:39 | 5290 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 | S22082700008 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-27 | 5290 | keep | 0 | Aug | 2022 | 0.003603 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-27 07:39 | 2022-08-27 13:20 | 171 | 5:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L Y SE REEMPLAZO AISLADOR Y DESGANCHE | R22082700030 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 341 | 2022-08-27 | 58311 | keep | 0 | Aug | 2022 | 0.039715 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2022-08-27 07:39 | 2022-08-27 09:43 | 247 | 2:04 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 SE SECCIONALIZO PARTE DEL 1204-04 Y SE CERRO POR SCADA EL 1336-08 SE CERRO PUENTE ABIERTO Y SE CERRO MACHETES MEDIANTE SJ-220827-01 | S22082700008 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 124 | 2022-08-27 | 30628 | keep | 0 | Aug | 2022 | 0.020861 | 0.00016823 | Sustained | FALSE | FALSE | Not_TMED_Event | 247
SAN JUAN | 2022-08-27 07:39 | 2022-08-27 09:23 | 3000 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 SE CERRO AMARRE CONTRA 1336-09 PARA LUEGO CERRAR PUENTE ABIERTO EN RAMOS ANTONINI | S22082700008 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 104 | 2022-08-27 | 312000 | keep | 0 | Aug | 2022 | 0.2125 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
CANOVANAS | 2022-08-27 07:39 | 2022-08-27 11:05 | 171 | 3:26 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO, SE DESGANCHO Y 1 X 40 EN C/L | R22082700011 | New_Event | Primary Wire Break | Include | Include | Equipment | 206 | 2022-08-27 | 35226 | keep | 0 | Aug | 2022 | 0.023992 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
PONCE | 2022-08-27 08:08 | 2022-08-27 12:00 | 50 | 3:52 | P | DESGANCHE | 1 X 40 EN C/L Y OTRO DE 50 EN DIFERENTES C/L DESGANCHE | P22082700079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-08-27 | 11600 | keep | 0 | Aug | 2022 | 0.0079007 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-27 08:24 | 2022-08-27 08:25 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082700093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 2379 | keep | 0 | Aug | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2022-08-27 08:36 | 2022-08-27 10:55 | 6 | 2:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22082700007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 139 | 2022-08-27 | 834 | keep | 0 | Aug | 2022 | 0.00056803 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-27 08:36 | 2022-08-27 10:18 | 15 | 1:42 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22082700011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2022-08-27 | 1530 | keep | 0 | Aug | 2022 | 0.0010421 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-27 08:40 | 2022-08-27 19:21 | 7 | 10:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON BARRAS DE PEDESTAL SECUNDARIO SULFATADOS | C22082700057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 641 | 2022-08-27 | 4487 | keep | 0 | Aug | 2022 | 0.0030561 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-27 08:43 | 2022-08-27 11:40 | 100 | 2:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M22082700017 | New_Event | Primary Wire Break | Include | Include | Equipment | 177 | 2022-08-27 | 17700 | keep | 0 | Aug | 2022 | 0.012055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-27 08:52 | 2022-08-27 12:00 | 60 | 3:08 | P | DESGANCHE | 2 X 65 EN C/L SE DESGANCHO | S22082700211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-08-27 | 11280 | keep | 0 | Aug | 2022 | 0.0076828 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-08-27 08:55 | 2022-08-27 10:30 | 10 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REMPLAZO BARRA EN PEDESTAL | B22082700012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2022-08-27 | 950 | keep | 0 | Aug | 2022 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-27 09:02 | 2022-08-27 15:02 | 60 | 6:00 | P | ANIMAL | 2 X 10 EN TRANSFORMADOR CRUCE CON AVE | C22082700066 | New_Event | Animals | Include | Include | Wildlife | 360 | 2022-08-27 | 21600 | keep | 0 | Aug | 2022 | 0.014712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-27 09:08 | 2022-08-27 11:56 | 25 | 2:48 | P | DESGANCHE | 1 X 10 EN BANCO DE XMR Y DESGANCHE | R22082700020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-08-27 | 4200 | keep | 0 | Aug | 2022 | 0.0028606 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-27 09:23 | 2022-08-27 11:25 | 1500 | 2:02 | P | CONDUCTOR ROTO O ABIERTO | DISPARO 1336-08 SE CERRO PUENTE ABIERTO EN RAMOS ANTONINI Y SE NORMALIZO LAS CARGAS | S22082700008 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 122 | 2022-08-27 | 183000 | keep | 0 | Aug | 2022 | 0.12464 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-27 09:23 | 2022-08-27 09:25 | 1746 | 0:02 | T | CAUSAS EXTERNAS | DISPARO Y SE CERRO POR CONTROL. SE REPORTA AVERIA POR AUTO QUE IMPACTO LOS SU-8 Y SU-9. 90% DE LA CARGA AFECTADA | B22082700014 | New_Event | Damage From Public | Include | Include | Public | 2 | 2022-08-27 | 3492 | keep | 0 | Aug | 2022 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2022-08-27 09:23 | 2022-08-27 11:36 | 9 | 2:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN XMR SE REMPLAZO CAJA QUEMADA EN XMR | P22082700114 | New_Event | Cutout Failure | Include | Include | Equipment | 133 | 2022-08-27 | 1197 | keep | 0 | Aug | 2022 | 0.00081527 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-08-27 09:25 | 2022-08-27 20:13 | 1570 | 10:48 | P | CAUSAS EXTERNAS | SECCIONALIZADO SU-8 Y SU-9 POR ACCIDENTE VEHICULAR | B22082700110 | 1st_after_momentary | Damage From Public | Include | Include | Public | 648 | 2022-08-27 | 1017360 | keep | 0 | Aug | 2022 | 0.69292 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
ARECIBO | 2022-08-27 09:30 | 2022-08-27 11:15 | 1600 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA Y SE RESETEO INTERRUPTOR INTELIGENTE | A22082700011 | New_Event | Primary Wire Break | Include | Include | Equipment | 105 | 2022-08-27 | 168000 | keep | 0 | Aug | 2022 | 0.11442 | 0.0010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1600
BAYAMON | 2022-08-27 09:42 | 2022-08-27 09:43 | 1498 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
MAYAGÃœEZ | 2022-08-27 09:53 | 2022-08-27 15:14 | 25 | 5:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22082700046 | New_Event | Cutout Failure | Include | Include | Equipment | 321 | 2022-08-27 | 8025 | keep | 0 | Aug | 2022 | 0.0054658 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-08-27 10:34 | 2022-08-27 10:35 | 5620 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE 1620-03 QUE LLEVA 1620-01 Y 90% DEL 1336-07 CERRADO POR SCADA | S22082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 5620 | keep | 0 | Aug | 2022 | 0.0038278 | 0.0038278 | Momentary | FALSE | FALSE | Not_TMED_Event | 5620
SAN JUAN | 2022-08-27 10:34 | 2022-08-27 10:35 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-03 QUE LLEVA 1620-01 Y 90% DEL 1336-07 CERRADO POR SCADA | S22082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 36 | keep | 0 | Aug | 2022 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-08-27 10:34 | 2022-08-27 10:35 | 1073 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-03 QUE LLEVA 1620-01 Y 90% DEL 1336-07 CERRADO POR SCADA | S22082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 1073 | keep | 0 | Aug | 2022 | 0.00073082 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
YAUCO | 2022-08-27 10:35 | 2022-08-27 17:50 | 70 | 7:15 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22082700124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2022-08-27 | 30450 | keep | 0 | Aug | 2022 | 0.020739 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2022-08-27 10:56 | 2022-08-27 10:57 | 1565 | 0:01 | T | DESGANCHE | SE CERRO POR CONTROL | C22082700100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-27 | 1565 | keep | 0 | Aug | 2022 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CANOVANAS | 2022-08-27 11:03 | 2022-08-27 14:03 | 5 | 3:00 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R22082700028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2022-08-27 | 900 | keep | 0 | Aug | 2022 | 0.00061299 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-27 11:14 | 2022-08-27 18:26 | 18 | 7:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO NEUTRAL | S22082700310 | New_Event | Secondary Wire Break | Include | Include | Equipment | 432 | 2022-08-27 | 7776 | keep | 0 | Aug | 2022 | 0.0052962 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2022-08-27 11:15 | 2022-08-27 13:00 | 1300 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA SE CERRO CORTE DE LINEA | A22082700049 | New_Event | Primary Wire Break | Include | Include | Equipment | 105 | 2022-08-27 | 136500 | keep | 0 | Aug | 2022 | 0.09297 | 0.00088542 | Sustained | FALSE | FALSE | Not_TMED_Event | 1300
ARECIBO | 2022-08-27 11:17 | 2022-08-27 15:45 | 8 | 4:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA | A22082700047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 268 | 2022-08-27 | 2144 | keep | 0 | Aug | 2022 | 0.0014603 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-27 11:20 | 2022-08-27 11:59 | 12 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22082600187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2022-08-27 | 468 | keep | 0 | Aug | 2022 | 0.00031875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-08-27 11:25 | 2022-08-27 11:26 | 1498 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22082700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BARRANQUITAS | 2022-08-27 11:29 | 2022-08-27 12:12 | 1565 | 0:43 | T | DESGANCHE | SE ABRIO MACHETE PARA SECCIONALIZAR POR DESGANCHE - MEDIANTE SINGLE-POINT G.O.I. CG-220827-01 - AUN FALTA 50% DE LA CARGA POR ENTRAR EN SERVICIO | C22082700108 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-08-27 | 67295 | keep | 0 | Aug | 2022 | 0.045834 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
SAN JUAN | 2022-08-27 11:30 | 2022-08-27 15:12 | 10 | 3:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22082700266 | New_Event | Secondary Wire Break | Include | Include | Equipment | 222 | 2022-08-27 | 2220 | keep | 0 | Aug | 2022 | 0.001512 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-27 11:34 | 2022-08-27 14:22 | 25 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-1 | S22082700324 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2022-08-27 | 4200 | keep | 0 | Aug | 2022 | 0.0028606 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-08-27 11:38 | 2022-08-27 14:11 | 20 | 2:33 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA | C22082700119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-08-27 | 3060 | keep | 0 | Aug | 2022 | 0.0020842 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-08-27 11:51 | 2022-08-27 16:11 | 1 | 4:20 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S22082700311 | New_Event | Primary Wire Break | Include | Include | Equipment | 260 | 2022-08-27 | 260 | keep | 0 | Aug | 2022 | 0.00017708 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-27 11:58 | 2022-08-27 16:30 | 10 | 4:32 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR Y SE REPARO CRUCETA | R22082700032 | New_Event | Primary Wire Break | Include | Include | Equipment | 272 | 2022-08-27 | 2720 | keep | 0 | Aug | 2022 | 0.0018526 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-27 12:05 | 2022-08-27 12:40 | 9 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22082700052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-08-27 | 315 | keep | 0 | Aug | 2022 | 0.00021455 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-08-27 12:07 | 2022-08-27 15:52 | 90 | 3:45 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22082700137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 225 | 2022-08-27 | 20250 | keep | 0 | Aug | 2022 | 0.013792 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-08-27 12:11 | 2022-08-27 13:22 | 4 | 1:11 | P | ANIMAL | 1 X 10 EN XMR LAGARTO | R22082700033 | New_Event | Animals | Include | Include | Wildlife | 71 | 2022-08-27 | 284 | keep | 0 | Aug | 2022 | 0.00019343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-08-27 12:12 | 2022-08-27 13:07 | 782 | 0:55 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO DE ENRREDADERA MEDIANTE SINGLE-POINT G.O.I. CG-220827-01 | C22082700108 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-08-27 | 43010 | keep | 0 | Aug | 2022 | 0.029294 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-27 12:25 | 2022-08-27 13:25 | 7 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M22082700014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-08-27 | 420 | keep | 0 | Aug | 2022 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-08-27 12:33 | 2022-08-27 14:53 | 15 | 2:20 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REPARO SECUNDARIA Y SE HIZO DESGANCHE SECUNDARIO | S22082700339 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 140 | 2022-08-27 | 2100 | keep | 0 | Aug | 2022 | 0.0014303 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-08-27 12:40 | 2022-08-27 13:57 | 10 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES SECUNDARIOS | P22082700141 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2022-08-27 | 770 | keep | 0 | Aug | 2022 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-08-27 12:40 | 2022-08-27 14:25 | 3 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS PARA REMPLAZAR BAJANTES SECUNDARIOS | P22082700013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2022-08-27 | 315 | keep | 0 | Aug | 2022 | 0.00021455 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-08-27 12:46 | 2022-08-27 14:53 | 60 | 2:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | M22082700067 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2022-08-27 | 7620 | keep | 0 | Aug | 2022 | 0.0051899 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-08-27 12:46 | 2022-08-27 16:05 | 60 | 3:19 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A22082700056 | New_Event | Primary Wire Break | Include | Include | Equipment | 199 | 2022-08-27 | 11940 | keep | 0 | Aug | 2022 | 0.0081323 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-27 12:48 | 2022-08-27 14:18 | 12 | 1:30 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | M22082700069 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 90 | 2022-08-27 | 1080 | keep | 0 | Aug | 2022 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-08-27 12:49 | 2022-08-27 16:30 | 12 | 3:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON BAJANTES SECUNDARIOS QUEMADOS | C22082700175 | New_Event | Secondary Wire Break | Include | Include | Equipment | 221 | 2022-08-27 | 2652 | keep | 0 | Aug | 2022 | 0.0018063 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-08-27 13:11 | 2022-08-27 13:12 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C22082700182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 181 | keep | 0 | Aug | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2022-08-27 13:22 | 2022-08-27 15:37 | 18 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BARRAS EN PEDESTAL SECUNDARIO | C22082700183 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2022-08-27 | 2430 | keep | 0 | Aug | 2022 | 0.0016551 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-08-27 13:22 | 2022-08-27 17:50 | 30 | 4:28 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA Y SE REPARO LINEA PRIMARI PARTIDA | M22082700073 | New_Event | Primary Wire Break | Include | Include | Equipment | 268 | 2022-08-27 | 8040 | keep | 0 | Aug | 2022 | 0.005476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-08-27 13:33 | 2022-08-27 17:40 | 70 | 4:07 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA | C22082700187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-08-27 | 17290 | keep | 0 | Aug | 2022 | 0.011776 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-08-27 13:34 | 2022-08-27 14:57 | 10 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES SULFATADOS EN LINEA SECUNDARIA | C22082700188 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2022-08-27 | 830 | keep | 0 | Aug | 2022 | 0.00056531 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-27 14:02 | 2022-08-27 17:16 | 10 | 3:14 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR CONECTORES | S22082700351 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 194 | 2022-08-27 | 1940 | keep | 0 | Aug | 2022 | 0.0013213 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-27 14:23 | 2022-08-27 18:30 | 40 | 4:07 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082700064 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 247 | 2022-08-27 | 9880 | keep | 0 | Aug | 2022 | 0.0067292 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-27 14:34 | 2022-08-27 16:53 | 12 | 2:19 | P | NO SE REPORTO CAUSA | 2 X 50 EN RISER NO SE ENCONTRO CAUSA | P22082700153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-08-27 | 1668 | keep | 0 | Aug | 2022 | 0.0011361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-27 14:49 | 2022-08-27 21:35 | 30 | 6:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA FURTE LLUVIA Y VIENTO | A22082700069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 406 | 2022-08-27 | 12180 | keep | 0 | Aug | 2022 | 0.0082957 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-27 15:09 | 2022-08-27 18:41 | 30 | 3:32 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M22082700086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 212 | 2022-08-27 | 6360 | keep | 0 | Aug | 2022 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-27 15:11 | 2022-08-27 19:16 | 40 | 4:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA | M22082700088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 245 | 2022-08-27 | 9800 | keep | 0 | Aug | 2022 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-08-27 15:14 | 2022-08-27 16:38 | 9 | 1:24 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR CRUCE X AVE | C22082700207 | New_Event | Animals | Include | Include | Wildlife | 84 | 2022-08-27 | 756 | keep | 0 | Aug | 2022 | 0.00051491 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2022-08-27 15:20 | 2022-08-27 19:10 | 150 | 3:50 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA POR RAYO | M22082700091 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 230 | 2022-08-27 | 34500 | keep | 0 | Aug | 2022 | 0.023498 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-27 15:21 | 2022-08-27 18:06 | 70 | 2:45 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M22082700092 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 165 | 2022-08-27 | 11550 | keep | 0 | Aug | 2022 | 0.0078667 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2022-08-27 15:30 | 2022-08-27 15:56 | 8 | 0:26 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | R22082700042 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 26 | 2022-08-27 | 208 | keep | 0 | Aug | 2022 | 0.00014167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-27 15:50 | 2022-08-27 17:10 | 600 | 1:20 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO SJ-220827-50 | R22082700047 | New_Event | Primary Wire Break | Include | Include | Equipment | 80 | 2022-08-27 | 48000 | keep | 0 | Aug | 2022 | 0.032693 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
UTUADO | 2022-08-27 15:50 | 2022-08-27 17:47 | 2 | 1:57 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22082700167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-08-27 | 234 | keep | 0 | Aug | 2022 | 0.00015938 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-27 15:54 | 2022-08-27 18:33 | 50 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | M22082700103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2022-08-27 | 7950 | keep | 0 | Aug | 2022 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-08-27 15:57 | 2022-08-27 19:26 | 70 | 3:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22082700215 | New_Event | Cutout Failure | Include | Include | Equipment | 209 | 2022-08-27 | 14630 | keep | 0 | Aug | 2022 | 0.0099644 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-08-27 15:59 | 2022-08-27 17:33 | 40 | 1:34 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M22082700106 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 94 | 2022-08-27 | 3760 | keep | 0 | Aug | 2022 | 0.0025609 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-08-27 16:10 | 2022-08-27 20:19 | 100 | 4:09 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22082700220 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2022-08-27 | 24900 | keep | 0 | Aug | 2022 | 0.016959 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-08-27 16:13 | 2022-08-27 18:20 | 60 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22082700073 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2022-08-27 | 7620 | keep | 0 | Aug | 2022 | 0.0051899 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-27 16:25 | 2022-08-28 15:05 | 10 | 22:40 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082700119 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1360 | 2022-08-27 | 13600 | keep | 0 | Aug | 2022 | 0.0092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-27 16:29 | 2022-08-27 17:27 | 60 | 0:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYO | M22082700120 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 58 | 2022-08-27 | 3480 | keep | 0 | Aug | 2022 | 0.0023702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-27 16:30 | 2022-08-27 21:50 | 200 | 5:20 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE | M22082700122 | New_Event | Primary Wire Break | Include | Include | Equipment | 320 | 2022-08-27 | 64000 | keep | 0 | Aug | 2022 | 0.04359 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-27 16:35 | 2022-08-28 11:30 | 30 | 18:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082800126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1135 | 2022-08-27 | 34050 | keep | 0 | Aug | 2022 | 0.023191 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-27 17:04 | 2022-08-27 19:05 | 2530 | 2:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE MACHETES PARA SECCIONALIZAR AVERIA DE AISLADO PARTIDO Y SE CIERRA INTERRUPTOR | M22082700137 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 121 | 2022-08-27 | 306130 | keep | 0 | Aug | 2022 | 0.2085 | 0.0017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-08-27 17:04 | 2022-08-27 17:05 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22082700138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-27 | 199 | keep | 0 | Aug | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-08-27 17:04 | 2022-08-28 08:56 | 50 | 15:52 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082700136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 952 | 2022-08-27 | 47600 | keep | 0 | Aug | 2022 | 0.03242 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-27 17:10 | 2022-08-27 18:54 | 5 | 1:44 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN XMR DESGANCHE SECUNDARIO | R22082700046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 104 | 2022-08-27 | 520 | keep | 0 | Aug | 2022 | 0.00035417 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-27 17:22 | 2022-08-27 22:00 | 150 | 4:38 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA SE RETIRO PELIGRO DE ARBOL CAIDO SOBRE LINEA PRIMARIA Y SE VOLVIO A CERRAR EL CORTE DE LINEA | M22082700142 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 278 | 2022-08-27 | 41700 | keep | 0 | Aug | 2022 | 0.028402 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-27 17:26 | 2022-08-27 22:10 | 80 | 4:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | M22082700146 | New_Event | Cutout Failure | Include | Include | Equipment | 284 | 2022-08-27 | 22720 | keep | 0 | Aug | 2022 | 0.015474 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-27 17:52 | 2022-08-28 12:43 | 6 | 18:51 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR POR DESGANCHE SECUNDARIO | B22082700087 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1131 | 2022-08-27 | 6786 | keep | 0 | Aug | 2022 | 0.0046219 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-08-27 17:56 | 2022-08-27 20:49 | 10 | 2:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES QUEMADOS EN BAJANTE | C22082700233 | New_Event | Secondary Wire Break | Include | Include | Equipment | 173 | 2022-08-27 | 1730 | keep | 0 | Aug | 2022 | 0.0011783 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-27 18:08 | 2022-08-28 10:35 | 1 | 16:27 | P | TRANSFORMADOR AVERIADO | SE TRANSFIRIO LA CARGA A OTRO XMR YA QUE PROBO MALO Y ERA UN SOLO CLIENTE | S22082700366 | New_Event | Service Transformer Failure | Include | Include | Equipment | 987 | 2022-08-27 | 987 | keep | 0 | Aug | 2022 | 0.00067224 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-27 18:18 | 2022-08-27 18:28 | 14 | 0:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22082700369 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-08-27 | 140 | keep | 0 | Aug | 2022 | 9.5353e-05 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-08-27 18:36 | 2022-08-28 09:11 | 10 | 14:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082700181 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 875 | 2022-08-27 | 8750 | keep | 0 | Aug | 2022 | 0.0059596 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-08-27 18:39 | 2022-08-27 19:43 | 12 | 1:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | A22082700082 | New_Event | Primary Wire Break | Include | Include | Equipment | 64 | 2022-08-27 | 768 | keep | 0 | Aug | 2022 | 0.00052308 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-08-27 18:52 | 2022-08-28 08:19 | 14 | 13:27 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M22082700188 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 807 | 2022-08-27 | 11298 | keep | 0 | Aug | 2022 | 0.007695 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-08-27 19:05 | 2022-08-27 22:30 | 400 | 3:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REALIZO DESGANCHE SE REMPLAZO AISLADORES ROTOS Y SE RETEZARON LINEAS PRIMARIAS SE CERRO LOS MACHETES | M22082700196 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 205 | 2022-08-27 | 82000 | keep | 0 | Aug | 2022 | 0.05585 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-27 19:16 | 2022-08-28 12:32 | 50 | 17:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO NO FUSIBLE | P22082700194 | New_Event | Primary Wire Break | Include | Include | Equipment | 1036 | 2022-08-27 | 51800 | keep | 0 | Aug | 2022 | 0.035281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-27 19:17 | 2022-08-28 08:15 | 10 | 12:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8 EN XMR MAL TIEMPO LLUVIAS | P22082700195 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 778 | 2022-08-27 | 7780 | keep | 0 | Aug | 2022 | 0.0052989 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-27 19:30 | 2022-08-27 21:03 | 19 | 1:33 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S22082700359 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 93 | 2022-08-27 | 1767 | keep | 0 | Aug | 2022 | 0.0012035 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2022-08-27 19:31 | 2022-08-28 09:36 | 6 | 14:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | R22082700050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 845 | 2022-08-27 | 5070 | keep | 0 | Aug | 2022 | 0.0034532 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-27 19:42 | 2022-08-28 12:04 | 30 | 16:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L RERMPLAZO PIN POLE TOP Y AISLADOR | C22082700239 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 982 | 2022-08-27 | 29460 | keep | 0 | Aug | 2022 | 0.020065 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-27 19:57 | 2022-08-28 11:00 | 80 | 15:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22082700084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 903 | 2022-08-27 | 72240 | keep | 0 | Aug | 2022 | 0.049202 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-27 20:21 | 2022-08-27 21:00 | 750 | 0:39 | P | CAUSAS EXTERNAS | SE REPARO TRAMO SOTERRADO DEL SU-8 @ SU-9 MEDIANTE G.O.I. BY-220827-01 - EN SERVICIO TOTAL | B22082700110 | New_Event | Damage From Public | Include | Include | Public | 39 | 2022-08-27 | 29250 | keep | 0 | Aug | 2022 | 0.019922 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
ARECIBO | 2022-08-27 20:35 | 2022-08-27 21:50 | 200 | 1:15 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082700091 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-08-27 | 15000 | keep | 0 | Aug | 2022 | 0.010216 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-27 21:02 | 2022-08-27 21:03 | 4188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | R22082700057 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-27 | 4188 | keep | 0 | Aug | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-08-27 21:03 | 2022-08-27 22:22 | 1382 | 1:19 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN LA SALIDA DEL ALIMENTADOR | R22082700057 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 79 | 2022-08-27 | 109178 | keep | 0 | Aug | 2022 | 0.074361 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-27 21:07 | 2022-08-28 12:30 | 750 | 15:23 | P | CAUSAS EXTERNAS | SE REPARO TRAMO SOTERRADO DEL SU-8 @ SU-9 MEDIANTE G.O.I. BY-220827-01 - EN SERVICIO TOTAL | B22082700110 | Partial_restoration | Damage From Public | Include | Include | Public | 923 | 2022-08-27 | 692250 | keep | 0 | Aug | 2022 | 0.47149 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-27 21:10 | 2022-08-28 10:44 | 15 | 13:34 | P | DESGANCHE | 1X30 EN RISER | B22082700123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 814 | 2022-08-27 | 12210 | keep | 0 | Aug | 2022 | 0.0083162 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-08-27 21:29 | 2022-08-27 23:03 | 50 | 1:34 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082700222 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 94 | 2022-08-27 | 4700 | keep | 0 | Aug | 2022 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-27 21:54 | 2022-08-28 08:45 | 200 | 10:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22082700115 | New_Event | Cutout Failure | Include | Include | Equipment | 651 | 2022-08-27 | 130200 | keep | 0 | Aug | 2022 | 0.088679 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2022-08-27 22:03 | 2022-08-27 23:55 | 225 | 1:52 | P | ANIMAL | 1 X 200 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M22082700232 | New_Event | Animals | Include | Include | Wildlife | 112 | 2022-08-27 | 25200 | keep | 0 | Aug | 2022 | 0.017164 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
CANOVANAS | 2022-08-27 22:22 | 2022-08-27 23:14 | 4188 | 0:52 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN TRONCAL GOI SJ-220827-51 | R22082700146 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 52 | 2022-08-27 | 217776 | keep | 0 | Aug | 2022 | 0.14833 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-27 22:29 | 2022-08-28 09:15 | 75 | 10:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082700011 | New_Event | Cutout Failure | Include | Include | Equipment | 646 | 2022-08-27 | 48450 | keep | 0 | Aug | 2022 | 0.032999 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-08-27 23:18 | 2022-08-28 10:04 | 50 | 10:46 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO | C22082700245 | New_Event | Vegetation Contact | Include | Include | Vegetation | 646 | 2022-08-27 | 32300 | keep | 0 | Aug | 2022 | 0.021999 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-27 23:35 | 2022-08-28 11:08 | 40 | 11:33 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | B22082700131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 693 | 2022-08-27 | 27720 | keep | 0 | Aug | 2022 | 0.01888 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-08-28 01:11 | 2022-08-28 08:44 | 70 | 7:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA EN C/L QUEMADA | P22082800009 | New_Event | Cutout Failure | Include | Include | Equipment | 453 | 2022-08-28 | 31710 | keep | 0 | Aug | 2022 | 0.021598 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2022-08-28 01:20 | 2022-08-28 11:39 | 50 | 10:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L SE REMPLAZO AISLADOR | P22082800015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 619 | 2022-08-28 | 30950 | keep | 0 | Aug | 2022 | 0.02108 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-08-28 01:23 | 2022-08-28 12:55 | 150 | 11:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22082800004 | New_Event | Cutout Failure | Include | Include | Equipment | 692 | 2022-08-28 | 103800 | keep | 0 | Aug | 2022 | 0.070698 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-08-28 02:10 | 2022-08-28 02:11 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C22082800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 1702 | keep | 0 | Aug | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-08-28 02:11 | 2022-08-28 07:30 | 28 | 5:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22082800004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 319 | 2022-08-28 | 8932 | keep | 0 | Aug | 2022 | 0.0060835 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
PONCE | 2022-08-28 02:35 | 2022-08-28 09:43 | 167 | 7:08 | T | ARBOL SOBRE LINEA | SE REMOVIO ARBOL SOBRE LINEAS | P22082800024 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 428 | 2022-08-28 | 71476 | keep | 0 | Aug | 2022 | 0.048682 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
CANOVANAS | 2022-08-28 03:08 | 2022-08-28 12:05 | 30 | 8:57 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO | R22082800009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 537 | 2022-08-28 | 16110 | keep | 0 | Aug | 2022 | 0.010972 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-28 03:44 | 2022-08-28 09:19 | 50 | 5:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | M22082800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 335 | 2022-08-28 | 16750 | keep | 0 | Aug | 2022 | 0.011408 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-28 05:12 | 2022-08-28 09:25 | 7 | 4:13 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22082800005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 253 | 2022-08-28 | 1771 | keep | 0 | Aug | 2022 | 0.0012062 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-08-28 05:48 | 2022-08-28 05:49 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C22082800005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2022-08-28 06:08 | 2022-08-28 12:09 | 22 | 6:01 | P | PARARRAYOS DEFECTUOSO | 1X30 EN C/L SE ELIMINO PARARRAYOS QUEMADO | B22082800013 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 361 | 2022-08-28 | 7942 | keep | 0 | Aug | 2022 | 0.0054093 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2022-08-28 06:40 | 2022-08-28 10:10 | 70 | 3:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO PARTIDO | A22082800011 | New_Event | Primary Pole Failure | Include | Include | Equipment | 210 | 2022-08-28 | 14700 | keep | 0 | Aug | 2022 | 0.010012 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-08-28 06:44 | 2022-08-28 16:54 | 62 | 10:10 | P | ANIMAL | 1 X 40 EN C/L AVE | B22082800014 | New_Event | Animals | Include | Include | Wildlife | 610 | 2022-08-28 | 37820 | keep | 0 | Aug | 2022 | 0.025759 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
SAN JUAN | 2022-08-28 06:52 | 2022-08-28 08:52 | 100 | 2:00 | P | ARBOL SOBRE LINEA | 3 X 65 EN C/L SE RETIRO ARBOL SOBRE LINEA | S22082800003 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 120 | 2022-08-28 | 12000 | keep | 0 | Aug | 2022 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-28 07:15 | 2022-08-28 10:43 | 5 | 3:28 | P | MAL TIEMPO/RAYOS | 1 X 30 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M22082800020 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 208 | 2022-08-28 | 1040 | keep | 0 | Aug | 2022 | 0.00070834 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-28 07:17 | 2022-08-28 11:04 | 17 | 3:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 XMR SE REMPLAZO CAJA PRIMARIA | S22082800006 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2022-08-28 | 3859 | keep | 0 | Aug | 2022 | 0.0026283 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2022-08-28 07:23 | 2022-08-29 12:32 | 7 | 29:09 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO - SE VOLVIO A CERRAR FUSIBLE (NO FUNDIO) | B22082800019 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1749 | 2022-08-28 | 12243 | keep | 0 | Aug | 2022 | 0.0083387 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-08-28 07:30 | 2022-08-28 09:44 | 542 | 2:14 | T | CAUSAS EXTERNAS | LINEAS CRUZADAS AUTO IMPACTO POSTE | P22082800058 | New_Event | Damage From Public | Include | Include | Public | 134 | 2022-08-28 | 72628 | keep | 0 | Aug | 2022 | 0.049467 | 0.00036915 | Sustained | FALSE | FALSE | Not_TMED_Event | 542
SAN JUAN | 2022-08-28 07:31 | 2022-08-28 09:59 | 20 | 2:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | S22082800008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 148 | 2022-08-28 | 2960 | keep | 0 | Aug | 2022 | 0.002016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-08-28 07:32 | 2022-08-28 12:35 | 10 | 5:03 | P | ANIMAL | 1 X 20 EN XMR AVE CRUZO LINEAS | P22082800059 | New_Event | Animals | Include | Include | Wildlife | 303 | 2022-08-28 | 3030 | keep | 0 | Aug | 2022 | 0.0020637 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-28 07:48 | 2022-08-28 15:11 | 20 | 7:23 | P | SECUNDARIA/DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22082800012 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 443 | 2022-08-28 | 8860 | keep | 0 | Aug | 2022 | 0.0060345 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-28 07:49 | 2022-08-28 09:35 | 1 | 1:46 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082800018 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 106 | 2022-08-28 | 106 | keep | 0 | Aug | 2022 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-28 08:08 | 2022-08-28 08:09 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082800070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 4279 | keep | 0 | Aug | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
SAN JUAN | 2022-08-28 08:13 | 2022-08-28 08:14 | 946 | 0:01 | T | DESGANCHE | DISPARO DE 1525-05 QUE LLEVA 1525-02 CERRADO POR SCADA | S22082800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-28 | 946 | keep | 0 | Aug | 2022 | 0.00064432 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2022-08-28 08:13 | 2022-08-28 08:14 | 937 | 0:01 | T | DESGANCHE | DISPARO DE 1525-05 QUE LLEVA 1525-02 CERRADO POR SCADA | S22082800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-28 | 937 | keep | 0 | Aug | 2022 | 0.00063819 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
SAN JUAN | 2022-08-28 08:14 | 2022-08-28 09:54 | 50 | 1:40 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22082800014 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 100 | 2022-08-28 | 5000 | keep | 0 | Aug | 2022 | 0.0034055 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-28 08:19 | 2022-08-28 08:20 | 31 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B22082800025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 31 | keep | 0 | Aug | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
HUMACAO | 2022-08-28 08:28 | 2022-08-28 12:21 | 10 | 3:53 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | C22082800012 | New_Event | Animals | Include | Include | Wildlife | 233 | 2022-08-28 | 2330 | keep | 0 | Aug | 2022 | 0.001587 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-28 08:34 | 2022-08-28 10:18 | 50 | 1:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA QUEMADA | R22082800014 | New_Event | Cutout Failure | Include | Include | Equipment | 104 | 2022-08-28 | 5200 | keep | 0 | Aug | 2022 | 0.0035417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-28 08:38 | 2022-08-28 12:19 | 80 | 3:41 | P | ANIMAL | 1X100 EN C/L POR CRUCE DE AVE | B22082800029 | New_Event | Animals | Include | Include | Wildlife | 221 | 2022-08-28 | 17680 | keep | 0 | Aug | 2022 | 0.012042 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-08-28 08:41 | 2022-08-28 09:26 | 60 | 0:45 | P | DESGANCHE | 1 X 25 Y 1 X 40 EN C/LS DESGANCHE | C22082800014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2022-08-28 | 2700 | keep | 0 | Aug | 2022 | 0.001839 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-28 08:45 | 2022-08-28 10:09 | 70 | 1:24 | P | ANIMAL | 1X40 EN C/L CRUCE POR AVE | S22082800015 | New_Event | Animals | Include | Include | Wildlife | 84 | 2022-08-28 | 5880 | keep | 0 | Aug | 2022 | 0.0040048 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-08-28 08:47 | 2022-08-28 08:48 | 413 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO 1620-02 CERRADO POR SCADA LLEVA 10% DEL 1206-03 | S22082800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 413 | keep | 0 | Aug | 2022 | 0.00028129 | 0.00028129 | Momentary | FALSE | FALSE | Not_TMED_Event | 413
SAN JUAN | 2022-08-28 08:47 | 2022-08-28 08:48 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-02 CERRADO POR SCADA LLEVA 10% DEL 1206-03 | S22082800016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 3718 | keep | 0 | Aug | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
AGUADILLA | 2022-08-28 08:47 | 2022-08-28 14:50 | 5 | 6:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22082800016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 363 | 2022-08-28 | 1815 | keep | 0 | Aug | 2022 | 0.0012362 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-08-28 08:48 | 2022-08-28 11:42 | 43 | 2:54 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22082800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-08-28 | 7482 | keep | 0 | Aug | 2022 | 0.005096 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2022-08-28 08:48 | 2022-08-28 15:09 | 15 | 6:21 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 25 KVA X 37.5 KVA | C22082800015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 381 | 2022-08-28 | 5715 | keep | 0 | Aug | 2022 | 0.0038925 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-28 09:03 | 2022-08-28 10:08 | 1 | 1:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22082800018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-08-28 | 65 | keep | 0 | Aug | 2022 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-08-28 09:07 | 2022-08-28 11:35 | 1606 | 2:28 | T | CONDUCTOR ROTO O ABIERTO | SE TRANSFIRIO CARGA AL 4602-02 ALAMBRE PARTIDO HACIA 3 XMR | P22082800083 | New_Event | Primary Wire Break | Include | Include | Equipment | 148 | 2022-08-28 | 237688 | keep | 0 | Aug | 2022 | 0.16189 | 0.0010938 | Sustained | FALSE | FALSE | Not_TMED_Event | 1606
CANOVANAS | 2022-08-28 09:17 | 2022-08-28 11:30 | 18 | 2:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L Y 1 X 10 EN XMR REPARO BAJANTE PRIMARIO | R22082800019 | New_Event | Primary Wire Break | Include | Include | Equipment | 133 | 2022-08-28 | 2394 | keep | 0 | Aug | 2022 | 0.0016305 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-08-28 09:17 | 2022-08-28 14:00 | 10 | 4:43 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082800019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2022-08-28 | 2830 | keep | 0 | Aug | 2022 | 0.0019275 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-28 09:50 | 2022-08-28 21:41 | 14 | 11:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 25KVA | R22082800046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 711 | 2022-08-28 | 9954 | keep | 0 | Aug | 2022 | 0.0067796 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2022-08-28 10:10 | 2022-08-28 11:55 | 70 | 1:45 | P | ANIMAL | 1 X 100 EN C/L AVE | S22082800021 | New_Event | Animals | Include | Include | Wildlife | 105 | 2022-08-28 | 7350 | keep | 0 | Aug | 2022 | 0.0050061 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-08-28 10:10 | 2022-08-28 12:00 | 2 | 1:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 40 EN CORTE DE LINEA SE REMOVIO POSTE PASANTE PARTIDO Y SE RETEZO LINEAS | A22082800011 | New_Event | Primary Pole Failure | Include | Include | Equipment | 110 | 2022-08-28 | 220 | keep | 0 | Aug | 2022 | 0.00014984 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-28 10:13 | 2022-08-28 13:56 | 6 | 3:43 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE RETIRO PALMA | S22082800025 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 223 | 2022-08-28 | 1338 | keep | 0 | Aug | 2022 | 0.00091131 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-08-28 10:13 | 2022-08-28 14:49 | 14 | 4:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22082800031 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2022-08-28 | 3864 | keep | 0 | Aug | 2022 | 0.0026318 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2022-08-28 10:19 | 2022-08-28 16:28 | 1 | 6:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN BANCO DE TRANSFORMADORES SE REEMPLAZO CAJA QUEMADA | R22082800032 | New_Event | Cutout Failure | Include | Include | Equipment | 369 | 2022-08-28 | 369 | keep | 0 | Aug | 2022 | 0.00025132 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-28 10:27 | 2022-08-28 10:28 | 1105 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22082800044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 1105 | keep | 0 | Aug | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BARRANQUITAS | 2022-08-28 10:27 | 2022-08-28 11:59 | 6 | 1:32 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C22082800027 | New_Event | Animals | Include | Include | Wildlife | 92 | 2022-08-28 | 552 | keep | 0 | Aug | 2022 | 0.00037596 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-28 10:34 | 2022-08-28 13:33 | 50 | 2:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-08-28 | 8950 | keep | 0 | Aug | 2022 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-08-28 11:14 | 2022-08-28 13:06 | 150 | 1:52 | P | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO CARGA AL 4504-02 HAY MACHETE QUEMADO DE AUX DE LINEA | P22082800108 | New_Event | Switch Failure | Include | Include | Equipment | 112 | 2022-08-28 | 16800 | keep | 0 | Aug | 2022 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-08-28 11:21 | 2022-08-28 14:44 | 1 | 3:23 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHO | C22082800031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-08-28 | 203 | keep | 0 | Aug | 2022 | 0.00013826 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-28 11:30 | 2022-08-28 13:56 | 2704 | 2:26 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA CERRAR ALIMENTADOR POR TRAMO | B22082800049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 146 | 2022-08-28 | 394784 | keep | 0 | Aug | 2022 | 0.26889 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2022-08-28 11:49 | 2022-08-28 12:23 | 8 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO PM Y REMPLAZO BARRA EN PEDESTAL | S22082700328 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2022-08-28 | 272 | keep | 0 | Aug | 2022 | 0.00018526 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-28 11:49 | 2022-08-28 11:50 | 4188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO X CONTROL | R22082800033 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-28 | 4188 | keep | 0 | Aug | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-08-28 11:51 | 2022-08-28 11:52 | 4188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | R22082800033 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-28 | 4188 | keep | 0 | Aug | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-08-28 11:52 | 2022-08-28 16:18 | 200 | 4:26 | P | CONDUCTOR ROTO O ABIERTO | SE CERRARON PUENTES ABIERTOS EN TRONCAL | R22082800056 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 266 | 2022-08-28 | 53200 | keep | 0 | Aug | 2022 | 0.036234 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-08-28 12:00 | 2022-08-28 12:53 | 1 | 0:53 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S22082800024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2022-08-28 | 53 | keep | 0 | Aug | 2022 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-28 12:00 | 2022-08-28 13:12 | 8 | 1:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22082800029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 72 | 2022-08-28 | 576 | keep | 0 | Aug | 2022 | 0.00039231 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-28 12:08 | 2022-08-28 17:10 | 50 | 5:02 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082800030 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 302 | 2022-08-28 | 15100 | keep | 0 | Aug | 2022 | 0.010285 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-28 12:21 | 2022-08-28 12:22 | 888 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22082800034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-28 | 888 | keep | 0 | Aug | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-08-28 12:21 | 2022-08-28 12:22 | 393 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22082800034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-28 | 393 | keep | 0 | Aug | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-08-28 12:21 | 2022-08-28 12:22 | 4 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1600 | M22082800034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-28 | 4 | keep | 0 | Aug | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-08-28 12:27 | 2022-08-28 12:28 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 3973 | keep | 0 | Aug | 2022 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
BAYAMON | 2022-08-28 12:29 | 2022-08-28 13:16 | 1382 | 0:47 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1706-02 LLEVA EL 1706-03 - SE ABRIO AMARRE PARA SECCIONALIZAR - SE CONTINUA PATRULLANDO | B22082800072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-08-28 | 64954 | keep | 0 | Aug | 2022 | 0.04424 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-08-28 12:29 | 2022-08-28 13:43 | 663 | 1:14 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1706-02 LLEVA EL 1706-03 - SE ABRIO AMARRE PARA SECCIONALIZAR - FALTA POR ENTRAR 70% DEL 1706-03 | B22082800072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 74 | 2022-08-28 | 49062 | keep | 0 | Aug | 2022 | 0.033416 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
MAYAGÃœEZ | 2022-08-28 12:30 | 2022-08-28 13:20 | 4 | 0:50 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22082800029 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2022-08-28 | 200 | keep | 0 | Aug | 2022 | 0.00013622 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-08-28 12:36 | 2022-08-28 15:46 | 10 | 3:10 | P | TRANSFORMADOR AVERIADO | SE AGREGARON CARGAS A OTRO TRANSFORMADOR POR ESTAR AVERIADO UNO DE 50KVA A 2400 TODO EN SERVICIO | P22082800116 | New_Event | Service Transformer Failure | Include | Include | Equipment | 190 | 2022-08-28 | 1900 | keep | 0 | Aug | 2022 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-28 12:39 | 2022-08-28 12:40 | 2234 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B22082800072 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-28 | 2234 | keep | 0 | Aug | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-08-28 12:40 | 2022-08-28 18:46 | 311 | 6:06 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | B22082800084 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 366 | 2022-08-28 | 113826 | keep | 0 | Aug | 2022 | 0.077526 | 0.00021182 | Sustained | FALSE | FALSE | Not_TMED_Event | 311
BAYAMON | 2022-08-28 12:44 | 2022-08-28 19:49 | 176 | 7:05 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B22082800078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2022-08-28 | 74800 | keep | 0 | Aug | 2022 | 0.050946 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
CANOVANAS | 2022-08-28 12:49 | 2022-08-28 18:17 | 70 | 5:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R22082800047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 328 | 2022-08-28 | 22960 | keep | 0 | Aug | 2022 | 0.015638 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-08-28 12:51 | 2022-08-28 16:30 | 7 | 3:39 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C22082800034 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 219 | 2022-08-28 | 1533 | keep | 0 | Aug | 2022 | 0.0010441 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2022-08-28 12:59 | 2022-08-28 14:28 | 90 | 1:29 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P22082800118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2022-08-28 | 8010 | keep | 0 | Aug | 2022 | 0.0054556 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2022-08-28 13:00 | 2022-08-28 16:00 | 10 | 3:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | A22082800047 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2022-08-28 | 1800 | keep | 0 | Aug | 2022 | 0.001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-28 13:01 | 2022-08-28 13:02 | 2231 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22082800036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 2231 | keep | 0 | Aug | 2022 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
SAN JUAN | 2022-08-28 13:19 | 2022-08-28 16:44 | 25 | 3:25 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | S22082800031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2022-08-28 | 5125 | keep | 0 | Aug | 2022 | 0.0034906 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-08-28 13:31 | 2022-08-28 13:32 | 978 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082800122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 978 | keep | 0 | Aug | 2022 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
BAYAMON | 2022-08-28 13:33 | 2022-08-28 13:42 | 50 | 0:09 | P | NO SE REPORTO CAUSA | 1X20 DE SU-8 @ RISER | B22082800110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-08-28 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-28 13:33 | 2022-08-28 18:20 | 10 | 4:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | M22082800042 | New_Event | Cutout Failure | Include | Include | Equipment | 287 | 2022-08-28 | 2870 | keep | 0 | Aug | 2022 | 0.0019547 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-08-28 13:35 | 2022-08-28 14:21 | 1 | 0:46 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22082800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-08-28 | 46 | keep | 0 | Aug | 2022 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-28 13:43 | 2022-08-28 14:07 | 198 | 0:24 | P | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1706-02 LLEVA EL 1706-03 SE CERRO POR PARTE QUEDO ENSERVICIO | B22082800072 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 24 | 2022-08-28 | 4752 | keep | 0 | Aug | 2022 | 0.0032366 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-28 13:44 | 2022-08-28 16:41 | 1 | 2:57 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN BANCO DE TRANSFORMADORES | R22082800055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 177 | 2022-08-28 | 177 | keep | 0 | Aug | 2022 | 0.00012055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-28 13:48 | 2022-08-28 13:49 | 3458 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR | M22082800047 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-28 | 3458 | keep | 0 | Aug | 2022 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2022-08-28 13:49 | 2022-08-28 14:45 | 100 | 0:56 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082800048 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 56 | 2022-08-28 | 5600 | keep | 0 | Aug | 2022 | 0.0038141 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-28 13:56 | 2022-08-28 15:50 | 1081 | 1:54 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA CERRAR ALIMENTADOR POR TRAMO | B22082800049 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-08-28 | 123234 | keep | 0 | Aug | 2022 | 0.083934 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-28 14:01 | 2022-08-28 15:20 | 2678 | 1:19 | T | CONDUCTOR ROTO O ABIERTO | REALIZAR DESGANCHE Y LEVANTAR CONDUCTOR EN EL SUELO | B22082800120 | New_Event | Primary Wire Break | Include | Include | Equipment | 79 | 2022-08-28 | 211562 | keep | 0 | Aug | 2022 | 0.14409 | 0.001824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2678
AGUADILLA | 2022-08-28 14:11 | 2022-08-28 17:00 | 75 | 2:49 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082800051 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 169 | 2022-08-28 | 12675 | keep | 0 | Aug | 2022 | 0.0086329 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-08-28 14:13 | 2022-08-28 20:00 | 100 | 5:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | M22082800053 | New_Event | Primary Wire Break | Include | Include | Equipment | 347 | 2022-08-28 | 34700 | keep | 0 | Aug | 2022 | 0.023634 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-08-28 14:38 | 2022-08-28 18:00 | 100 | 3:22 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082800069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-08-28 | 20200 | keep | 0 | Aug | 2022 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-28 14:43 | 2022-08-28 14:44 | 3626 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 20% DE SU CARGA POR EL 1801-02 | B22082800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 3626 | keep | 0 | Aug | 2022 | 0.0024697 | 0.0024697 | Momentary | FALSE | FALSE | Not_TMED_Event | 3626
VEGA BAJA | 2022-08-28 14:43 | 2022-08-28 19:42 | 25 | 4:59 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN C/L Y 1X 15 EN XMR DESGANCE | B22082800151 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 299 | 2022-08-28 | 7475 | keep | 0 | Aug | 2022 | 0.0050912 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-08-28 14:45 | 2022-08-28 20:03 | 1860 | 5:18 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR SE REPARA 2 TRAMOS DE LINEA PRIMARIA PARTIDAS EN TRONCAL DE ALIMENTADOR | A22082800040 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 318 | 2022-08-28 | 591480 | keep | 0 | Aug | 2022 | 0.40285 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
GUAYAMA | 2022-08-28 14:47 | 2022-08-28 16:32 | 70 | 1:45 | P | CRUCETA DEFECTUOSA O AVERIADA | CRUCETA PARTIDA POR ACCIDENTE DE AUTO 1 X 65 EN CORTE DE LINEA SE INSTALARON 2 AISLADORES | P22082800127 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 105 | 2022-08-28 | 7350 | keep | 0 | Aug | 2022 | 0.0050061 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-08-28 14:55 | 2022-08-29 11:50 | 800 | 20:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA SE CERRO CORTE DE LINEA | M22082800073 | New_Event | Primary Wire Break | Include | Include | Equipment | 1255 | 2022-08-28 | 1004000 | keep | 0 | Aug | 2022 | 0.68382 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
AGUADILLA | 2022-08-28 14:58 | 2022-08-28 18:20 | 70 | 3:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082800074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-08-28 | 14140 | keep | 0 | Aug | 2022 | 0.0096307 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-08-28 14:58 | 2022-08-28 21:29 | 10 | 6:31 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A22082800159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2022-08-28 | 3910 | keep | 0 | Aug | 2022 | 0.0026631 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-28 14:58 | 2022-08-29 08:25 | 7 | 17:27 | P | NO SE REPORTO CAUSA | 1X20 EN XMR | B22082800159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1047 | 2022-08-28 | 7329 | keep | 0 | Aug | 2022 | 0.0049917 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-28 15:08 | 2022-08-28 17:20 | 40 | 2:12 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22082800037 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 132 | 2022-08-28 | 5280 | keep | 0 | Aug | 2022 | 0.0035962 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-28 15:11 | 2022-08-28 16:15 | 30 | 1:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082800075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 64 | 2022-08-28 | 1920 | keep | 0 | Aug | 2022 | 0.0013077 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-28 15:12 | 2022-08-28 19:25 | 40 | 4:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082800076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2022-08-28 | 10120 | keep | 0 | Aug | 2022 | 0.0068927 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-28 15:20 | 2022-08-28 18:40 | 670 | 3:20 | P | CONDUCTOR ROTO O ABIERTO | REALIZAR DESGANCHE Y LEVANTAR CONDUCTOR EN EL SUELO | B22082800120 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 200 | 2022-08-28 | 134000 | keep | 0 | Aug | 2022 | 0.091267 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-28 15:50 | 2022-08-28 16:32 | 756 | 0:42 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA CERRAR ALIMENTADOR POR TRAMO | B22082800049 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 42 | 2022-08-28 | 31752 | keep | 0 | Aug | 2022 | 0.021626 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-28 15:52 | 2022-08-28 19:15 | 50 | 3:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082800106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 203 | 2022-08-28 | 10150 | keep | 0 | Aug | 2022 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-08-28 16:21 | 2022-08-28 20:31 | 150 | 4:10 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA POR RAYOS | A22082800055 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 250 | 2022-08-28 | 37500 | keep | 0 | Aug | 2022 | 0.025541 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-08-28 16:26 | 2022-08-28 18:04 | 10 | 1:38 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C22082800044 | New_Event | Animals | Include | Include | Wildlife | 98 | 2022-08-28 | 980 | keep | 0 | Aug | 2022 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-28 16:34 | 2022-08-29 12:43 | 8 | 20:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2X15 EN XMR SE REMPLAZO CAJA PRIMARIA | B22082800188 | New_Event | Cutout Failure | Include | Include | Equipment | 1209 | 2022-08-28 | 9672 | keep | 0 | Aug | 2022 | 0.0065876 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-28 16:43 | 2022-08-28 19:56 | 5 | 3:13 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | 1 X 30 EN CORTE DE LINEA POR POSTE SECUNDARIO PARTIDO | A22082800061 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 193 | 2022-08-28 | 965 | keep | 0 | Aug | 2022 | 0.00065726 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-08-28 16:43 | 2022-08-29 08:26 | 45 | 15:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X40 EN C/L POR LLUVIAS | B22082800190 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 943 | 2022-08-28 | 42435 | keep | 0 | Aug | 2022 | 0.028902 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-08-28 16:49 | 2022-08-29 07:34 | 20 | 14:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L REEMPLAZO AISLADOR | C22082800045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 885 | 2022-08-28 | 17700 | keep | 0 | Aug | 2022 | 0.012055 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-08-28 16:50 | 2022-08-28 22:56 | 2 | 6:06 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A22082800065 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 366 | 2022-08-28 | 732 | keep | 0 | Aug | 2022 | 0.00049856 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2022-08-28 16:55 | 2022-08-29 08:15 | 10 | 15:20 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082800070 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 920 | 2022-08-28 | 9200 | keep | 0 | Aug | 2022 | 0.0062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-28 17:05 | 2022-08-28 20:35 | 6 | 3:30 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082800132 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 210 | 2022-08-28 | 1260 | keep | 0 | Aug | 2022 | 0.00085818 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-28 17:20 | 2022-08-28 21:58 | 60 | 4:38 | P | DESGANCHE | 1X50 EN C/L | B22082800199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-08-28 | 16680 | keep | 0 | Aug | 2022 | 0.011361 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-28 17:22 | 2022-08-28 18:36 | 70 | 1:14 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO AVERIADO | R22082800071 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 74 | 2022-08-28 | 5180 | keep | 0 | Aug | 2022 | 0.0035281 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-08-28 17:23 | 2022-08-29 15:00 | 250 | 21:37 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22082800087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1297 | 2022-08-28 | 324250 | keep | 0 | Aug | 2022 | 0.22085 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2022-08-28 17:33 | 2022-08-28 21:20 | 100 | 3:47 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082800140 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 227 | 2022-08-28 | 22700 | keep | 0 | Aug | 2022 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-28 17:37 | 2022-08-29 11:13 | 60 | 17:36 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | S22082800044 | New_Event | Primary Wire Break | Include | Include | Equipment | 1056 | 2022-08-28 | 63360 | keep | 0 | Aug | 2022 | 0.043154 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-08-28 17:38 | 2022-08-28 21:15 | 80 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A22082800094 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2022-08-28 | 17360 | keep | 0 | Aug | 2022 | 0.011824 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-08-28 17:38 | 2022-08-28 21:14 | 20 | 3:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A22082800093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 216 | 2022-08-28 | 4320 | keep | 0 | Aug | 2022 | 0.0029423 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-08-28 17:51 | 2022-08-28 21:43 | 57 | 3:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | A22082800098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2022-08-28 | 13224 | keep | 0 | Aug | 2022 | 0.0090068 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
MAYAGÃœEZ | 2022-08-28 17:55 | 2022-08-28 22:39 | 40 | 4:44 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22082800145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2022-08-28 | 11360 | keep | 0 | Aug | 2022 | 0.0077372 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-08-28 18:06 | 2022-08-28 20:06 | 90 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22082800217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2022-08-28 | 10800 | keep | 0 | Aug | 2022 | 0.0073558 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2022-08-28 18:09 | 2022-08-28 18:52 | 58 | 0:43 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C22082800046 | New_Event | Animals | Include | Include | Wildlife | 43 | 2022-08-28 | 2494 | keep | 0 | Aug | 2022 | 0.0016987 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-08-28 18:11 | 2022-08-29 11:11 | 1 | 17:00 | P | ANIMAL | 2X20 DE RISER @ MONTURA DE XMR POR CRUCE DE AVE | S22082800048 | New_Event | Animals | Include | Include | Wildlife | 1020 | 2022-08-28 | 1020 | keep | 0 | Aug | 2022 | 0.00069472 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-28 18:14 | 2022-08-28 20:50 | 30 | 2:36 | P | DESGANCHE | DESGANCHE 1 X40 EN C/L | B22082800229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-08-28 | 4680 | keep | 0 | Aug | 2022 | 0.0031875 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-28 18:15 | 2022-08-28 23:15 | 356 | 5:00 | P | DESGANCHE | 1 X 140 EN C/L SE DESGANCHO | S22082800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2022-08-28 | 106800 | keep | 0 | Aug | 2022 | 0.072741 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
PONCE | 2022-08-28 18:15 | 2022-08-29 06:02 | 125 | 11:47 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P22082800159 | New_Event | Animals | Include | Include | Wildlife | 707 | 2022-08-28 | 88375 | keep | 0 | Aug | 2022 | 0.060192 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-08-28 18:22 | 2022-08-28 19:49 | 150 | 1:27 | P | MAL TIEMPO/RAYOS | 1 X 200 EN CORTE DE LINEA POR RAYOS | A22082800107 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 87 | 2022-08-28 | 13050 | keep | 0 | Aug | 2022 | 0.0088883 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-08-28 18:30 | 2022-08-28 18:45 | 8 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL SECUNDARIO | M22082800144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2022-08-28 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-08-28 18:59 | 2022-08-29 00:40 | 25 | 5:41 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22082800113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 341 | 2022-08-28 | 8525 | keep | 0 | Aug | 2022 | 0.0058063 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-28 19:11 | 2022-08-29 10:22 | 25 | 15:11 | P | ARBOL SOBRE LINEA | 2X30 EN C/L SE RETIRO ARBOL DE LA LINEA | B22082800255 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 911 | 2022-08-28 | 22775 | keep | 0 | Aug | 2022 | 0.015512 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-28 19:20 | 2022-08-29 11:20 | 2 | 16:00 | P | ANIMAL | 1X50 EN C/L SE RETIRO IGUANA | B22082800260 | New_Event | Animals | Include | Include | Wildlife | 960 | 2022-08-28 | 1920 | keep | 0 | Aug | 2022 | 0.0013077 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-28 19:30 | 2022-08-29 02:23 | 5 | 6:53 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22082800173 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 413 | 2022-08-28 | 2065 | keep | 0 | Aug | 2022 | 0.0014065 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2022-08-28 19:51 | 2022-08-28 22:20 | 100 | 2:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | A22082800120 | New_Event | Primary Wire Break | Include | Include | Equipment | 149 | 2022-08-28 | 14900 | keep | 0 | Aug | 2022 | 0.010148 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-28 19:56 | 2022-08-29 17:45 | 3 | 21:49 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE CON TRANSFORMADOR AVERIADO DE 25KVA | A22082800061 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1309 | 2022-08-28 | 3927 | keep | 0 | Aug | 2022 | 0.0026747 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-28 20:10 | 2022-08-28 21:49 | 100 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22082800266 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-08-28 | 9900 | keep | 0 | Aug | 2022 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-28 20:17 | 2022-08-28 21:50 | 3 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A22082800128 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2022-08-28 | 279 | keep | 0 | Aug | 2022 | 0.00019003 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-08-28 20:49 | 2022-08-29 12:03 | 10 | 15:14 | P | NO SE REPORTO CAUSA | 2X15 EN XMR | B22082800278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 914 | 2022-08-28 | 9140 | keep | 0 | Aug | 2022 | 0.0062252 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-28 20:51 | 2022-08-29 09:45 | 50 | 12:54 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22082800179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 774 | 2022-08-28 | 38700 | keep | 0 | Aug | 2022 | 0.026358 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-28 20:56 | 2022-08-28 20:58 | 539 | 0:02 | T | CAUSAS EXTERNAS | DISPARO SE CERRO POR CONTROL | R22082800079 | New_Event | Damage From Public | Include | Include | Public | 2 | 2022-08-28 | 1078 | keep | 0 | Aug | 2022 | 0.00073422 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
VEGA BAJA | 2022-08-28 20:57 | 2022-08-29 02:00 | 75 | 5:03 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y UN PUENTE PRIMARIO ABIERTO | M22082800134 | New_Event | Primary Wire Break | Include | Include | Equipment | 303 | 2022-08-28 | 22725 | keep | 0 | Aug | 2022 | 0.015478 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2022-08-28 20:59 | 2022-08-28 23:38 | 539 | 2:39 | T | CAUSAS EXTERNAS | DISPARO INTERRUPTOR SE DESCRUZO CABLE DE TELEFONO Y SE DEJO LA CARGA TRANSFERIDA POR EL 2305-04, INTERRUPTOR ESTABA DESCARGADO SJ-220828-51 | R22082800079 | 1st_after_momentary | Damage From Public | Include | Include | Public | 159 | 2022-08-28 | 85701 | keep | 0 | Aug | 2022 | 0.058371 | 0.00036711 | Sustained | FALSE | FALSE | Not_TMED_Event | 539
GUAYAMA | 2022-08-28 21:47 | 2022-08-29 13:00 | 1 | 15:13 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE BOMBAS AAA | P22082800217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 913 | 2022-08-28 | 913 | keep | 0 | Aug | 2022 | 0.00062184 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-28 21:58 | 2022-08-28 23:21 | 5809 | 1:23 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO POSTE PARTIDO 10% EN SERVICIO | B22082800284 | New_Event | Primary Pole Failure | Include | Include | Equipment | 83 | 2022-08-28 | 482147 | keep | 0 | Aug | 2022 | 0.32839 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
FAJARDO | 2022-08-28 22:48 | 2022-08-29 10:34 | 58 | 11:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22082800117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 706 | 2022-08-28 | 40948 | keep | 0 | Aug | 2022 | 0.027889 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-08-28 22:49 | 2022-08-28 22:50 | 723 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL LLEVA 1711-05 10% 1711-04 | B22082800368 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 723 | keep | 0 | Aug | 2022 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-08-28 22:49 | 2022-08-28 22:50 | 198 | 0:01 | P | NO SE REPORTO CAUSA | 10% DE LA CARGA TRANSFERIDA AL 1711-02 DISPARO Y SE CERRO POR CONTROL | B22082800368 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 198 | keep | 0 | Aug | 2022 | 0.00013486 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-08-28 22:49 | 2022-08-28 22:50 | 1976 | 0:01 | T | NO SE REPORTO CAUSA | CARGA TRANSFERIDA AL 1711-02 DISPARO Y SE CERRO POR CONTROL | B22082800368 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-28 | 1976 | keep | 0 | Aug | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CANOVANAS | 2022-08-28 22:49 | 2022-08-29 10:30 | 14 | 11:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTES SECUNDARIOS QUEMADOS | R22082800118 | New_Event | Secondary Wire Break | Include | Include | Equipment | 701 | 2022-08-28 | 9814 | keep | 0 | Aug | 2022 | 0.0066843 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
FAJARDO | 2022-08-28 23:07 | 2022-08-29 14:50 | 2 | 15:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA ABIERTA | R22082900120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 943 | 2022-08-28 | 1886 | keep | 0 | Aug | 2022 | 0.0012845 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-08-28 23:20 | 2022-08-29 16:13 | 67 | 16:53 | P | DESGANCHE | 1 X 100 EN C/L | C22082800052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1013 | 2022-08-28 | 67871 | keep | 0 | Aug | 2022 | 0.046227 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2022-08-28 23:21 | 2022-08-29 12:23 | 60 | 13:02 | P | DESGANCHE | 1X50 EN C/L | B22082800199 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 782 | 2022-08-28 | 46920 | keep | 0 | Aug | 2022 | 0.031957 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-28 23:21 | 2022-08-29 01:50 | 5228 | 2:29 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR Y SE TRANSFIRIO 10% ADICIONAL AL 1716-03 | B22082800284 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 149 | 2022-08-28 | 778972 | keep | 0 | Aug | 2022 | 0.53055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-28 23:26 | 2022-08-29 13:00 | 25 | 13:34 | P | DESGANCHE | 1X50 DE AEREO PROVISIONAL @ T-54 | B22082800388 | New_Event | Vegetation Contact | Include | Include | Vegetation | 814 | 2022-08-28 | 20350 | keep | 0 | Aug | 2022 | 0.01386 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-28 23:29 | 2022-08-30 15:50 | 19 | 40:21 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL AEREO | B22082800388 | New_Event | UG Cable Fault | Include | Include | Equipment | 2421 | 2022-08-28 | 45999 | keep | 0 | Aug | 2022 | 0.03133 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2022-08-29 00:33 | 2022-08-29 00:34 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22082900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 990 | keep | 0 | Aug | 2022 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BAYAMON | 2022-08-29 01:50 | 2022-08-29 02:04 | 4647 | 0:14 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO POSTE PARTIDO Y SE CERRO MACHETES 79% EN SERVICIO | B22082800289 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 14 | 2022-08-29 | 65058 | keep | 0 | Aug | 2022 | 0.044311 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-29 02:04 | 2022-08-29 08:37 | 1220 | 6:33 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO POSTE PARTIDO PARA SU REEMPLAZO | B22082800289 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 393 | 2022-08-29 | 479460 | keep | 0 | Aug | 2022 | 0.32656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-29 03:20 | 2022-08-29 08:00 | 10 | 4:40 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | B22082900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 280 | 2022-08-29 | 2800 | keep | 0 | Aug | 2022 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-29 04:43 | 2022-08-29 06:37 | 50 | 1:54 | P | DESGANCHE | 1 X 65 EN C/L | C22082900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-08-29 | 5700 | keep | 0 | Aug | 2022 | 0.0038822 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-29 05:00 | 2022-08-29 09:30 | 77 | 4:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R22082900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-08-29 | 20790 | keep | 0 | Aug | 2022 | 0.01416 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
SAN JUAN | 2022-08-29 05:04 | 2022-08-29 08:31 | 3433 | 3:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | EN RECIERRE DEL 1204-02 QUE LLEVA SOLO EL 80% DE SU CARGA Y EL 10% DEL 1204-03 ABRIO BKR SECUNDARIO DE PORTATIL SE INSPECCIONO TODO SE SECCIONALIZO EL 1204-02, SE CERRO PORTATIL Y LUEGO SE CERRO 1204-02 45% EN SERVICIO | S22082900012 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 207 | 2022-08-29 | 710631 | keep | 0 | Aug | 2022 | 0.48401 | 0.0023382 | Sustained | FALSE | FALSE | Not_TMED_Event | 3433
SAN JUAN | 2022-08-29 05:04 | 2022-08-29 08:31 | 138 | 3:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | EN RECIERRE DEL 1204-02 QUE LLEVA SOLO EL 80% DE SU CARGA Y EL 10% DEL 1204-03 ABRIO BKR SECUNDARIO DE PORTATIL SE INSPECCIONO TODO SE SECCIONALIZO EL 1204-02, SE CERRO PORTATIL Y LUEGO SE CERRO 1204-02 45% EN SERVICIO Y LA CARGA DEL 10% DEL 1204-03 | S22082900675 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 207 | 2022-08-29 | 28566 | keep | 0 | Aug | 2022 | 0.019456 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
MAYAGÃœEZ | 2022-08-29 05:32 | 2022-08-29 18:04 | 30 | 12:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M22082900054 | New_Event | Primary Pole Failure | Include | Include | Equipment | 752 | 2022-08-29 | 22560 | keep | 0 | Aug | 2022 | 0.015366 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-29 05:54 | 2022-08-29 05:55 | 1417 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22082900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 1417 | keep | 0 | Aug | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
CAGUAS | 2022-08-29 06:08 | 2022-08-29 14:22 | 100 | 8:14 | P | PROBLEMA DEL CLIENTE | 2 X 40 Y 2 X 65 EN C/LS PROA EN BOMBAS AAA, SE DEJARON TIERRAS INTALADAS | C22082900024 | New_Event | Customer-Related Interruption | Include | Include | Public | 494 | 2022-08-29 | 49400 | keep | 0 | Aug | 2022 | 0.033646 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-29 06:14 | 2022-08-29 06:15 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22082900009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 4304 | keep | 0 | Aug | 2022 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CANOVANAS | 2022-08-29 06:43 | 2022-08-29 09:15 | 150 | 2:32 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | R22082900005 | New_Event | Animals | Include | Include | Wildlife | 152 | 2022-08-29 | 22800 | keep | 0 | Aug | 2022 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-29 06:57 | 2022-08-29 13:07 | 80 | 6:10 | P | CONDUCTOR ROTO O ABIERTO | 1X80 EN C/L 1X65 EN RISER SE REPARO CONDUCTOR PRIMARIO @ LA SALIDA (RADIAL) | B22082900034 | New_Event | Primary Wire Break | Include | Include | Equipment | 370 | 2022-08-29 | 29600 | keep | 0 | Aug | 2022 | 0.02016 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-08-29 07:06 | 2022-08-29 10:37 | 78 | 3:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S22082900104 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2022-08-29 | 16458 | keep | 0 | Aug | 2022 | 0.011209 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
BAYAMON | 2022-08-29 07:08 | 2022-08-29 14:55 | 100 | 7:47 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | B22082900044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2022-08-29 | 46700 | keep | 0 | Aug | 2022 | 0.031807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-29 07:16 | 2022-08-29 10:15 | 300 | 2:59 | P | CONDUCTOR ROTO O ABIERTO | SE SUBIO CONDUCTOR MEDIANTE GOI SJ-220829-02 | S22082900109 | New_Event | Primary Wire Break | Include | Include | Equipment | 179 | 2022-08-29 | 53700 | keep | 0 | Aug | 2022 | 0.036575 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-08-29 07:17 | 2022-08-29 10:15 | 4 | 2:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22082900017 | New_Event | Cutout Failure | Include | Include | Equipment | 178 | 2022-08-29 | 712 | keep | 0 | Aug | 2022 | 0.00048494 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-29 07:24 | 2022-08-29 09:50 | 25 | 2:26 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082900020 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 146 | 2022-08-29 | 3650 | keep | 0 | Aug | 2022 | 0.002486 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-08-29 07:28 | 2022-08-29 14:23 | 26 | 6:55 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L AVE | B22082900052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 415 | 2022-08-29 | 10790 | keep | 0 | Aug | 2022 | 0.007349 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
MAYAGÃœEZ | 2022-08-29 07:30 | 2022-08-29 09:30 | 30 | 2:00 | P | DESGANCHE | SE RETIRO BAMBUAS SOBRE LAS LINEAS Y SE REPARO LINEA PRIMARIA ROTA | M22082900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-08-29 | 3600 | keep | 0 | Aug | 2022 | 0.0024519 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-29 07:37 | 2022-08-29 07:38 | 2697 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22082900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-29 | 2697 | keep | 0 | Aug | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2022-08-29 07:38 | 2022-08-29 10:15 | 100 | 2:37 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082900008 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-08-29 | 15700 | keep | 0 | Aug | 2022 | 0.010693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-08-29 08:00 | 2022-08-29 09:05 | 7 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN LINEA SECUNDARIA | M22082900027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2022-08-29 | 455 | keep | 0 | Aug | 2022 | 0.0003099 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-08-29 08:00 | 2022-08-29 08:02 | 2368 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22082900071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-29 | 4736 | keep | 0 | Aug | 2022 | 0.0032257 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2022-08-29 08:00 | 2022-08-29 08:02 | 538 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22082900071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-29 | 1076 | keep | 0 | Aug | 2022 | 0.00073286 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2022-08-29 08:00 | 2022-08-29 08:02 | 1284 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22082900071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-08-29 | 2568 | keep | 0 | Aug | 2022 | 0.0017491 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2022-08-29 08:02 | 2022-08-29 12:53 | 10 | 4:51 | P | NO SE REPORTO CAUSA | 1X10 EN XMR | B22082900012 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 291 | 2022-08-29 | 2910 | keep | 0 | Aug | 2022 | 0.001982 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-29 08:07 | 2022-08-29 08:09 | 1403 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22082900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-29 | 2806 | keep | 0 | Aug | 2022 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
VEGA BAJA | 2022-08-29 08:12 | 2022-08-29 12:54 | 5 | 4:42 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B22082900076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2022-08-29 | 1410 | keep | 0 | Aug | 2022 | 0.00096034 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-29 08:18 | 2022-08-29 11:13 | 90 | 2:55 | P | DESGANCHE | 1 X 100 C/L SE REALIZO DESGANCHE | S22082900127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2022-08-29 | 15750 | keep | 0 | Aug | 2022 | 0.010727 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-08-29 08:24 | 2022-08-29 14:47 | 2 | 6:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22082900012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-08-29 | 766 | keep | 0 | Aug | 2022 | 0.00052172 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-08-29 08:26 | 2022-08-29 15:40 | 40 | 7:14 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22082900050 | New_Event | Animals | Include | Include | Wildlife | 434 | 2022-08-29 | 17360 | keep | 0 | Aug | 2022 | 0.011824 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-29 08:31 | 2022-08-29 09:06 | 2360 | 0:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01 DISPARO ALIMENTADOR 1204-02 LLEVANDO 10% DEL 1204-03 | S22082900012 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 35 | 2022-08-29 | 82600 | keep | 0 | Aug | 2022 | 0.056258 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-29 08:37 | 2022-08-30 13:07 | 9 | 28:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE NORMALIZO CARGAS CAMBIO DE POSTE PRIMARIO BY-220828-04 | B22082800284 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1710 | 2022-08-29 | 15390 | keep | 0 | Aug | 2022 | 0.010482 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-29 08:42 | 2022-08-29 11:20 | 1 | 2:38 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082900016 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 158 | 2022-08-29 | 158 | keep | 0 | Aug | 2022 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-29 08:52 | 2022-08-29 09:29 | 1 | 0:37 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22082900040 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 37 | 2022-08-29 | 37 | keep | 0 | Aug | 2022 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-29 08:52 | 2022-08-29 14:36 | 8 | 5:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EN XMR SE REMPLAZO BAJANTE Y LINEA SECUNDARIA | C22082900056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 344 | 2022-08-29 | 2752 | keep | 0 | Aug | 2022 | 0.0018744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-08-29 09:04 | 2022-08-29 16:14 | 1 | 7:10 | P | TRANSFORMADOR AVERIADO | 2 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 37.5KVA | A22082900021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 430 | 2022-08-29 | 430 | keep | 0 | Aug | 2022 | 0.00029287 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-29 09:04 | 2022-08-29 21:46 | 2 | 12:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA X 50KVA | A22082900020 | New_Event | Service Transformer Failure | Include | Include | Equipment | 762 | 2022-08-29 | 1524 | keep | 0 | Aug | 2022 | 0.001038 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-29 09:06 | 2022-08-29 09:09 | 3433 | 0:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01 DISPARO ALIMENTADOR 1204-02 LLEVANDO 10% DEL 1204-03 | S22082900148 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-08-29 | 10299 | keep | 0 | Aug | 2022 | 0.0070146 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-29 09:06 | 2022-08-29 09:09 | 138 | 0:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES DEL 1204-02 ESTE DISPARO QUE LLEVA 10% DEL 1204-03 | S22082900012 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 3 | 2022-08-29 | 414 | keep | 0 | Aug | 2022 | 0.00028197 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-29 09:08 | 2022-08-29 17:02 | 1 | 7:54 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22082900093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 474 | 2022-08-29 | 474 | keep | 0 | Aug | 2022 | 0.00032284 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-29 09:09 | 2022-08-29 11:30 | 2000 | 2:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01 SE REMPLAZARON MACHETES Y SE CONTINUO SECCIONALIZANDO ALIMENTADOR 1204-02 LLEVANDO 10% DEL 1204-03 | S22082900148 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 141 | 2022-08-29 | 282000 | keep | 0 | Aug | 2022 | 0.19207 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
GUAYAMA | 2022-08-29 09:15 | 2022-08-29 12:42 | 1 | 3:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO | P22082900066 | New_Event | Primary Wire Break | Include | Include | Equipment | 207 | 2022-08-29 | 207 | keep | 0 | Aug | 2022 | 0.00014099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-29 09:27 | 2022-08-29 10:04 | 18 | 0:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22082900025 | New_Event | Primary Wire Break | Include | Include | Equipment | 37 | 2022-08-29 | 666 | keep | 0 | Aug | 2022 | 0.00045361 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2022-08-29 09:29 | 2022-08-29 13:40 | 15 | 4:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22082900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2022-08-29 | 3765 | keep | 0 | Aug | 2022 | 0.0025643 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-29 09:38 | 2022-08-29 14:06 | 2 | 4:28 | P | NO SE REPORTO CAUSA | 1 X 20 , 1 X30 , 1 X 50 EN CORTES DE LINEA | B22082900096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2022-08-29 | 536 | keep | 0 | Aug | 2022 | 0.00036507 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-08-29 09:57 | 2022-08-29 12:30 | 27 | 2:33 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R22082900023 | New_Event | Animals | Include | Include | Wildlife | 153 | 2022-08-29 | 4131 | keep | 0 | Aug | 2022 | 0.0028136 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2022-08-29 10:07 | 2022-08-29 14:52 | 7 | 4:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22082900261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2022-08-29 | 1995 | keep | 0 | Aug | 2022 | 0.0013588 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2022-08-29 10:07 | 2022-08-29 15:50 | 4 | 5:43 | P | SECUNDARIA/OTROS | ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRAS Y PEDESTAL SECUNDARIO | C22082800042 | New_Event |  |  |  |  | 343 | 2022-08-29 | 1372 | keep | 0 | Aug | 2022 | 0.00093446 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-08-29 10:18 | 2022-08-29 13:03 | 12 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22082900079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2022-08-29 | 1980 | keep | 0 | Aug | 2022 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-08-29 10:37 | 2022-08-29 10:49 | 1 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S22082900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-08-29 | 12 | keep | 0 | Aug | 2022 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-29 10:37 | 2022-08-29 10:49 | 738 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S22082900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-08-29 | 8856 | keep | 0 | Aug | 2022 | 0.0060318 | 0.00050265 | Sustained | FALSE | FALSE | Not_TMED_Event | 738
SAN JUAN | 2022-08-29 10:37 | 2022-08-29 10:49 | 2422 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3400 | S22082900000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-08-29 | 29064 | keep | 0 | Aug | 2022 | 0.019795 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
BAYAMON | 2022-08-29 10:37 | 2022-08-29 10:42 | 959 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22082900353 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-29 | 4795 | keep | 0 | Aug | 2022 | 0.0032659 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-08-29 10:37 | 2022-08-29 10:42 | 1297 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22082900353 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-29 | 6485 | keep | 0 | Aug | 2022 | 0.0044169 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2022-08-29 10:37 | 2022-08-29 10:42 | 451 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22082900353 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-29 | 2255 | keep | 0 | Aug | 2022 | 0.0015359 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2022-08-29 10:37 | 2022-08-29 10:42 | 1264 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22082900353 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-29 | 6320 | keep | 0 | Aug | 2022 | 0.0043045 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2022-08-29 10:37 | 2022-08-29 10:42 | 620 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3400 | S22082900353 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-29 | 3100 | keep | 0 | Aug | 2022 | 0.0021114 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
SAN JUAN | 2022-08-29 10:49 | 2022-08-29 11:11 | 858 | 0:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES PARA DAR SERVICIO SE AMARRO Y OCASIONO DISPARO DE 1303-02 QUE LLEVA 80% DE SU CARGA, LLEVA 30% DEL 1204-04 Y 20% DEL 1204-02 SE ABRIO AMARRE SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S22082900134 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 22 | 2022-08-29 | 18876 | keep | 0 | Aug | 2022 | 0.012856 | 0.00058438 | Sustained | FALSE | FALSE | Not_TMED_Event | 858
SAN JUAN | 2022-08-29 10:49 | 2022-08-29 11:11 | 1977 | 0:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES PARA DAR SERVICIO SE AMARRO Y OCASIONO DISPARO DE 1303-02 QUE LLEVA 80% DE SU CARGA, LLEVA 30% DEL 1204-04 Y 20% DEL 1204-02 SE ABRIO AMARRE SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S22082900134 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 22 | 2022-08-29 | 43494 | keep | 0 | Aug | 2022 | 0.029624 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-08-29 10:49 | 2022-08-29 11:08 | 1681 | 0:19 | T | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES PARA DAR SERVICIO SE AMARRO 1204-02 CON 1303-02 Y OCASIONO DISPARO DE 1303-02 Y 1303-04 QUE LLEVA 1303-01 Y LLEVA 1346-06 PERO 1303-04 ESTA TRANSFERIDO AL 1303-05 | S22082900134 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 19 | 2022-08-29 | 31939 | keep | 0 | Aug | 2022 | 0.021754 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-08-29 10:49 | 2022-08-29 11:11 | 1948 | 0:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES PARA DAR SERVICIO SE AMARRO Y OCASIONO DISPARO DE 1303-02 QUE LLEVA 80% DE SU CARGA, LLEVA 30% DEL 1204-04 Y 20% DEL 1204-02 SE ABRIO AMARRE SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S22082900134 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 22 | 2022-08-29 | 42856 | keep | 0 | Aug | 2022 | 0.029189 | 0.0013268 | Sustained | FALSE | FALSE | Not_TMED_Event | 1948
SAN JUAN | 2022-08-29 10:49 | 2022-08-29 13:40 | 78 | 2:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S22082900104 | New_Event | Cutout Failure | Include | Include | Equipment | 171 | 2022-08-29 | 13338 | keep | 0 | Aug | 2022 | 0.0090845 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
SAN JUAN | 2022-08-29 10:49 | 2022-08-29 11:08 | 1598 | 0:19 | T | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES PARA DAR SERVICIO SE AMARRO 1204-02 CON 1303-02 Y OCASIONO DISPARO DE 1303-02 Y 1303-04 QUE LLEVA 1303-01 Y LLEVA 1346-06 PERO 1303-04 ESTA TRANSFERIDO AL 1303-05 | S22082900134 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 19 | 2022-08-29 | 30362 | keep | 0 | Aug | 2022 | 0.020679 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
YAUCO | 2022-08-29 10:57 | 2022-08-29 12:20 | 1 | 1:23 | P | ANIMAL | 2 X 8 EN MONTURA DE TRANSFORMADORES AVE CRUZO FASES | M22082900059 | New_Event | Animals | Include | Include | Wildlife | 83 | 2022-08-29 | 83 | keep | 0 | Aug | 2022 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-29 11:02 | 2022-08-29 13:40 | 282 | 2:38 | P | DESGANCHE | 1 X 40 EN C/L | C22082900090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2022-08-29 | 44556 | keep | 0 | Aug | 2022 | 0.030347 | 0.00019207 | Sustained | FALSE | FALSE | Not_TMED_Event | 282
MAYAGÃœEZ | 2022-08-29 11:02 | 2022-08-29 13:17 | 10 | 2:15 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M22082900061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-08-29 | 1350 | keep | 0 | Aug | 2022 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-29 11:04 | 2022-08-29 15:00 | 50 | 3:56 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22082900088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-08-29 | 11800 | keep | 0 | Aug | 2022 | 0.0080369 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-29 11:11 | 2022-08-29 14:09 | 400 | 2:58 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | S22082900134 | New_Event | Switch Failure | Include | Include | Equipment | 178 | 2022-08-29 | 71200 | keep | 0 | Aug | 2022 | 0.048494 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
UTUADO | 2022-08-29 11:12 | 2022-08-29 16:22 | 8 | 5:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082900041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2022-08-29 | 2480 | keep | 0 | Aug | 2022 | 0.0016891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-08-29 11:13 | 2022-08-29 16:00 | 200 | 4:47 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | P22082900089 | New_Event | Primary Wire Break | Include | Include | Equipment | 287 | 2022-08-29 | 57400 | keep | 0 | Aug | 2022 | 0.039095 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-08-29 11:14 | 2022-08-29 14:15 | 20 | 3:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES SECUNDARIAS DE TRANSFORMADOR | M22082900062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 181 | 2022-08-29 | 3620 | keep | 0 | Aug | 2022 | 0.0024656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-08-29 11:21 | 2022-08-29 13:48 | 1 | 2:27 | P | DESGANCHE | 1 X 15 EN RISER | R22082900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-08-29 | 147 | keep | 0 | Aug | 2022 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-29 11:29 | 2022-08-29 13:30 | 8 | 2:01 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR AVE CRUZO LINEAS | A22082900042 | New_Event | Animals | Include | Include | Wildlife | 121 | 2022-08-29 | 968 | keep | 0 | Aug | 2022 | 0.0006593 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-29 11:29 | 2022-08-29 16:53 | 50 | 5:24 | P | CONDUCTOR ROTO O ABIERTO | 3 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22082900043 | New_Event | Primary Wire Break | Include | Include | Equipment | 324 | 2022-08-29 | 16200 | keep | 0 | Aug | 2022 | 0.011034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-29 11:30 | 2022-08-29 11:55 | 1800 | 0:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01 SE CONTINUO SECCIONALIZANDO ALIMENTADOR 1204-02 LLEVANDO 10% DEL 1204-03 | S22082900675 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 25 | 2022-08-29 | 45000 | keep | 0 | Aug | 2022 | 0.030649 | 0.001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 1800
CANOVANAS | 2022-08-29 11:41 | 2022-08-29 13:27 | 138 | 1:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22082900038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-08-29 | 14628 | keep | 0 | Aug | 2022 | 0.0099631 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
FAJARDO | 2022-08-29 11:44 | 2022-08-29 16:47 | 26 | 5:03 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE CORTO PEDAZO DE POSTE PARTIDO EN EL TOPE | R22082900039 | New_Event | Primary Pole Failure | Include | Include | Equipment | 303 | 2022-08-29 | 7878 | keep | 0 | Aug | 2022 | 0.0053657 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
AGUADILLA | 2022-08-29 11:48 | 2022-08-29 17:30 | 200 | 5:42 | P | ARBOL SOBRE LINEA | 2 X 200 EN C/L, SE REPARO LINEA PRIMARIA PARTIDA POR ARBOL | M22082900066 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 342 | 2022-08-29 | 68400 | keep | 0 | Aug | 2022 | 0.046587 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-08-29 11:55 | 2022-08-29 12:07 | 1500 | 0:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01 SE CONTINUO SECCIONALIZANDO ALIMENTADOR 1204-02 LLEVANDO 10% DEL 1204-03 | S22082900675 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 12 | 2022-08-29 | 18000 | keep | 0 | Aug | 2022 | 0.01226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-29 11:58 | 2022-08-29 15:57 | 15 | 3:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS | M22082900070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 239 | 2022-08-29 | 3585 | keep | 0 | Aug | 2022 | 0.0024417 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-08-29 11:59 | 2022-08-29 12:13 | 934 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 13076 | keep | 0 | Aug | 2022 | 0.008906 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-08-29 11:59 | 2022-08-29 12:13 | 4 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 56 | keep | 0 | Aug | 2022 | 3.8141e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-08-29 11:59 | 2022-08-29 12:13 | 1479 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 20706 | keep | 0 | Aug | 2022 | 0.014103 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-08-29 11:59 | 2022-08-29 12:13 | 1841 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900050 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 25774 | keep | 0 | Aug | 2022 | 0.017555 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-08-29 11:59 | 2022-08-29 12:13 | 1950 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900050 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 27300 | keep | 0 | Aug | 2022 | 0.018594 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
VEGA BAJA | 2022-08-29 11:59 | 2022-08-29 12:13 | 2791 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900052 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 39074 | keep | 0 | Aug | 2022 | 0.026613 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2022-08-29 11:59 | 2022-08-29 12:13 | 1464 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900052 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 20496 | keep | 0 | Aug | 2022 | 0.01396 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2022-08-29 11:59 | 2022-08-29 12:13 | 759 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900052 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 10626 | keep | 0 | Aug | 2022 | 0.0072373 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2022-08-29 11:59 | 2022-08-29 12:13 | 1500 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 115 KV DOS BOCAS | A22082900052 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-08-29 | 21000 | keep | 0 | Aug | 2022 | 0.014303 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-08-29 12:07 | 2022-08-29 13:28 | 1000 | 1:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01 SE REMPLAZO AISLADOR PARTIDO SE CONTINUO SECCIONALIZANDO ALIMENTADOR 1204-02 LLEVANDO 10% DEL 1204-03 | S22082900675 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 81 | 2022-08-29 | 81000 | keep | 0 | Aug | 2022 | 0.055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-29 12:13 | 2022-08-29 12:14 | 1702 | 0:01 | T | ANIMAL | RECIERRE | C22082900103 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-29 | 1702 | keep | 0 | Aug | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
UTUADO | 2022-08-29 12:13 | 2022-08-29 12:50 | 1 | 0:37 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE NECESITA DESGANCHE | A22082900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2022-08-29 | 37 | keep | 0 | Aug | 2022 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-29 12:14 | 2022-08-29 17:30 | 80 | 5:16 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C22082900105 | 1st_after_momentary | Animals | Include | Include | Wildlife | 316 | 2022-08-29 | 25280 | keep | 0 | Aug | 2022 | 0.017218 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-29 12:18 | 2022-08-29 13:35 | 10 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | M22082900034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2022-08-29 | 770 | keep | 0 | Aug | 2022 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-29 12:26 | 2022-08-30 05:45 | 10 | 17:19 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082900074 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1039 | 2022-08-29 | 10390 | keep | 0 | Aug | 2022 | 0.0070766 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-08-29 12:27 | 2022-08-29 12:28 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22082900120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 3511 | keep | 0 | Aug | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
ARECIBO | 2022-08-29 12:34 | 2022-08-29 15:50 | 15 | 3:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22082900063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-08-29 | 2940 | keep | 0 | Aug | 2022 | 0.0020024 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-08-29 12:39 | 2022-08-29 14:31 | 80 | 1:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REEMPLAZO AISLADOR PRIMARIO | C22082900113 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 112 | 2022-08-29 | 8960 | keep | 0 | Aug | 2022 | 0.0061026 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-29 12:40 | 2022-08-29 12:41 | 966 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22082900124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 966 | keep | 0 | Aug | 2022 | 0.00065794 | 0.00065794 | Momentary | FALSE | FALSE | Not_TMED_Event | 966
MAYAGÃœEZ | 2022-08-29 12:42 | 2022-08-29 16:25 | 100 | 3:43 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2022-08-29 | 22300 | keep | 0 | Aug | 2022 | 0.015188 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-08-29 12:44 | 2022-08-29 14:00 | 867 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05SE ABRIO PUENTE HACIA CAJAS QUEMADAS Y SE CERO POR SCADA | S22082900000 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2022-08-29 | 65892 | keep | 0 | Aug | 2022 | 0.044879 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2022-08-29 12:44 | 2022-08-29 14:00 | 863 | 1:16 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO 1119-04 SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05 SE ABRIO PUENTE HACIA CAJAS QUEMADAS Y SE CERO POR SCADA. ADEMAS LLEVA 1119-02 | S22082900000 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2022-08-29 | 65588 | keep | 0 | Aug | 2022 | 0.044672 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
SAN JUAN | 2022-08-29 12:44 | 2022-08-29 14:00 | 2720 | 1:16 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO SE SECCIONALIZO Y SE CERRO POR SCADA LLEVA 95% DEL 1115-05SE ABRIO PUENTE HACIA CAJAS QUEMADAS Y SE CERO POR SCADA | S22082900000 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2022-08-29 | 206720 | keep | 0 | Aug | 2022 | 0.1408 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2022-08-29 12:55 | 2022-08-29 15:03 | 30 | 2:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA POR PORTAFUSIBLE AVERIADO | A22082900064 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-08-29 | 3840 | keep | 0 | Aug | 2022 | 0.0026154 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-29 12:59 | 2022-08-29 18:33 | 9 | 5:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22082900065 | New_Event | Cutout Failure | Include | Include | Equipment | 334 | 2022-08-29 | 3006 | keep | 0 | Aug | 2022 | 0.0020474 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2022-08-29 13:08 | 2022-08-29 20:38 | 80 | 7:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP | R22082900055 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 450 | 2022-08-29 | 36000 | keep | 0 | Aug | 2022 | 0.024519 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-29 13:16 | 2022-08-29 14:42 | 53 | 1:26 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22082900126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-08-29 | 4558 | keep | 0 | Aug | 2022 | 0.0031044 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2022-08-29 13:28 | 2022-08-29 13:30 | 3433 | 0:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES PARA NORMALIZAR 1204-02 QUE LLEVA 10% DEL 1204-03 DISPARO SE SECCIONALIZO Y SE CERRO POR SCADA | S22082900675 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-08-29 | 6866 | keep | 0 | Aug | 2022 | 0.0046764 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-08-29 13:28 | 2022-08-29 13:30 | 138 | 0:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES PARA NORMALIZAR 1204-02 QUE LLEVA 10% DEL 1204-03 DISPARO SE SECCIONALIZO Y SE CERRO POR SCADA | S22082900000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2022-08-29 | 276 | keep | 0 | Aug | 2022 | 0.00018798 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2022-08-29 13:30 | 2022-08-29 14:00 | 800 | 0:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01 SE REMPLAZO PARARRAYOS SE CONTINUO SECCIONALIZANDO ALIMENTADOR 1204-02 | S22082900675 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 30 | 2022-08-29 | 24000 | keep | 0 | Aug | 2022 | 0.016346 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
VEGA BAJA | 2022-08-29 13:36 | 2022-08-29 14:44 | 60 | 1:08 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L SE ELIMINO PARARAYO | B22082900127 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 68 | 2022-08-29 | 4080 | keep | 0 | Aug | 2022 | 0.0027789 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-08-29 14:00 | 2022-08-29 14:27 | 200 | 0:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | HACIENDO OPERACIONES MEDIANTE SJ-220829-01SE NORMALIZO ULTIMO TRAMO DE ALIMENTADOR | S22082900675 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 27 | 2022-08-29 | 5400 | keep | 0 | Aug | 2022 | 0.0036779 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-29 14:07 | 2022-08-29 17:35 | 150 | 3:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082900095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2022-08-29 | 31200 | keep | 0 | Aug | 2022 | 0.02125 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-29 14:12 | 2022-08-29 21:00 | 150 | 6:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M22082900098 | New_Event | Cutout Failure | Include | Include | Equipment | 408 | 2022-08-29 | 61200 | keep | 0 | Aug | 2022 | 0.041683 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-08-29 14:13 | 2022-08-29 20:00 | 80 | 5:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082900099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2022-08-29 | 27760 | keep | 0 | Aug | 2022 | 0.018907 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-08-29 14:16 | 2022-08-29 15:29 | 46 | 1:13 | P | DESGANCHE | 1 X 40 EN RISER Y 1 X 80 EN SU | R22082900061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2022-08-29 | 3358 | keep | 0 | Aug | 2022 | 0.0022871 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
GUAYAMA | 2022-08-29 14:16 | 2022-08-29 18:12 | 35 | 3:56 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22082900141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-08-29 | 8260 | keep | 0 | Aug | 2022 | 0.0056258 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-08-29 14:19 | 2022-08-29 14:20 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M22082900104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 1192 | keep | 0 | Aug | 2022 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2022-08-29 14:37 | 2022-08-30 14:35 | 300 | 23:58 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L SE REPARO TRES TRAMOS DE LINEA PARTIDA | M22082900116 | New_Event | Primary Wire Break | Include | Include | Equipment | 1438 | 2022-08-29 | 431400 | keep | 0 | Aug | 2022 | 0.29382 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-08-29 14:39 | 2022-08-29 16:37 | 90 | 1:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22082900064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-08-29 | 10620 | keep | 0 | Aug | 2022 | 0.0072332 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-08-29 14:44 | 2022-08-29 17:36 | 45 | 2:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS | M22082900124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 172 | 2022-08-29 | 7740 | keep | 0 | Aug | 2022 | 0.0052717 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-08-29 14:46 | 2022-08-29 14:47 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZO PRUEBA Y QUEDO EN SERVICIO | M22082900126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 1017 | keep | 0 | Aug | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
ARECIBO | 2022-08-29 14:53 | 2022-08-29 17:00 | 10 | 2:07 | P | DESGANCHE | 2 X 20 EN TRANSFORMADOR SE NECESITA DESGANCHE | A22082900085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-08-29 | 1270 | keep | 0 | Aug | 2022 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-08-29 14:59 | 2022-08-29 17:28 | 50 | 2:29 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082900088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 149 | 2022-08-29 | 7450 | keep | 0 | Aug | 2022 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-08-29 15:16 | 2022-08-29 21:33 | 8 | 6:17 | P | ANIMAL | 1 X 15 EN XMR AVE | B22082900139 | New_Event | Animals | Include | Include | Wildlife | 377 | 2022-08-29 | 3016 | keep | 0 | Aug | 2022 | 0.0020542 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-29 15:16 | 2022-08-29 17:35 | 10 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22082900140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-08-29 | 1390 | keep | 0 | Aug | 2022 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-29 15:24 | 2022-08-29 15:56 | 4085 | 0:32 | T | ANIMAL | DISPARO LAGARTO QUEMADO SOBRE TRANSFORMADOR | R22082900069 | New_Event | Animals | Include | Include | Wildlife | 32 | 2022-08-29 | 130720 | keep | 0 | Aug | 2022 | 0.089033 | 0.0027823 | Sustained | FALSE | FALSE | Not_TMED_Event | 4085
VEGA BAJA | 2022-08-29 15:32 | 2022-08-29 20:16 | 75 | 4:44 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082900093 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 284 | 2022-08-29 | 21300 | keep | 0 | Aug | 2022 | 0.014507 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-08-29 15:38 | 2022-08-29 20:55 | 200 | 5:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMP | A22082900094 | New_Event | Cutout Failure | Include | Include | Equipment | 317 | 2022-08-29 | 63400 | keep | 0 | Aug | 2022 | 0.043181 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-08-29 15:50 | 2022-08-29 15:51 | 327 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | C22082900183 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-29 | 327 | keep | 0 | Aug | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BARRANQUITAS | 2022-08-29 15:51 | 2022-08-30 05:48 | 60 | 13:57 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA MAQUINARIA TOCO LA LINEA | C22082900183 | 1st_after_momentary | Damage From Public | Include | Include | Public | 837 | 2022-08-29 | 50220 | keep | 0 | Aug | 2022 | 0.034205 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-08-29 16:14 | 2022-08-29 17:55 | 30 | 1:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082900105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-08-29 | 3030 | keep | 0 | Aug | 2022 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-29 16:20 | 2022-08-29 16:21 | 3626 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PARTE POR EL 1801-02 | B22082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 3626 | keep | 0 | Aug | 2022 | 0.0024697 | 0.0024697 | Momentary | FALSE | FALSE | Not_TMED_Event | 3626
CANOVANAS | 2022-08-29 16:21 | 2022-08-29 18:52 | 50 | 2:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R22082900094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-08-29 | 7550 | keep | 0 | Aug | 2022 | 0.0051423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-29 16:23 | 2022-08-29 22:54 | 10 | 6:31 | P | NO SE REPORTO CAUSA | 2 X 25 SM4 EN TRANSCLOSURE | S22082900894 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2022-08-29 | 3910 | keep | 0 | Aug | 2022 | 0.0026631 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-29 16:26 | 2022-08-29 23:20 | 200 | 6:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REMPLAZARON 2 CAJAS PRIMARIAS AVERIADAS | M22082900182 | New_Event | Cutout Failure | Include | Include | Equipment | 414 | 2022-08-29 | 82800 | keep | 0 | Aug | 2022 | 0.056395 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-08-29 16:45 | 2022-08-29 19:24 | 100 | 2:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | R22082900099 | New_Event | Primary Wire Break | Include | Include | Equipment | 159 | 2022-08-29 | 15900 | keep | 0 | Aug | 2022 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-08-29 16:47 | 2022-08-29 22:26 | 79 | 5:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C22082900169 | New_Event | Cutout Failure | Include | Include | Equipment | 339 | 2022-08-29 | 26781 | keep | 0 | Aug | 2022 | 0.01824 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2022-08-29 16:59 | 2022-08-29 17:52 | 36 | 0:53 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | B22082900153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2022-08-29 | 1908 | keep | 0 | Aug | 2022 | 0.0012995 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-08-29 17:00 | 2022-08-29 17:18 | 6 | 0:18 | P | NO SE REPORTO CAUSA | 1 X50 EN RISER | B22082900152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2022-08-29 | 108 | keep | 0 | Aug | 2022 | 7.3558e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-29 17:03 | 2022-08-30 10:25 | 40 | 17:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22082900194 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1042 | 2022-08-29 | 41680 | keep | 0 | Aug | 2022 | 0.028388 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-29 17:04 | 2022-08-29 21:46 | 50 | 4:42 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082900195 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 282 | 2022-08-29 | 14100 | keep | 0 | Aug | 2022 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-29 17:05 | 2022-08-29 20:20 | 23 | 3:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO PISTOLA Y 1 X 20 EN C/L | B22082900156 | New_Event | Secondary Wire Break | Include | Include | Equipment | 195 | 2022-08-29 | 4485 | keep | 0 | Aug | 2022 | 0.0030547 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2022-08-29 17:05 | 2022-08-29 20:59 | 23 | 3:54 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B22082900169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2022-08-29 | 5382 | keep | 0 | Aug | 2022 | 0.0036657 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
UTUADO | 2022-08-29 17:09 | 2022-08-29 18:05 | 1 | 0:56 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082900117 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 56 | 2022-08-29 | 56 | keep | 0 | Aug | 2022 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-08-29 17:11 | 2022-08-29 18:20 | 75 | 1:09 | P | ANIMAL | 1 X 140 EN C/L CRUCE X AVE | C22082900172 | New_Event | Animals | Include | Include | Wildlife | 69 | 2022-08-29 | 5175 | keep | 0 | Aug | 2022 | 0.0035247 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-08-29 17:18 | 2022-08-30 09:51 | 7 | 16:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A TRANSFORMADOR | M22082900202 | New_Event | Primary Wire Break | Include | Include | Equipment | 993 | 2022-08-29 | 6951 | keep | 0 | Aug | 2022 | 0.0047343 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-08-29 17:39 | 2022-08-29 18:56 | 25 | 1:17 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P22082900199 | New_Event | Animals | Include | Include | Wildlife | 77 | 2022-08-29 | 1925 | keep | 0 | Aug | 2022 | 0.0013111 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2022-08-29 18:10 | 2022-08-29 22:20 | 130 | 4:10 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22082900220 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 250 | 2022-08-29 | 32500 | keep | 0 | Aug | 2022 | 0.022136 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2022-08-29 18:13 | 2022-08-29 19:14 | 150 | 1:01 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22082900134 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 61 | 2022-08-29 | 9150 | keep | 0 | Aug | 2022 | 0.006232 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-08-29 18:17 | 2022-08-29 20:02 | 50 | 1:45 | P | DESGANCHE | 1 X 65 EN C/L | C22082900208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-08-29 | 5250 | keep | 0 | Aug | 2022 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-29 18:27 | 2022-08-30 11:04 | 7 | 16:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO 1 X 20 EN TRANSFORMADOR | S22082900948 | New_Event | Secondary Wire Break | Include | Include | Equipment | 997 | 2022-08-29 | 6979 | keep | 0 | Aug | 2022 | 0.0047534 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-08-29 18:37 | 2022-08-30 09:21 | 150 | 14:44 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082900230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 884 | 2022-08-29 | 132600 | keep | 0 | Aug | 2022 | 0.090313 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-08-29 18:54 | 2022-08-29 21:00 | 80 | 2:06 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22082900215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-29 | 10080 | keep | 0 | Aug | 2022 | 0.0068654 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-29 18:58 | 2022-08-30 15:23 | 9 | 20:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 37.5 POR 50KVA | B22082900167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1225 | 2022-08-29 | 11025 | keep | 0 | Aug | 2022 | 0.0075091 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-08-29 19:27 | 2022-08-30 10:20 | 85 | 14:53 | P | DESGANCHE | 1 X 100 EN C/L | C22082900223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 893 | 2022-08-29 | 75905 | keep | 0 | Aug | 2022 | 0.051699 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-08-29 19:31 | 2022-08-29 19:32 | 1784 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 90% DE SU CARGA POR EL 1801-02 | B22082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 1784 | keep | 0 | Aug | 2022 | 0.0012151 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2022-08-29 19:31 | 2022-08-29 19:32 | 906 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% DE SU CARGA POR EL 1801-02 | B22082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 906 | keep | 0 | Aug | 2022 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
BAYAMON | 2022-08-29 19:31 | 2022-08-29 19:32 | 186 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 90% DEL 1711-04 Y 20% DEL 1717-01 | B22082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 186 | keep | 0 | Aug | 2022 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
GUAYAMA | 2022-08-29 19:33 | 2022-08-29 19:34 | 2235 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082900240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 2235 | keep | 0 | Aug | 2022 | 0.0015222 | 0.0015222 | Momentary | FALSE | FALSE | Not_TMED_Event | 2235
BAYAMON | 2022-08-29 19:40 | 2022-08-29 21:49 | 241 | 2:09 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | B22082900231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-08-29 | 31089 | keep | 0 | Aug | 2022 | 0.021175 | 0.00016414 | Sustained | FALSE | FALSE | Not_TMED_Event | 241
HUMACAO | 2022-08-29 19:45 | 2022-08-30 06:42 | 35 | 10:57 | P | DESGANCHE | 1 X 50 EN C/L | C22082900228 | New_Event | Vegetation Contact | Include | Include | Vegetation | 657 | 2022-08-29 | 22995 | keep | 0 | Aug | 2022 | 0.015662 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-08-29 19:45 | 2022-08-30 06:45 | 50 | 11:00 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22082900227 | New_Event | Animals | Include | Include | Wildlife | 660 | 2022-08-29 | 33000 | keep | 0 | Aug | 2022 | 0.022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-29 19:59 | 2022-08-30 11:13 | 16 | 15:14 | P | CAUSAS EXTERNAS | SE REEMPLAZO TRANSFORMADOR IMPACTADO POR VEHICULO DE 100 X 100KVA | R22082900143 | New_Event | Damage From Public | Include | Include | Public | 914 | 2022-08-29 | 14624 | keep | 0 | Aug | 2022 | 0.0099603 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
UTUADO | 2022-08-29 20:03 | 2022-08-29 22:25 | 4 | 2:22 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22082900160 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 142 | 2022-08-29 | 568 | keep | 0 | Aug | 2022 | 0.00038686 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-08-29 20:12 | 2022-08-29 23:53 | 164 | 3:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22082900989 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-08-29 | 36244 | keep | 0 | Aug | 2022 | 0.024686 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
GUAYAMA | 2022-08-29 20:21 | 2022-08-29 20:22 | 2235 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22082900255 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 2235 | keep | 0 | Aug | 2022 | 0.0015222 | 0.0015222 | Momentary | FALSE | FALSE | Not_TMED_Event | 2235
ARECIBO | 2022-08-29 20:27 | 2022-08-30 13:00 | 1 | 16:33 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22082900162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 993 | 2022-08-29 | 993 | keep | 0 | Aug | 2022 | 0.00067633 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-29 20:32 | 2022-08-30 09:08 | 60 | 12:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | S22082901004 | New_Event | Cutout Failure | Include | Include | Equipment | 756 | 2022-08-29 | 45360 | keep | 0 | Aug | 2022 | 0.030894 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-08-29 20:45 | 2022-08-29 20:46 | 1894 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR CARGA POR EL 2301-03 EN SERVICIO | R22082900146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 1894 | keep | 0 | Aug | 2022 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2022-08-29 20:45 | 2022-08-29 20:46 | 424 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR LLEVA LA CARGA DEL 2301-01 EN SERVICIO | R22082900146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 424 | keep | 0 | Aug | 2022 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
CANOVANAS | 2022-08-29 20:45 | 2022-08-29 20:46 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22082900145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 1648 | keep | 0 | Aug | 2022 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
ARECIBO | 2022-08-29 20:59 | 2022-08-30 08:25 | 30 | 11:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A22082900164 | New_Event | Primary Wire Break | Include | Include | Equipment | 686 | 2022-08-29 | 20580 | keep | 0 | Aug | 2022 | 0.014017 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-29 21:22 | 2022-08-30 00:25 | 25 | 3:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA AVERIADA | M22082900318 | New_Event | Secondary Wire Break | Include | Include | Equipment | 183 | 2022-08-29 | 4575 | keep | 0 | Aug | 2022 | 0.003116 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-08-29 21:30 | 2022-08-30 06:15 | 183 | 8:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LINEA Y SE FIJO LINEA AL AISLADOR | P22082900261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 525 | 2022-08-29 | 96075 | keep | 0 | Aug | 2022 | 0.065436 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
YAUCO | 2022-08-29 21:30 | 2022-08-30 00:40 | 1268 | 3:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 SE RESTABLECIO CARGA 6501-1 Y 6501-02 | M22082900327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-08-29 | 240920 | keep | 0 | Aug | 2022 | 0.16409 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
YAUCO | 2022-08-29 21:30 | 2022-08-30 00:40 | 2064 | 3:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 SE RESTABLECIO CARGA 6501-1 Y 6501-02 | M22082900327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2022-08-29 | 392160 | keep | 0 | Aug | 2022 | 0.2671 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
YAUCO | 2022-08-29 21:30 | 2022-08-29 23:12 | 3036 | 1:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 1200 Y SE ENERGIZO SUB. 6501-00 CON LA CARGA DEL LOS ALIMENTADORES 6501-03 Y 6501-04 POR CARGA COMPROMETIDA EN BARRA 38 KV YAUCO II | M22082900327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2022-08-29 | 309672 | keep | 0 | Aug | 2022 | 0.21092 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
YAUCO | 2022-08-29 21:30 | 2022-08-29 23:12 | 2952 | 1:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 1200 Y SE ENERGIZO SUB. 6501-00 CON LA CARGA DEL LOS ALIMENTADORES 6501-03 Y 6501-04 POR CARGA COMPROMETIDA EN BARRA 38 KV YAUCO II | M22082900327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 102 | 2022-08-29 | 301104 | keep | 0 | Aug | 2022 | 0.20508 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
ARECIBO | 2022-08-29 21:44 | 2022-08-30 07:30 | 25 | 9:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | A22082900167 | New_Event | Cutout Failure | Include | Include | Equipment | 586 | 2022-08-29 | 14650 | keep | 0 | Aug | 2022 | 0.009978 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-29 21:52 | 2022-08-30 03:34 | 200 | 5:42 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M22082900361 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2022-08-29 | 68400 | keep | 0 | Aug | 2022 | 0.046587 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-08-29 21:52 | 2022-08-30 03:45 | 150 | 5:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22082900261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2022-08-29 | 52950 | keep | 0 | Aug | 2022 | 0.036064 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-08-29 22:08 | 2022-08-29 22:09 | 966 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22082900265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 966 | keep | 0 | Aug | 2022 | 0.00065794 | 0.00065794 | Momentary | FALSE | FALSE | Not_TMED_Event | 966
FAJARDO | 2022-08-29 22:13 | 2022-08-30 09:59 | 1 | 11:46 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO DE TRANSFORMADORES | R22082900151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 706 | 2022-08-29 | 706 | keep | 0 | Aug | 2022 | 0.00048085 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-29 22:48 | 2022-08-30 02:15 | 90 | 3:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22082900267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2022-08-29 | 18630 | keep | 0 | Aug | 2022 | 0.012689 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2022-08-29 22:57 | 2022-08-30 02:30 | 282 | 3:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGNCHE | C22082900249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-08-29 | 60066 | keep | 0 | Aug | 2022 | 0.040911 | 0.00019207 | Sustained | FALSE | FALSE | Not_TMED_Event | 282
SAN JUAN | 2022-08-29 23:09 | 2022-08-29 23:11 | 500 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1330-04 CON PARTE DE SU CARGA TRANSFERIDA AL 1345-02 | S22082900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-29 | 1000 | keep | 0 | Aug | 2022 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2022-08-29 23:12 | 2022-08-29 23:13 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22082900251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-29 | 5630 | keep | 0 | Aug | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
SAN JUAN | 2022-08-29 23:15 | 2022-08-30 01:28 | 1984 | 2:13 | T | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA SE CERRO POR SCADA | S22082901054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-08-29 | 263872 | keep | 0 | Aug | 2022 | 0.17972 | 0.0013513 | Sustained | FALSE | FALSE | Not_TMED_Event | 1984
CAGUAS | 2022-08-29 23:17 | 2022-08-30 07:53 | 80 | 8:36 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22082900254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 516 | 2022-08-29 | 41280 | keep | 0 | Aug | 2022 | 0.028116 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-08-29 23:54 | 2022-08-29 23:55 | 2366 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR REQUIERE DESGANCHE | A22082900169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-29 | 2366 | keep | 0 | Aug | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-08-29 23:55 | 2022-08-30 03:00 | 200 | 3:05 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE EVENTO SALIO CON ESA FECHA | A22083000007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-08-29 | 37000 | keep | 0 | Aug | 2022 | 0.025201 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-08-29 23:59 | 2022-08-30 09:00 | 8 | 9:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REEMPLAZO CAJA QUEMADA | C22082900268 | New_Event | Cutout Failure | Include | Include | Equipment | 541 | 2022-08-29 | 4328 | keep | 0 | Aug | 2022 | 0.0029478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-08-30 00:18 | 2022-08-30 07:29 | 45 | 7:11 | P | DESGANCHE | 1 X 50 EN C/L Y 2 X 10 EN XMR DESGANCHO | C22083000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 431 | 2022-08-30 | 19395 | keep | 0 | Aug | 2022 | 0.01321 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2022-08-30 00:22 | 2022-08-30 00:23 | 154 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1342-04 LLEVANDO 25% 1203-03 | S22083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 154 | keep | 0 | Aug | 2022 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2022-08-30 00:22 | 2022-08-30 00:23 | 390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR 1342-04 LLEVANDO 25% 1203-03 | S22083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 390 | keep | 0 | Aug | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2022-08-30 01:30 | 2022-08-30 09:28 | 22 | 7:58 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22083000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 478 | 2022-08-30 | 10516 | keep | 0 | Aug | 2022 | 0.0071624 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2022-08-30 02:13 | 2022-08-30 19:10 | 50 | 16:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR SUMERGIBLE DE 300 KVA @ 13 KV | M22083000004 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1017 | 2022-08-30 | 50850 | keep | 0 | Aug | 2022 | 0.034634 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-30 02:20 | 2022-08-30 10:51 | 70 | 8:31 | P | NO SE REPORTO CAUSA | 3 X 65 Y 2 X 100 EN CORTE DE LINEA NO CAUSA | S22083000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 511 | 2022-08-30 | 35770 | keep | 0 | Aug | 2022 | 0.024363 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-08-30 02:23 | 2022-08-30 09:45 | 4 | 7:22 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22083000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 442 | 2022-08-30 | 1768 | keep | 0 | Aug | 2022 | 0.0012042 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2022-08-30 02:25 | 2022-08-30 09:31 | 250 | 7:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | M22083000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 426 | 2022-08-30 | 106500 | keep | 0 | Aug | 2022 | 0.072537 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
VEGA BAJA | 2022-08-30 02:30 | 2022-08-30 09:20 | 40 | 6:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22083000010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 410 | 2022-08-30 | 16400 | keep | 0 | Aug | 2022 | 0.01117 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-08-30 02:33 | 2022-08-30 02:35 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C22083000022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-30 | 4252 | keep | 0 | Aug | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2022-08-30 03:14 | 2022-08-30 06:22 | 83 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22083000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-08-30 | 15604 | keep | 0 | Aug | 2022 | 0.010628 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
CAGUAS | 2022-08-30 03:48 | 2022-08-30 04:18 | 21 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | C22082900213 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-08-30 | 630 | keep | 0 | Aug | 2022 | 0.00042909 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-08-30 04:53 | 2022-08-30 09:54 | 40 | 5:01 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B22083000003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2022-08-30 | 12040 | keep | 0 | Aug | 2022 | 0.0082004 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-08-30 05:09 | 2022-08-30 05:10 | 2635 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22083000025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 2635 | keep | 0 | Aug | 2022 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2022-08-30 05:10 | 2022-08-30 08:49 | 50 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22083000056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-08-30 | 10950 | keep | 0 | Aug | 2022 | 0.007458 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-30 05:31 | 2022-08-30 17:10 | 30 | 11:39 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22083000028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 699 | 2022-08-30 | 20970 | keep | 0 | Aug | 2022 | 0.014283 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-08-30 05:42 | 2022-08-30 07:25 | 30 | 1:43 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22083000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-08-30 | 3090 | keep | 0 | Aug | 2022 | 0.0021046 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-08-30 06:00 | 2022-08-30 11:08 | 15 | 5:08 | P | DESGANCHE | 2 X 65 EN CL DESGANCHE | S22083000030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-08-30 | 4620 | keep | 0 | Aug | 2022 | 0.0031467 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-08-30 06:01 | 2022-08-30 10:15 | 190 | 4:14 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 140 EN C/L REEMPLAZO AISLADOR | C22083000033 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 254 | 2022-08-30 | 48260 | keep | 0 | Aug | 2022 | 0.03287 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
BARRANQUITAS | 2022-08-30 06:10 | 2022-08-30 09:44 | 30 | 3:34 | P | ARBOL SOBRE LINEA | 1 X 30 EN C/L RETIRO ARBOL DE LAS LINEAS | C22083000035 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 214 | 2022-08-30 | 6420 | keep | 0 | Aug | 2022 | 0.0043726 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-08-30 06:25 | 2022-08-30 12:39 | 34 | 6:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22083000003 | New_Event | Cutout Failure | Include | Include | Equipment | 374 | 2022-08-30 | 12716 | keep | 0 | Aug | 2022 | 0.0086608 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-08-30 06:42 | 2022-08-30 09:40 | 40 | 2:58 | P | ANIMAL | 2 X 100 EN C/L AVE | B22083000008 | New_Event | Animals | Include | Include | Wildlife | 178 | 2022-08-30 | 7120 | keep | 0 | Aug | 2022 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-30 06:43 | 2022-08-30 10:38 | 5 | 3:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | S22083000034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2022-08-30 | 1175 | keep | 0 | Aug | 2022 | 0.00080029 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-08-30 07:14 | 2022-08-30 17:55 | 334 | 10:41 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN C/L REEMPLAZO 80 PIES DE CABLE 2 EMPALMES Y 2 TERMINACIONES EN RISER | C22083000053 | New_Event | UG Cable Fault | Include | Include | Equipment | 641 | 2022-08-30 | 214094 | keep | 0 | Aug | 2022 | 0.14582 | 0.00022749 | Sustained | FALSE | FALSE | Not_TMED_Event | 334
BAYAMON | 2022-08-30 07:29 | 2022-08-30 07:30 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 QUE LLEVA 1909-09 | S22083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 222 | keep | 0 | Aug | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-08-30 07:29 | 2022-08-30 07:30 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 QUE LLEVA 1909-09 | S22083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 4456 | keep | 0 | Aug | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
UTUADO | 2022-08-30 07:47 | 2022-08-30 18:25 | 3 | 10:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA @ 4 KV POR UNO DE 37.5 KVA @ 4 KV | A22083000017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 638 | 2022-08-30 | 1914 | keep | 0 | Aug | 2022 | 0.0013036 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-08-30 07:53 | 2022-08-30 09:54 | 1 | 2:01 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO CAUSA | S22083000045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-08-30 | 121 | keep | 0 | Aug | 2022 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-08-30 07:53 | 2022-08-30 10:56 | 1 | 3:03 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R22083000004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2022-08-30 | 183 | keep | 0 | Aug | 2022 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-30 07:53 | 2022-08-30 09:35 | 60 | 1:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | A22083000020 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2022-08-30 | 6120 | keep | 0 | Aug | 2022 | 0.0041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-08-30 08:13 | 2022-08-30 12:06 | 6 | 3:53 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN RISER Y 1 X 65 EN SU CONTAMINACION | B22083000011 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 233 | 2022-08-30 | 1398 | keep | 0 | Aug | 2022 | 0.00095217 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-08-30 08:37 | 2022-08-30 11:09 | 172 | 2:32 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | P22083000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-08-30 | 26144 | keep | 0 | Aug | 2022 | 0.017807 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
SAN JUAN | 2022-08-30 08:39 | 2022-08-30 11:47 | 65 | 3:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | S22083000056 | New_Event | Cutout Failure | Include | Include | Equipment | 188 | 2022-08-30 | 12220 | keep | 0 | Aug | 2022 | 0.008323 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-08-30 08:53 | 2022-08-30 10:38 | 7 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO QUEMADO | R22083000007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2022-08-30 | 735 | keep | 0 | Aug | 2022 | 0.00050061 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-08-30 09:04 | 2022-08-30 19:53 | 1 | 10:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L | C22083000082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 649 | 2022-08-30 | 649 | keep | 0 | Aug | 2022 | 0.00044203 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-30 09:04 | 2022-08-30 11:28 | 20 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22083000037 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2022-08-30 | 2880 | keep | 0 | Aug | 2022 | 0.0019616 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-30 09:04 | 2022-08-30 12:20 | 12 | 3:16 | P | DESGANCHE | ABRIR C/L PARA DESGANCHAR Y SE CERRO C/L | B22083000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-08-30 | 2352 | keep | 0 | Aug | 2022 | 0.0016019 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-08-30 09:08 | 2022-08-30 12:45 | 8 | 3:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE VREPARO BAJANTE SAFADO SECUNDARIO DE TRANSFORMADOR | R22083000008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 217 | 2022-08-30 | 1736 | keep | 0 | Aug | 2022 | 0.0011824 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-08-30 09:18 | 2022-08-30 11:10 | 100 | 1:52 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTES DE LINEA | R22083000009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2022-08-30 | 11200 | keep | 0 | Aug | 2022 | 0.0076283 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-08-30 09:57 | 2022-08-30 10:30 | 40 | 0:33 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22083000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2022-08-30 | 1320 | keep | 0 | Aug | 2022 | 0.00089905 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-08-30 10:22 | 2022-08-30 12:12 | 5 | 1:50 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA 2 X 50 EN RISER | B22083000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-08-30 | 550 | keep | 0 | Aug | 2022 | 0.0003746 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-08-30 10:25 | 2022-08-30 12:27 | 8 | 2:02 | P | CABLE SOTERRADO AVERIADO | SE ABRE T-8 A T-9 PARA CONTRATISTA REPARE TOMA AUTORIZADO POR LUIS SANCHEZ | S22083000077 | New_Event | UG Cable Fault | Include | Include | Equipment | 122 | 2022-08-30 | 976 | keep | 0 | Aug | 2022 | 0.00066475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-08-30 10:26 | 2022-08-30 13:14 | 200 | 2:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100AMP X UNA DE 200AMP | M22083000045 | New_Event | Cutout Failure | Include | Include | Equipment | 168 | 2022-08-30 | 33600 | keep | 0 | Aug | 2022 | 0.022885 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2022-08-30 10:28 | 2022-08-30 14:10 | 12 | 3:42 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA A 4.16KV AVERIADO | M22083000046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 222 | 2022-08-30 | 2664 | keep | 0 | Aug | 2022 | 0.0018144 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-08-30 10:37 | 2022-08-30 13:25 | 30 | 2:48 | P | ARBOL SOBRE LINEA | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22083000039 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 168 | 2022-08-30 | 5040 | keep | 0 | Aug | 2022 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-30 10:50 | 2022-08-30 11:34 | 4 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA PARTIDA | M22083000050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2022-08-30 | 176 | keep | 0 | Aug | 2022 | 0.00011987 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-08-30 11:00 | 2022-08-30 12:15 | 7 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIA | S22083000078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2022-08-30 | 525 | keep | 0 | Aug | 2022 | 0.00035758 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2022-08-30 11:34 | 2022-08-30 12:55 | 50 | 1:21 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22083000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-08-30 | 4050 | keep | 0 | Aug | 2022 | 0.0027584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-30 12:10 | 2022-08-30 16:02 | 10 | 3:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTOR EN LA SALIDA SECUNDARIA | B22083000040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 232 | 2022-08-30 | 2320 | keep | 0 | Aug | 2022 | 0.0015801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-08-30 12:15 | 2022-08-30 14:16 | 30 | 2:01 | P | DESGANCHE | 1 X 50 EN C/L | C22083000106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-08-30 | 3630 | keep | 0 | Aug | 2022 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-30 12:16 | 2022-08-30 14:48 | 1 | 2:32 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 X 25KVA | R22083000026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2022-08-30 | 152 | keep | 0 | Aug | 2022 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-08-30 12:20 | 2022-08-30 13:28 | 5 | 1:08 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | R22083000028 | New_Event | Animals | Include | Include | Wildlife | 68 | 2022-08-30 | 340 | keep | 0 | Aug | 2022 | 0.00023157 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2022-08-30 12:22 | 2022-08-30 13:59 | 20 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES LLUVIAS | C22083000109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2022-08-30 | 1940 | keep | 0 | Aug | 2022 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-08-30 12:24 | 2022-08-30 12:27 | 2842 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO CERRADO X CONTROL NO CAUSA | C22083000111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-30 | 8526 | keep | 0 | Aug | 2022 | 0.005807 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-08-30 12:24 | 2022-08-30 13:58 | 472 | 1:34 | P | CONDUCTOR ROTO O ABIERTO | ABRIO MACHETES PARA LEVANTAR NEUTRAL PRIMARIO | C22083000110 | New_Event | Primary Wire Break | Include | Include | Equipment | 94 | 2022-08-30 | 44368 | keep | 0 | Aug | 2022 | 0.030219 | 0.00032148 | Sustained | FALSE | FALSE | Not_TMED_Event | 472
PONCE | 2022-08-30 12:30 | 2022-08-31 19:02 | 43 | 30:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 50 EN CORTE DE LINEA TRABAJAR REMPLAZANDO POSTE PRIMARIO PARTIDO | P22083000239 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1832 | 2022-08-30 | 78776 | keep | 0 | Aug | 2022 | 0.053654 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
ARECIBO | 2022-08-30 12:35 | 2022-08-30 13:50 | 2 | 1:15 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 37.5 KVA X 37.5 KVA | A22083000049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 75 | 2022-08-30 | 150 | keep | 0 | Aug | 2022 | 0.00010216 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-30 12:45 | 2022-08-30 12:46 | 1420 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S22083000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 1420 | keep | 0 | Aug | 2022 | 0.00096716 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
AGUADILLA | 2022-08-30 12:46 | 2022-08-30 14:20 | 8 | 1:34 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | M22083000067 | New_Event | Animals | Include | Include | Wildlife | 94 | 2022-08-30 | 752 | keep | 0 | Aug | 2022 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-08-30 12:55 | 2022-08-30 14:01 | 50 | 1:06 | P | PARARRAYOS DEFECTUOSO | 1 X 15 Y 1 X 30 EN TRANSFORMADOR Y CORTE DE LINEA SE REEMPLAZO PARARRAYO EXPLOTADO | R22083000033 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 66 | 2022-08-30 | 3300 | keep | 0 | Aug | 2022 | 0.0022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-30 13:06 | 2022-08-30 13:09 | 2999 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR | M22083000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2022-08-30 | 8997 | keep | 0 | Aug | 2022 | 0.0061278 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
UTUADO | 2022-08-30 13:07 | 2022-08-30 13:37 | 3502 | 0:30 | T | ARBOL SOBRE LINEA | DISPARO DEL INTERRUPTOR SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR Y PODER CERRARLO | A22083000059 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 30 | 2022-08-30 | 105060 | keep | 0 | Aug | 2022 | 0.071556 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
BARRANQUITAS | 2022-08-30 13:08 | 2022-08-30 13:19 | 4 | 0:11 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 15 KVA X 25 KVA | C22081900250 | New_Event | Service Transformer Failure | Include | Include | Equipment | 11 | 2022-08-30 | 44 | keep | 0 | Aug | 2022 | 2.9968e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-30 13:09 | 2022-08-30 13:10 | 281 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR MAL TIEMPO RAYOS | M22083000074 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-30 | 281 | keep | 0 | Aug | 2022 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-08-30 13:15 | 2022-08-30 16:00 | 150 | 2:45 | P | CONDUCTOR ROTO O ABIERTO | ABRIR C/L CARR 330 KM 3.0 BO. DUEY BAJO Y SE CERRO RECLOSER EN C/L CARR 114 INT 319 | M22083000079 | New_Event | Primary Wire Break | Include | Include | Equipment | 165 | 2022-08-30 | 24750 | keep | 0 | Aug | 2022 | 0.016857 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-08-30 13:19 | 2022-08-30 13:22 | 229 | 0:03 | T | MAL TIEMPO/RAYOS | DISPARO, LLEVA LA CARGA DEL 9901-02, CERRADO X CONTROL SE VERIFICO PERSONAL FUERA MAL TIEMPO | C22083000128 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 3 | 2022-08-30 | 687 | keep | 0 | Aug | 2022 | 0.00046791 | 0.00015597 | Momentary | FALSE | FALSE | Not_TMED_Event | 229
BARRANQUITAS | 2022-08-30 13:19 | 2022-08-30 13:22 | 1246 | 0:03 | T | MAL TIEMPO/RAYOS | DISPARO DEL 9901-01 | C22083000128 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 3 | 2022-08-30 | 3738 | keep | 0 | Aug | 2022 | 0.0025459 | 0.00084864 | Momentary | FALSE | FALSE | Not_TMED_Event | 1246
BARRANQUITAS | 2022-08-30 13:22 | 2022-08-30 17:37 | 4 | 4:15 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR QUEMADO DE 15 KVA X 25 KVA | C22081900250 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 255 | 2022-08-30 | 1020 | keep | 0 | Aug | 2022 | 0.00069472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-08-30 13:22 | 2022-08-30 18:57 | 150 | 5:35 | P | MAL TIEMPO/RAYOS | 2 X 100 EN C/L RAYOS | C22083000133 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 335 | 2022-08-30 | 50250 | keep | 0 | Aug | 2022 | 0.034225 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-30 13:25 | 2022-08-30 13:30 | 281 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-30 | 1405 | keep | 0 | Aug | 2022 | 0.00095694 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2022-08-30 13:25 | 2022-08-30 13:30 | 1252 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-30 | 6260 | keep | 0 | Aug | 2022 | 0.0042637 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2022-08-30 13:25 | 2022-08-30 13:30 | 595 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-30 | 2975 | keep | 0 | Aug | 2022 | 0.0020263 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2022-08-30 13:25 | 2022-08-30 13:30 | 51 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-30 | 255 | keep | 0 | Aug | 2022 | 0.00017368 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-30 13:25 | 2022-08-30 13:30 | 721 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-30 | 3605 | keep | 0 | Aug | 2022 | 0.0024553 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2022-08-30 13:25 | 2022-08-30 13:30 | 1382 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22083000069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-30 | 6910 | keep | 0 | Aug | 2022 | 0.0047064 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2022-08-30 13:25 | 2022-08-30 13:30 | 654 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22083000069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-08-30 | 3270 | keep | 0 | Aug | 2022 | 0.0022272 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
CAGUAS | 2022-08-30 13:27 | 2022-08-30 18:07 | 100 | 4:40 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYO | C22083000130 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 280 | 2022-08-30 | 28000 | keep | 0 | Aug | 2022 | 0.019071 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-30 13:35 | 2022-08-30 14:50 | 110 | 1:15 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22083000071 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-08-30 | 8250 | keep | 0 | Aug | 2022 | 0.005619 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2022-08-30 13:37 | 2022-08-30 13:44 | 281 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000104 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 1967 | keep | 0 | Aug | 2022 | 0.0013397 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-30 13:37 | 2022-08-30 13:44 | 1252 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000104 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 8764 | keep | 0 | Aug | 2022 | 0.0059691 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-30 13:37 | 2022-08-30 13:44 | 595 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000105 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 4165 | keep | 0 | Aug | 2022 | 0.0028368 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-30 13:37 | 2022-08-30 13:44 | 51 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000105 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 357 | keep | 0 | Aug | 2022 | 0.00024315 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-30 13:37 | 2022-08-30 13:44 | 721 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000105 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 5047 | keep | 0 | Aug | 2022 | 0.0034375 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-30 13:37 | 2022-08-30 13:44 | 3502 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22083000076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 24514 | keep | 0 | Aug | 2022 | 0.016696 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2022-08-30 13:37 | 2022-08-30 13:44 | 1241 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22083000076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 8687 | keep | 0 | Aug | 2022 | 0.0059167 | 0.00084524 | Sustained | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2022-08-30 13:37 | 2022-08-30 13:44 | 650 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22083000076 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 4550 | keep | 0 | Aug | 2022 | 0.003099 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2022-08-30 13:37 | 2022-08-30 13:44 | 1382 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22083000077 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 9674 | keep | 0 | Aug | 2022 | 0.0065889 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-30 13:37 | 2022-08-30 13:44 | 654 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | A22083000077 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-08-30 | 4578 | keep | 0 | Aug | 2022 | 0.0031181 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-30 13:44 | 2022-08-30 15:36 | 3502 | 1:52 | T | ARBOL SOBRE LINEA | DISPARO DEL INTERRUPTOR SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR Y PODER CERRARLO | A22083000059 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 112 | 2022-08-30 | 392224 | keep | 0 | Aug | 2022 | 0.26714 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-30 13:51 | 2022-08-30 14:20 | 2999 | 0:29 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA RETIRAR RAMAS QUEMANDO SOBRE LINEAS | M22083000116 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 29 | 2022-08-30 | 86971 | keep | 0 | Aug | 2022 | 0.059236 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
UTUADO | 2022-08-30 13:54 | 2022-08-30 15:11 | 50 | 1:17 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS TRASFERIDO | M22083000119 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 77 | 2022-08-30 | 3850 | keep | 0 | Aug | 2022 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-08-30 13:55 | 2022-08-30 18:47 | 24 | 4:52 | P | DESGANCHE | 1 X 50 EN C/L | C22083000138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 292 | 2022-08-30 | 7008 | keep | 0 | Aug | 2022 | 0.0047731 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
AGUADILLA | 2022-08-30 14:10 | 2022-08-30 14:31 | 1617 | 0:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22083000191 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-08-30 | 33957 | keep | 0 | Aug | 2022 | 0.023128 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-08-30 14:10 | 2022-08-30 14:31 | 1017 | 0:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22083000191 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-08-30 | 21357 | keep | 0 | Aug | 2022 | 0.014546 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-08-30 14:10 | 2022-08-30 14:31 | 828 | 0:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22083000191 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2022-08-30 | 17388 | keep | 0 | Aug | 2022 | 0.011843 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
HUMACAO | 2022-08-30 14:12 | 2022-08-30 16:35 | 1 | 2:23 | P | DESGANCHE | 1 X 30 EN RISER Y 1 X 10 EN XMR DESGANCHO | C22083000142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-08-30 | 143 | keep | 0 | Aug | 2022 | 9.7397e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-30 14:12 | 2022-08-30 17:19 | 80 | 3:07 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | M22083000149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2022-08-30 | 14960 | keep | 0 | Aug | 2022 | 0.010189 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-08-30 14:14 | 2022-08-30 14:15 | 2190 | 0:01 | T | MAL TIEMPO/RAYOS | REALIZA UNA OPERACION QUEDA Y EN SERVICIO | M22083000153 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-30 | 2190 | keep | 0 | Aug | 2022 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2022-08-30 14:15 | 2022-08-30 19:57 | 80 | 5:42 | P | MAL TIEMPO/RAYOS | 1 X 65 Y 1 X 100 EN C/L DESCARGAS ELECTRICAS | M22083000450 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 342 | 2022-08-30 | 27360 | keep | 0 | Aug | 2022 | 0.018635 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-30 14:30 | 2022-08-30 19:30 | 250 | 5:00 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L Y 1 X 80 EN C/L DESCARGAS ELECTRICAS | M22083000192 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 300 | 2022-08-30 | 75000 | keep | 0 | Aug | 2022 | 0.051082 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2022-08-30 14:30 | 2022-08-30 20:54 | 50 | 6:24 | P | MAL TIEMPO/RAYOS | 2 X 30 EN C/L DESCARGAS ELECTRICAS | M22083000194 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 384 | 2022-08-30 | 19200 | keep | 0 | Aug | 2022 | 0.013077 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-30 14:31 | 2022-08-30 17:10 | 12 | 2:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA A 4.16KV AVERIADO | M22083000046 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 159 | 2022-08-30 | 1908 | keep | 0 | Aug | 2022 | 0.0012995 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-30 14:31 | 2022-08-30 14:57 | 1017 | 0:26 | T | MAL TIEMPO/RAYOS | DISPARO INTERRUPTOR (NO HABIA RTU EN SUBESTACION) MAL TIEMPO LUEGO DE DISPARO DE LINEA 2000 | M22083000157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 26 | 2022-08-30 | 26442 | keep | 0 | Aug | 2022 | 0.01801 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2022-08-30 14:35 | 2022-08-30 14:36 | 1825 | 0:01 | T | DESGANCHE | REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | M22083000217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-30 | 1825 | keep | 0 | Aug | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
AGUADILLA | 2022-08-30 14:35 | 2022-08-30 14:36 | 1497 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE UNA OPERACION Y QUEDA EN SERVICIO. MAL TIEMPO | M22083000210 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-30 | 1497 | keep | 0 | Aug | 2022 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | Not_TMED_Event | 1497
MAYAGÃœEZ | 2022-08-30 14:36 | 2022-08-30 21:45 | 500 | 7:09 | P | DESGANCHE | 3 X 140 EN C/L Y 2 X 65 EN C/L Y 2 X 50 EN C/L Y 1 X 100 EN C/L DESGANCHE | M22083000262 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 429 | 2022-08-30 | 214500 | keep | 0 | Aug | 2022 | 0.14609 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-08-30 14:37 | 2022-08-30 19:04 | 5 | 4:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y SE REGULO XMR | B22083000062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 267 | 2022-08-30 | 1335 | keep | 0 | Aug | 2022 | 0.00090926 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-08-30 14:42 | 2022-08-30 14:43 | 2067 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | M22083000233 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-08-30 | 2067 | keep | 0 | Aug | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2022-08-30 14:43 | 2022-08-30 17:20 | 75 | 2:37 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGAS ELECTRICAS | M22083000205 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 157 | 2022-08-30 | 11775 | keep | 0 | Aug | 2022 | 0.0080199 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-08-30 14:48 | 2022-08-30 16:10 | 5 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | A22083000094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-08-30 | 410 | keep | 0 | Aug | 2022 | 0.00027925 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2022-08-30 14:49 | 2022-08-30 20:25 | 25 | 5:36 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO 1 X 65 EN CORTE DE LINEA | P22083000112 | New_Event | Primary Wire Break | Include | Include | Equipment | 336 | 2022-08-30 | 8400 | keep | 0 | Aug | 2022 | 0.0057212 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-30 14:50 | 2022-08-30 16:37 | 14 | 1:47 | P | MAL TIEMPO/RAYOS | 1 X 8 XMR DESCARGAS ELECTRICAS | M22083000252 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 107 | 2022-08-30 | 1498 | keep | 0 | Aug | 2022 | 0.0010203 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2022-08-30 14:50 | 2022-08-30 15:55 | 8 | 1:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA | A22083000084 | New_Event | Service Transformer Failure | Include | Include | Equipment | 65 | 2022-08-30 | 520 | keep | 0 | Aug | 2022 | 0.00035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-08-30 14:50 | 2022-08-30 15:50 | 2 | 1:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA | A22083000093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 60 | 2022-08-30 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-08-30 14:51 | 2022-08-30 17:00 | 150 | 2:09 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L DESCARGAS ELECTRICAS | M22083000253 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 129 | 2022-08-30 | 19350 | keep | 0 | Aug | 2022 | 0.013179 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-30 14:52 | 2022-08-31 05:13 | 30 | 14:21 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22083000257 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 861 | 2022-08-30 | 25830 | keep | 0 | Aug | 2022 | 0.017593 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-08-30 15:00 | 2022-08-30 15:19 | 1 | 0:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22083000066 | New_Event | Secondary Wire Break | Include | Include | Equipment | 19 | 2022-08-30 | 19 | keep | 0 | Aug | 2022 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-30 15:09 | 2022-08-30 17:30 | 80 | 2:21 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22083000097 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 141 | 2022-08-30 | 11280 | keep | 0 | Aug | 2022 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-08-30 15:11 | 2022-08-30 15:12 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000086 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-30 | 51 | keep | 0 | Aug | 2022 | 3.4736e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-30 15:11 | 2022-08-30 15:12 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8100 | M22083000086 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-30 | 721 | keep | 0 | Aug | 2022 | 0.00049107 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-30 15:12 | 2022-08-30 18:20 | 90 | 3:08 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L DESCARGA ELECTRICAS | M22083000295 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 188 | 2022-08-30 | 16920 | keep | 0 | Aug | 2022 | 0.011524 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2022-08-30 15:12 | 2022-08-30 18:10 | 150 | 2:58 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L Y 1 X 50 EN C/L Y 1 X 20 EN XMR DESCARGAS ELECTRICAS | M22083000292 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 178 | 2022-08-30 | 26700 | keep | 0 | Aug | 2022 | 0.018185 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-08-30 15:12 | 2022-08-30 19:00 | 50 | 3:48 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22083000119 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 228 | 2022-08-30 | 11400 | keep | 0 | Aug | 2022 | 0.0077645 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-30 15:25 | 2022-08-31 17:18 | 100 | 25:53 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22083000314 | New_Event | Primary Wire Break | Include | Include | Equipment | 1553 | 2022-08-30 | 155300 | keep | 0 | Aug | 2022 | 0.10577 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-08-30 15:28 | 2022-08-30 16:47 | 6 | 1:19 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES HACIA POSTE PRIMARIO PARTIDO VACANTE FINAL DE LINEA | C22083000152 | New_Event | Primary Pole Failure | Include | Include | Equipment | 79 | 2022-08-30 | 474 | keep | 0 | Aug | 2022 | 0.00032284 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-08-30 15:30 | 2022-08-30 17:50 | 150 | 2:20 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C.L PARA CERRAR PUEBTE PRIMARIO | M22083000321 | New_Event | Primary Wire Break | Include | Include | Equipment | 140 | 2022-08-30 | 21000 | keep | 0 | Aug | 2022 | 0.014303 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-08-30 15:31 | 2022-08-30 22:25 | 50 | 6:54 | P | MAL TIEMPO/RAYOS | 2 X 50 EN C/L DESCARGA ELECTRICAS | M22083000322 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 414 | 2022-08-30 | 20700 | keep | 0 | Aug | 2022 | 0.014099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-30 15:33 | 2022-08-30 15:37 | 4 | 0:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR REPARARON VARIAS CONDICIONES EN LA LINEA NEUTRAL | R22081600082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 4 | 2022-08-30 | 16 | keep | 0 | Aug | 2022 | 1.0898e-05 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2022-08-30 15:34 | 2022-08-30 16:37 | 7 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECUNDARIA | R22083000037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2022-08-30 | 441 | keep | 0 | Aug | 2022 | 0.00030036 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2022-08-30 15:34 | 2022-08-30 17:40 | 55 | 2:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P22083000125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-08-30 | 6930 | keep | 0 | Aug | 2022 | 0.00472 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
AGUADILLA | 2022-08-30 15:35 | 2022-08-30 17:10 | 12 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A22083000100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2022-08-30 | 1140 | keep | 0 | Aug | 2022 | 0.00077645 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2022-08-30 15:36 | 2022-08-30 16:06 | 400 | 0:30 | P | ARBOL SOBRE LINEA | 2 X 140 EN CONVERTIDOR SE RETIRO ARBOL SOBRE LAS LINEAS Y SE CERRO CORTE DE LINEA | A22083000102 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 30 | 2022-08-30 | 12000 | keep | 0 | Aug | 2022 | 0.0081731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-08-30 15:37 | 2022-08-30 15:39 | 7621 | 0:02 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR POR ERROR SE VERIFICO PERSONAL FUERA | R22083000038 | New_Event | Human Error | Include | Include | Other | 2 | 2022-08-30 | 15242 | keep | 0 | Aug | 2022 | 0.010381 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
ARECIBO | 2022-08-30 15:38 | 2022-08-30 15:40 | 30 | 0:02 | P | CAUSAS EXTERNAS | 2 X 30 EN CORTE DE LINEA CLIENTES DESGANCHANDO ARBOLES CRUZARON LAS LINEAS | A22083000101 | New_Event | Damage From Public | Include | Include | Public | 2 | 2022-08-30 | 60 | keep | 0 | Aug | 2022 | 4.0866e-05 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-08-30 15:39 | 2022-08-30 15:49 | 4 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR REPARARON VARIAS CONDICIONES EN LA LINEA NEUTRAL | R22081600082 | 1st_after_momentary | Secondary Wire Break | Include | Include | Equipment | 10 | 2022-08-30 | 40 | keep | 0 | Aug | 2022 | 2.7244e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-30 15:46 | 2022-08-30 16:16 | 2999 | 0:30 | T | DESGANCHE | DISPARO INTERRUPTOR SE RETIRO BAMBUS Y SE COLOCO INTERRUPTOR EN SERVICIO | M22083000337 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-08-30 | 89970 | keep | 0 | Aug | 2022 | 0.061278 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-08-30 15:47 | 2022-08-30 23:01 | 50 | 7:14 | P | DESGANCHE | 2 X 65 EN CORTE DE INEA POR DESGANCHE | P22083000132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2022-08-30 | 21700 | keep | 0 | Aug | 2022 | 0.01478 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-30 15:52 | 2022-08-30 21:57 | 68 | 6:05 | P | DESGANCHE | 2 X 65 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22083000138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 365 | 2022-08-30 | 24820 | keep | 0 | Aug | 2022 | 0.016905 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2022-08-30 15:52 | 2022-08-30 16:25 | 1 | 0:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | A22083000105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2022-08-30 | 33 | keep | 0 | Aug | 2022 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-30 15:54 | 2022-08-30 21:26 | 250 | 5:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 65 EN C/L Y 1 X 100 EN C/L LLUVIA | M22083000349 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 332 | 2022-08-30 | 83000 | keep | 0 | Aug | 2022 | 0.056531 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2022-08-30 15:54 | 2022-08-30 16:30 | 60 | 0:36 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGAS ELECTRICAS | M22083000348 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 36 | 2022-08-30 | 2160 | keep | 0 | Aug | 2022 | 0.0014712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-30 16:00 | 2022-08-30 19:07 | 300 | 3:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO C/L | M22083000079 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 187 | 2022-08-30 | 56100 | keep | 0 | Aug | 2022 | 0.038209 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-30 16:06 | 2022-08-31 12:49 | 200 | 20:43 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22083000378 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1243 | 2022-08-30 | 248600 | keep | 0 | Aug | 2022 | 0.16932 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2022-08-30 16:06 | 2022-08-30 16:07 | 3502 | 0:01 | T | ARBOL SOBRE LINEA | DISPARO DEL INTERRUPTOR SE CERRO POR SCADA | A22083000109 | Additional_clients | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-08-30 | 3502 | keep | 0 | Aug | 2022 | 0.0023852 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-08-30 16:07 | 2022-08-30 17:43 | 400 | 1:36 | P | ARBOL SOBRE LINEA | 2 X 140 EN CONVERTIDOR SE RETIRO ARBOL SOBRE LAS LINEAS Y SE CERRO CORTE DE LINEA | A22083000102 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 96 | 2022-08-30 | 38400 | keep | 0 | Aug | 2022 | 0.026154 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2022-08-30 16:09 | 2022-08-30 19:55 | 40 | 3:46 | P | MAL TIEMPO/RAYOS | 2 X 50 EN C/L DESCARGAS ELECTRICAS | M22083000385 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 226 | 2022-08-30 | 9040 | keep | 0 | Aug | 2022 | 0.0061571 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-30 16:13 | 2022-08-30 20:02 | 40 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGAS ELECTRICAS | M22083000390 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2022-08-30 | 9160 | keep | 0 | Aug | 2022 | 0.0062388 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-30 16:16 | 2022-08-30 17:00 | 25 | 0:44 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE DE BAMBU | M22083000337 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 44 | 2022-08-30 | 1100 | keep | 0 | Aug | 2022 | 0.0007492 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-30 16:29 | 2022-08-30 20:45 | 65 | 4:16 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | M22083000404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-08-30 | 16640 | keep | 0 | Aug | 2022 | 0.011333 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
AGUADILLA | 2022-08-30 16:30 | 2022-08-30 19:00 | 80 | 2:30 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | M22083000405 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-08-30 | 12000 | keep | 0 | Aug | 2022 | 0.0081731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-08-30 16:32 | 2022-08-30 21:59 | 9 | 5:27 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 37.5 KVA | R22083000051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 327 | 2022-08-30 | 2943 | keep | 0 | Aug | 2022 | 0.0020045 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-08-30 16:39 | 2022-08-30 18:49 | 20 | 2:10 | P | ANIMAL | 1 X 15 EN TRANSORMADOR CRUCE CON AVE | R22083000052 | New_Event | Animals | Include | Include | Wildlife | 130 | 2022-08-30 | 2600 | keep | 0 | Aug | 2022 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-30 16:43 | 2022-08-30 17:50 | 1 | 1:07 | P | DESGANCHE | 1 X 30 EN RISER | B22083000071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-08-30 | 67 | keep | 0 | Aug | 2022 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-08-30 16:57 | 2022-08-30 21:48 | 100 | 4:51 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L Y 1 X 40 EN C/L DESCARGAS ELECTRICAS | M22083000441 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 291 | 2022-08-30 | 29100 | keep | 0 | Aug | 2022 | 0.01982 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-30 17:00 | 2022-08-30 20:12 | 25 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO C/L | M22083000442 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2022-08-30 | 4800 | keep | 0 | Aug | 2022 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-08-30 17:01 | 2022-08-30 19:20 | 50 | 2:19 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L DESCARGA ELECTRICA | M22083000444 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 139 | 2022-08-30 | 6950 | keep | 0 | Aug | 2022 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-30 17:01 | 2022-08-30 20:05 | 30 | 3:04 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L DESCARGAS ELECTRICAS | M22083000445 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 184 | 2022-08-30 | 5520 | keep | 0 | Aug | 2022 | 0.0037596 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-08-30 17:05 | 2022-08-31 23:20 | 150 | 30:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22083000449 | New_Event | Primary Wire Break | Include | Include | Equipment | 1815 | 2022-08-30 | 272250 | keep | 0 | Aug | 2022 | 0.18543 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-08-30 17:10 | 2022-08-30 18:25 | 100 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE EN EL PISO 1 X 65 EN CORTE DE LINEA | P22083000086 | New_Event | Primary Wire Break | Include | Include | Equipment | 75 | 2022-08-30 | 7500 | keep | 0 | Aug | 2022 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-08-30 17:12 | 2022-08-30 23:13 | 75 | 6:01 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LA LINEA | M22083000457 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 361 | 2022-08-30 | 27075 | keep | 0 | Aug | 2022 | 0.018441 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-08-30 17:12 | 2022-08-31 08:18 | 9 | 15:06 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22083000113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 906 | 2022-08-30 | 8154 | keep | 0 | Aug | 2022 | 0.0055537 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2022-08-30 17:33 | 2022-08-30 21:24 | 210 | 3:51 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN TRONCAL PRIMARIO SE ABRE INTERRUPTOR PARA REPARAR CONDICION | M22083000477 | New_Event | Primary Wire Break | Include | Include | Equipment | 231 | 2022-08-30 | 48510 | keep | 0 | Aug | 2022 | 0.03304 | 0.00014303 | Sustained | FALSE | FALSE | Not_TMED_Event | 210
ARECIBO | 2022-08-30 17:41 | 2022-08-30 21:00 | 40 | 3:19 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A22083000115 | New_Event | Primary Wire Break | Include | Include | Equipment | 199 | 2022-08-30 | 7960 | keep | 0 | Aug | 2022 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-08-30 17:57 | 2022-08-30 21:24 | 25 | 3:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZA EN FID: 19498199 PARA REPARAR LUEGO TRAMO AVERIADO | M22083000493 | New_Event | Primary Wire Break | Include | Include | Equipment | 207 | 2022-08-30 | 5175 | keep | 0 | Aug | 2022 | 0.0035247 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2022-08-30 18:09 | 2022-08-30 18:35 | 3 | 0:26 | P | MAL TIEMPO/RAYOS | 2 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22083000118 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 26 | 2022-08-30 | 78 | keep | 0 | Aug | 2022 | 5.3125e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-08-30 18:16 | 2022-08-30 21:53 | 130 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | M22083000502 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2022-08-30 | 28210 | keep | 0 | Aug | 2022 | 0.019214 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
UTUADO | 2022-08-30 18:23 | 2022-08-30 19:15 | 40 | 0:52 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22083000119 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 52 | 2022-08-30 | 2080 | keep | 0 | Aug | 2022 | 0.0014167 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-30 18:25 | 2022-08-31 16:48 | 76 | 22:23 | P | ERROR HUMANO | SE LEVANTO LINEA PRIMARIA POR DESGANCHE HECHO POR COMPANIA PRIVADA | P22083000212 | New_Event | Human Error | Include | Include | Other | 1343 | 2022-08-30 | 102068 | keep | 0 | Aug | 2022 | 0.069518 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
AGUADILLA | 2022-08-30 18:32 | 2022-08-30 23:23 | 50 | 4:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22083000511 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 291 | 2022-08-30 | 14550 | keep | 0 | Aug | 2022 | 0.0099099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-30 18:53 | 2022-08-31 10:45 | 20 | 15:52 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22083000523 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 952 | 2022-08-30 | 19040 | keep | 0 | Aug | 2022 | 0.012968 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-08-30 18:53 | 2022-08-30 18:54 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22083000120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 1227 | keep | 0 | Aug | 2022 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
HUMACAO | 2022-08-30 18:55 | 2022-08-30 21:00 | 20 | 2:05 | P | DESGANCHE | 1 X 25 EN C/L | C22083000168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-08-30 | 2500 | keep | 0 | Aug | 2022 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-08-30 19:00 | 2022-08-30 20:13 | 1 | 1:13 | P | ANIMAL | 1 X 30 EN RISER AVE | S22083000139 | New_Event | Animals | Include | Include | Wildlife | 73 | 2022-08-30 | 73 | keep | 0 | Aug | 2022 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-30 19:13 | 2022-08-31 07:50 | 5 | 12:37 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGA ELECTRICA | P22083000221 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 757 | 2022-08-30 | 3785 | keep | 0 | Aug | 2022 | 0.0025779 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-08-30 19:15 | 2022-08-31 12:05 | 80 | 16:50 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PARTIDA | M22083000543 | New_Event | Primary Wire Break | Include | Include | Equipment | 1010 | 2022-08-30 | 80800 | keep | 0 | Aug | 2022 | 0.055033 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-30 19:23 | 2022-08-30 20:25 | 40 | 1:02 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGAS ELECTRICAS | M22083000551 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 62 | 2022-08-30 | 2480 | keep | 0 | Aug | 2022 | 0.0016891 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-08-30 19:29 | 2022-08-31 16:40 | 309 | 21:11 | P | CONDUCTOR ROTO O ABIERTO | GOI MY-220831-01A PARA REPARAR LINEA PRIMARIA | M22083000557 | New_Event | Primary Wire Break | Include | Include | Equipment | 1271 | 2022-08-30 | 392739 | keep | 0 | Aug | 2022 | 0.26749 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-08-30 19:33 | 2022-08-30 21:35 | 13 | 2:02 | P | MAL TIEMPO/RAYOS | 2 X 30 EN RISER Y 2 X 25 EN RISER, DESCARGAS ELECTRICAS | M22083000561 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 122 | 2022-08-30 | 1586 | keep | 0 | Aug | 2022 | 0.0010802 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-08-30 19:38 | 2022-08-30 22:32 | 150 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S22083000145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2022-08-30 | 26100 | keep | 0 | Aug | 2022 | 0.017777 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-08-30 19:50 | 2022-08-30 19:52 | 1565 | 0:02 | T | PARARRAYOS DEFECTUOSO | DISPARO NO RECIERRA CERRADO X CONTROL | C22083000175 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2022-08-30 | 3130 | keep | 0 | Aug | 2022 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
MAYAGÃœEZ | 2022-08-30 19:50 | 2022-08-30 21:30 | 75 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO C/L | M22083000577 | New_Event | Primary Wire Break | Include | Include | Equipment | 100 | 2022-08-30 | 7500 | keep | 0 | Aug | 2022 | 0.0051082 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-08-30 19:52 | 2022-08-31 06:50 | 96 | 10:58 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L REEMPLAZO PARARRAYO | C22083000186 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 658 | 2022-08-30 | 63168 | keep | 0 | Aug | 2022 | 0.043023 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
HUMACAO | 2022-08-30 19:54 | 2022-08-30 21:53 | 50 | 1:59 | P | DESGANCHE | 1 X 50 EN C/L | C22083000182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-08-30 | 5950 | keep | 0 | Aug | 2022 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-08-30 19:55 | 2022-08-30 22:30 | 10 | 2:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22083000087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 155 | 2022-08-30 | 1550 | keep | 0 | Aug | 2022 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-30 20:11 | 2022-08-30 20:12 | 1494 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA SE CERRO POR SCADA | A22083000125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-30 | 1494 | keep | 0 | Aug | 2022 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
AGUADILLA | 2022-08-30 20:27 | 2022-08-30 22:00 | 50 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIA | M22083000594 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2022-08-30 | 4650 | keep | 0 | Aug | 2022 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-30 20:48 | 2022-08-30 20:49 | 3699 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | R22083000063 | New_Event | Damage From Public | Include | Include | Public | 1 | 2022-08-30 | 3699 | keep | 0 | Aug | 2022 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2022-08-30 20:49 | 2022-08-30 21:55 | 290 | 1:06 | P | CAUSAS EXTERNAS | 1 X 80 EN RISER Y 1 X 100 EN CORTE DE LINEA CRUCE POR GLOBO | R22083000063 | 1st_after_momentary | Damage From Public | Include | Include | Public | 66 | 2022-08-30 | 19140 | keep | 0 | Aug | 2022 | 0.013036 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
MAYAGÃœEZ | 2022-08-30 20:50 | 2022-08-31 00:19 | 60 | 3:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22083000600 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 209 | 2022-08-30 | 12540 | keep | 0 | Aug | 2022 | 0.0085409 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-08-30 20:52 | 2022-08-31 15:13 | 50 | 18:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22083000602 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1101 | 2022-08-30 | 55050 | keep | 0 | Aug | 2022 | 0.037494 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-30 21:08 | 2022-08-31 12:21 | 20 | 15:13 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22083000606 | New_Event | Vegetation Contact | Include | Include | Vegetation | 913 | 2022-08-30 | 18260 | keep | 0 | Aug | 2022 | 0.012437 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-30 21:19 | 2022-08-31 08:59 | 10 | 11:40 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22083000198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 700 | 2022-08-30 | 7000 | keep | 0 | Aug | 2022 | 0.0047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-08-30 21:24 | 2022-08-30 21:37 | 595 | 0:13 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE EN TRONCAL Y SE COLOCO INTERRUPTOR 7902-01 CON CARGA DE 7902-02 EN SERVICIO | M22083000477 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 13 | 2022-08-30 | 7735 | keep | 0 | Aug | 2022 | 0.0052683 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-30 21:24 | 2022-08-30 21:37 | 51 | 0:13 | T | CONDUCTOR ROTO O ABIERTO | SE BRIO INTERRUPTOR 7902-01 CON CARGA 7902-02 PARA CERRAR PUENTE EN TRONCAL PRIMARIO | M22083000477 | New_Event | Primary Wire Break | Include | Include | Equipment | 13 | 2022-08-30 | 663 | keep | 0 | Aug | 2022 | 0.00045157 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2022-08-30 21:37 | 2022-08-31 22:57 | 25 | 25:20 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZA EN FID: 19498199 PARA REPARAR LUEGO TRAMO AVERIADO CONTINUA | M22083000493 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1520 | 2022-08-30 | 38000 | keep | 0 | Aug | 2022 | 0.025882 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-08-30 21:40 | 2022-08-30 21:41 | 718 | 0:01 | T | DESGANCHE | RECIERRE | C22083000200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-08-30 | 718 | keep | 0 | Aug | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
CAGUAS | 2022-08-30 21:41 | 2022-08-31 06:35 | 50 | 8:54 | P | DESGANCHE | 1 X 50 EN C/L | C22083000202 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 534 | 2022-08-30 | 26700 | keep | 0 | Aug | 2022 | 0.018185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-30 21:54 | 2022-08-31 10:35 | 25 | 12:41 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22083000615 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 761 | 2022-08-30 | 19025 | keep | 0 | Aug | 2022 | 0.012958 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-08-30 22:01 | 2022-08-31 19:29 | 25 | 21:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22083000266 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1288 | 2022-08-30 | 32200 | keep | 0 | Aug | 2022 | 0.021931 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-08-30 22:12 | 2022-08-31 10:02 | 10 | 11:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE CERRO C/L | B22083000098 | New_Event | Primary Wire Break | Include | Include | Equipment | 710 | 2022-08-30 | 7100 | keep | 0 | Aug | 2022 | 0.0048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-08-30 22:13 | 2022-08-31 15:21 | 450 | 17:08 | P | DESGANCHE | 5 X 65, 2 X 50 Y 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22083000616 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1028 | 2022-08-30 | 462600 | keep | 0 | Aug | 2022 | 0.31507 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2022-08-30 22:18 | 2022-08-31 15:57 | 7 | 17:39 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL T-15 @ T-16 | B22083000099 | New_Event | UG Cable Fault | Include | Include | Equipment | 1059 | 2022-08-30 | 7413 | keep | 0 | Aug | 2022 | 0.005049 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-08-30 22:37 | 2022-08-31 13:53 | 14 | 15:16 | P | DESGANCHE | 1 X 15 EN XMR Y SE REALIZO DESGANCHE | B22083000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 916 | 2022-08-30 | 12824 | keep | 0 | Aug | 2022 | 0.0087344 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2022-08-30 22:54 | 2022-08-31 00:27 | 3 | 1:33 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22083000622 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 93 | 2022-08-30 | 279 | keep | 0 | Aug | 2022 | 0.00019003 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-08-30 22:57 | 2022-09-01 13:30 | 3 | 38:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | M22083000493 | New_Event | Primary Wire Break | Include | Include | Equipment | 2313 | 2022-08-30 | 6939 | keep | 0 | Aug | 2022 | 0.0047261 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-08-30 23:27 | 2022-08-31 09:47 | 50 | 10:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R22083000070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 620 | 2022-08-30 | 31000 | keep | 0 | Aug | 2022 | 0.021114 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-08-30 23:54 | 2022-08-31 03:16 | 100 | 3:22 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO CAUSA | P22083000279 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-08-30 | 20200 | keep | 0 | Aug | 2022 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-08-31 00:04 | 2022-08-31 12:25 | 20 | 12:21 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22083100001 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 741 | 2022-08-31 | 14820 | keep | 0 | Aug | 2022 | 0.010094 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-08-31 00:15 | 2022-08-31 11:55 | 30 | 11:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22083100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 700 | 2022-08-31 | 21000 | keep | 0 | Aug | 2022 | 0.014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-08-31 00:34 | 2022-08-31 06:25 | 34 | 5:51 | P | DESGANCHE | 1 X 15 EN CORTE DE LNEA POR DESGANCHE | P22083100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2022-08-31 | 11934 | keep | 0 | Aug | 2022 | 0.0081282 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2022-08-31 01:12 | 2022-08-31 09:30 | 42 | 8:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22083100004 | New_Event | Cutout Failure | Include | Include | Equipment | 498 | 2022-08-31 | 20916 | keep | 0 | Aug | 2022 | 0.014246 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CANOVANAS | 2022-08-31 01:33 | 2022-08-31 01:34 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R22083100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 4085 | keep | 0 | Aug | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
BAYAMON | 2022-08-31 01:46 | 2022-08-31 01:47 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22083100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 3438 | keep | 0 | Aug | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
ARECIBO | 2022-08-31 02:53 | 2022-08-31 08:40 | 50 | 5:47 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A22083100002 | New_Event | Primary Wire Break | Include | Include | Equipment | 347 | 2022-08-31 | 17350 | keep | 0 | Aug | 2022 | 0.011817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-31 03:26 | 2022-08-31 10:34 | 45 | 7:08 | P | CABLE SOTERRADO AVERIADO | 1 X 80 SUM-20 AVERIA NUEVA T-1 A T-1A AVERIA VIEJA T-2 A T-1A SE VA A CONTRUIR PROVISIONAL | R22083100002 | New_Event | UG Cable Fault | Include | Include | Equipment | 428 | 2022-08-31 | 19260 | keep | 0 | Aug | 2022 | 0.013118 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2022-08-31 03:49 | 2022-08-31 07:48 | 150 | 3:59 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN C/LS DESGANCHO | C22083100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-08-31 | 35850 | keep | 0 | Aug | 2022 | 0.024417 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-08-31 03:56 | 2022-08-31 03:57 | 1131 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22083100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1131 | keep | 0 | Aug | 2022 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
VEGA BAJA | 2022-08-31 04:13 | 2022-08-31 04:14 | 2368 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22083100010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-31 | 2368 | keep | 0 | Aug | 2022 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2022-08-31 04:13 | 2022-08-31 04:14 | 538 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22083100010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-31 | 538 | keep | 0 | Aug | 2022 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2022-08-31 04:13 | 2022-08-31 04:14 | 1284 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B22083100010 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-08-31 | 1284 | keep | 0 | Aug | 2022 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
BARRANQUITAS | 2022-08-31 04:22 | 2022-08-31 07:39 | 117 | 3:17 | P | DESGANCHE | 1 X 50 EN C/L | C22083100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-08-31 | 23049 | keep | 0 | Aug | 2022 | 0.015699 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2022-08-31 04:35 | 2022-08-31 04:36 | 1647 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22083100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1647 | keep | 0 | Aug | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
SAN JUAN | 2022-08-31 04:48 | 2022-08-31 04:50 | 225 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-31 | 450 | keep | 0 | Aug | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-08-31 04:48 | 2022-08-31 04:50 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 SE CERRO POR SCADA | S22083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-08-31 | 1740 | keep | 0 | Aug | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2022-08-31 05:08 | 2022-08-31 14:25 | 6 | 9:17 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22083100017 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 557 | 2022-08-31 | 3342 | keep | 0 | Aug | 2022 | 0.0022762 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2022-08-31 05:53 | 2022-08-31 09:00 | 45 | 3:07 | P | NO SE REPORTO CAUSA | 1 X 40 EN CONVERTIDOR NO SE REPORTO CAUSA | A22083100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2022-08-31 | 8415 | keep | 0 | Aug | 2022 | 0.0057314 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-08-31 06:00 | 2022-08-31 10:35 | 1 | 4:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE RISER A TRANSFORMADOR | M22083100137 | New_Event | Primary Wire Break | Include | Include | Equipment | 275 | 2022-08-31 | 275 | keep | 0 | Aug | 2022 | 0.0001873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-31 06:03 | 2022-08-31 17:30 | 1200 | 11:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE ABRE CORTE DE LINEA EN FID: 23632143 PARA SECCIONALIZAR Y REPARAR LINEA PRIMARIA ROTA | M22083100020 | New_Event | Primary Wire Break | Include | Include | Equipment | 687 | 2022-08-31 | 824400 | keep | 0 | Aug | 2022 | 0.5615 | 0.00081731 | Sustained | FALSE | FALSE | Not_TMED_Event | 1200
FAJARDO | 2022-08-31 06:06 | 2022-08-31 08:43 | 75 | 2:37 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA ANIMAL CRUZO FASE | R22083100006 | New_Event | Animals | Include | Include | Wildlife | 157 | 2022-08-31 | 11775 | keep | 0 | Aug | 2022 | 0.0080199 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-08-31 06:51 | 2022-08-31 08:44 | 35 | 1:53 | P | DESGANCHE | 1 X 50 EN C/L | C22083100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-08-31 | 3955 | keep | 0 | Aug | 2022 | 0.0026937 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-08-31 06:51 | 2022-08-31 18:23 | 30 | 11:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22083100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 692 | 2022-08-31 | 20760 | keep | 0 | Aug | 2022 | 0.01414 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-08-31 06:52 | 2022-08-31 12:19 | 8 | 5:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 SE REMPLAZO PORTAFUSIBLES | B22083100019 | New_Event | Cutout Failure | Include | Include | Equipment | 327 | 2022-08-31 | 2616 | keep | 0 | Aug | 2022 | 0.0017817 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2022-08-31 07:01 | 2022-08-31 09:50 | 12 | 2:49 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGA ELECTRICA | P22083100022 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 169 | 2022-08-31 | 2028 | keep | 0 | Aug | 2022 | 0.0013813 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-08-31 07:01 | 2022-08-31 16:31 | 25 | 9:30 | P | DESGANCHE | 2 X 5 EN TRANSFORMADOR Y 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22083100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 570 | 2022-08-31 | 14250 | keep | 0 | Aug | 2022 | 0.0097056 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-08-31 07:03 | 2022-08-31 10:09 | 65 | 3:06 | P | DESGANCHE | 2 X 30 EN C/L | C22083100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-08-31 | 12090 | keep | 0 | Aug | 2022 | 0.0082344 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-08-31 07:43 | 2022-09-02 14:30 | 200 | 54:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22083100045 | New_Event | Primary Wire Break | Include | Include | Equipment | 3287 | 2022-08-31 | 657400 | keep | 0 | Aug | 2022 | 0.44775 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-08-31 07:45 | 2022-08-31 08:15 | 4 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A22083100006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-08-31 | 120 | keep | 0 | Aug | 2022 | 8.1731e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-08-31 07:47 | 2022-08-31 07:48 | 8679 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DEL 1206-03 LLEVA 90% DE SU CARGA Y LLEVA EL 85% DEL 1204-05 | S22083100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 8679 | keep | 0 | Aug | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-08-31 07:47 | 2022-08-31 07:48 | 3719 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE LLEVA 90% DE SU CARGA Y LLEVA EL 85% DEL 1204-05 | S22083100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 3719 | keep | 0 | Aug | 2022 | 0.002533 | 0.002533 | Momentary | FALSE | FALSE | Not_TMED_Event | 3719
SAN JUAN | 2022-08-31 08:00 | 2022-08-31 08:03 | 5619 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 1620-04 LLEVA EL 90% DEL 1336-07 | S22083100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-31 | 16857 | keep | 0 | Aug | 2022 | 0.011481 | 0.0038271 | Momentary | FALSE | FALSE | Not_TMED_Event | 5619
CANOVANAS | 2022-08-31 08:00 | 2022-08-31 08:03 | 172 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1620-04 LLEVA EL 90% DEL 1336-07 | S22083100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-31 | 516 | keep | 0 | Aug | 2022 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
YAUCO | 2022-08-31 08:10 | 2022-08-31 12:05 | 18 | 3:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P22083100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-08-31 | 4230 | keep | 0 | Aug | 2022 | 0.002881 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-08-31 08:11 | 2022-08-31 17:40 | 2 | 9:29 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | M22083100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 569 | 2022-08-31 | 1138 | keep | 0 | Aug | 2022 | 0.00077509 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-08-31 08:20 | 2022-08-31 08:21 | 67 | 0:01 | T | ANIMAL | RECIERRE DEL INTERRUPTOR AVE CRUZO LINEAS | A22083100004 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-08-31 | 67 | keep | 0 | Aug | 2022 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2022-08-31 08:21 | 2022-08-31 10:15 | 66 | 1:54 | P | ANIMAL | 2 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | A22083100010 | 1st_after_momentary | Animals | Include | Include | Wildlife | 114 | 2022-08-31 | 7524 | keep | 0 | Aug | 2022 | 0.0051246 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
MAYAGÃœEZ | 2022-08-31 08:27 | 2022-09-01 09:35 | 1 | 25:08 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22083100074 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1508 | 2022-08-31 | 1508 | keep | 0 | Aug | 2022 | 0.0010271 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2022-08-31 08:28 | 2022-08-31 09:35 | 82 | 1:07 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA DESCARGA ELECTRICA | P22083100035 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 67 | 2022-08-31 | 5494 | keep | 0 | Aug | 2022 | 0.0037419 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
MAYAGÃœEZ | 2022-08-31 08:29 | 2022-08-31 21:39 | 30 | 13:10 | P | DESGANCHE | SE RETEZO LINEA PRIMARIA A CAUSA DE DESGANCHE | M22083100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 790 | 2022-08-31 | 23700 | keep | 0 | Aug | 2022 | 0.016142 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-31 08:39 | 2022-09-01 06:39 | 1 | 22:00 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22083100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1320 | 2022-08-31 | 1320 | keep | 0 | Aug | 2022 | 0.00089905 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-31 08:40 | 2022-08-31 09:47 | 16 | 1:07 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REMPLAZO PEDESTAL | B22083000078 | New_Event |  |  |  |  | 67 | 2022-08-31 | 1072 | keep | 0 | Aug | 2022 | 0.00073013 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-08-31 08:47 | 2022-08-31 12:05 | 1 | 3:18 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22083100094 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 198 | 2022-08-31 | 198 | keep | 0 | Aug | 2022 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-31 08:49 | 2022-08-31 10:17 | 58 | 1:28 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L CAMION SACUDIO LAS LINEAS | C22083100034 | New_Event | Damage From Public | Include | Include | Public | 88 | 2022-08-31 | 5104 | keep | 0 | Aug | 2022 | 0.0034763 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
VEGA BAJA | 2022-08-31 09:00 | 2022-08-31 16:44 | 11 | 7:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22083100018 | New_Event | Cutout Failure | Include | Include | Equipment | 464 | 2022-08-31 | 5104 | keep | 0 | Aug | 2022 | 0.0034763 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-08-31 09:11 | 2022-08-31 11:44 | 100 | 2:33 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN C/L DESGANCHE | B22083100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2022-08-31 | 15300 | keep | 0 | Aug | 2022 | 0.010421 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-31 09:13 | 2022-08-31 19:52 | 15 | 10:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B22083100040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 639 | 2022-08-31 | 9585 | keep | 0 | Aug | 2022 | 0.0065283 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-08-31 09:14 | 2022-08-31 12:39 | 1 | 3:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | S22083100013 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2022-08-31 | 205 | keep | 0 | Aug | 2022 | 0.00013962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-08-31 09:17 | 2022-08-31 16:30 | 19 | 7:13 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE MASIVO | M22083100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2022-08-31 | 8227 | keep | 0 | Aug | 2022 | 0.0056034 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2022-08-31 09:24 | 2022-08-31 09:25 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22083100050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1922 | keep | 0 | Aug | 2022 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
AGUADILLA | 2022-08-31 09:32 | 2022-08-31 15:35 | 2 | 6:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22083100122 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 363 | 2022-08-31 | 726 | keep | 0 | Aug | 2022 | 0.00049448 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-31 09:34 | 2022-08-31 12:47 | 1 | 3:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE DE XMR SECUNDARIO | S22083100020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 193 | 2022-08-31 | 193 | keep | 0 | Aug | 2022 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-08-31 09:34 | 2022-08-31 09:41 | 4622 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22083100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-08-31 | 32354 | keep | 0 | Aug | 2022 | 0.022036 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2022-08-31 09:39 | 2022-08-31 09:40 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B22083100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1746 | keep | 0 | Aug | 2022 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2022-08-31 09:40 | 2022-08-31 16:38 | 20 | 6:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L Y 1 X 65 EN SU-7A | B22083100096 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 418 | 2022-08-31 | 8360 | keep | 0 | Aug | 2022 | 0.005694 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-08-31 10:00 | 2022-08-31 12:37 | 19 | 2:37 | P | ARBOL SOBRE LINEA | 1 X 50 EN C/L RETIRO ARBOL DE LAS LINEAS, ENDEREZO POSTE Y RETEZO LINEAS | C22083100047 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 157 | 2022-08-31 | 2983 | keep | 0 | Aug | 2022 | 0.0020317 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2022-08-31 10:06 | 2022-08-31 10:07 | 1935 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR SCADA | B22083100097 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-08-31 | 1935 | keep | 0 | Aug | 2022 | 0.0013179 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-08-31 10:07 | 2022-08-31 10:46 | 600 | 0:39 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR MEDIANTE BY-220831-01 PARA SUBIR ALAMBRE PRIMARIO PARTIDO A LA SALIDA DE SUBESTACION | B22083100097 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 39 | 2022-08-31 | 23400 | keep | 0 | Aug | 2022 | 0.015938 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
AGUADILLA | 2022-08-31 10:13 | 2022-08-31 15:01 | 1 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M22083100144 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2022-08-31 | 288 | keep | 0 | Aug | 2022 | 0.00019616 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-31 10:24 | 2022-08-31 15:00 | 6 | 4:36 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE TRANSFIRIO XMR A POSTE NUEVO, POSTE EXISTENTE ESTA EN MALAS CONDICIONES | C22083100044 | New_Event | Primary Pole Failure | Include | Include | Equipment | 276 | 2022-08-31 | 1656 | keep | 0 | Aug | 2022 | 0.0011279 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-08-31 10:30 | 2022-08-31 14:22 | 40 | 3:52 | P | ARBOL SOBRE LINEA | 1 X 40 EN C/L SE RETIRO ARBOL DE LAS LINEAS | C22083100046 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 232 | 2022-08-31 | 9280 | keep | 0 | Aug | 2022 | 0.0063206 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-08-31 10:34 | 2022-08-31 12:27 | 50 | 1:53 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PPROVISIONAL DE EXISTENTE A T-1A 1 X 30 EN PROVISIONAL | R22083100002 | New_Event | UG Cable Fault | Include | Include | Equipment | 113 | 2022-08-31 | 5650 | keep | 0 | Aug | 2022 | 0.0038482 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-08-31 10:40 | 2022-08-31 12:05 | 1 | 1:25 | P | DESGANCHE | DESGANCHE Y SE REEMPLAZO CAJA PRIMARIA | S22083100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-08-31 | 85 | keep | 0 | Aug | 2022 | 5.7893e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-08-31 10:44 | 2022-08-31 11:27 | 8 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR REEMPLAZO BAJANTE SECUNDARIO QUEMADO NO FUNDIO | C22083100049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2022-08-31 | 344 | keep | 0 | Aug | 2022 | 0.0002343 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-31 10:46 | 2022-08-31 13:41 | 1935 | 2:55 | T | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO MEDIANTE GOI BY-220831-01 Y SE NORMALIZO CARGAS | B22083100097 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 175 | 2022-08-31 | 338625 | keep | 0 | Aug | 2022 | 0.23064 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-08-31 11:17 | 2022-08-31 17:00 | 1 | 5:43 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B22083100115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 343 | 2022-08-31 | 343 | keep | 0 | Aug | 2022 | 0.00023362 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-08-31 11:30 | 2022-09-01 07:00 | 1 | 19:30 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | P22083100069 | New_Event | Animals | Include | Include | Wildlife | 1170 | 2022-08-31 | 1170 | keep | 0 | Aug | 2022 | 0.00079688 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-08-31 11:36 | 2022-08-31 12:30 | 6 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR REEMPLAZO BAJANTE SECUNDARIO Y REPARO LINEA SECUNDARIA | C22083100040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2022-08-31 | 324 | keep | 0 | Aug | 2022 | 0.00022067 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-08-31 11:40 | 2022-08-31 13:16 | 8 | 1:36 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZO DE POSTE SECUNDARIO | M22083100180 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 96 | 2022-08-31 | 768 | keep | 0 | Aug | 2022 | 0.00052308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-31 11:50 | 2022-08-31 14:16 | 100 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO PARTIDO | A22083100032 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2022-08-31 | 14600 | keep | 0 | Aug | 2022 | 0.009944 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-08-31 11:59 | 2022-08-31 15:30 | 4 | 3:31 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A22083100033 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 211 | 2022-08-31 | 844 | keep | 0 | Aug | 2022 | 0.00057484 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-08-31 12:10 | 2022-08-31 13:07 | 10 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22083100142 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2022-08-31 | 570 | keep | 0 | Aug | 2022 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 4027 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 24162 | keep | 0 | Aug | 2022 | 0.016457 | 0.0027428 | Sustained | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 2468 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 14808 | keep | 0 | Aug | 2022 | 0.010086 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 1494 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 8964 | keep | 0 | Aug | 2022 | 0.0061053 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 15:15 | 2368 | 3:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 CARGA POR EL 9103-02 | B22083100161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-08-31 | 426240 | keep | 0 | Aug | 2022 | 0.29031 | 0.0016128 | Sustained | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 15:15 | 538 | 3:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 LLEVA LA CARGA DEL 9103-01 | B22083100161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-08-31 | 96840 | keep | 0 | Aug | 2022 | 0.065957 | 0.00036643 | Sustained | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 15:15 | 1284 | 3:00 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B22083100161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 180 | 2022-08-31 | 231120 | keep | 0 | Aug | 2022 | 0.15741 | 0.00087453 | Sustained | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 1310 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 7860 | keep | 0 | Aug | 2022 | 0.0053534 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 215 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 1290 | keep | 0 | Aug | 2022 | 0.00087861 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 1 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 6 | keep | 0 | Aug | 2022 | 4.0866e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 652 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 3912 | keep | 0 | Aug | 2022 | 0.0026644 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-08-31 12:15 | 2022-08-31 12:21 | 2704 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE L-2200 E INTERRUPTOR 16870 PROVOCANDO QUE SE APAGARA LA BARRA DE VEGA ALTA | B22083100134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-08-31 | 16224 | keep | 0 | Aug | 2022 | 0.01105 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
GUAYAMA | 2022-08-31 12:30 | 2022-08-31 19:41 | 80 | 7:11 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO Y NEUTRAL 1 X 100 EN CORTE DE LINEA | P22083100085 | New_Event | Primary Wire Break | Include | Include | Equipment | 431 | 2022-08-31 | 34480 | keep | 0 | Aug | 2022 | 0.023484 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-08-31 12:34 | 2022-08-31 15:04 | 10 | 2:30 | P | DESGANCHE | 2 X 40 EN C/L Y SE REALIZO DESGANCHE | B22083100166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-08-31 | 1500 | keep | 0 | Aug | 2022 | 0.0010216 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-31 12:59 | 2022-08-31 13:00 | 3766 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUED EN SERVICIO SU CARGA POR 2306-03 | R22083100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 3766 | keep | 0 | Aug | 2022 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
AGUADILLA | 2022-08-31 13:02 | 2022-08-31 20:09 | 7 | 7:07 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 15KVA POR UNO DE 15KVA | M22083100215 | New_Event | Service Transformer Failure | Include | Include | Equipment | 427 | 2022-08-31 | 2989 | keep | 0 | Aug | 2022 | 0.0020358 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-08-31 13:05 | 2022-08-31 13:06 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22083100095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1606 | keep | 0 | Aug | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CANOVANAS | 2022-08-31 13:09 | 2022-08-31 13:10 | 2005 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 1619-03 | R22083100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 2005 | keep | 0 | Aug | 2022 | 0.0013656 | 0.0013656 | Momentary | FALSE | FALSE | Not_TMED_Event | 2005
CANOVANAS | 2022-08-31 13:09 | 2022-08-31 13:10 | 5062 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1619-02 | R22083100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 5062 | keep | 0 | Aug | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
GUAYAMA | 2022-08-31 13:14 | 2022-08-31 13:15 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22083100103 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1606 | keep | 0 | Aug | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BAYAMON | 2022-08-31 13:20 | 2022-08-31 21:40 | 54 | 8:20 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DE RISER @ T-12 | S22083100056 | New_Event | UG Cable Fault | Include | Include | Equipment | 500 | 2022-08-31 | 27000 | keep | 0 | Aug | 2022 | 0.01839 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
GUAYAMA | 2022-08-31 13:27 | 2022-08-31 13:28 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22083100107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 3718 | keep | 0 | Aug | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2022-08-31 13:27 | 2022-08-31 20:02 | 100 | 6:35 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P22083100109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2022-08-31 | 39500 | keep | 0 | Aug | 2022 | 0.026903 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-31 13:29 | 2022-08-31 13:30 | 449 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | P22083100117 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-31 | 449 | keep | 0 | Aug | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
PONCE | 2022-08-31 13:32 | 2022-08-31 16:43 | 1262 | 3:11 | T | DESGANCHE | SE PUSO EN SERVICIO Y SE CERRARON CORTES DE LINEA 1 X 80 EN CORTE DE LINEA | P22083100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-08-31 | 241042 | keep | 0 | Aug | 2022 | 0.16417 | 0.00085954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1262
GUAYAMA | 2022-08-31 13:46 | 2022-08-31 13:47 | 449 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | P22083100121 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-31 | 449 | keep | 0 | Aug | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
GUAYAMA | 2022-08-31 13:47 | 2022-08-31 17:34 | 50 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 80 EN DIFERENTES CORTES DE LINEA POR MAL TIEMPO | P22083100118 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2022-08-31 | 11350 | keep | 0 | Aug | 2022 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-08-31 13:47 | 2022-08-31 16:10 | 600 | 2:23 | P | MAL TIEMPO/RAYOS | 3 X 200 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22083100237 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 143 | 2022-08-31 | 85800 | keep | 0 | Aug | 2022 | 0.058438 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
GUAYAMA | 2022-08-31 13:52 | 2022-08-31 16:06 | 8 | 2:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA DE NEUTRAL EN PEDESTAL SECUNDARIO | P22083100127 | New_Event | Secondary Wire Break | Include | Include | Equipment | 134 | 2022-08-31 | 1072 | keep | 0 | Aug | 2022 | 0.00073013 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2022-08-31 13:55 | 2022-08-31 15:30 | 100 | 1:35 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22083100050 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 95 | 2022-08-31 | 9500 | keep | 0 | Aug | 2022 | 0.0064704 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-08-31 13:56 | 2022-08-31 20:19 | 15 | 6:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y SE REGULO VOLTAGE EN XMR | B22083100239 | New_Event | Secondary Wire Break | Include | Include | Equipment | 383 | 2022-08-31 | 5745 | keep | 0 | Aug | 2022 | 0.0039129 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-08-31 13:57 | 2022-08-31 14:33 | 15 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BARRA SECUNDARIA | B22083100222 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2022-08-31 | 540 | keep | 0 | Aug | 2022 | 0.00036779 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-08-31 14:01 | 2022-08-31 16:57 | 1085 | 2:56 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE SECCIONALIZO ABRIENDO PUENTES Y MACHETES | S22083100063 | New_Event | Primary Wire Break | Include | Include | Equipment | 176 | 2022-08-31 | 190960 | keep | 0 | Aug | 2022 | 0.13006 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
SAN JUAN | 2022-08-31 14:02 | 2022-08-31 14:05 | 1825 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1118-09 SE VERIFICO PERSONAL FUERA LLEVA EL 1118-08 | S22083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-31 | 5475 | keep | 0 | Aug | 2022 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-08-31 14:02 | 2022-08-31 14:05 | 4398 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE VERIFICO PERSONAL FUERA LLEVA EL 1118-08 | S22083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-31 | 13194 | keep | 0 | Aug | 2022 | 0.0089864 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
PONCE | 2022-08-31 14:05 | 2022-08-31 14:06 | 732 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | P22083100131 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-08-31 | 732 | keep | 0 | Aug | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
PONCE | 2022-08-31 14:06 | 2022-08-31 18:03 | 80 | 3:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P22083100140 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 237 | 2022-08-31 | 18960 | keep | 0 | Aug | 2022 | 0.012914 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-08-31 14:10 | 2022-09-01 01:00 | 70 | 10:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22083100262 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 650 | 2022-08-31 | 45500 | keep | 0 | Aug | 2022 | 0.03099 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-08-31 14:14 | 2022-08-31 16:15 | 250 | 2:01 | P | DESGANCHE | 1 X 50 Y 2 X 80 EN CORTE DE LINEA SE REFIRIO PARA DESGANCHAR EL AREA. SE REQUIERE DESGANCHE MASIVO | M22083100265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-08-31 | 30250 | keep | 0 | Aug | 2022 | 0.020603 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-08-31 14:16 | 2022-08-31 18:22 | 12 | 4:06 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO | B22083000059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 246 | 2022-08-31 | 2952 | keep | 0 | Aug | 2022 | 0.0020106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-08-31 14:21 | 2022-08-31 18:52 | 65 | 4:31 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P22083100150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2022-08-31 | 17615 | keep | 0 | Aug | 2022 | 0.011997 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2022-08-31 14:23 | 2022-08-31 22:10 | 40 | 7:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22083100281 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2022-08-31 | 18680 | keep | 0 | Aug | 2022 | 0.012723 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-08-31 14:31 | 2022-08-31 15:29 | 18 | 0:58 | P | DESGANCHE | SE ABRIO C/L PARA REALIZAR DESGANCHE DE EMERGENCIA ESTABA QUEMANDO | S22083100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-08-31 | 1044 | keep | 0 | Aug | 2022 | 0.00071106 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2022-08-31 14:37 | 2022-08-31 16:40 | 1 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE AVERIADO | A22083100055 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2022-08-31 | 123 | keep | 0 | Aug | 2022 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-08-31 14:41 | 2022-08-31 15:40 | 78 | 0:59 | P | ANIMAL | 1 X 30 EN C/L AVE | B22083100233 | New_Event | Animals | Include | Include | Wildlife | 59 | 2022-08-31 | 4602 | keep | 0 | Aug | 2022 | 0.0031344 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
SAN JUAN | 2022-08-31 14:49 | 2022-08-31 17:25 | 3 | 2:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTOR SECUNDARIO | S22083100107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 156 | 2022-08-31 | 468 | keep | 0 | Aug | 2022 | 0.00031875 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-08-31 14:56 | 2022-08-31 19:03 | 30 | 4:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22083100313 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2022-08-31 | 7410 | keep | 0 | Aug | 2022 | 0.0050469 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-08-31 14:57 | 2022-09-01 14:45 | 50 | 23:48 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22083100316 | New_Event | Primary Wire Break | Include | Include | Equipment | 1428 | 2022-08-31 | 71400 | keep | 0 | Aug | 2022 | 0.04863 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-08-31 15:01 | 2022-08-31 15:04 | 1017 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | M22083100321 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-08-31 | 3051 | keep | 0 | Aug | 2022 | 0.002078 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-08-31 15:04 | 2022-08-31 16:29 | 1 | 1:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M22083100144 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 85 | 2022-08-31 | 85 | keep | 0 | Aug | 2022 | 5.7893e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-08-31 15:17 | 2022-08-31 17:02 | 80 | 1:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REFIRIO PARA ATENDER DESGANCHE MASIVO | M22083100336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-08-31 | 8400 | keep | 0 | Aug | 2022 | 0.0057212 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-08-31 15:17 | 2022-08-31 16:40 | 8 | 1:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 25KVA X 37.5KVA | A22083100057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 83 | 2022-08-31 | 664 | keep | 0 | Aug | 2022 | 0.00045225 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-08-31 15:19 | 2022-08-31 16:31 | 40 | 1:12 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | B22083100249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-08-31 | 2880 | keep | 0 | Aug | 2022 | 0.0019616 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-31 15:29 | 2022-08-31 21:15 | 75 | 5:46 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN RISER 1 X 15 EN XMR Y EL T-11 FUERA 25 CLIENTES | P22083100207 | New_Event | Service Transformer Failure | Include | Include | Equipment | 346 | 2022-08-31 | 25950 | keep | 0 | Aug | 2022 | 0.017674 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-08-31 15:31 | 2022-08-31 19:32 | 20 | 4:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22083100126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 241 | 2022-08-31 | 4820 | keep | 0 | Aug | 2022 | 0.0032829 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-08-31 15:36 | 2022-08-31 16:46 | 2 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO BANCO DE XMRS PARA REPARAR BAJANTE SECUNDARIO | C22083100076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-08-31 | 140 | keep | 0 | Aug | 2022 | 9.5353e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-08-31 15:53 | 2022-08-31 16:38 | 6 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S22083100133 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2022-08-31 | 270 | keep | 0 | Aug | 2022 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2022-08-31 16:29 | 2022-08-31 18:03 | 85 | 1:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22083100398 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2022-08-31 | 7990 | keep | 0 | Aug | 2022 | 0.005442 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2022-08-31 16:46 | 2022-08-31 21:16 | 45 | 4:30 | P | DESGANCHE | 1 X 80 EN C/L | C22083100090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-08-31 | 12150 | keep | 0 | Aug | 2022 | 0.0082753 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-08-31 16:48 | 2022-08-31 17:52 | 4 | 1:04 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE SECUNDARIO | B22083000028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 64 | 2022-08-31 | 256 | keep | 0 | Aug | 2022 | 0.00017436 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-08-31 16:50 | 2022-08-31 18:35 | 70 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SECCIONALIZO LINEA PRIMARIA ROTA ABRIENDO PUENTES PARA REFERIR Y TRABAJAR | M22083100316 | New_Event | Primary Wire Break | Include | Include | Equipment | 105 | 2022-08-31 | 7350 | keep | 0 | Aug | 2022 | 0.0050061 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-08-31 16:55 | 2022-08-31 18:30 | 10 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA ROTA | M22083100231 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2022-08-31 | 950 | keep | 0 | Aug | 2022 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-08-31 16:57 | 2022-08-31 19:09 | 217 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | S22083100063 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 132 | 2022-08-31 | 28644 | keep | 0 | Aug | 2022 | 0.019509 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-08-31 16:57 | 2022-09-01 03:00 | 120 | 10:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22083100415 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 603 | 2022-08-31 | 72360 | keep | 0 | Aug | 2022 | 0.049284 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-08-31 16:57 | 2022-08-31 22:12 | 75 | 5:15 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22083100415 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 315 | 2022-08-31 | 23625 | keep | 0 | Aug | 2022 | 0.016091 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-08-31 17:06 | 2022-08-31 20:28 | 60 | 3:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22083100425 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 202 | 2022-08-31 | 12120 | keep | 0 | Aug | 2022 | 0.0082549 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-08-31 17:12 | 2022-08-31 17:13 | 2446 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22083100257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 2446 | keep | 0 | Aug | 2022 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2022-08-31 17:22 | 2022-08-31 22:24 | 35 | 5:02 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | P22083100259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-08-31 | 10570 | keep | 0 | Aug | 2022 | 0.0071992 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-08-31 17:30 | 2022-08-31 23:30 | 800 | 6:00 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE ABRE CORTE DE LINEA EN FID: 23632143 PARA SECCIONALIZAR Y REPARAR LINEA PRIMARIA ROTA | M22083100020 | New_Event | Primary Wire Break | Include | Include | Equipment | 360 | 2022-08-31 | 288000 | keep | 0 | Aug | 2022 | 0.19616 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
MAYAGÃœEZ | 2022-08-31 17:30 | 2022-09-01 18:40 | 6 | 25:10 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE MASIVO Y SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M22083100448 | New_Event | Primary Wire Break | Include | Include | Equipment | 1510 | 2022-08-31 | 9060 | keep | 0 | Aug | 2022 | 0.0061707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-08-31 17:44 | 2022-08-31 18:36 | 1 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B22083100264 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-08-31 | 52 | keep | 0 | Aug | 2022 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-08-31 18:07 | 2022-08-31 22:10 | 225 | 4:03 | P | CONDUCTOR ROTO O ABIERTO | 3 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A22083100068 | New_Event | Primary Wire Break | Include | Include | Equipment | 243 | 2022-08-31 | 54675 | keep | 0 | Aug | 2022 | 0.037239 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
MAYAGÃœEZ | 2022-08-31 18:15 | 2022-08-31 18:34 | 1800 | 0:19 | P | MAL TIEMPO/RAYOS | SE CERRO RECLOSER DE DISTRIBUCION MAL TIEMPO DESCARGAS ELECTRICAS | M22083100523 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 19 | 2022-08-31 | 34200 | keep | 0 | Aug | 2022 | 0.023293 | 0.001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 1800
ARECIBO | 2022-08-31 18:26 | 2022-08-31 20:13 | 100 | 1:47 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22083100070 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 107 | 2022-08-31 | 10700 | keep | 0 | Aug | 2022 | 0.0072877 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-08-31 18:32 | 2022-08-31 19:43 | 4 | 1:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO PORTA FUSIBLE | M22083100536 | New_Event | Cutout Failure | Include | Include | Equipment | 71 | 2022-08-31 | 284 | keep | 0 | Aug | 2022 | 0.00019343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2022-08-31 18:44 | 2022-08-31 18:45 | 3896 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22083100093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 3896 | keep | 0 | Aug | 2022 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
BAYAMON | 2022-08-31 18:55 | 2022-08-31 18:56 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B22083100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1859 | keep | 0 | Aug | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2022-08-31 19:02 | 2022-08-31 20:43 | 13 | 1:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22083100271 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-08-31 | 1313 | keep | 0 | Aug | 2022 | 0.00089428 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2022-08-31 19:08 | 2022-09-01 09:30 | 1 | 14:22 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO Y SE REPARO LINEAS CRUZADAS | M22083100566 | New_Event | Vegetation Contact | Include | Include | Vegetation | 862 | 2022-08-31 | 862 | keep | 0 | Aug | 2022 | 0.0005871 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-08-31 19:09 | 2022-08-31 19:42 | 1085 | 0:33 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR PARA CERRAR PUENTES ABIERTOS Y CERRAR MACHETES DEL AREA SECCIONALIZADA | S22083100063 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 33 | 2022-08-31 | 35805 | keep | 0 | Aug | 2022 | 0.024387 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-08-31 20:00 | 2022-09-01 00:10 | 5 | 4:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M22083100597 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 250 | 2022-08-31 | 1250 | keep | 0 | Aug | 2022 | 0.00085137 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-08-31 20:01 | 2022-09-01 10:24 | 25 | 14:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR VIENTO | A22083100086 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 863 | 2022-08-31 | 21575 | keep | 0 | Aug | 2022 | 0.014695 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-08-31 20:26 | 2022-08-31 21:41 | 100 | 1:15 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | A22083100091 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-08-31 | 7500 | keep | 0 | Aug | 2022 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-08-31 20:38 | 2022-09-01 06:49 | 4 | 10:11 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P22083100331 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 611 | 2022-08-31 | 2444 | keep | 0 | Aug | 2022 | 0.0016646 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-08-31 20:38 | 2022-09-01 14:00 | 8 | 17:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A22083100094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1042 | 2022-08-31 | 8336 | keep | 0 | Aug | 2022 | 0.0056776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-08-31 20:43 | 2022-09-01 00:58 | 1 | 4:15 | P | NO SE REPORTO CAUSA | 1 X 10 EN RISER NO SE IDENTIFICO CAUSA | M22083100621 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2022-08-31 | 255 | keep | 0 | Aug | 2022 | 0.00017368 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-08-31 20:51 | 2022-09-01 08:26 | 4 | 11:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZA CAJA PRIMARIA QUEMADA 2 X 15 EN TRANSFORMADOR | A22083100097 | New_Event | Cutout Failure | Include | Include | Equipment | 695 | 2022-08-31 | 2780 | keep | 0 | Aug | 2022 | 0.0018934 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-08-31 20:53 | 2022-08-31 23:13 | 50 | 2:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P22083100336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-08-31 | 7000 | keep | 0 | Aug | 2022 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-08-31 20:55 | 2022-09-01 06:45 | 50 | 9:50 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22083100629 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 590 | 2022-08-31 | 29500 | keep | 0 | Aug | 2022 | 0.020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-08-31 20:58 | 2022-08-31 22:48 | 8 | 1:50 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R22083100053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2022-08-31 | 880 | keep | 0 | Aug | 2022 | 0.00059936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-08-31 21:03 | 2022-09-01 07:10 | 40 | 10:07 | P | CONDUCTOR ROTO O ABIERTO | FIJO BAJANTE DE LINEA A CAJA NO FUNDIO | C22083100121 | New_Event | Primary Wire Break | Include | Include | Equipment | 607 | 2022-08-31 | 24280 | keep | 0 | Aug | 2022 | 0.016537 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-08-31 21:15 | 2022-09-01 09:05 | 15 | 11:50 | P | TRANSFORMADOR AVERIADO | 1 X 25 EN TRANSFORMADOR REMPLAZO XMER DE 75 KVA A 7620V | P22083100207 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 710 | 2022-08-31 | 10650 | keep | 0 | Aug | 2022 | 0.0072537 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-08-31 21:30 | 2022-08-31 23:24 | 10 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | A22083100101 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2022-08-31 | 1140 | keep | 0 | Aug | 2022 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-08-31 21:51 | 2022-08-31 22:10 | 9 | 0:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR VARIOS CONECTORES | R22083100052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 19 | 2022-08-31 | 171 | keep | 0 | Aug | 2022 | 0.00011647 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2022-08-31 22:07 | 2022-08-31 22:08 | 200 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-03 LLEVANDO PARTE 9201-01 Y 17% DE SU CARGA POR 9202-02 | B22083100278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 200 | keep | 0 | Aug | 2022 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-08-31 22:07 | 2022-08-31 22:08 | 1160 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-03 LLEVANDO PARTE 9201-01 Y 17% DE SU CARGA POR 9202-02 | B22083100278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 1160 | keep | 0 | Aug | 2022 | 0.00079007 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
CAGUAS | 2022-08-31 22:10 | 2022-09-01 07:45 | 80 | 9:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REEMPLAZO CAJA QUEMADA | C22083100123 | New_Event | Cutout Failure | Include | Include | Equipment | 575 | 2022-08-31 | 46000 | keep | 0 | Aug | 2022 | 0.03133 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-08-31 22:22 | 2022-09-01 08:00 | 3 | 9:38 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22083100662 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 578 | 2022-08-31 | 1734 | keep | 0 | Aug | 2022 | 0.001181 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-08-31 22:44 | 2022-08-31 22:45 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22083100347 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 3744 | keep | 0 | Aug | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
FAJARDO | 2022-08-31 23:40 | 2022-09-01 08:35 | 62 | 8:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R22083100057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 535 | 2022-08-31 | 33170 | keep | 0 | Aug | 2022 | 0.022592 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BARRANQUITAS | 2022-08-31 23:51 | 2022-08-31 23:52 | 327 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22083100130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-08-31 | 327 | keep | 0 | Aug | 2022 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
VEGA BAJA | 2022-09-01 00:12 | 2022-09-01 01:45 | 75 | 1:33 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA PARARRAYO DEFECTUOSO | P22090100002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 93 | 2022-09-01 | 6975 | keep | 0 | Sep | 2022 | 0.0047506 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-09-01 01:06 | 2022-09-01 01:07 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 3332 | keep | 0 | Sep | 2022 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
BARRANQUITAS | 2022-09-01 01:21 | 2022-09-01 08:29 | 45 | 7:08 | P | DESGANCHE | 1 X 50 EN C/L | C22090100004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 428 | 2022-09-01 | 19260 | keep | 0 | Sep | 2022 | 0.013118 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-09-01 02:07 | 2022-09-01 11:30 | 60 | 9:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA EN CAJA PRIMARIA | A22090100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 563 | 2022-09-01 | 33780 | keep | 0 | Sep | 2022 | 0.023007 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-01 03:03 | 2022-09-01 10:31 | 25 | 7:28 | P | DESGANCHE | 1X65 EN C/L | S22090100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2022-09-01 | 11200 | keep | 0 | Sep | 2022 | 0.0076283 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-09-01 03:08 | 2022-09-01 10:08 | 150 | 7:00 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR IGUANA | A22090100007 | New_Event | Animals | Include | Include | Wildlife | 420 | 2022-09-01 | 63000 | keep | 0 | Sep | 2022 | 0.042909 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-09-01 03:24 | 2022-09-01 06:25 | 1827 | 3:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES Y SE CERRO EL INTERRUPTOR SE CONTINUA PATRULLANDO | M22090100002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 181 | 2022-09-01 | 330687 | keep | 0 | Sep | 2022 | 0.22523 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2022-09-01 03:35 | 2022-09-01 03:36 | 640 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO ESTA RECERRANDO CERRADO POR CONTROL | C22090100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 640 | keep | 0 | Sep | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-09-01 03:47 | 2022-09-01 03:50 | 225 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 | S22090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-01 | 675 | keep | 0 | Sep | 2022 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-09-01 03:47 | 2022-09-01 03:50 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1303-05 LLEVANDO CARGA 1303-04 | S22090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-01 | 2610 | keep | 0 | Sep | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
AGUADILLA | 2022-09-01 03:58 | 2022-09-01 16:34 | 120 | 12:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO Y SE REPARO NEUTRAL PRIMARIO | M22090100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 756 | 2022-09-01 | 90720 | keep | 0 | Sep | 2022 | 0.061789 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-09-01 04:14 | 2022-09-01 04:15 | 5961 | 0:01 | T | DESGANCHE | RECIERRE 1713-05 LLEVANDO 95% 1717-02 | B22090100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-01 | 5961 | keep | 0 | Sep | 2022 | 0.00406 | 0.00406 | Momentary | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-09-01 04:14 | 2022-09-01 04:15 | 865 | 0:01 | P | DESGANCHE | RECIERRE 1713-05 LLEVANDO 95% 1717-02 | B22090100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-01 | 865 | keep | 0 | Sep | 2022 | 0.00058915 | 0.00058915 | Momentary | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2022-09-01 04:15 | 2022-09-01 10:40 | 50 | 6:25 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | B22090100006 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 385 | 2022-09-01 | 19250 | keep | 0 | Sep | 2022 | 0.013111 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-09-01 04:45 | 2022-09-01 09:54 | 1 | 5:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARARON CONEXIONES EN LINEA SECUNDARIA | P22090100019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 309 | 2022-09-01 | 309 | keep | 0 | Sep | 2022 | 0.00021046 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-09-01 05:01 | 2022-09-01 17:50 | 12 | 12:49 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22090100018 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 769 | 2022-09-01 | 9228 | keep | 0 | Sep | 2022 | 0.0062851 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-09-01 06:00 | 2022-09-01 10:41 | 19 | 4:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO PORTAFUSIBLE | R22090100055 | New_Event | Cutout Failure | Include | Include | Equipment | 281 | 2022-09-01 | 5339 | keep | 0 | Sep | 2022 | 0.0036364 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BARRANQUITAS | 2022-09-01 06:04 | 2022-09-01 09:48 | 20 | 3:44 | P | DESGANCHE | 1 X 40 EN C/L | C22090100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-09-01 | 4480 | keep | 0 | Sep | 2022 | 0.0030513 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-01 06:13 | 2022-09-01 11:06 | 12 | 4:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR SE REPARO BAJANTE SECUNDARIO | S22090100013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 293 | 2022-09-01 | 3516 | keep | 0 | Sep | 2022 | 0.0023947 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-09-01 06:23 | 2022-09-01 06:24 | 2281 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090100018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 2281 | keep | 0 | Sep | 2022 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
AGUADILLA | 2022-09-01 06:25 | 2022-09-01 08:47 | 1110 | 2:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR AL CERRAR MACHETES | M22090100033 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 142 | 2022-09-01 | 157620 | keep | 0 | Sep | 2022 | 0.10735 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-09-01 06:31 | 2022-09-01 09:55 | 80 | 3:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R22090100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-09-01 | 16320 | keep | 0 | Sep | 2022 | 0.011115 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 1253 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 3759 | keep | 0 | Sep | 2022 | 0.0025602 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 1266 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 3798 | keep | 0 | Sep | 2022 | 0.0025868 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 411 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 1233 | keep | 0 | Sep | 2022 | 0.00083979 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2022-09-01 06:39 | 2022-09-01 06:42 | 1617 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 4851 | keep | 0 | Sep | 2022 | 0.003304 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-09-01 06:39 | 2022-09-01 06:42 | 1017 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 3051 | keep | 0 | Sep | 2022 | 0.002078 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-09-01 06:39 | 2022-09-01 06:42 | 828 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 2484 | keep | 0 | Sep | 2022 | 0.0016918 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 863 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 2589 | keep | 0 | Sep | 2022 | 0.0017634 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 309 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 927 | keep | 0 | Sep | 2022 | 0.00063138 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 176 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100037 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 528 | keep | 0 | Sep | 2022 | 0.00035962 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 108 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 324 | keep | 0 | Sep | 2022 | 0.00022067 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-09-01 06:39 | 2022-09-01 06:42 | 974 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2000 | M22090100039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-01 | 2922 | keep | 0 | Sep | 2022 | 0.0019902 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
MAYAGÃœEZ | 2022-09-01 06:42 | 2022-09-01 17:41 | 1 | 10:59 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M22083100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 659 | 2022-09-01 | 659 | keep | 0 | Sep | 2022 | 0.00044884 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-09-01 06:43 | 2022-09-01 09:00 | 62 | 2:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REEMPLAZO CAJA QUEMADA | C22090100021 | New_Event | Cutout Failure | Include | Include | Equipment | 137 | 2022-09-01 | 8494 | keep | 0 | Sep | 2022 | 0.0057852 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
GUAYAMA | 2022-09-01 06:48 | 2022-09-01 06:49 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 3718 | keep | 0 | Sep | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-09-01 06:49 | 2022-09-01 10:02 | 159 | 3:13 | P | ANIMAL | 1 X 30 Y 1 X 65 EN C/L AVE | B22090100015 | New_Event | Animals | Include | Include | Wildlife | 193 | 2022-09-01 | 30687 | keep | 0 | Sep | 2022 | 0.020901 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
GUAYAMA | 2022-09-01 06:50 | 2022-09-01 11:45 | 4 | 4:55 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P22083100331 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 295 | 2022-09-01 | 1180 | keep | 0 | Sep | 2022 | 0.00080369 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-01 06:59 | 2022-09-01 16:35 | 3 | 9:36 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR / DESCARGAS ELECTRICAS | M22090100041 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 576 | 2022-09-01 | 1728 | keep | 0 | Sep | 2022 | 0.0011769 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2022-09-01 07:15 | 2022-09-01 10:45 | 80 | 3:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M22090100049 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2022-09-01 | 16800 | keep | 0 | Sep | 2022 | 0.011442 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-09-01 07:20 | 2022-09-01 11:40 | 70 | 4:20 | P | SECUNDARIA/DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22090100051 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 260 | 2022-09-01 | 18200 | keep | 0 | Sep | 2022 | 0.012396 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-09-01 07:23 | 2022-09-01 19:33 | 120 | 12:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22090100054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 730 | 2022-09-01 | 87600 | keep | 0 | Sep | 2022 | 0.059664 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2022-09-01 07:34 | 2022-09-01 07:35 | 3833 | 0:01 | T | ANIMAL | RECIERRE | C22090100025 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-01 | 3833 | keep | 0 | Sep | 2022 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2022-09-01 07:35 | 2022-09-01 13:26 | 49 | 5:51 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C22090100027 | 1st_after_momentary | Animals | Include | Include | Wildlife | 351 | 2022-09-01 | 17199 | keep | 0 | Sep | 2022 | 0.011714 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
HUMACAO | 2022-09-01 07:37 | 2022-09-01 15:29 | 19 | 7:52 | P | CABLE SOTERRADO AVERIADO | 1 X 25 RBA EN SU - 3 SE ENERGIZO CABLE NUEVO PREVIAMENTE REGADO DEL SU - 3 AL T - 5 Y SE ELIMINO TRAMO AVERIADO | C22090100080 | New_Event | UG Cable Fault | Include | Include | Equipment | 472 | 2022-09-01 | 8968 | keep | 0 | Sep | 2022 | 0.0061081 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2022-09-01 07:39 | 2022-09-01 09:23 | 10 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARO A TRANSFORMADOR | P22090100039 | New_Event | Primary Wire Break | Include | Include | Equipment | 104 | 2022-09-01 | 1040 | keep | 0 | Sep | 2022 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-01 07:39 | 2022-09-01 13:06 | 15 | 5:27 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE RETIRO TRES ARBOLES CAIDOS SOBRE LAS LINEAS , SE SEPARO LINEAS PRIMARIAS CRUZADAS Y SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR Y SE REMPLAZAO LINEA SECUNDARIA AVERIADA | M22090100061 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 327 | 2022-09-01 | 4905 | keep | 0 | Sep | 2022 | 0.0033408 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-09-01 07:46 | 2022-09-01 11:30 | 9 | 3:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA EN MONTURA DE TRANSFORMADOR | A22090100013 | New_Event | Cutout Failure | Include | Include | Equipment | 224 | 2022-09-01 | 2016 | keep | 0 | Sep | 2022 | 0.0013731 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-09-01 07:49 | 2022-09-01 10:30 | 1 | 2:41 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22090100066 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 161 | 2022-09-01 | 161 | keep | 0 | Sep | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-01 07:51 | 2022-09-01 10:46 | 164 | 2:55 | P | ANIMAL | 1 X 140 Y 1 X 30 EN CORTE DE LINEA PALOMA CRUZO FASE | R22090100008 | New_Event | Animals | Include | Include | Wildlife | 175 | 2022-09-01 | 28700 | keep | 0 | Sep | 2022 | 0.019547 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
CAGUAS | 2022-09-01 08:02 | 2022-09-01 08:03 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 1702 | keep | 0 | Sep | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
GUAYAMA | 2022-09-01 08:02 | 2022-09-01 10:55 | 45 | 2:53 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETIRO PARTE DE POSTE QUE SE CRUZABA CON LINEA PRIMARIA | P22090100008 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 173 | 2022-09-01 | 7785 | keep | 0 | Sep | 2022 | 0.0053023 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-09-01 08:04 | 2022-09-01 09:25 | 35 | 1:21 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R22090100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-09-01 | 2835 | keep | 0 | Sep | 2022 | 0.0019309 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-09-01 08:08 | 2022-09-01 11:25 | 1 | 3:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-09-01 | 197 | keep | 0 | Sep | 2022 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-09-01 08:10 | 2022-09-01 08:12 | 1185 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE LE REALIZO PRUEBA Y SE QUEDO EN SERVICIO | A22090100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 2370 | keep | 0 | Sep | 2022 | 0.0016142 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
PONCE | 2022-09-01 08:13 | 2022-09-01 10:10 | 1 | 1:57 | P | DESGANCHE | 2 X 100 EN RISER SE RETIRO ENREDADERA EN RISER | P22090100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-09-01 | 117 | keep | 0 | Sep | 2022 | 7.9688e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-09-01 08:26 | 2022-09-01 12:20 | 10 | 3:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22090100084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 234 | 2022-09-01 | 2340 | keep | 0 | Sep | 2022 | 0.0015938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-01 08:40 | 2022-09-01 12:00 | 30 | 3:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22090100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2022-09-01 | 6000 | keep | 0 | Sep | 2022 | 0.0040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-09-01 08:47 | 2022-09-01 08:51 | 1827 | 0:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE VOLVIO A ABRIR MACHETES Y SE CERRO EL INTERRUPTOR | M22090100002 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2022-09-01 | 7308 | keep | 0 | Sep | 2022 | 0.0049774 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-01 08:51 | 2022-09-01 09:43 | 1110 | 0:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PRIMARIO ROTO Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR | M22090100033 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2022-09-01 | 57720 | keep | 0 | Sep | 2022 | 0.039313 | 0.00075602 | Sustained | FALSE | FALSE | Not_TMED_Event | 1110
AGUADILLA | 2022-09-01 08:57 | 2022-09-01 16:00 | 8 | 7:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22090100101 | New_Event | Primary Wire Break | Include | Include | Equipment | 423 | 2022-09-01 | 3384 | keep | 0 | Sep | 2022 | 0.0023048 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-09-01 09:02 | 2022-09-01 14:48 | 10 | 5:46 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C22090100051 | New_Event | Animals | Include | Include | Wildlife | 346 | 2022-09-01 | 3460 | keep | 0 | Sep | 2022 | 0.0023566 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-09-01 09:05 | 2022-09-01 15:11 | 12 | 6:06 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 75 KVA 7620 VOLT AVERIADO | P22090100058 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 366 | 2022-09-01 | 4392 | keep | 0 | Sep | 2022 | 0.0029914 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-09-01 09:10 | 2022-09-01 13:23 | 7 | 4:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | P22090100056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 253 | 2022-09-01 | 1771 | keep | 0 | Sep | 2022 | 0.0012062 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2022-09-01 09:16 | 2022-09-01 13:32 | 20 | 4:16 | P | NO SE REPORTO CAUSA | CARR. 4474, KM. 3.5 | A22090100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 256 | 2022-09-01 | 5120 | keep | 0 | Sep | 2022 | 0.0034872 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-09-01 09:19 | 2022-09-01 12:04 | 60 | 2:45 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR PAJARO | A22090100021 | New_Event | Animals | Include | Include | Wildlife | 165 | 2022-09-01 | 9900 | keep | 0 | Sep | 2022 | 0.0067428 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-09-01 09:23 | 2022-09-01 14:22 | 15 | 4:59 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22090100111 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 299 | 2022-09-01 | 4485 | keep | 0 | Sep | 2022 | 0.0030547 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-09-01 09:23 | 2022-09-01 12:08 | 30 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REEMPLAZAN CONEXIONES SECUNDARIAS | A22090100024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2022-09-01 | 4950 | keep | 0 | Sep | 2022 | 0.0033714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-01 09:25 | 2022-09-01 09:26 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R22090100035 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 4188 | keep | 0 | Sep | 2022 | 0.0028524 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-01 09:26 | 2022-09-01 14:37 | 35 | 5:11 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA | R22090100017 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 311 | 2022-09-01 | 10885 | keep | 0 | Sep | 2022 | 0.0074137 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-09-01 09:28 | 2022-09-01 12:00 | 8 | 2:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN XMR (TRASPATIO) | S22090100027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 152 | 2022-09-01 | 1216 | keep | 0 | Sep | 2022 | 0.00082821 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-01 09:44 | 2022-09-01 13:33 | 200 | 3:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE PRIMARIO | R22090100037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2022-09-01 | 45800 | keep | 0 | Sep | 2022 | 0.031194 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-09-01 09:45 | 2022-09-01 12:01 | 50 | 2:16 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R22090100038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2022-09-01 | 6800 | keep | 0 | Sep | 2022 | 0.0046314 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-09-01 09:45 | 2022-09-01 12:00 | 1 | 2:15 | P | NO SE REPORTO CAUSA | 1 X 5 EN BANCO DE XMRS | C22090100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2022-09-01 | 135 | keep | 0 | Sep | 2022 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-09-01 09:52 | 2022-09-01 15:20 | 150 | 5:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | A22090100025 | New_Event | Primary Wire Break | Include | Include | Equipment | 328 | 2022-09-01 | 49200 | keep | 0 | Sep | 2022 | 0.03351 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2022-09-01 09:57 | 2022-09-01 12:40 | 2 | 2:43 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22090100124 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 163 | 2022-09-01 | 326 | keep | 0 | Sep | 2022 | 0.00022204 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-09-01 10:00 | 2022-09-01 13:37 | 21 | 3:37 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | ABRIO CAJA DE XMR PARA REEMPLAZAR POSTE SECUNDARIO | C22090100059 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 217 | 2022-09-01 | 4557 | keep | 0 | Sep | 2022 | 0.0031038 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BARRANQUITAS | 2022-09-01 10:20 | 2022-09-01 16:29 | 13 | 6:09 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | ABRIO C/L PARA REEMPLAZAR POSTE PRIMARIO PARTIDO | C22090100062 | New_Event | Primary Pole Failure | Include | Include | Equipment | 369 | 2022-09-01 | 4797 | keep | 0 | Sep | 2022 | 0.0032672 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2022-09-01 10:25 | 2022-09-01 13:00 | 1 | 2:35 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 25 EN C/L SE LIGO CONDUCTOR A AISLADOR | B22090100040 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 155 | 2022-09-01 | 155 | keep | 0 | Sep | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-09-01 10:32 | 2022-09-01 10:34 | 860 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | P22090100069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 1720 | keep | 0 | Sep | 2022 | 0.0011715 | 0.00058574 | Momentary | FALSE | FALSE | Not_TMED_Event | 860
AGUADILLA | 2022-09-01 10:36 | 2022-09-01 10:50 | 80 | 0:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-09-01 | 1120 | keep | 0 | Sep | 2022 | 0.00076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-01 10:40 | 2022-09-01 11:50 | 10 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BARRAS EN PEDESTAL | S22083100037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-09-01 | 700 | keep | 0 | Sep | 2022 | 0.00047677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-01 10:42 | 2022-09-01 12:40 | 15 | 1:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO PORTAFUSIBLE EVENTO TRANSFERIDO DE PONCE | P22090100071 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2022-09-01 | 1770 | keep | 0 | Sep | 2022 | 0.0012055 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-09-01 11:00 | 2022-09-01 21:20 | 1 | 10:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN RISER MAL TIEMPO LLUVIAS | P22090100074 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 620 | 2022-09-01 | 620 | keep | 0 | Sep | 2022 | 0.00042228 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-01 11:25 | 2022-09-01 11:26 | 2216 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22090100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 2216 | keep | 0 | Sep | 2022 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
BARRANQUITAS | 2022-09-01 11:25 | 2022-09-01 12:02 | 50 | 0:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22090100075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-09-01 | 1850 | keep | 0 | Sep | 2022 | 0.00126 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-09-01 11:26 | 2022-09-01 13:05 | 40 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B22090100051 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-09-01 | 3960 | keep | 0 | Sep | 2022 | 0.0026971 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-09-01 11:31 | 2022-09-01 15:46 | 1 | 4:15 | P | NO SE REPORTO CAUSA | 2 X 20 EN TRANSFIORMADOR NO SE ENCONTRO CAUSA | M22090100145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2022-09-01 | 255 | keep | 0 | Sep | 2022 | 0.00017368 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-01 11:36 | 2022-09-01 12:40 | 15 | 1:04 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22090100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 64 | 2022-09-01 | 960 | keep | 0 | Sep | 2022 | 0.00065385 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-01 11:37 | 2022-09-01 19:01 | 200 | 7:24 | P | NO SE REPORTO CAUSA | 1 X 80 DE RISER, 1 X 65 Y 1 X 80 EN SU | B22090100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 444 | 2022-09-01 | 88800 | keep | 0 | Sep | 2022 | 0.060481 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-09-01 11:40 | 2022-09-01 12:30 | 10 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22083100187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-09-01 | 500 | keep | 0 | Sep | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-09-01 11:44 | 2022-09-02 09:00 | 2 | 21:16 | P | OTRAS CAUSAS | 1 X 100 EN CORTE DE LINEA FUSIBLE CON PUNTO CALIENTE | P22090200089 | New_Event | Other Causes | Include | Include | Other | 1276 | 2022-09-01 | 2552 | keep | 0 | Sep | 2022 | 0.0017382 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-09-01 11:44 | 2022-09-02 01:10 | 2 | 13:26 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | P22090100088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 806 | 2022-09-01 | 1612 | keep | 0 | Sep | 2022 | 0.0010979 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-09-01 11:46 | 2022-09-01 15:25 | 79 | 3:39 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C22090100077 | New_Event | Animals | Include | Include | Wildlife | 219 | 2022-09-01 | 17301 | keep | 0 | Sep | 2022 | 0.011784 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2022-09-01 12:10 | 2022-09-01 18:45 | 70 | 6:35 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO TRAMO ABRIENDO PUENTES Y SE REFIRIO A CONSTRUCCION PARA REEMPLAZAR POSTE PARTIDO TRAMO RADIAL | B22090100056 | New_Event | Primary Pole Failure | Include | Include | Equipment | 395 | 2022-09-01 | 27650 | keep | 0 | Sep | 2022 | 0.018832 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2022-09-01 12:16 | 2022-09-01 18:40 | 500 | 6:24 | P | CONDUCTOR ROTO O ABIERTO | 3 X 65 EN C/L LEVANTO CONDUCTOR | C22090100083 | New_Event | Primary Wire Break | Include | Include | Equipment | 384 | 2022-09-01 | 192000 | keep | 0 | Sep | 2022 | 0.13077 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2022-09-01 12:23 | 2022-09-01 14:23 | 959 | 2:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090100062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-09-01 | 115080 | keep | 0 | Sep | 2022 | 0.07838 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-09-01 12:23 | 2022-09-01 14:23 | 1382 | 2:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090100062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-09-01 | 165840 | keep | 0 | Sep | 2022 | 0.11295 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-09-01 12:23 | 2022-09-01 14:23 | 663 | 2:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090100062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-09-01 | 79560 | keep | 0 | Sep | 2022 | 0.054188 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-09-01 12:23 | 2022-09-01 14:23 | 1514 | 2:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090100060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-09-01 | 181680 | keep | 0 | Sep | 2022 | 0.12374 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-09-01 12:23 | 2022-09-01 14:23 | 1105 | 2:00 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090100060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 120 | 2022-09-01 | 132600 | keep | 0 | Sep | 2022 | 0.090313 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
PONCE | 2022-09-01 12:23 | 2022-09-01 17:42 | 10 | 5:19 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | P22090100099 | New_Event | Animals | Include | Include | Wildlife | 319 | 2022-09-01 | 3190 | keep | 0 | Sep | 2022 | 0.0021727 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-01 12:31 | 2022-09-01 23:06 | 200 | 10:35 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO | S22090100033 | New_Event | Primary Pole Failure | Include | Include | Equipment | 635 | 2022-09-01 | 127000 | keep | 0 | Sep | 2022 | 0.086499 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-09-01 12:32 | 2022-09-01 15:07 | 6 | 2:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | R22090100068 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2022-09-01 | 930 | keep | 0 | Sep | 2022 | 0.00063342 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-09-01 12:38 | 2022-09-01 17:23 | 100 | 4:45 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L SE DESCRUZO FASE DE NEUTRAL | B22090100068 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 285 | 2022-09-01 | 28500 | keep | 0 | Sep | 2022 | 0.019411 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-01 12:40 | 2022-09-01 15:52 | 1 | 3:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN XMR FUERTES LLUVIAS | C22090100091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 192 | 2022-09-01 | 192 | keep | 0 | Sep | 2022 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-01 12:54 | 2022-09-01 12:56 | 1106 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1529-15 LLEVA 60% DE LA CARGA DEL 1346-02 | S22090100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 2212 | keep | 0 | Sep | 2022 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-09-01 12:54 | 2022-09-01 12:56 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1529-15 LLEVA 60% DE LA CARGA DEL 1346-02 | S22090100035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 3604 | keep | 0 | Sep | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
YAUCO | 2022-09-01 12:55 | 2022-09-01 14:03 | 100 | 1:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090100163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-09-01 | 6800 | keep | 0 | Sep | 2022 | 0.0046314 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-01 13:05 | 2022-09-01 14:40 | 15 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR ,SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR Y SE AJUSTO VOLTAJE SECUNDARIO EN TRANSFORMADOR | M22090100123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2022-09-01 | 1425 | keep | 0 | Sep | 2022 | 0.00097056 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-01 13:06 | 2022-09-01 13:07 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 320 | keep | 0 | Sep | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2022-09-01 13:19 | 2022-09-01 15:05 | 70 | 1:46 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S22090100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2022-09-01 | 7420 | keep | 0 | Sep | 2022 | 0.0050537 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-09-01 13:29 | 2022-09-01 13:31 | 2696 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | P22090100119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 5392 | keep | 0 | Sep | 2022 | 0.0036725 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
UTUADO | 2022-09-01 13:32 | 2022-09-01 17:27 | 40 | 3:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090100043 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 235 | 2022-09-01 | 9400 | keep | 0 | Sep | 2022 | 0.0064023 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-09-01 13:34 | 2022-09-01 18:58 | 65 | 5:24 | P | CABLE SOTERRADO AVERIADO | 1 SMU 20 DE 40A EN SU-1 Y 1 X 10 EN XMR, AVERIA DEL T-5 @ T-6, CERRO N/O EN SU-2 @ T-10 | C22090100101 | New_Event | UG Cable Fault | Include | Include | Equipment | 324 | 2022-09-01 | 21060 | keep | 0 | Sep | 2022 | 0.014344 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2022-09-01 13:37 | 2022-09-01 14:05 | 60 | 0:28 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | R22090100074 | New_Event | Animals | Include | Include | Wildlife | 28 | 2022-09-01 | 1680 | keep | 0 | Sep | 2022 | 0.0011442 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-01 13:38 | 2022-09-01 17:40 | 10 | 4:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22090100044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 242 | 2022-09-01 | 2420 | keep | 0 | Sep | 2022 | 0.0016483 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-09-01 13:40 | 2022-09-02 08:00 | 5 | 18:20 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P22090100123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1100 | 2022-09-01 | 5500 | keep | 0 | Sep | 2022 | 0.003746 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2022-09-01 13:42 | 2022-09-01 19:05 | 30 | 5:23 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22090100045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2022-09-01 | 9690 | keep | 0 | Sep | 2022 | 0.0065998 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-01 13:43 | 2022-09-01 15:28 | 1 | 1:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090100216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-09-01 | 105 | keep | 0 | Sep | 2022 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-09-01 13:44 | 2022-09-01 18:10 | 80 | 4:26 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22090100128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2022-09-01 | 21280 | keep | 0 | Sep | 2022 | 0.014494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-01 13:50 | 2022-09-01 17:04 | 8 | 3:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR SECUNDARIA | B22090100104 | New_Event | Secondary Wire Break | Include | Include | Equipment | 194 | 2022-09-01 | 1552 | keep | 0 | Sep | 2022 | 0.0010571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-01 13:56 | 2022-09-01 19:42 | 40 | 5:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22090100180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 346 | 2022-09-01 | 13840 | keep | 0 | Sep | 2022 | 0.0094264 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-09-01 13:57 | 2022-09-01 16:12 | 50 | 2:15 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22090100133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-09-01 | 6750 | keep | 0 | Sep | 2022 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-09-01 13:58 | 2022-09-01 17:35 | 80 | 3:37 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22090100134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-09-01 | 17360 | keep | 0 | Sep | 2022 | 0.011824 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2022-09-01 14:00 | 2022-09-01 19:10 | 300 | 5:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO PRIMARIO | P22090100138 | New_Event | Primary Wire Break | Include | Include | Equipment | 310 | 2022-09-01 | 93000 | keep | 0 | Sep | 2022 | 0.063342 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2022-09-01 14:01 | 2022-09-01 15:34 | 3458 | 1:33 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO MACHETES Y SE CERRO EL INTERRUPTOR | M22090100183 | New_Event | Switch Failure | Include | Include | Equipment | 93 | 2022-09-01 | 321594 | keep | 0 | Sep | 2022 | 0.21904 | 0.0023552 | Sustained | FALSE | FALSE | Not_TMED_Event | 3458
PONCE | 2022-09-01 14:08 | 2022-09-01 16:39 | 2113 | 2:31 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLASO AISLADORES | P22090100140 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2022-09-01 | 319063 | keep | 0 | Sep | 2022 | 0.21731 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2022-09-01 14:15 | 2022-09-01 14:16 | 79 | 0:01 | P | PARARRAYOS DEFECTUOSO | SE ABRE RISER PARA REEMPLAZO PARARRAYO Y AISLADOR | R22090100076 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-09-01 | 79 | keep | 0 | Sep | 2022 | 5.3807e-05 | 5.3807e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 79
MAYAGÃœEZ | 2022-09-01 14:15 | 2022-09-01 17:25 | 75 | 3:10 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22090100193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-09-01 | 14250 | keep | 0 | Sep | 2022 | 0.0097056 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2022-09-01 14:29 | 2022-09-01 16:00 | 100 | 1:31 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22090100154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-09-01 | 9100 | keep | 0 | Sep | 2022 | 0.006198 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-01 14:40 | 2022-09-01 17:30 | 20 | 2:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22090100125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 170 | 2022-09-01 | 3400 | keep | 0 | Sep | 2022 | 0.0023157 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-09-01 14:40 | 2022-09-01 14:51 | 934 | 0:11 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090100059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-09-01 | 10274 | keep | 0 | Sep | 2022 | 0.0069976 | 0.00063614 | Sustained | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-09-01 14:40 | 2022-09-01 14:51 | 4 | 0:11 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090100059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-09-01 | 44 | keep | 0 | Sep | 2022 | 2.9968e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-09-01 14:40 | 2022-09-01 14:51 | 1479 | 0:11 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090100059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-09-01 | 16269 | keep | 0 | Sep | 2022 | 0.011081 | 0.0010073 | Sustained | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-09-01 14:40 | 2022-09-01 14:51 | 1841 | 0:11 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090100061 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-09-01 | 20251 | keep | 0 | Sep | 2022 | 0.013793 | 0.0012539 | Sustained | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-09-01 14:40 | 2022-09-01 14:51 | 1950 | 0:11 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090100061 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 11 | 2022-09-01 | 21450 | keep | 0 | Sep | 2022 | 0.014609 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 888 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22090100223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 888 | keep | 0 | Sep | 2022 | 0.00060481 | 0.00060481 | Momentary | FALSE | FALSE | Not_TMED_Event | 888
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 393 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 CARGA ESTA POR 6007-05 | M22090100223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 393 | keep | 0 | Sep | 2022 | 0.00026767 | 0.00026767 | Momentary | FALSE | FALSE | Not_TMED_Event | 393
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 4 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 LLEVA CARGA DE 6007-04 | M22090100223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 4 | keep | 0 | Sep | 2022 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 372 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 CARGA ESTA POR 6008-03 QUE ES SPARE | M22090100226 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 372 | keep | 0 | Sep | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 2530 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22090100226 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 2530 | keep | 0 | Sep | 2022 | 0.0017232 | 0.0017232 | Momentary | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 199 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22090100226 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 199 | keep | 0 | Sep | 2022 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 312 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22090100227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 312 | keep | 0 | Sep | 2022 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2022-09-01 14:41 | 2022-09-01 14:42 | 4641 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1600 | M22090100227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-01 | 4641 | keep | 0 | Sep | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
BAYAMON | 2022-09-01 14:43 | 2022-09-01 15:43 | 1382 | 1:00 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE SECCIONALIZO ENTRO EN SERVICIO 100% 1706-02 Y 30% DEL 1706-03 | B22090100137 | New_Event | Primary Wire Break | Include | Include | Equipment | 60 | 2022-09-01 | 82920 | keep | 0 | Sep | 2022 | 0.056476 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-09-01 14:43 | 2022-09-01 15:43 | 663 | 1:00 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE SECCIONALIZO ENTRO EN SERVICIO 100% 1706-02 Y 30% DEL 1706-03 | B22090100137 | New_Event | Primary Wire Break | Include | Include | Equipment | 60 | 2022-09-01 | 39780 | keep | 0 | Sep | 2022 | 0.027094 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
MAYAGÃœEZ | 2022-09-01 14:43 | 2022-09-01 14:44 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22090100218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 4641 | keep | 0 | Sep | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
SAN JUAN | 2022-09-01 14:49 | 2022-09-01 16:11 | 100 | 1:22 | P | NO SE REPORTO CAUSA | 1X50 DE RISER @ C/L | S22090100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2022-09-01 | 8200 | keep | 0 | Sep | 2022 | 0.005585 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-09-01 14:53 | 2022-09-01 16:25 | 100 | 1:32 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22090100220 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 92 | 2022-09-01 | 9200 | keep | 0 | Sep | 2022 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-09-01 15:15 | 2022-09-01 17:16 | 75 | 2:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C22090100110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2022-09-01 | 9075 | keep | 0 | Sep | 2022 | 0.0061809 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-09-01 15:16 | 2022-09-01 16:51 | 12 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA @ CAJA EN C/L | S22090100057 | New_Event | Primary Wire Break | Include | Include | Equipment | 95 | 2022-09-01 | 1140 | keep | 0 | Sep | 2022 | 0.00077645 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-09-01 15:17 | 2022-09-01 19:55 | 40 | 4:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M22090100237 | New_Event | Primary Wire Break | Include | Include | Equipment | 278 | 2022-09-01 | 11120 | keep | 0 | Sep | 2022 | 0.0075738 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-09-01 15:19 | 2022-09-01 15:20 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R22090100084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 1234 | keep | 0 | Sep | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
BAYAMON | 2022-09-01 15:22 | 2022-09-01 16:04 | 5 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22090100135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2022-09-01 | 210 | keep | 0 | Sep | 2022 | 0.00014303 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-09-01 15:23 | 2022-09-01 16:01 | 10 | 0:38 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO Y SE CERRO FUSIBLE EN XMR (NO FUNDIO) | S22090100059 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 38 | 2022-09-01 | 380 | keep | 0 | Sep | 2022 | 0.00025882 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-01 15:31 | 2022-09-01 21:20 | 40 | 5:49 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA Y 1 X 50 EN BOMBA AAA DESCARGAS ELECTRICAS | M22090100241 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 349 | 2022-09-01 | 13960 | keep | 0 | Sep | 2022 | 0.0095081 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-09-01 15:34 | 2022-09-02 00:10 | 1037 | 8:36 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES EN VARIOS PUNTOS Y AISLADORES | M22090100245 | Partial_restoration | Switch Failure | Include | Include | Equipment | 516 | 2022-09-01 | 535092 | keep | 0 | Sep | 2022 | 0.36445 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-01 15:43 | 2022-09-01 16:45 | 464 | 1:02 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES Y SE SECICONALIZO PARA TRABAJAR CONDICION DE CONDUCTOR EN EL SUELO 60% EN SERVICIO DEL 1706-03 | B22090100137 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 62 | 2022-09-01 | 28768 | keep | 0 | Sep | 2022 | 0.019594 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-01 15:58 | 2022-09-01 18:30 | 10 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A22090100067 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2022-09-01 | 1520 | keep | 0 | Sep | 2022 | 0.0010353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-01 16:02 | 2022-09-01 18:41 | 10 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22090100068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2022-09-01 | 1590 | keep | 0 | Sep | 2022 | 0.0010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-09-01 16:12 | 2022-09-01 20:00 | 30 | 3:48 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22090100128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2022-09-01 | 6840 | keep | 0 | Sep | 2022 | 0.0046587 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-09-01 16:18 | 2022-09-01 17:00 | 40 | 0:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090100070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 42 | 2022-09-01 | 1680 | keep | 0 | Sep | 2022 | 0.0011442 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-09-01 16:23 | 2022-09-01 19:00 | 75 | 2:37 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22090100195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2022-09-01 | 11775 | keep | 0 | Sep | 2022 | 0.0080199 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2022-09-01 16:29 | 2022-09-01 19:28 | 83 | 2:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES LLUVIAS | C22090100114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 179 | 2022-09-01 | 14857 | keep | 0 | Sep | 2022 | 0.010119 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
YAUCO | 2022-09-01 16:30 | 2022-09-01 17:25 | 200 | 0:55 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22090100274 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 55 | 2022-09-01 | 11000 | keep | 0 | Sep | 2022 | 0.007492 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-09-01 16:38 | 2022-09-01 19:21 | 8 | 2:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO/LEVANTO SECUNDARIA DEL SUELO (NO FUNDIO) | S22090100070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 163 | 2022-09-01 | 1304 | keep | 0 | Sep | 2022 | 0.00088815 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-09-01 16:39 | 2022-09-01 18:27 | 60 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L Y 1 X 40 EN RISER | B22090100164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-09-01 | 6480 | keep | 0 | Sep | 2022 | 0.0044135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-09-01 16:40 | 2022-09-01 18:12 | 60 | 1:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090100278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-09-01 | 5520 | keep | 0 | Sep | 2022 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-09-01 16:43 | 2022-09-01 20:30 | 100 | 3:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | P22090100200 | New_Event | Primary Wire Break | Include | Include | Equipment | 227 | 2022-09-01 | 22700 | keep | 0 | Sep | 2022 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-01 16:45 | 2022-09-01 23:20 | 265 | 6:35 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRARON MACHETES 100% EN SERVICIO | B22090100137 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 395 | 2022-09-01 | 104675 | keep | 0 | Sep | 2022 | 0.071294 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-01 16:51 | 2022-09-01 21:13 | 70 | 4:22 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | S22090100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2022-09-01 | 18340 | keep | 0 | Sep | 2022 | 0.012491 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-09-01 16:53 | 2022-09-02 10:32 | 100 | 17:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M22090100287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1059 | 2022-09-01 | 105900 | keep | 0 | Sep | 2022 | 0.072128 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-09-01 16:53 | 2022-09-01 18:14 | 100 | 1:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22090100071 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2022-09-01 | 8100 | keep | 0 | Sep | 2022 | 0.0055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-09-01 17:02 | 2022-09-01 18:25 | 50 | 1:23 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22090100294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-09-01 | 4150 | keep | 0 | Sep | 2022 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-09-01 17:05 | 2022-09-01 18:07 | 80 | 1:02 | P | DESGANCHE | 1 X 50 Y 1 X 40 EN C/LS | C22090100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-09-01 | 4960 | keep | 0 | Sep | 2022 | 0.0033782 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-09-01 17:09 | 2022-09-01 19:25 | 20 | 2:16 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | B22090100169 | New_Event | Animals | Include | Include | Wildlife | 136 | 2022-09-01 | 2720 | keep | 0 | Sep | 2022 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-09-01 17:17 | 2022-09-01 20:25 | 35 | 3:08 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22090100298 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 188 | 2022-09-01 | 6580 | keep | 0 | Sep | 2022 | 0.0044816 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2022-09-01 17:20 | 2022-09-01 20:06 | 16 | 2:46 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR POR DESGANCHE | A22090100302 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2022-09-01 | 2656 | keep | 0 | Sep | 2022 | 0.001809 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2022-09-01 17:33 | 2022-09-01 20:03 | 80 | 2:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LAS LINEAS | M22090100307 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-09-01 | 12000 | keep | 0 | Sep | 2022 | 0.0081731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-09-01 17:40 | 2022-09-01 19:25 | 100 | 1:45 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 SUM-20 EN SU-73 CONTAMINACION | R22090100085 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 105 | 2022-09-01 | 10500 | keep | 0 | Sep | 2022 | 0.0071515 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-09-01 17:43 | 2022-09-01 18:53 | 14 | 1:10 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22090100315 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 70 | 2022-09-01 | 980 | keep | 0 | Sep | 2022 | 0.00066747 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2022-09-01 17:53 | 2022-09-01 21:00 | 15 | 3:07 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN RISER CABLE SOTERRADO AVERIADO AVERIA DEL RISER AL T- 3 | P22090100224 | New_Event | UG Cable Fault | Include | Include | Equipment | 187 | 2022-09-01 | 2805 | keep | 0 | Sep | 2022 | 0.0019105 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-01 18:03 | 2022-09-01 18:40 | 15 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22090100082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2022-09-01 | 555 | keep | 0 | Sep | 2022 | 0.00037801 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2022-09-01 18:13 | 2022-09-01 22:30 | 50 | 4:17 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090100230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-09-01 | 12850 | keep | 0 | Sep | 2022 | 0.0087521 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-01 18:23 | 2022-09-01 18:26 | 413 | 0:03 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL DISPARO DE INTERRUPTOR 1620-02 LLEVA 10% DE LA CARGA DEL 1206-03 | S22090100083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-01 | 1239 | keep | 0 | Sep | 2022 | 0.00084388 | 0.00028129 | Momentary | FALSE | FALSE | Not_TMED_Event | 413
SAN JUAN | 2022-09-01 18:23 | 2022-09-01 18:26 | 3718 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL DISPARO DE INTERRUPTOR 1620-02 LLEVA 10% DE LA CARGA DEL 1206-03 | S22090100083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-01 | 11154 | keep | 0 | Sep | 2022 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
FAJARDO | 2022-09-01 18:36 | 2022-09-02 09:45 | 100 | 15:09 | P | OTRAS CAUSAS | 2 X 50 EN CORTE DE LINEA HAY QUE HACER MEJORA CAPITAL VARIAS AREAS CONTAMINADAS | R22090100090 | New_Event | Other Causes | Include | Include | Other | 909 | 2022-09-01 | 90900 | keep | 0 | Sep | 2022 | 0.061912 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-01 18:36 | 2022-09-01 18:37 | 1417 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22090100330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 1417 | keep | 0 | Sep | 2022 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
HUMACAO | 2022-09-01 18:38 | 2022-09-01 18:40 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C22090100131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 4252 | keep | 0 | Sep | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
CAGUAS | 2022-09-01 18:44 | 2022-09-01 20:36 | 10 | 1:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22090100133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2022-09-01 | 1120 | keep | 0 | Sep | 2022 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-01 18:45 | 2022-09-02 00:46 | 15 | 6:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PARTIDO TRAMO RADIAL | B22090100056 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 361 | 2022-09-01 | 5415 | keep | 0 | Sep | 2022 | 0.0036881 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-01 18:45 | 2022-09-02 00:43 | 20 | 5:58 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE PRIMARIO PARTIDO POR CAMION | B22090100056 | New_Event | Damage From Public | Include | Include | Public | 358 | 2022-09-01 | 7160 | keep | 0 | Sep | 2022 | 0.0048766 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-01 18:54 | 2022-09-02 11:31 | 20 | 16:37 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22090100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 997 | 2022-09-01 | 19940 | keep | 0 | Sep | 2022 | 0.013581 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-09-01 18:58 | 2022-09-01 19:18 | 150 | 0:20 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22090100304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2022-09-01 | 3000 | keep | 0 | Sep | 2022 | 0.0020433 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-09-01 19:12 | 2022-09-02 19:30 | 30 | 24:18 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO | P22090100246 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1458 | 2022-09-01 | 43740 | keep | 0 | Sep | 2022 | 0.029791 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-01 19:16 | 2022-09-02 02:00 | 9 | 6:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN TRANSFORMADOR | M22090100341 | New_Event | Primary Wire Break | Include | Include | Equipment | 404 | 2022-09-01 | 3636 | keep | 0 | Sep | 2022 | 0.0024765 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-09-01 19:27 | 2022-09-01 22:15 | 75 | 2:48 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22090100346 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 168 | 2022-09-01 | 12600 | keep | 0 | Sep | 2022 | 0.0085818 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2022-09-01 19:32 | 2022-09-01 19:34 | 635 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 2306-02 SE PROBO QUEDO EN SERVICIO | R22090100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 1270 | keep | 0 | Sep | 2022 | 0.00086499 | 0.0004325 | Momentary | FALSE | FALSE | Not_TMED_Event | 635
CANOVANAS | 2022-09-01 19:32 | 2022-09-01 19:34 | 1380 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 2305-04 SE PROBO QUEDO EN SERVICIO | R22090100094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-01 | 2760 | keep | 0 | Sep | 2022 | 0.0018798 | 0.00093991 | Momentary | FALSE | FALSE | Not_TMED_Event | 1380
AGUADILLA | 2022-09-01 19:37 | 2022-09-01 19:38 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22090100355 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 1827 | keep | 0 | Sep | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BAYAMON | 2022-09-01 19:46 | 2022-09-01 22:17 | 1 | 2:31 | P | NO SE REPORTO CAUSA | 1 X 20 EN MONTURA DE XMR | B22090100200 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2022-09-01 | 151 | keep | 0 | Sep | 2022 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-01 19:47 | 2022-09-02 10:10 | 12 | 14:23 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A XMR | B22090100201 | New_Event | Primary Wire Break | Include | Include | Equipment | 863 | 2022-09-01 | 10356 | keep | 0 | Sep | 2022 | 0.0070534 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-09-01 19:47 | 2022-09-01 22:05 | 100 | 2:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA CAJA PRIMARIA | A22090100088 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2022-09-01 | 13800 | keep | 0 | Sep | 2022 | 0.0093991 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-09-01 19:49 | 2022-09-02 08:24 | 15 | 12:35 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B22090100202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 755 | 2022-09-01 | 11325 | keep | 0 | Sep | 2022 | 0.0077134 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-09-01 20:23 | 2022-09-02 01:45 | 75 | 5:22 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P22090100264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-09-01 | 24150 | keep | 0 | Sep | 2022 | 0.016448 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-09-01 20:28 | 2022-09-02 04:20 | 1483 | 7:52 | P | CABLE SOTERRADO AVERIADO | SE CERRO AMARRE CONTRA 1336-08 Y QUEDO EN SERVICIO. SE DEJO FUERA RISER HACIA ESCUELA | S22090100124 | New_Event | UG Cable Fault | Include | Include | Equipment | 472 | 2022-09-01 | 699976 | keep | 0 | Sep | 2022 | 0.47675 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-09-01 20:28 | 2022-09-02 01:30 | 1531 | 5:02 | P | CABLE SOTERRADO AVERIADO | SE CERRO AMARRE EN SU 2 CONTRA 1336-09. ENTRANDO CARGA DE 15% 1204-05 | S22090100124 | New_Event | UG Cable Fault | Include | Include | Equipment | 302 | 2022-09-01 | 462362 | keep | 0 | Sep | 2022 | 0.31491 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2022-09-01 20:28 | 2022-09-01 21:51 | 4761 | 1:23 | P | CABLE SOTERRADO AVERIADO | SE PASO 20% DE LA CARGA 1336-08 AL 1348-06 (PORTATIL) PARA DAR SEVICIO A HOSPITAL Y CONTINUAR PATRULLANDO. 10% DE SU CARGA TRANSFERIDA AL 1424-08 SE ABRIO AMARRE CONTRA 15% 1204-05 Y 30% 1204-04 | S22090100124 | New_Event | UG Cable Fault | Include | Include | Equipment | 83 | 2022-09-01 | 395163 | keep | 0 | Sep | 2022 | 0.26914 | 0.0032427 | Sustained | FALSE | FALSE | Not_TMED_Event | 4761
SAN JUAN | 2022-09-01 20:30 | 2022-09-01 21:38 | 427 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10100 | S22090100156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-09-01 | 29036 | keep | 0 | Sep | 2022 | 0.019776 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2022-09-01 20:30 | 2022-09-01 21:38 | 716 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10100 | S22090100156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-09-01 | 48688 | keep | 0 | Sep | 2022 | 0.033161 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2022-09-01 20:30 | 2022-09-01 21:38 | 867 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10100 | S22090100156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-09-01 | 58956 | keep | 0 | Sep | 2022 | 0.040155 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2022-09-01 20:30 | 2022-09-01 21:38 | 353 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10100 | S22090100156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2022-09-01 | 24004 | keep | 0 | Sep | 2022 | 0.016349 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
SAN JUAN | 2022-09-01 20:42 | 2022-09-01 20:46 | 922 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 CARGA POR EL 1401-08 | S22090100207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-09-01 | 3688 | keep | 0 | Sep | 2022 | 0.0025119 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-09-01 20:42 | 2022-09-01 20:46 | 135 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 LLEVA 1346-05 | S22090100207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-09-01 | 540 | keep | 0 | Sep | 2022 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-09-01 20:43 | 2022-09-01 20:44 | 790 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 1345-03 LLEVA LA CARGA DEL 1342-02 | S22090100203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 790 | keep | 0 | Sep | 2022 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2022-09-01 20:43 | 2022-09-01 20:44 | 259 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR 1345-03 LLEVA LA CARGA DEL 1342-02 | S22090100203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 259 | keep | 0 | Sep | 2022 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
CANOVANAS | 2022-09-01 20:49 | 2022-09-01 21:45 | 4188 | 0:56 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR TRAMO LINEA CRUZADA Y AISLADOR PARTIDO | R22090100104 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 56 | 2022-09-01 | 234528 | keep | 0 | Sep | 2022 | 0.15974 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
YAUCO | 2022-09-01 21:01 | 2022-09-01 23:00 | 50 | 1:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090100364 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 119 | 2022-09-01 | 5950 | keep | 0 | Sep | 2022 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-01 21:02 | 2022-09-01 23:49 | 172 | 2:47 | P | DESGANCHE | DESGANCHE 1 X 65 EN C/L Y 1 X 100 EN SU | B22090100213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-09-01 | 28724 | keep | 0 | Sep | 2022 | 0.019564 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BAYAMON | 2022-09-01 21:14 | 2022-09-01 21:17 | 450 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B22090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-01 | 1350 | keep | 0 | Sep | 2022 | 0.00091948 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
YAUCO | 2022-09-01 21:33 | 2022-09-02 00:36 | 40 | 3:03 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22090100285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-09-01 | 7320 | keep | 0 | Sep | 2022 | 0.0049856 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-09-01 21:34 | 2022-09-02 09:56 | 1 | 12:22 | P | MAL TIEMPO/RAYOS | 1 X 20 EN XMR MAL TIEMPO RAYOS | P22090100286 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 742 | 2022-09-01 | 742 | keep | 0 | Sep | 2022 | 0.00050537 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-01 21:45 | 2022-09-01 21:56 | 1675 | 0:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO AISLADOR ROTO Y CONDUCTORES CRUZADOS GOI SJ-220901-50A SE CERRO N/O CON EL 2302-03 100% EN SERVICIO | R22090100104 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 11 | 2022-09-01 | 18425 | keep | 0 | Sep | 2022 | 0.012549 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-01 21:51 | 2022-09-01 22:18 | 3332 | 0:27 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1336-09 AL CERRAR N/O CONTRA 1336-08. FUERA CARGA 30% 1204-04 Y 15% 1204-05 | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 27 | 2022-09-01 | 89964 | keep | 0 | Sep | 2022 | 0.061274 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-01 22:09 | 2022-09-02 09:34 | 40 | 11:25 | P | DESGANCHE | 1X65 EN C/L | S22090100408 | New_Event | Vegetation Contact | Include | Include | Vegetation | 685 | 2022-09-01 | 27400 | keep | 0 | Sep | 2022 | 0.018662 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-01 22:09 | 2022-09-02 07:47 | 60 | 9:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C22090100145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 578 | 2022-09-01 | 34680 | keep | 0 | Sep | 2022 | 0.02362 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-01 22:17 | 2022-09-02 01:07 | 46 | 2:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 1X 80 Y 1X100 EN C/L LLUVIA Y VIENTO FUERTE | B22090100237 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 170 | 2022-09-01 | 7820 | keep | 0 | Sep | 2022 | 0.0053262 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
SAN JUAN | 2022-09-01 22:18 | 2022-09-01 22:42 | 3332 | 0:24 | P | CABLE SOTERRADO AVERIADO | SE CERRO N/O CON 1336-09 Y QUEDO EN SERVICIO 70% DE LA CARGA 1336-08. FUERA 30% 1204-04 Y 15% 1204-05 | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 24 | 2022-09-01 | 79968 | keep | 0 | Sep | 2022 | 0.054466 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-01 22:18 | 2022-09-01 22:33 | 207 | 0:15 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR AL PASAR CARGA 1336-08 AL 1336-09. SE ABRIO N/O Y SE CERRO INTERRUPTOR 1336-09. FUERA CARGA 1336-08, 30% 1204-04 Y 15% 1204-05 | S22090100448 | New_Event | UG Cable Fault | Include | Include | Equipment | 15 | 2022-09-01 | 3105 | keep | 0 | Sep | 2022 | 0.0021148 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
CANOVANAS | 2022-09-01 22:18 | 2022-09-02 01:40 | 133 | 3:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R22090100154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2022-09-01 | 26866 | keep | 0 | Sep | 2022 | 0.018298 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
AGUADILLA | 2022-09-01 22:37 | 2022-09-02 09:00 | 100 | 10:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | M22090100374 | New_Event | Primary Wire Break | Include | Include | Equipment | 623 | 2022-09-01 | 62300 | keep | 0 | Sep | 2022 | 0.042432 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-01 22:48 | 2022-09-01 22:55 | 3332 | 0:07 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1336-09 LLEVANDO 70% CARGA 1336-08 | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 7 | 2022-09-01 | 23324 | keep | 0 | Sep | 2022 | 0.015886 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-01 22:48 | 2022-09-01 22:55 | 207 | 0:07 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1336-09 LLEVANDO 70% CARGA 1336-08 | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 7 | 2022-09-01 | 1449 | keep | 0 | Sep | 2022 | 0.00098691 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-01 22:55 | 2022-09-01 22:56 | 3941 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22090100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-01 | 3941 | keep | 0 | Sep | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-09-01 22:58 | 2022-09-02 10:51 | 15 | 11:53 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S22090100531 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 713 | 2022-09-01 | 10695 | keep | 0 | Sep | 2022 | 0.0072843 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-01 23:00 | 2022-09-02 | 3332 | 1:00 | P | CABLE SOTERRADO AVERIADO | SE CERRO MACHETES DE AMARRE ENTRE 1336-09/1336-08 Y SE SECCIONALIZO PARTE DE 1336-08. 20% 1336-08 EN SERVICIO | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 60 | 2022-09-01 | 199920 | keep | 0 | Sep | 2022 | 0.13616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-01 23:00 | 2022-09-01 23:23 | 207 | 0:23 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1336-09 LLEVANDO 70% 1336-08. SE ABRIO MACHETES DE AMARRE ENTRE AMBOS Y SE CERRO POR SCADA. EN SERVICIO 1336-09 | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 23 | 2022-09-01 | 4761 | keep | 0 | Sep | 2022 | 0.0032427 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-09-01 23:00 | 2022-09-02 00:25 | 10 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | P22090100250 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2022-09-01 | 850 | keep | 0 | Sep | 2022 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-09-01 23:22 | 2022-09-02 01:30 | 40 | 2:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | A22090100107 | New_Event | Cutout Failure | Include | Include | Equipment | 128 | 2022-09-01 | 5120 | keep | 0 | Sep | 2022 | 0.0034872 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-09-01 23:27 | 2022-09-02 11:01 | 2 | 11:34 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGA ELECTRICA | P22090100299 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 694 | 2022-09-01 | 1388 | keep | 0 | Sep | 2022 | 0.00094536 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-09-01 23:32 | 2022-09-02 08:47 | 25 | 9:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22090100174 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 555 | 2022-09-01 | 13875 | keep | 0 | Sep | 2022 | 0.0094502 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-09-01 23:49 | 2022-09-02 04:40 | 56 | 4:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA QUEMADA | B22090100253 | New_Event | Cutout Failure | Include | Include | Equipment | 291 | 2022-09-01 | 16296 | keep | 0 | Sep | 2022 | 0.011099 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
SAN JUAN | 2022-09-02 | 2022-09-02 00:22 | 2666 | 0:22 | P | CABLE SOTERRADO AVERIADO | SE CERRO MACHETES DE AMARRE ENTRE 1336-09/1336-08 Y SE SECCIONALIZO PARTE DE 1336-08. 20% 1336-08 EN SERVICIO | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 22 | 2022-09-02 | 58652 | keep | 0 | Sep | 2022 | 0.039948 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-02 00:06 | 2022-09-02 00:07 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4100 | B22090200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 4176 | keep | 0 | Sep | 2022 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-09-02 00:06 | 2022-09-02 00:07 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4100 | B22090200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 252 | keep | 0 | Sep | 2022 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2022-09-02 00:06 | 2022-09-02 00:07 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4100 | B22090200003 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 2147 | keep | 0 | Sep | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-09-02 00:06 | 2022-09-02 00:07 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4100 | B22090200004 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 2858 | keep | 0 | Sep | 2022 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
SAN JUAN | 2022-09-02 00:22 | 2022-09-02 00:41 | 333 | 0:19 | P | CABLE SOTERRADO AVERIADO | SE CERRO INTERRUPTOR 1336-08 SECCIONALIZANDO ALIMENTADOR POR CABLE SOTERRADO AVERIADO HACIA ESCUELA, 10% EN SERVICIO. FUERA 15%1204-05 Y 30% 1204-04 | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 19 | 2022-09-02 | 6327 | keep | 0 | Sep | 2022 | 0.0043093 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-02 00:22 | 2022-09-02 00:29 | 207 | 0:07 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1336-09 LLEVANDO 20% CARGA 1336-08. SE ABRIO AMARRE Y SE CERRO POR SCADA | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 7 | 2022-09-02 | 1449 | keep | 0 | Sep | 2022 | 0.00098691 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-02 00:41 | 2022-09-02 01:04 | 2999 | 0:23 | P | DESGANCHE | SE DISPARO INTERRUPTR 1336-08 CON 10% DE SU CARGA POR ARBOL QUEMANDO. SE RETIRO RAMA CON VARETA | S22090100124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2022-09-02 | 68977 | keep | 0 | Sep | 2022 | 0.04698 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
CAGUAS | 2022-09-02 00:59 | 2022-09-02 01:00 | 4369 | 0:01 | T | TRANSFORMADOR AVERIADO | RECERRO INTERRUPTOR EN SERVICIO | C22090200002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1 | 2022-09-02 | 4369 | keep | 0 | Sep | 2022 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2022-09-02 01:00 | 2022-09-02 15:40 | 23 | 14:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 75KVA X 50KVA | C22090200003 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 880 | 2022-09-02 | 20240 | keep | 0 | Sep | 2022 | 0.013785 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2022-09-02 01:04 | 2022-09-02 02:25 | 3332 | 1:21 | P | DESGANCHE | SE RETIRO RAMA CON VARETA | S22090100124 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-09-02 | 269892 | keep | 0 | Sep | 2022 | 0.18382 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-02 01:29 | 2022-09-02 07:20 | 50 | 5:51 | P | MAL TIEMPO/RAYOS | 1 X 30 Y 1 X 40 EN DISTINTOS CORTES DE LINEA DESCARGAS ELECTRICAS | A22090200004 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 351 | 2022-09-02 | 17550 | keep | 0 | Sep | 2022 | 0.011953 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-02 01:37 | 2022-09-02 03:42 | 1531 | 2:05 | P | CABLE SOTERRADO AVERIADO | SE CERRO AMARRE EN SU 2 CONTRA 1336-08. ENTRANDO CARGA DE 15% 1204-05. SE HABIA RETIRADO AL DISPARAR 1336-09 | S22090100124 | New_Event | UG Cable Fault | Include | Include | Equipment | 125 | 2022-09-02 | 191375 | keep | 0 | Sep | 2022 | 0.13034 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2022-09-02 01:37 | 2022-09-02 03:42 | 207 | 2:05 | T | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR 1336-09 AL CERRAR EN VS HACIA ESCUELA. SE PASO CARGA A 1336-08 ENTRANDO TAMBIEN CARGA DEL 15% 1204-05. Y ABRIENDO HACIA CARGA DEL 30% 1204-04 INTERRUPTOR DIO FTO | S22090100124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 125 | 2022-09-02 | 25875 | keep | 0 | Sep | 2022 | 0.017623 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-02 02:25 | 2022-09-02 02:30 | 2999 | 0:05 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1336-08 LLEVANDO SOLO 10% DE SU CARGA. PENCA DE PALMA CRUZANDO LINEAS | S22090100124 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-09-02 | 14995 | keep | 0 | Sep | 2022 | 0.010213 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-02 02:30 | 2022-09-02 02:36 | 3332 | 0:06 | P | DESGANCHE | SE RETIRO PENCA CRUZANDO LINEAS. 10% DE LA CARGA EN SERVICIO | S22090100124 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-09-02 | 19992 | keep | 0 | Sep | 2022 | 0.013616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-02 02:36 | 2022-09-02 03:25 | 2999 | 0:49 | P | DESGANCHE | SE CERRO MACHETES QUEDANDO EN SERVICIO 100% 1336-08 QUEDANDO FUERA CARGA 1336-09 15% 1204-05 Y 30% 1204-04 | S22090100124 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 49 | 2022-09-02 | 146951 | keep | 0 | Sep | 2022 | 0.10009 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-02 04:53 | 2022-09-02 04:56 | 363 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 90% 1336-10 Y 1620-01 SE CERRO POR SCADA | S22090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-02 | 1089 | keep | 0 | Sep | 2022 | 0.00074171 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
SAN JUAN | 2022-09-02 04:53 | 2022-09-02 04:56 | 36 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 90% 1336-10 Y 1620-01 SE CERRO POR SCADA | S22090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-02 | 108 | keep | 0 | Sep | 2022 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-09-02 04:53 | 2022-09-02 04:56 | 1073 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO 1620-03 LLEVA 90%1336-10 Y 1620-01 SE CERRO POR SCADA | S22090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-02 | 3219 | keep | 0 | Sep | 2022 | 0.0021924 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
CAGUAS | 2022-09-02 05:14 | 2022-09-02 07:47 | 65 | 2:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | C22090200005 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-09-02 | 9945 | keep | 0 | Sep | 2022 | 0.0067735 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2022-09-02 05:42 | 2022-09-02 15:30 | 4 | 9:48 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2022-09-02 | 2352 | keep | 0 | Sep | 2022 | 0.0016019 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-09-02 05:46 | 2022-09-03 16:00 | 12 | 34:14 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO HACIA T-26 | B22090200011 | New_Event | UG Cable Fault | Include | Include | Equipment | 2054 | 2022-09-02 | 24648 | keep | 0 | Sep | 2022 | 0.016788 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-09-02 05:46 | 2022-09-02 08:00 | 25 | 2:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y VIENTO FUERTE | A22090200007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 134 | 2022-09-02 | 3350 | keep | 0 | Sep | 2022 | 0.0022817 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-09-02 06:09 | 2022-09-02 11:54 | 25 | 5:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M22090200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2022-09-02 | 8625 | keep | 0 | Sep | 2022 | 0.0058744 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-09-02 06:14 | 2022-09-02 06:15 | 732 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090200041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 732 | keep | 0 | Sep | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
AGUADILLA | 2022-09-02 06:17 | 2022-09-02 09:18 | 45 | 3:01 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22090200010 | New_Event | Animals | Include | Include | Wildlife | 181 | 2022-09-02 | 8145 | keep | 0 | Sep | 2022 | 0.0055475 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-09-02 06:36 | 2022-09-02 06:37 | 61 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R22090200013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 61 | keep | 0 | Sep | 2022 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
MAYAGÃœEZ | 2022-09-02 06:43 | 2022-09-02 09:03 | 20 | 2:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE PALMA | M22090200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-09-02 | 2800 | keep | 0 | Sep | 2022 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-02 06:56 | 2022-09-02 17:10 | 20 | 10:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50 KVA | S22090200169 | New_Event | Service Transformer Failure | Include | Include | Equipment | 614 | 2022-09-02 | 12280 | keep | 0 | Sep | 2022 | 0.0083639 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-02 06:57 | 2022-09-02 14:17 | 20 | 7:20 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | C22090200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2022-09-02 | 8800 | keep | 0 | Sep | 2022 | 0.0059936 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-02 07:08 | 2022-09-02 09:49 | 40 | 2:41 | P | DESGANCHE | 1X65 EN C/L | S22090200171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-09-02 | 6440 | keep | 0 | Sep | 2022 | 0.0043863 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-09-02 07:20 | 2022-09-02 07:21 | 2132 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22090200016 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 2132 | keep | 0 | Sep | 2022 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-02 07:20 | 2022-09-02 07:21 | 2366 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22090200016 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 2366 | keep | 0 | Sep | 2022 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-09-02 07:20 | 2022-09-02 07:21 | 1976 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22090200016 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 1976 | keep | 0 | Sep | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-09-02 07:20 | 2022-09-02 07:21 | 3688 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LINEA 36100 | A22090200016 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 3688 | keep | 0 | Sep | 2022 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECERRO LINEA 36100 | B22090200018 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 3070 | keep | 0 | Sep | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECERRO LINEA 36100 | B22090200018 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 2735 | keep | 0 | Sep | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECERRO LINEA 36100 | B22090200018 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 1070 | keep | 0 | Sep | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B22090200017 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 1647 | keep | 0 | Sep | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B22090200017 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 3295 | keep | 0 | Sep | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B22090200017 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 1180 | keep | 0 | Sep | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B22090200019 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 320 | keep | 0 | Sep | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-09-02 07:20 | 2022-09-02 07:21 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 | B22090200019 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-02 | 2234 | keep | 0 | Sep | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2022-09-02 07:21 | 2022-09-02 12:28 | 50 | 5:07 | P | MAL TIEMPO/RAYOS | 1 X 30 Y 1 X 40 EN DISTINTOS CORTES DE LINEA DESCARGAS ELECTRICAS | A22090200004 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 307 | 2022-09-02 | 15350 | keep | 0 | Sep | 2022 | 0.010455 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-02 07:23 | 2022-09-02 09:00 | 100 | 1:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C22090200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-09-02 | 9700 | keep | 0 | Sep | 2022 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-09-02 07:33 | 2022-09-02 07:34 | 661 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090200048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 661 | keep | 0 | Sep | 2022 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
VEGA BAJA | 2022-09-02 07:36 | 2022-09-02 17:10 | 1 | 9:34 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA RANA CRUZO LINEAS | A22090200018 | New_Event | Animals | Include | Include | Wildlife | 574 | 2022-09-02 | 574 | keep | 0 | Sep | 2022 | 0.00039095 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-02 07:40 | 2022-09-02 09:25 | 20 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22090200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-09-02 | 2100 | keep | 0 | Sep | 2022 | 0.0014303 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-02 07:46 | 2022-09-02 10:36 | 40 | 2:50 | P | ARBOL SOBRE LINEA | 1 X 40 EN C/L SE RETIRO ARBOL SOBRE LINEA | S22090200174 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 170 | 2022-09-02 | 6800 | keep | 0 | Sep | 2022 | 0.0046314 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-02 07:46 | 2022-09-02 11:37 | 3070 | 3:51 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZO PARARAYOS EN BARRA DE DISTRIBUCION SE TRANSFIRIO EL 90% DE LA CARGA AL 9502-01 | B22090200049 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 231 | 2022-09-02 | 709170 | keep | 0 | Sep | 2022 | 0.48301 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-09-02 07:46 | 2022-09-02 14:47 | 2735 | 7:01 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZO PARARAYOS EN BARRA DE DISTRIBUCION | B22090200049 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 421 | 2022-09-02 | 1151435 | keep | 0 | Sep | 2022 | 0.78424 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-09-02 07:46 | 2022-09-02 14:47 | 1070 | 7:01 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZO PARARAYOS EN BARRA DE DISTRIBUCION | B22090200049 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 421 | 2022-09-02 | 450470 | keep | 0 | Sep | 2022 | 0.30681 | 0.00072877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-09-02 07:54 | 2022-09-02 12:54 | 10 | 5:00 | P | ANIMAL | 1 X 15 EN XMR SE RETIRO AVE | B22090200052 | New_Event | Animals | Include | Include | Wildlife | 300 | 2022-09-02 | 3000 | keep | 0 | Sep | 2022 | 0.0020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-02 07:58 | 2022-09-02 09:28 | 150 | 1:30 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R22090200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-09-02 | 13500 | keep | 0 | Sep | 2022 | 0.0091948 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-09-02 08:00 | 2022-09-02 13:21 | 150 | 5:21 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | M22090200051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-09-02 | 48150 | keep | 0 | Sep | 2022 | 0.032795 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-09-02 08:02 | 2022-09-02 14:34 | 50 | 6:32 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P22090200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-09-02 | 19600 | keep | 0 | Sep | 2022 | 0.013349 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-09-02 08:15 | 2022-09-02 14:37 | 908 | 6:22 | T | CRUCETA DEFECTUOSA O AVERIADA | SE REEMPLAZO CRUCETA PARTIDA GOI BY 220902-01 | B22090200064 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 382 | 2022-09-02 | 346856 | keep | 0 | Sep | 2022 | 0.23624 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
ARECIBO | 2022-09-02 08:22 | 2022-09-02 10:02 | 40 | 1:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 Y 1 X 25 EN DISTINTOS CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | A22090200024 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2022-09-02 | 4000 | keep | 0 | Sep | 2022 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-09-02 08:35 | 2022-09-02 11:01 | 7 | 2:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON CONECTORES QUEMADOS EN TRANSFORMADOR | C22090200036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 146 | 2022-09-02 | 1022 | keep | 0 | Sep | 2022 | 0.00069608 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-09-02 08:40 | 2022-09-02 15:30 | 10 | 6:50 | P | DESGANCHE | 1 X 30 EN AEREO PROVISIONAL SE RETIRO RAMA | R22090200022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 410 | 2022-09-02 | 4100 | keep | 0 | Sep | 2022 | 0.0027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-02 08:42 | 2022-09-02 11:36 | 3 | 2:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BAJANTES SECUNDARIOS EN BANCO DE XMRS | S22090200184 | New_Event | Secondary Wire Break | Include | Include | Equipment | 174 | 2022-09-02 | 522 | keep | 0 | Sep | 2022 | 0.00035553 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2022-09-02 08:43 | 2022-09-02 08:44 | 1475 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090200061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 1475 | keep | 0 | Sep | 2022 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
MAYAGÃœEZ | 2022-09-02 08:45 | 2022-09-02 14:38 | 30 | 5:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090200037 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 353 | 2022-09-02 | 10590 | keep | 0 | Sep | 2022 | 0.0072128 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-02 09:03 | 2022-09-02 11:26 | 105 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REEMPLAZO CAJA PRIMARIA | B22090200071 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2022-09-02 | 15015 | keep | 0 | Sep | 2022 | 0.010227 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2022-09-02 09:06 | 2022-09-02 12:20 | 43 | 3:14 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA, SE FIJO Y SE REPARO BAJANTE SECUNDARIO (NO FUNDIO) | S22090200191 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 194 | 2022-09-02 | 8342 | keep | 0 | Sep | 2022 | 0.0056817 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2022-09-02 09:17 | 2022-09-02 09:56 | 30 | 0:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO PUENTE DE LINEA A CAJA CORTE DE LINEA | R22090200028 | New_Event | Primary Wire Break | Include | Include | Equipment | 39 | 2022-09-02 | 1170 | keep | 0 | Sep | 2022 | 0.00079688 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-02 09:19 | 2022-09-02 15:09 | 2 | 5:50 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090200039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2022-09-02 | 700 | keep | 0 | Sep | 2022 | 0.00047677 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-09-02 09:20 | 2022-09-02 13:15 | 2 | 3:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA EN TRANSFORMADOR | P22090200066 | New_Event | Cutout Failure | Include | Include | Equipment | 235 | 2022-09-02 | 470 | keep | 0 | Sep | 2022 | 0.00032011 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-09-02 09:29 | 2022-09-02 15:45 | 10 | 6:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22090200080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 376 | 2022-09-02 | 3760 | keep | 0 | Sep | 2022 | 0.0025609 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-02 09:36 | 2022-09-02 15:20 | 20 | 5:44 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 50 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M22090200053 | New_Event | Primary Pole Failure | Include | Include | Equipment | 344 | 2022-09-02 | 6880 | keep | 0 | Sep | 2022 | 0.0046859 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-02 09:38 | 2022-09-02 14:00 | 10 | 4:22 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE QUE CRUZO LINEAS | A22090200035 | New_Event | Animals | Include | Include | Wildlife | 262 | 2022-09-02 | 2620 | keep | 0 | Sep | 2022 | 0.0017845 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-02 09:43 | 2022-09-02 12:30 | 3 | 2:47 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO CORTE DE LINEA | M22090200044 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 167 | 2022-09-02 | 501 | keep | 0 | Sep | 2022 | 0.00034123 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-09-02 09:43 | 2022-09-02 17:44 | 4 | 8:01 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | M22090200043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 481 | 2022-09-02 | 1924 | keep | 0 | Sep | 2022 | 0.0013104 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-09-02 09:45 | 2022-09-02 12:02 | 10 | 2:17 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR Y SE REEMPLAZARON TOMAS EN MALAS CONDICIONES | M22090200046 | New_Event |  |  |  |  | 137 | 2022-09-02 | 1370 | keep | 0 | Sep | 2022 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-02 09:47 | 2022-09-02 14:55 | 100 | 5:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090200036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-09-02 | 30800 | keep | 0 | Sep | 2022 | 0.020978 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-09-02 09:57 | 2022-09-02 13:30 | 1862 | 3:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 PERSONAL MUNICIPIO LIMPIANDO SOLAR Y ARBOLES CAYERON SOBRE LINEA | R22090200046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 213 | 2022-09-02 | 396606 | keep | 0 | Sep | 2022 | 0.27013 | 0.0012682 | Sustained | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2022-09-02 09:57 | 2022-09-02 13:30 | 1613 | 3:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 PERSONAL MUNICIPIO LIMPIANDO SOLAR Y ARBOLES CAYERON SOBRE LINEA | R22090200046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 213 | 2022-09-02 | 343569 | keep | 0 | Sep | 2022 | 0.234 | 0.0010986 | Sustained | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2022-09-02 09:57 | 2022-09-02 13:30 | 1448 | 3:33 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 PERSONAL MUNICIPIO LIMPIANDO SOLAR Y ARBOLES CAYERON SOBRE LINEA | R22090200046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 213 | 2022-09-02 | 308424 | keep | 0 | Sep | 2022 | 0.21007 | 0.00098623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1448
MAYAGÃœEZ | 2022-09-02 10:12 | 2022-09-02 18:01 | 20 | 7:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO | M22090200053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 469 | 2022-09-02 | 9380 | keep | 0 | Sep | 2022 | 0.0063887 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-02 10:12 | 2022-09-02 11:52 | 40 | 1:40 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L SE RETIRO GLOBO | B22090200087 | New_Event | Damage From Public | Include | Include | Public | 100 | 2022-09-02 | 4000 | keep | 0 | Sep | 2022 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-02 10:15 | 2022-09-02 10:40 | 1202 | 0:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | CG-220902-01 REEMPLAZO DE AISLADOR QUEMADO EN TRONCAL | C22090200116 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 25 | 2022-09-02 | 30050 | keep | 0 | Sep | 2022 | 0.020467 | 0.00081868 | Sustained | FALSE | FALSE | Not_TMED_Event | 1202
BAYAMON | 2022-09-02 10:19 | 2022-09-02 15:45 | 50 | 5:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER Y 1 X 20 EN SU @ FERRETERIA NATIONAL | B22090200089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 326 | 2022-09-02 | 16300 | keep | 0 | Sep | 2022 | 0.011102 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-02 10:34 | 2022-09-02 13:42 | 77 | 3:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C22090200059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2022-09-02 | 14476 | keep | 0 | Sep | 2022 | 0.0098595 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
UTUADO | 2022-09-02 10:38 | 2022-09-02 16:40 | 60 | 6:02 | P | ARBOL SOBRE LINEA | 1 X 80 Y 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOLES SOBRE LAS LINEAS | A22090200046 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 362 | 2022-09-02 | 21720 | keep | 0 | Sep | 2022 | 0.014793 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-02 10:39 | 2022-09-02 14:19 | 85 | 3:40 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA | M22090200061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2022-09-02 | 18700 | keep | 0 | Sep | 2022 | 0.012736 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2022-09-02 10:55 | 2022-09-02 14:00 | 60 | 3:05 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | B22090200096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2022-09-02 | 11100 | keep | 0 | Sep | 2022 | 0.0075602 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-09-02 11:01 | 2022-09-02 12:14 | 1 | 1:13 | P | MAL TIEMPO/RAYOS | 1 X 20 EN RISER DESCARGA ELECTRICA | P22090200093 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 73 | 2022-09-02 | 73 | keep | 0 | Sep | 2022 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-02 11:04 | 2022-09-02 15:03 | 1 | 3:59 | P | NO SE REPORTO CAUSA | 1X15 DE RISER @ T-1 | S22090200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 239 | 2022-09-02 | 239 | keep | 0 | Sep | 2022 | 0.00016278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-02 11:06 | 2022-09-02 12:42 | 476 | 1:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090200064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2022-09-02 | 45696 | keep | 0 | Sep | 2022 | 0.031123 | 0.0003242 | Sustained | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-09-02 11:06 | 2022-09-02 12:42 | 1655 | 1:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090200064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2022-09-02 | 158880 | keep | 0 | Sep | 2022 | 0.10821 | 0.0011272 | Sustained | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-09-02 11:06 | 2022-09-02 12:42 | 361 | 1:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090200064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2022-09-02 | 34656 | keep | 0 | Sep | 2022 | 0.023604 | 0.00024588 | Sustained | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-09-02 11:06 | 2022-09-02 12:42 | 2842 | 1:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090200064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2022-09-02 | 272832 | keep | 0 | Sep | 2022 | 0.18582 | 0.0019357 | Sustained | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-09-02 11:06 | 2022-09-02 12:42 | 1702 | 1:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090200080 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2022-09-02 | 163392 | keep | 0 | Sep | 2022 | 0.11129 | 0.0011592 | Sustained | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-09-02 11:06 | 2022-09-02 12:42 | 918 | 1:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090200080 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 96 | 2022-09-02 | 88128 | keep | 0 | Sep | 2022 | 0.060024 | 0.00062525 | Sustained | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2022-09-02 11:06 | 2022-09-02 12:51 | 1725 | 1:45 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090200066 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 105 | 2022-09-02 | 181125 | keep | 0 | Sep | 2022 | 0.12336 | 0.0011749 | Sustained | FALSE | FALSE | Not_TMED_Event | 1725
BARRANQUITAS | 2022-09-02 11:10 | 2022-09-02 15:41 | 5 | 4:31 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C22090200075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2022-09-02 | 1355 | keep | 0 | Sep | 2022 | 0.00092288 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-09-02 11:21 | 2022-09-02 11:24 | 817 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C22090200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-02 | 2451 | keep | 0 | Sep | 2022 | 0.0016694 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
MAYAGÃœEZ | 2022-09-02 11:25 | 2022-09-02 11:26 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22090200071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 2067 | keep | 0 | Sep | 2022 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2022-09-02 11:27 | 2022-09-02 13:31 | 25 | 2:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22090200070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-09-02 | 3100 | keep | 0 | Sep | 2022 | 0.0021114 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-09-02 11:37 | 2022-09-02 14:47 | 300 | 3:10 | P | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZO PARARAYOS EN BARRA DE DISTRIBUCION | B22090200049 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 190 | 2022-09-02 | 57000 | keep | 0 | Sep | 2022 | 0.038822 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-09-02 11:57 | 2022-09-02 12:31 | 437 | 0:34 | T | CABLE SOTERRADO AVERIADO | SE REALIZO OPERACIONES PARA SECCIONALIZAR CABLE SOTERRADO AVERIADO 15% EN SERVICIO | R22090200060 | New_Event | UG Cable Fault | Include | Include | Equipment | 34 | 2022-09-02 | 14858 | keep | 0 | Sep | 2022 | 0.01012 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
BARRANQUITAS | 2022-09-02 11:57 | 2022-09-02 14:40 | 70 | 2:43 | P | ARBOL SOBRE LINEA | 1 X 80 EN C/L SE LEVANTO CONDUCTOR PRIMARIO ARBOL SOBRE LINEA | C22090200125 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 163 | 2022-09-02 | 11410 | keep | 0 | Sep | 2022 | 0.0077713 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-09-02 12:08 | 2022-09-02 14:31 | 8 | 2:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE PRIMARIO DE LINEA @ CAJA EN XMR | S22090200236 | New_Event | Secondary Wire Break | Include | Include | Equipment | 143 | 2022-09-02 | 1144 | keep | 0 | Sep | 2022 | 0.00077917 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-09-02 12:13 | 2022-09-02 15:54 | 10 | 3:41 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22090200141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-09-02 | 2210 | keep | 0 | Sep | 2022 | 0.0015052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-02 12:31 | 2022-09-02 12:37 | 371 | 0:06 | P | CABLE SOTERRADO AVERIADO | ALIMENTADOR SECCIONALIZADO | R22090200060 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 6 | 2022-09-02 | 2226 | keep | 0 | Sep | 2022 | 0.0015161 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-02 12:37 | 2022-09-02 12:39 | 437 | 0:02 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR DEL SU-24 A SU-7 | R22090200060 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 2 | 2022-09-02 | 874 | keep | 0 | Sep | 2022 | 0.00059528 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-02 12:39 | 2022-09-02 13:23 | 371 | 0:44 | P | CABLE SOTERRADO AVERIADO | SE REALIZO OPERACIONES PARA SECCIONALIZAR CABLE SOTERRADO AVERIADO 15% EN SERVICIO | R22090200060 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 44 | 2022-09-02 | 16324 | keep | 0 | Sep | 2022 | 0.011118 | 0.00025269 | Sustained | FALSE | FALSE | Not_TMED_Event | 371
MAYAGÃœEZ | 2022-09-02 12:42 | 2022-09-02 17:37 | 40 | 4:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2022-09-02 | 11800 | keep | 0 | Sep | 2022 | 0.0080369 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-02 12:49 | 2022-09-02 14:35 | 5 | 1:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C22090200026 | New_Event | Secondary Wire Break | Include | Include | Equipment | 106 | 2022-09-02 | 530 | keep | 0 | Sep | 2022 | 0.00036098 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2022-09-02 13:06 | 2022-09-02 16:00 | 3 | 2:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090200095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 174 | 2022-09-02 | 522 | keep | 0 | Sep | 2022 | 0.00035553 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-09-02 13:14 | 2022-09-02 18:59 | 15 | 5:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | S22090200247 | New_Event | Primary Pole Failure | Include | Include | Equipment | 345 | 2022-09-02 | 5175 | keep | 0 | Sep | 2022 | 0.0035247 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-02 13:23 | 2022-09-02 13:24 | 437 | 0:01 | T | CABLE SOTERRADO AVERIADO | DISPARO AL CERRAR DEL SU-24 A SU-7 | R22090200060 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-09-02 | 437 | keep | 0 | Sep | 2022 | 0.00029764 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-02 13:24 | 2022-09-02 13:40 | 371 | 0:16 | P | CABLE SOTERRADO AVERIADO | SE DEJO ABIERTO SU-24 A SU-7 Y SU-7 A SU-24 SE CERRO N/O CONTRA 1658-14 EN SU-28 A SU-7 85% POR 1658-14 | R22090200060 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 16 | 2022-09-02 | 5936 | keep | 0 | Sep | 2022 | 0.004043 | 0.00025269 | Sustained | FALSE | FALSE | Not_TMED_Event | 371
UTUADO | 2022-09-02 13:44 | 2022-09-02 15:15 | 60 | 1:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090200065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-09-02 | 5460 | keep | 0 | Sep | 2022 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-02 13:50 | 2022-09-02 14:53 | 70 | 1:03 | P | DESGANCHE | 2X80 EN C/L | S22090200212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-09-02 | 4410 | keep | 0 | Sep | 2022 | 0.0030036 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-09-02 13:50 | 2022-09-02 15:49 | 4 | 1:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO CONDUCTOR SECUNDARIO (TRASPATIO) | S22090200252 | New_Event | Secondary Wire Break | Include | Include | Equipment | 119 | 2022-09-02 | 476 | keep | 0 | Sep | 2022 | 0.0003242 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-02 13:51 | 2022-09-02 15:49 | 2 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN XMR | S22090200253 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2022-09-02 | 236 | keep | 0 | Sep | 2022 | 0.00016074 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-09-02 14:23 | 2022-09-02 20:57 | 1 | 6:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | M22090200112 | New_Event | Cutout Failure | Include | Include | Equipment | 394 | 2022-09-02 | 394 | keep | 0 | Sep | 2022 | 0.00026835 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-02 14:43 | 2022-09-02 14:56 | 12 | 0:13 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | R22090200124 | New_Event | Animals | Include | Include | Wildlife | 13 | 2022-09-02 | 156 | keep | 0 | Sep | 2022 | 0.00010625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-09-02 14:45 | 2022-09-02 18:40 | 150 | 3:55 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22090200075 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 235 | 2022-09-02 | 35250 | keep | 0 | Sep | 2022 | 0.024009 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-09-02 14:46 | 2022-09-02 16:37 | 80 | 1:51 | P | ERROR HUMANO | 1 X 65 EN C/L PERSONAL CONTRATISTA (WTS) CRUZO LINEAS | R22090200125 | New_Event | Human Error | Include | Include | Other | 111 | 2022-09-02 | 8880 | keep | 0 | Sep | 2022 | 0.0060481 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-02 14:48 | 2022-09-02 17:49 | 59 | 3:01 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DEL ALIMENTADOR 1117-09 LLEVA 50% DE LA CARGA DEL 1115-02 | S22090200259 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2022-09-02 | 10679 | keep | 0 | Sep | 2022 | 0.0072734 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
SAN JUAN | 2022-09-02 14:48 | 2022-09-02 17:49 | 316 | 3:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DEL ALIMENTADOR 1117-09 LLEVA 50% DE LA CARGA DEL 1115-02 | S22090200259 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2022-09-02 | 57196 | keep | 0 | Sep | 2022 | 0.038956 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
UTUADO | 2022-09-02 14:56 | 2022-09-02 16:32 | 15 | 1:36 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090200077 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 96 | 2022-09-02 | 1440 | keep | 0 | Sep | 2022 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2022-09-02 14:57 | 2022-09-02 18:00 | 70 | 3:03 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090200135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-09-02 | 12810 | keep | 0 | Sep | 2022 | 0.0087248 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2022-09-02 15:07 | 2022-09-02 17:34 | 50 | 2:27 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22090200188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-09-02 | 7350 | keep | 0 | Sep | 2022 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-02 15:09 | 2022-09-02 16:57 | 40 | 1:48 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B22090200124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-09-02 | 4320 | keep | 0 | Sep | 2022 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-02 15:19 | 2022-09-02 17:38 | 50 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22090200128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2022-09-02 | 6950 | keep | 0 | Sep | 2022 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-09-02 15:22 | 2022-09-02 16:22 | 50 | 1:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090200121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2022-09-02 | 3000 | keep | 0 | Sep | 2022 | 0.0020433 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-02 15:27 | 2022-09-02 15:33 | 1202 | 0:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | CG-220902-01 VIA LIBRE DE EMERGENCIA REEMPLAZO DE AISLADOR QUEMADO EN TRONCAL OPERACIONES PARA NORMALIZAR | C22090200116 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 6 | 2022-09-02 | 7212 | keep | 0 | Sep | 2022 | 0.0049121 | 0.00081868 | Sustained | FALSE | FALSE | Not_TMED_Event | 1202
MAYAGÃœEZ | 2022-09-02 15:27 | 2022-09-02 15:28 | 637 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR LLEVA 6703-03 | M22090200123 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-02 | 637 | keep | 0 | Sep | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-09-02 15:27 | 2022-09-02 15:28 | 1491 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR CARGA POR 6703-02 | M22090200123 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-02 | 1491 | keep | 0 | Sep | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-09-02 15:28 | 2022-09-02 17:29 | 200 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090200130 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2022-09-02 | 24200 | keep | 0 | Sep | 2022 | 0.016483 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-09-02 15:31 | 2022-09-02 16:57 | 15 | 1:26 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | C22090200190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-09-02 | 1290 | keep | 0 | Sep | 2022 | 0.00087861 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-09-02 15:33 | 2022-09-02 20:57 | 50 | 5:24 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22090200146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2022-09-02 | 16200 | keep | 0 | Sep | 2022 | 0.011034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-09-02 15:40 | 2022-09-02 16:15 | 8 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22090200081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-09-02 | 280 | keep | 0 | Sep | 2022 | 0.00019071 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2022-09-02 15:58 | 2022-09-02 19:16 | 21 | 3:18 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50KVA POR 75 KVA | P22090200149 | New_Event | Service Transformer Failure | Include | Include | Equipment | 198 | 2022-09-02 | 4158 | keep | 0 | Sep | 2022 | 0.002832 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-09-02 16:00 | 2022-09-02 16:07 | 108 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22090200148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-02 | 756 | keep | 0 | Sep | 2022 | 0.00051491 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
MAYAGÃœEZ | 2022-09-02 16:00 | 2022-09-02 16:07 | 974 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 1500 | M22090200149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-02 | 6818 | keep | 0 | Sep | 2022 | 0.0046437 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2022-09-02 16:02 | 2022-09-02 17:41 | 50 | 1:39 | P | DESCONECTIVO DEFECTUOSO | 1 X 50 EN C/L PORTA FUSIBLE DEFECTUOSO | P22090200151 | New_Event | Switch Failure | Include | Include | Equipment | 99 | 2022-09-02 | 4950 | keep | 0 | Sep | 2022 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-09-02 16:02 | 2022-09-02 17:24 | 1 | 1:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | P22090200011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 82 | 2022-09-02 | 82 | keep | 0 | Sep | 2022 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-02 16:13 | 2022-09-02 17:49 | 130 | 1:36 | P | ANIMAL | 1X100 EN C/L SE RETIRO AVE | S22090200300 | New_Event | Animals | Include | Include | Wildlife | 96 | 2022-09-02 | 12480 | keep | 0 | Sep | 2022 | 0.0085001 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
MAYAGÃœEZ | 2022-09-02 16:15 | 2022-09-02 18:11 | 375 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090200152 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2022-09-02 | 43500 | keep | 0 | Sep | 2022 | 0.029628 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
MAYAGÃœEZ | 2022-09-02 16:49 | 2022-09-02 18:05 | 14 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090200166 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2022-09-02 | 1064 | keep | 0 | Sep | 2022 | 0.00072469 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-09-02 16:50 | 2022-09-02 18:55 | 20 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B22090200129 | New_Event | Primary Wire Break | Include | Include | Equipment | 125 | 2022-09-02 | 2500 | keep | 0 | Sep | 2022 | 0.0017027 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-09-02 16:51 | 2022-09-02 22:50 | 10 | 5:59 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 15KVA AVERIADO POR 37.5 KVA A 2.4KV | P22090200165 | New_Event | Service Transformer Failure | Include | Include | Equipment | 359 | 2022-09-02 | 3590 | keep | 0 | Sep | 2022 | 0.0024451 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-02 17:02 | 2022-09-02 22:41 | 30 | 5:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE REMPLAZO MACHETE | S22090200378 | New_Event | Primary Wire Break | Include | Include | Equipment | 339 | 2022-09-02 | 10170 | keep | 0 | Sep | 2022 | 0.0069267 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-09-02 17:17 | 2022-09-02 19:10 | 60 | 1:53 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 80 EN C/L CRUCE POR AVE | C22090200198 | New_Event | Animals | Include | Include | Wildlife | 113 | 2022-09-02 | 6780 | keep | 0 | Sep | 2022 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2022-09-02 17:20 | 2022-09-02 19:08 | 100 | 1:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M22090200089 | New_Event | Primary Wire Break | Include | Include | Equipment | 108 | 2022-09-02 | 10800 | keep | 0 | Sep | 2022 | 0.0073558 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-09-02 17:21 | 2022-09-03 13:12 | 10 | 19:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARO SECUNDARIA | R22090200155 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1191 | 2022-09-02 | 11910 | keep | 0 | Sep | 2022 | 0.0081118 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-09-02 17:25 | 2022-09-02 17:57 | 6 | 0:32 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE RETEZO LINEA ARRIADA | C22090200199 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 32 | 2022-09-02 | 192 | keep | 0 | Sep | 2022 | 0.00013077 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-09-02 17:27 | 2022-09-02 20:15 | 1000 | 2:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L SE REMPLAZO CAJA | B22090200132 | New_Event | Cutout Failure | Include | Include | Equipment | 168 | 2022-09-02 | 168000 | keep | 0 | Sep | 2022 | 0.11442 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
MAYAGÃœEZ | 2022-09-02 17:38 | 2022-09-02 22:30 | 20 | 4:52 | P | NO SE REPORTO CAUSA | SE REEMPLAZO 1X25 NX EN UN PM NO SE IDENTIFICO CAUSA | M22090200175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2022-09-02 | 5840 | keep | 0 | Sep | 2022 | 0.0039776 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-02 17:46 | 2022-09-02 18:26 | 8 | 0:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22090200202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2022-09-02 | 320 | keep | 0 | Sep | 2022 | 0.00021795 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-09-02 17:49 | 2022-09-02 20:33 | 59 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO MEDIANTE G.O.I. SJ-220902-01 - 50% DE SU CARGA TRANSFERIDA AL 1117-09 | S22090200259 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 164 | 2022-09-02 | 9676 | keep | 0 | Sep | 2022 | 0.0065903 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-02 17:49 | 2022-09-02 20:33 | 221 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO MEDIANTE G.O.I. SJ-220902-01 - LLEVA 50% DE LA CARGA DEL 1115-02 | S22090200259 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 164 | 2022-09-02 | 36244 | keep | 0 | Sep | 2022 | 0.024686 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-09-02 18:10 | 2022-09-02 19:40 | 10 | 1:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A22090200090 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2022-09-02 | 900 | keep | 0 | Sep | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-02 18:27 | 2022-09-02 20:06 | 50 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C22090200207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2022-09-02 | 4950 | keep | 0 | Sep | 2022 | 0.0033714 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-09-02 18:41 | 2022-09-02 18:53 | 10 | 0:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | R22090200160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2022-09-02 | 120 | keep | 0 | Sep | 2022 | 8.1731e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-09-02 19:01 | 2022-09-02 21:51 | 1 | 2:50 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22090200183 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 170 | 2022-09-02 | 170 | keep | 0 | Sep | 2022 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-09-02 19:16 | 2022-09-02 21:30 | 3744 | 2:14 | T | LINEA DE TRANSMISION 38KV | TERMINACION 38 KV AVERIADA ENTRADA TRANSFORMADOR 5004-00, SE TRANSFIERE CARGA A 5018-02 | P22090200197 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 134 | 2022-09-02 | 501696 | keep | 0 | Sep | 2022 | 0.3417 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2022-09-02 19:16 | 2022-09-02 22:15 | 2379 | 2:59 | T | LINEA DE TRANSMISION 38KV | TERMINACION 38 KV AVERIADA ENTRADA TRANSFORMADOR 5004-00,SE TRANSFIERE 5004-07 A 5016-01 POR BARRA DE INSPECCION | P22090200193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 179 | 2022-09-02 | 425841 | keep | 0 | Sep | 2022 | 0.29004 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-09-02 19:16 | 2022-09-02 21:15 | 778 | 1:59 | T | LINEA DE TRANSMISION 38KV | TERMINACION 38KV AVERIADA ENTRADA TRANSFORMADOR 5004-00, SE TRANSFGIERE 5004-08 A 5016-01 POR BARRA DE INSPECCION EN 5004-00 | P22090200195 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 119 | 2022-09-02 | 92582 | keep | 0 | Sep | 2022 | 0.063057 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2022-09-02 19:16 | 2022-09-02 21:08 | 1746 | 1:52 | T | LINEA DE TRANSMISION 38KV | TERMINACION 38 KV AVERIADA ENTRADA TRANSFORMADOR 5004-00, SE TRANSFIERE 5004-09 A 5018-04 EN MH 405 CALLE TORRES PONCE | P22090200196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 112 | 2022-09-02 | 195552 | keep | 0 | Sep | 2022 | 0.13319 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2022-09-02 19:16 | 2022-09-02 22:15 | 11 | 2:59 | T | LINEA DE TRANSMISION 38KV | TERMINACION 38 KV AVERIADA ENTRADA TRANSFORMADOR 5004-00, SE TRANSFIERE 5004-10 A 5016-01 POR BARRA DE INSPECCION DE 5004-00 | P22090200194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 179 | 2022-09-02 | 1969 | keep | 0 | Sep | 2022 | 0.0013411 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2022-09-02 19:17 | 2022-09-02 21:21 | 60 | 2:04 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22090200212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-09-02 | 7440 | keep | 0 | Sep | 2022 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-02 19:23 | 2022-09-02 22:10 | 6 | 2:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR BAJANTES SECUNDARIOS | M22090200186 | New_Event | Secondary Wire Break | Include | Include | Equipment | 167 | 2022-09-02 | 1002 | keep | 0 | Sep | 2022 | 0.00068246 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-09-02 19:35 | 2022-09-04 09:00 | 5 | 37:25 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | P22090200219 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2245 | 2022-09-02 | 11225 | keep | 0 | Sep | 2022 | 0.0076453 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-09-02 19:37 | 2022-09-02 23:00 | 10 | 3:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES SECUNDARIOS | A22090200099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 203 | 2022-09-02 | 2030 | keep | 0 | Sep | 2022 | 0.0013826 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2022-09-02 19:58 | 2022-09-02 19:59 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22090200100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 3431 | keep | 0 | Sep | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2022-09-02 19:59 | 2022-09-02 21:10 | 150 | 1:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22090200106 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 71 | 2022-09-02 | 10650 | keep | 0 | Sep | 2022 | 0.0072537 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-09-02 20:07 | 2022-09-02 22:30 | 100 | 2:23 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22090200164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2022-09-02 | 14300 | keep | 0 | Sep | 2022 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-09-02 20:36 | 2022-09-03 12:45 | 30 | 16:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22090200193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 969 | 2022-09-02 | 29070 | keep | 0 | Sep | 2022 | 0.019799 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-09-02 20:42 | 2022-09-02 23:12 | 17 | 2:30 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R22090200180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-09-02 | 2550 | keep | 0 | Sep | 2022 | 0.0017368 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2022-09-02 20:45 | 2022-09-02 23:58 | 40 | 3:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090200196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-09-02 | 7720 | keep | 0 | Sep | 2022 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-09-02 20:46 | 2022-09-02 23:36 | 25 | 2:50 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C22090200215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-09-02 | 4250 | keep | 0 | Sep | 2022 | 0.0028947 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-09-02 21:09 | 2022-09-03 11:18 | 22 | 14:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR Y 1 X 40 EN C/L SE REMPLAZO PORTAFUSIBLES | S22090200704 | New_Event | Cutout Failure | Include | Include | Equipment | 849 | 2022-09-02 | 18678 | keep | 0 | Sep | 2022 | 0.012722 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2022-09-02 21:09 | 2022-09-02 22:00 | 250 | 0:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | M22090200200 | New_Event | Cutout Failure | Include | Include | Equipment | 51 | 2022-09-02 | 12750 | keep | 0 | Sep | 2022 | 0.008684 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-09-02 21:26 | 2022-09-03 13:18 | 100 | 15:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA QUEMADA | S22090200070 | New_Event | Cutout Failure | Include | Include | Equipment | 952 | 2022-09-02 | 95200 | keep | 0 | Sep | 2022 | 0.06484 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-02 21:28 | 2022-09-03 01:32 | 11 | 4:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22090200707 | New_Event | Secondary Wire Break | Include | Include | Equipment | 244 | 2022-09-02 | 2684 | keep | 0 | Sep | 2022 | 0.0018281 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2022-09-02 21:30 | 2022-09-03 09:02 | 21 | 11:32 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR 50 KVA AVERIADO POR 75 KVA | P22090200149 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 692 | 2022-09-02 | 14532 | keep | 0 | Sep | 2022 | 0.0098977 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-02 21:32 | 2022-09-02 22:30 | 25 | 0:58 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S22090200716 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2022-09-02 | 1450 | keep | 0 | Sep | 2022 | 0.00098759 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-09-02 21:50 | 2022-09-02 21:51 | 2308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090200347 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 2308 | keep | 0 | Sep | 2022 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
BAYAMON | 2022-09-02 22:01 | 2022-09-03 02:54 | 80 | 4:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIA FUERTE | B22090200145 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 293 | 2022-09-02 | 23440 | keep | 0 | Sep | 2022 | 0.015965 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-09-02 22:04 | 2022-09-02 23:20 | 40 | 1:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090200224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-09-02 | 3040 | keep | 0 | Sep | 2022 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-09-02 22:11 | 2022-09-03 08:29 | 5 | 10:18 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P22090200301 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 618 | 2022-09-02 | 3090 | keep | 0 | Sep | 2022 | 0.0021046 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-09-02 22:37 | 2022-09-02 22:38 | 2859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 2859 | keep | 0 | Sep | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
PONCE | 2022-09-02 22:37 | 2022-09-03 00:28 | 2379 | 1:51 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE 5016-01 LLEVANDO CARGA DE 5004-07 SE REEMPLAZAROR TRES AISLADORES QUEMADOS | P22090200307 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 111 | 2022-09-02 | 264069 | keep | 0 | Sep | 2022 | 0.17986 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-09-02 22:37 | 2022-09-03 00:28 | 778 | 1:51 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE 5016-01 CON LA CARGA DE 5004-08, SE REEMPLAZARON TRES AISLADORES QUEMADOS | P22090200307 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 111 | 2022-09-02 | 86358 | keep | 0 | Sep | 2022 | 0.058818 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2022-09-02 22:37 | 2022-09-03 00:28 | 11 | 1:51 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE 5016-01 CON LA CARGA DE 5004-10, SE REEMPLAZARON TRES AISLADORES QUEMADOS | P22090200307 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 111 | 2022-09-02 | 1221 | keep | 0 | Sep | 2022 | 0.00083162 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2022-09-02 22:37 | 2022-09-03 00:28 | 2113 | 1:51 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE ALIMENTADOR LLEVANDO CARGA DE 5004-07,08,10, SE REEMPLAZARON TRES AISLADORES QUEMADOS | P22090200307 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 111 | 2022-09-02 | 234543 | keep | 0 | Sep | 2022 | 0.15975 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
SAN JUAN | 2022-09-02 22:44 | 2022-09-02 22:45 | 1573 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S22090200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-02 | 1573 | keep | 0 | Sep | 2022 | 0.0010714 | 0.0010714 | Momentary | FALSE | FALSE | Not_TMED_Event | 1573
FAJARDO | 2022-09-02 23:26 | 2022-09-03 13:47 | 15 | 14:21 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETESO LINEA | R22090200205 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 861 | 2022-09-02 | 12915 | keep | 0 | Sep | 2022 | 0.0087963 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-02 23:34 | 2022-09-03 08:35 | 100 | 9:01 | P | DESGANCHE | 2 X 100 EN AEREO 1 SMU-100 EN SU-4 Y DESGANCHE | S22090200723 | New_Event | Vegetation Contact | Include | Include | Vegetation | 541 | 2022-09-02 | 54100 | keep | 0 | Sep | 2022 | 0.036847 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-09-02 23:38 | 2022-09-02 23:40 | 1745 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR 15% POR 1646-03 SE CERRO POR CONTROL MAL TIEMPO LLUVIAS | R22090200208 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-02 | 3490 | keep | 0 | Sep | 2022 | 0.002377 | 0.0011885 | Momentary | FALSE | FALSE | Not_TMED_Event | 1745
CANOVANAS | 2022-09-03 00:07 | 2022-09-03 00:09 | 2580 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R22090300005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-03 | 5160 | keep | 0 | Sep | 2022 | 0.0035145 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2022-09-03 00:07 | 2022-09-03 00:09 | 500 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R22090300005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-03 | 1000 | keep | 0 | Sep | 2022 | 0.0006811 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2022-09-03 00:09 | 2022-09-03 00:10 | 2141 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090300001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 2141 | keep | 0 | Sep | 2022 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2022-09-03 00:11 | 2022-09-03 10:49 | 40 | 10:38 | P | DESGANCHE | 1X40 EN C/L | C22090300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 638 | 2022-09-03 | 25520 | keep | 0 | Sep | 2022 | 0.017382 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-03 00:17 | 2022-09-03 08:12 | 100 | 7:55 | P | DESGANCHE | 2 X 65 Y 1 X 100 EN CORTE DE LINEA BAMBUAS SOBRE FASE | R22090300006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2022-09-03 | 47500 | keep | 0 | Sep | 2022 | 0.032352 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-03 00:21 | 2022-09-03 00:22 | 2859 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090300003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 2859 | keep | 0 | Sep | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
CANOVANAS | 2022-09-03 00:23 | 2022-09-03 00:24 | 4085 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | R22090300010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 4085 | keep | 0 | Sep | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
BARRANQUITAS | 2022-09-03 00:23 | 2022-09-03 00:24 | 2859 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090300005 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 2859 | keep | 0 | Sep | 2022 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
VEGA BAJA | 2022-09-03 00:24 | 2022-09-03 00:25 | 652 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22090300005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-03 | 652 | keep | 0 | Sep | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-09-03 00:24 | 2022-09-03 00:25 | 2704 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B22090300005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-03 | 2704 | keep | 0 | Sep | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2022-09-03 00:29 | 2022-09-03 00:32 | 137 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 411 | keep | 0 | Sep | 2022 | 0.00027993 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-09-03 00:29 | 2022-09-03 00:32 | 760 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 2280 | keep | 0 | Sep | 2022 | 0.0015529 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2022-09-03 00:29 | 2022-09-03 00:32 | 1225 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 3675 | keep | 0 | Sep | 2022 | 0.002503 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-09-03 00:29 | 2022-09-03 00:32 | 1452 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 4356 | keep | 0 | Sep | 2022 | 0.0029669 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-09-03 00:29 | 2022-09-03 00:32 | 616 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 1848 | keep | 0 | Sep | 2022 | 0.0012587 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-09-03 00:29 | 2022-09-03 00:32 | 3432 | 0:03 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 BKR LLEVA 80% 1204-02 Y 10% 1204-03 | S22090300024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 10296 | keep | 0 | Sep | 2022 | 0.0070126 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-09-03 00:29 | 2022-09-03 00:32 | 552 | 0:03 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 BKR PORTATIL SOLO LLEVA 40% 1204-03 (10% POR 1204-02 Y 30% 1204-01) | S22090300024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 1656 | keep | 0 | Sep | 2022 | 0.0011279 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
CANOVANAS | 2022-09-03 00:43 | 2022-09-03 08:47 | 10 | 8:04 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE PRIMARIO | R22090300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 484 | 2022-09-03 | 4840 | keep | 0 | Sep | 2022 | 0.0032965 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-03 00:53 | 2022-09-03 12:56 | 40 | 12:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22090300034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 723 | 2022-09-03 | 28920 | keep | 0 | Sep | 2022 | 0.019697 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-09-03 00:55 | 2022-09-03 00:57 | 1825 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 1118-09 LLEVANDO 1118-08 SE CERRO POR SCADA LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-03 | 3650 | keep | 0 | Sep | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-09-03 00:55 | 2022-09-03 00:57 | 4398 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 1118-09 LLEVANDO 1118-08 SE CERRO POR SCADA LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-03 | 8796 | keep | 0 | Sep | 2022 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 849 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 13584 | keep | 0 | Sep | 2022 | 0.009252 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 893 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 14288 | keep | 0 | Sep | 2022 | 0.0097315 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 602 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 9632 | keep | 0 | Sep | 2022 | 0.0065603 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 43 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 688 | keep | 0 | Sep | 2022 | 0.00046859 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 1389 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 22224 | keep | 0 | Sep | 2022 | 0.015137 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 673 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH | S22090300049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 10095 | keep | 0 | Sep | 2022 | 0.0068757 | 0.00045838 | Sustained | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 372 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH | S22090300049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 5580 | keep | 0 | Sep | 2022 | 0.0038005 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 732 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH | S22090300049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 10980 | keep | 0 | Sep | 2022 | 0.0074784 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 637 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA BALDRICH | S22090300049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 9555 | keep | 0 | Sep | 2022 | 0.0065079 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 721 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 11536 | keep | 0 | Sep | 2022 | 0.0078571 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 325 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 5200 | keep | 0 | Sep | 2022 | 0.0035417 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 600 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 9600 | keep | 0 | Sep | 2022 | 0.0065385 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 267 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 4272 | keep | 0 | Sep | 2022 | 0.0029096 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 621 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300188 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 9936 | keep | 0 | Sep | 2022 | 0.0067674 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 2203 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 35248 | keep | 0 | Sep | 2022 | 0.024007 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 246 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 3936 | keep | 0 | Sep | 2022 | 0.0026808 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:16 | 9 | 0:16 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH 1424-08 LLEVA CARGA 1348-07 80% 1348-06 Y PARTE 1336-08 | S22090300173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 16 | 2022-09-03 | 144 | keep | 0 | Sep | 2022 | 9.8078e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 601 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 9015 | keep | 0 | Sep | 2022 | 0.0061401 | 0.00040934 | Sustained | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 640 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 9600 | keep | 0 | Sep | 2022 | 0.0065385 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 1699 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 25485 | keep | 0 | Sep | 2022 | 0.017358 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 892 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 13380 | keep | 0 | Sep | 2022 | 0.0091131 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-09-03 01:00 | 2022-09-03 01:15 | 1066 | 0:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BARRA BALDRICH | S22090300177 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 15 | 2022-09-03 | 15990 | keep | 0 | Sep | 2022 | 0.010891 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:19 | 137 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300171 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2022-09-03 | 2466 | keep | 0 | Sep | 2022 | 0.0016796 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:19 | 760 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300171 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2022-09-03 | 13680 | keep | 0 | Sep | 2022 | 0.0093174 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:19 | 1225 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2022-09-03 | 22050 | keep | 0 | Sep | 2022 | 0.015018 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:19 | 1452 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2022-09-03 | 26136 | keep | 0 | Sep | 2022 | 0.017801 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:19 | 616 | 0:18 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090300168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2022-09-03 | 11088 | keep | 0 | Sep | 2022 | 0.007552 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:19 | 3432 | 0:18 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 BKR LLEVA 80% 1204-02 Y 10% 1204-03 | S22090300024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2022-09-03 | 61776 | keep | 0 | Sep | 2022 | 0.042075 | 0.0023375 | Sustained | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:19 | 552 | 0:18 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 BKR PORTATIL SOLO LLEVA 40% 1204-03 (10% POR 1204-02 Y 30% 1204-01) | S22090300024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 18 | 2022-09-03 | 9936 | keep | 0 | Sep | 2022 | 0.0067674 | 0.00037596 | Sustained | FALSE | FALSE | Not_TMED_Event | 552
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:29 | 1681 | 0:28 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06 Y SU CARGA TRANSFERIDA AL 1303-05 | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 28 | 2022-09-03 | 47068 | keep | 0 | Sep | 2022 | 0.032058 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-09-03 01:01 | 2022-09-03 01:29 | 1598 | 0:28 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1303-04 LLEVANDO CARGA 1303-01 Y 1346-06 Y SU CARGA TRANSFERIDA AL 1303-05 | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 28 | 2022-09-03 | 44744 | keep | 0 | Sep | 2022 | 0.030475 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-09-03 01:03 | 2022-09-03 01:16 | 2000 | 0:13 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH 1424-08 LLEVA CARGA 1348-07 80% 1348-06 Y PARTE 1336-08 | S22090300173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2022-09-03 | 26000 | keep | 0 | Sep | 2022 | 0.017708 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
SAN JUAN | 2022-09-03 01:03 | 2022-09-03 01:16 | 1000 | 0:13 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV 1424-08 LLEVA CARGA 1348-07 80% 1348-06 Y PARTE 1336-08 | S22090300173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2022-09-03 | 13000 | keep | 0 | Sep | 2022 | 0.0088542 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2022-09-03 01:03 | 2022-09-03 01:16 | 278 | 0:13 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH 1424-08 LLEVA CARGA 1348-07 80% 1348-06 Y PARTE 1336-08 | S22090300173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 13 | 2022-09-03 | 3614 | keep | 0 | Sep | 2022 | 0.0024615 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
CAGUAS | 2022-09-03 01:03 | 2022-09-03 01:11 | 476 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-03 | 3808 | keep | 0 | Sep | 2022 | 0.0025936 | 0.0003242 | Sustained | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2022-09-03 01:03 | 2022-09-03 01:11 | 1655 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-03 | 13240 | keep | 0 | Sep | 2022 | 0.0090177 | 0.0011272 | Sustained | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-09-03 01:03 | 2022-09-03 01:11 | 361 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-03 | 2888 | keep | 0 | Sep | 2022 | 0.001967 | 0.00024588 | Sustained | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2022-09-03 01:03 | 2022-09-03 01:11 | 2842 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-03 | 22736 | keep | 0 | Sep | 2022 | 0.015485 | 0.0019357 | Sustained | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-09-03 01:03 | 2022-09-03 01:11 | 1702 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-03 | 13616 | keep | 0 | Sep | 2022 | 0.0092738 | 0.0011592 | Sustained | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-09-03 01:03 | 2022-09-03 01:11 | 918 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-03 | 7344 | keep | 0 | Sep | 2022 | 0.005002 | 0.00062525 | Sustained | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2022-09-03 01:03 | 2022-09-03 01:11 | 1725 | 0:08 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-03 | 13800 | keep | 0 | Sep | 2022 | 0.0093991 | 0.0011749 | Sustained | FALSE | FALSE | Not_TMED_Event | 1725
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 828 | 1:33 | P | LINEA DE TRANSMISION 115KV | DISPARO L-37900 60% POR 1206-04 | S22090300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 93 | 2022-09-03 | 77004 | keep | 0 | Sep | 2022 | 0.052447 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 1977 | 1:33 | P | LINEA DE TRANSMISION 115KV | DISPARO L-37900 40% POR 1206-04 | S22090300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 93 | 2022-09-03 | 183861 | keep | 0 | Sep | 2022 | 0.12523 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 8679 | 1:33 | P | LINEA DE TRANSMISION 115KV | DISPARO L-37900 85% POR 1206-03 | S22090300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 93 | 2022-09-03 | 807147 | keep | 0 | Sep | 2022 | 0.54974 | 0.0059112 | Sustained | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 338 | 1:33 | S | MAL TIEMPO/RAYOS | DISPARO ALTA DE TRANSFORMADOR RAYOS Y LLUVIA FUERTE | S22090300204 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2022-09-03 | 31434 | keep | 0 | Sep | 2022 | 0.02141 | 0.00023021 | Sustained | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 733 | 1:33 | S | MAL TIEMPO/RAYOS | DISPARO ALTA DE TRANSFORMADOR RAYOS Y LLUVIA FUERTE | S22090300204 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2022-09-03 | 68169 | keep | 0 | Sep | 2022 | 0.04643 | 0.00049924 | Sustained | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 4133 | 1:33 | S | MAL TIEMPO/RAYOS | DISPARO ALTA DE TRANSFORMADOR RAYOS Y LLUVIA FUERTE | S22090300204 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2022-09-03 | 384369 | keep | 0 | Sep | 2022 | 0.26179 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 1799 | 1:33 | S | MAL TIEMPO/RAYOS | DISPARO ALTA DE TRANSFORMADOR RAYOS Y LLUVIA FUERTE | S22090300204 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2022-09-03 | 167307 | keep | 0 | Sep | 2022 | 0.11395 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 02:37 | 487 | 1:33 | P | LINEA DE TRANSMISION 115KV | DISPARO L-37900 20% POR 1206-04 | S22090300000 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 93 | 2022-09-03 | 45291 | keep | 0 | Sep | 2022 | 0.030847 | 0.00033169 | Sustained | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-09-03 01:04 | 2022-09-03 01:05 | 390 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE MAL TIEMP RAYOS Y LLUVIA FUUERTE | S22090300049 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-03 | 390 | keep | 0 | Sep | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
HUMACAO | 2022-09-03 01:05 | 2022-09-03 01:08 | 989 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR SE CERRO POR CONTROL MAL TIEMPO LLUVIAS | C22090300007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-09-03 | 2967 | keep | 0 | Sep | 2022 | 0.0020208 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:23 | 1825 | 0:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090300201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-09-03 | 29200 | keep | 0 | Sep | 2022 | 0.019888 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:23 | 47 | 0:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090300201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-09-03 | 752 | keep | 0 | Sep | 2022 | 0.00051218 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:23 | 315 | 0:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090300201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-09-03 | 5040 | keep | 0 | Sep | 2022 | 0.0034327 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:23 | 2 | 0:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090300201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-09-03 | 32 | keep | 0 | Sep | 2022 | 2.1795e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:23 | 2391 | 0:16 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090300201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 16 | 2022-09-03 | 38256 | keep | 0 | Sep | 2022 | 0.026056 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:32 | 837 | 0:25 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220903-02 | S22090300409 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2022-09-03 | 20925 | keep | 0 | Sep | 2022 | 0.014252 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:32 | 908 | 0:25 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220903-02 | S22090300409 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2022-09-03 | 22700 | keep | 0 | Sep | 2022 | 0.015461 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-09-03 01:07 | 2022-09-03 01:32 | 97 | 0:25 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220903-02 | S22090300409 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2022-09-03 | 2425 | keep | 0 | Sep | 2022 | 0.0016517 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
SAN JUAN | 2022-09-03 01:16 | 2022-09-03 03:23 | 1000 | 2:07 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH PARTE POR 1424-08 | S22090300173 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 127 | 2022-09-03 | 127000 | keep | 0 | Sep | 2022 | 0.086499 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-03 01:16 | 2022-09-03 01:17 | 222 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 SE CERRO POR SCADA RAYOS Y LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-03 | 222 | keep | 0 | Sep | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-09-03 01:16 | 2022-09-03 01:17 | 4456 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 SE CERRO POR SCADA RAYOS Y LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-03 | 4456 | keep | 0 | Sep | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CAGUAS | 2022-09-03 01:16 | 2022-09-03 02:28 | 476 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-09-03 | 34272 | keep | 0 | Sep | 2022 | 0.023343 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-03 01:16 | 2022-09-03 02:28 | 1655 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-09-03 | 119160 | keep | 0 | Sep | 2022 | 0.081159 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-03 01:16 | 2022-09-03 02:28 | 361 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-09-03 | 25992 | keep | 0 | Sep | 2022 | 0.017703 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-03 01:16 | 2022-09-03 02:28 | 2842 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300011 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-09-03 | 204624 | keep | 0 | Sep | 2022 | 0.13937 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-03 01:16 | 2022-09-03 02:28 | 1702 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300014 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-09-03 | 122544 | keep | 0 | Sep | 2022 | 0.083464 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-03 01:16 | 2022-09-03 02:28 | 918 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300014 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-09-03 | 66096 | keep | 0 | Sep | 2022 | 0.045018 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-03 01:16 | 2022-09-03 02:28 | 1725 | 1:12 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C22090300015 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 72 | 2022-09-03 | 124200 | keep | 0 | Sep | 2022 | 0.084592 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 1000 | 2:06 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH 80% POR 1424-08 | S22090300173 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 126000 | keep | 0 | Sep | 2022 | 0.085818 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 278 | 2:06 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH SU CARGA POR 1424-08 | S22090300173 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 35028 | keep | 0 | Sep | 2022 | 0.023857 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:26 | 849 | 2:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 129 | 2022-09-03 | 109521 | keep | 0 | Sep | 2022 | 0.074594 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:26 | 893 | 2:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 129 | 2022-09-03 | 115197 | keep | 0 | Sep | 2022 | 0.07846 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:26 | 602 | 2:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 129 | 2022-09-03 | 77658 | keep | 0 | Sep | 2022 | 0.052893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:26 | 43 | 2:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 129 | 2022-09-03 | 5547 | keep | 0 | Sep | 2022 | 0.003778 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:26 | 1389 | 2:09 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 129 | 2022-09-03 | 179181 | keep | 0 | Sep | 2022 | 0.12204 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 673 | 2:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 84798 | keep | 0 | Sep | 2022 | 0.057756 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 372 | 2:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 46872 | keep | 0 | Sep | 2022 | 0.031924 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 732 | 2:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 92232 | keep | 0 | Sep | 2022 | 0.062819 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 637 | 2:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 80262 | keep | 0 | Sep | 2022 | 0.054666 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 2203 | 2:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 277578 | keep | 0 | Sep | 2022 | 0.18906 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 246 | 2:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 30996 | keep | 0 | Sep | 2022 | 0.021111 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:17 | 2022-09-03 03:23 | 9 | 2:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH | S22090300085 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 126 | 2022-09-03 | 1134 | keep | 0 | Sep | 2022 | 0.00077236 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-03 01:18 | 2022-09-03 01:19 | 5809 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | B22090300000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 5809 | keep | 0 | Sep | 2022 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2022-09-03 01:19 | 2022-09-03 09:30 | 93 | 8:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L SE REPORTA MAL TIEMPO FUERTES LLUVIAS | B22090300007 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 491 | 2022-09-03 | 45663 | keep | 0 | Sep | 2022 | 0.031101 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 627 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 11913 | keep | 0 | Sep | 2022 | 0.0081139 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 293 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 5567 | keep | 0 | Sep | 2022 | 0.0037917 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 761 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 14459 | keep | 0 | Sep | 2022 | 0.009848 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 451 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 8569 | keep | 0 | Sep | 2022 | 0.0058363 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:33 | 7 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR RAYOS Y LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-03 | 7 | keep | 0 | Sep | 2022 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:33 | 15 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR RAYOS Y LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-03 | 15 | keep | 0 | Sep | 2022 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 922 | 0:19 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 SU CARGA POR 1401-08 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 17518 | keep | 0 | Sep | 2022 | 0.011931 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 837 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 15903 | keep | 0 | Sep | 2022 | 0.010831 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 908 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 17252 | keep | 0 | Sep | 2022 | 0.01175 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 135 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 2565 | keep | 0 | Sep | 2022 | 0.001747 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 1 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 19 | keep | 0 | Sep | 2022 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 1295 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 24605 | keep | 0 | Sep | 2022 | 0.016758 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 1498 | 0:19 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1310-04 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 28462 | keep | 0 | Sep | 2022 | 0.019385 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:51 | 766 | 0:19 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1310-03 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 14554 | keep | 0 | Sep | 2022 | 0.0099127 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
SAN JUAN | 2022-09-03 01:32 | 2022-09-03 01:33 | 771 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO SU CARGA POR 1327-09 MAL TIEMPO LLUVIA | S22090300000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 771 | keep | 0 | Sep | 2022 | 0.00052512 | 0.00052512 | Momentary | FALSE | FALSE | Not_TMED_Event | 771
SAN JUAN | 2022-09-03 01:33 | 2022-09-03 10:44 | 11 | 9:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22090200707 | New_Event | Secondary Wire Break | Include | Include | Equipment | 551 | 2022-09-03 | 6061 | keep | 0 | Sep | 2022 | 0.0041281 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-09-03 01:34 | 2022-09-03 01:41 | 1106 | 0:07 | P | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1529-15 LLEVANDO 60% 1346-02 SE CERRO POR SCADA RAYOS Y LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 7 | 2022-09-03 | 7742 | keep | 0 | Sep | 2022 | 0.005273 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-09-03 01:34 | 2022-09-03 01:41 | 1802 | 0:07 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1529-15 LLEVANDO 60% 1346-02 SE CERRO POR SCADA RAYOS Y LLUVIA FUERTE | S22090300000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 7 | 2022-09-03 | 12614 | keep | 0 | Sep | 2022 | 0.0085913 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-09-03 01:34 | 2022-09-03 01:41 | 1310 | 0:07 | T | MAL TIEMPO/RAYOS | SE CERRO POR SCADA RAYOS Y LLUVIA FUERTE | S22090300127 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 7 | 2022-09-03 | 9170 | keep | 0 | Sep | 2022 | 0.0062456 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2022-09-03 01:35 | 2022-09-03 01:54 | 164 | 0:19 | T | LINEA DE TRANSMISION 38KV | DISPARO L-8900 SU CARGA POR 1531-02 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 3116 | keep | 0 | Sep | 2022 | 0.0021223 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2022-09-03 01:35 | 2022-09-03 01:54 | 427 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 8113 | keep | 0 | Sep | 2022 | 0.0055257 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2022-09-03 01:35 | 2022-09-03 01:54 | 716 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 13604 | keep | 0 | Sep | 2022 | 0.0092656 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2022-09-03 01:35 | 2022-09-03 01:54 | 867 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 16473 | keep | 0 | Sep | 2022 | 0.01122 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2022-09-03 01:35 | 2022-09-03 01:54 | 353 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090300204 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2022-09-03 | 6707 | keep | 0 | Sep | 2022 | 0.0045681 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
BARRANQUITAS | 2022-09-03 01:45 | 2022-09-03 07:09 | 1834 | 5:24 | T | TERMINACION SOTERRADA AVERIADA | DISPARO BKR 3501-02 QUE LLEVA LA CARGA DEL 3501-03. SE SECCIONALIZO PARA LEVANTAR ALAMBRE PRIMARIO PARTIDO SOBRE CRUCETA ENTRO 70% EN SERVICIO | C22090300019 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 324 | 2022-09-03 | 594216 | keep | 0 | Sep | 2022 | 0.40472 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-09-03 01:45 | 2022-09-03 05:03 | 1437 | 3:18 | T | TERMINACION SOTERRADA AVERIADA | DISPARO BKR 3501-02 QUE LLEVA LA CARGA DEL 3501-03. LA CARGA DEL 3501-03 SE NORMALIZO POR SU BKR Y ENTRO EN SERVICIO. | C22090300019 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 198 | 2022-09-03 | 284526 | keep | 0 | Sep | 2022 | 0.19379 | 0.00097873 | Sustained | FALSE | FALSE | Not_TMED_Event | 1437
SAN JUAN | 2022-09-03 01:47 | 2022-09-03 03:35 | 681 | 1:48 | T | DESGANCHE | SE CERRO INTERRUPTOR SECCIONALIZANDO ALIMENTADOR 30% EN SERVICIO | S22090300150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-09-03 | 73548 | keep | 0 | Sep | 2022 | 0.050093 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2022-09-03 01:47 | 2022-09-03 12:47 | 120 | 11:00 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S22090300148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 660 | 2022-09-03 | 79200 | keep | 0 | Sep | 2022 | 0.053943 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-09-03 01:51 | 2022-09-03 05:34 | 837 | 3:43 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220903-02 | S22090300409 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-09-03 | 186651 | keep | 0 | Sep | 2022 | 0.12713 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:51 | 2022-09-03 05:34 | 908 | 3:43 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-09 SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220903-02 | S22090300409 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 223 | 2022-09-03 | 202484 | keep | 0 | Sep | 2022 | 0.13791 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 01:51 | 2022-09-03 03:12 | 97 | 1:21 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220903-02 | S22090300409 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 81 | 2022-09-03 | 7857 | keep | 0 | Sep | 2022 | 0.0053514 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-09-03 02:00 | 2022-09-03 09:03 | 2379 | 7:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR CON LA CARGA DE 5004-07,5004-08,5004-10, SE TRANSFIERE 5004-07 A 5018-02 POR BARRA DE INSPECCION DE 5004-00 A TRAVES DE 5004-06 | P22090300086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 423 | 2022-09-03 | 1006317 | keep | 0 | Sep | 2022 | 0.6854 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-09-03 02:00 | 2022-09-03 05:11 | 778 | 3:11 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR CON LA CARGA DE 5004-07,5004-08,5004-10 | P22090300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-09-03 | 148598 | keep | 0 | Sep | 2022 | 0.10121 | 0.00052989 | Sustained | FALSE | FALSE | Not_TMED_Event | 778
PONCE | 2022-09-03 02:00 | 2022-09-03 06:29 | 11 | 4:29 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR CON LA CARGA DE 5004-07,5004-08,5004-10 | P22090300087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2022-09-03 | 2959 | keep | 0 | Sep | 2022 | 0.0020154 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2022-09-03 02:00 | 2022-09-03 05:11 | 2113 | 3:11 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR CON LA CARGA DE 5004-07,5004-08,5004-10 | P22090300024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-09-03 | 403583 | keep | 0 | Sep | 2022 | 0.27488 | 0.0014392 | Sustained | FALSE | FALSE | Not_TMED_Event | 2113
VEGA BAJA | 2022-09-03 02:11 | 2022-09-03 02:14 | 3387 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO INTERRUPTOR 9004-08 SE CERRO POR CONTROL RAYOS Y LLUVIA FUERTE | B22090300010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-09-03 | 10161 | keep | 0 | Sep | 2022 | 0.0069206 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
CANOVANAS | 2022-09-03 02:13 | 2022-09-03 08:44 | 50 | 6:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R22090300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 391 | 2022-09-03 | 19550 | keep | 0 | Sep | 2022 | 0.013315 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-03 02:18 | 2022-09-03 04:55 | 100 | 2:37 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYOS Y LLUVIA FUERTE | B22090300011 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 157 | 2022-09-03 | 15700 | keep | 0 | Sep | 2022 | 0.010693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-09-03 02:39 | 2022-09-03 09:25 | 12 | 6:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | R22090300036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 406 | 2022-09-03 | 4872 | keep | 0 | Sep | 2022 | 0.0033183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-09-03 02:45 | 2022-09-03 10:53 | 150 | 8:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L SE REMPLAZO PORTAFUSIBLE | C22090300036 | New_Event | Cutout Failure | Include | Include | Equipment | 488 | 2022-09-03 | 73200 | keep | 0 | Sep | 2022 | 0.049856 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2022-09-03 02:54 | 2022-09-03 02:55 | 1571 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 1571 | keep | 0 | Sep | 2022 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
BAYAMON | 2022-09-03 03:05 | 2022-09-03 08:38 | 80 | 5:33 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B22090300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2022-09-03 | 26640 | keep | 0 | Sep | 2022 | 0.018144 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 04:27 | 72 | 1:15 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC 5% POR 1404-07 | S22090300404 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 75 | 2022-09-03 | 5400 | keep | 0 | Sep | 2022 | 0.0036779 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 04:27 | 143 | 1:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV HATO REY TC | S22090300404 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 75 | 2022-09-03 | 10725 | keep | 0 | Sep | 2022 | 0.0073047 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 04:27 | 1357 | 1:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV HATO REY TC | S22090300404 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 75 | 2022-09-03 | 101775 | keep | 0 | Sep | 2022 | 0.069318 | 0.00092425 | Sustained | FALSE | FALSE | Not_TMED_Event | 1357
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 04:27 | 328 | 1:15 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV HATO REY TC | S22090300404 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 75 | 2022-09-03 | 24600 | keep | 0 | Sep | 2022 | 0.016755 | 0.0002234 | Sustained | FALSE | FALSE | Not_TMED_Event | 328
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 04:27 | 388 | 1:15 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA 38 KV HATO REY TC | S22090300404 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 75 | 2022-09-03 | 29100 | keep | 0 | Sep | 2022 | 0.01982 | 0.00026427 | Sustained | FALSE | FALSE | Not_TMED_Event | 388
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:36 | 23 | 0:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2022-09-03 | 552 | keep | 0 | Sep | 2022 | 0.00037596 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:36 | 530 | 0:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2022-09-03 | 12720 | keep | 0 | Sep | 2022 | 0.0086635 | 0.00036098 | Sustained | FALSE | FALSE | Not_TMED_Event | 530
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:36 | 37 | 0:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2022-09-03 | 888 | keep | 0 | Sep | 2022 | 0.00060481 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:36 | 929 | 0:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2022-09-03 | 22296 | keep | 0 | Sep | 2022 | 0.015186 | 0.00063274 | Sustained | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:36 | 21 | 0:24 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2022-09-03 | 504 | keep | 0 | Sep | 2022 | 0.00034327 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 04:27 | 4 | 1:15 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA HATO REY TC SU CARGA POR 1404-09 | S22090300404 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 75 | 2022-09-03 | 300 | keep | 0 | Sep | 2022 | 0.00020433 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:36 | 533 | 0:24 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH SU CARGA POR 1414-04 | S22090300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2022-09-03 | 12792 | keep | 0 | Sep | 2022 | 0.0087126 | 0.00036302 | Sustained | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:36 | 451 | 0:24 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA BALDRICH SU CARGA POR 1414-04 | S22090300000 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 24 | 2022-09-03 | 10824 | keep | 0 | Sep | 2022 | 0.0073722 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:26 | 721 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-09-03 | 10094 | keep | 0 | Sep | 2022 | 0.006875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:26 | 325 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-09-03 | 4550 | keep | 0 | Sep | 2022 | 0.003099 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:26 | 600 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-09-03 | 8400 | keep | 0 | Sep | 2022 | 0.0057212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:26 | 267 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-09-03 | 3738 | keep | 0 | Sep | 2022 | 0.0025459 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:26 | 621 | 0:14 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | Partial_restoration | Transmission Substation Bus Outage | Include | Include | Power supply | 14 | 2022-09-03 | 8694 | keep | 0 | Sep | 2022 | 0.0059214 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:35 | 34 | 0:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 23 | 2022-09-03 | 782 | keep | 0 | Sep | 2022 | 0.00053262 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:35 | 19 | 0:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 23 | 2022-09-03 | 437 | keep | 0 | Sep | 2022 | 0.00029764 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:35 | 514 | 0:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 23 | 2022-09-03 | 11822 | keep | 0 | Sep | 2022 | 0.0080519 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:35 | 752 | 0:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 23 | 2022-09-03 | 17296 | keep | 0 | Sep | 2022 | 0.01178 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2022-09-03 03:12 | 2022-09-03 03:35 | 68 | 0:23 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38 KV HATO REY TC | S22090300375 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 23 | 2022-09-03 | 1564 | keep | 0 | Sep | 2022 | 0.0010652 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2022-09-03 03:12 | 2022-09-03 03:35 | 37 | 0:23 | T | LINEA DE TRANSMISION 38KV | DISPARO L-6800 SU CARGA POR 1512-05 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-09-03 | 851 | keep | 0 | Sep | 2022 | 0.00057961 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2022-09-03 03:12 | 2022-09-03 09:15 | 30 | 6:03 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22090300017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 363 | 2022-09-03 | 10890 | keep | 0 | Sep | 2022 | 0.0074171 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-03 03:23 | 2022-09-03 07:24 | 92 | 4:01 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | S22090300300 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 241 | 2022-09-03 | 22172 | keep | 0 | Sep | 2022 | 0.015101 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
VEGA BAJA | 2022-09-03 03:24 | 2022-09-03 08:58 | 350 | 5:34 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE A ENTRADA DE MACHETE | A22090300004 | New_Event | Primary Wire Break | Include | Include | Equipment | 334 | 2022-09-03 | 116900 | keep | 0 | Sep | 2022 | 0.07962 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
PONCE | 2022-09-03 03:25 | 2022-09-03 03:28 | 1979 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | P22090200047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-03 | 5937 | keep | 0 | Sep | 2022 | 0.0040437 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
FAJARDO | 2022-09-03 03:33 | 2022-09-03 10:38 | 200 | 7:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN PROVISIONAL 1 X 10 EN RISER 2 X 50 EN CORTE DE LINEA 2 X 10 EN TRANSFORMADOR 2 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22090300042 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 425 | 2022-09-03 | 85000 | keep | 0 | Sep | 2022 | 0.057893 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-09-03 03:35 | 2022-09-03 03:49 | 476 | 0:14 | P | DESGANCHE | DISPARO DE INTERRUPTOR AL CERRAR MACHETES SECCIONALIZANDO ALIMENTADOR | S22090300150 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 14 | 2022-09-03 | 6664 | keep | 0 | Sep | 2022 | 0.0045388 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 03:49 | 2022-09-03 03:51 | 681 | 0:02 | T | DESGANCHE | SE SECIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 30% EN SERVICIO | S22090300150 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-09-03 | 1362 | keep | 0 | Sep | 2022 | 0.00092765 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 03:51 | 2022-09-03 04:03 | 476 | 0:12 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO MACHETES 40% EN SERVICIO | S22090300150 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 12 | 2022-09-03 | 5712 | keep | 0 | Sep | 2022 | 0.0038904 | 0.0003242 | Sustained | FALSE | FALSE | Not_TMED_Event | 476
SAN JUAN | 2022-09-03 04:03 | 2022-09-03 09:30 | 409 | 5:27 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO Y SE CERRO MACHETES 100% EN SERVICIO | S22090300150 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 327 | 2022-09-03 | 133743 | keep | 0 | Sep | 2022 | 0.091092 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-09-03 04:03 | 2022-09-03 09:10 | 60 | 5:07 | P | ANIMAL | 1 X 30 1 X 20 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR SE RETIRO NIDO PICHONES CRUZANDO FASE | R22090300048 | New_Event | Animals | Include | Include | Wildlife | 307 | 2022-09-03 | 18420 | keep | 0 | Sep | 2022 | 0.012546 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-03 04:18 | 2022-09-03 07:23 | 75 | 3:05 | P | MAL TIEMPO/RAYOS | 1 X 80 Y 1 X 100 EN C/L RAYOS | B22090300032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 185 | 2022-09-03 | 13875 | keep | 0 | Sep | 2022 | 0.0094502 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2022-09-03 04:24 | 2022-09-03 12:41 | 20 | 8:17 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | C22090300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2022-09-03 | 9940 | keep | 0 | Sep | 2022 | 0.0067701 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-03 04:27 | 2022-09-03 05:34 | 97 | 1:07 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE SECCIONALIZO Y SE CERRO POR SCADA SJ-220903-02 | S22090300409 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-09-03 | 6499 | keep | 0 | Sep | 2022 | 0.0044264 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-03 04:28 | 2022-09-03 11:06 | 200 | 6:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | B22090300036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 398 | 2022-09-03 | 79600 | keep | 0 | Sep | 2022 | 0.054215 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-09-03 04:31 | 2022-09-03 11:06 | 75 | 6:35 | P | DESGANCHE | 2 X 65 EN C/L SE DESGANCHO | B22090300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 395 | 2022-09-03 | 29625 | keep | 0 | Sep | 2022 | 0.020177 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2022-09-03 04:31 | 2022-09-03 14:15 | 200 | 9:44 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO AVERIA Y SE TRANSFIRIO LOS CLIENTES AL ALIMENTADOR 7201-05 | M22090300008 | New_Event | Primary Wire Break | Include | Include | Equipment | 584 | 2022-09-03 | 116800 | keep | 0 | Sep | 2022 | 0.079552 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-09-03 05:23 | 2022-09-03 09:59 | 50 | 4:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22090300058 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 276 | 2022-09-03 | 13800 | keep | 0 | Sep | 2022 | 0.0093991 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-03 05:26 | 2022-09-03 11:23 | 73 | 5:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L SE REPORTA MAL TIEMPO FUERTES LLUVIAS | B22090300044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 357 | 2022-09-03 | 26061 | keep | 0 | Sep | 2022 | 0.01775 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2022-09-03 05:34 | 2022-09-03 06:19 | 272 | 0:45 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE SECCIONALIZO NUEVAMENTE Y SE CERRO MACHETES SJ-220903-02 | S22090300409 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 45 | 2022-09-03 | 12240 | keep | 0 | Sep | 2022 | 0.0083366 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-03 05:36 | 2022-09-03 05:39 | 2126 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR SE CERRO POR CONTROL MAL TIEMPO LLUVIAS | C22090300104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-09-03 | 6378 | keep | 0 | Sep | 2022 | 0.004344 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2022-09-03 05:44 | 2022-09-03 06:47 | 293 | 1:03 | S | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLES EN LA ALTA DE LA SUBESTACION CDS NO REPORTO CAUSA | S22090300204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-09-03 | 18459 | keep | 0 | Sep | 2022 | 0.012572 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2022-09-03 05:44 | 2022-09-03 06:47 | 315 | 1:03 | S | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLES EN LA ALTA DE LA SUBESTACION CDS NO REPORTO CAUSA | S22090300204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-09-03 | 19845 | keep | 0 | Sep | 2022 | 0.013516 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2022-09-03 05:44 | 2022-09-03 06:47 | 216 | 1:03 | S | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLES EN LA ALTA DE LA SUBESTACION CDS NO REPORTO CAUSA | S22090300204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-09-03 | 13608 | keep | 0 | Sep | 2022 | 0.0092683 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2022-09-03 05:44 | 2022-09-03 06:47 | 1310 | 1:03 | S | NO SE REPORTO CAUSA | SE REMPLAZO FUSIBLES EN LA ALTA DE LA SUBESTACION CDS NO REPORTO CAUSA | S22090300204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2022-09-03 | 82530 | keep | 0 | Sep | 2022 | 0.056211 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
HUMACAO | 2022-09-03 05:44 | 2022-09-03 05:45 | 2450 | 0:01 | T | ANIMAL | RECIERRE | C22090300106 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-03 | 2450 | keep | 0 | Sep | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
SAN JUAN | 2022-09-03 05:45 | 2022-09-03 18:04 | 85 | 12:19 | P | TERMINACION SOTERRADA AVERIADA | 1 X 80 RBA SU-1 SE REMPLAZO TERMINACION EN RISER HACIA T-4 | S22090300481 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 739 | 2022-09-03 | 62815 | keep | 0 | Sep | 2022 | 0.042783 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
HUMACAO | 2022-09-03 05:45 | 2022-09-03 08:41 | 80 | 2:56 | P | ANIMAL | 1X100 EN C/L POR CRUCE DE AVE | C22090300112 | 1st_after_momentary | Animals | Include | Include | Wildlife | 176 | 2022-09-03 | 14080 | keep | 0 | Sep | 2022 | 0.0095898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-09-03 05:48 | 2022-09-03 05:49 | 1105 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22090300031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 1105 | keep | 0 | Sep | 2022 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
HUMACAO | 2022-09-03 05:54 | 2022-09-03 12:17 | 100 | 6:23 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | C22090300110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2022-09-03 | 38300 | keep | 0 | Sep | 2022 | 0.026086 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-03 05:59 | 2022-09-03 09:23 | 80 | 3:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M22090300010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 204 | 2022-09-03 | 16320 | keep | 0 | Sep | 2022 | 0.011115 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-03 06:12 | 2022-09-03 12:59 | 32 | 6:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN PROVISIONAL | S22090300495 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 407 | 2022-09-03 | 13024 | keep | 0 | Sep | 2022 | 0.0088706 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2022-09-03 06:15 | 2022-09-03 11:32 | 65 | 5:17 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN PROVISIONAL SE LEVANTO PRIMARIA | S22090300497 | New_Event | Primary Wire Break | Include | Include | Equipment | 317 | 2022-09-03 | 20605 | keep | 0 | Sep | 2022 | 0.014034 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2022-09-03 06:18 | 2022-09-03 12:00 | 70 | 5:42 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A22090300038 | New_Event | Primary Wire Break | Include | Include | Equipment | 342 | 2022-09-03 | 23940 | keep | 0 | Sep | 2022 | 0.016305 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-09-03 06:19 | 2022-09-03 06:20 | 760 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S22090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 760 | keep | 0 | Sep | 2022 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2022-09-03 06:19 | 2022-09-03 06:50 | 91 | 0:31 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-09 SE SE PATRULLO NO SE VIO NADA ADICIONAL Y SE CERRO ULTIMO 10% NO CAUSA APARENTE SJ-220903-02 | S22090300409 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 31 | 2022-09-03 | 2821 | keep | 0 | Sep | 2022 | 0.0019214 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 06:20 | 2022-09-03 13:44 | 80 | 7:24 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22090300606 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 444 | 2022-09-03 | 35520 | keep | 0 | Sep | 2022 | 0.024193 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-09-03 06:21 | 2022-09-03 11:00 | 11 | 4:39 | P | ARBOL SOBRE LINEA | 1 X 10 EN TRANSFORMADOR SE RETIRO ARBOL DE LINEA PRIMARIA | P22090300102 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 279 | 2022-09-03 | 3069 | keep | 0 | Sep | 2022 | 0.0020903 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-09-03 06:23 | 2022-09-03 10:00 | 300 | 3:37 | P | DESGANCHE | 1 X 100 EN C/L SE RETIRO BAMBUA | B22090300050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-09-03 | 65100 | keep | 0 | Sep | 2022 | 0.044339 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-09-03 06:41 | 2022-09-03 11:21 | 40 | 4:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22090300071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 280 | 2022-09-03 | 11200 | keep | 0 | Sep | 2022 | 0.0076283 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-03 06:46 | 2022-09-03 06:47 | 5630 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO MAL TIEMPO LLUVIAS | C22090300117 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 5630 | keep | 0 | Sep | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
CANOVANAS | 2022-09-03 06:50 | 2022-09-03 14:33 | 50 | 7:43 | P | DESGANCHE | 1 X 50, 1 X 15 Y 2 X 10 EN CORTE DE LINEA Y TRANSFORMADORES DESGANCHE PRIMARIO | R22090300078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2022-09-03 | 23150 | keep | 0 | Sep | 2022 | 0.015767 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-03 06:56 | 2022-09-03 10:00 | 40 | 3:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22090300059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2022-09-03 | 7360 | keep | 0 | Sep | 2022 | 0.0050129 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-03 07:06 | 2022-09-03 08:45 | 8 | 1:39 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE | R22090300086 | New_Event | Animals | Include | Include | Wildlife | 99 | 2022-09-03 | 792 | keep | 0 | Sep | 2022 | 0.00053943 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-09-03 07:09 | 2022-09-03 08:27 | 550 | 1:18 | P | TERMINACION SOTERRADA AVERIADA | SE LEVANTO ALAMBRE PRIMARIO PARTIDO DE CRUCETA MEDIANTE G.O.I. CG-220903-01 - QUEDAN 125 PERSONAS FUERA POR AVERIA SOTERRADA SE REFIRIO A SOTERRADO. | C22090300019 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 78 | 2022-09-03 | 42900 | keep | 0 | Sep | 2022 | 0.029219 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-09-03 07:12 | 2022-09-03 10:27 | 60 | 3:15 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA POR BAJANTE PEGANDO A POSTE | A22090300048 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 195 | 2022-09-03 | 11700 | keep | 0 | Sep | 2022 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-03 07:12 | 2022-09-03 12:15 | 1 | 5:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22090300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 303 | 2022-09-03 | 303 | keep | 0 | Sep | 2022 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-03 07:19 | 2022-09-03 07:20 | 837 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE CERRO POR SCADA | S22090300409 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 837 | keep | 0 | Sep | 2022 | 0.00057008 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 07:19 | 2022-09-03 07:20 | 908 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE CERRO POR SCADA | S22090300409 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 908 | keep | 0 | Sep | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-09-03 07:19 | 2022-09-03 07:20 | 97 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06 Y 20% 1404-9 SE CERRO POR SCADA | S22090300000 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 97 | keep | 0 | Sep | 2022 | 6.6066e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-03 07:19 | 2022-09-03 20:40 | 27 | 13:21 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S22090300541 | New_Event | Vegetation Contact | Include | Include | Vegetation | 801 | 2022-09-03 | 21627 | keep | 0 | Sep | 2022 | 0.01473 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2022-09-03 07:24 | 2022-09-03 11:00 | 20 | 3:36 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO FASE | R22090300089 | New_Event | Animals | Include | Include | Wildlife | 216 | 2022-09-03 | 4320 | keep | 0 | Sep | 2022 | 0.0029423 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-03 07:24 | 2022-09-03 07:25 | 3957 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO Y SE CERRO POR SCADA MAL TIEMPO LLUVIA | S22090300000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-03 | 3957 | keep | 0 | Sep | 2022 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2022-09-03 07:25 | 2022-09-03 13:00 | 1 | 5:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN MONTURA SE REMPLAZO CAJA | S22090300594 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2022-09-03 | 335 | keep | 0 | Sep | 2022 | 0.00022817 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-03 07:25 | 2022-09-03 13:22 | 92 | 5:57 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | S22090300300 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 357 | 2022-09-03 | 32844 | keep | 0 | Sep | 2022 | 0.02237 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-03 07:33 | 2022-09-03 10:29 | 3 | 2:56 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR DESGANCHE SECUNDARIO | C22090300129 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 176 | 2022-09-03 | 528 | keep | 0 | Sep | 2022 | 0.00035962 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-09-03 07:34 | 2022-09-03 11:08 | 7 | 3:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22090300063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2022-09-03 | 1498 | keep | 0 | Sep | 2022 | 0.0010203 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2022-09-03 07:45 | 2022-09-03 07:46 | 1026 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | R22090300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-09-03 | 1026 | keep | 0 | Sep | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2022-09-03 07:46 | 2022-09-03 10:17 | 1 | 2:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPPLAZO AISLADOR Y PUENTE DE LINEA A CAJA DE TRANSFORMADOR | R22090300137 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 151 | 2022-09-03 | 151 | keep | 0 | Sep | 2022 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-03 07:54 | 2022-09-03 09:51 | 15 | 1:57 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR RAYOS | S22090300566 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-09-03 | 1755 | keep | 0 | Sep | 2022 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-09-03 07:54 | 2022-09-03 14:20 | 100 | 6:26 | P | ARBOL SOBRE LINEA | 1 X 80 Y 1 X 100 EN C/L SE REEMPLAZO AISLADOR PRIMARIO Y SE RETIRO ARBOL SOBRE LINEA | C22090300133 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 386 | 2022-09-03 | 38600 | keep | 0 | Sep | 2022 | 0.02629 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-09-03 07:56 | 2022-09-03 09:07 | 100 | 1:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | A22090300058 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2022-09-03 | 7100 | keep | 0 | Sep | 2022 | 0.0048358 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-03 08:04 | 2022-09-03 09:43 | 8 | 1:39 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | C22090300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2022-09-03 | 792 | keep | 0 | Sep | 2022 | 0.00053943 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2022-09-03 08:11 | 2022-09-03 08:12 | 1185 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A22090300063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 1185 | keep | 0 | Sep | 2022 | 0.0008071 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
AGUADILLA | 2022-09-03 08:17 | 2022-09-03 12:31 | 10 | 4:14 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINE POR LINEA CRUZADA | A22090300067 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 254 | 2022-09-03 | 2540 | keep | 0 | Sep | 2022 | 0.00173 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-09-03 08:27 | 2022-09-03 20:54 | 125 | 12:27 | P | TERMINACION SOTERRADA AVERIADA | SE REPARRO 3 TERMINACIONES TIPO PISTOLA Y REEMPLAZO DE CAJAS SECAS 100% EN SERVICIO | C22090300019 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 747 | 2022-09-03 | 93375 | keep | 0 | Sep | 2022 | 0.063597 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-03 08:36 | 2022-09-03 10:43 | 12 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M22090200221 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2022-09-03 | 1524 | keep | 0 | Sep | 2022 | 0.001038 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-09-03 08:37 | 2022-09-03 08:38 | 5062 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R22090300130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 5062 | keep | 0 | Sep | 2022 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
YAUCO | 2022-09-03 08:38 | 2022-09-03 11:55 | 400 | 3:17 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-09-03 | 78800 | keep | 0 | Sep | 2022 | 0.05367 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
ARECIBO | 2022-09-03 08:38 | 2022-09-03 12:22 | 150 | 3:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR LLUVIAS | A22090300083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 224 | 2022-09-03 | 33600 | keep | 0 | Sep | 2022 | 0.022885 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2022-09-03 08:39 | 2022-09-03 10:47 | 3 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 5 EN TRANSFORMADOR SE LEVANTO SECUNDARIA | R22090300131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2022-09-03 | 384 | keep | 0 | Sep | 2022 | 0.00026154 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-09-03 08:42 | 2022-09-03 11:47 | 25 | 3:05 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | R22090300132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2022-09-03 | 4625 | keep | 0 | Sep | 2022 | 0.0031501 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-09-03 08:43 | 2022-09-03 18:13 | 65 | 9:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE SUBIO PRIMARIA | S22090300607 | New_Event | Primary Wire Break | Include | Include | Equipment | 570 | 2022-09-03 | 37050 | keep | 0 | Sep | 2022 | 0.025235 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-09-03 08:47 | 2022-09-03 08:48 | 4533 | 0:01 | T | DESGANCHE | RECERRO | B22090300000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-03 | 4533 | keep | 0 | Sep | 2022 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
SAN JUAN | 2022-09-03 08:48 | 2022-09-03 15:51 | 101 | 7:03 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S22090300612 | New_Event | Vegetation Contact | Include | Include | Vegetation | 423 | 2022-09-03 | 42723 | keep | 0 | Sep | 2022 | 0.029098 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
BAYAMON | 2022-09-03 08:48 | 2022-09-03 14:00 | 40 | 5:12 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | B22090300105 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 312 | 2022-09-03 | 12480 | keep | 0 | Sep | 2022 | 0.0085001 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-09-03 08:50 | 2022-09-03 19:00 | 200 | 10:10 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN C/L SE REPARO ALAMBRES PRIMARIOS | P22090300169 | New_Event | Primary Wire Break | Include | Include | Equipment | 610 | 2022-09-03 | 122000 | keep | 0 | Sep | 2022 | 0.083094 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-09-03 08:51 | 2022-09-03 12:16 | 500 | 3:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. CG-220903-02 | C22090300164 | New_Event | Primary Wire Break | Include | Include | Equipment | 205 | 2022-09-03 | 102500 | keep | 0 | Sep | 2022 | 0.069812 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
SAN JUAN | 2022-09-03 09:02 | 2022-09-03 15:10 | 14 | 6:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22090300622 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2022-09-03 | 5152 | keep | 0 | Sep | 2022 | 0.003509 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2022-09-03 09:02 | 2022-09-03 09:03 | 3744 | 0:01 | T | LINEA DE TRANSMISION 38KV | TERMINACION 38 KV AVERIDA SE ABRE INTERRUPTOR PARA TRANSFERIR CARGA DE 5004-06 Y 5004-07 HACIA 5018-02 | P22090300187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-03 | 3744 | keep | 0 | Sep | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2022-09-03 09:02 | 2022-09-03 09:03 | 1557 | 0:01 | P | OTRAS CAUSAS | SE ABRE INTERRUPTOR PARA CERRAR MACHETES Y TRANSFERIR CARGAS DE 5004-07 Y 5004-06 A 5018-02 | P22090300187 | New_Event | Other Causes | Include | Include | Other | 1 | 2022-09-03 | 1557 | keep | 0 | Sep | 2022 | 0.0010605 | 0.0010605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1557
PONCE | 2022-09-03 09:03 | 2022-09-03 09:13 | 21 | 0:10 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 50 KVA AVERIADO POR 75 KVA | P22090200149 | New_Event | Service Transformer Failure | Include | Include | Equipment | 10 | 2022-09-03 | 210 | keep | 0 | Sep | 2022 | 0.00014303 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2022-09-03 09:08 | 2022-09-03 11:35 | 18 | 2:27 | P | NO SE REPORTO CAUSA | 2 X 15 EN XMR | S22090300628 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2022-09-03 | 2646 | keep | 0 | Sep | 2022 | 0.0018022 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2022-09-03 09:13 | 2022-09-03 10:14 | 3744 | 1:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO CONDUCTOR PRIMARIO CRUZADO Y SE ELIMINO PARARRAYO AVERIADO | P22090300193 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 61 | 2022-09-03 | 228384 | keep | 0 | Sep | 2022 | 0.15555 | 0.00255 | Sustained | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2022-09-03 09:13 | 2022-09-03 10:14 | 2379 | 1:01 | T | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO CONDUCTOR PRIMARIO CRUZADO Y SE ELIMINO PARARRAYO AVERIADO | P22090300193 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 61 | 2022-09-03 | 145119 | keep | 0 | Sep | 2022 | 0.09884 | 0.0016203 | Sustained | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-09-03 09:13 | 2022-09-03 10:14 | 1557 | 1:01 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO CONDUCTOR PRIMARIO CRUZADO Y SE ELIMINO PARARRAYO AVERIADO | P22090300193 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 61 | 2022-09-03 | 94977 | keep | 0 | Sep | 2022 | 0.064688 | 0.0010605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1557
SAN JUAN | 2022-09-03 09:15 | 2022-09-03 12:48 | 144 | 3:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22090300637 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2022-09-03 | 30672 | keep | 0 | Sep | 2022 | 0.020891 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
CAGUAS | 2022-09-03 09:30 | 2022-09-03 11:53 | 20 | 2:23 | P | ARBOL SOBRE LINEA | 1X50 EN C/L SE RETIRO ARBOL COMPLETO DE PRIMARIA | C22090300193 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 143 | 2022-09-03 | 2860 | keep | 0 | Sep | 2022 | 0.0019479 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-03 09:33 | 2022-09-03 16:23 | 22 | 6:50 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA | S22090300652 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 410 | 2022-09-03 | 9020 | keep | 0 | Sep | 2022 | 0.0061435 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2022-09-03 09:37 | 2022-09-03 11:20 | 2 | 1:43 | P | NO SE REPORTO CAUSA | 1X15 EN BANCO DE XMRS | C22090300198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 103 | 2022-09-03 | 206 | keep | 0 | Sep | 2022 | 0.00014031 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-09-03 09:56 | 2022-09-03 13:50 | 6 | 3:54 | P | ARBOL SOBRE LINEA | 1 X 20 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A22090300101 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 234 | 2022-09-03 | 1404 | keep | 0 | Sep | 2022 | 0.00095626 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2022-09-03 10:00 | 2022-09-03 12:07 | 7 | 2:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | R22090300162 | New_Event | Cutout Failure | Include | Include | Equipment | 127 | 2022-09-03 | 889 | keep | 0 | Sep | 2022 | 0.00060549 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-09-03 10:00 | 2022-09-03 15:17 | 55 | 5:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO PRIMARIO | P22090300326 | New_Event | Primary Wire Break | Include | Include | Equipment | 317 | 2022-09-03 | 17435 | keep | 0 | Sep | 2022 | 0.011875 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
PONCE | 2022-09-03 10:14 | 2022-09-03 11:50 | 21 | 1:36 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 50 KVA AVERIADO POR 75 KVA | P22090200149 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 96 | 2022-09-03 | 2016 | keep | 0 | Sep | 2022 | 0.0013731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-03 10:19 | 2022-09-04 09:27 | 5 | 23:08 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | P22090300258 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1388 | 2022-09-03 | 6940 | keep | 0 | Sep | 2022 | 0.0047268 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-09-03 10:21 | 2022-09-03 12:45 | 50 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22090300690 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2022-09-03 | 7200 | keep | 0 | Sep | 2022 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-03 10:24 | 2022-09-03 13:40 | 30 | 3:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L Y 1 X 20 EN XMR | B22090300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2022-09-03 | 5880 | keep | 0 | Sep | 2022 | 0.0040048 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-09-03 10:24 | 2022-09-03 15:45 | 8 | 5:21 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 321 | 2022-09-03 | 2568 | keep | 0 | Sep | 2022 | 0.0017491 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-09-03 10:36 | 2022-09-03 10:37 | 766 | 0:01 | P | ANIMAL | RECERRO LLEVA 1709-05 50% POR 1909-07 | S22090300000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-03 | 766 | keep | 0 | Sep | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2022-09-03 10:36 | 2022-09-03 10:37 | 2364 | 0:01 | T | ANIMAL | BKR 1709-03 RECERRO Y LLEVA LA CARGA DEL 1709-05 | S22090300000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-03 | 2364 | keep | 0 | Sep | 2022 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2022-09-03 10:37 | 2022-09-03 14:38 | 50 | 4:01 | P | ANIMAL | 1 X 80 EN C/L SE RETIRO AVE | S22090300748 | 1st_after_momentary | Animals | Include | Include | Wildlife | 241 | 2022-09-03 | 12050 | keep | 0 | Sep | 2022 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-03 10:45 | 2022-09-03 21:35 | 3 | 10:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN BANCO DE XMR Y SE REMPLAZO CAJA PRIMARIA | S22090300706 | New_Event | Cutout Failure | Include | Include | Equipment | 650 | 2022-09-03 | 1950 | keep | 0 | Sep | 2022 | 0.0013281 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-09-03 10:46 | 2022-09-03 16:48 | 30 | 6:02 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22090300275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 362 | 2022-09-03 | 10860 | keep | 0 | Sep | 2022 | 0.0073967 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-03 10:52 | 2022-09-03 12:11 | 8 | 1:19 | P | CAUSAS EXTERNAS | 2 X 10 EN TRANSFORMADOR VEHICULO IMPACTO POSTE PASANTE SE RECOMIENDO PARA CAMBIO | R22090300154 | New_Event | Damage From Public | Include | Include | Public | 79 | 2022-09-03 | 632 | keep | 0 | Sep | 2022 | 0.00043045 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-03 10:57 | 2022-09-03 12:59 | 3 | 2:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA CAJA QUEMADA | R22090300155 | New_Event | Cutout Failure | Include | Include | Equipment | 122 | 2022-09-03 | 366 | keep | 0 | Sep | 2022 | 0.00024928 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-09-03 11:15 | 2022-09-03 16:06 | 200 | 4:51 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA PARTIDA EMERGENCIA CASI POR CAER Y SE NORMALIZO CARGAS MEDIANTE SJ-220903-04 | S22090300676 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 291 | 2022-09-03 | 58200 | keep | 0 | Sep | 2022 | 0.03964 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-09-03 11:15 | 2022-09-03 16:00 | 50 | 4:45 | P | DESGANCHE | 1 X 40EN C/L DESGANCHE | P22090300288 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2022-09-03 | 14250 | keep | 0 | Sep | 2022 | 0.0097056 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-09-03 11:20 | 2022-09-03 19:41 | 15 | 8:21 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | C22090300285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 501 | 2022-09-03 | 7515 | keep | 0 | Sep | 2022 | 0.0051184 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-09-03 11:34 | 2022-09-07 13:45 | 20 | 98:11 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA REPARAR VERIFICADO EN BITACORA | M22090300063 | New_Event | Primary Wire Break | Include | Include | Equipment | 5891 | 2022-09-03 | 117820 | keep | 0 | Sep | 2022 | 0.080247 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-03 11:45 | 2022-09-03 14:20 | 18 | 2:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22090300131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 155 | 2022-09-03 | 2790 | keep | 0 | Sep | 2022 | 0.0019003 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2022-09-03 11:51 | 2022-09-03 18:21 | 3 | 6:30 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C22090300306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2022-09-03 | 1170 | keep | 0 | Sep | 2022 | 0.00079688 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-09-03 11:59 | 2022-09-03 13:41 | 30 | 1:42 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22090300066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-09-03 | 3060 | keep | 0 | Sep | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-03 11:59 | 2022-09-03 15:13 | 15 | 3:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22090300136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2022-09-03 | 2910 | keep | 0 | Sep | 2022 | 0.001982 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-09-03 12:00 | 2022-09-03 14:47 | 50 | 2:47 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | C22090300311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-09-03 | 8350 | keep | 0 | Sep | 2022 | 0.0056871 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-03 12:09 | 2022-09-03 15:50 | 12 | 3:41 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22090300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2022-09-03 | 2652 | keep | 0 | Sep | 2022 | 0.0018063 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-09-03 12:18 | 2022-09-03 16:08 | 100 | 3:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO PRIMARIO | P22090300306 | New_Event | Primary Wire Break | Include | Include | Equipment | 230 | 2022-09-03 | 23000 | keep | 0 | Sep | 2022 | 0.015665 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-09-03 12:21 | 2022-09-03 14:15 | 40 | 1:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22090300070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2022-09-03 | 4560 | keep | 0 | Sep | 2022 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-03 12:25 | 2022-09-03 17:22 | 18 | 4:57 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN XMR | B22090300141 | New_Event | Service Transformer Failure | Include | Include | Equipment | 297 | 2022-09-03 | 5346 | keep | 0 | Sep | 2022 | 0.0036411 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-09-03 12:27 | 2022-09-03 18:00 | 10 | 5:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B22090300142 | New_Event | Primary Wire Break | Include | Include | Equipment | 333 | 2022-09-03 | 3330 | keep | 0 | Sep | 2022 | 0.002268 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-03 12:27 | 2022-09-03 13:45 | 20 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | B22090300143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2022-09-03 | 1560 | keep | 0 | Sep | 2022 | 0.0010625 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-09-03 12:43 | 2022-09-03 12:44 | 4132 | 0:01 | T | DESGANCHE | RECIERRE | P22090300314 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-03 | 4132 | keep | 0 | Sep | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-09-03 12:44 | 2022-09-03 15:35 | 100 | 2:51 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | P22090300339 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-09-03 | 17100 | keep | 0 | Sep | 2022 | 0.011647 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-03 12:46 | 2022-09-03 17:00 | 15 | 4:14 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/L DESGANCHE | C22090300325 | New_Event | Vegetation Contact | Include | Include | Vegetation | 254 | 2022-09-03 | 3810 | keep | 0 | Sep | 2022 | 0.002595 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-03 12:59 | 2022-09-03 13:02 | 1681 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE 1303-04 QUE ESTA TRANSFERIDO AL 1303-05 PERO LLEVA 1303-01 Y 1346-06 CERRADO POR SCADA | S22090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-03 | 5043 | keep | 0 | Sep | 2022 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-09-03 12:59 | 2022-09-03 13:01 | 1106 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 1529-15 QUE LLEVA 60% DEL 1346-02 CERRADO POR SCADA | S22090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-03 | 2212 | keep | 0 | Sep | 2022 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-09-03 12:59 | 2022-09-03 13:02 | 1598 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE 1303-04 QUE ESTA TRANSFERIDO AL 1303-05 PERO LLEVA 1303-01 Y 1346-06 CERRADO POR SCADA | S22090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-03 | 4794 | keep | 0 | Sep | 2022 | 0.0032652 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-09-03 12:59 | 2022-09-03 13:01 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 1529-15 QUE LLEVA 60% DEL 1346-02 CERRADO POR SCADA | S22090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-03 | 3604 | keep | 0 | Sep | 2022 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-09-03 13:02 | 2022-09-03 14:35 | 32 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 80 EN PROVISIONAL | S22090300495 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-09-03 | 2976 | keep | 0 | Sep | 2022 | 0.0020269 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CANOVANAS | 2022-09-03 13:08 | 2022-09-03 13:59 | 90 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA | R22090300176 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2022-09-03 | 4590 | keep | 0 | Sep | 2022 | 0.0031262 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-09-03 13:08 | 2022-09-03 13:09 | 2825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22090300078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 2825 | keep | 0 | Sep | 2022 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
FAJARDO | 2022-09-03 13:11 | 2022-09-03 14:31 | 3 | 1:20 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN TRANSFORMADOR PROBLEMA DEL CLIENTE | R22090300177 | New_Event | Customer-Related Interruption | Include | Include | Public | 80 | 2022-09-03 | 240 | keep | 0 | Sep | 2022 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2022-09-03 13:17 | 2022-09-03 17:39 | 100 | 4:22 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22090300336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2022-09-03 | 26200 | keep | 0 | Sep | 2022 | 0.017845 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-03 13:22 | 2022-09-03 15:18 | 65 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 50 EN SU-2 Y 1 X 40 EN C/L | S22090300807 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2022-09-03 | 7540 | keep | 0 | Sep | 2022 | 0.0051355 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-09-03 13:22 | 2022-09-03 18:10 | 40 | 4:48 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090300121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-09-03 | 11520 | keep | 0 | Sep | 2022 | 0.0078462 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-09-03 13:31 | 2022-09-03 17:08 | 8 | 3:37 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A22090300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2022-09-03 | 1736 | keep | 0 | Sep | 2022 | 0.0011824 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-09-03 13:32 | 2022-09-03 16:00 | 20 | 2:28 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22090300335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-09-03 | 2960 | keep | 0 | Sep | 2022 | 0.002016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-09-03 13:35 | 2022-09-03 16:00 | 100 | 2:25 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LAS LINEAS | M22090300086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2022-09-03 | 14500 | keep | 0 | Sep | 2022 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-03 13:43 | 2022-09-03 16:15 | 30 | 2:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090300123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2022-09-03 | 4560 | keep | 0 | Sep | 2022 | 0.0031058 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-09-03 13:47 | 2022-09-03 15:13 | 1467 | 1:26 | T | DESGANCHE | DISPARO DE BKR SE REALIZO DESGANCHE DESDE EL PISO CON VARETA Y SE CERRO POR CONTROL | C22090300340 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-09-03 | 126162 | keep | 0 | Sep | 2022 | 0.085928 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
YAUCO | 2022-09-03 13:48 | 2022-09-03 20:04 | 120 | 6:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ZAFADA DE AISLADOR | M22090300093 | New_Event | Primary Wire Break | Include | Include | Equipment | 376 | 2022-09-03 | 45120 | keep | 0 | Sep | 2022 | 0.030731 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2022-09-03 13:48 | 2022-09-03 17:20 | 250 | 3:32 | P | ARBOL SOBRE LINEA | 2 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22090300091 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 212 | 2022-09-03 | 53000 | keep | 0 | Sep | 2022 | 0.036098 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
YAUCO | 2022-09-03 13:52 | 2022-09-03 22:30 | 70 | 8:38 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 518 | 2022-09-03 | 36260 | keep | 0 | Sep | 2022 | 0.024697 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2022-09-03 13:52 | 2022-09-03 15:08 | 1 | 1:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22090300124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-09-03 | 76 | keep | 0 | Sep | 2022 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-09-03 14:05 | 2022-09-03 14:06 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 6014-03 | M22090300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 1352 | keep | 0 | Sep | 2022 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2022-09-03 14:06 | 2022-09-03 14:07 | 871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 6012-05 QUE LLEVA LA CARGA DEL 6014-03 | M22090300104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 871 | keep | 0 | Sep | 2022 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2022-09-03 14:10 | 2022-09-03 14:50 | 10 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | M22090300096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2022-09-03 | 400 | keep | 0 | Sep | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-03 14:13 | 2022-09-03 17:53 | 57 | 3:40 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-5 | S22090300831 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2022-09-03 | 12540 | keep | 0 | Sep | 2022 | 0.0085409 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
MAYAGÃœEZ | 2022-09-03 14:22 | 2022-09-03 16:08 | 2560 | 1:46 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR NO CERRO POR SCADA SE VERIFICO EL ALIMENTADOR Y LO QUE SE REPORTO FUE MAL TIEMPO EN EL AREA SE CERRO EN LA SUBESTACION | M22090300119 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 106 | 2022-09-03 | 271360 | keep | 0 | Sep | 2022 | 0.18482 | 0.0017436 | Sustained | FALSE | FALSE | Not_TMED_Event | 2560
CANOVANAS | 2022-09-03 14:32 | 2022-09-03 16:26 | 15 | 1:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO CAJA PRIMARIA | R22090300181 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2022-09-03 | 1710 | keep | 0 | Sep | 2022 | 0.0011647 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-03 14:34 | 2022-09-03 18:20 | 66 | 3:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA | S22090300842 | New_Event | Cutout Failure | Include | Include | Equipment | 226 | 2022-09-03 | 14916 | keep | 0 | Sep | 2022 | 0.010159 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
GUAYAMA | 2022-09-03 14:40 | 2022-09-03 18:22 | 3 | 3:42 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090300357 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-09-03 | 666 | keep | 0 | Sep | 2022 | 0.00045361 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-09-03 14:47 | 2022-09-03 20:09 | 80 | 5:22 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M22090300138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2022-09-03 | 25760 | keep | 0 | Sep | 2022 | 0.017545 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-09-03 14:50 | 2022-09-03 18:34 | 250 | 3:44 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090300141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2022-09-03 | 56000 | keep | 0 | Sep | 2022 | 0.038141 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-09-03 14:51 | 2022-09-03 18:40 | 50 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S22090300848 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2022-09-03 | 11450 | keep | 0 | Sep | 2022 | 0.0077985 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-09-03 14:51 | 2022-09-03 15:46 | 968 | 0:55 | T | DESCONECTIVO DEFECTUOSO | HAY MACHETE QUEMADO EN N/O SE TRANSFIRIO CARGA 5404-02 | P22090300361 | New_Event | Switch Failure | Include | Include | Equipment | 55 | 2022-09-03 | 53240 | keep | 0 | Sep | 2022 | 0.036262 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
CANOVANAS | 2022-09-03 14:53 | 2022-09-03 17:24 | 170 | 2:31 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE PRIMARIO | R22090300186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-09-03 | 25670 | keep | 0 | Sep | 2022 | 0.017484 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
MAYAGÃœEZ | 2022-09-03 14:57 | 2022-09-03 18:29 | 70 | 3:32 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M22090300147 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 212 | 2022-09-03 | 14840 | keep | 0 | Sep | 2022 | 0.010107 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2022-09-03 14:58 | 2022-09-03 16:02 | 8 | 1:04 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22090300149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 64 | 2022-09-03 | 512 | keep | 0 | Sep | 2022 | 0.00034872 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-03 15:00 | 2022-09-03 16:55 | 1036 | 1:55 | T | DESGANCHE | SE RETIRO RAMA SOBRE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M22090300151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-09-03 | 119140 | keep | 0 | Sep | 2022 | 0.081146 | 0.00070561 | Sustained | FALSE | FALSE | Not_TMED_Event | 1036
CAGUAS | 2022-09-03 15:02 | 2022-09-03 17:02 | 10 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR MAL TIEMPO LLUVIAS | C22090300356 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2022-09-03 | 1200 | keep | 0 | Sep | 2022 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-03 15:03 | 2022-09-03 19:27 | 20 | 4:24 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 15 EN XMR | S22090300856 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 264 | 2022-09-03 | 5280 | keep | 0 | Sep | 2022 | 0.0035962 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-09-03 15:03 | 2022-09-03 19:51 | 10 | 4:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22090300205 | New_Event | Secondary Wire Break | Include | Include | Equipment | 288 | 2022-09-03 | 2880 | keep | 0 | Sep | 2022 | 0.0019616 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-03 15:05 | 2022-09-03 16:45 | 10 | 1:40 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR LAGARTIJO CRUZO FASE A TIERRA | A22090300126 | New_Event | Animals | Include | Include | Wildlife | 100 | 2022-09-03 | 1000 | keep | 0 | Sep | 2022 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-09-03 15:11 | 2022-09-03 16:51 | 9 | 1:40 | P | NO SE REPORTO CAUSA | 1 X 18 EN SU | R22090300190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2022-09-03 | 900 | keep | 0 | Sep | 2022 | 0.00061299 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2022-09-03 15:11 | 2022-09-03 15:27 | 20 | 0:16 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22090300079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2022-09-03 | 320 | keep | 0 | Sep | 2022 | 0.00021795 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-09-03 15:13 | 2022-09-03 18:48 | 60 | 3:35 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C22090300357 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-09-03 | 12900 | keep | 0 | Sep | 2022 | 0.0087861 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-09-03 15:14 | 2022-09-03 15:40 | 30 | 0:26 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA | R22090300191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-09-03 | 780 | keep | 0 | Sep | 2022 | 0.00053125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-03 15:20 | 2022-09-04 14:34 | 13 | 23:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 100KVA Y SE INSTALO CAJA PRIMARIA | S22090300857 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1394 | 2022-09-03 | 18122 | keep | 0 | Sep | 2022 | 0.012343 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2022-09-03 15:32 | 2022-09-04 11:56 | 4 | 20:24 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | S22090300864 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1224 | 2022-09-03 | 4896 | keep | 0 | Sep | 2022 | 0.0033346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-09-03 15:43 | 2022-09-03 18:05 | 1 | 2:22 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE PRIMARIO | R22090300194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-09-03 | 142 | keep | 0 | Sep | 2022 | 9.6716e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-03 15:44 | 2022-09-03 17:11 | 50 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22090300865 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2022-09-03 | 4350 | keep | 0 | Sep | 2022 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-03 15:47 | 2022-09-03 17:30 | 100 | 1:43 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C22090300367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-09-03 | 10300 | keep | 0 | Sep | 2022 | 0.0070153 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-03 16:13 | 2022-09-03 18:25 | 10 | 2:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22090300872 | New_Event | Secondary Wire Break | Include | Include | Equipment | 132 | 2022-09-03 | 1320 | keep | 0 | Sep | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-03 16:13 | 2022-09-03 19:36 | 100 | 3:23 | P | DESGANCHE | 2 X 50 EN C/L SE DESGANCHO | B22090300163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-09-03 | 20300 | keep | 0 | Sep | 2022 | 0.013826 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-09-03 16:17 | 2022-09-03 16:18 | 1310 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO | B22090300000 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-09-03 | 1310 | keep | 0 | Sep | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2022-09-03 16:18 | 2022-09-03 19:27 | 200 | 3:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L SE REMPLAZO AISLADOR | B22090300170 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 189 | 2022-09-03 | 37800 | keep | 0 | Sep | 2022 | 0.025745 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-09-03 16:23 | 2022-09-03 20:41 | 30 | 4:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN C/L MAL TIEMPO LLUVIAS | C22090300375 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 258 | 2022-09-03 | 7740 | keep | 0 | Sep | 2022 | 0.0052717 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-03 16:26 | 2022-09-03 16:28 | 4188 | 0:02 | T | CAUSAS EXTERNAS | DISPARO SE CERRO POR CONTROL | R22090300200 | New_Event | Damage From Public | Include | Include | Public | 2 | 2022-09-03 | 8376 | keep | 0 | Sep | 2022 | 0.0057049 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2022-09-03 16:28 | 2022-09-03 18:02 | 15 | 1:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR Y SE REEMPLAZO CAJA PRIMARIA | R22090300181 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 94 | 2022-09-03 | 1410 | keep | 0 | Sep | 2022 | 0.00096034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-03 16:28 | 2022-09-03 17:21 | 130 | 0:53 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA EXCAVADORA PRIVADA IMPACTO POSTE | R22090300204 | 1st_after_momentary | Damage From Public | Include | Include | Public | 53 | 2022-09-03 | 6890 | keep | 0 | Sep | 2022 | 0.0046927 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-09-03 16:29 | 2022-09-04 09:13 | 1 | 16:44 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | S22090300877 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1004 | 2022-09-03 | 1004 | keep | 0 | Sep | 2022 | 0.00068382 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-03 17:15 | 2022-09-04 10:00 | 40 | 16:45 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN RISER Y T2-T3-T4 ESTAN EN SERVICIO. SE QUEDO XMR T1 SIN SERVICIO QUEMADO | S22090300896 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1005 | 2022-09-03 | 40200 | keep | 0 | Sep | 2022 | 0.02738 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-03 17:15 | 2022-09-03 19:00 | 21 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | C22090300380 | New_Event | Primary Wire Break | Include | Include | Equipment | 105 | 2022-09-03 | 2205 | keep | 0 | Sep | 2022 | 0.0015018 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2022-09-03 17:15 | 2022-09-03 19:35 | 20 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIAS Y VIENTO | A22090300133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2022-09-03 | 2800 | keep | 0 | Sep | 2022 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-03 17:39 | 2022-09-03 19:20 | 55 | 1:41 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22090300902 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2022-09-03 | 5555 | keep | 0 | Sep | 2022 | 0.0037835 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2022-09-03 17:45 | 2022-09-03 19:10 | 20 | 1:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090300136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-09-03 | 1700 | keep | 0 | Sep | 2022 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-09-03 17:46 | 2022-09-03 17:47 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 6197 | keep | 0 | Sep | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CANOVANAS | 2022-09-03 17:51 | 2022-09-03 18:46 | 20 | 0:55 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | R22090300212 | New_Event | Animals | Include | Include | Wildlife | 55 | 2022-09-03 | 1100 | keep | 0 | Sep | 2022 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-09-03 18:04 | 2022-09-03 20:00 | 100 | 1:56 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090300250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2022-09-03 | 11600 | keep | 0 | Sep | 2022 | 0.0079007 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-03 18:07 | 2022-09-03 21:20 | 100 | 3:13 | P | DESGANCHE | 1 X 80 Y 1 X 40 EN CORTES DE LINEA DISTINTOS SE RETIRO RAMA DE LAS LINEAS | M22090300255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-09-03 | 19300 | keep | 0 | Sep | 2022 | 0.013145 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-03 18:08 | 2022-09-04 16:36 | 10 | 22:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO (TRASPATIO) | B22090300190 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1348 | 2022-09-03 | 13480 | keep | 0 | Sep | 2022 | 0.0091812 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-03 18:12 | 2022-09-03 18:15 | 137 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 411 | keep | 0 | Sep | 2022 | 0.00027993 | 9.331e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-09-03 18:12 | 2022-09-03 18:15 | 760 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 2280 | keep | 0 | Sep | 2022 | 0.0015529 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2022-09-03 18:12 | 2022-09-03 18:15 | 1225 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 3675 | keep | 0 | Sep | 2022 | 0.002503 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-09-03 18:12 | 2022-09-03 18:15 | 1452 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 4356 | keep | 0 | Sep | 2022 | 0.0029669 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-09-03 18:12 | 2022-09-03 18:15 | 616 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 1848 | keep | 0 | Sep | 2022 | 0.0012587 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-09-03 18:12 | 2022-09-03 18:15 | 3433 | 0:03 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600 1204-02 FUERA, 20% POR 1303-02 LLEVA 10% 1204-03 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 10299 | keep | 0 | Sep | 2022 | 0.0070146 | 0.0023382 | Momentary | FALSE | FALSE | Not_TMED_Event | 3433
SAN JUAN | 2022-09-03 18:12 | 2022-09-03 18:15 | 552 | 0:03 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3600, 10 % DE LA CARGA DEL 1204-03 POR 1204-02 Y 30% POR 1204-01 | S22090300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-03 | 1656 | keep | 0 | Sep | 2022 | 0.0011279 | 0.00037596 | Momentary | FALSE | FALSE | Not_TMED_Event | 552
CANOVANAS | 2022-09-03 18:35 | 2022-09-03 20:11 | 70 | 1:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R22090300212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-09-03 | 6720 | keep | 0 | Sep | 2022 | 0.004577 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-09-03 18:35 | 2022-09-03 19:08 | 160 | 0:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER HACIA SU NO SE REPORTO CAUSAS | P22090300422 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2022-09-03 | 5280 | keep | 0 | Sep | 2022 | 0.0035962 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
PONCE | 2022-09-03 18:40 | 2022-09-03 18:51 | 6 | 0:11 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO SE REPORTO CAUSAS | P22090300431 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-09-03 | 66 | keep | 0 | Sep | 2022 | 4.4952e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-09-03 18:49 | 2022-09-03 21:39 | 50 | 2:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | B22090300196 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 170 | 2022-09-03 | 8500 | keep | 0 | Sep | 2022 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-09-03 18:49 | 2022-09-04 08:40 | 1 | 13:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN MONTURA DE TRANSFORMADOR LLUVIA Y VIENTO FUERTE | A22090300144 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 831 | 2022-09-03 | 831 | keep | 0 | Sep | 2022 | 0.00056599 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-03 19:07 | 2022-09-03 21:00 | 20 | 1:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE CERRO SECUNDARIA ABIERTA | R22090300217 | New_Event | Secondary Wire Break | Include | Include | Equipment | 113 | 2022-09-03 | 2260 | keep | 0 | Sep | 2022 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-09-03 19:09 | 2022-09-04 09:27 | 50 | 14:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090300148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 858 | 2022-09-03 | 42900 | keep | 0 | Sep | 2022 | 0.029219 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-09-03 19:11 | 2022-09-03 22:00 | 35 | 2:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090300293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-09-03 | 5915 | keep | 0 | Sep | 2022 | 0.0040287 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
GUAYAMA | 2022-09-03 19:20 | 2022-09-04 09:04 | 4 | 13:44 | P | ANIMAL | 1 X 15 EN XMR AVE CRUZO LINEAS | P22090300443 | New_Event | Animals | Include | Include | Wildlife | 824 | 2022-09-03 | 3296 | keep | 0 | Sep | 2022 | 0.0022449 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-09-03 19:24 | 2022-09-05 12:37 | 30 | 41:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | CAMBIO DE LINEA A POSTE NUEVO 1 X 30 Y 1 X 50 EN CORTE DE LINEA | A22090300150 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2473 | 2022-09-03 | 74190 | keep | 0 | Sep | 2022 | 0.05053 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2022-09-03 19:27 | 2022-09-03 21:58 | 100 | 2:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | R22090300220 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2022-09-03 | 15100 | keep | 0 | Sep | 2022 | 0.010285 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2022-09-03 19:28 | 2022-09-03 20:12 | 150 | 0:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 SMU-20 EN SU 11 MAL TIEMPO LLUVIAS | P22090300444 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 44 | 2022-09-03 | 6600 | keep | 0 | Sep | 2022 | 0.0044952 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-09-03 19:33 | 2022-09-03 21:30 | 22 | 1:57 | P | MAL TIEMPO/RAYOS | 1 X 20 Y 1 X 15 EN DISTINTOS TRANSFORMADORES DESCARGAS ELECTRICAS | M22090300304 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-09-03 | 2574 | keep | 0 | Sep | 2022 | 0.0017531 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2022-09-03 19:54 | 2022-09-03 21:41 | 120 | 1:47 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L 1 X 80 EN C/L | S22090300887 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2022-09-03 | 12840 | keep | 0 | Sep | 2022 | 0.0087453 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-09-03 19:56 | 2022-09-03 19:57 | 2035 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090300450 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-03 | 2035 | keep | 0 | Sep | 2022 | 0.001386 | 0.001386 | Momentary | FALSE | FALSE | Not_TMED_Event | 2035
VEGA BAJA | 2022-09-03 20:09 | 2022-09-03 22:10 | 80 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090300155 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2022-09-03 | 9680 | keep | 0 | Sep | 2022 | 0.006593 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-09-03 20:19 | 2022-09-04 00:25 | 2 | 4:06 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L, SE ENCONTRO PUENTE PRIMARIO ABIERTO; NO HAY PASO, ALREDEDOR DE 100 CLIENTES CONTINUAN SIN SERVICIO. | M22090300323 | New_Event | Primary Wire Break | Include | Include | Equipment | 246 | 2022-09-03 | 492 | keep | 0 | Sep | 2022 | 0.0003351 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2022-09-03 20:20 | 2022-09-03 23:00 | 18 | 2:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | A22090300158 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2022-09-03 | 2880 | keep | 0 | Sep | 2022 | 0.0019616 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2022-09-03 20:21 | 2022-09-04 10:58 | 4 | 14:37 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090300455 | New_Event | Vegetation Contact | Include | Include | Vegetation | 877 | 2022-09-03 | 3508 | keep | 0 | Sep | 2022 | 0.0023893 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-09-03 20:21 | 2022-09-03 20:58 | 100 | 0:37 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M22090300324 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 37 | 2022-09-03 | 3700 | keep | 0 | Sep | 2022 | 0.0025201 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-09-03 20:49 | 2022-09-04 16:25 | 8 | 19:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | A22090300162 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1176 | 2022-09-03 | 9408 | keep | 0 | Sep | 2022 | 0.0064077 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-03 21:00 | 2022-09-03 21:55 | 25 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M22090300248 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-09-03 | 1375 | keep | 0 | Sep | 2022 | 0.00093651 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-09-03 21:20 | 2022-09-04 01:10 | 50 | 3:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090300339 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-09-03 | 11500 | keep | 0 | Sep | 2022 | 0.0078326 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-03 21:23 | 2022-09-05 09:38 | 8 | 36:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON VARIAS CONDICIONES EN LA LINEA SECINDARIA | S22090300945 | New_Event | Secondary Wire Break | Include | Include | Equipment | 2175 | 2022-09-03 | 17400 | keep | 0 | Sep | 2022 | 0.011851 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-03 21:46 | 2022-09-04 01:10 | 14 | 3:24 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22090300348 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2022-09-03 | 2856 | keep | 0 | Sep | 2022 | 0.0019452 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2022-09-03 21:48 | 2022-09-04 11:40 | 100 | 13:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTRE DE LINEA LLUVIA Y VIENTO FUERTE | A22090300167 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 832 | 2022-09-03 | 83200 | keep | 0 | Sep | 2022 | 0.056667 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-03 21:50 | 2022-09-04 09:41 | 225 | 11:51 | P | DESGANCHE | 2 X 65 EN CORTES DE LINEA | C22090300398 | New_Event | Vegetation Contact | Include | Include | Vegetation | 711 | 2022-09-03 | 159975 | keep | 0 | Sep | 2022 | 0.10896 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-09-03 22:31 | 2022-09-04 08:07 | 28 | 9:36 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 X 80 EN SU-2 | S22090300951 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 576 | 2022-09-03 | 16128 | keep | 0 | Sep | 2022 | 0.010985 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2022-09-03 22:55 | 2022-09-04 01:00 | 100 | 2:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR | M22090300358 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 125 | 2022-09-03 | 12500 | keep | 0 | Sep | 2022 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-03 22:57 | 2022-09-04 10:20 | 12 | 11:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | M22090300359 | New_Event | Cutout Failure | Include | Include | Equipment | 683 | 2022-09-03 | 8196 | keep | 0 | Sep | 2022 | 0.0055823 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-09-03 23:09 | 2022-09-04 09:05 | 80 | 9:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090300362 | New_Event | Vegetation Contact | Include | Include | Vegetation | 596 | 2022-09-03 | 47680 | keep | 0 | Sep | 2022 | 0.032475 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-09-03 23:10 | 2022-09-04 10:13 | 181 | 11:03 | P | DESGANCHE | 2 X 200 Y DOS CAJAS PRIMARIAS Y DESGANCHE | R22090300295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 663 | 2022-09-03 | 120003 | keep | 0 | Sep | 2022 | 0.081733 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
CANOVANAS | 2022-09-03 23:16 | 2022-09-04 12:30 | 22 | 13:14 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y DESGANCHE SECUNDARIO | R22090300298 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 794 | 2022-09-03 | 17468 | keep | 0 | Sep | 2022 | 0.011897 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BARRANQUITAS | 2022-09-03 23:16 | 2022-09-04 11:13 | 50 | 11:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22090300040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 717 | 2022-09-03 | 35850 | keep | 0 | Sep | 2022 | 0.024417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-09-03 23:32 | 2022-09-04 10:10 | 75 | 10:38 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA REPARAR | M22090300365 | New_Event | Primary Wire Break | Include | Include | Equipment | 638 | 2022-09-03 | 47850 | keep | 0 | Sep | 2022 | 0.03259 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-09-04 00:07 | 2022-09-04 09:00 | 100 | 8:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22090400002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 533 | 2022-09-04 | 53300 | keep | 0 | Sep | 2022 | 0.036302 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-04 00:12 | 2022-09-04 10:00 | 30 | 9:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN C/L | B22090400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 588 | 2022-09-04 | 17640 | keep | 0 | Sep | 2022 | 0.012015 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-09-04 00:17 | 2022-09-04 08:36 | 50 | 8:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA LLUVIA Y VIENTO FUERTE | A22090400001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 499 | 2022-09-04 | 24950 | keep | 0 | Sep | 2022 | 0.016993 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-09-04 00:25 | 2022-09-04 12:36 | 150 | 12:11 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | M22090300323 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 731 | 2022-09-04 | 109650 | keep | 0 | Sep | 2022 | 0.074682 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-04 00:56 | 2022-09-04 00:57 | 2276 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C22090400001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 2276 | keep | 0 | Sep | 2022 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-09-04 00:56 | 2022-09-04 00:57 | 777 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C22090400001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 777 | keep | 0 | Sep | 2022 | 0.00052921 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-09-04 00:56 | 2022-09-04 00:57 | 12 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C22090400001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 12 | keep | 0 | Sep | 2022 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-09-04 00:56 | 2022-09-04 00:57 | 1290 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 3000 | C22090400001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 1290 | keep | 0 | Sep | 2022 | 0.00087861 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2022-09-04 00:57 | 2022-09-04 11:45 | 40 | 10:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22090400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 648 | 2022-09-04 | 25920 | keep | 0 | Sep | 2022 | 0.017654 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-04 01:03 | 2022-09-04 01:04 | 4085 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R22090400004 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-09-04 | 4085 | keep | 0 | Sep | 2022 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-09-04 01:04 | 2022-09-04 11:43 | 1 | 10:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO DOS CAJAS PRIMARIAS Y 2 X 40 EN C/L Y 2X 30 EN RISER | R22090400019 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 639 | 2022-09-04 | 639 | keep | 0 | Sep | 2022 | 0.00043522 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-09-04 01:13 | 2022-09-04 05:45 | 10 | 4:32 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M22090400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 272 | 2022-09-04 | 2720 | keep | 0 | Sep | 2022 | 0.0018526 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-09-04 01:23 | 2022-09-04 01:24 | 1655 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 1655 | keep | 0 | Sep | 2022 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2022-09-04 01:25 | 2022-09-04 06:12 | 150 | 4:47 | P | SECUNDARIA/DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHO SECUNDARIA | C22090400002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 287 | 2022-09-04 | 43050 | keep | 0 | Sep | 2022 | 0.029321 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-09-04 02:08 | 2022-09-04 02:09 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 676 | keep | 0 | Sep | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-09-04 03:14 | 2022-09-04 03:15 | 1835 | 0:01 | T | DESGANCHE | RECIERRE | C22090400007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-04 | 1835 | keep | 0 | Sep | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2022-09-04 03:15 | 2022-09-04 08:21 | 1835 | 5:06 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | C22090400008 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 306 | 2022-09-04 | 561510 | keep | 0 | Sep | 2022 | 0.38244 | 0.0012498 | Sustained | FALSE | FALSE | Not_TMED_Event | 1835
ARECIBO | 2022-09-04 03:33 | 2022-09-04 07:48 | 30 | 4:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA LLUVIA Y VIENTO FUERTE | A22090400012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 255 | 2022-09-04 | 7650 | keep | 0 | Sep | 2022 | 0.0052104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-04 03:45 | 2022-09-04 06:36 | 513 | 2:51 | P | DESGANCHE | EN DISPARO DEL 1118-10 QUE LLEVA 20% DEL 1111-01 SE LIMPIO BANDERAS EN TODAS LAS FASES Y NEUTRAL, SE RETIRO RAMAS CERCA DE LA SALIDA SE CERRO BREAKER Y LUEGO MACHETES ABIERTOS EN LA CALLE BARTOLOME LAS CASAS | S22090400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2022-09-04 | 87723 | keep | 0 | Sep | 2022 | 0.059748 | 0.0003494 | Sustained | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2022-09-04 03:45 | 2022-09-04 06:34 | 2782 | 2:49 | T | DESGANCHE | SE LIMPIO BANDERAS EN TODAS LAS FASES Y NEUTRAL, SE RETIRO RAMAS CERCA DE LA SALIDA SE CERRO BREAKER CON MACHETES ABIERTOS EN LA CALLE BARTOLOME LAS CASAS | S22090400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-09-04 | 470158 | keep | 0 | Sep | 2022 | 0.32022 | 0.0018948 | Sustained | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2022-09-04 03:53 | 2022-09-04 08:48 | 93 | 4:55 | P | DESGANCHE | 1 X 30 EN PROVICIONAL AEREO Y DESGANCHE | R22090400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2022-09-04 | 27435 | keep | 0 | Sep | 2022 | 0.018686 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
AGUADILLA | 2022-09-04 04:00 | 2022-09-04 10:50 | 100 | 6:50 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22090400094 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 410 | 2022-09-04 | 41000 | keep | 0 | Sep | 2022 | 0.027925 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-04 04:10 | 2022-09-04 09:58 | 35 | 5:48 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER | B22090400003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2022-09-04 | 12180 | keep | 0 | Sep | 2022 | 0.0082957 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-09-04 05:13 | 2022-09-04 07:14 | 1812 | 2:01 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO ALIMENTADOR 75% EN SERVICIO | B22090400198 | New_Event | UG Cable Fault | Include | Include | Equipment | 121 | 2022-09-04 | 219252 | keep | 0 | Sep | 2022 | 0.14933 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
VEGA BAJA | 2022-09-04 05:15 | 2022-09-04 07:10 | 258 | 1:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22090400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2022-09-04 | 29670 | keep | 0 | Sep | 2022 | 0.020208 | 0.00017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 258
VEGA BAJA | 2022-09-04 05:52 | 2022-09-04 12:22 | 30 | 6:30 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22090400046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2022-09-04 | 11700 | keep | 0 | Sep | 2022 | 0.0079688 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-04 06:02 | 2022-09-04 10:25 | 40 | 4:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22090400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2022-09-04 | 10520 | keep | 0 | Sep | 2022 | 0.0071651 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-04 06:10 | 2022-09-04 06:12 | 2192 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-04 | 4384 | keep | 0 | Sep | 2022 | 0.0029859 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
CAGUAS | 2022-09-04 06:12 | 2022-09-04 08:58 | 200 | 2:46 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO | C2209040019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 166 | 2022-09-04 | 33200 | keep | 0 | Sep | 2022 | 0.022612 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-09-04 06:24 | 2022-09-04 12:10 | 36 | 5:46 | P | CABLE SOTERRADO AVERIADO | 1 X 20 SMU-20 SE DEJO ABIERTO DE T-11 @ T-12 | S22090400066 | New_Event | UG Cable Fault | Include | Include | Equipment | 346 | 2022-09-04 | 12456 | keep | 0 | Sep | 2022 | 0.0084837 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2022-09-04 06:25 | 2022-09-04 09:10 | 1 | 2:45 | P | DESGANCHE | 2 X 30 EN C/L SE DESGANCHO | B22090400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-09-04 | 165 | keep | 0 | Sep | 2022 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-04 06:34 | 2022-09-04 06:36 | 2643 | 0:02 | P | DESGANCHE | SE LIMPIO BANDERAS EN TODAS LAS FASES Y NEUTRAL, SE RETIRO RAMAS CERCA DE LA SALIDA SE CERRO BREAKER Y LUEGO SE CERRO MACHETES ABIERTOS EN LA CALLE BARTOLOME LAS CASAS. LLEVA 20% DEL 1111-01 SJ-220904-01 | S22090400011 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-09-04 | 5286 | keep | 0 | Sep | 2022 | 0.0036003 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-09-04 06:51 | 2022-09-04 10:44 | 40 | 3:53 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22090400032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 233 | 2022-09-04 | 9320 | keep | 0 | Sep | 2022 | 0.0063478 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-04 06:59 | 2022-09-04 07:00 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 3511 | keep | 0 | Sep | 2022 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2022-09-04 07:00 | 2022-09-04 18:27 | 20 | 11:27 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B22090400468 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 687 | 2022-09-04 | 13740 | keep | 0 | Sep | 2022 | 0.0093583 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-04 07:01 | 2022-09-04 07:02 | 2450 | 0:01 | T | ANIMAL | RECIERRE | C22090400024 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-04 | 2450 | keep | 0 | Sep | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-09-04 07:02 | 2022-09-04 11:10 | 50 | 4:08 | P | ANIMAL | 1 X 30 Y 1 X 40 EN CORTES DE LINEA CRUCE CON AVE | C22090400025 | 1st_after_momentary | Animals | Include | Include | Wildlife | 248 | 2022-09-04 | 12400 | keep | 0 | Sep | 2022 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-09-04 07:09 | 2022-09-04 10:55 | 60 | 3:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090400053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2022-09-04 | 13560 | keep | 0 | Sep | 2022 | 0.0092357 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-04 07:11 | 2022-09-04 10:05 | 40 | 2:54 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | B22090400093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-09-04 | 6960 | keep | 0 | Sep | 2022 | 0.0047404 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-04 07:14 | 2022-09-04 07:55 | 453 | 0:41 | P | CABLE SOTERRADO AVERIADO | 25% DE LA CARGA, SE SECCIONALIZO ALIMENTADOR | B22090400198 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 41 | 2022-09-04 | 18573 | keep | 0 | Sep | 2022 | 0.01265 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-04 07:26 | 2022-09-04 10:13 | 80 | 2:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X140 EN C/L Y 1X80 EN OTRO C/L SE REMPLAZO CAJA PRIMARIA | B22090400105 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2022-09-04 | 13360 | keep | 0 | Sep | 2022 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-09-04 07:45 | 2022-09-04 09:54 | 20 | 2:09 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | R22090400029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-09-04 | 2580 | keep | 0 | Sep | 2022 | 0.0017572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2022-09-04 07:54 | 2022-09-04 14:41 | 40 | 6:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P22090400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2022-09-04 | 16280 | keep | 0 | Sep | 2022 | 0.011088 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-04 07:55 | 2022-09-04 07:56 | 1812 | 0:01 | T | CABLE SOTERRADO AVERIADO | 75% DE LA CARGA SE SECCIONALIZO ALIMENTADOR | B22090400198 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-09-04 | 1812 | keep | 0 | Sep | 2022 | 0.0012341 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-04 07:56 | 2022-09-04 08:23 | 453 | 0:27 | P | CABLE SOTERRADO AVERIADO | 25% DE LA CARGA, SE SECCIONALIZO ALIMENTADOR | B22090400198 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 27 | 2022-09-04 | 12231 | keep | 0 | Sep | 2022 | 0.0083305 | 0.00030854 | Sustained | FALSE | FALSE | Not_TMED_Event | 453
HUMACAO | 2022-09-04 08:18 | 2022-09-04 08:19 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090400033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 5630 | keep | 0 | Sep | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BARRANQUITAS | 2022-09-04 08:18 | 2022-09-04 09:10 | 9 | 0:52 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHO | C22090400031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-09-04 | 468 | keep | 0 | Sep | 2022 | 0.00031875 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-09-04 08:23 | 2022-09-04 08:24 | 1812 | 0:01 | T | CABLE SOTERRADO AVERIADO | 75% DE LA CARGA SE SECCIONALIZO ALIMENTADOR | B22090400198 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2022-09-04 | 1812 | keep | 0 | Sep | 2022 | 0.0012341 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-04 08:24 | 2022-09-04 08:52 | 453 | 0:28 | P | CABLE SOTERRADO AVERIADO | 25% DE LA CARGA, SE SECCIONALIZO ALIMENTADOR | B22090400198 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 28 | 2022-09-04 | 12684 | keep | 0 | Sep | 2022 | 0.008639 | 0.00030854 | Sustained | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2022-09-04 08:52 | 2022-09-04 10:48 | 1 | 1:56 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO DE SU-1A @ RISER DE VISTA BELLA BACKUP DEL HOSPITAL AVERIADO | B22090400198 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 116 | 2022-09-04 | 116 | keep | 0 | Sep | 2022 | 7.9007e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-09-04 08:56 | 2022-09-04 10:04 | 12 | 1:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO LA CAJA PRIMARIA AVERIADA EN TRANSFORMADOR | A22090400038 | New_Event | Cutout Failure | Include | Include | Equipment | 68 | 2022-09-04 | 816 | keep | 0 | Sep | 2022 | 0.00055577 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-09-04 08:59 | 2022-09-04 10:20 | 60 | 1:21 | P | ANIMAL | 1 X 80 EN C/L SE RETIRO AVE | B22090400168 | New_Event | Animals | Include | Include | Wildlife | 81 | 2022-09-04 | 4860 | keep | 0 | Sep | 2022 | 0.0033101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-04 08:59 | 2022-09-04 13:00 | 40 | 4:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | A22090400040 | New_Event | Primary Wire Break | Include | Include | Equipment | 241 | 2022-09-04 | 9640 | keep | 0 | Sep | 2022 | 0.0065658 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-04 09:04 | 2022-09-04 09:05 | 3838 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | R22090400000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-04 | 3838 | keep | 0 | Sep | 2022 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
CANOVANAS | 2022-09-04 09:05 | 2022-09-04 19:16 | 40 | 10:11 | P | CONDUCTOR ROTO O ABIERTO | LEVANTO CONDUCTOR NO FUNDIO | R22090400334 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 611 | 2022-09-04 | 24440 | keep | 0 | Sep | 2022 | 0.016646 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-04 09:05 | 2022-09-04 09:09 | 120 | 0:04 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22090400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4 | 2022-09-04 | 480 | keep | 0 | Sep | 2022 | 0.00032693 | 8.1731e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-09-04 09:08 | 2022-09-04 11:13 | 10 | 2:05 | P | ANIMAL | 1 X 30 EN C/L AVE | R22090400055 | New_Event | Animals | Include | Include | Wildlife | 125 | 2022-09-04 | 1250 | keep | 0 | Sep | 2022 | 0.00085137 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-04 09:17 | 2022-09-04 16:05 | 30 | 6:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090400069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 408 | 2022-09-04 | 12240 | keep | 0 | Sep | 2022 | 0.0083366 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-04 09:18 | 2022-09-04 11:44 | 80 | 2:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN C/L SE REMPLAZO CAJA | S22090400078 | New_Event | Cutout Failure | Include | Include | Equipment | 146 | 2022-09-04 | 11680 | keep | 0 | Sep | 2022 | 0.0079552 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-09-04 09:18 | 2022-09-04 13:09 | 5 | 3:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C22090400042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 231 | 2022-09-04 | 1155 | keep | 0 | Sep | 2022 | 0.00078667 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-09-04 09:20 | 2022-09-04 11:56 | 16 | 2:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO LINEA SECUNDARIA SULFATADA | C22090400043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 156 | 2022-09-04 | 2496 | keep | 0 | Sep | 2022 | 0.0017 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-09-04 09:22 | 2022-09-04 09:23 | 413 | 0:01 | P | DESGANCHE | DISPARO 1620-02 Y SE CERRO POR SCADA LLEVA 10% DEL 1206-03 | S22090400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-04 | 413 | keep | 0 | Sep | 2022 | 0.00028129 | 0.00028129 | Momentary | FALSE | FALSE | Not_TMED_Event | 413
SAN JUAN | 2022-09-04 09:22 | 2022-09-04 09:23 | 3718 | 0:01 | T | DESGANCHE | DISPARO 1620-02 Y SE CERRO POR SCADA LLEVA 10% DEL 1206-03 | S22090400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-04 | 3718 | keep | 0 | Sep | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2022-09-04 09:22 | 2022-09-04 09:23 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 2704 | keep | 0 | Sep | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2022-09-04 09:23 | 2022-09-04 12:33 | 26 | 3:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | S22090400084 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 190 | 2022-09-04 | 4940 | keep | 0 | Sep | 2022 | 0.0033646 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
PONCE | 2022-09-04 09:34 | 2022-09-04 13:08 | 60 | 3:34 | P | MAL TIEMPO/RAYOS | 1 X 100 EN RISER 1 X 80 EN SU-1 DESCARGAS ELECTRICAS | P22090400047 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 214 | 2022-09-04 | 12840 | keep | 0 | Sep | 2022 | 0.0087453 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-04 09:38 | 2022-09-04 13:15 | 60 | 3:37 | P | DESGANCHE | SE DESGANCHO ARBOL Y SE CERRO CORTE DE LINEA | M22090400071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-09-04 | 13020 | keep | 0 | Sep | 2022 | 0.0088679 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-04 09:45 | 2022-09-04 09:46 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22090400000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 2704 | keep | 0 | Sep | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
SAN JUAN | 2022-09-04 09:52 | 2022-09-04 11:45 | 100 | 1:53 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22090400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2022-09-04 | 11300 | keep | 0 | Sep | 2022 | 0.0076964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-04 09:52 | 2022-09-04 09:53 | 2147 | 0:01 | T | DESGANCHE | RECIERRE | B22090400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-04 | 2147 | keep | 0 | Sep | 2022 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-09-04 09:53 | 2022-09-04 13:35 | 222 | 3:42 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B22090400190 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 222 | 2022-09-04 | 49284 | keep | 0 | Sep | 2022 | 0.033567 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
AGUADILLA | 2022-09-04 09:56 | 2022-09-04 12:00 | 10 | 2:04 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR / NO SE ENCONTRO CAUSA | A22090400046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-09-04 | 1240 | keep | 0 | Sep | 2022 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-09-04 09:58 | 2022-09-04 11:25 | 20 | 1:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA QUEMADA EN RISER | P22090400050 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2022-09-04 | 1740 | keep | 0 | Sep | 2022 | 0.0011851 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-04 09:59 | 2022-09-04 10:00 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 652 | keep | 0 | Sep | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
SAN JUAN | 2022-09-04 10:00 | 2022-09-04 15:38 | 150 | 5:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L SE REMPLAZO CAJA PRIMARIA | S22090400092 | New_Event | Cutout Failure | Include | Include | Equipment | 338 | 2022-09-04 | 50700 | keep | 0 | Sep | 2022 | 0.034532 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-09-04 10:00 | 2022-09-04 13:28 | 10 | 3:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 37.5KVA POR UNO DE 100KVA | S22090300896 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 208 | 2022-09-04 | 2080 | keep | 0 | Sep | 2022 | 0.0014167 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 10:01 | 2022-09-04 12:19 | 30 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22090400093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-09-04 | 4140 | keep | 0 | Sep | 2022 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-04 10:01 | 2022-09-04 10:02 | 2179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 2179 | keep | 0 | Sep | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2022-09-04 10:02 | 2022-09-04 12:38 | 4 | 2:36 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | R22090400065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-09-04 | 624 | keep | 0 | Sep | 2022 | 0.000425 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-09-04 10:07 | 2022-09-04 12:46 | 60 | 2:39 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA ARBOL CAYO Y CAUSO CRUCE DE LINEAS | A22090400047 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 159 | 2022-09-04 | 9540 | keep | 0 | Sep | 2022 | 0.0064977 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2022-09-04 10:10 | 2022-09-04 11:50 | 200 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | M22090300365 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 100 | 2022-09-04 | 20000 | keep | 0 | Sep | 2022 | 0.013622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-04 10:11 | 2022-09-04 15:12 | 8 | 5:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO PORTAFUSIBLE | B22090400193 | New_Event | Cutout Failure | Include | Include | Equipment | 301 | 2022-09-04 | 2408 | keep | 0 | Sep | 2022 | 0.0016401 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-09-04 10:13 | 2022-09-04 10:44 | 290 | 0:31 | T | DESGANCHE | RECERRO Y QUEDO FUERA SE PROBO Y SE QUEDO EN SERVICIO | S22090400096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2022-09-04 | 8990 | keep | 0 | Sep | 2022 | 0.006123 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
BAYAMON | 2022-09-04 10:13 | 2022-09-04 12:35 | 4622 | 2:22 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO POR MACHETES QUEMADOS MEDIANTE G.O.I. BY-220904-02 Y SE TRANSFIRIO 60% AL 1806-01 | B22090400198 | New_Event | Switch Failure | Include | Include | Equipment | 142 | 2022-09-04 | 656324 | keep | 0 | Sep | 2022 | 0.44702 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
CANOVANAS | 2022-09-04 10:15 | 2022-09-04 11:55 | 2005 | 1:40 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR | R22090400070 | New_Event | Switch Failure | Include | Include | Equipment | 100 | 2022-09-04 | 200500 | keep | 0 | Sep | 2022 | 0.13656 | 0.0013656 | Sustained | FALSE | FALSE | Not_TMED_Event | 2005
CANOVANAS | 2022-09-04 10:25 | 2022-09-04 10:26 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2209040000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 1026 | keep | 0 | Sep | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 849 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 849 | keep | 0 | Sep | 2022 | 0.00057825 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 893 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 893 | keep | 0 | Sep | 2022 | 0.00060822 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 602 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 602 | keep | 0 | Sep | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 43 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 43 | keep | 0 | Sep | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 1389 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 1389 | keep | 0 | Sep | 2022 | 0.00094604 | 0.00094604 | Momentary | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 721 | keep | 0 | Sep | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 325 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 325 | keep | 0 | Sep | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 600 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 600 | keep | 0 | Sep | 2022 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 267 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 267 | keep | 0 | Sep | 2022 | 0.00018185 | 0.00018185 | Momentary | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-09-04 10:34 | 2022-09-04 10:35 | 621 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 | S22090400108 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 621 | keep | 0 | Sep | 2022 | 0.00042296 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
PONCE | 2022-09-04 10:37 | 2022-09-05 08:50 | 1 | 22:13 | P | DESGANCHE | SE FIJO BAJANTE SAFADO EN CAJA TRANSFORMADOR DEBIDO A CAIDA DE RAMA | P22090400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1333 | 2022-09-04 | 1333 | keep | 0 | Sep | 2022 | 0.0009079 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-04 10:38 | 2022-09-04 10:39 | 627 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 627 | keep | 0 | Sep | 2022 | 0.00042705 | 0.00042705 | Momentary | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2022-09-04 10:38 | 2022-09-04 10:39 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 1310-03 LLEVA 1421-05 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 293 | keep | 0 | Sep | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2022-09-04 10:38 | 2022-09-04 10:39 | 761 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900, 1310-04 LLEVA 1421-01 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 761 | keep | 0 | Sep | 2022 | 0.00051831 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-09-04 10:38 | 2022-09-04 10:39 | 451 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 | S22090400105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 451 | keep | 0 | Sep | 2022 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2022-09-04 10:38 | 2022-09-04 10:39 | 1498 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 CARGA DEL 1421-01 ESTA POR 1310-04 | S22090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 1498 | keep | 0 | Sep | 2022 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
PONCE | 2022-09-04 10:43 | 2022-09-04 10:44 | 2308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090400060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 2308 | keep | 0 | Sep | 2022 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
CAGUAS | 2022-09-04 10:47 | 2022-09-04 11:22 | 3 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON TOMAS SULFATADAS | C22090400045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-09-04 | 105 | keep | 0 | Sep | 2022 | 7.1515e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-09-04 10:54 | 2022-09-04 11:33 | 290 | 0:39 | T | DESGANCHE | SE DESGANCHO Y SE CERRO POR SCADA | S22090400096 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 39 | 2022-09-04 | 11310 | keep | 0 | Sep | 2022 | 0.0077032 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-09-04 11:01 | 2022-09-04 16:25 | 6 | 5:24 | P | DESCONECTIVO DEFECTUOSO | 2 X 100 EN CORTE DE LINEA PORTA FUSIBLE DEFECTUOSO | P22090400063 | New_Event | Switch Failure | Include | Include | Equipment | 324 | 2022-09-04 | 1944 | keep | 0 | Sep | 2022 | 0.001324 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-09-04 11:03 | 2022-09-04 14:01 | 50 | 2:58 | P | ANIMAL | 1X30EN C/L & 1X15 EN XMR AVE EN LA LINEA | B22090400268 | New_Event | Animals | Include | Include | Wildlife | 178 | 2022-09-04 | 8900 | keep | 0 | Sep | 2022 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-04 11:05 | 2022-09-05 13:45 | 10 | 26:40 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO @ T-59 | B22090400270 | New_Event | UG Cable Fault | Include | Include | Equipment | 1600 | 2022-09-04 | 16000 | keep | 0 | Sep | 2022 | 0.010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-04 11:06 | 2022-09-04 15:47 | 130 | 4:41 | P | NO SE REPORTO CAUSA | 2X80 EN C/L | B22090400272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 281 | 2022-09-04 | 36530 | keep | 0 | Sep | 2022 | 0.02488 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
HUMACAO | 2022-09-04 11:10 | 2022-09-04 11:11 | 2450 | 0:01 | T | ANIMAL | RECIERRE | C22090400051 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-04 | 2450 | keep | 0 | Sep | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-09-04 11:11 | 2022-09-04 14:05 | 50 | 2:54 | P | ANIMAL | 1 X 65 EN C/L SE REEMPLAZO ASILADOR CRUCE POR AVE | C22090400055 | 1st_after_momentary | Animals | Include | Include | Wildlife | 174 | 2022-09-04 | 8700 | keep | 0 | Sep | 2022 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-04 11:11 | 2022-09-04 11:56 | 50 | 0:45 | P | ANIMAL | 1 X 30 Y 1 X 40 EN CORTES DE LINEA CRUCE CON AVE | C22090400025 | New_Event | Animals | Include | Include | Wildlife | 45 | 2022-09-04 | 2250 | keep | 0 | Sep | 2022 | 0.0015325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-04 11:17 | 2022-09-04 16:09 | 60 | 4:52 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | B22090400287 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2022-09-04 | 17520 | keep | 0 | Sep | 2022 | 0.011933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-04 11:19 | 2022-09-04 12:56 | 50 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22090400123 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2022-09-04 | 4850 | keep | 0 | Sep | 2022 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-04 11:23 | 2022-09-04 11:24 | 766 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 CARGA DEL 1421-05 ESTA POR 1310-03 | S22090400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 766 | keep | 0 | Sep | 2022 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 849 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22090400165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 22923 | keep | 0 | Sep | 2022 | 0.015613 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 893 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22090400165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 24111 | keep | 0 | Sep | 2022 | 0.016422 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 602 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22090400165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 16254 | keep | 0 | Sep | 2022 | 0.011071 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 43 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22090400165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 1161 | keep | 0 | Sep | 2022 | 0.00079075 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 1389 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 | S22090400165 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 37503 | keep | 0 | Sep | 2022 | 0.025543 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 673 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400131 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 16825 | keep | 0 | Sep | 2022 | 0.011459 | 0.00045838 | Sustained | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 372 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400131 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 9300 | keep | 0 | Sep | 2022 | 0.0063342 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 732 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400131 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 18300 | keep | 0 | Sep | 2022 | 0.012464 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 721 | 0:27 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 19467 | keep | 0 | Sep | 2022 | 0.013259 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 325 | 0:27 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 8775 | keep | 0 | Sep | 2022 | 0.0059766 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 600 | 0:27 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 16200 | keep | 0 | Sep | 2022 | 0.011034 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 267 | 0:27 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 7209 | keep | 0 | Sep | 2022 | 0.00491 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:54 | 621 | 0:27 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2022-09-04 | 16767 | keep | 0 | Sep | 2022 | 0.01142 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 2203 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 55075 | keep | 0 | Sep | 2022 | 0.037511 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 246 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 6150 | keep | 0 | Sep | 2022 | 0.0041887 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 9 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 225 | keep | 0 | Sep | 2022 | 0.00015325 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 601 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 15025 | keep | 0 | Sep | 2022 | 0.010233 | 0.00040934 | Sustained | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 640 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 16000 | keep | 0 | Sep | 2022 | 0.010898 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 1699 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 42475 | keep | 0 | Sep | 2022 | 0.02893 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 892 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 22300 | keep | 0 | Sep | 2022 | 0.015188 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-09-04 11:27 | 2022-09-04 11:52 | 1066 | 0:25 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 25 | 2022-09-04 | 26650 | keep | 0 | Sep | 2022 | 0.018151 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2022-09-04 11:29 | 2022-09-04 13:05 | 3 | 1:36 | T | DESGANCHE | SE RETIRO RAMA DE LA LINEA Y SE CERRO BKR POR CONTROL LLEVA 1707-03 | B22090400303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-09-04 | 288 | keep | 0 | Sep | 2022 | 0.00019616 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-09-04 11:29 | 2022-09-04 13:05 | 61 | 1:36 | T | DESGANCHE | SE RETIRO RAMA DE LA LINEA Y SE CERRO BKR 1707-02 POR CONTROL LLEVA 1707-03 | B22090400303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-09-04 | 5856 | keep | 0 | Sep | 2022 | 0.0039885 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
HUMACAO | 2022-09-04 11:31 | 2022-09-05 11:40 | 225 | 24:09 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50, 1 X 30, 1 X 25 Y 1 X 10 EN CORTES DE LINEA Y TRANSFORMADOR SE LEVANTO CONDUCTOR DEL SUELO | C22090400581 | New_Event | Primary Wire Break | Include | Include | Equipment | 1449 | 2022-09-04 | 326025 | keep | 0 | Sep | 2022 | 0.22205 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
MAYAGÃœEZ | 2022-09-04 11:31 | 2022-09-04 22:22 | 150 | 10:51 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M22090400124 | New_Event | Primary Wire Break | Include | Include | Equipment | 651 | 2022-09-04 | 97650 | keep | 0 | Sep | 2022 | 0.066509 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2022-09-04 11:44 | 2022-09-04 17:03 | 30 | 5:19 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | C22090400086 | New_Event | Primary Wire Break | Include | Include | Equipment | 319 | 2022-09-04 | 9570 | keep | 0 | Sep | 2022 | 0.0065181 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-09-04 11:44 | 2022-09-04 16:31 | 25 | 4:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C22090400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 287 | 2022-09-04 | 7175 | keep | 0 | Sep | 2022 | 0.0048869 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-09-04 11:45 | 2022-09-04 11:50 | 1106 | 0:05 | P | DESGANCHE | DISPARO 1529-15 QUE LLEVA 60% DEL 1346-02 Y SE CERRO POR SCADA | S22090400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-09-04 | 5530 | keep | 0 | Sep | 2022 | 0.0037665 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-09-04 11:45 | 2022-09-04 11:50 | 1802 | 0:05 | T | DESGANCHE | DISPARO 1529-15 QUE LLEVA 60% DEL 1346-02 Y SE CERRO POR SCADA | S22090400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-09-04 | 9010 | keep | 0 | Sep | 2022 | 0.0061367 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2022-09-04 11:50 | 2022-09-04 13:09 | 100 | 1:19 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S22090400090 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 79 | 2022-09-04 | 7900 | keep | 0 | Sep | 2022 | 0.0053807 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 11:51 | 2022-09-04 12:33 | 627 | 0:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400202 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-09-04 | 26334 | keep | 0 | Sep | 2022 | 0.017936 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2022-09-04 11:51 | 2022-09-04 12:33 | 293 | 0:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400202 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-09-04 | 12306 | keep | 0 | Sep | 2022 | 0.0083816 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2022-09-04 11:51 | 2022-09-04 12:33 | 761 | 0:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400202 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-09-04 | 31962 | keep | 0 | Sep | 2022 | 0.021769 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2022-09-04 11:51 | 2022-09-04 12:33 | 451 | 0:42 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400202 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-09-04 | 18942 | keep | 0 | Sep | 2022 | 0.012901 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
UTUADO | 2022-09-04 11:52 | 2022-09-04 14:21 | 90 | 2:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-09-04 | 13410 | keep | 0 | Sep | 2022 | 0.0091335 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2022-09-04 11:53 | 2022-09-04 19:00 | 18 | 7:07 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L LEVANTO CONDUCTOR | R22090400167 | New_Event | Primary Wire Break | Include | Include | Equipment | 427 | 2022-09-04 | 7686 | keep | 0 | Sep | 2022 | 0.0052349 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2022-09-04 11:55 | 2022-09-04 14:20 | 802 | 2:25 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES EN VARIOS PUNTOS | R22090400070 | Partial_restoration | Switch Failure | Include | Include | Equipment | 145 | 2022-09-04 | 116290 | keep | 0 | Sep | 2022 | 0.079205 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-04 12:06 | 2022-09-05 03:44 | 20 | 15:38 | P | ARBOL SOBRE LINEA | 1 X 25 EN CORTE DE LINEA SE RETIRO ARBOL Y SE LEVANTO LINEA | C22090400064 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 938 | 2022-09-04 | 18760 | keep | 0 | Sep | 2022 | 0.012777 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-09-04 12:08 | 2022-09-04 13:50 | 60 | 1:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M22090400132 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 102 | 2022-09-04 | 6120 | keep | 0 | Sep | 2022 | 0.0041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-04 12:09 | 2022-09-04 13:16 | 1221 | 1:07 | T | DESGANCHE | SE RETIRO RAMA Y SE CERRO POR CONTROL | B22090400328 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2022-09-04 | 81807 | keep | 0 | Sep | 2022 | 0.055718 | 0.00083162 | Sustained | FALSE | FALSE | Not_TMED_Event | 1221
SAN JUAN | 2022-09-04 12:10 | 2022-09-05 15:39 | 20 | 27:29 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL T-12 @ T-11 MEDIANTE G.O.I. SJ-220904-03 TODO QUEDO EN SERVICIO | S22090400454 | New_Event | UG Cable Fault | Include | Include | Equipment | 1649 | 2022-09-04 | 32980 | keep | 0 | Sep | 2022 | 0.022463 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-04 12:10 | 2022-09-04 12:11 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090400066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 181 | keep | 0 | Sep | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
MAYAGÃœEZ | 2022-09-04 12:11 | 2022-09-04 14:54 | 11 | 2:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090400133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 163 | 2022-09-04 | 1793 | keep | 0 | Sep | 2022 | 0.0012212 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2022-09-04 12:13 | 2022-09-04 15:30 | 3 | 3:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | M22090400134 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2022-09-04 | 591 | keep | 0 | Sep | 2022 | 0.00040253 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2022-09-04 12:15 | 2022-09-04 12:18 | 853 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-04 | 2559 | keep | 0 | Sep | 2022 | 0.0017429 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
HUMACAO | 2022-09-04 12:19 | 2022-09-04 15:11 | 80 | 2:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22090400072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2022-09-04 | 13760 | keep | 0 | Sep | 2022 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 849 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZO POR LINEA 7200 | S22090400165 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 105276 | keep | 0 | Sep | 2022 | 0.071703 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 893 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZO POR LINEA 7200 | S22090400165 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 110732 | keep | 0 | Sep | 2022 | 0.075419 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 602 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE ENERGIZO POR LINEA 7200 | S22090400165 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 74648 | keep | 0 | Sep | 2022 | 0.050842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 43 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400165 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 5332 | keep | 0 | Sep | 2022 | 0.0036316 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 1389 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400165 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 172236 | keep | 0 | Sep | 2022 | 0.11731 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 12:33 | 673 | 0:12 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400134 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-04 | 8076 | keep | 0 | Sep | 2022 | 0.0055005 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 12:33 | 372 | 0:12 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400131 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-04 | 4464 | keep | 0 | Sep | 2022 | 0.0030404 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 12:33 | 732 | 0:12 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400134 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-04 | 8784 | keep | 0 | Sep | 2022 | 0.0059827 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 12:33 | 637 | 0:12 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-04 | 7644 | keep | 0 | Sep | 2022 | 0.0052063 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 721 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400167 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 89404 | keep | 0 | Sep | 2022 | 0.060893 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 325 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 40300 | keep | 0 | Sep | 2022 | 0.027448 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 600 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 74400 | keep | 0 | Sep | 2022 | 0.050674 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 267 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400167 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 33108 | keep | 0 | Sep | 2022 | 0.02255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 12:21 | 2022-09-04 14:25 | 621 | 2:04 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 3200 | S22090400163 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 124 | 2022-09-04 | 77004 | keep | 0 | Sep | 2022 | 0.052447 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-09-04 12:22 | 2022-09-04 19:40 | 60 | 7:18 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M22090400139 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 438 | 2022-09-04 | 26280 | keep | 0 | Sep | 2022 | 0.017899 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-04 12:23 | 2022-09-04 12:24 | 1526 | 0:01 | T | ANIMAL | RECERRO | B22090400000 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-04 | 1526 | keep | 0 | Sep | 2022 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
HUMACAO | 2022-09-04 12:24 | 2022-09-04 17:04 | 15 | 4:40 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO | C22090400075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2022-09-04 | 4200 | keep | 0 | Sep | 2022 | 0.0028606 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-04 12:24 | 2022-09-04 15:21 | 40 | 2:57 | P | ANIMAL | 1X50 EN C/L POR CRUCE DE AVE | B22090400362 | 1st_after_momentary | Animals | Include | Include | Wildlife | 177 | 2022-09-04 | 7080 | keep | 0 | Sep | 2022 | 0.0048222 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-04 12:35 | 2022-09-04 20:39 | 80 | 8:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X140 EN C/L Y 1X80 EN OTRO C/L SE REMPLAZO CAJA PRIMARIA | B22090400105 | New_Event | Cutout Failure | Include | Include | Equipment | 484 | 2022-09-04 | 38720 | keep | 0 | Sep | 2022 | 0.026372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-04 12:35 | 2022-09-04 18:59 | 1848 | 6:24 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO Y SE ELIMINO ARBOL A VARETA (DESDE EL PISO) MEDIANTE G.O.I. BY-220904-02 (SE NORMALIZARON LAS CARGAS) | B22090400198 | Partial_restoration | Switch Failure | Include | Include | Equipment | 384 | 2022-09-04 | 709632 | keep | 0 | Sep | 2022 | 0.48333 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-04 12:35 | 2022-09-04 14:40 | 80 | 2:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090400140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-09-04 | 10000 | keep | 0 | Sep | 2022 | 0.006811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2022-09-04 12:36 | 2022-09-04 13:40 | 215 | 1:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS SE CERRO CORTE DE LINEA | M22090300323 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 64 | 2022-09-04 | 13760 | keep | 0 | Sep | 2022 | 0.0093719 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-09-04 12:45 | 2022-09-04 12:46 | 2308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090400074 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 2308 | keep | 0 | Sep | 2022 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
MAYAGÃœEZ | 2022-09-04 12:46 | 2022-09-04 15:10 | 20 | 2:24 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR SOBRE CARGA | M22090400145 | New_Event | Trip Due To Overload | Include | Include | Other | 144 | 2022-09-04 | 2880 | keep | 0 | Sep | 2022 | 0.0019616 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-09-04 13:02 | 2022-09-04 17:21 | 30 | 4:19 | P | DESGANCHE | 1 X 30 EN C/L | R22090400211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2022-09-04 | 7770 | keep | 0 | Sep | 2022 | 0.0052921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-09-04 13:07 | 2022-09-04 13:08 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090400088 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 181 | keep | 0 | Sep | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
CANOVANAS | 2022-09-04 13:14 | 2022-09-04 16:20 | 30 | 3:06 | P | DESGANCHE | 1 X 30 EN C/L | R22090400214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-09-04 | 5580 | keep | 0 | Sep | 2022 | 0.0038005 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-09-04 13:17 | 2022-09-04 15:08 | 30 | 1:51 | P | DESGANCHE | 1 X 10 EN XMR Y 1 X 50 EN C/L DESGANCHE | C22090400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2022-09-04 | 3330 | keep | 0 | Sep | 2022 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-04 13:32 | 2022-09-04 14:26 | 10 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S22090400069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2022-09-04 | 540 | keep | 0 | Sep | 2022 | 0.00036779 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-09-04 13:34 | 2022-09-04 13:51 | 6 | 0:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | A22090400044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 17 | 2022-09-04 | 102 | keep | 0 | Sep | 2022 | 6.9472e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-09-04 13:35 | 2022-09-05 10:03 | 60 | 20:28 | P | ANIMAL | 1X30 EN XMR SE RETIRO IGUANA | S22090400455 | New_Event | Animals | Include | Include | Wildlife | 1228 | 2022-09-04 | 73680 | keep | 0 | Sep | 2022 | 0.050183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-04 13:35 | 2022-09-04 13:36 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 2704 | keep | 0 | Sep | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
VEGA BAJA | 2022-09-04 13:47 | 2022-09-04 13:48 | 652 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B22090400000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-04 | 652 | keep | 0 | Sep | 2022 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2022-09-04 13:48 | 2022-09-05 10:55 | 10 | 21:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN RISER | B22090400542 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1267 | 2022-09-04 | 12670 | keep | 0 | Sep | 2022 | 0.0086295 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-04 13:53 | 2022-09-04 13:55 | 827 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 1620-05 LLEVA 20% DE 1206-03 CERRADO POR SCADA | S22090400469 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-04 | 1654 | keep | 0 | Sep | 2022 | 0.0011265 | 0.00056327 | Momentary | FALSE | FALSE | Not_TMED_Event | 827
SAN JUAN | 2022-09-04 13:53 | 2022-09-04 13:55 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 1620-05 LLEVA 20% DE 1206-03 CERRADO POR SCADA | S22090400469 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-04 | 3230 | keep | 0 | Sep | 2022 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
UTUADO | 2022-09-04 13:53 | 2022-09-04 16:08 | 50 | 2:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090400074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2022-09-04 | 6750 | keep | 0 | Sep | 2022 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-09-04 13:54 | 2022-09-04 15:47 | 8 | 1:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22090400088 | New_Event | Secondary Wire Break | Include | Include | Equipment | 113 | 2022-09-04 | 904 | keep | 0 | Sep | 2022 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-09-04 13:56 | 2022-09-04 13:57 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090400089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 449 | keep | 0 | Sep | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
SAN JUAN | 2022-09-04 13:58 | 2022-09-04 14:05 | 2203 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 OCASIONO DISPARO DEL 0050, SE SECCIONALIZO Y SE ENERGIZO LINEA 17000 | S22090400134 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-04 | 15421 | keep | 0 | Sep | 2022 | 0.010503 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 13:58 | 2022-09-04 14:05 | 246 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 OCASIONO DISPARO DEL 0050, SE SECCIONALIZO Y SE ENERGIZO LINEA 17000 | S22090400134 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-04 | 1722 | keep | 0 | Sep | 2022 | 0.0011728 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 13:58 | 2022-09-04 14:05 | 9 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3200 OCASIONO DISPARO DEL 0050, SE SECCIONALIZO Y SE ENERGIZO LINEA 17000 | S22090400134 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-04 | 63 | keep | 0 | Sep | 2022 | 4.2909e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-04 14:03 | 2022-09-04 18:11 | 20 | 4:08 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHO | R22090400250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2022-09-04 | 4960 | keep | 0 | Sep | 2022 | 0.0033782 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-04 14:03 | 2022-09-04 14:04 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22090400431 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 2704 | keep | 0 | Sep | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2022-09-04 14:14 | 2022-09-04 16:26 | 1221 | 2:12 | T | DESGANCHE | SE SECCIONALIZO PARA DESGANCHE - MEDIANTE G.O.I. BY-220904-05 - 80% EN SERVICIO | B22090400433 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-09-04 | 161172 | keep | 0 | Sep | 2022 | 0.10977 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-09-04 14:15 | 2022-09-04 17:34 | 15 | 3:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22090401009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-09-04 | 2985 | keep | 0 | Sep | 2022 | 0.0020331 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-09-04 14:17 | 2022-09-04 16:37 | 40 | 2:20 | P | DESGANCHE | 1 X 40 EN C/L | R22090400261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-09-04 | 5600 | keep | 0 | Sep | 2022 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-04 14:20 | 2022-09-04 14:21 | 2005 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO PERSONAL REALIZANDO OPERACIONES | R22090400070 | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2022-09-04 | 2005 | keep | 0 | Sep | 2022 | 0.0013656 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-04 14:20 | 2022-09-04 14:21 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22090400460 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 1362 | keep | 0 | Sep | 2022 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2022-09-04 14:20 | 2022-09-04 16:06 | 60 | 1:46 | P | ARBOL SOBRE LINEA | 1X50 EN C/L SE RETIRO ARBOL COMPLETO DE LA LINEA | B22090400453 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 106 | 2022-09-04 | 6360 | keep | 0 | Sep | 2022 | 0.0043318 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-09-04 14:21 | 2022-09-04 15:40 | 802 | 1:19 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZARON MACHETES EN VARIOS PUNTOS | R22090400070 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 79 | 2022-09-04 | 63358 | keep | 0 | Sep | 2022 | 0.043153 | 0.00054624 | Sustained | FALSE | FALSE | Not_TMED_Event | 802
BARRANQUITAS | 2022-09-04 14:22 | 2022-09-04 17:38 | 25 | 3:16 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | C22090400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2022-09-04 | 4900 | keep | 0 | Sep | 2022 | 0.0033374 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-09-04 14:23 | 2022-09-04 16:54 | 8 | 2:31 | P | ANIMAL | 1X15 EN XMR POR SERPIENTE QUE SE CRUZO | B22090400456 | New_Event | Animals | Include | Include | Wildlife | 151 | 2022-09-04 | 1208 | keep | 0 | Sep | 2022 | 0.00082276 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-09-04 14:28 | 2022-09-04 14:29 | 2770 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 2770 | keep | 0 | Sep | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
HUMACAO | 2022-09-04 14:30 | 2022-09-04 14:31 | 181 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 181 | keep | 0 | Sep | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
GUAYAMA | 2022-09-04 14:31 | 2022-09-04 16:01 | 15 | 1:30 | P | DESGANCHE | 1 X 65 C/L DESGANCHE | P22090400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2022-09-04 | 1350 | keep | 0 | Sep | 2022 | 0.00091948 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-09-04 14:38 | 2022-09-04 16:13 | 100 | 1:35 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090400163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-09-04 | 9500 | keep | 0 | Sep | 2022 | 0.0064704 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-04 14:48 | 2022-09-04 15:58 | 1565 | 1:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22090400126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-09-04 | 109550 | keep | 0 | Sep | 2022 | 0.074614 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2022-09-04 14:48 | 2022-09-04 15:58 | 976 | 1:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22090400126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-09-04 | 68320 | keep | 0 | Sep | 2022 | 0.046532 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2022-09-04 14:48 | 2022-09-04 15:58 | 548 | 1:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 | C22090400126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 70 | 2022-09-04 | 38360 | keep | 0 | Sep | 2022 | 0.026127 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
SAN JUAN | 2022-09-04 14:52 | 2022-09-04 17:51 | 5 | 2:59 | P | DESGANCHE | 2 X 30 EN C/L | S22090400521 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2022-09-04 | 895 | keep | 0 | Sep | 2022 | 0.00060958 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-09-04 14:56 | 2022-09-04 18:27 | 1 | 3:31 | P | NO SE REPORTO CAUSA | 1X65 EN C/L1X65 EN C/L | B22090400476 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2022-09-04 | 211 | keep | 0 | Sep | 2022 | 0.00014371 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-04 14:59 | 2022-09-04 15:00 | 2302 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 2302 | keep | 0 | Sep | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
FAJARDO | 2022-09-04 15:03 | 2022-09-04 21:10 | 10 | 6:07 | P | DESGANCHE | 1 X 20 EN C/L | R22090400285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2022-09-04 | 3670 | keep | 0 | Sep | 2022 | 0.0024996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-04 15:07 | 2022-09-04 19:19 | 20 | 4:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | R22090400287 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 252 | 2022-09-04 | 5040 | keep | 0 | Sep | 2022 | 0.0034327 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-04 15:10 | 2022-09-04 15:40 | 673 | 0:30 | T | POWER TRANSFORMER AVERIADO | MEDIANTE SJ-220904-02 SE RETIRO CARGA PARA TRABAJAR CON REGULADOR TRANCADO SE CORRIGIO Y SE NORMALIZO LAS CARGAS | S22090400530 | New_Event | Power Transformer Failure | Include | Include | Equipment | 30 | 2022-09-04 | 20190 | keep | 0 | Sep | 2022 | 0.013751 | 0.00045838 | Sustained | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2022-09-04 15:10 | 2022-09-04 15:40 | 372 | 0:30 | T | POWER TRANSFORMER AVERIADO | MEDIANTE SJ-220904-02 SE RETIRO CARGA PARA TRABAJAR CON REGULADOR TRANCADO SE CORRIGIO Y SE NORMALIZO LAS CARGAS | S22090400530 | New_Event | Power Transformer Failure | Include | Include | Equipment | 30 | 2022-09-04 | 11160 | keep | 0 | Sep | 2022 | 0.007601 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-09-04 15:10 | 2022-09-04 15:40 | 732 | 0:30 | T | POWER TRANSFORMER AVERIADO | MEDIANTE SJ-220904-02 SE RETIRO CARGA PARA TRABAJAR CON REGULADOR TRANCADO SE CORRIGIO Y SE NORMALIZO LAS CARGAS | S22090400530 | New_Event | Power Transformer Failure | Include | Include | Equipment | 30 | 2022-09-04 | 21960 | keep | 0 | Sep | 2022 | 0.014957 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
CAGUAS | 2022-09-04 15:18 | 2022-09-04 16:56 | 40 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | C22090400232 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2022-09-04 | 3920 | keep | 0 | Sep | 2022 | 0.0026699 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-09-04 15:18 | 2022-09-05 15:58 | 835 | 24:40 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA Y SE LEVANTO CONDUCTOR PRIMARIO | C22090400358 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1480 | 2022-09-04 | 1235800 | keep | 0 | Sep | 2022 | 0.8417 | 0.00056871 | Sustained | FALSE | FALSE | Not_TMED_Event | 835
BARRANQUITAS | 2022-09-04 15:18 | 2022-09-04 18:50 | 20 | 3:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REEMPLAZO AISLADOR | C22090400236 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 212 | 2022-09-04 | 4240 | keep | 0 | Sep | 2022 | 0.0028878 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-09-04 15:19 | 2022-09-04 15:20 | 1830 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 1830 | keep | 0 | Sep | 2022 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
HUMACAO | 2022-09-04 15:24 | 2022-09-04 15:25 | 181 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 181 | keep | 0 | Sep | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
CAGUAS | 2022-09-04 15:24 | 2022-09-04 18:17 | 50 | 2:53 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22090400258 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2022-09-04 | 8650 | keep | 0 | Sep | 2022 | 0.0058915 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-04 15:25 | 2022-09-04 15:26 | 776 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400276 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 776 | keep | 0 | Sep | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2022-09-04 15:26 | 2022-09-04 15:28 | 1089 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 3000 | C22090400556 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-04 | 2178 | keep | 0 | Sep | 2022 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2022-09-04 15:26 | 2022-09-04 15:28 | 3896 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 3000 | C22090400556 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-04 | 7792 | keep | 0 | Sep | 2022 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2022-09-04 15:26 | 2022-09-04 15:28 | 1467 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 3000 | C22090400556 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-04 | 2934 | keep | 0 | Sep | 2022 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-09-04 15:28 | 2022-09-04 15:29 | 181 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400284 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 181 | keep | 0 | Sep | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2022-09-04 15:28 | 2022-09-04 15:32 | 2126 | 0:04 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR SE CERRO POR CONTROL MAL TIEMPO LLUVIAS | C22090400284 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 4 | 2022-09-04 | 8504 | keep | 0 | Sep | 2022 | 0.005792 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2022-09-04 15:30 | 2022-09-05 03:44 | 73 | 12:14 | P | DESGANCHE | 2 X 65 EN CORTES DE LINEA | C22090400601 | New_Event | Vegetation Contact | Include | Include | Vegetation | 734 | 2022-09-04 | 53582 | keep | 0 | Sep | 2022 | 0.036494 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
CAGUAS | 2022-09-04 15:30 | 2022-09-04 16:33 | 10 | 1:03 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C22090400291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-09-04 | 630 | keep | 0 | Sep | 2022 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-04 15:31 | 2022-09-05 06:21 | 80 | 14:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22090400295 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 890 | 2022-09-04 | 71200 | keep | 0 | Sep | 2022 | 0.048494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-09-04 15:31 | 2022-09-04 17:02 | 6 | 1:31 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO BAMBUA CAIDA SOBRE EL TRANSFORMADOR | A22090400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-09-04 | 546 | keep | 0 | Sep | 2022 | 0.00037188 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-09-04 15:32 | 2022-09-05 09:32 | 150 | 18:00 | P | DESGANCHE | 1X80 EN C/L | S22090400537 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1080 | 2022-09-04 | 162000 | keep | 0 | Sep | 2022 | 0.11034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-09-04 15:32 | 2022-09-04 15:33 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090400105 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 449 | keep | 0 | Sep | 2022 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
AGUADILLA | 2022-09-04 15:32 | 2022-09-04 16:40 | 30 | 1:08 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22090400090 | New_Event | Animals | Include | Include | Wildlife | 68 | 2022-09-04 | 2040 | keep | 0 | Sep | 2022 | 0.0013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2022-09-04 15:35 | 2022-09-04 19:41 | 105 | 4:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | C22090400323 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 246 | 2022-09-04 | 25830 | keep | 0 | Sep | 2022 | 0.017593 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2022-09-04 15:36 | 2022-09-04 17:40 | 1079 | 2:04 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA DE MH-20 @ MH-24 Y SE CERRO POR SCADA EN SERVICIO SJ-220904-04 90% EN SERVICIO | S22090400538 | New_Event | UG Cable Fault | Include | Include | Equipment | 124 | 2022-09-04 | 133796 | keep | 0 | Sep | 2022 | 0.091128 | 0.0007349 | Sustained | FALSE | FALSE | Not_TMED_Event | 1079
PONCE | 2022-09-04 15:38 | 2022-09-04 16:34 | 653 | 0:56 | T | DESGANCHE | DISPARO INTERRUPTOR | P22090400108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-09-04 | 36568 | keep | 0 | Sep | 2022 | 0.024906 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
HUMACAO | 2022-09-04 15:39 | 2022-09-04 15:40 | 776 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 776 | keep | 0 | Sep | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2022-09-04 15:41 | 2022-09-04 15:42 | 181 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | C22090400000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-04 | 181 | keep | 0 | Sep | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
CAGUAS | 2022-09-04 15:41 | 2022-09-04 17:02 | 50 | 1:21 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L MAL TIEMPO RAYO | C22090400345 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 81 | 2022-09-04 | 4050 | keep | 0 | Sep | 2022 | 0.0027584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-04 15:42 | 2022-09-04 15:44 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S22090400545 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-04 | 4932 | keep | 0 | Sep | 2022 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
HUMACAO | 2022-09-04 15:42 | 2022-09-04 15:43 | 3701 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | C22090400504 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 3701 | keep | 0 | Sep | 2022 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2022-09-04 15:42 | 2022-09-04 15:43 | 989 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | C22090400504 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 989 | keep | 0 | Sep | 2022 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2022-09-04 15:42 | 2022-09-04 15:43 | 1467 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 | C22090400504 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-04 | 1467 | keep | 0 | Sep | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
CAGUAS | 2022-09-04 15:43 | 2022-09-05 13:13 | 20 | 21:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | S22090400539 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1290 | 2022-09-04 | 25800 | keep | 0 | Sep | 2022 | 0.017572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-09-04 15:44 | 2022-09-04 18:20 | 1 | 2:36 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22090400171 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 156 | 2022-09-04 | 156 | keep | 0 | Sep | 2022 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-09-04 15:48 | 2022-09-04 17:05 | 80 | 1:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22090400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-09-04 | 6160 | keep | 0 | Sep | 2022 | 0.0041955 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-09-04 15:54 | 2022-09-04 20:42 | 70 | 4:48 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L MAL TIEMPO RAYOS | C22090400402 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 288 | 2022-09-04 | 20160 | keep | 0 | Sep | 2022 | 0.013731 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-09-04 15:55 | 2022-09-04 17:33 | 40 | 1:38 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | P22090400118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2022-09-04 | 3920 | keep | 0 | Sep | 2022 | 0.0026699 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-09-04 15:58 | 2022-09-04 17:14 | 100 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA / LLUVIA Y VIENTO FUERTE VERIFICADO EN OMS EVENTO CON M | M22090400175 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2022-09-04 | 7600 | keep | 0 | Sep | 2022 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-04 15:59 | 2022-09-04 16:57 | 50 | 0:58 | P | ANIMAL | 1X100 EN C/L POR AVE EN LA LINEA | B22090400506 | New_Event | Animals | Include | Include | Wildlife | 58 | 2022-09-04 | 2900 | keep | 0 | Sep | 2022 | 0.0019752 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-09-04 16:00 | 2022-09-04 18:30 | 80 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | 2 X 10 EN XMR SE LEVANTO CONDUCTOR PRIMARIO | C22090400426 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2022-09-04 | 12000 | keep | 0 | Sep | 2022 | 0.0081731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-09-04 16:01 | 2022-09-04 16:02 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090400123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 527 | keep | 0 | Sep | 2022 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
GUAYAMA | 2022-09-04 16:02 | 2022-09-04 17:45 | 15 | 1:43 | P | DESGANCHE | 1 X 65 C/L DESGANCHE | P22090400094 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-09-04 | 1545 | keep | 0 | Sep | 2022 | 0.0010523 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-04 16:04 | 2022-09-05 12:03 | 120 | 19:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | S22090400561 | New_Event | Cutout Failure | Include | Include | Equipment | 1199 | 2022-09-04 | 143880 | keep | 0 | Sep | 2022 | 0.097996 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
FAJARDO | 2022-09-04 16:04 | 2022-09-04 17:11 | 45 | 1:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES LLUVIAS | R22090400305 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 67 | 2022-09-04 | 3015 | keep | 0 | Sep | 2022 | 0.0020535 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2022-09-04 16:05 | 2022-09-04 17:52 | 20 | 1:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L POR LLUVIAS | B22090400514 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 107 | 2022-09-04 | 2140 | keep | 0 | Sep | 2022 | 0.0014575 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-09-04 16:10 | 2022-09-04 20:21 | 30 | 4:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L Y 1 X 10 EN XMR LLUVIAS | R22090400311 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 251 | 2022-09-04 | 7530 | keep | 0 | Sep | 2022 | 0.0051286 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-09-04 16:20 | 2022-09-04 19:20 | 290 | 3:00 | T | CONDUCTOR ROTO O ABIERTO | PUNTES ABIERTOS | P22090400133 | New_Event | Primary Wire Break | Include | Include | Equipment | 180 | 2022-09-04 | 52200 | keep | 0 | Sep | 2022 | 0.035553 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
MAYAGÃœEZ | 2022-09-04 16:20 | 2022-09-04 16:45 | 25 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22090400180 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-09-04 | 625 | keep | 0 | Sep | 2022 | 0.00042568 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-09-04 16:26 | 2022-09-04 18:26 | 244 | 2:00 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO MASIVO - MEDIANTE G.O.I. BY-220904-05 - EN SERVICIO EL 20% QUE QUEDABA FUERA | B22090400433 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 120 | 2022-09-04 | 29280 | keep | 0 | Sep | 2022 | 0.019942 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-04 16:26 | 2022-09-04 17:32 | 200 | 1:06 | P | DESGANCHE | 2 X 140 EN RISER 1 X 200 EN C/L DESGANCHE | C22090400516 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2022-09-04 | 13200 | keep | 0 | Sep | 2022 | 0.0089905 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2022-09-04 16:28 | 2022-09-04 17:12 | 266 | 0:44 | P | MAL TIEMPO/RAYOS | SE CERRO EL PB-2501-3F RAYOS | R22090400319 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 44 | 2022-09-04 | 11704 | keep | 0 | Sep | 2022 | 0.0079715 | 0.00018117 | Sustained | FALSE | FALSE | Not_TMED_Event | 266
PONCE | 2022-09-04 16:34 | 2022-09-04 17:09 | 65 | 0:35 | P | DESGANCHE | SE HIZO DESGANCHE Y SE CERRO CORTE DE LINEA COMPLETANDO EL SERVICIO | P22090400108 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 35 | 2022-09-04 | 2275 | keep | 0 | Sep | 2022 | 0.0015495 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-04 16:37 | 2022-09-04 19:30 | 80 | 2:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | C22090400561 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 173 | 2022-09-04 | 13840 | keep | 0 | Sep | 2022 | 0.0094264 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-09-04 16:37 | 2022-09-04 16:38 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090400140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 4279 | keep | 0 | Sep | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
YAUCO | 2022-09-04 16:39 | 2022-09-04 18:33 | 70 | 1:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22090400142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-09-04 | 7980 | keep | 0 | Sep | 2022 | 0.0054351 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2022-09-04 16:43 | 2022-09-04 16:44 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090400149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 4132 | keep | 0 | Sep | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2022-09-04 16:43 | 2022-09-04 22:42 | 50 | 5:59 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090400145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2022-09-04 | 17950 | keep | 0 | Sep | 2022 | 0.012226 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-09-04 16:45 | 2022-09-04 18:25 | 3 | 1:40 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA ROTA | A22090400096 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 100 | 2022-09-04 | 300 | keep | 0 | Sep | 2022 | 0.00020433 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2022-09-04 16:48 | 2022-09-04 21:00 | 25 | 4:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | C22090400585 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 252 | 2022-09-04 | 6300 | keep | 0 | Sep | 2022 | 0.0042909 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2022-09-04 16:53 | 2022-09-04 16:54 | 2697 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | A22090400099 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-04 | 2697 | keep | 0 | Sep | 2022 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2022-09-04 16:54 | 2022-09-04 18:53 | 400 | 1:59 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA SE REPARO CONDICION DE PUENTE PRIMARIO QUE ESTABA MUY CERCA DE POSTE DE METAL Y UN AVE CAUSO CRUCE A TIERRA | A22090400100 | 1st_after_momentary | Animals | Include | Include | Wildlife | 119 | 2022-09-04 | 47600 | keep | 0 | Sep | 2022 | 0.03242 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
GUAYAMA | 2022-09-04 16:56 | 2022-09-04 16:57 | 4279 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | P22090400153 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-04 | 4279 | keep | 0 | Sep | 2022 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2022-09-04 16:57 | 2022-09-04 23:00 | 40 | 6:03 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L DESCARGAS ELECTRICAS | P22090400155 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 363 | 2022-09-04 | 14520 | keep | 0 | Sep | 2022 | 0.0098895 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-04 16:59 | 2022-09-04 19:58 | 30 | 2:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L NAL TIEMPO LLUVIAS | C22090400628 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 179 | 2022-09-04 | 5370 | keep | 0 | Sep | 2022 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-09-04 17:00 | 2022-09-04 17:25 | 4 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARA | M22090400146 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2022-09-04 | 100 | keep | 0 | Sep | 2022 | 6.811e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-09-04 17:05 | 2022-09-04 19:10 | 14 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22090400104 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2022-09-04 | 1750 | keep | 0 | Sep | 2022 | 0.0011919 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2022-09-04 17:09 | 2022-09-04 21:52 | 10 | 4:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P22090400156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2022-09-04 | 2830 | keep | 0 | Sep | 2022 | 0.0019275 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-09-04 17:10 | 2022-09-05 10:46 | 300 | 17:36 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 Y 1 X 25 EN CORTES DE LINEA SE REPARO BAJANTE HACIA CAJA PRIMARIA ZAFADO Y PEGADOS A POSTE DE METAL. | C22090400643 | New_Event | Primary Wire Break | Include | Include | Equipment | 1056 | 2022-09-04 | 316800 | keep | 0 | Sep | 2022 | 0.21577 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-09-04 17:11 | 2022-09-04 21:56 | 15 | 4:45 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R22090400341 | New_Event | Animals | Include | Include | Wildlife | 285 | 2022-09-04 | 4275 | keep | 0 | Sep | 2022 | 0.0029117 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-09-04 17:12 | 2022-09-04 18:00 | 560 | 0:48 | P | MAL TIEMPO/RAYOS | IR 2501-3E CON FASE FUERA, CERRO BY PASS AL 2501-3E RAYOS | R22090400319 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 48 | 2022-09-04 | 26880 | keep | 0 | Sep | 2022 | 0.018308 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-04 17:15 | 2022-09-04 17:56 | 6 | 0:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR MAL TIEMPO LLUVIAS | C22090400659 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 41 | 2022-09-04 | 246 | keep | 0 | Sep | 2022 | 0.00016755 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-09-04 17:15 | 2022-09-04 19:24 | 828 | 2:09 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES Y SE DEJO SECCIONALIZADO EL CONDUCTOR EN EL SUELO PARA SER TRABAJADO MAÃ‘ANA SIGUEN FUERA APROX 20 CLIENTES | C22090400358 | New_Event | Primary Wire Break | Include | Include | Equipment | 129 | 2022-09-04 | 106812 | keep | 0 | Sep | 2022 | 0.072749 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
PONCE | 2022-09-04 17:20 | 2022-09-04 18:40 | 653 | 1:20 | T | DESGANCHE | DISPARO INTERRUPTOR SE REMOVIO RAMA SOBRE LA LINEA | P22090400162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2022-09-04 | 52240 | keep | 0 | Sep | 2022 | 0.03558 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
HUMACAO | 2022-09-04 17:24 | 2022-09-05 14:18 | 1475 | 20:54 | P | MAL TIEMPO/RAYOS | 2 X 8 Y 1 X 10 EN TRANSFORMADORES Y 1 X 80, 2 X 65, 2 X 50, 1 X 50 Y 1 X 20 EN CORTES DE LINEA MAL TIEMPO RAYOS | C22090400662 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1254 | 2022-09-04 | 1849650 | keep | 0 | Sep | 2022 | 1.2598 | 0.0010046 | Sustained | FALSE | FALSE | Not_TMED_Event | 1475
SAN JUAN | 2022-09-04 17:25 | 2022-09-05 10:34 | 1 | 17:09 | P | PROBLEMA DEL CLIENTE | 1X30 EN RISER (PROA) | S22090400610 | New_Event | Customer-Related Interruption | Include | Include | Public | 1029 | 2022-09-04 | 1029 | keep | 0 | Sep | 2022 | 0.00070085 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-09-04 17:25 | 2022-09-04 19:26 | 20 | 2:01 | P | DESGANCHE | 1 X 20 EN C/L | R22090400347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2022-09-04 | 2420 | keep | 0 | Sep | 2022 | 0.0016483 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-09-04 17:25 | 2022-09-04 21:03 | 8 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR MAL TIEMPO LLUVIAS | C22090400663 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2022-09-04 | 1744 | keep | 0 | Sep | 2022 | 0.0011878 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-09-04 17:29 | 2022-09-04 22:09 | 7 | 4:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIAS | C22090400672 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 280 | 2022-09-04 | 1960 | keep | 0 | Sep | 2022 | 0.0013349 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2022-09-04 17:29 | 2022-09-04 20:29 | 120 | 3:00 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L NEUTRAL PRIMARIO ROTO | R22090400353 | New_Event | Primary Wire Break | Include | Include | Equipment | 180 | 2022-09-04 | 21600 | keep | 0 | Sep | 2022 | 0.014712 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2022-09-04 17:30 | 2022-09-04 20:07 | 1712 | 2:37 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE DE LINEA QUEMADO DEL INTERRUPTOR | P22090400176 | New_Event | Switch Failure | Include | Include | Equipment | 157 | 2022-09-04 | 268784 | keep | 0 | Sep | 2022 | 0.18307 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
FAJARDO | 2022-09-04 17:33 | 2022-09-04 18:14 | 153 | 0:41 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R22090400362 | New_Event | Vegetation Contact | Include | Include | Vegetation | 41 | 2022-09-04 | 6273 | keep | 0 | Sep | 2022 | 0.0042725 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
GUAYAMA | 2022-09-04 17:38 | 2022-09-04 21:48 | 120 | 4:10 | P | DESGANCHE | SE LEVANTO ALAMBRE PRIMARIO SE HIZO DESGANCHE 1 X 140 EN CORTE DE LINEA | P22090400183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2022-09-04 | 30000 | keep | 0 | Sep | 2022 | 0.020433 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
SAN JUAN | 2022-09-04 17:40 | 2022-09-04 18:03 | 108 | 0:23 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA DE MH-20 @ MH-24 Y SE CERRO POR SCADA 95% EN SERVICIO SJ-220904-04 | S22090400538 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 23 | 2022-09-04 | 2484 | keep | 0 | Sep | 2022 | 0.0016918 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-04 17:46 | 2022-09-05 11:30 | 5 | 17:44 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090400691 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1064 | 2022-09-04 | 5320 | keep | 0 | Sep | 2022 | 0.0036234 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-09-04 17:47 | 2022-09-05 12:09 | 20 | 18:22 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22090400623 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1102 | 2022-09-04 | 22040 | keep | 0 | Sep | 2022 | 0.015011 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-09-04 17:50 | 2022-09-04 20:07 | 80 | 2:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C22090400700 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 137 | 2022-09-04 | 10960 | keep | 0 | Sep | 2022 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-09-04 17:56 | 2022-09-04 21:26 | 15 | 3:30 | P | TRANSFORMADOR AVERIADO | 1 X 40 Y 1 X 65 EN C/LS Y 1 X 10 EN XMR REMPLAZO PARARRAYO Y SE SECCIONALIZO TRANSFORMADOR QUEMADO | R22090400381 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2022-09-04 | 3150 | keep | 0 | Sep | 2022 | 0.0021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-04 18:03 | 2022-09-04 18:20 | 54 | 0:17 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA DE MH-20 @ MH-24 Y SE CERRO N/O CONTRA EL MISMO 1107-05 97% EN SERVICIO | S22090400538 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 17 | 2022-09-04 | 918 | keep | 0 | Sep | 2022 | 0.00062525 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-04 18:03 | 2022-09-05 10:19 | 500 | 16:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100, 1 X 80, 1 X 40, 1 X 30 Y 2 X 10 EN CORTES DE LINEA Y TRANSFORMADORES MAL TIEMPO | C22090400719 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 976 | 2022-09-04 | 488000 | keep | 0 | Sep | 2022 | 0.33237 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2022-09-04 18:04 | 2022-09-04 20:18 | 314 | 2:14 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN C/L Y 1 X 65 EN RISER SE DEJO FUERA DEL SU - 10 @ SU - 9 POR CONTAMINACION NO HAY CLIENTES FUERA | R22090400386 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 134 | 2022-09-04 | 42076 | keep | 0 | Sep | 2022 | 0.028658 | 0.00021386 | Sustained | FALSE | FALSE | Not_TMED_Event | 314
HUMACAO | 2022-09-04 18:04 | 2022-09-06 13:31 | 20 | 43:27 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 50 X 50KVA | C22090400720 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2607 | 2022-09-04 | 52140 | keep | 0 | Sep | 2022 | 0.035512 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-04 18:11 | 2022-09-05 09:09 | 4 | 14:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C22090400729 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 898 | 2022-09-04 | 3592 | keep | 0 | Sep | 2022 | 0.0024465 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-04 18:20 | 2022-09-04 18:50 | 12 | 0:30 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO AVERIA DE MH-20 @ MH-24 100% EN SERVICIO CERRANDO N/O CONTRA EL MISMO 1107-05 | S22090400538 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 30 | 2022-09-04 | 360 | keep | 0 | Sep | 2022 | 0.00024519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-09-04 18:40 | 2022-09-05 11:45 | 70 | 17:05 | P | MAL TIEMPO/RAYOS | 2 X 80 EN C/L DESCARGAS ELECTRICAS | P22090400230 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1025 | 2022-09-04 | 71750 | keep | 0 | Sep | 2022 | 0.048869 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2022-09-04 18:40 | 2022-09-04 19:30 | 10 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA | M22090400170 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2022-09-04 | 500 | keep | 0 | Sep | 2022 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-04 18:43 | 2022-09-04 21:06 | 200 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50, 1 X 65 Y 1 X 80 EN C/L MAL TIEMPO LLUVIAS | C22090400762 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2022-09-04 | 28600 | keep | 0 | Sep | 2022 | 0.019479 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-09-04 18:45 | 2022-09-05 08:38 | 100 | 13:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50, 1 X 40 Y 1 X 30 EN CORTES DE LINEA | C22090400763 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 833 | 2022-09-04 | 83300 | keep | 0 | Sep | 2022 | 0.056735 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-09-04 19:00 | 2022-09-04 23:38 | 70 | 4:38 | P | DESGANCHE | 2 X 65 EN C/L | R22090400430 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2022-09-04 | 19460 | keep | 0 | Sep | 2022 | 0.013254 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2022-09-04 19:09 | 2022-09-04 20:34 | 35 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 EN C/L POR LLUVIAS | B22090400564 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2022-09-04 | 2975 | keep | 0 | Sep | 2022 | 0.0020263 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2022-09-04 19:16 | 2022-09-05 12:24 | 10 | 17:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA 1 X 30 EN C/L | R22090400440 | New_Event | Cutout Failure | Include | Include | Equipment | 1028 | 2022-09-04 | 10280 | keep | 0 | Sep | 2022 | 0.0070017 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-04 19:16 | 2022-09-05 10:25 | 15 | 15:09 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO BUSHING SECUNDARIO | R22090400440 | New_Event | Service Transformer Failure | Include | Include | Equipment | 909 | 2022-09-04 | 13635 | keep | 0 | Sep | 2022 | 0.0092867 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-09-04 19:18 | 2022-09-04 21:10 | 150 | 1:52 | P | ARBOL SOBRE LINEA | 1 X 30 Y 1 X 50 EN DISTINTOS CORTES DE LINEA ARBOL CAYO Y CAUSO QUE LAS LINEAS SE CRUZARAN | A22090400119 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 112 | 2022-09-04 | 16800 | keep | 0 | Sep | 2022 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2022-09-04 19:20 | 2022-09-04 19:44 | 1067 | 0:24 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA CERRAR PUENTES CONSULTADO CON JOSE T MORALES DM GUAYAMA SE CERRO INTERRUPTOR MANUALMENTE | P22090400265 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 24 | 2022-09-04 | 25608 | keep | 0 | Sep | 2022 | 0.017441 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-09-04 19:20 | 2022-09-04 21:14 | 3718 | 1:54 | T | DESGANCHE | LUEGO DE PATRULLAR SE CERRO INTERRUPTOR Y QUEDO EN SERVICIO VARIOS PUNTOS DE DESGANCHE MASIVO | P22090400270 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-09-04 | 423852 | keep | 0 | Sep | 2022 | 0.28868 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
CANOVANAS | 2022-09-04 19:21 | 2022-09-05 10:58 | 12 | 15:37 | P | PARARRAYOS DEFECTUOSO | 1 X 20 N XMR Y REEMPLAZO DE PARARRAYO | R22090400443 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 937 | 2022-09-04 | 11244 | keep | 0 | Sep | 2022 | 0.0076582 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2022-09-04 19:40 | 2022-09-04 21:08 | 40 | 1:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | A22090400123 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2022-09-04 | 3520 | keep | 0 | Sep | 2022 | 0.0023975 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2022-09-04 20:07 | 2022-09-04 20:19 | 171 | 0:12 | P | DESCONECTIVO DEFECTUOSO | SE CERRARON MACHETES | P22090400176 | Partial_restoration | Switch Failure | Include | Include | Equipment | 12 | 2022-09-04 | 2052 | keep | 0 | Sep | 2022 | 0.0013976 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-04 20:09 | 2022-09-05 18:09 | 10 | 22:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO BUSHING SECUNDARIO DE XMR | B22090400570 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1320 | 2022-09-04 | 13200 | keep | 0 | Sep | 2022 | 0.0089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-04 20:10 | 2022-09-04 20:11 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 QUE LLEVA TRANSFERIDA LA CARGA DEL 1909-09 | S22090400686 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 222 | keep | 0 | Sep | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-09-04 20:10 | 2022-09-04 20:11 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 QUE LLEVA TRANSFERIDA LA CARGA DEL 1909-09 | S22090400686 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 4456 | keep | 0 | Sep | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
ARECIBO | 2022-09-04 20:14 | 2022-09-04 22:20 | 250 | 2:06 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090400131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2022-09-04 | 31500 | keep | 0 | Sep | 2022 | 0.021455 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2022-09-04 20:18 | 2022-09-04 20:19 | 2524 | 0:01 | T | ERROR HUMANO | SE BKR A PETICION DE ANGEL PANELL PARA CERRAR C/L QUE NO CERRO BIEN | R22090400456 | New_Event | Human Error | Include | Include | Other | 1 | 2022-09-04 | 2524 | keep | 0 | Sep | 2022 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-09-04 20:19 | 2022-09-04 21:24 | 314 | 1:05 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN C/L Y 1 X 65 EN RISER SE DEJO FUERA DEL SU - 10 @ SU - 9 POR CONTAMINACION NO HAY CLIENTES FUERA | R22090400386 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 65 | 2022-09-04 | 20410 | keep | 0 | Sep | 2022 | 0.013901 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-04 20:28 | 2022-09-05 09:35 | 200 | 13:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M22090400198 | New_Event | Primary Wire Break | Include | Include | Equipment | 787 | 2022-09-04 | 157400 | keep | 0 | Sep | 2022 | 0.1072 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-09-04 20:32 | 2022-09-05 07:12 | 100 | 10:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22090400854 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 640 | 2022-09-04 | 64000 | keep | 0 | Sep | 2022 | 0.04359 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-09-04 20:34 | 2022-09-05 08:38 | 8 | 12:04 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X15 EN TRANSFORMADOR SE RETIRO ENREDADERAS | A22090400142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 724 | 2022-09-04 | 5792 | keep | 0 | Sep | 2022 | 0.0039449 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-04 20:37 | 2022-09-04 23:59 | 50 | 3:22 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22090400206 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 202 | 2022-09-04 | 10100 | keep | 0 | Sep | 2022 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-09-04 21:07 | 2022-09-05 09:37 | 100 | 12:30 | P | DESGANCHE | 3 X 30 EN CORTES DE LINEA | C22080400868 | New_Event | Vegetation Contact | Include | Include | Vegetation | 750 | 2022-09-04 | 75000 | keep | 0 | Sep | 2022 | 0.051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-09-04 21:16 | 2022-09-06 15:12 | 12 | 41:56 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA | C22090400874 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2516 | 2022-09-04 | 30192 | keep | 0 | Sep | 2022 | 0.020564 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-09-04 21:16 | 2022-09-05 12:08 | 78 | 14:52 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN CORTE DE LINEA TRANSFORMADOR QUEMADO DE 50KVA | C22090400874 | New_Event | Service Transformer Failure | Include | Include | Equipment | 892 | 2022-09-04 | 69576 | keep | 0 | Sep | 2022 | 0.047388 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
HUMACAO | 2022-09-04 21:20 | 2022-09-05 08:29 | 6 | 11:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C22090400877 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 669 | 2022-09-04 | 4014 | keep | 0 | Sep | 2022 | 0.0027339 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-09-04 21:26 | 2022-09-05 12:29 | 1 | 15:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 15KVA X 25 KVA | R22090400381 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 903 | 2022-09-04 | 903 | keep | 0 | Sep | 2022 | 0.00061503 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-04 21:31 | 2022-09-04 21:32 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22090400578 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 1859 | keep | 0 | Sep | 2022 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2022-09-04 21:37 | 2022-09-04 23:25 | 125 | 1:48 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090400169 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 108 | 2022-09-04 | 13500 | keep | 0 | Sep | 2022 | 0.0091948 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BARRANQUITAS | 2022-09-04 21:44 | 2022-09-05 18:24 | 53 | 20:40 | P | MAL TIEMPO/RAYOS | 1 X 40 Y 1 X 20 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090400890 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1240 | 2022-09-04 | 65720 | keep | 0 | Sep | 2022 | 0.044762 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2022-09-04 21:48 | 2022-09-05 13:00 | 15 | 15:12 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR 37.5KVA | M22090400222 | New_Event | Service Transformer Failure | Include | Include | Equipment | 912 | 2022-09-04 | 13680 | keep | 0 | Sep | 2022 | 0.0093174 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2022-09-04 22:04 | 2022-09-05 08:47 | 60 | 10:43 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR AVE | A22090400177 | New_Event | Animals | Include | Include | Wildlife | 643 | 2022-09-04 | 38580 | keep | 0 | Sep | 2022 | 0.026277 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-09-04 22:08 | 2022-09-05 15:08 | 2 | 17:00 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090400900 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1020 | 2022-09-04 | 2040 | keep | 0 | Sep | 2022 | 0.0013894 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2022-09-04 22:12 | 2022-09-04 23:37 | 20 | 1:25 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090400408 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2022-09-04 | 1700 | keep | 0 | Sep | 2022 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2022-09-04 22:46 | 2022-09-05 11:50 | 40 | 13:04 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE REPARO LINEA PRIMARIA | P22090400426 | New_Event | Primary Wire Break | Include | Include | Equipment | 784 | 2022-09-04 | 31360 | keep | 0 | Sep | 2022 | 0.021359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2022-09-04 22:47 | 2022-09-05 12:38 | 60 | 13:51 | P | ANIMAL | 1 X 50 EN C/L Y 1 X 50 EN OTRO C/L CRUCE DE FASES PRIMARIAS POR CULEBRA | P22090400427 | New_Event | Animals | Include | Include | Wildlife | 831 | 2022-09-04 | 49860 | keep | 0 | Sep | 2022 | 0.033959 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-09-04 22:50 | 2022-09-05 08:42 | 20 | 9:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | A22090400189 | New_Event | Cutout Failure | Include | Include | Equipment | 592 | 2022-09-04 | 11840 | keep | 0 | Sep | 2022 | 0.0080642 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-04 22:54 | 2022-09-05 15:07 | 50 | 16:13 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S22090400754 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 973 | 2022-09-04 | 48650 | keep | 0 | Sep | 2022 | 0.033135 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-04 23:05 | 2022-09-05 09:55 | 87 | 10:50 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | S22090400756 | New_Event | Vegetation Contact | Include | Include | Vegetation | 650 | 2022-09-04 | 56550 | keep | 0 | Sep | 2022 | 0.038516 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
FAJARDO | 2022-09-04 23:16 | 2022-09-05 00:06 | 55 | 0:50 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22090400486 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2022-09-04 | 2750 | keep | 0 | Sep | 2022 | 0.001873 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2022-09-04 23:20 | 2022-09-04 23:21 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-04 | 6197 | keep | 0 | Sep | 2022 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
SAN JUAN | 2022-09-04 23:23 | 2022-09-05 10:36 | 30 | 11:13 | P | NO SE REPORTO CAUSA | 1X40 DE PROVISIONAL AEREO @ T-28 | S22090400801 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 673 | 2022-09-04 | 20190 | keep | 0 | Sep | 2022 | 0.013751 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-09-04 23:40 | 2022-09-05 10:36 | 120 | 10:56 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA | C22090400929 | New_Event | Vegetation Contact | Include | Include | Vegetation | 656 | 2022-09-04 | 78720 | keep | 0 | Sep | 2022 | 0.053616 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2022-09-04 23:41 | 2022-09-05 01:30 | 30 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22090400199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2022-09-04 | 3270 | keep | 0 | Sep | 2022 | 0.0022272 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-09-05 00:12 | 2022-09-05 09:04 | 20 | 8:52 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090500002 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 532 | 2022-09-05 | 10640 | keep | 0 | Sep | 2022 | 0.0072469 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-05 00:42 | 2022-09-05 20:22 | 1 | 19:40 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DEL SU-1 @ MH-11 MEDIANTE G.O.I. SJ-220904-06 | S22090400669 | New_Event | UG Cable Fault | Include | Include | Equipment | 1180 | 2022-09-05 | 1180 | keep | 0 | Sep | 2022 | 0.00080369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-09-05 00:45 | 2022-09-05 07:00 | 30 | 6:15 | P | MAL TIEMPO/RAYOS | 1 X 140 EN C/L RAYO | P22090500001 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 375 | 2022-09-05 | 11250 | keep | 0 | Sep | 2022 | 0.0076623 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-09-05 00:47 | 2022-09-05 00:48 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 5004-10 CON CARGA DEL 5004-07 | P22090500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 2379 | keep | 0 | Sep | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-09-05 00:47 | 2022-09-05 00:48 | 11 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CON CARGA DEL 5004-07 | P22090500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 11 | keep | 0 | Sep | 2022 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2022-09-05 00:50 | 2022-09-05 09:00 | 50 | 8:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22090500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 490 | 2022-09-05 | 24500 | keep | 0 | Sep | 2022 | 0.016687 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-09-05 01:07 | 2022-09-05 10:03 | 20 | 8:56 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22090500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2022-09-05 | 10720 | keep | 0 | Sep | 2022 | 0.0073013 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-05 01:10 | 2022-09-05 16:39 | 30 | 15:29 | P | DESGANCHE | 1 X 65 EN CORT DE LINEA | S22090500043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 929 | 2022-09-05 | 27870 | keep | 0 | Sep | 2022 | 0.018982 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-05 01:19 | 2022-09-05 10:37 | 10 | 9:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN PM | R22090500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 558 | 2022-09-05 | 5580 | keep | 0 | Sep | 2022 | 0.0038005 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-05 02:10 | 2022-09-05 11:52 | 220 | 9:42 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE LE DIO MANTENIMIENTO POR CONTAMINACION AL SU-1 MEDIANTE G.O.I. SJ-220905-01 EN SERVICIO EL 10% QUE FALTABA POR ENTRAR | S22090400835 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 582 | 2022-09-05 | 128040 | keep | 0 | Sep | 2022 | 0.087207 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
CANOVANAS | 2022-09-05 02:17 | 2022-09-05 13:48 | 8 | 11:31 | P | DESGANCHE | DESGANCHE SECUNDARIO Y PRIMARIO | R22090500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 691 | 2022-09-05 | 5528 | keep | 0 | Sep | 2022 | 0.0037651 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-09-05 03:44 | 2022-09-05 03:45 | 1250 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2901-04 | C22090500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 1250 | keep | 0 | Sep | 2022 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-09-05 03:44 | 2022-09-05 03:45 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 2901-02 | C22090500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 1827 | keep | 0 | Sep | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2022-09-05 03:45 | 2022-09-05 05:33 | 20 | 1:48 | P | ARBOL SOBRE LINEA | 1 X 25 EN CORTE DE LINEA SE RETIRO ARBOL Y SE LEVANTO LINEA | C22090400064 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 108 | 2022-09-05 | 2160 | keep | 0 | Sep | 2022 | 0.0014712 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 03:45 | 2022-09-05 05:33 | 73 | 1:48 | P | DESGANCHE | 2 X 65 EN CORTES DE LINEA | C22090400601 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-09-05 | 7884 | keep | 0 | Sep | 2022 | 0.0053698 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-05 03:54 | 2022-09-05 10:50 | 120 | 6:56 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C22090500013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2022-09-05 | 49920 | keep | 0 | Sep | 2022 | 0.034 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2022-09-05 03:58 | 2022-09-05 10:50 | 50 | 6:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | B22090500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2022-09-05 | 20600 | keep | 0 | Sep | 2022 | 0.014031 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-05 04:36 | 2022-09-05 08:16 | 12 | 3:40 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | B22090500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2022-09-05 | 2640 | keep | 0 | Sep | 2022 | 0.0017981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2022-09-05 04:47 | 2022-09-05 09:45 | 60 | 4:58 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CRUCETA PARTIDA | M22090500003 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 298 | 2022-09-05 | 17880 | keep | 0 | Sep | 2022 | 0.012178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-09-05 05:16 | 2022-09-05 12:10 | 500 | 6:54 | P | DESGANCHE | CG-220905-02A 3 X 65 EN CORTES DE LINEA SE RETIRARON BAMBUAS SOBRE LINEA | C22090500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2022-09-05 | 207000 | keep | 0 | Sep | 2022 | 0.14099 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2022-09-05 05:33 | 2022-09-05 05:34 | 1250 | 0:01 | T | DESGANCHE | RECIERRE LLEVA LA CARGA DEL 2901-04 | C22090500030 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-05 | 1250 | keep | 0 | Sep | 2022 | 0.00085137 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 05:33 | 2022-09-05 05:34 | 1827 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL 2901-02 | C22090500030 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-05 | 1827 | keep | 0 | Sep | 2022 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
HUMACAO | 2022-09-05 05:34 | 2022-09-05 08:15 | 20 | 2:41 | P | ARBOL SOBRE LINEA | 1 X 25 EN CORTE DE LINEA SE RETIRO ARBOL Y SE LEVANTO LINEA | C22090400064 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 161 | 2022-09-05 | 3220 | keep | 0 | Sep | 2022 | 0.0021931 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 05:34 | 2022-09-05 08:15 | 73 | 2:41 | P | DESGANCHE | 2 X 65 EN CORTES DE LINEA | C22090400601 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 161 | 2022-09-05 | 11753 | keep | 0 | Sep | 2022 | 0.0080049 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
HUMACAO | 2022-09-05 05:34 | 2022-09-05 08:15 | 411 | 2:41 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO PARTIDO | C22090500164 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 161 | 2022-09-05 | 66171 | keep | 0 | Sep | 2022 | 0.045069 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
GUAYAMA | 2022-09-05 05:37 | 2022-09-05 10:18 | 20 | 4:41 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR CRUCE DE FASE CON RAMA DE FLAMBOYAN | P22090500046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 281 | 2022-09-05 | 5620 | keep | 0 | Sep | 2022 | 0.0038278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-05 05:38 | 2022-09-05 05:39 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090500033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 181 | keep | 0 | Sep | 2022 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2022-09-05 05:38 | 2022-09-05 05:39 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090500034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 5630 | keep | 0 | Sep | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2022-09-05 06:03 | 2022-09-06 09:13 | 16 | 27:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B22090500055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1630 | 2022-09-05 | 26080 | keep | 0 | Sep | 2022 | 0.017763 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-09-05 06:04 | 2022-09-05 06:05 | 222 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 1907-03 LLEVA LA CARGA DEL 1909-09 SE CERRO POR CONTROL | S22090500080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 222 | keep | 0 | Sep | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-09-05 06:04 | 2022-09-05 06:05 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 1907-03 LLEVA LA CARGA DEL 1909-09 SE CERRO POR CONTROL | S22090700080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 4456 | keep | 0 | Sep | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CAGUAS | 2022-09-05 06:08 | 2022-09-05 12:06 | 100 | 5:58 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO EXPLOTADO | C22090500051 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 358 | 2022-09-05 | 35800 | keep | 0 | Sep | 2022 | 0.024383 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2022-09-05 06:10 | 2022-09-05 16:00 | 60 | 9:50 | P | MAL TIEMPO/RAYOS | 2 X 10 EN XMR RAYOS | P22090500052 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 590 | 2022-09-05 | 35400 | keep | 0 | Sep | 2022 | 0.024111 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-09-05 06:16 | 2022-09-05 10:25 | 35 | 4:09 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR CULEBRA | A22090500011 | New_Event | Animals | Include | Include | Wildlife | 249 | 2022-09-05 | 8715 | keep | 0 | Sep | 2022 | 0.0059357 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2022-09-05 06:38 | 2022-09-05 09:50 | 234 | 3:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA | R22090500013 | New_Event | Cutout Failure | Include | Include | Equipment | 192 | 2022-09-05 | 44928 | keep | 0 | Sep | 2022 | 0.0306 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
HUMACAO | 2022-09-05 07:08 | 2022-09-06 09:10 | 100 | 26:02 | P | DESGANCHE | 1 X 65 EN CORTES DE LINEA | C22090500079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1562 | 2022-09-05 | 156200 | keep | 0 | Sep | 2022 | 0.10639 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-09-05 07:11 | 2022-09-05 14:01 | 30 | 6:50 | P | MAL TIEMPO/RAYOS | 2 X 15 EN DOS TRANSFORMADORES MAL TIEMPO RAYOS | C22090500084 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 410 | 2022-09-05 | 12300 | keep | 0 | Sep | 2022 | 0.0083775 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-05 07:12 | 2022-09-05 21:30 | 10 | 14:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA EN VARIOS PUNTOS | S22090500093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 858 | 2022-09-05 | 8580 | keep | 0 | Sep | 2022 | 0.0058438 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-09-05 07:13 | 2022-09-05 11:00 | 80 | 3:47 | P | DESGANCHE | 1 X 80, 1 X 50 Y 1 X 40 EN CORTES DE LINEA SE REALIZO DESGANCHE CRITICO Y SE CERRO PUENTE ABIERTO | S22090500094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2022-09-05 | 18160 | keep | 0 | Sep | 2022 | 0.012369 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-09-05 07:15 | 2022-09-05 14:44 | 40 | 7:29 | P | DESGANCHE | 1 X 30, 1 X 20 Y 1 X 10 EN CORTES DE LINEA Y TRANSFORMADOR | R22090500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2022-09-05 | 17960 | keep | 0 | Sep | 2022 | 0.012232 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-09-05 07:16 | 2022-09-05 15:11 | 20 | 7:55 | P | DESGANCHE | 1 X 30 EN C/L | R22090500020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2022-09-05 | 9500 | keep | 0 | Sep | 2022 | 0.0064704 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-09-05 07:22 | 2022-09-05 14:17 | 6 | 6:55 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22090500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 415 | 2022-09-05 | 2490 | keep | 0 | Sep | 2022 | 0.0016959 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-09-05 07:23 | 2022-09-05 07:24 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090500101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 2608 | keep | 0 | Sep | 2022 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2022-09-05 07:26 | 2022-09-05 07:27 | 1606 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE | C22090500114 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-09-05 | 1606 | keep | 0 | Sep | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2022-09-05 07:27 | 2022-09-05 13:34 | 100 | 6:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP | C22090500101 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 367 | 2022-09-05 | 36700 | keep | 0 | Sep | 2022 | 0.024996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-09-05 07:35 | 2022-09-05 07:36 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 1234 | keep | 0 | Sep | 2022 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
BAYAMON | 2022-09-05 07:41 | 2022-09-05 10:50 | 18 | 3:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARAR SECUNDARIA | B22090500014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 189 | 2022-09-05 | 3402 | keep | 0 | Sep | 2022 | 0.0023171 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2022-09-05 07:47 | 2022-09-05 18:11 | 11 | 10:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO CAJA EN XMR | P22090500078 | New_Event | Cutout Failure | Include | Include | Equipment | 624 | 2022-09-05 | 6864 | keep | 0 | Sep | 2022 | 0.004675 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2022-09-05 07:50 | 2022-09-05 18:35 | 28 | 10:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22090500122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2022-09-05 | 18060 | keep | 0 | Sep | 2022 | 0.012301 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
PONCE | 2022-09-05 07:53 | 2022-09-05 07:54 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 5004-10 CON CARGA DEL 5004-07 | P22090500082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 2379 | keep | 0 | Sep | 2022 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2022-09-05 07:53 | 2022-09-05 07:54 | 11 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR CON CARGA DEL 5004-07 | P22090500082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 11 | keep | 0 | Sep | 2022 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2022-09-05 07:53 | 2022-09-05 09:21 | 60 | 1:28 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | A22090500015 | New_Event | Animals | Include | Include | Wildlife | 88 | 2022-09-05 | 5280 | keep | 0 | Sep | 2022 | 0.0035962 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-09-05 08:12 | 2022-09-05 11:30 | 15 | 3:18 | P | PROBLEMA DEL CLIENTE | 1 X 10 EN TRANSFORMADOR AVERIA EN RESIDENCIA SE REMOVIO CONTADOR AFECTADO | P22090500086 | New_Event | Customer-Related Interruption | Include | Include | Public | 198 | 2022-09-05 | 2970 | keep | 0 | Sep | 2022 | 0.0020229 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-09-05 08:13 | 2022-09-05 19:20 | 50 | 11:07 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P22090500092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 667 | 2022-09-05 | 33350 | keep | 0 | Sep | 2022 | 0.022715 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-05 08:15 | 2022-09-05 08:20 | 1250 | 0:05 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUTOR PARA SECCIONALIZAR CONDUCTOR DEL 2901-4 EN EL SUELO INFORMADO POR CARLOS TIRADO | C22090500154 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2022-09-05 | 6250 | keep | 0 | Sep | 2022 | 0.0042568 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2022-09-05 08:15 | 2022-09-05 08:20 | 1827 | 0:05 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO INFORMADO POR CARLOS TIRADO | C22090500154 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 5 | 2022-09-05 | 9135 | keep | 0 | Sep | 2022 | 0.0062218 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 08:20 | 2022-09-05 15:00 | 20 | 6:40 | P | ARBOL SOBRE LINEA | 1 X 25 EN CORTE DE LINEA SE RETIRO ARBOL Y SE LEVANTO LINEA | C22090400064 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 400 | 2022-09-05 | 8000 | keep | 0 | Sep | 2022 | 0.0054488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 08:20 | 2022-09-05 16:52 | 73 | 8:32 | P | DESGANCHE | 2 X 65 EN CORTES DE LINEA | C22090400601 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 512 | 2022-09-05 | 37376 | keep | 0 | Sep | 2022 | 0.025457 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 08:20 | 2022-09-06 13:11 | 64 | 28:51 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y 1 X 10 EN TRANSFORMADOR | C22090500022 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1731 | 2022-09-05 | 110784 | keep | 0 | Sep | 2022 | 0.075454 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 08:20 | 2022-09-05 15:35 | 1233 | 7:15 | P | CONDUCTOR ROTO O ABIERTO | 3 X 140 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C22090500164 | New_Event | Primary Wire Break | Include | Include | Equipment | 435 | 2022-09-05 | 536355 | keep | 0 | Sep | 2022 | 0.36531 | 0.00083979 | Sustained | FALSE | FALSE | Not_TMED_Event | 1233
HUMACAO | 2022-09-05 08:21 | 2022-09-05 12:55 | 130 | 4:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C22090500164 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 274 | 2022-09-05 | 35620 | keep | 0 | Sep | 2022 | 0.024261 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
FAJARDO | 2022-09-05 08:22 | 2022-09-05 13:11 | 12 | 4:49 | P | DESGANCHE | SE REALIZO DESGANCHE Y 1 X 50 EN C/L | R22090500029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 289 | 2022-09-05 | 3468 | keep | 0 | Sep | 2022 | 0.002362 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-09-05 08:23 | 2022-09-05 09:00 | 2 | 0:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22090500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2022-09-05 | 74 | keep | 0 | Sep | 2022 | 5.0401e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2022-09-05 08:31 | 2022-09-05 14:31 | 42 | 6:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P22090500090 | New_Event | Cutout Failure | Include | Include | Equipment | 360 | 2022-09-05 | 15120 | keep | 0 | Sep | 2022 | 0.010298 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
AGUADILLA | 2022-09-05 08:38 | 2022-09-05 09:45 | 12 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR BARRA SECUNDARIA EN PEDESTAL | M22090500006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2022-09-05 | 804 | keep | 0 | Sep | 2022 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-09-05 08:39 | 2022-09-05 18:45 | 87 | 10:06 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22090500169 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 606 | 2022-09-05 | 52722 | keep | 0 | Sep | 2022 | 0.035909 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
BAYAMON | 2022-09-05 08:40 | 2022-09-05 09:35 | 12 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22090500013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-09-05 | 660 | keep | 0 | Sep | 2022 | 0.00044952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2022-09-05 08:51 | 2022-09-05 11:05 | 150 | 2:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22090500187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2022-09-05 | 20100 | keep | 0 | Sep | 2022 | 0.01369 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-09-05 08:54 | 2022-09-06 09:23 | 200 | 24:29 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 80 EN CORTE DE LINEA CONDUCTOR CRUZADO CON BRAZO DE ALUMBRADO SE INSTALARON TIGUEROS | C22090500196 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1469 | 2022-09-05 | 293800 | keep | 0 | Sep | 2022 | 0.20011 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-09-05 08:55 | 2022-09-05 15:29 | 5 | 6:34 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | S22090500134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2022-09-05 | 1970 | keep | 0 | Sep | 2022 | 0.0013418 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-09-05 08:57 | 2022-09-05 12:12 | 20 | 3:15 | P | PARARRAYOS DEFECTUOSO | 3 X 80 EN C/L SE ELIMINO PARARAYO | B22090500017 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 195 | 2022-09-05 | 3900 | keep | 0 | Sep | 2022 | 0.0026563 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2022-09-05 08:58 | 2022-09-05 11:10 | 1 | 2:12 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | P22090500111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-09-05 | 132 | keep | 0 | Sep | 2022 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-05 09:00 | 2022-09-05 10:30 | 12 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22090500070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2022-09-05 | 1080 | keep | 0 | Sep | 2022 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-09-05 09:05 | 2022-09-05 12:31 | 169 | 3:26 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S22090500142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2022-09-05 | 34814 | keep | 0 | Sep | 2022 | 0.023712 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
CANOVANAS | 2022-09-05 09:13 | 2022-09-05 14:06 | 20 | 4:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22090500038 | New_Event | Cutout Failure | Include | Include | Equipment | 293 | 2022-09-05 | 5860 | keep | 0 | Sep | 2022 | 0.0039912 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-05 09:13 | 2022-09-05 12:23 | 3 | 3:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO NEUTRAL | B22090500021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 190 | 2022-09-05 | 570 | keep | 0 | Sep | 2022 | 0.00038822 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-09-05 09:13 | 2022-09-05 13:51 | 15 | 4:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | C22090500216 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 278 | 2022-09-05 | 4170 | keep | 0 | Sep | 2022 | 0.0028402 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-09-05 09:20 | 2022-09-05 09:43 | 181 | 0:23 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA RETIRAR CONDUCTOR OVERHEAD SOBRE LINEA 9900 | C22090500224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-09-05 | 4163 | keep | 0 | Sep | 2022 | 0.0028354 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
HUMACAO | 2022-09-05 09:20 | 2022-09-05 09:43 | 5630 | 0:23 | T | LINEA DE TRANSMISION 38KV | SE ABRIO INTERRUPTOR PARA RETIRAR CONDUCTOR OVERHEAD SOBRE LINEA 9900 | C22090500224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-09-05 | 129490 | keep | 0 | Sep | 2022 | 0.088195 | 0.0038346 | Sustained | FALSE | FALSE | Not_TMED_Event | 5630
FAJARDO | 2022-09-05 09:23 | 2022-09-05 15:50 | 1 | 6:27 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | R22090500041 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 387 | 2022-09-05 | 387 | keep | 0 | Sep | 2022 | 0.00026358 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-09-05 09:42 | 2022-09-05 10:50 | 1 | 1:08 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGA ELECTRICA | P22090500122 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 68 | 2022-09-05 | 68 | keep | 0 | Sep | 2022 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-05 09:45 | 2022-09-05 12:15 | 15 | 2:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22090500024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 150 | 2022-09-05 | 2250 | keep | 0 | Sep | 2022 | 0.0015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-09-05 09:48 | 2022-09-06 10:28 | 3 | 24:40 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | R22090500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1480 | 2022-09-05 | 4440 | keep | 0 | Sep | 2022 | 0.0030241 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-09-05 09:50 | 2022-09-05 12:00 | 8 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A22090500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-09-05 | 1040 | keep | 0 | Sep | 2022 | 0.00070834 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2022-09-05 10:00 | 2022-09-05 13:27 | 65 | 3:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L LLUVIAS | R22090500046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 207 | 2022-09-05 | 13455 | keep | 0 | Sep | 2022 | 0.0091641 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2022-09-05 10:06 | 2022-09-06 11:54 | 100 | 25:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C22090500270 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1548 | 2022-09-05 | 154800 | keep | 0 | Sep | 2022 | 0.10543 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-09-05 10:10 | 2022-09-05 16:40 | 4 | 6:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22090500013 | New_Event | Primary Wire Break | Include | Include | Equipment | 390 | 2022-09-05 | 1560 | keep | 0 | Sep | 2022 | 0.0010625 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 849 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500216 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 849 | keep | 0 | Sep | 2022 | 0.00057825 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 893 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500216 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 893 | keep | 0 | Sep | 2022 | 0.00060822 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 602 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500216 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 602 | keep | 0 | Sep | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 43 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500216 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 43 | keep | 0 | Sep | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 1389 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500216 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 1389 | keep | 0 | Sep | 2022 | 0.00094604 | 0.00094604 | Momentary | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 673 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500217 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 673 | keep | 0 | Sep | 2022 | 0.00045838 | 0.00045838 | Momentary | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 372 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500217 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 372 | keep | 0 | Sep | 2022 | 0.00025337 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 732 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500217 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 732 | keep | 0 | Sep | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 721 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500218 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 721 | keep | 0 | Sep | 2022 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 325 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500218 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 325 | keep | 0 | Sep | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 600 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500218 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 600 | keep | 0 | Sep | 2022 | 0.00040866 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 267 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500218 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 267 | keep | 0 | Sep | 2022 | 0.00018185 | 0.00018185 | Momentary | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 621 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500218 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 621 | keep | 0 | Sep | 2022 | 0.00042296 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 601 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500219 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 601 | keep | 0 | Sep | 2022 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 640 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500219 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 640 | keep | 0 | Sep | 2022 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 1699 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500219 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 1699 | keep | 0 | Sep | 2022 | 0.0011572 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 892 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500219 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 892 | keep | 0 | Sep | 2022 | 0.00060754 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-09-05 10:19 | 2022-09-05 10:20 | 1066 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA DE BALDRICH | S22090500219 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 1066 | keep | 0 | Sep | 2022 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
BARRANQUITAS | 2022-09-05 10:19 | 2022-09-05 10:20 | 2770 | 0:01 | T | DESGANCHE | RECIERRE | C22090500280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-05 | 2770 | keep | 0 | Sep | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
FAJARDO | 2022-09-05 10:20 | 2022-09-05 14:12 | 31 | 3:52 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | R22090500057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2022-09-05 | 7192 | keep | 0 | Sep | 2022 | 0.0048984 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BARRANQUITAS | 2022-09-05 10:20 | 2022-09-05 17:38 | 30 | 7:18 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22090500603 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 438 | 2022-09-05 | 13140 | keep | 0 | Sep | 2022 | 0.0089496 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-09-05 10:20 | 2022-09-05 12:40 | 500 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100, 1 X 80, 1 X 40, 1 X 30 Y 2 X 10 EN CORTES DE LINEA Y TRANSFORMADORES MAL TIEMPO | C22090400719 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2022-09-05 | 70000 | keep | 0 | Sep | 2022 | 0.047677 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-05 10:24 | 2022-09-05 18:29 | 15 | 8:05 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYOS | S22090500187 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 485 | 2022-09-05 | 7275 | keep | 0 | Sep | 2022 | 0.004955 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-09-05 10:26 | 2022-09-05 12:15 | 10 | 1:49 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR CRUCE DE FASE POR RAMA | P22090500157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-09-05 | 1090 | keep | 0 | Sep | 2022 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-09-05 10:28 | 2022-09-05 12:21 | 30 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A22090500037 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2022-09-05 | 3390 | keep | 0 | Sep | 2022 | 0.0023089 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-09-05 10:49 | 2022-09-05 15:58 | 8 | 5:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARA BAJANTES Y CONECIONES SECUNDARIAS | A22090500041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 309 | 2022-09-05 | 2472 | keep | 0 | Sep | 2022 | 0.0016837 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-09-05 11:04 | 2022-09-05 12:09 | 50 | 1:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22090500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2022-09-05 | 3250 | keep | 0 | Sep | 2022 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-09-05 11:07 | 2022-09-05 13:43 | 20 | 2:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A22090500045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 156 | 2022-09-05 | 3120 | keep | 0 | Sep | 2022 | 0.002125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-05 11:10 | 2022-09-06 07:25 | 56 | 20:15 | P | PROBLEMA DEL CLIENTE | 1 X 40 EN SU | C22090500359 | New_Event | Customer-Related Interruption | Include | Include | Public | 1215 | 2022-09-05 | 68040 | keep | 0 | Sep | 2022 | 0.046342 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
VEGA BAJA | 2022-09-05 11:20 | 2022-09-05 13:24 | 60 | 2:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L LLUVIAS | B22090500036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 124 | 2022-09-05 | 7440 | keep | 0 | Sep | 2022 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-05 11:23 | 2022-09-05 17:55 | 10 | 6:32 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | S22090500237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2022-09-05 | 3920 | keep | 0 | Sep | 2022 | 0.0026699 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-05 11:38 | 2022-09-05 11:45 | 4533 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL SE VERIFICO PERSONAL FUERA CON HO | B22090500043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2022-09-05 | 31731 | keep | 0 | Sep | 2022 | 0.021612 | 0.0030874 | Sustained | FALSE | FALSE | Not_TMED_Event | 4533
HUMACAO | 2022-09-05 11:43 | 2022-09-05 11:44 | 5630 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090500382 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 5630 | keep | 0 | Sep | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BARRANQUITAS | 2022-09-05 11:46 | 2022-09-05 16:25 | 38 | 4:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22090500385 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2022-09-05 | 10602 | keep | 0 | Sep | 2022 | 0.007221 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2022-09-05 12:11 | 2022-09-05 14:15 | 40 | 2:04 | P | ANIMAL | 1 X 50 EN C/L SE RETIRO AVE | B22090500056 | New_Event | Animals | Include | Include | Wildlife | 124 | 2022-09-05 | 4960 | keep | 0 | Sep | 2022 | 0.0033782 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2022-09-05 12:27 | 2022-09-05 12:28 | 2704 | 0:01 | T | ARBOL SOBRE LINEA | RECERRO | B22090500000 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-09-05 | 2704 | keep | 0 | Sep | 2022 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
GUAYAMA | 2022-09-05 12:30 | 2022-09-05 17:23 | 6 | 4:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | P22090500233 | New_Event | Secondary Wire Break | Include | Include | Equipment | 293 | 2022-09-05 | 1758 | keep | 0 | Sep | 2022 | 0.0011974 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-09-05 12:32 | 2022-09-05 19:37 | 5 | 7:05 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | S22090500252 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 425 | 2022-09-05 | 2125 | keep | 0 | Sep | 2022 | 0.0014473 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-09-05 12:32 | 2022-09-06 10:17 | 5 | 21:45 | P | DESGANCHE | 2 X 65 EN C/L Y SE RETIRO BAMBUA | S22090500252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1305 | 2022-09-05 | 6525 | keep | 0 | Sep | 2022 | 0.0044441 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2022-09-05 12:32 | 2022-09-05 20:06 | 100 | 7:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090500022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 454 | 2022-09-05 | 45400 | keep | 0 | Sep | 2022 | 0.030922 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-05 12:37 | 2022-09-05 12:38 | 922 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090500262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 922 | keep | 0 | Sep | 2022 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2022-09-05 12:37 | 2022-09-05 12:38 | 837 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090500262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 837 | keep | 0 | Sep | 2022 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2022-09-05 12:37 | 2022-09-05 12:38 | 908 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090500262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 908 | keep | 0 | Sep | 2022 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2022-09-05 12:37 | 2022-09-05 12:38 | 135 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 LLEVA LA CARGA DEL 1346-05 | S22090500262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 135 | keep | 0 | Sep | 2022 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-09-05 12:37 | 2022-09-05 12:38 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090500262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1 | keep | 0 | Sep | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-05 12:37 | 2022-09-05 12:38 | 1295 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 | S22090500262 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1295 | keep | 0 | Sep | 2022 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
ARECIBO | 2022-09-05 12:37 | 2022-09-05 15:34 | 20 | 2:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-09-05 | 3540 | keep | 0 | Sep | 2022 | 0.0024111 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-05 12:40 | 2022-09-05 12:41 | 602 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1418-03 LLEVA TRANSFERIDA LA CARGA DEL 1418-04 | S22090500257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 602 | keep | 0 | Sep | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-05 12:40 | 2022-09-05 12:41 | 43 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1418-03 LLEVA TRANSFERIDA LA CARGA DEL 1418-04 | S22090500257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 43 | keep | 0 | Sep | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2022-09-05 12:41 | 2022-09-06 06:09 | 35 | 17:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | C22090500426 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1048 | 2022-09-05 | 36680 | keep | 0 | Sep | 2022 | 0.024983 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-09-05 12:44 | 2022-09-05 12:45 | 602 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1418-03 LLEVA TRANSFERIDA LA CARGA DEL 1418-04 | S22090500260 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 602 | keep | 0 | Sep | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-05 12:44 | 2022-09-05 12:45 | 43 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1418-03 LLEVA TRANSFERIDA LA CARGA DEL 1418-04 | S22090500260 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 43 | keep | 0 | Sep | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2022-09-05 12:44 | 2022-09-05 12:45 | 2005 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R22090500000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-05 | 2005 | keep | 0 | Sep | 2022 | 0.0013656 | 0.0013656 | Momentary | FALSE | FALSE | Not_TMED_Event | 2005
BAYAMON | 2022-09-05 12:46 | 2022-09-05 16:11 | 80 | 3:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22090500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 205 | 2022-09-05 | 16400 | keep | 0 | Sep | 2022 | 0.01117 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-09-05 12:47 | 2022-09-05 13:07 | 2 | 0:20 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | R22090500084 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 20 | 2022-09-05 | 40 | keep | 0 | Sep | 2022 | 2.7244e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-09-05 12:51 | 2022-09-05 14:00 | 5961 | 1:09 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR 75% EN SERVICIO | B22090500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-09-05 | 411309 | keep | 0 | Sep | 2022 | 0.28014 | 0.00406 | Sustained | FALSE | FALSE | Not_TMED_Event | 5961
BAYAMON | 2022-09-05 12:51 | 2022-09-05 14:00 | 865 | 1:09 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR 1713-05 Y SE CERRO INTERRUPTOR ENTRO 95% DEL 1717-02 QUE ESTA POR EL 1713-05 | B22090500069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2022-09-05 | 59685 | keep | 0 | Sep | 2022 | 0.040651 | 0.00058915 | Sustained | FALSE | FALSE | Not_TMED_Event | 865
BAYAMON | 2022-09-05 12:52 | 2022-09-05 14:54 | 63 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN C/L | B22090500073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2022-09-05 | 7686 | keep | 0 | Sep | 2022 | 0.0052349 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CANOVANAS | 2022-09-05 12:53 | 2022-09-05 16:16 | 90 | 3:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 40 EN CORTES DE LINEA SE REEMPLAZARON DISCOS ROTOS Y CAJA QUEMADA | R22090500087 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 203 | 2022-09-05 | 18270 | keep | 0 | Sep | 2022 | 0.012444 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2022-09-05 12:55 | 2022-09-05 14:46 | 2704 | 1:51 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL | B22090500087 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 111 | 2022-09-05 | 300144 | keep | 0 | Sep | 2022 | 0.20443 | 0.0018417 | Sustained | FALSE | FALSE | Not_TMED_Event | 2704
CANOVANAS | 2022-09-05 12:59 | 2022-09-05 13:00 | 2005 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | R22090500000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-05 | 2005 | keep | 0 | Sep | 2022 | 0.0013656 | 0.0013656 | Momentary | FALSE | FALSE | Not_TMED_Event | 2005
CANOVANAS | 2022-09-05 12:59 | 2022-09-05 13:00 | 1026 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | R22090500000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-05 | 1026 | keep | 0 | Sep | 2022 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
BAYAMON | 2022-09-05 12:59 | 2022-09-05 14:22 | 4533 | 1:23 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE TRANSFIRIO 30% AL 1806-02 | B22090500097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2022-09-05 | 376239 | keep | 0 | Sep | 2022 | 0.25625 | 0.0030874 | Sustained | FALSE | FALSE | Not_TMED_Event | 4533
SAN JUAN | 2022-09-05 13:00 | 2022-09-06 10:50 | 2 | 21:50 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR CLIENTES ESTABAN FUERA DESDE AYER 13:00 SE HIZO EVENTO HOY YA QUE EL EVENTO DE AYER LO CERRARON. | S22090600461 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1310 | 2022-09-05 | 2620 | keep | 0 | Sep | 2022 | 0.0017845 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-09-05 13:00 | 2022-09-05 18:32 | 31 | 5:32 | P | CONDUCTOR ROTO O ABIERTO | REPARO PUENTE DE LINEA A MACHETE | R22090500100 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 332 | 2022-09-05 | 10292 | keep | 0 | Sep | 2022 | 0.0070098 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2022-09-05 13:03 | 2022-09-05 17:26 | 103 | 4:23 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO CON GOI BY-220905-04 | B22090500111 | New_Event | Primary Wire Break | Include | Include | Equipment | 263 | 2022-09-05 | 27089 | keep | 0 | Sep | 2022 | 0.01845 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
YAUCO | 2022-09-05 13:03 | 2022-09-05 14:21 | 500 | 1:18 | P | DESGANCHE | 2 X 140 EN C/L DESGANCHE | P22090500186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-09-05 | 39000 | keep | 0 | Sep | 2022 | 0.026563 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2022-09-05 13:04 | 2022-09-05 15:00 | 2276 | 1:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090500443 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 116 | 2022-09-05 | 264016 | keep | 0 | Sep | 2022 | 0.17982 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2022-09-05 13:04 | 2022-09-05 15:00 | 777 | 1:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090500443 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 116 | 2022-09-05 | 90132 | keep | 0 | Sep | 2022 | 0.061388 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2022-09-05 13:04 | 2022-09-05 15:00 | 12 | 1:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090500443 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 116 | 2022-09-05 | 1392 | keep | 0 | Sep | 2022 | 0.00094808 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-09-05 13:04 | 2022-09-05 15:00 | 1290 | 1:56 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C22090500443 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 116 | 2022-09-05 | 149640 | keep | 0 | Sep | 2022 | 0.10192 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
VEGA BAJA | 2022-09-05 13:04 | 2022-09-05 18:29 | 2132 | 5:25 | S | MAL TIEMPO/RAYOS | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR FUNDIDO POR DESCARGA ELECTRICA SE RESTABLECIO CARGA | A22090500109 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 325 | 2022-09-05 | 692900 | keep | 0 | Sep | 2022 | 0.47193 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-05 13:04 | 2022-09-05 18:29 | 2366 | 5:25 | S | MAL TIEMPO/RAYOS | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR FUNDIDO POR DESCARGA ELECTRICA SE RESTABLECIO CARGA | A22090500109 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 325 | 2022-09-05 | 768950 | keep | 0 | Sep | 2022 | 0.52373 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-09-05 13:04 | 2022-09-05 18:29 | 1976 | 5:25 | S | MAL TIEMPO/RAYOS | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR FUNDIDO POR DESCARGA ELECTRICA SE RESTABLECIO CARGA | A22090500109 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 325 | 2022-09-05 | 642200 | keep | 0 | Sep | 2022 | 0.4374 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-09-05 13:04 | 2022-09-05 18:29 | 3688 | 5:25 | S | MAL TIEMPO/RAYOS | SE REMPLAZO FUSIBLE EN LA ALTA DEL TRANSFORMADOR FUNDIDO POR DESCARGA ELECTRICA SE RESTABLECIO CARGA | A22090500109 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 325 | 2022-09-05 | 1198600 | keep | 0 | Sep | 2022 | 0.81636 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
CAGUAS | 2022-09-05 13:06 | 2022-09-05 19:00 | 105 | 5:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 30 SE REEMPLAZO DISCO PARTIDO Y SE REALIZO DESGANCHE | C22090500444 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 354 | 2022-09-05 | 37170 | keep | 0 | Sep | 2022 | 0.025316 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
MAYAGÃœEZ | 2022-09-05 13:08 | 2022-09-05 18:45 | 30 | 5:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M22090500024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 337 | 2022-09-05 | 10110 | keep | 0 | Sep | 2022 | 0.0068859 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-09-05 13:10 | 2022-09-05 17:23 | 6 | 4:13 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P22090500254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2022-09-05 | 1518 | keep | 0 | Sep | 2022 | 0.0010339 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-09-05 13:16 | 2022-09-05 13:17 | 602 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1418-03 LLEVA LA CARGA DEL 1418-04 | S22090500276 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 602 | keep | 0 | Sep | 2022 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-05 13:16 | 2022-09-05 13:17 | 43 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1418-03 LLEVA LA CARGA DEL 1418-04 | S22090500276 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 43 | keep | 0 | Sep | 2022 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
PONCE | 2022-09-05 13:18 | 2022-09-05 13:44 | 2696 | 0:26 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR | P22090500173 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 26 | 2022-09-05 | 70096 | keep | 0 | Sep | 2022 | 0.047742 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2022-09-05 13:20 | 2022-09-05 16:55 | 60 | 3:35 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | B22090500172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-09-05 | 12900 | keep | 0 | Sep | 2022 | 0.0087861 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2022-09-05 13:23 | 2022-09-05 13:24 | 2280 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090500471 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 2280 | keep | 0 | Sep | 2022 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
SAN JUAN | 2022-09-05 13:24 | 2022-09-05 13:27 | 164 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL MAL TIEMPO CARGA POR EL 1531-02 | S22090500281 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-09-05 | 492 | keep | 0 | Sep | 2022 | 0.0003351 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2022-09-05 13:24 | 2022-09-05 13:27 | 716 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL MAL TIEMPO LLEVANDO LA CARGA DEL 1421-02 | S22090500281 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-09-05 | 2148 | keep | 0 | Sep | 2022 | 0.001463 | 0.00048766 | Momentary | FALSE | FALSE | Not_TMED_Event | 716
CAGUAS | 2022-09-05 13:27 | 2022-09-05 16:30 | 60 | 3:03 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C22090500463 | New_Event | Primary Wire Break | Include | Include | Equipment | 183 | 2022-09-05 | 10980 | keep | 0 | Sep | 2022 | 0.0074784 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-05 13:30 | 2022-09-05 13:31 | 823 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DEL 1119-04 LLEVA 95% DEL 1115-05 SE CERRO POR CONTROL | S22090500288 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 823 | keep | 0 | Sep | 2022 | 0.00056054 | 0.00056054 | Momentary | FALSE | FALSE | Not_TMED_Event | 823
SAN JUAN | 2022-09-05 13:30 | 2022-09-05 13:31 | 2720 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL 1119-04 LLEVA 95% DEL 1115-05 SE CERRO POR CONTROL | S22090500288 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 2720 | keep | 0 | Sep | 2022 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
MAYAGÃœEZ | 2022-09-05 13:33 | 2022-09-05 18:38 | 60 | 5:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2022-09-05 | 18300 | keep | 0 | Sep | 2022 | 0.012464 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-09-05 13:34 | 2022-09-05 14:41 | 1712 | 1:07 | T | NO SE REPORTO CAUSA | SE CERRO BREAKER MANUAL NO OPERO POR SCADA NO SE REPORTO CAUSA | P22090500202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2022-09-05 | 114704 | keep | 0 | Sep | 2022 | 0.078124 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
BARRANQUITAS | 2022-09-05 13:38 | 2022-09-05 15:45 | 4 | 2:07 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22090500469 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2022-09-05 | 508 | keep | 0 | Sep | 2022 | 0.000346 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-09-05 13:43 | 2022-09-05 16:42 | 30 | 2:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN TRANSFORMADOR BACK TO BACK POR MAL TIEMPO | A22090500127 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 179 | 2022-09-05 | 5370 | keep | 0 | Sep | 2022 | 0.0036575 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-05 13:44 | 2022-09-05 16:26 | 55 | 2:42 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L RAYOS | R22090500104 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 162 | 2022-09-05 | 8910 | keep | 0 | Sep | 2022 | 0.0060686 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2022-09-05 13:48 | 2022-09-05 13:49 | 1709 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | C22090500480 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 1709 | keep | 0 | Sep | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
YAUCO | 2022-09-05 13:48 | 2022-09-05 16:19 | 50 | 2:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22090500218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-09-05 | 7550 | keep | 0 | Sep | 2022 | 0.0051423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-05 13:49 | 2022-09-05 16:00 | 50 | 2:11 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B22090500239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-09-05 | 6550 | keep | 0 | Sep | 2022 | 0.0044612 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-09-05 13:49 | 2022-09-05 13:50 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R22090500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 3464 | keep | 0 | Sep | 2022 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
HUMACAO | 2022-09-05 13:52 | 2022-09-05 17:25 | 1304 | 3:33 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTES DE LINEA MAL TIEMPO RAYOS | C22090500483 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 213 | 2022-09-05 | 277752 | keep | 0 | Sep | 2022 | 0.18918 | 0.00088815 | Sustained | FALSE | FALSE | Not_TMED_Event | 1304
CANOVANAS | 2022-09-05 13:57 | 2022-09-05 17:20 | 47 | 3:23 | P | DESGANCHE | 1 X 65 EN C/L Y 1 X 10 EN XMR | R22090500111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2022-09-05 | 9541 | keep | 0 | Sep | 2022 | 0.0064983 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2022-09-05 14:00 | 2022-09-05 15:49 | 1490 | 1:49 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE NORMALIZO ALIMENTADOR 25% ADICIONAL EN SERVICIO GOI BY-220905-02 | B22090500069 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-09-05 | 162410 | keep | 0 | Sep | 2022 | 0.11062 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-05 14:01 | 2022-09-05 21:32 | 350 | 7:31 | P | MAL TIEMPO/RAYOS | 1 X 200 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090500496 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 451 | 2022-09-05 | 157850 | keep | 0 | Sep | 2022 | 0.10751 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
GUAYAMA | 2022-09-05 14:04 | 2022-09-05 19:43 | 1 | 5:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | P22090500230 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 339 | 2022-09-05 | 339 | keep | 0 | Sep | 2022 | 0.00023089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-05 14:06 | 2022-09-05 14:08 | 1681 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL MAL TIEMPO | S22090500313 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-05 | 3362 | keep | 0 | Sep | 2022 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2022-09-05 14:06 | 2022-09-05 14:08 | 1598 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL MAL TIEMPO | S22090500313 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-05 | 3196 | keep | 0 | Sep | 2022 | 0.0021768 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2022-09-05 14:07 | 2022-09-05 16:00 | 148 | 1:53 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L 1 X 15 EN XMR RAYOS | S22090500312 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 113 | 2022-09-05 | 16724 | keep | 0 | Sep | 2022 | 0.011391 | 0.0001008 | Sustained | FALSE | FALSE | Not_TMED_Event | 148
SAN JUAN | 2022-09-05 14:08 | 2022-09-05 14:09 | 338 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | S22090500318 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 338 | keep | 0 | Sep | 2022 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2022-09-05 14:08 | 2022-09-05 14:09 | 733 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | S22090500313 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 733 | keep | 0 | Sep | 2022 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-09-05 14:13 | 2022-09-05 14:14 | 8679 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 85% DE SU CARGA TRANSFERIDA AL 1206-03 1204-05 | S22090500348 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 8679 | keep | 0 | Sep | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-09-05 14:13 | 2022-09-05 14:14 | 3719 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 10% DE SU CARGA TRANSFERIDA AL 1620-02 LLEVA 85% DEL 1204-05 | S22090500348 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 3719 | keep | 0 | Sep | 2022 | 0.002533 | 0.002533 | Momentary | FALSE | FALSE | Not_TMED_Event | 3719
BAYAMON | 2022-09-05 14:13 | 2022-09-05 17:30 | 60 | 3:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L LLUVIAS | B22090500300 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 197 | 2022-09-05 | 11820 | keep | 0 | Sep | 2022 | 0.0080505 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 1 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 2 | keep | 0 | Sep | 2022 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 1964 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 3928 | keep | 0 | Sep | 2022 | 0.0026753 | 0.0013377 | Momentary | FALSE | FALSE | Not_TMED_Event | 1964
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 733 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 1466 | keep | 0 | Sep | 2022 | 0.00099849 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 2124 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 4248 | keep | 0 | Sep | 2022 | 0.0028933 | 0.0014466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2124
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 1825 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 3650 | keep | 0 | Sep | 2022 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 4398 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 8796 | keep | 0 | Sep | 2022 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 2782 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 5564 | keep | 0 | Sep | 2022 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 262 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 524 | keep | 0 | Sep | 2022 | 0.00035689 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 296 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 592 | keep | 0 | Sep | 2022 | 0.00040321 | 0.0002016 | Momentary | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 79 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 158 | keep | 0 | Sep | 2022 | 0.00010761 | 5.3807e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 1129 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 2258 | keep | 0 | Sep | 2022 | 0.0015379 | 0.00076896 | Momentary | FALSE | FALSE | Not_TMED_Event | 1129
SAN JUAN | 2022-09-05 14:14 | 2022-09-05 14:16 | 1573 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090500319 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-05 | 3146 | keep | 0 | Sep | 2022 | 0.0021427 | 0.0010714 | Momentary | FALSE | FALSE | Not_TMED_Event | 1573
ARECIBO | 2022-09-05 14:16 | 2022-09-05 16:10 | 1883 | 1:54 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA SE CERRO INTERRUPTOR | A22090500145 | New_Event | Primary Wire Break | Include | Include | Equipment | 114 | 2022-09-05 | 214662 | keep | 0 | Sep | 2022 | 0.14621 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
SAN JUAN | 2022-09-05 14:20 | 2022-09-05 18:16 | 130 | 3:56 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | S22090500339 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-09-05 | 30680 | keep | 0 | Sep | 2022 | 0.020896 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2022-09-05 14:22 | 2022-09-05 14:27 | 2891 | 0:05 | T | MAL TIEMPO/LLUVIA O VIENTO | CERRADO X CONTROL FUERTES LLUVIAS Y TRONADAS | R22090500120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-09-05 | 14455 | keep | 0 | Sep | 2022 | 0.0098452 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
CANOVANAS | 2022-09-05 14:22 | 2022-09-05 14:27 | 1474 | 0:05 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO CERRADO X CONTROL FUERTES LLUVIAS Y TRONADAS | R22090500120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-09-05 | 7370 | keep | 0 | Sep | 2022 | 0.0050197 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
BAYAMON | 2022-09-05 14:22 | 2022-09-05 14:58 | 3173 | 0:36 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE NORMALIZO LA CARGA ENTRO 70% ADICIONAL | B22090500097 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 36 | 2022-09-05 | 114228 | keep | 0 | Sep | 2022 | 0.0778 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-05 14:25 | 2022-09-05 14:28 | 2005 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | CERRADO X CONTROL | R22090500000 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 3 | 2022-09-05 | 6015 | keep | 0 | Sep | 2022 | 0.0040968 | 0.0013656 | Momentary | FALSE | FALSE | Not_TMED_Event | 2005
UTUADO | 2022-09-05 14:25 | 2022-09-05 16:36 | 12 | 2:11 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A22090500154 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 131 | 2022-09-05 | 1572 | keep | 0 | Sep | 2022 | 0.0010707 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-09-05 14:31 | 2022-09-05 15:14 | 10 | 0:43 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR RAYOS | R22090500128 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 43 | 2022-09-05 | 430 | keep | 0 | Sep | 2022 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-05 14:36 | 2022-09-05 14:37 | 1835 | 0:01 | T | MAL TIEMPO/RAYOS | RECERRO INTERRUPTOR EN SERVICIO | C22090500540 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-05 | 1835 | keep | 0 | Sep | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
CANOVANAS | 2022-09-05 14:37 | 2022-09-05 14:42 | 2580 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R22090500140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-09-05 | 12900 | keep | 0 | Sep | 2022 | 0.0087861 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2022-09-05 14:37 | 2022-09-05 14:42 | 500 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11100 | R22090500140 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2022-09-05 | 2500 | keep | 0 | Sep | 2022 | 0.0017027 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
HUMACAO | 2022-09-05 14:37 | 2022-09-05 16:13 | 15 | 1:36 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090500545 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 96 | 2022-09-05 | 1440 | keep | 0 | Sep | 2022 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-09-05 14:38 | 2022-09-05 14:39 | 1394 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 16500 | R22090500151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1394 | keep | 0 | Sep | 2022 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2022-09-05 14:38 | 2022-09-05 14:39 | 412 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 16500 | R22090500151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 412 | keep | 0 | Sep | 2022 | 0.00028061 | 0.00028061 | Momentary | FALSE | FALSE | Not_TMED_Event | 412
FAJARDO | 2022-09-05 14:38 | 2022-09-05 14:39 | 2286 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | R22090500000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 2286 | keep | 0 | Sep | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-09-05 14:38 | 2022-09-05 14:39 | 693 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | R22090500000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 693 | keep | 0 | Sep | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
CANOVANAS | 2022-09-05 14:39 | 2022-09-05 17:56 | 1 | 3:17 | P | DESGANCHE | 1 X 30 EN C/L Y 1 X 10 EN XMR DESGANCHO REMPLAZO 2 JUEGOS DE DISCOS | R22090400276 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2022-09-05 | 197 | keep | 0 | Sep | 2022 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-05 14:43 | 2022-09-05 17:58 | 40 | 3:15 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTES DE LINEA | B22090500346 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2022-09-05 | 7800 | keep | 0 | Sep | 2022 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-05 14:47 | 2022-09-05 18:00 | 80 | 3:13 | P | MAL TIEMPO/RAYOS | 2 X 100 EN C/L RAYOS | B22090500354 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 193 | 2022-09-05 | 15440 | keep | 0 | Sep | 2022 | 0.010516 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-05 14:53 | 2022-09-05 14:55 | 1061 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S22090500386 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-05 | 2122 | keep | 0 | Sep | 2022 | 0.0014453 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
CANOVANAS | 2022-09-05 14:55 | 2022-09-06 14:25 | 7 | 23:30 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA DEL BAJANTE PRIMARIO | R22090500142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1410 | 2022-09-05 | 9870 | keep | 0 | Sep | 2022 | 0.0067224 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2022-09-05 14:55 | 2022-09-05 16:00 | 15 | 1:05 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P22090500246 | New_Event | Animals | Include | Include | Wildlife | 65 | 2022-09-05 | 975 | keep | 0 | Sep | 2022 | 0.00066407 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-09-05 15:03 | 2022-09-05 15:04 | 1131 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | C22090500564 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 1131 | keep | 0 | Sep | 2022 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
HUMACAO | 2022-09-05 15:09 | 2022-09-05 16:40 | 22 | 1:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C22090500573 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-09-05 | 2002 | keep | 0 | Sep | 2022 | 0.0013636 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2022-09-05 15:10 | 2022-09-05 15:11 | 2302 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | C22090500578 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 2302 | keep | 0 | Sep | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
PONCE | 2022-09-05 15:10 | 2022-09-05 20:15 | 35 | 5:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE ABRIO PUENTE HACIA ALAMBRE EN EL SUELO | P22090500271 | New_Event | Primary Wire Break | Include | Include | Equipment | 305 | 2022-09-05 | 10675 | keep | 0 | Sep | 2022 | 0.0072707 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2022-09-05 15:11 | 2022-09-05 15:13 | 1879 | 0:02 | T | MAL TIEMPO/RAYOS | DISPARO INTERRUPTOR CERRADO POR CONTROL HUBO MAL TIEMPO | C22090500576 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2 | 2022-09-05 | 3758 | keep | 0 | Sep | 2022 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2022-09-05 15:14 | 2022-09-05 17:10 | 1879 | 1:56 | T | MAL TIEMPO/RAYOS | DISPARO INTERRUPTOR SE PATRULLO NO SE ENCONTRO NADA CERRADO POR CONTROL HUBO MAL TIEMPO | C22090500576 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 116 | 2022-09-05 | 217964 | keep | 0 | Sep | 2022 | 0.14845 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
BARRANQUITAS | 2022-09-05 15:16 | 2022-09-05 17:10 | 45 | 1:54 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090500584 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 114 | 2022-09-05 | 5130 | keep | 0 | Sep | 2022 | 0.003494 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2022-09-05 15:17 | 2022-09-06 09:54 | 60 | 18:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R22090500156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1117 | 2022-09-05 | 67020 | keep | 0 | Sep | 2022 | 0.045647 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 849 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 16980 | keep | 0 | Sep | 2022 | 0.011565 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 893 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 17860 | keep | 0 | Sep | 2022 | 0.012164 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 602 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 12040 | keep | 0 | Sep | 2022 | 0.0082004 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 43 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 860 | keep | 0 | Sep | 2022 | 0.00058574 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 1389 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 27780 | keep | 0 | Sep | 2022 | 0.018921 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 673 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 13460 | keep | 0 | Sep | 2022 | 0.0091675 | 0.00045838 | Sustained | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 94 | 0:20 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 1880 | keep | 0 | Sep | 2022 | 0.0012805 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 732 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500436 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 14640 | keep | 0 | Sep | 2022 | 0.0099712 | 0.00049856 | Sustained | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 721 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 14420 | keep | 0 | Sep | 2022 | 0.0098214 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 325 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 6500 | keep | 0 | Sep | 2022 | 0.0044271 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 600 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 12000 | keep | 0 | Sep | 2022 | 0.0081731 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 267 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 5340 | keep | 0 | Sep | 2022 | 0.003637 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 621 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 12420 | keep | 0 | Sep | 2022 | 0.0084592 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 2203 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 44060 | keep | 0 | Sep | 2022 | 0.030009 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 246 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 4920 | keep | 0 | Sep | 2022 | 0.003351 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 15:40 | 9 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2022-09-05 | 180 | keep | 0 | Sep | 2022 | 0.0001226 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 16:16 | 601 | 0:56 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500438 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 56 | 2022-09-05 | 33656 | keep | 0 | Sep | 2022 | 0.022923 | 0.00040934 | Sustained | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 16:16 | 1699 | 0:56 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500438 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 56 | 2022-09-05 | 95144 | keep | 0 | Sep | 2022 | 0.064802 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 16:16 | 892 | 0:56 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500438 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 56 | 2022-09-05 | 49952 | keep | 0 | Sep | 2022 | 0.034022 | 0.00060754 | Sustained | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2022-09-05 15:20 | 2022-09-05 16:16 | 1066 | 0:56 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500438 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 56 | 2022-09-05 | 59696 | keep | 0 | Sep | 2022 | 0.040659 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
HUMACAO | 2022-09-05 15:31 | 2022-09-05 20:48 | 181 | 5:17 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR PRIMARIO EN BRACKET | C22090500602 | New_Event | Primary Wire Break | Include | Include | Equipment | 317 | 2022-09-05 | 57377 | keep | 0 | Sep | 2022 | 0.039079 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
PONCE | 2022-09-05 15:34 | 2022-09-05 21:50 | 35 | 6:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE REPARO ALAMBRE PRIMARIO | P22090500257 | New_Event | Primary Wire Break | Include | Include | Equipment | 376 | 2022-09-05 | 13160 | keep | 0 | Sep | 2022 | 0.0089632 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2022-09-05 15:37 | 2022-09-05 19:18 | 587 | 3:41 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LA LINEA | C22090500599 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2022-09-05 | 129727 | keep | 0 | Sep | 2022 | 0.088356 | 0.0003998 | Sustained | FALSE | FALSE | Not_TMED_Event | 587
CAGUAS | 2022-09-05 15:39 | 2022-09-05 20:35 | 769 | 4:56 | P | DESGANCHE | 1 X 100 Y 3 X 100 EN CORTES DE LINEA SE REALIZO DESGANCHE CRITICO Y SE REEMPLAZO CAJA PARTIDA | C22090500608 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-09-05 | 227624 | keep | 0 | Sep | 2022 | 0.15503 | 0.00052376 | Sustained | FALSE | FALSE | Not_TMED_Event | 769
BAYAMON | 2022-09-05 15:42 | 2022-09-05 17:59 | 60 | 2:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L LLUVIAS | B22090500412 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 137 | 2022-09-05 | 8220 | keep | 0 | Sep | 2022 | 0.0055986 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2022-09-05 15:44 | 2022-09-05 15:50 | 625 | 0:06 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR POR CONDUCTOR VIVO EN EL SUELO | R22090500165 | New_Event | Primary Wire Break | Include | Include | Equipment | 6 | 2022-09-05 | 3750 | keep | 0 | Sep | 2022 | 0.0025541 | 0.00042568 | Sustained | FALSE | FALSE | Not_TMED_Event | 625
CANOVANAS | 2022-09-05 15:44 | 2022-09-06 08:44 | 47 | 17:00 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CULEBRA CRUZO FASE | R22090500164 | New_Event | Animals | Include | Include | Wildlife | 1020 | 2022-09-05 | 47940 | keep | 0 | Sep | 2022 | 0.032652 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2022-09-05 15:47 | 2022-09-06 13:57 | 8 | 22:10 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYOS | C22090500620 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1330 | 2022-09-05 | 10640 | keep | 0 | Sep | 2022 | 0.0072469 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-09-05 15:47 | 2022-09-05 15:48 | 215 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090500261 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 215 | keep | 0 | Sep | 2022 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
FAJARDO | 2022-09-05 15:50 | 2022-09-05 16:37 | 469 | 0:47 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR Y SE TRANSFIRIO 45% DE LA CARGA AL 2101-01 | R22090500165 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 47 | 2022-09-05 | 22043 | keep | 0 | Sep | 2022 | 0.015013 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-05 15:52 | 2022-09-05 17:27 | 60 | 1:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 Y 1 X 50 EN CORTES DE LINEA SE REEMPLAZO CAJA PRIMARIA PARTIDA | S22090500503 | New_Event | Cutout Failure | Include | Include | Equipment | 95 | 2022-09-05 | 5700 | keep | 0 | Sep | 2022 | 0.0038822 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-05 15:56 | 2022-09-05 15:57 | 1058 | 0:01 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 1058 | keep | 0 | Sep | 2022 | 0.0007206 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2022-09-05 15:56 | 2022-09-05 15:57 | 100 | 0:01 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 100 | keep | 0 | Sep | 2022 | 6.811e-05 | 6.811e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-05 15:56 | 2022-09-05 15:57 | 278 | 0:01 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE BALDRICH | S22090500450 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2022-09-05 | 278 | keep | 0 | Sep | 2022 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
CAGUAS | 2022-09-05 16:00 | 2022-09-05 20:33 | 10 | 4:33 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGACHE CRITICO | C22090500636 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 273 | 2022-09-05 | 2730 | keep | 0 | Sep | 2022 | 0.0018594 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-05 16:08 | 2022-09-05 16:40 | 6 | 0:32 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR Y SE REALIZA DESGANCHE | A22090500165 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 32 | 2022-09-05 | 192 | keep | 0 | Sep | 2022 | 0.00013077 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-09-05 16:09 | 2022-09-05 16:10 | 776 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | C22090500646 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 776 | keep | 0 | Sep | 2022 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
ARECIBO | 2022-09-05 16:10 | 2022-09-05 17:40 | 985 | 1:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO MACHETES | A22090500190 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 90 | 2022-09-05 | 88650 | keep | 0 | Sep | 2022 | 0.060379 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-05 16:13 | 2022-09-05 16:14 | 1835 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE MAL TIEMPO | C22090500655 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-05 | 1835 | keep | 0 | Sep | 2022 | 0.0012498 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-05 16:13 | 2022-09-05 20:40 | 40 | 4:27 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN C/L SE ELIMIO PARARAYO | B22090500419 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 267 | 2022-09-05 | 10680 | keep | 0 | Sep | 2022 | 0.0072741 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-05 16:14 | 2022-09-05 16:49 | 15 | 0:35 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090500545 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 35 | 2022-09-05 | 525 | keep | 0 | Sep | 2022 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-09-05 16:15 | 2022-09-05 16:16 | 5630 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | C22090500658 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 5630 | keep | 0 | Sep | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
BAYAMON | 2022-09-05 16:17 | 2022-09-05 20:40 | 30 | 4:23 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO EXPLOTADO | B22090500041 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 263 | 2022-09-05 | 7890 | keep | 0 | Sep | 2022 | 0.0053738 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-09-05 16:18 | 2022-09-05 16:55 | 12 | 0:37 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C22090500664 | New_Event | Animals | Include | Include | Wildlife | 37 | 2022-09-05 | 444 | keep | 0 | Sep | 2022 | 0.00030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2022-09-05 16:22 | 2022-09-05 19:10 | 28 | 2:48 | P | MAL TIEMPO/RAYOS | 1 X 25 Y 1 X 20 EN CORTES DE LINEA MAL TIEMPO | C22090500670 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 168 | 2022-09-05 | 4704 | keep | 0 | Sep | 2022 | 0.0032039 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BARRANQUITAS | 2022-09-05 16:23 | 2022-09-05 18:28 | 90 | 2:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22090500671 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2022-09-05 | 11250 | keep | 0 | Sep | 2022 | 0.0076623 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
FAJARDO | 2022-09-05 16:25 | 2022-09-05 21:23 | 10 | 4:58 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO RAYOS | R22090500185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 298 | 2022-09-05 | 2980 | keep | 0 | Sep | 2022 | 0.0020297 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2022-09-05 16:25 | 2022-09-05 18:50 | 10 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR NO CAUSA | P22090500244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2022-09-05 | 1450 | keep | 0 | Sep | 2022 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-05 16:26 | 2022-09-05 17:57 | 50 | 1:31 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | B22090500412 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 91 | 2022-09-05 | 4550 | keep | 0 | Sep | 2022 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-05 16:27 | 2022-09-05 18:24 | 150 | 1:57 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTES DE LINEA MAL TIEMPO | C22090500682 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-09-05 | 17550 | keep | 0 | Sep | 2022 | 0.011953 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-09-05 16:27 | 2022-09-05 16:28 | 1131 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | C22090500684 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 1131 | keep | 0 | Sep | 2022 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
SAN JUAN | 2022-09-05 16:31 | 2022-09-05 19:02 | 45 | 2:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO EN ANCLADA MEDIANTE G.O.I. SJ-220905-02 | S22090500554 | New_Event | Primary Wire Break | Include | Include | Equipment | 151 | 2022-09-05 | 6795 | keep | 0 | Sep | 2022 | 0.004628 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-09-05 16:36 | 2022-09-06 08:29 | 423 | 15:53 | P | CONDUCTOR ROTO O ABIERTO | CG-220906-01A SE SECCIONALIZO CONDUCTO DEL SUELO | C22090500698 | New_Event | Primary Wire Break | Include | Include | Equipment | 953 | 2022-09-05 | 403119 | keep | 0 | Sep | 2022 | 0.27456 | 0.0002881 | Sustained | FALSE | FALSE | Not_TMED_Event | 423
FAJARDO | 2022-09-05 16:37 | 2022-09-05 19:30 | 156 | 2:53 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO, NO HAY CLIENTES FUERA | R22090500165 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 173 | 2022-09-05 | 26988 | keep | 0 | Sep | 2022 | 0.018381 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-05 16:40 | 2022-09-06 10:50 | 99 | 18:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C22090500705 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1090 | 2022-09-05 | 107910 | keep | 0 | Sep | 2022 | 0.073497 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
CANOVANAS | 2022-09-05 16:44 | 2022-09-05 19:24 | 2005 | 2:40 | T | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE LINEA A MACHETE | R22090500219 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 160 | 2022-09-05 | 320800 | keep | 0 | Sep | 2022 | 0.2185 | 0.0013656 | Sustained | FALSE | FALSE | Not_TMED_Event | 2005
SAN JUAN | 2022-09-05 16:46 | 2022-09-06 16:21 | 51 | 23:35 | P | CABLE SOTERRADO AVERIADO | AVERIA NUEVA T-65 A T-66 AVERIA VIEJA T-68 A T-69 2 SUM20 40 AMP 2 X 65 EN RISER | S22090500567 | New_Event | UG Cable Fault | Include | Include | Equipment | 1415 | 2022-09-05 | 72165 | keep | 0 | Sep | 2022 | 0.049151 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
GUAYAMA | 2022-09-05 16:51 | 2022-09-06 13:37 | 3 | 20:46 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR AVERIADO DE 25KVA A 2.4KV POR UNO DE LA MISMA CAPACIDAD | P22090500052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1246 | 2022-09-05 | 3738 | keep | 0 | Sep | 2022 | 0.0025459 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-09-05 16:54 | 2022-09-06 13:27 | 1 | 20:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C22090500725 | New_Event | Cutout Failure | Include | Include | Equipment | 1233 | 2022-09-05 | 1233 | keep | 0 | Sep | 2022 | 0.00083979 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-05 17:06 | 2022-09-05 17:07 | 1825 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090500587 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1825 | keep | 0 | Sep | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-09-05 17:06 | 2022-09-05 17:07 | 47 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090500587 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 47 | keep | 0 | Sep | 2022 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2022-09-05 17:06 | 2022-09-05 17:07 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090500587 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 315 | keep | 0 | Sep | 2022 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2022-09-05 17:06 | 2022-09-05 17:07 | 2 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090500587 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 2 | keep | 0 | Sep | 2022 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-09-05 17:06 | 2022-09-05 17:07 | 2391 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S22090500587 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 2391 | keep | 0 | Sep | 2022 | 0.0016285 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2022-09-05 17:07 | 2022-09-05 17:28 | 8 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO MONTURA Y SE REPARO BAJANTE SECUNDARIO | S22090500226 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2022-09-05 | 168 | keep | 0 | Sep | 2022 | 0.00011442 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-09-05 17:10 | 2022-09-05 17:14 | 972 | 0:04 | P | MAL TIEMPO/RAYOS | SE PATRULLO NO SE ENCONTRO CAUSA SE CERRO MACHETES | C22090500576 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 4 | 2022-09-05 | 3888 | keep | 0 | Sep | 2022 | 0.0026481 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2022-09-05 17:14 | 2022-09-05 18:28 | 1 | 1:14 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | R22090500249 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 74 | 2022-09-05 | 74 | keep | 0 | Sep | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-09-05 17:14 | 2022-09-05 19:40 | 35 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22090500747 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2022-09-05 | 5110 | keep | 0 | Sep | 2022 | 0.0034804 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2022-09-05 17:16 | 2022-09-05 20:24 | 76 | 3:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 25 EN CORTES DE LINEA MAL TIEMPO | C22090500748 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 188 | 2022-09-05 | 14288 | keep | 0 | Sep | 2022 | 0.0097315 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
BAYAMON | 2022-09-05 17:19 | 2022-09-05 18:55 | 60 | 1:36 | P | DESGANCHE | 3 X 50 EN C/L SE DESGANCHO | B22090500481 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 96 | 2022-09-05 | 5760 | keep | 0 | Sep | 2022 | 0.0039231 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-05 17:21 | 2022-09-05 17:23 | 4533 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22090500485 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-05 | 9066 | keep | 0 | Sep | 2022 | 0.0061748 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
FAJARDO | 2022-09-05 17:23 | 2022-09-05 23:11 | 30 | 5:48 | P | DESGANCHE | 1 X 30 EN C/L | R22090500264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2022-09-05 | 10440 | keep | 0 | Sep | 2022 | 0.0071106 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-05 17:27 | 2022-09-05 21:15 | 40 | 3:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M22090500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2022-09-05 | 9120 | keep | 0 | Sep | 2022 | 0.0062116 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-05 17:30 | 2022-09-05 18:52 | 1364 | 1:22 | T | DESGANCHE | DISPARO SE RETIRARON BAMBUAS SOBRE LINEAS CON VARETA | C22090500772 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-09-05 | 111848 | keep | 0 | Sep | 2022 | 0.076179 | 0.00092901 | Sustained | FALSE | FALSE | Not_TMED_Event | 1364
HUMACAO | 2022-09-05 17:34 | 2022-09-06 12:01 | 24 | 18:27 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE CON AVE | C22090500765 | New_Event | Animals | Include | Include | Wildlife | 1107 | 2022-09-05 | 26568 | keep | 0 | Sep | 2022 | 0.018095 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2022-09-05 17:46 | 2022-09-05 20:21 | 20 | 2:35 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR RAYOS | A22090500200 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 155 | 2022-09-05 | 3100 | keep | 0 | Sep | 2022 | 0.0021114 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-05 17:51 | 2022-09-05 18:04 | 31 | 0:13 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | C22090500808 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 13 | 2022-09-05 | 403 | keep | 0 | Sep | 2022 | 0.00027448 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2022-09-05 17:56 | 2022-09-05 18:59 | 15 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO VARIAS CONDICIONES EN LA LINEA SECUNDARIA | B22090500232 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2022-09-05 | 945 | keep | 0 | Sep | 2022 | 0.00064364 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-09-05 17:59 | 2022-09-05 20:56 | 676 | 2:57 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C22090501004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-09-05 | 119652 | keep | 0 | Sep | 2022 | 0.081494 | 0.00046042 | Sustained | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2022-09-05 17:59 | 2022-09-05 18:00 | 2302 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | C22090500825 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 2302 | keep | 0 | Sep | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
BARRANQUITAS | 2022-09-05 18:03 | 2022-09-06 00:31 | 145 | 6:28 | P | DESGANCHE | 2 X 50 Y 1 X 80 EN C/LS | C22090500826 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2022-09-05 | 56260 | keep | 0 | Sep | 2022 | 0.038318 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
HUMACAO | 2022-09-05 18:15 | 2022-09-05 19:52 | 40 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22090500841 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2022-09-05 | 3880 | keep | 0 | Sep | 2022 | 0.0026427 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-05 18:17 | 2022-09-05 20:21 | 40 | 2:04 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA | B22090500506 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2022-09-05 | 4960 | keep | 0 | Sep | 2022 | 0.0033782 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2022-09-05 18:28 | 2022-09-05 18:29 | 2286 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | R22090500359 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 2286 | keep | 0 | Sep | 2022 | 0.001557 | 0.001557 | Momentary | FALSE | FALSE | Not_TMED_Event | 2286
FAJARDO | 2022-09-05 18:28 | 2022-09-05 18:29 | 693 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | R22090500360 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 693 | keep | 0 | Sep | 2022 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
FAJARDO | 2022-09-05 18:28 | 2022-09-05 18:29 | 4098 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO | R22090500361 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-05 | 4098 | keep | 0 | Sep | 2022 | 0.0027911 | 0.0027911 | Momentary | FALSE | FALSE | Not_TMED_Event | 4098
FAJARDO | 2022-09-05 18:29 | 2022-09-06 08:37 | 1 | 14:08 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | R22090500249 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 848 | 2022-09-05 | 848 | keep | 0 | Sep | 2022 | 0.00057757 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-05 18:29 | 2022-09-05 20:20 | 1 | 1:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA LINEA PRIMARIA PARTIDA Y SE CERRO PUENTE | A22090500217 | New_Event | Primary Wire Break | Include | Include | Equipment | 111 | 2022-09-05 | 111 | keep | 0 | Sep | 2022 | 7.5602e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-09-05 18:46 | 2022-09-05 18:52 | 3296 | 0:06 | T | DESGANCHE | SE ABRIO INTERRUPTOR PARA RETIRAR BAMBUA SOBRE LINEA | C22090500772 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-09-05 | 19776 | keep | 0 | Sep | 2022 | 0.013469 | 0.0022449 | Sustained | FALSE | FALSE | Not_TMED_Event | 3296
PONCE | 2022-09-05 18:53 | 2022-09-06 09:35 | 6 | 14:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22090500297 | New_Event | Vegetation Contact | Include | Include | Vegetation | 882 | 2022-09-05 | 5292 | keep | 0 | Sep | 2022 | 0.0036044 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-09-05 18:59 | 2022-09-05 19:00 | 1597 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22090500047 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-09-05 | 1597 | keep | 0 | Sep | 2022 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
MAYAGÃœEZ | 2022-09-05 19:00 | 2022-09-05 21:23 | 532 | 2:23 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETE QUEMADO SE CERRO N/O CON ALIM 6406-02 | M22090500057 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 143 | 2022-09-05 | 76076 | keep | 0 | Sep | 2022 | 0.051815 | 0.00036234 | Sustained | FALSE | FALSE | Not_TMED_Event | 532
YAUCO | 2022-09-05 19:22 | 2022-09-05 21:54 | 50 | 2:32 | P | ARBOL SOBRE LINEA | SOLO SE ABRIO MACHETE PARA REMOVER ARBOL SOBRE LAS LINEAS Y SE CERRO NUEVAMENTE | M22090500066 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 152 | 2022-09-05 | 7600 | keep | 0 | Sep | 2022 | 0.0051763 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-09-05 19:24 | 2022-09-05 19:58 | 1000 | 0:34 | P | CONDUCTOR ROTO O ABIERTO | DISPARO PERSONAL REALIZANDO OPERACIONES | R22090500219 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 34 | 2022-09-05 | 34000 | keep | 0 | Sep | 2022 | 0.023157 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2022-09-05 19:26 | 2022-09-06 16:50 | 300 | 21:24 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LAS LINEAS Y SE CERRO INTELLIRUPTER | A22090500227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1284 | 2022-09-05 | 385200 | keep | 0 | Sep | 2022 | 0.26236 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-09-05 19:28 | 2022-09-06 11:25 | 5 | 15:57 | P | ARBOL SOBRE LINEA | 1 X 20 EN C/L SE RETIRO ARBOL | B22090500510 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 957 | 2022-09-05 | 4785 | keep | 0 | Sep | 2022 | 0.003259 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2022-09-05 19:30 | 2022-09-05 21:23 | 1 | 1:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER POR CAJA DEFECTUOSA | A22090500267 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2022-09-05 | 113 | keep | 0 | Sep | 2022 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-05 19:38 | 2022-09-06 08:16 | 781 | 12:38 | P | MAL TIEMPO/RAYOS | 3 X 200 EN CORTES DE LINEA MAL TIEMPO | C22090500964 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 758 | 2022-09-05 | 591998 | keep | 0 | Sep | 2022 | 0.40321 | 0.00053194 | Sustained | FALSE | FALSE | Not_TMED_Event | 781
BAYAMON | 2022-09-05 19:40 | 2022-09-05 20:50 | 15 | 1:10 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO | B22090500524 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 70 | 2022-09-05 | 1050 | keep | 0 | Sep | 2022 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-09-05 19:49 | 2022-09-05 19:50 | 1839 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22090500469 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1839 | keep | 0 | Sep | 2022 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2022-09-05 19:49 | 2022-09-05 19:50 | 1778 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22090500469 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1778 | keep | 0 | Sep | 2022 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2022-09-05 19:49 | 2022-09-05 19:50 | 1376 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22090500469 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1376 | keep | 0 | Sep | 2022 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2022-09-05 19:49 | 2022-09-05 19:50 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22090500467 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 293 | keep | 0 | Sep | 2022 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2022-09-05 19:49 | 2022-09-05 19:50 | 1215 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5400 | R22090500467 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-05 | 1215 | keep | 0 | Sep | 2022 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
AGUADILLA | 2022-09-05 19:54 | 2022-09-05 22:00 | 200 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M22090500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-09-05 | 25200 | keep | 0 | Sep | 2022 | 0.017164 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-09-05 19:57 | 2022-09-06 10:11 | 1 | 14:14 | P | DESGANCHE | 2 X 15 EN XMR Y DESGANCHE | B22090500528 | New_Event | Vegetation Contact | Include | Include | Vegetation | 854 | 2022-09-05 | 854 | keep | 0 | Sep | 2022 | 0.00058166 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-05 19:58 | 2022-09-05 20:00 | 143 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL 1404-06 LLEVA 80% DE LA CARGA DEL 1404-07 SE CERRO POR CONTROL | S22090500793 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-05 | 286 | keep | 0 | Sep | 2022 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-09-05 19:58 | 2022-09-05 20:00 | 1085 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DEL 1404-06 LLEVA 80% DE LA CARGA DEL 1404-07 SE CERRO POR CONTROL | S22090500793 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-05 | 2170 | keep | 0 | Sep | 2022 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
CANOVANAS | 2022-09-05 19:58 | 2022-09-05 19:59 | 2005 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO PERSONAL REALIZANDO OPERACIONES | R22090500219 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-05 | 2005 | keep | 0 | Sep | 2022 | 0.0013656 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-05 19:59 | 2022-09-05 20:28 | 1000 | 0:29 | P | CONDUCTOR ROTO O ABIERTO | PERSONAL REALIZANDO OPERACIONES | R22090500219 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 29 | 2022-09-05 | 29000 | keep | 0 | Sep | 2022 | 0.019752 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
HUMACAO | 2022-09-05 20:08 | 2022-09-06 18:38 | 15 | 22:30 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO DE 37.5 KVA X 37.5 KVA | C22090501008 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1350 | 2022-09-05 | 20250 | keep | 0 | Sep | 2022 | 0.013792 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-05 20:26 | 2022-09-06 12:49 | 12 | 16:23 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER | S22090500816 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 983 | 2022-09-05 | 11796 | keep | 0 | Sep | 2022 | 0.0080342 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-09-05 20:28 | 2022-09-05 21:34 | 505 | 1:06 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PUENTE ABIERTO Y SE TRANSFIRIO LA CARGA AL 1619-01 GOI SJ-220905-51 | R22090500219 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 66 | 2022-09-05 | 33330 | keep | 0 | Sep | 2022 | 0.022701 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-05 20:29 | 2022-09-05 21:15 | 12 | 0:46 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | C22090501023 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 46 | 2022-09-05 | 552 | keep | 0 | Sep | 2022 | 0.00037596 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-09-05 20:43 | 2022-09-06 18:44 | 50 | 22:01 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | S22090500829 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1321 | 2022-09-05 | 66050 | keep | 0 | Sep | 2022 | 0.044986 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2022-09-05 20:49 | 2022-09-05 22:37 | 3 | 1:48 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y REMPLAZO AISLADOR | R22090500536 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2022-09-05 | 324 | keep | 0 | Sep | 2022 | 0.00022067 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-09-05 20:59 | 2022-09-06 13:08 | 5 | 16:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 320 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22090500531 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 969 | 2022-09-05 | 4845 | keep | 0 | Sep | 2022 | 0.0032999 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2022-09-05 21:00 | 2022-09-06 00:17 | 30 | 3:17 | P | CAUSAS EXTERNAS | 1 X 30 EN C/L CRUCE X TENSOR | R22090500533 | New_Event | Damage From Public | Include | Include | Public | 197 | 2022-09-05 | 5910 | keep | 0 | Sep | 2022 | 0.0040253 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-05 21:00 | 2022-09-05 21:01 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22090500535 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-05 | 7621 | keep | 0 | Sep | 2022 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
FAJARDO | 2022-09-05 21:10 | 2022-09-05 21:52 | 8 | 0:42 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | R22090500541 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 42 | 2022-09-05 | 336 | keep | 0 | Sep | 2022 | 0.00022885 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-09-05 21:46 | 2022-09-06 11:35 | 800 | 13:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y SE REALIZO DESGANCHE | M22090500124 | New_Event | Primary Wire Break | Include | Include | Equipment | 829 | 2022-09-05 | 663200 | keep | 0 | Sep | 2022 | 0.4517 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
PONCE | 2022-09-05 21:56 | 2022-09-05 23:13 | 200 | 1:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22090500324 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2022-09-05 | 15400 | keep | 0 | Sep | 2022 | 0.010489 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2022-09-05 22:06 | 2022-09-06 00:33 | 100 | 2:27 | P | DESGANCHE | 2 X 65 EN C/L | C22090501066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-09-05 | 14700 | keep | 0 | Sep | 2022 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-05 22:32 | 2022-09-06 05:34 | 867 | 7:02 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALAMBRE PRIMARIO PARTIDO Y SE CERRO INTERRUPTOR MANUAL YA QUE NO HAY RTU EN SUBESTACION. | M22090500140 | New_Event | Primary Wire Break | Include | Include | Equipment | 422 | 2022-09-05 | 365874 | keep | 0 | Sep | 2022 | 0.2492 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2022-09-05 22:49 | 2022-09-06 02:36 | 1497 | 3:47 | T | ARBOL SOBRE LINEA | SE REMOVIO ARBOL SOBRE LAS LINEAS. SE CERRO INTERRUPTOR MANUAL EN SUBESTACION YA QUE NO TIENE RTU. | M22090500145 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 227 | 2022-09-05 | 339819 | keep | 0 | Sep | 2022 | 0.23145 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
BAYAMON | 2022-09-05 22:53 | 2022-09-06 18:15 | 48 | 19:22 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA NO FUNDIO | B22090500580 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1162 | 2022-09-05 | 55776 | keep | 0 | Sep | 2022 | 0.037989 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
SAN JUAN | 2022-09-05 23:06 | 2022-09-06 09:32 | 21 | 10:26 | P | DESGANCHE | 1 X 40 EN C/L Y SE REALIZO DESGANCHE | S22090501009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 626 | 2022-09-05 | 13146 | keep | 0 | Sep | 2022 | 0.0089537 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2022-09-06 00:06 | 2022-09-06 00:07 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR | M22090600010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 4641 | keep | 0 | Sep | 2022 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
SAN JUAN | 2022-09-06 00:14 | 2022-09-06 17:45 | 300 | 17:31 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | AVERIA NUEVA SU-11B A SU-12 TERMINACION AVERIA Y AISLADORES AVERIADO SE RECOMIENDA CAMBIO SU-12 Y SE DEJO ABIERTO SU-12 A SU-13 SE CERRO LAZO Y SE DIO SERVICIO A CLIENTE | S22090500529 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1051 | 2022-09-06 | 315300 | keep | 0 | Sep | 2022 | 0.21475 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2022-09-06 00:25 | 2022-09-06 13:26 | 75 | 13:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22090600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 781 | 2022-09-06 | 58575 | keep | 0 | Sep | 2022 | 0.039895 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-09-06 00:44 | 2022-09-06 06:49 | 53 | 6:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | B22090600010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 365 | 2022-09-06 | 19345 | keep | 0 | Sep | 2022 | 0.013176 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2022-09-06 00:56 | 2022-09-06 07:13 | 150 | 6:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2022-09-06 | 56550 | keep | 0 | Sep | 2022 | 0.038516 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-09-06 01:26 | 2022-09-06 13:42 | 125 | 12:16 | P | DESGANCHE | SE REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L | S22090600030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 736 | 2022-09-06 | 92000 | keep | 0 | Sep | 2022 | 0.062661 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2022-09-06 02:04 | 2022-09-06 02:05 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22090600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 3464 | keep | 0 | Sep | 2022 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
AGUADILLA | 2022-09-06 02:10 | 2022-09-07 01:08 | 80 | 22:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | M22090600005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1378 | 2022-09-06 | 110240 | keep | 0 | Sep | 2022 | 0.075084 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-06 02:25 | 2022-09-06 10:07 | 86 | 7:42 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA PROVISIONAL 1 X 80 EN CORTE DE LINEA | S22090600036 | New_Event | Primary Wire Break | Include | Include | Equipment | 462 | 2022-09-06 | 39732 | keep | 0 | Sep | 2022 | 0.027061 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
SAN JUAN | 2022-09-06 02:49 | 2022-09-06 19:53 | 33 | 17:04 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL DE RISER A T-29 1 X 40 EN PROVISIONAL | S22090600039 | New_Event | UG Cable Fault | Include | Include | Equipment | 1024 | 2022-09-06 | 33792 | keep | 0 | Sep | 2022 | 0.023016 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
VEGA BAJA | 2022-09-06 03:46 | 2022-09-06 10:50 | 25 | 7:04 | P | ARBOL SOBRE LINEA | 1 X 65 EN C/L SE RETIRO ARBOL SOBRE LINEA | B22090600031 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 424 | 2022-09-06 | 10600 | keep | 0 | Sep | 2022 | 0.0072196 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-09-06 04:23 | 2022-09-06 09:55 | 4 | 5:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | R22090600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 332 | 2022-09-06 | 1328 | keep | 0 | Sep | 2022 | 0.00090449 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-06 04:34 | 2022-09-06 10:23 | 131 | 5:49 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | S22090600050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 349 | 2022-09-06 | 45719 | keep | 0 | Sep | 2022 | 0.031139 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
PONCE | 2022-09-06 04:51 | 2022-09-06 04:52 | 11 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090600058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 11 | keep | 0 | Sep | 2022 | 7.492e-06 | 7.492e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 11
GUAYAMA | 2022-09-06 05:07 | 2022-09-06 05:08 | 4035 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090600062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 4035 | keep | 0 | Sep | 2022 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
CAGUAS | 2022-09-06 05:09 | 2022-09-06 06:44 | 120 | 1:35 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA | C22090600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2022-09-06 | 11400 | keep | 0 | Sep | 2022 | 0.0077645 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2022-09-06 05:34 | 2022-09-06 10:22 | 200 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M22090500140 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 288 | 2022-09-06 | 57600 | keep | 0 | Sep | 2022 | 0.039231 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-06 05:39 | 2022-09-06 06:49 | 60 | 1:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | B22090600035 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 70 | 2022-09-06 | 4200 | keep | 0 | Sep | 2022 | 0.0028606 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-06 05:49 | 2022-09-06 12:14 | 40 | 6:25 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU17 A T 19 AVERIA NUEVA DE T17 @ T 18 AVERIA VIEJA DE T16 @ T17 | B22090600037 | New_Event | UG Cable Fault | Include | Include | Equipment | 385 | 2022-09-06 | 15400 | keep | 0 | Sep | 2022 | 0.010489 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-06 05:59 | 2022-09-06 07:06 | 30 | 1:07 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA LEVANTAR CONDUCTOR PRIMARIO | S22090600054 | New_Event | Primary Wire Break | Include | Include | Equipment | 67 | 2022-09-06 | 2010 | keep | 0 | Sep | 2022 | 0.001369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-06 06:05 | 2022-09-06 11:34 | 115 | 5:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | S22090600056 | New_Event | Primary Wire Break | Include | Include | Equipment | 329 | 2022-09-06 | 37835 | keep | 0 | Sep | 2022 | 0.025769 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CAGUAS | 2022-09-06 06:13 | 2022-09-06 09:25 | 350 | 3:12 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C22090600069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-09-06 | 67200 | keep | 0 | Sep | 2022 | 0.04577 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
PONCE | 2022-09-06 06:34 | 2022-09-06 12:40 | 60 | 6:06 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO DESGANCHE INTERIOR | P22090600081 | New_Event | Primary Wire Break | Include | Include | Equipment | 366 | 2022-09-06 | 21960 | keep | 0 | Sep | 2022 | 0.014957 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-06 06:39 | 2022-09-06 10:07 | 100 | 3:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090600069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 208 | 2022-09-06 | 20800 | keep | 0 | Sep | 2022 | 0.014167 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-06 06:49 | 2022-09-06 06:51 | 320 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 9503-05 SE CERRO POR SCADA | B22090600046 | Additional_clients | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-06 | 640 | keep | 0 | Sep | 2022 | 0.0004359 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-06 06:51 | 2022-09-06 10:20 | 53 | 3:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | B22090600010 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 209 | 2022-09-06 | 11077 | keep | 0 | Sep | 2022 | 0.0075445 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2022-09-06 06:51 | 2022-09-06 10:59 | 60 | 4:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | B22090600035 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 248 | 2022-09-06 | 14880 | keep | 0 | Sep | 2022 | 0.010135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-06 06:59 | 2022-09-06 11:09 | 100 | 4:10 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 200 EN C/L CONDUCTOR ARRIADO | S22090600075 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 250 | 2022-09-06 | 25000 | keep | 0 | Sep | 2022 | 0.017027 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2022-09-06 07:03 | 2022-09-06 07:18 | 39 | 0:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C22090600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 15 | 2022-09-06 | 585 | keep | 0 | Sep | 2022 | 0.00039844 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2022-09-06 07:03 | 2022-09-06 07:04 | 4607 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22090600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 4607 | keep | 0 | Sep | 2022 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
CANOVANAS | 2022-09-06 07:10 | 2022-09-06 10:22 | 30 | 3:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R22090600036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2022-09-06 | 5760 | keep | 0 | Sep | 2022 | 0.0039231 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-06 07:12 | 2022-09-06 07:13 | 1784 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 90% 1711-04 Y PARTE DE 1717-01 SE CERRO POR SCADA | B22090600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 1784 | keep | 0 | Sep | 2022 | 0.0012151 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2022-09-06 07:12 | 2022-09-06 07:13 | 2000 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 90% 1711-04 Y PARTE DE 1717-01 SE CERRO POR SCADA | B22090600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2000 | keep | 0 | Sep | 2022 | 0.0013622 | 0.0013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 2000
BARRANQUITAS | 2022-09-06 07:12 | 2022-09-06 07:13 | 2937 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2937 | keep | 0 | Sep | 2022 | 0.0020004 | 0.0020004 | Momentary | FALSE | FALSE | Not_TMED_Event | 2937
PONCE | 2022-09-06 07:23 | 2022-09-06 15:45 | 8 | 8:22 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 25KVA A 4160VOLTS AVERIADO | P22090600093 | New_Event | Service Transformer Failure | Include | Include | Equipment | 502 | 2022-09-06 | 4016 | keep | 0 | Sep | 2022 | 0.0027353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2022-09-06 07:25 | 2022-09-06 13:16 | 9 | 5:51 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L Y 1 X 25 EN XMR MAL TIEMPO | S22090600086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 351 | 2022-09-06 | 3159 | keep | 0 | Sep | 2022 | 0.0021516 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-09-06 07:27 | 2022-09-06 13:31 | 9 | 6:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO SECUNDARIA | S22090600089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 364 | 2022-09-06 | 3276 | keep | 0 | Sep | 2022 | 0.0022313 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-09-06 07:29 | 2022-09-06 09:32 | 35 | 2:03 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B22090600052 | New_Event | Animals | Include | Include | Wildlife | 123 | 2022-09-06 | 4305 | keep | 0 | Sep | 2022 | 0.0029321 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-09-06 07:34 | 2022-09-06 11:39 | 80 | 4:05 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA | C22090600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2022-09-06 | 19600 | keep | 0 | Sep | 2022 | 0.013349 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-09-06 07:34 | 2022-09-06 11:35 | 100 | 4:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 80 EN CORTE DE LINEA SE SECCIONALIZO POSTE PARTIDO | A22090600015 | New_Event | Primary Pole Failure | Include | Include | Equipment | 241 | 2022-09-06 | 24100 | keep | 0 | Sep | 2022 | 0.016414 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-09-06 07:42 | 2022-09-06 10:53 | 1 | 3:11 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | R22090600041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-09-06 | 191 | keep | 0 | Sep | 2022 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-09-06 07:52 | 2022-09-06 12:00 | 1 | 4:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R22090600091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 248 | 2022-09-06 | 248 | keep | 0 | Sep | 2022 | 0.00016891 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-06 08:00 | 2022-09-06 20:00 | 3 | 12:00 | P | DESGANCHE | 2 X 15 EN C/L | C22090600126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 720 | 2022-09-06 | 2160 | keep | 0 | Sep | 2022 | 0.0014712 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2022-09-06 08:04 | 2022-09-06 09:49 | 70 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | A22090600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2022-09-06 | 7350 | keep | 0 | Sep | 2022 | 0.0050061 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2022-09-06 08:12 | 2022-09-06 16:43 | 10 | 8:31 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R22090600047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 511 | 2022-09-06 | 5110 | keep | 0 | Sep | 2022 | 0.0034804 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-06 08:25 | 2022-09-06 18:05 | 5 | 9:40 | P | DESGANCHE | 2 X 20 EN MONTURA XMR SE REALIZO DESGANCHE PRIMARIO | B22090600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 580 | 2022-09-06 | 2900 | keep | 0 | Sep | 2022 | 0.0019752 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-09-06 08:27 | 2022-09-06 11:19 | 28 | 2:52 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 40 SUM-20 SU-1CA CONTAMINADO | R22090600050 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 172 | 2022-09-06 | 4816 | keep | 0 | Sep | 2022 | 0.0032802 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2022-09-06 08:28 | 2022-09-06 08:49 | 2 | 0:21 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22090600068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2022-09-06 | 42 | keep | 0 | Sep | 2022 | 2.8606e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-09-06 08:28 | 2022-09-06 10:14 | 1 | 1:46 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA SOBRE TRANSFORMADOR | M22090600112 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 106 | 2022-09-06 | 106 | keep | 0 | Sep | 2022 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-09-06 08:29 | 2022-09-06 17:45 | 1 | 9:16 | P | DESGANCHE | 1 X 80 EN C/L | C22090600137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2022-09-06 | 556 | keep | 0 | Sep | 2022 | 0.00037869 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-09-06 08:29 | 2022-09-06 11:27 | 100 | 2:58 | P | CONDUCTOR ROTO O ABIERTO | CG-220906-01A SE LEVANTO CONDUCTOR DEL SUELO | C22090500698 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 178 | 2022-09-06 | 17800 | keep | 0 | Sep | 2022 | 0.012123 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-06 08:32 | 2022-09-06 14:54 | 10 | 6:22 | P | ANIMAL | 1 X 25 EN TRANSFORMADOR SE RETIRO LAGARTO | S22090600120 | New_Event | Animals | Include | Include | Wildlife | 382 | 2022-09-06 | 3820 | keep | 0 | Sep | 2022 | 0.0026018 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-06 08:37 | 2022-09-06 12:31 | 8 | 3:54 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR PODA SECUNDARIA Y REPARAR SECUNDARIA | S22090600126 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 234 | 2022-09-06 | 1872 | keep | 0 | Sep | 2022 | 0.001275 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-09-06 08:39 | 2022-09-06 08:40 | 4369 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C22090600163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-06 | 4369 | keep | 0 | Sep | 2022 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2022-09-06 08:39 | 2022-09-06 08:40 | 676 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C22090600163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-06 | 676 | keep | 0 | Sep | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2022-09-06 08:39 | 2022-09-06 08:40 | 1606 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C22090600163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-06 | 1606 | keep | 0 | Sep | 2022 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2022-09-06 08:39 | 2022-09-06 08:40 | 725 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 600 | C22090600163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-06 | 725 | keep | 0 | Sep | 2022 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
BAYAMON | 2022-09-06 08:40 | 2022-09-06 11:37 | 108 | 2:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIA | B22090600069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 177 | 2022-09-06 | 19116 | keep | 0 | Sep | 2022 | 0.01302 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
HUMACAO | 2022-09-06 08:42 | 2022-09-06 16:00 | 3 | 7:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN RISER REMPLAZO PORTAFUSIBLES | C22090600142 | New_Event | Cutout Failure | Include | Include | Equipment | 438 | 2022-09-06 | 1314 | keep | 0 | Sep | 2022 | 0.00089496 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-09-06 08:49 | 2022-09-06 08:51 | 186 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 90% 1711-04 Y PARTE DE 1717-01 SE CERRO POR SCADA | B22090600007 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-06 | 372 | keep | 0 | Sep | 2022 | 0.00025337 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-06 08:49 | 2022-09-06 16:35 | 20 | 7:46 | P | MAL TIEMPO/RAYOS | 1 X 25 EN C/L RAYO | C22090600149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 466 | 2022-09-06 | 9320 | keep | 0 | Sep | 2022 | 0.0063478 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2022-09-06 08:50 | 2022-09-07 11:11 | 5 | 26:21 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 25KVA X 25KVA | R22090600053 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1581 | 2022-09-06 | 7905 | keep | 0 | Sep | 2022 | 0.0053841 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-09-06 08:51 | 2022-09-06 10:39 | 2 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B22090600068 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 108 | 2022-09-06 | 216 | keep | 0 | Sep | 2022 | 0.00014712 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2022-09-06 09:04 | 2022-09-06 10:13 | 60 | 1:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C22090600156 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 69 | 2022-09-06 | 4140 | keep | 0 | Sep | 2022 | 0.0028197 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2022-09-06 09:04 | 2022-09-06 09:38 | 1 | 0:34 | P | DESGANCHE | 1 X 40 EN MONTURA TRIFASICA POR DESGANCHE | P22090600119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2022-09-06 | 34 | keep | 0 | Sep | 2022 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-06 09:07 | 2022-09-06 09:09 | 143 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 80% DEL 1404-07 | S22090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-06 | 286 | keep | 0 | Sep | 2022 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-09-06 09:07 | 2022-09-06 09:09 | 1085 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 80% DE SU CARGA POR EL 1404-06 | S22090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-06 | 2170 | keep | 0 | Sep | 2022 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
BAYAMON | 2022-09-06 09:07 | 2022-09-06 10:40 | 50 | 1:33 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B22090600081 | New_Event | Animals | Include | Include | Wildlife | 93 | 2022-09-06 | 4650 | keep | 0 | Sep | 2022 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-09-06 09:09 | 2022-09-06 11:00 | 40 | 1:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A22090600027 | New_Event | Cutout Failure | Include | Include | Equipment | 111 | 2022-09-06 | 4440 | keep | 0 | Sep | 2022 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-09-06 09:13 | 2022-09-06 17:49 | 15 | 8:36 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE PRIMARIO | S22090600153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2022-09-06 | 7740 | keep | 0 | Sep | 2022 | 0.0052717 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-09-06 09:13 | 2022-09-06 10:45 | 1 | 1:32 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C22090600164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2022-09-06 | 92 | keep | 0 | Sep | 2022 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-06 09:14 | 2022-09-06 14:20 | 40 | 5:06 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C22090600165 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 306 | 2022-09-06 | 12240 | keep | 0 | Sep | 2022 | 0.0083366 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-06 09:16 | 2022-09-06 15:17 | 30 | 6:01 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L RAYOS | C22090600169 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 361 | 2022-09-06 | 10830 | keep | 0 | Sep | 2022 | 0.0073763 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-06 09:17 | 2022-09-06 18:23 | 100 | 9:06 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN CORTE DE LINEA AVERIA NUEVA RISER A T-9 AVERIA VIEJA T-9 A T-10 SE DEJO FUERA T-9 | S22090600154 | New_Event | UG Cable Fault | Include | Include | Equipment | 546 | 2022-09-06 | 54600 | keep | 0 | Sep | 2022 | 0.037188 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-09-06 09:20 | 2022-09-06 12:02 | 100 | 2:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | C22090600171 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 162 | 2022-09-06 | 16200 | keep | 0 | Sep | 2022 | 0.011034 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-06 09:25 | 2022-09-06 12:22 | 1 | 2:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER HACIA SUBESTACION PRIVADA | B22090600084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2022-09-06 | 177 | keep | 0 | Sep | 2022 | 0.00012055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-09-06 09:31 | 2022-09-06 14:30 | 1 | 4:59 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA, SE RETIRO BAMBUA, SE RETEZO LINEA PRIMARIA | P22090600121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-09-06 | 299 | keep | 0 | Sep | 2022 | 0.00020365 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-09-06 09:43 | 2022-09-06 13:39 | 5 | 3:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES SULFATADOS EN LINEA SECUNDARIA | C22090600188 | New_Event | Secondary Wire Break | Include | Include | Equipment | 236 | 2022-09-06 | 1180 | keep | 0 | Sep | 2022 | 0.00080369 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2022-09-06 09:44 | 2022-09-06 18:20 | 5 | 8:36 | P | SECUNDARIA/OTROS | SE REEMPLAZO PEDESTAL Y SECUNDARIA | R22090600071 | New_Event |  |  |  |  | 516 | 2022-09-06 | 2580 | keep | 0 | Sep | 2022 | 0.0017572 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-09-06 09:57 | 2022-09-06 13:22 | 4 | 3:25 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE CRITICO Y SE REPARO BAJANTE SAFADO | C22090600193 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 205 | 2022-09-06 | 820 | keep | 0 | Sep | 2022 | 0.0005585 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-09-06 10:00 | 2022-09-06 13:30 | 15 | 3:30 | P | DESGANCHE | SE ABRIO CORTE DE LINEA Y SE RETIRO ARBOL SOBRE LAS LINEAS | A22090600047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2022-09-06 | 3150 | keep | 0 | Sep | 2022 | 0.0021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-09-06 10:01 | 2022-09-06 11:50 | 1 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A22090600045 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2022-09-06 | 109 | keep | 0 | Sep | 2022 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-09-06 10:04 | 2022-09-06 16:30 | 1 | 6:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR , SE REMPLAZARON 3 PARARRAYOS Y 3 X 20 EN SU#2 | P22090600131 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 386 | 2022-09-06 | 386 | keep | 0 | Sep | 2022 | 0.0002629 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-06 10:05 | 2022-09-06 13:49 | 134 | 3:44 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU | S22090600173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2022-09-06 | 30016 | keep | 0 | Sep | 2022 | 0.020444 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
SAN JUAN | 2022-09-06 10:07 | 2022-09-06 14:55 | 10 | 4:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S22090600176 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 288 | 2022-09-06 | 2880 | keep | 0 | Sep | 2022 | 0.0019616 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-06 10:08 | 2022-09-06 19:49 | 6 | 9:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 37.5 KVA X 37.5 KVA | C22090600200 | New_Event | Service Transformer Failure | Include | Include | Equipment | 581 | 2022-09-06 | 3486 | keep | 0 | Sep | 2022 | 0.0023743 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-09-06 10:09 | 2022-09-06 13:20 | 1 | 3:11 | P | NO SE REPORTO CAUSA | 2 X 50 EN SUB | S22090600178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2022-09-06 | 191 | keep | 0 | Sep | 2022 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-09-06 10:10 | 2022-09-06 15:57 | 40 | 5:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE | A22090600048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 347 | 2022-09-06 | 13880 | keep | 0 | Sep | 2022 | 0.0094536 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-09-06 10:16 | 2022-09-06 16:15 | 4 | 5:59 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA RAYOS | S22090600180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 359 | 2022-09-06 | 1436 | keep | 0 | Sep | 2022 | 0.00097805 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-09-06 10:18 | 2022-09-06 12:00 | 40 | 1:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO PIN Y 1 X 50 EN CORTE DE LINEA | R22090600056 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 102 | 2022-09-06 | 4080 | keep | 0 | Sep | 2022 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-09-06 10:18 | 2022-09-06 13:25 | 20 | 3:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA DE 100 AMP | M22090600155 | New_Event | Cutout Failure | Include | Include | Equipment | 187 | 2022-09-06 | 3740 | keep | 0 | Sep | 2022 | 0.0025473 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-06 10:21 | 2022-09-06 13:38 | 6 | 3:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S22090600183 | New_Event | Secondary Wire Break | Include | Include | Equipment | 197 | 2022-09-06 | 1182 | keep | 0 | Sep | 2022 | 0.00080505 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-09-06 10:50 | 2022-09-06 12:35 | 2064 | 1:45 | T | DESGANCHE | SE SECCIONALIZO AREA Y SE CERRO POR SCADA | S22090600193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2022-09-06 | 216720 | keep | 0 | Sep | 2022 | 0.14761 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
BAYAMON | 2022-09-06 10:57 | 2022-09-06 12:23 | 1 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN MONTURA XMR LLUVIA FUERTE | B22090600104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2022-09-06 | 86 | keep | 0 | Sep | 2022 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-09-06 11:00 | 2022-09-06 11:40 | 10 | 0:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22090600172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-09-06 | 400 | keep | 0 | Sep | 2022 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-06 11:09 | 2022-09-06 13:20 | 4 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER 2 SUM20 DE 40AMP EN SU-6 | R22090600082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2022-09-06 | 524 | keep | 0 | Sep | 2022 | 0.00035689 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-09-06 11:28 | 2022-09-06 11:30 | 2842 | 0:02 | T | ARBOL SOBRE LINEA | DISPARO SE CERRO POR CONTROL | C22090600247 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 2 | 2022-09-06 | 5684 | keep | 0 | Sep | 2022 | 0.0038713 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2022-09-06 11:30 | 2022-09-06 12:38 | 2842 | 1:08 | T | ARBOL SOBRE LINEA | DISPARO | C22090600247 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 68 | 2022-09-06 | 193256 | keep | 0 | Sep | 2022 | 0.13163 | 0.0019357 | Sustained | FALSE | FALSE | Not_TMED_Event | 2842
BARRANQUITAS | 2022-09-06 11:31 | 2022-09-06 11:32 | 1516 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 1516 | keep | 0 | Sep | 2022 | 0.0010325 | 0.0010325 | Momentary | FALSE | FALSE | Not_TMED_Event | 1516
ARECIBO | 2022-09-06 11:31 | 2022-09-06 11:32 | 2201 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22090600069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2201 | keep | 0 | Sep | 2022 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2022-09-06 11:32 | 2022-09-06 13:03 | 20 | 1:31 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A22090600016 | New_Event | Animals | Include | Include | Wildlife | 91 | 2022-09-06 | 1820 | keep | 0 | Sep | 2022 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-09-06 11:35 | 2022-09-06 18:30 | 100 | 6:55 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES Y CERRO N/O CON EL 8302-05 PARA SECCIONALIZAR POSTE PARTIDO Y ENERGIZAR CLIENTES A TRAVES DE ESE ALIMENTADOR | A22090600015 | New_Event | Primary Pole Failure | Include | Include | Equipment | 415 | 2022-09-06 | 41500 | keep | 0 | Sep | 2022 | 0.028265 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-06 11:42 | 2022-09-06 11:43 | 1516 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600251 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 1516 | keep | 0 | Sep | 2022 | 0.0010325 | 0.0010325 | Momentary | FALSE | FALSE | Not_TMED_Event | 1516
BAYAMON | 2022-09-06 11:43 | 2022-09-06 15:25 | 15 | 3:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B22090600107 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2022-09-06 | 3330 | keep | 0 | Sep | 2022 | 0.002268 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-06 11:50 | 2022-09-06 14:13 | 4 | 2:23 | P | ERROR HUMANO | SE REPARO SECUNDARIA Y SE CONECTO TOMA NUEVA HACIA EL CLIENTE COMPANIA WTS PARTIO SECUNDARIA AL DEJAR CAER RAMAS SOBRE ELLA | B22090600078 | New_Event | Human Error | Include | Include | Other | 143 | 2022-09-06 | 572 | keep | 0 | Sep | 2022 | 0.00038959 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-09-06 11:55 | 2022-09-06 14:00 | 80 | 2:05 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYOS | C22090600261 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 125 | 2022-09-06 | 10000 | keep | 0 | Sep | 2022 | 0.006811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-09-06 12:00 | 2022-09-06 14:35 | 1 | 2:35 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R22090600094 | New_Event | Animals | Include | Include | Wildlife | 155 | 2022-09-06 | 155 | keep | 0 | Sep | 2022 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-09-06 12:03 | 2022-09-06 12:04 | 1712 | 0:01 | T | ARBOL SOBRE LINEA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P22090600155 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-09-06 | 1712 | keep | 0 | Sep | 2022 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
PONCE | 2022-09-06 12:07 | 2022-09-06 12:08 | 1712 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | P22090600156 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2022-09-06 | 1712 | keep | 0 | Sep | 2022 | 0.001166 | 0.001166 | Momentary | FALSE | FALSE | Not_TMED_Event | 1712
CANOVANAS | 2022-09-06 12:08 | 2022-09-06 16:03 | 12 | 3:55 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | R22090600096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-09-06 | 2820 | keep | 0 | Sep | 2022 | 0.0019207 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-09-06 12:14 | 2022-09-06 13:31 | 1712 | 1:17 | T | ARBOL SOBRE LINEA | SE SACO ARBOL SOBRE LINEAS Y SE HIZO DESGANCHE EN VARIOS PUNTOS CRITICOS | P22090600159 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 77 | 2022-09-06 | 131824 | keep | 0 | Sep | 2022 | 0.089785 | 0.001166 | Sustained | FALSE | FALSE | Not_TMED_Event | 1712
BAYAMON | 2022-09-06 12:14 | 2022-09-07 19:30 | 20 | 31:16 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO 90 PIES DE CABLE PRIMARIO SOTERRADO | B22090600037 | New_Event | UG Cable Fault | Include | Include | Equipment | 1876 | 2022-09-06 | 37520 | keep | 0 | Sep | 2022 | 0.025555 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-06 12:25 | 2022-09-06 18:07 | 1 | 5:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE | C22090600281 | New_Event | Cutout Failure | Include | Include | Equipment | 342 | 2022-09-06 | 342 | keep | 0 | Sep | 2022 | 0.00023293 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-09-06 12:28 | 2022-09-06 22:03 | 40 | 9:35 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE REMOVIO ARBOL SOBRE LA LINEA | A22090600114 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 575 | 2022-09-06 | 23000 | keep | 0 | Sep | 2022 | 0.015665 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-06 12:30 | 2022-09-06 15:26 | 35 | 2:56 | P | DESGANCHE | 1 X 50 EN C/L Y 1 X 15 EN XMR | C22090600287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-09-06 | 6160 | keep | 0 | Sep | 2022 | 0.0041955 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2022-09-06 12:31 | 2022-09-06 15:55 | 70 | 3:24 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M22090600187 | New_Event | Primary Wire Break | Include | Include | Equipment | 204 | 2022-09-06 | 14280 | keep | 0 | Sep | 2022 | 0.009726 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-09-06 12:35 | 2022-09-06 13:39 | 722 | 1:04 | P | DESGANCHE | SE REALIZO DESGANCHE A VARETA | S22090600193 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 64 | 2022-09-06 | 46208 | keep | 0 | Sep | 2022 | 0.031472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-06 12:35 | 2022-09-06 16:24 | 2 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR CLIENTES ESTABAN FUERA DESDE AYER 13:00 SE HIZO EVENTO HOY YA QUE EL EVENTO DE AYER LO CERRARON. | S22090600461 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2022-09-06 | 458 | keep | 0 | Sep | 2022 | 0.00031194 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-06 12:35 | 2022-09-06 14:50 | 60 | 2:15 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO MH #23 Y SE REPARO AISLADORES ROTOS EN SWITCHING UNIT #1 | A22090600014 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 135 | 2022-09-06 | 8100 | keep | 0 | Sep | 2022 | 0.0055169 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-06 12:37 | 2022-09-06 12:39 | 908 | 0:02 | T | DESGANCHE | DISPARO INTERRUPTOR SE CERRO POR SCADA | B22090600125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-09-06 | 1816 | keep | 0 | Sep | 2022 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
CAGUAS | 2022-09-06 12:38 | 2022-09-06 12:55 | 568 | 0:17 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEAS | C22090600247 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 17 | 2022-09-06 | 9656 | keep | 0 | Sep | 2022 | 0.0065767 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-06 12:39 | 2022-09-06 13:50 | 6 | 1:11 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | B22090600126 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 71 | 2022-09-06 | 426 | keep | 0 | Sep | 2022 | 0.00029015 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-09-06 12:40 | 2022-09-06 16:48 | 1 | 4:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | C22090600294 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2022-09-06 | 248 | keep | 0 | Sep | 2022 | 0.00016891 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-06 12:43 | 2022-09-06 12:44 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S22090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2203 | keep | 0 | Sep | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2022-09-06 12:43 | 2022-09-06 14:13 | 10 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO SECUNDARIA Y BAJANTE DE XMR | B22090600127 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2022-09-06 | 900 | keep | 0 | Sep | 2022 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-06 12:54 | 2022-09-06 12:55 | 16 | 0:01 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | S22090600052 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-06 | 16 | keep | 0 | Sep | 2022 | 1.0898e-05 | 1.0898e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2022-09-06 12:56 | 2022-09-06 17:55 | 50 | 4:59 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090600087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 299 | 2022-09-06 | 14950 | keep | 0 | Sep | 2022 | 0.010182 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-06 12:59 | 2022-09-06 14:15 | 357 | 1:16 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | S22090600111 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2022-09-06 | 27132 | keep | 0 | Sep | 2022 | 0.018479 | 0.00024315 | Sustained | FALSE | FALSE | Not_TMED_Event | 357
CAGUAS | 2022-09-06 12:59 | 2022-09-06 18:13 | 1307 | 5:14 | T | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZO VARIOS AISLADORES QUEMADOS | C22090600311 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 314 | 2022-09-06 | 410398 | keep | 0 | Sep | 2022 | 0.27952 | 0.00089019 | Sustained | FALSE | FALSE | Not_TMED_Event | 1307
BAYAMON | 2022-09-06 13:17 | 2022-09-06 16:08 | 1 | 2:51 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | B22090600134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-09-06 | 171 | keep | 0 | Sep | 2022 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2022-09-06 13:20 | 2022-09-06 16:00 | 3 | 2:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE 15 KVA X 25 KVA | M22090600091 | New_Event | Service Transformer Failure | Include | Include | Equipment | 160 | 2022-09-06 | 480 | keep | 0 | Sep | 2022 | 0.00032693 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-09-06 13:21 | 2022-09-06 16:21 | 55 | 3:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO 2 CAJAS AVERIADAS | C22090600311 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2022-09-06 | 9900 | keep | 0 | Sep | 2022 | 0.0067428 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2022-09-06 13:23 | 2022-09-06 15:39 | 1 | 2:16 | P | ANIMAL | 1 X 15 EN BANCO XMRS CRUCE X REPTIL | C22090600312 | New_Event | Animals | Include | Include | Wildlife | 136 | 2022-09-06 | 136 | keep | 0 | Sep | 2022 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-06 13:31 | 2022-09-06 15:15 | 15 | 1:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA | S22090600310 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 104 | 2022-09-06 | 1560 | keep | 0 | Sep | 2022 | 0.0010625 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2022-09-06 13:38 | 2022-09-06 17:28 | 72 | 3:50 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L RAYOS | C22090600317 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 230 | 2022-09-06 | 16560 | keep | 0 | Sep | 2022 | 0.011279 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
HUMACAO | 2022-09-06 13:51 | 2022-09-06 15:32 | 65 | 1:41 | P | DESGANCHE | 1 X 50 EN C/L | C22090600327 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-09-06 | 6565 | keep | 0 | Sep | 2022 | 0.0044714 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2022-09-06 13:53 | 2022-09-06 16:35 | 10 | 2:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO HERRAJE DE CAJA | C22090600328 | New_Event | Cutout Failure | Include | Include | Equipment | 162 | 2022-09-06 | 1620 | keep | 0 | Sep | 2022 | 0.0011034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-06 13:56 | 2022-09-06 14:24 | 1106 | 0:28 | P | DESGANCHE | DISPARO 60% POR 1529-15 PERSONAL ATENDIENDO EVENTO CERCA CAYO ARBOL SOBRE LINEA SE RETIRO CON VARETA Y SE CERRO INTERRUPTOR | S22090600353 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-09-06 | 30968 | keep | 0 | Sep | 2022 | 0.021092 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-09-06 13:56 | 2022-09-06 14:24 | 1802 | 0:28 | T | DESGANCHE | DISPARO LLEVA 60% DEL 1346-02 PERSONAL ATENDIENDO EVENTO CERCA RAMA SOBRE LINEA SE RETIRO CON VARETA Y SE CERRO INTERRUPTOR | S22090600353 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-09-06 | 50456 | keep | 0 | Sep | 2022 | 0.034365 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
ARECIBO | 2022-09-06 13:59 | 2022-09-06 15:15 | 15 | 1:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A22090600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2022-09-06 | 1140 | keep | 0 | Sep | 2022 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-06 14:00 | 2022-09-06 17:32 | 30 | 3:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 150 EN SU-2 MAL TIEMPO LLUVIA | S22090600403 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 212 | 2022-09-06 | 6360 | keep | 0 | Sep | 2022 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-06 14:00 | 2022-09-06 15:38 | 1 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | M22090600227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2022-09-06 | 98 | keep | 0 | Sep | 2022 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-06 14:03 | 2022-09-06 14:04 | 742 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S22090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 742 | keep | 0 | Sep | 2022 | 0.00050537 | 0.00050537 | Momentary | FALSE | FALSE | Not_TMED_Event | 742
FAJARDO | 2022-09-06 14:08 | 2022-09-06 17:40 | 12 | 3:32 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR DE 50 KVA X 50 KVA | R22090600109 | New_Event | Service Transformer Failure | Include | Include | Equipment | 212 | 2022-09-06 | 2544 | keep | 0 | Sep | 2022 | 0.0017327 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-09-06 14:09 | 2022-09-06 16:50 | 1 | 2:41 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN MONTURA TRIFASICA AAA | P22090600213 | New_Event | Primary Wire Break | Include | Include | Equipment | 161 | 2022-09-06 | 161 | keep | 0 | Sep | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-09-06 14:10 | 2022-09-06 14:55 | 15 | 0:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA X 37.5 KVA | A22090600089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2022-09-06 | 675 | keep | 0 | Sep | 2022 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-06 14:11 | 2022-09-06 17:00 | 50 | 2:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE REMPLAZO CAJA PRIMARIA | S22090600347 | New_Event | Cutout Failure | Include | Include | Equipment | 169 | 2022-09-06 | 8450 | keep | 0 | Sep | 2022 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-09-06 14:12 | 2022-09-06 17:50 | 80 | 3:38 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22090600097 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 218 | 2022-09-06 | 17440 | keep | 0 | Sep | 2022 | 0.011878 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-06 14:13 | 2022-09-06 16:23 | 1514 | 2:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-09-06 | 196820 | keep | 0 | Sep | 2022 | 0.13405 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-09-06 14:13 | 2022-09-06 16:23 | 1105 | 2:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-09-06 | 143650 | keep | 0 | Sep | 2022 | 0.097839 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-09-06 14:14 | 2022-09-06 16:25 | 959 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-09-06 | 125629 | keep | 0 | Sep | 2022 | 0.085565 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-09-06 14:14 | 2022-09-06 16:25 | 1382 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-09-06 | 181042 | keep | 0 | Sep | 2022 | 0.12331 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-09-06 14:14 | 2022-09-06 16:25 | 663 | 2:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 131 | 2022-09-06 | 86853 | keep | 0 | Sep | 2022 | 0.059155 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BARRANQUITAS | 2022-09-06 14:14 | 2022-09-06 14:15 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600333 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2203 | keep | 0 | Sep | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BAYAMON | 2022-09-06 14:14 | 2022-09-06 16:24 | 4176 | 2:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-09-06 | 542880 | keep | 0 | Sep | 2022 | 0.36975 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-09-06 14:14 | 2022-09-06 16:24 | 252 | 2:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-09-06 | 32760 | keep | 0 | Sep | 2022 | 0.022313 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2022-09-06 14:14 | 2022-09-06 16:24 | 2147 | 2:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600156 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-09-06 | 279110 | keep | 0 | Sep | 2022 | 0.1901 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-09-06 14:14 | 2022-09-06 16:24 | 2858 | 2:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B22090600158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 130 | 2022-09-06 | 371540 | keep | 0 | Sep | 2022 | 0.25305 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
CAGUAS | 2022-09-06 14:23 | 2022-09-06 14:24 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600339 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 1709 | keep | 0 | Sep | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-09-06 14:25 | 2022-09-06 14:26 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600341 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2302 | keep | 0 | Sep | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
BARRANQUITAS | 2022-09-06 14:25 | 2022-09-06 16:43 | 1843 | 2:18 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | C22090600341 | New_Event | Primary Wire Break | Include | Include | Equipment | 138 | 2022-09-06 | 254334 | keep | 0 | Sep | 2022 | 0.17323 | 0.0012553 | Sustained | FALSE | FALSE | Not_TMED_Event | 1843
UTUADO | 2022-09-06 14:26 | 2022-09-06 16:50 | 50 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090600100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2022-09-06 | 7200 | keep | 0 | Sep | 2022 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-06 14:27 | 2022-09-06 14:28 | 3432 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 80% DE SU CARGA Y LLEVA 10% DE 1204-03 | S22090600362 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 3432 | keep | 0 | Sep | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-09-06 14:27 | 2022-09-06 14:28 | 138 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 10% POR 1204-02 | S22090600362 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 138 | keep | 0 | Sep | 2022 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
CAGUAS | 2022-09-06 14:27 | 2022-09-06 14:28 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600343 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2302 | keep | 0 | Sep | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2022-09-06 14:30 | 2022-09-06 14:31 | 718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600346 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 718 | keep | 0 | Sep | 2022 | 0.00048903 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
AGUADILLA | 2022-09-06 14:30 | 2022-09-06 16:42 | 709 | 2:12 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO POSTE PRIMARIO PARTIDO SE CERRO INTERRUPTOR TIENE CONTINUACION | M22090600206 | New_Event | Primary Pole Failure | Include | Include | Equipment | 132 | 2022-09-06 | 93588 | keep | 0 | Sep | 2022 | 0.063742 | 0.0004829 | Sustained | FALSE | FALSE | Not_TMED_Event | 709
CAGUAS | 2022-09-06 14:32 | 2022-09-06 16:50 | 65 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | C22090600345 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2022-09-06 | 8970 | keep | 0 | Sep | 2022 | 0.0061094 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CAGUAS | 2022-09-06 14:35 | 2022-09-06 14:36 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600352 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 1709 | keep | 0 | Sep | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2022-09-06 14:38 | 2022-09-06 16:54 | 125 | 2:16 | P | MAL TIEMPO/RAYOS | 2 X 100 EN C/L RAYOS | C22090600353 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 136 | 2022-09-06 | 17000 | keep | 0 | Sep | 2022 | 0.011579 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2022-09-06 14:38 | 2022-09-06 14:39 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600343 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2302 | keep | 0 | Sep | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
MAYAGÃœEZ | 2022-09-06 14:43 | 2022-09-06 19:00 | 1 | 4:17 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22090600210 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 257 | 2022-09-06 | 257 | keep | 0 | Sep | 2022 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-06 14:46 | 2022-09-06 18:45 | 288 | 3:59 | P | DESGANCHE | 3 X 200 EN C/L DESGANCHE | S22090600374 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2022-09-06 | 68832 | keep | 0 | Sep | 2022 | 0.046881 | 0.00019616 | Sustained | FALSE | FALSE | Not_TMED_Event | 288
CAGUAS | 2022-09-06 14:46 | 2022-09-06 14:47 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090600363 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 1702 | keep | 0 | Sep | 2022 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2022-09-06 15:01 | 2022-09-06 18:37 | 65 | 3:36 | P | DESGANCHE | 1 X 80 EN C/L | C22090600379 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2022-09-06 | 14040 | keep | 0 | Sep | 2022 | 0.0095626 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2022-09-06 15:02 | 2022-09-06 15:03 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A22090600108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 3431 | keep | 0 | Sep | 2022 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
PONCE | 2022-09-06 15:04 | 2022-09-06 17:45 | 1 | 2:41 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO LINEA PRIMARIA CRUZADA 1 X 65 EN CORTE DE LINEA | P22090600234 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 161 | 2022-09-06 | 161 | keep | 0 | Sep | 2022 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-06 15:17 | 2022-09-06 18:40 | 45 | 3:23 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600112 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 203 | 2022-09-06 | 9135 | keep | 0 | Sep | 2022 | 0.0062218 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2022-09-06 15:20 | 2022-09-06 20:15 | 40 | 4:55 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090600113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2022-09-06 | 11800 | keep | 0 | Sep | 2022 | 0.0080369 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-06 15:26 | 2022-09-06 18:13 | 93 | 2:47 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 50 EN C/L SE ELIMINARON 5 PARARRAYOS DEFECTUOSOS | B22090600227 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 167 | 2022-09-06 | 15531 | keep | 0 | Sep | 2022 | 0.010578 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
CAGUAS | 2022-09-06 15:27 | 2022-09-06 20:23 | 30 | 4:56 | P | DESGANCHE | 1 X 50 EN C/L | C22090600406 | New_Event | Vegetation Contact | Include | Include | Vegetation | 296 | 2022-09-06 | 8880 | keep | 0 | Sep | 2022 | 0.0060481 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2022-09-06 15:33 | 2022-09-06 19:05 | 1 | 3:32 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P22090600241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2022-09-06 | 212 | keep | 0 | Sep | 2022 | 0.00014439 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-06 15:34 | 2022-09-06 16:56 | 157 | 1:22 | P | DESGANCHE | 2 X 100 EN C/L RAMA CRUZO LINEAS | B22090600240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-09-06 | 12874 | keep | 0 | Sep | 2022 | 0.0087684 | 0.00010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 157
HUMACAO | 2022-09-06 15:34 | 2022-09-06 18:39 | 15 | 3:05 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR RAYOS | C22090600415 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 185 | 2022-09-06 | 2775 | keep | 0 | Sep | 2022 | 0.00189 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-09-06 15:37 | 2022-09-06 22:00 | 10 | 6:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO AVERIADO | M22090600185 | New_Event | Secondary Wire Break | Include | Include | Equipment | 383 | 2022-09-06 | 3830 | keep | 0 | Sep | 2022 | 0.0026086 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-06 15:39 | 2022-09-06 16:55 | 1613 | 1:16 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO 310 CLIENTES FUERA | R22090600136 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2022-09-06 | 122588 | keep | 0 | Sep | 2022 | 0.083494 | 0.0010986 | Sustained | FALSE | FALSE | Not_TMED_Event | 1613
CAGUAS | 2022-09-06 15:39 | 2022-09-06 19:23 | 2 | 3:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR FUERTES LLUVIAS | C22090600422 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 224 | 2022-09-06 | 448 | keep | 0 | Sep | 2022 | 0.00030513 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-09-06 15:46 | 2022-09-06 18:43 | 169 | 2:57 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B22090600256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2022-09-06 | 29913 | keep | 0 | Sep | 2022 | 0.020374 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
VEGA BAJA | 2022-09-06 15:49 | 2022-09-06 19:20 | 20 | 3:31 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600116 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 211 | 2022-09-06 | 4220 | keep | 0 | Sep | 2022 | 0.0028742 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-06 15:52 | 2022-09-06 16:55 | 1368 | 1:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE VERIFICO EN SUBESTACION BK.R FUERA (RTU DOWN) SE CERRO LOCALMENTE MAL TIEMPO LLUVIA | S22090600438 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 63 | 2022-09-06 | 86184 | keep | 0 | Sep | 2022 | 0.0587 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
CANOVANAS | 2022-09-06 15:54 | 2022-09-07 11:55 | 80 | 20:01 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 50 EN C/L | R22090600138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1201 | 2022-09-06 | 96080 | keep | 0 | Sep | 2022 | 0.06544 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-06 15:55 | 2022-09-06 18:00 | 120 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S22090600441 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2022-09-06 | 15000 | keep | 0 | Sep | 2022 | 0.010216 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
UTUADO | 2022-09-06 16:00 | 2022-09-06 19:05 | 50 | 3:05 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600118 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 185 | 2022-09-06 | 9250 | keep | 0 | Sep | 2022 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-09-06 16:04 | 2022-09-06 19:05 | 15 | 3:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090600120 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-09-06 | 2715 | keep | 0 | Sep | 2022 | 0.0018492 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-06 16:05 | 2022-09-06 18:53 | 15 | 2:48 | P | DESGANCHE | 1 X 80 Y 1 X 50 EN CORTES DE LINEA DESGANCHE | R22090600145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-09-06 | 2520 | keep | 0 | Sep | 2022 | 0.0017164 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-06 16:10 | 2022-09-06 21:56 | 10 | 5:46 | P | SECUNDARIA/OTROS | SE REEMPLAZO DOS PEDESTALES Y POSTE SECUNDARIO CON AEREO PROVISIONAL SECUNDARIO | R22090600149 | New_Event |  |  |  |  | 346 | 2022-09-06 | 3460 | keep | 0 | Sep | 2022 | 0.0023566 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-06 16:12 | 2022-09-06 16:13 | 2533 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR PARTE POR EL 1801-02 | B22090600293 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 2533 | keep | 0 | Sep | 2022 | 0.0017252 | 0.0017252 | Momentary | FALSE | FALSE | Not_TMED_Event | 2533
VEGA BAJA | 2022-09-06 16:15 | 2022-09-06 21:28 | 80 | 5:13 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600125 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 313 | 2022-09-06 | 25040 | keep | 0 | Sep | 2022 | 0.017055 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-09-06 16:16 | 2022-09-06 16:17 | 4132 | 0:01 | T | ANIMAL | RECIERRE | P22090600248 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-06 | 4132 | keep | 0 | Sep | 2022 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
ARECIBO | 2022-09-06 16:16 | 2022-09-07 14:43 | 1 | 22:27 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600126 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1347 | 2022-09-06 | 1347 | keep | 0 | Sep | 2022 | 0.00091744 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2022-09-06 16:17 | 2022-09-06 18:15 | 25 | 1:58 | P | ANIMAL | 1 X 40 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P22090600254 | 1st_after_momentary | Animals | Include | Include | Wildlife | 118 | 2022-09-06 | 2950 | keep | 0 | Sep | 2022 | 0.0020092 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2022-09-06 16:18 | 2022-09-06 21:54 | 40 | 5:36 | P | DESGANCHE | 1 X 65 EN C/L | C22090600454 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2022-09-06 | 13440 | keep | 0 | Sep | 2022 | 0.0091539 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2022-09-06 16:19 | 2022-09-06 18:13 | 2064 | 1:54 | T | DESGANCHE | SE RETIRO RAMAS SOBRE LINEAS PRIMARIAS SE CERRO INTERRUPTOR | M22090600249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2022-09-06 | 235296 | keep | 0 | Sep | 2022 | 0.16026 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
VEGA BAJA | 2022-09-06 16:19 | 2022-09-06 16:20 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22090600280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 4702 | keep | 0 | Sep | 2022 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
UTUADO | 2022-09-06 16:30 | 2022-09-06 18:25 | 30 | 1:55 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600135 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 115 | 2022-09-06 | 3450 | keep | 0 | Sep | 2022 | 0.0023498 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-06 16:33 | 2022-09-06 16:43 | 10 | 0:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | S22090600203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 10 | 2022-09-06 | 100 | keep | 0 | Sep | 2022 | 6.811e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-06 16:38 | 2022-09-06 18:00 | 50 | 1:22 | P | CAUSAS EXTERNAS | 2 X 65 EN CORTE DE LINEA GLOBO CRUZO FASE | S22090600485 | New_Event | Damage From Public | Include | Include | Public | 82 | 2022-09-06 | 4100 | keep | 0 | Sep | 2022 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-06 16:39 | 2022-09-06 21:33 | 22 | 4:54 | P | DESGANCHE | DESGANCHE Y SE REPUSO 2 X 65 EN RISER | B22090600311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-09-06 | 6468 | keep | 0 | Sep | 2022 | 0.0044053 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
AGUADILLA | 2022-09-06 16:42 | 2022-09-07 00:18 | 300 | 7:36 | P | CONDUCTOR ROTO O ABIERTO | 3 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22090600286 | New_Event | Primary Wire Break | Include | Include | Equipment | 456 | 2022-09-06 | 136800 | keep | 0 | Sep | 2022 | 0.093174 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-09-06 16:43 | 2022-09-06 18:02 | 222 | 1:19 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 SE CERRO POR SCADA SECCIONALIZANDO ALIMENTADOR 1909-09. EN SERVICIO 100% 1907-03 Y 5% 1909-09 | S22090600497 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-09-06 | 17538 | keep | 0 | Sep | 2022 | 0.011945 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-09-06 16:43 | 2022-09-06 18:02 | 4456 | 1:19 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 SE CERRO POR SCADA SECCIONALIZANDO ALIMENTADOR 1909-09. EN SERVICIO 100% 1907-03 Y 5% 1909-09 | S22090600497 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2022-09-06 | 352024 | keep | 0 | Sep | 2022 | 0.23976 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
BARRANQUITAS | 2022-09-06 16:43 | 2022-09-06 18:38 | 1106 | 1:55 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR CON EL GOI CG-220906-06 | C22090600341 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 115 | 2022-09-06 | 127190 | keep | 0 | Sep | 2022 | 0.086629 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-09-06 16:45 | 2022-09-06 20:50 | 50 | 4:05 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600142 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 245 | 2022-09-06 | 12250 | keep | 0 | Sep | 2022 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-09-06 16:54 | 2022-09-06 20:49 | 105 | 3:55 | P | DESGANCHE | 2 X 65 EN C/L | C22090600485 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2022-09-06 | 24675 | keep | 0 | Sep | 2022 | 0.016806 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
CANOVANAS | 2022-09-06 16:55 | 2022-09-06 20:11 | 310 | 3:16 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRO MACHETES | R22090600136 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 196 | 2022-09-06 | 60760 | keep | 0 | Sep | 2022 | 0.041383 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-06 17:01 | 2022-09-06 23:26 | 1 | 6:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | A22090600150 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2022-09-06 | 385 | keep | 0 | Sep | 2022 | 0.00026222 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2022-09-06 17:02 | 2022-09-06 17:57 | 80 | 0:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | R22090600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2022-09-06 | 4400 | keep | 0 | Sep | 2022 | 0.0029968 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-09-06 17:04 | 2022-09-07 14:10 | 3 | 21:06 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C22090600493 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1266 | 2022-09-06 | 3798 | keep | 0 | Sep | 2022 | 0.0025868 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-09-06 17:05 | 2022-09-06 18:57 | 75 | 1:52 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L RAYOS | C22090600494 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 112 | 2022-09-06 | 8400 | keep | 0 | Sep | 2022 | 0.0057212 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2022-09-06 17:10 | 2022-09-06 19:10 | 60 | 2:00 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A22090600153 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 120 | 2022-09-06 | 7200 | keep | 0 | Sep | 2022 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-09-06 17:16 | 2022-09-06 21:03 | 1 | 3:47 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO 37.5 KVA X 50 KVA | C22090600503 | New_Event | Service Transformer Failure | Include | Include | Equipment | 227 | 2022-09-06 | 227 | keep | 0 | Sep | 2022 | 0.00015461 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-06 17:19 | 2022-09-06 20:50 | 50 | 3:31 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600158 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 211 | 2022-09-06 | 10550 | keep | 0 | Sep | 2022 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-06 17:21 | 2022-09-06 18:32 | 4 | 1:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA EN PEDESTAL | C22090600509 | New_Event | Secondary Wire Break | Include | Include | Equipment | 71 | 2022-09-06 | 284 | keep | 0 | Sep | 2022 | 0.00019343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2022-09-06 17:26 | 2022-09-06 19:08 | 74 | 1:42 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHO Y REPARO LINEA SECUNDARIA | C22090600511 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-09-06 | 7548 | keep | 0 | Sep | 2022 | 0.0051409 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
HUMACAO | 2022-09-06 17:29 | 2022-09-06 19:58 | 25 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES LLUVIAS | C22090600514 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2022-09-06 | 3725 | keep | 0 | Sep | 2022 | 0.0025371 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2022-09-06 17:31 | 2022-09-07 20:35 | 45 | 27:04 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE HIZO DESGANCHE | S22090600551 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1624 | 2022-09-06 | 73080 | keep | 0 | Sep | 2022 | 0.049774 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2022-09-06 17:33 | 2022-09-06 17:34 | 2770 | 0:01 | T | DESGANCHE | RECIERRE | C22090600518 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-06 | 2770 | keep | 0 | Sep | 2022 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
BARRANQUITAS | 2022-09-06 17:34 | 2022-09-06 23:00 | 100 | 5:26 | P | DESGANCHE | 1 X 100 EN C/L Y 1 X 10 EN XMR | C22090600519 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 326 | 2022-09-06 | 32600 | keep | 0 | Sep | 2022 | 0.022204 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2022-09-06 17:35 | 2022-09-06 19:32 | 20 | 1:57 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22090600168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-09-06 | 2340 | keep | 0 | Sep | 2022 | 0.0015938 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-06 17:39 | 2022-09-06 19:05 | 80 | 1:26 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A22090600169 | New_Event | Animals | Include | Include | Wildlife | 86 | 2022-09-06 | 6880 | keep | 0 | Sep | 2022 | 0.0046859 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-09-06 17:46 | 2022-09-06 18:12 | 40 | 0:26 | P | DESGANCHE | 1 X 65 EN C/L | C22090600531 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2022-09-06 | 1040 | keep | 0 | Sep | 2022 | 0.00070834 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-06 17:57 | 2022-09-06 17:58 | 450 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22090600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 450 | keep | 0 | Sep | 2022 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2022-09-06 18:02 | 2022-09-06 18:48 | 4233 | 0:46 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES ABRIENDO EN OTRO PUNTO PARA ENERGIZAR ALIMENTADOR SECCIONALIZANDOLO 70% EN SERVICIO | S22090600497 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 46 | 2022-09-06 | 194718 | keep | 0 | Sep | 2022 | 0.13262 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2022-09-06 18:03 | 2022-09-06 20:10 | 21 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN TRANSFORMADOR | P22090600277 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2022-09-06 | 2667 | keep | 0 | Sep | 2022 | 0.0018165 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2022-09-06 18:04 | 2022-09-06 21:38 | 200 | 3:34 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090600175 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 214 | 2022-09-06 | 42800 | keep | 0 | Sep | 2022 | 0.029151 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-09-06 18:10 | 2022-09-07 10:57 | 5 | 16:47 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R22090600180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1007 | 2022-09-06 | 5035 | keep | 0 | Sep | 2022 | 0.0034293 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2022-09-06 18:10 | 2022-09-07 07:12 | 113 | 13:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO DISCO PARTIDO | C22090600548 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 782 | 2022-09-06 | 88366 | keep | 0 | Sep | 2022 | 0.060186 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
VEGA BAJA | 2022-09-06 18:14 | 2022-09-06 20:02 | 40 | 1:48 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS 000 | A22090600182 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 108 | 2022-09-06 | 4320 | keep | 0 | Sep | 2022 | 0.0029423 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-06 18:21 | 2022-09-07 12:05 | 7 | 17:44 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE SECUNDARIO | B22090600360 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1064 | 2022-09-06 | 7448 | keep | 0 | Sep | 2022 | 0.0050728 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-09-06 18:23 | 2022-09-07 20:14 | 15 | 25:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 100 KVA Y CAJA EN PROVISIONAL | S22090700423 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1551 | 2022-09-06 | 23265 | keep | 0 | Sep | 2022 | 0.015846 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2022-09-06 18:25 | 2022-09-07 00:10 | 60 | 5:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A22090600186 | New_Event | Primary Wire Break | Include | Include | Equipment | 345 | 2022-09-06 | 20700 | keep | 0 | Sep | 2022 | 0.014099 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-06 18:28 | 2022-09-06 19:21 | 2858 | 0:53 | T | ARBOL SOBRE LINEA | SE ABRIO INTERRUPTOR PARA PODER SECCIONALIZAR AVERIA DE ARBOL SOBRE LINEAS. 85% EN SERVICIO | B22090600036 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 53 | 2022-09-06 | 151474 | keep | 0 | Sep | 2022 | 0.10317 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
CANOVANAS | 2022-09-06 18:29 | 2022-09-06 21:05 | 361 | 2:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | R22090600184 | New_Event | Cutout Failure | Include | Include | Equipment | 156 | 2022-09-06 | 56316 | keep | 0 | Sep | 2022 | 0.038357 | 0.00024588 | Sustained | FALSE | FALSE | Not_TMED_Event | 361
UTUADO | 2022-09-06 18:30 | 2022-09-07 19:40 | 25 | 25:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO SE REALIZO DESGANCHE Y SE HIZO CAMBIO PRIMARIO | A22090600015 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1510 | 2022-09-06 | 37750 | keep | 0 | Sep | 2022 | 0.025711 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-06 18:40 | 2022-09-06 19:37 | 6 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A22090600139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2022-09-06 | 342 | keep | 0 | Sep | 2022 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-09-06 18:48 | 2022-09-06 19:35 | 1269 | 0:47 | P | NO SE REPORTO CAUSA | SE CERRO MACHETES ALIMENTADOR 100% EN SERVICIO. NO SE ENCONTRO CAUSA | S22090600497 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 47 | 2022-09-06 | 59643 | keep | 0 | Sep | 2022 | 0.040623 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-06 19:17 | 2022-09-07 01:08 | 2 | 5:51 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090600590 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 351 | 2022-09-06 | 702 | keep | 0 | Sep | 2022 | 0.00047813 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2022-09-06 19:18 | 2022-09-07 13:50 | 6 | 18:32 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHO | R22090600195 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1112 | 2022-09-06 | 6672 | keep | 0 | Sep | 2022 | 0.0045443 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-09-06 19:36 | 2022-09-07 12:38 | 15 | 17:02 | P | DESGANCHE | SE REALIZO DESGANCHE SE RETEZO LINEA PRIMARIA Y 1 X 30 EN C/L | B22090600387 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1022 | 2022-09-06 | 15330 | keep | 0 | Sep | 2022 | 0.010441 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-09-06 19:54 | 2022-09-06 22:43 | 79 | 2:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22090600314 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2022-09-06 | 13351 | keep | 0 | Sep | 2022 | 0.0090933 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2022-09-06 19:55 | 2022-09-07 12:53 | 6 | 16:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 25 KVA | S22090600670 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1018 | 2022-09-06 | 6108 | keep | 0 | Sep | 2022 | 0.0041601 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-09-06 19:55 | 2022-09-06 20:25 | 6 | 0:30 | P | TRANSFORMADOR AVERIADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZAR BUSHING QUEMADO | A22090600022 | New_Event | Service Transformer Failure | Include | Include | Equipment | 30 | 2022-09-06 | 180 | keep | 0 | Sep | 2022 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-09-06 19:58 | 2022-09-07 01:08 | 7 | 5:10 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090600602 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 310 | 2022-09-06 | 2170 | keep | 0 | Sep | 2022 | 0.001478 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-09-06 20:00 | 2022-09-06 20:30 | 12 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22090600304 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-09-06 | 360 | keep | 0 | Sep | 2022 | 0.00024519 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-09-06 20:00 | 2022-09-06 20:45 | 8 | 0:45 | P | ARBOL SOBRE LINEA | SE ABRIO CAJAS DE TRANSFORMADOR PARA PARA RETIRAR ARBOL SOBRE LAS LINEAS | A22090600151 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 45 | 2022-09-06 | 360 | keep | 0 | Sep | 2022 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-06 20:04 | 2022-09-07 10:22 | 25 | 14:18 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R22090600204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 858 | 2022-09-06 | 21450 | keep | 0 | Sep | 2022 | 0.014609 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2022-09-06 20:07 | 2022-09-07 17:58 | 22 | 21:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO CON CONTRATISTA | C22090600611 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1311 | 2022-09-06 | 28842 | keep | 0 | Sep | 2022 | 0.019644 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
YAUCO | 2022-09-06 20:10 | 2022-09-06 21:05 | 10 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M22090600307 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-09-06 | 550 | keep | 0 | Sep | 2022 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-06 20:11 | 2022-09-07 13:35 | 12 | 17:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | S22090600679 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1044 | 2022-09-06 | 12528 | keep | 0 | Sep | 2022 | 0.0085328 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-09-06 20:14 | 2022-09-07 09:34 | 5 | 13:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA PARTIDA | A22090600203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 800 | 2022-09-06 | 4000 | keep | 0 | Sep | 2022 | 0.0027244 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2022-09-06 20:15 | 2022-09-06 23:20 | 75 | 3:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | P22090600318 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2022-09-06 | 13875 | keep | 0 | Sep | 2022 | 0.0094502 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-09-06 20:21 | 2022-09-06 20:22 | 31 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B22090600398 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 31 | keep | 0 | Sep | 2022 | 2.1114e-05 | 2.1114e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 31
AGUADILLA | 2022-09-06 20:34 | 2022-09-06 23:10 | 80 | 2:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090600207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-09-06 | 12480 | keep | 0 | Sep | 2022 | 0.0085001 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-09-06 20:48 | 2022-09-06 20:49 | 637 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6703-03 | M22090600333 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-06 | 637 | keep | 0 | Sep | 2022 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2022-09-06 20:48 | 2022-09-06 20:49 | 1491 | 0:01 | T | NO SE REPORTO CAUSA | CARGA POR 6703-02 | M22090600333 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-06 | 1491 | keep | 0 | Sep | 2022 | 0.0010155 | 0.0010155 | Momentary | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2022-09-06 20:49 | 2022-09-06 22:26 | 80 | 1:37 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M22090600371 | 1st_after_momentary | Animals | Include | Include | Wildlife | 97 | 2022-09-06 | 7760 | keep | 0 | Sep | 2022 | 0.0052853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-09-06 20:52 | 2022-09-06 23:03 | 300 | 2:11 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REFIRIO SITUACION DE DESGANCHE | M22090600342 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2022-09-06 | 39300 | keep | 0 | Sep | 2022 | 0.026767 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2022-09-06 20:54 | 2022-09-06 20:56 | 143 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 80% DE 1404-07 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22090600695 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-06 | 286 | keep | 0 | Sep | 2022 | 0.00019479 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-09-06 20:54 | 2022-09-06 20:56 | 1085 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 80% POR 1404-06 | S22090600695 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-06 | 2170 | keep | 0 | Sep | 2022 | 0.001478 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
YAUCO | 2022-09-06 20:56 | 2022-09-06 22:05 | 5 | 1:09 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | M22090600352 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-09-06 | 345 | keep | 0 | Sep | 2022 | 0.00023498 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-09-06 21:01 | 2022-09-06 21:04 | 225 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SU CARGA POR 1303-05 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22090600702 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-06 | 675 | keep | 0 | Sep | 2022 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-09-06 21:01 | 2022-09-06 21:04 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1303-04 SE PROBO POR CONTROL QUEDO EN SERVICIO | S22090600702 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-06 | 2610 | keep | 0 | Sep | 2022 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
VEGA BAJA | 2022-09-06 21:41 | 2022-09-07 08:55 | 50 | 11:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090600212 | New_Event | Vegetation Contact | Include | Include | Vegetation | 674 | 2022-09-06 | 33700 | keep | 0 | Sep | 2022 | 0.022953 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-06 22:00 | 2022-09-07 10:40 | 4 | 12:40 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | S22090600717 | New_Event | Vegetation Contact | Include | Include | Vegetation | 760 | 2022-09-06 | 3040 | keep | 0 | Sep | 2022 | 0.0020705 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-06 22:38 | 2022-09-07 21:31 | 8 | 22:53 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL DE EXISTENTE A RISER Y A T-9 | S22090600718 | New_Event | UG Cable Fault | Include | Include | Equipment | 1373 | 2022-09-06 | 10984 | keep | 0 | Sep | 2022 | 0.0074812 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-09-06 22:49 | 2022-09-07 01:07 | 250 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 80 Y 1 X 200 EN CORTE DE LINEA | A22090600408 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2022-09-06 | 34500 | keep | 0 | Sep | 2022 | 0.023498 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2022-09-06 22:53 | 2022-09-07 11:22 | 10 | 12:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B22090600580 | New_Event | Secondary Wire Break | Include | Include | Equipment | 749 | 2022-09-06 | 7490 | keep | 0 | Sep | 2022 | 0.0051014 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-06 23:00 | 2022-09-07 10:52 | 10 | 11:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL XMR Y SE REMPLAZO BAJANTE SECUNDARIO | C22090600364 | New_Event | Secondary Wire Break | Include | Include | Equipment | 712 | 2022-09-06 | 7120 | keep | 0 | Sep | 2022 | 0.0048494 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-06 23:18 | 2022-09-07 13:28 | 16 | 14:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO | B22090600440 | New_Event | Service Transformer Failure | Include | Include | Equipment | 850 | 2022-09-06 | 13600 | keep | 0 | Sep | 2022 | 0.0092629 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2022-09-07 00:13 | 2022-09-07 11:06 | 15 | 10:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO PORTAFUSIBLE | C22090700002 | New_Event | Cutout Failure | Include | Include | Equipment | 653 | 2022-09-07 | 9795 | keep | 0 | Sep | 2022 | 0.0066713 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-07 00:17 | 2022-09-07 11:52 | 3 | 11:35 | P | TRANSFORMADOR AVERIADO | SE PASO CARGA A OTRO XMR POR XMR AVERIADO | B22090700001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 695 | 2022-09-07 | 2085 | keep | 0 | Sep | 2022 | 0.0014201 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-09-07 01:12 | 2022-09-07 04:51 | 80 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | M22090600005 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 219 | 2022-09-07 | 17520 | keep | 0 | Sep | 2022 | 0.011933 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-07 01:21 | 2022-09-07 08:17 | 2 | 6:56 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090600590 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 416 | 2022-09-07 | 832 | keep | 0 | Sep | 2022 | 0.00056667 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-07 01:58 | 2022-09-07 09:07 | 7 | 7:09 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090600602 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 429 | 2022-09-07 | 3003 | keep | 0 | Sep | 2022 | 0.0020453 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2022-09-07 02:08 | 2022-09-07 08:48 | 50 | 6:40 | P | OTRAS CAUSAS | 1 X 50 EN CORTE DE LINEA POR CONTAMINACION (SALITRE) LIGADURA, CONDUCTOR Y AISLADORES | A22090700007 | New_Event | Other Causes | Include | Include | Other | 400 | 2022-09-07 | 20000 | keep | 0 | Sep | 2022 | 0.013622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2022-09-07 02:24 | 2022-09-07 12:30 | 30 | 10:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO AISLADOR PRIMARIO PARTIDO | A22090700009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 606 | 2022-09-07 | 18180 | keep | 0 | Sep | 2022 | 0.012382 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-09-07 03:03 | 2022-09-07 07:18 | 70 | 4:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A22090700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2022-09-07 | 17850 | keep | 0 | Sep | 2022 | 0.012158 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2022-09-07 04:17 | 2022-09-07 06:37 | 100 | 2:20 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22090700053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2022-09-07 | 14000 | keep | 0 | Sep | 2022 | 0.0095353 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-09-07 04:48 | 2022-09-07 04:49 | 2179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22090700066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 2179 | keep | 0 | Sep | 2022 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2022-09-07 05:02 | 2022-09-07 14:46 | 10 | 9:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO 50 KVA X 50 KVA | R22090700067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 584 | 2022-09-07 | 5840 | keep | 0 | Sep | 2022 | 0.0039776 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-09-07 05:30 | 2022-09-07 08:34 | 200 | 3:04 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA POR DESGANCHE | P22090700064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2022-09-07 | 36800 | keep | 0 | Sep | 2022 | 0.025064 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-09-07 05:49 | 2022-09-07 05:50 | 3744 | 0:01 | T | ANIMAL | RECIERRE | P22090700071 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-07 | 3744 | keep | 0 | Sep | 2022 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
PONCE | 2022-09-07 05:50 | 2022-09-07 09:43 | 95 | 3:53 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P22090700124 | 1st_after_momentary | Animals | Include | Include | Wildlife | 233 | 2022-09-07 | 22135 | keep | 0 | Sep | 2022 | 0.015076 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2022-09-07 06:08 | 2022-09-07 07:29 | 2466 | 1:21 | T | DESGANCHE | SE SECCIONALIZO Y ENTRO 25 % EN SERVICIO | S22090700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2022-09-07 | 199746 | keep | 0 | Sep | 2022 | 0.13605 | 0.0016796 | Sustained | FALSE | FALSE | Not_TMED_Event | 2466
HUMACAO | 2022-09-07 06:09 | 2022-09-07 06:10 | 1530 | 0:01 | P | ANIMAL | RECIERRE 65% DE SU CARGA POR 2604-03 | C22090700154 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-07 | 1530 | keep | 0 | Sep | 2022 | 0.0010421 | 0.0010421 | Momentary | FALSE | FALSE | Not_TMED_Event | 1530
HUMACAO | 2022-09-07 06:09 | 2022-09-07 06:10 | 1593 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22090700154 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-07 | 1593 | keep | 0 | Sep | 2022 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2022-09-07 06:10 | 2022-09-07 08:45 | 68 | 2:35 | P | ANIMAL | 1 X 65 EN LA SALIDA DEL RISER Y 1 X 80 EN LA ENTRADA DEL RISER CRUCE POR PALOMA | C22090700155 | 1st_after_momentary | Animals | Include | Include | Wildlife | 155 | 2022-09-07 | 10540 | keep | 0 | Sep | 2022 | 0.0071787 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
HUMACAO | 2022-09-07 06:19 | 2022-09-07 06:20 | 5630 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22090700157 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-07 | 5630 | keep | 0 | Sep | 2022 | 0.0038346 | 0.0038346 | Momentary | FALSE | FALSE | Not_TMED_Event | 5630
HUMACAO | 2022-09-07 06:19 | 2022-09-07 12:08 | 2 | 5:49 | P | ANIMAL | 1 X 25 EN C/L CRUCE POR CHANGO | C22090700156 | New_Event | Animals | Include | Include | Wildlife | 349 | 2022-09-07 | 698 | keep | 0 | Sep | 2022 | 0.0004754 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2022-09-07 06:20 | 2022-09-07 09:17 | 198 | 2:57 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR PALOMA | C22090700187 | 1st_after_momentary | Animals | Include | Include | Wildlife | 177 | 2022-09-07 | 35046 | keep | 0 | Sep | 2022 | 0.02387 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
HUMACAO | 2022-09-07 06:22 | 2022-09-07 09:58 | 71 | 3:36 | P | ANIMAL | 1 X 100 EN RISER CRUCE POR PALOMA | C22090700158 | New_Event | Animals | Include | Include | Wildlife | 216 | 2022-09-07 | 15336 | keep | 0 | Sep | 2022 | 0.010445 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
AGUADILLA | 2022-09-07 06:22 | 2022-09-07 06:23 | 390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22090700011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 390 | keep | 0 | Sep | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
CAGUAS | 2022-09-07 06:34 | 2022-09-07 16:03 | 11 | 9:29 | P | SECUNDARIA/DESGANCHE | 2 X 8 EN TRANSFORMADOR SE REALIZO DESCGANCHE SECUNDARIO Y SE DEJO FUERA CLIENTE CON PROBLEMA INTERNO | C22090700162 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 569 | 2022-09-07 | 6259 | keep | 0 | Sep | 2022 | 0.004263 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-09-07 06:42 | 2022-09-07 06:44 | 271 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S22090700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-07 | 542 | keep | 0 | Sep | 2022 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2022-09-07 07:04 | 2022-09-07 12:27 | 30 | 5:23 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN XMR Y 1 X 65 EN C/L REEMPLAZO DE PARARRAYO AVERIADO | R22090700073 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 323 | 2022-09-07 | 9690 | keep | 0 | Sep | 2022 | 0.0065998 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-07 07:15 | 2022-09-07 07:17 | 2524 | 0:02 | T | ANIMAL | DISAPRO DE BKR SE CERRO POR CONTROL | R22090700075 | New_Event | Animals | Include | Include | Wildlife | 2 | 2022-09-07 | 5048 | keep | 0 | Sep | 2022 | 0.0034382 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2022-09-07 07:17 | 2022-09-07 09:40 | 100 | 2:23 | P | ANIMAL | 2 X 100 EN C/L CRUCE POR AVE | R22090700082 | 1st_after_momentary | Animals | Include | Include | Wildlife | 143 | 2022-09-07 | 14300 | keep | 0 | Sep | 2022 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-07 07:19 | 2022-09-07 10:25 | 10 | 3:06 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PARARRAYO Y SE DESGANCHO | C22090700166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2022-09-07 | 1860 | keep | 0 | Sep | 2022 | 0.0012668 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-07 07:21 | 2022-09-07 14:00 | 30 | 6:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S22090700133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2022-09-07 | 11970 | keep | 0 | Sep | 2022 | 0.0081527 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-09-07 07:23 | 2022-09-07 10:12 | 2900 | 2:49 | T | DESCONECTIVO DEFECTUOSO | DISPARO INTERRUPTOR SE SECCIONALIZO CON UN 35% EN SERVICIO CERRADO POR CONTROL SE CONTINUA PATRULLANDO | C22090700167 | New_Event | Switch Failure | Include | Include | Equipment | 169 | 2022-09-07 | 490100 | keep | 0 | Sep | 2022 | 0.3338 | 0.0019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 2900
VEGA BAJA | 2022-09-07 07:24 | 2022-09-07 11:09 | 40 | 3:45 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER 1X 30 Y 1 X 65 EN C/L | B22090700068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2022-09-07 | 9000 | keep | 0 | Sep | 2022 | 0.0061299 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-09-07 07:27 | 2022-09-07 20:08 | 8 | 12:41 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090700168 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 761 | 2022-09-07 | 6088 | keep | 0 | Sep | 2022 | 0.0041465 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-09-07 07:29 | 2022-09-07 10:27 | 1849 | 2:58 | P | DESGANCHE | SE SECCIONALIZO TRAMO Y SE REMPLAZO MACHETE POR CRUCE DE RAMA EN LA LINEA. 80 % EN SERVICO. | S22090700095 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-09-07 | 329122 | keep | 0 | Sep | 2022 | 0.22416 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2022-09-07 07:32 | 2022-09-07 08:45 | 150 | 1:13 | P | CONDUCTOR ROTO O ABIERTO | ABRIR CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO PARTIDO | M22090700018 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2022-09-07 | 10950 | keep | 0 | Sep | 2022 | 0.007458 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-09-07 07:37 | 2022-09-07 11:32 | 1784 | 3:55 | P | TERMINACION SOTERRADA AVERIADA | SE CERRO AMARRE ENTRE 1711-04 Y 1801-02 SECCIONALIZANDO CARGA 1717-01. 100% CARGA 1711-04 FUERA CARGA 1717-01 | B22090700071 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 235 | 2022-09-07 | 419240 | keep | 0 | Sep | 2022 | 0.28554 | 0.0012151 | Sustained | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2022-09-07 07:37 | 2022-09-07 12:35 | 2000 | 4:58 | P | TERMINACION SOTERRADA AVERIADA | SE CERRO AMARRE CON 1717-01 SECCIONALIZANDO HACIA SU 6 POR TERMINACIONES SOTERRADAS AVERIADAS. 50% DE LA CARGA DE 1717-01 EN SERVICIO | B22090700071 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 298 | 2022-09-07 | 596000 | keep | 0 | Sep | 2022 | 0.40593 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2022-09-07 07:37 | 2022-09-07 10:12 | 186 | 2:35 | T | TERMINACION SOTERRADA AVERIADA | DISPARO INTERRUPTOR 1801-02 LLEVANDO 90% DEL 1711-04 Y PARTE DEL 1717-01 SE CERRO POR SCADA ABRIENDO AMARRE ENTRE ALIMENTADORES. 100% 1801-02 FUERA 1711-04 Y 1717-01 | B22090700071 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 155 | 2022-09-07 | 28830 | keep | 0 | Sep | 2022 | 0.019636 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
HUMACAO | 2022-09-07 07:38 | 2022-09-07 10:08 | 6 | 2:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 15 EN TRANSFORMADOR SE REEMPLAZO BAJANTE SECUNDARIO | C22090700170 | New_Event | Secondary Wire Break | Include | Include | Equipment | 150 | 2022-09-07 | 900 | keep | 0 | Sep | 2022 | 0.00061299 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-09-07 07:47 | 2022-09-07 08:15 | 188 | 0:28 | P | DESGANCHE | SE ABRIO CORTE DE LINEA TOTAL PARA SECCIONALIZAR Y ENTREGAR AL PERSONAL DE DESGANCHE | C22090700174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2022-09-07 | 5264 | keep | 0 | Sep | 2022 | 0.0035853 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
BAYAMON | 2022-09-07 07:50 | 2022-09-07 14:20 | 84 | 6:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | B22090700078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 390 | 2022-09-07 | 32760 | keep | 0 | Sep | 2022 | 0.022313 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
ARECIBO | 2022-09-07 07:51 | 2022-09-07 09:32 | 20 | 1:41 | P | OTRAS CAUSAS | 1 X 25 EN CORTE DE LINEA POR CONTAMINACION (SALITRE) LIGADURAS, CONDUCTOR AISLADORES, TORNILLOS ETC | A22090700025 | New_Event | Other Causes | Include | Include | Other | 101 | 2022-09-07 | 2020 | keep | 0 | Sep | 2022 | 0.0013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-07 07:55 | 2022-09-07 10:19 | 25 | 2:24 | P | DESGANCHE | 2 X 40 EN RISER Y SE RELIAZO DESGANCHE | S22090700152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-09-07 | 3600 | keep | 0 | Sep | 2022 | 0.0024519 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2022-09-07 07:57 | 2022-09-07 13:58 | 20 | 6:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C22090700176 | New_Event | Secondary Wire Break | Include | Include | Equipment | 361 | 2022-09-07 | 7220 | keep | 0 | Sep | 2022 | 0.0049175 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-07 08:01 | 2022-09-07 08:02 | 222 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22090700000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 222 | keep | 0 | Sep | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-09-07 08:01 | 2022-09-07 08:02 | 4456 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 | S22090700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 4456 | keep | 0 | Sep | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-09-07 08:02 | 2022-09-07 13:26 | 10 | 5:24 | P | MAL TIEMPO/RAYOS | 3 X 100 EN C/L MAL TIEMPO RAYOS | S22090700304 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 324 | 2022-09-07 | 3240 | keep | 0 | Sep | 2022 | 0.0022067 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-09-07 08:15 | 2022-09-07 20:40 | 188 | 12:25 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJAS PRIMARIAS Y SE REALIZO DESGANCHE MASIVO GOI CG-220907-02 | C22090700174 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 745 | 2022-09-07 | 140060 | keep | 0 | Sep | 2022 | 0.095394 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
HUMACAO | 2022-09-07 08:17 | 2022-09-07 14:10 | 150 | 5:53 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C22090700180 | New_Event | Animals | Include | Include | Wildlife | 353 | 2022-09-07 | 52950 | keep | 0 | Sep | 2022 | 0.036064 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-09-07 08:20 | 2022-09-07 12:39 | 5 | 4:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S22090700166 | New_Event | Secondary Wire Break | Include | Include | Equipment | 259 | 2022-09-07 | 1295 | keep | 0 | Sep | 2022 | 0.00088202 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2022-09-07 08:20 | 2022-09-07 10:48 | 5 | 2:28 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 65 EN C/L, CONTAMINACION EN TRANSCLOSURE | C22090700181 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 148 | 2022-09-07 | 740 | keep | 0 | Sep | 2022 | 0.00050401 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-09-07 08:27 | 2022-09-07 12:00 | 8 | 3:33 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 37.5KVA X 25KVA | B22090700092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 213 | 2022-09-07 | 1704 | keep | 0 | Sep | 2022 | 0.0011606 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-09-07 08:28 | 2022-09-07 11:43 | 50 | 3:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B22090700093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2022-09-07 | 9750 | keep | 0 | Sep | 2022 | 0.0066407 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-09-07 08:29 | 2022-09-07 09:31 | 1 | 1:02 | P | ANIMAL | 2 X 30 Y 3 X 40 EN C/L CRUCE POR AVE | R22090700137 | New_Event | Animals | Include | Include | Wildlife | 62 | 2022-09-07 | 62 | keep | 0 | Sep | 2022 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-09-07 08:30 | 2022-09-07 15:56 | 46 | 7:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REPARO CONDUCTOR PRIMARIO Y SE REALIZO DESGANCHE | C22090700189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 446 | 2022-09-07 | 20516 | keep | 0 | Sep | 2022 | 0.013973 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BAYAMON | 2022-09-07 08:41 | 2022-09-07 08:42 | 13 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22090700102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 13 | keep | 0 | Sep | 2022 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2022-09-07 08:44 | 2022-09-07 10:11 | 111 | 1:27 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S22090700106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2022-09-07 | 9657 | keep | 0 | Sep | 2022 | 0.0065773 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
BARRANQUITAS | 2022-09-07 08:50 | 2022-09-07 16:34 | 66 | 7:44 | P | DESGANCHE | 1 X 100 EN C/L, DESGANCHE | C22090700201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 464 | 2022-09-07 | 30624 | keep | 0 | Sep | 2022 | 0.020858 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
UTUADO | 2022-09-07 08:59 | 2022-09-07 13:43 | 20 | 4:44 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22090700031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2022-09-07 | 5680 | keep | 0 | Sep | 2022 | 0.0038686 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-07 09:02 | 2022-09-07 16:35 | 187 | 7:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER 1 X 80 EN SU Y 1 X 65 EN SALIDA DE RISER SE REEMPLAZO CAJA PRIMARIA | B22090700110 | New_Event | Cutout Failure | Include | Include | Equipment | 453 | 2022-09-07 | 84711 | keep | 0 | Sep | 2022 | 0.057696 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
ARECIBO | 2022-09-07 09:05 | 2022-09-07 17:14 | 30 | 8:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | A22090700032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 489 | 2022-09-07 | 14670 | keep | 0 | Sep | 2022 | 0.0099917 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2022-09-07 09:07 | 2022-09-07 12:45 | 10 | 3:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A22090700034 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2022-09-07 | 2180 | keep | 0 | Sep | 2022 | 0.0014848 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-07 09:12 | 2022-09-07 13:13 | 1 | 4:01 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | R22090700173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2022-09-07 | 241 | keep | 0 | Sep | 2022 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-07 09:15 | 2022-09-07 09:57 | 1129 | 0:42 | P | DESGANCHE | SE REALIZARON OPERACIONES PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO SE AFECTO EL 70% | R22090700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2022-09-07 | 47418 | keep | 0 | Sep | 2022 | 0.032296 | 0.00076896 | Sustained | FALSE | FALSE | Not_TMED_Event | 1129
BAYAMON | 2022-09-07 09:21 | 2022-09-07 10:11 | 8 | 0:50 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE SECUNDARIO Y SE REPARO SECUNDARIA | B22090600364 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2022-09-07 | 400 | keep | 0 | Sep | 2022 | 0.00027244 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-09-07 09:22 | 2022-09-07 11:51 | 250 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 50 EN RISER | B22090700115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2022-09-07 | 37250 | keep | 0 | Sep | 2022 | 0.025371 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
UTUADO | 2022-09-07 09:30 | 2022-09-07 10:06 | 9 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS PARTIDAS | A22090700037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2022-09-07 | 324 | keep | 0 | Sep | 2022 | 0.00022067 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2022-09-07 09:56 | 2022-09-07 10:50 | 1 | 0:54 | P | TRANSFORMADOR AVERIADO | SE REPARO EL CONTACTO DEL BUSHING DE XMR NO FUNDIO FUSIBLE | R22090700193 | New_Event | Service Transformer Failure | Include | Include | Equipment | 54 | 2022-09-07 | 54 | keep | 0 | Sep | 2022 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-07 09:57 | 2022-09-07 12:00 | 161 | 2:03 | P | DESGANCHE | SE LEVANTO CONDUCTOR DEL SUELO Y DESGANCHE SE AFECTO EL 10% | R22090700083 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 123 | 2022-09-07 | 19803 | keep | 0 | Sep | 2022 | 0.013488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-09-07 10:09 | 2022-09-07 10:12 | 1185 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE RETIRO PELIGRO DE LINEA PARTIDA | A22090700044 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2022-09-07 | 3555 | keep | 0 | Sep | 2022 | 0.0024213 | 0.0008071 | Momentary | FALSE | FALSE | Not_TMED_Event | 1185
CAGUAS | 2022-09-07 10:12 | 2022-09-07 11:11 | 1843 | 0:59 | P | DESCONECTIVO DEFECTUOSO | SE ABRIERON MACHETES Y SE PROBO TRAMO CERRANDO EL BKR | C22090700167 | New_Event | Switch Failure | Include | Include | Equipment | 59 | 2022-09-07 | 108737 | keep | 0 | Sep | 2022 | 0.07406 | 0.0012553 | Sustained | FALSE | FALSE | Not_TMED_Event | 1843
ARECIBO | 2022-09-07 10:12 | 2022-09-07 14:36 | 40 | 4:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 35 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A22090700046 | New_Event | Cutout Failure | Include | Include | Equipment | 264 | 2022-09-07 | 10560 | keep | 0 | Sep | 2022 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-07 10:27 | 2022-09-07 10:32 | 369 | 0:05 | P | DESGANCHE | SE RETIRO RAMA ARBOL CRUZANDO LINEA CON VARETA | S22090700095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-09-07 | 1845 | keep | 0 | Sep | 2022 | 0.0012566 | 0.00025132 | Momentary | FALSE | FALSE | Not_TMED_Event | 369
CANOVANAS | 2022-09-07 10:27 | 2022-09-07 10:32 | 1 | 0:05 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R22090700199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2022-09-07 | 5 | keep | 0 | Sep | 2022 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-09-07 10:30 | 2022-09-07 11:30 | 16 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M22090700075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-09-07 | 960 | keep | 0 | Sep | 2022 | 0.00065385 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-09-07 10:37 | 2022-09-07 11:40 | 12 | 1:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | S22090700261 | New_Event | Cutout Failure | Include | Include | Equipment | 63 | 2022-09-07 | 756 | keep | 0 | Sep | 2022 | 0.00051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-09-07 10:39 | 2022-09-07 10:44 | 353 | 0:05 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA EN SERVICIO | S22090700265 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2022-09-07 | 1765 | keep | 0 | Sep | 2022 | 0.0012021 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
SAN JUAN | 2022-09-07 10:44 | 2022-09-07 15:54 | 117 | 5:10 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO SE VA A ABRIR INTERRUPTOR PARA REPARAR | S22090700281 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 310 | 2022-09-07 | 36270 | keep | 0 | Sep | 2022 | 0.024703 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2022-09-07 10:53 | 2022-09-07 11:44 | 12 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO TOMA DEL CLIENTE Y REMPLAZO CONEXIONES EN PEDESTAL | P22090700198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2022-09-07 | 612 | keep | 0 | Sep | 2022 | 0.00041683 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2022-09-07 11:01 | 2022-09-07 19:02 | 53 | 8:01 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 Y 1 X 25 EN CORTES DE LINEA Y LEVANTARON CONDUCTOR PRIMARIO | C22090700249 | New_Event | Primary Wire Break | Include | Include | Equipment | 481 | 2022-09-07 | 25493 | keep | 0 | Sep | 2022 | 0.017363 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
AGUADILLA | 2022-09-07 11:02 | 2022-09-07 11:03 | 390 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR CAJA PRIMARIA QUEMADA | M22090700076 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-09-07 | 390 | keep | 0 | Sep | 2022 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2022-09-07 11:03 | 2022-09-07 13:20 | 73 | 2:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22090700082 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 137 | 2022-09-07 | 10001 | keep | 0 | Sep | 2022 | 0.0068116 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
CANOVANAS | 2022-09-07 11:11 | 2022-09-07 11:14 | 2106 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | R22090700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-07 | 6318 | keep | 0 | Sep | 2022 | 0.0043032 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
CAGUAS | 2022-09-07 11:11 | 2022-09-07 11:31 | 2900 | 0:20 | T | DESCONECTIVO DEFECTUOSO | DISPARO BKR SE SECCIONALIZO MACHETE AVERIADO | C22090700167 | Additional_clients | Switch Failure | Include | Include | Equipment | 20 | 2022-09-07 | 58000 | keep | 0 | Sep | 2022 | 0.039504 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-07 11:14 | 2022-09-07 15:27 | 165 | 4:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S22090700284 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 253 | 2022-09-07 | 41745 | keep | 0 | Sep | 2022 | 0.028432 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
HUMACAO | 2022-09-07 11:14 | 2022-09-07 15:02 | 20 | 3:48 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR 37.5 KVA X 37.5 KVA | C22090700255 | New_Event | Service Transformer Failure | Include | Include | Equipment | 228 | 2022-09-07 | 4560 | keep | 0 | Sep | 2022 | 0.0031058 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-09-07 11:18 | 2022-09-07 11:46 | 10 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | R22090600207 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2022-09-07 | 280 | keep | 0 | Sep | 2022 | 0.00019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-07 11:18 | 2022-09-07 11:58 | 11 | 0:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO Y SE CERRO C/L | C22090700258 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 40 | 2022-09-07 | 440 | keep | 0 | Sep | 2022 | 0.00029968 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-09-07 11:20 | 2022-09-07 15:36 | 40 | 4:16 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22090700216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2022-09-07 | 10240 | keep | 0 | Sep | 2022 | 0.0069744 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-07 11:22 | 2022-09-07 11:52 | 6 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON BARRAS SECUNDARIAS EN PEDESTAL | S22090600664 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2022-09-07 | 180 | keep | 0 | Sep | 2022 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2022-09-07 11:27 | 2022-09-07 13:33 | 10 | 2:06 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S22090700290 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 126 | 2022-09-07 | 1260 | keep | 0 | Sep | 2022 | 0.00085818 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-09-07 11:31 | 2022-09-07 14:20 | 1449 | 2:49 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETE AVERIADO | C22090700167 | Partial_restoration | Switch Failure | Include | Include | Equipment | 169 | 2022-09-07 | 244881 | keep | 0 | Sep | 2022 | 0.16679 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-07 11:38 | 2022-09-07 15:13 | 30 | 3:35 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S22090700294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-09-07 | 6450 | keep | 0 | Sep | 2022 | 0.0043931 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-07 11:39 | 2022-09-07 12:42 | 40 | 1:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R22090700221 | New_Event | Cutout Failure | Include | Include | Equipment | 63 | 2022-09-07 | 2520 | keep | 0 | Sep | 2022 | 0.0017164 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-07 11:52 | 2022-09-07 14:58 | 7 | 3:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR FUERTES LLUVIAS | R22090700223 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 186 | 2022-09-07 | 1302 | keep | 0 | Sep | 2022 | 0.00088679 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 12:07 | 2791 | 0:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-07 | 33492 | keep | 0 | Sep | 2022 | 0.022811 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 12:07 | 1464 | 0:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-07 | 17568 | keep | 0 | Sep | 2022 | 0.011965 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 12:07 | 759 | 0:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-07 | 9108 | keep | 0 | Sep | 2022 | 0.0062034 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 12:07 | 1500 | 0:12 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700060 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 12 | 2022-09-07 | 18000 | keep | 0 | Sep | 2022 | 0.01226 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 13:19 | 2132 | 1:24 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700058 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-09-07 | 179088 | keep | 0 | Sep | 2022 | 0.12198 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 13:19 | 2366 | 1:24 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700058 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-09-07 | 198744 | keep | 0 | Sep | 2022 | 0.13536 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 13:19 | 1976 | 1:24 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700058 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-09-07 | 165984 | keep | 0 | Sep | 2022 | 0.11305 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-09-07 11:55 | 2022-09-07 13:19 | 3688 | 1:24 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090700058 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 84 | 2022-09-07 | 309792 | keep | 0 | Sep | 2022 | 0.211 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 3070 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700188 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 9210 | keep | 0 | Sep | 2022 | 0.0062729 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 2735 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700188 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 8205 | keep | 0 | Sep | 2022 | 0.0055884 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 1070 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700188 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 3210 | keep | 0 | Sep | 2022 | 0.0021863 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 1647 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700189 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 4941 | keep | 0 | Sep | 2022 | 0.0033653 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 3295 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700189 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 9885 | keep | 0 | Sep | 2022 | 0.0067326 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 1180 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700189 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 3540 | keep | 0 | Sep | 2022 | 0.0024111 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 320 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700198 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 960 | keep | 0 | Sep | 2022 | 0.00065385 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-09-07 11:55 | 2022-09-07 11:58 | 2234 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700198 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-07 | 6702 | keep | 0 | Sep | 2022 | 0.0045647 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 3070 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700188 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 6140 | keep | 0 | Sep | 2022 | 0.0041819 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 2735 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700188 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 5470 | keep | 0 | Sep | 2022 | 0.0037256 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 1070 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700188 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 2140 | keep | 0 | Sep | 2022 | 0.0014575 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 1647 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700189 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 3294 | keep | 0 | Sep | 2022 | 0.0022435 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 3295 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700189 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 6590 | keep | 0 | Sep | 2022 | 0.0044884 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 1180 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700189 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 2360 | keep | 0 | Sep | 2022 | 0.0016074 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 320 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700198 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 640 | keep | 0 | Sep | 2022 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-09-07 11:59 | 2022-09-07 12:01 | 2234 | 0:02 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LA LINEA 36100 | B22090700198 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-07 | 4468 | keep | 0 | Sep | 2022 | 0.0030431 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CAGUAS | 2022-09-07 12:06 | 2022-09-07 13:13 | 14 | 1:07 | P | SECUNDARIA/DESGANCHE | SE REALIZO DESGANCHE SECUNDARIO Y LEVANTO SECUNDARIA | C22090700164 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 67 | 2022-09-07 | 938 | keep | 0 | Sep | 2022 | 0.00063887 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2022-09-07 12:07 | 2022-09-07 13:35 | 15 | 1:28 | P | ARBOL SOBRE LINEA | 1 X 25 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22090700022 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 88 | 2022-09-07 | 1320 | keep | 0 | Sep | 2022 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-09-07 12:09 | 2022-09-07 16:10 | 64 | 4:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C22090700275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-09-07 | 15424 | keep | 0 | Sep | 2022 | 0.010505 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
BARRANQUITAS | 2022-09-07 12:10 | 2022-09-07 13:46 | 10 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA EN PEDESTAL | C22090600593 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2022-09-07 | 960 | keep | 0 | Sep | 2022 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-07 12:12 | 2022-09-07 12:13 | 1467 | 0:01 | T | DESGANCHE | RECIERRE | C22090700279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-07 | 1467 | keep | 0 | Sep | 2022 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2022-09-07 12:13 | 2022-09-07 18:21 | 17 | 6:08 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C22090700306 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 368 | 2022-09-07 | 6256 | keep | 0 | Sep | 2022 | 0.0042609 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CAGUAS | 2022-09-07 12:14 | 2022-09-07 16:25 | 150 | 4:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | C22090700280 | New_Event | Primary Wire Break | Include | Include | Equipment | 251 | 2022-09-07 | 37650 | keep | 0 | Sep | 2022 | 0.025643 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-09-07 12:20 | 2022-09-07 13:22 | 1802 | 1:02 | T | DESGANCHE | SE SECCIONALIZO Y SE CERRO INTERRUPTOR 10% EN SERVICIO | S22090700409 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2022-09-07 | 111724 | keep | 0 | Sep | 2022 | 0.076095 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
HUMACAO | 2022-09-07 12:20 | 2022-09-07 16:46 | 3 | 4:26 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | C22090700283 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 266 | 2022-09-07 | 798 | keep | 0 | Sep | 2022 | 0.00054351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-09-07 12:27 | 2022-09-07 15:00 | 20 | 2:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | C22090700288 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2022-09-07 | 3060 | keep | 0 | Sep | 2022 | 0.0020842 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-07 12:30 | 2022-09-07 13:27 | 6 | 0:57 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR SE REMPLAZO XMR DE 25 KVA X 37.5 KVA | C22090700286 | New_Event | Service Transformer Failure | Include | Include | Equipment | 57 | 2022-09-07 | 342 | keep | 0 | Sep | 2022 | 0.00023293 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2022-09-07 12:33 | 2022-09-07 12:34 | 1835 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | C22090700279 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 1835 | keep | 0 | Sep | 2022 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2022-09-07 12:34 | 2022-09-07 13:20 | 9 | 0:46 | P | MAL TIEMPO/RAYOS | 3 X 65 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO RAYO | C22090700363 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 46 | 2022-09-07 | 414 | keep | 0 | Sep | 2022 | 0.00028197 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2022-09-07 12:35 | 2022-09-07 16:20 | 1000 | 3:45 | P | TERMINACION SOTERRADA AVERIADA | SE CERRO N/O CON MISMO ALIMENTADOR PARA ENERGIZAR Y SECCIONALIZAR AVERIA DE TERMINACION SOTERRADA AVERIADA EN SU 6 | B22090700071 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 225 | 2022-09-07 | 225000 | keep | 0 | Sep | 2022 | 0.15325 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
HUMACAO | 2022-09-07 12:35 | 2022-09-07 17:38 | 20 | 5:03 | P | TRANSFORMADOR AVERIADO | 1 X 8 EN TRANSFORMADOR SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA X 37.5 KVA | C22090700292 | New_Event | Service Transformer Failure | Include | Include | Equipment | 303 | 2022-09-07 | 6060 | keep | 0 | Sep | 2022 | 0.0041274 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-07 12:37 | 2022-09-07 14:30 | 1 | 1:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA | S22090600263 | New_Event | Secondary Wire Break | Include | Include | Equipment | 113 | 2022-09-07 | 113 | keep | 0 | Sep | 2022 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-07 12:40 | 2022-09-07 16:56 | 30 | 4:16 | P | ARBOL SOBRE LINEA | 1 X 50 EN C/L RETIRO ARBOL DE LAS LINEAS | R22090700230 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 256 | 2022-09-07 | 7680 | keep | 0 | Sep | 2022 | 0.0052308 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-07 12:42 | 2022-09-07 13:39 | 1448 | 0:57 | T | ARBOL SOBRE LINEA | DISPARO DE BKR SE RETIRO ARBOL SOBRE LINEA Y SE CERRO BKR | R22090700231 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 57 | 2022-09-07 | 82536 | keep | 0 | Sep | 2022 | 0.056215 | 0.00098623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1448
BAYAMON | 2022-09-07 12:43 | 2022-09-07 13:03 | 478 | 0:20 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO INTERRUPTOR 1705-01 LLEVANDO CARGA 1705-03 SE CERRO POR SCADA LLUVIA FUERTE | B22090800093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 20 | 2022-09-07 | 9560 | keep | 0 | Sep | 2022 | 0.0065113 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
SAN JUAN | 2022-09-07 12:44 | 2022-09-07 12:46 | 271 | 0:02 | T | NO SE REPORTO CAUSA | DISAPRO DE INTERRUPTOR SE CERRO POR SCADA | S22090700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-07 | 542 | keep | 0 | Sep | 2022 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2022-09-07 12:45 | 2022-09-07 18:53 | 1 | 6:08 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L RAYOS | R22090700232 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 368 | 2022-09-07 | 368 | keep | 0 | Sep | 2022 | 0.00025064 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-07 12:51 | 2022-09-07 12:53 | 2617 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B22090700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-07 | 5234 | keep | 0 | Sep | 2022 | 0.0035649 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BARRANQUITAS | 2022-09-07 12:51 | 2022-09-07 15:18 | 9 | 2:27 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C22090700302 | New_Event | Service Transformer Failure | Include | Include | Equipment | 147 | 2022-09-07 | 1323 | keep | 0 | Sep | 2022 | 0.00090109 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2022-09-07 12:58 | 2022-09-07 19:35 | 92 | 6:37 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090700304 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 397 | 2022-09-07 | 36524 | keep | 0 | Sep | 2022 | 0.024876 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
ARECIBO | 2022-09-07 12:58 | 2022-09-07 14:29 | 4 | 1:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR | A22090700079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2022-09-07 | 364 | keep | 0 | Sep | 2022 | 0.00024792 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2022-09-07 12:59 | 2022-09-07 13:00 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M22090700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 3041 | keep | 0 | Sep | 2022 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
YAUCO | 2022-09-07 13:00 | 2022-09-07 14:50 | 540 | 1:50 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR NEUTRAL PRIMARIO PARTIDO | M22090700086 | New_Event | Primary Wire Break | Include | Include | Equipment | 110 | 2022-09-07 | 59400 | keep | 0 | Sep | 2022 | 0.040457 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
AGUADILLA | 2022-09-07 13:00 | 2022-09-07 15:10 | 2 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M22090700140 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 130 | 2022-09-07 | 260 | keep | 0 | Sep | 2022 | 0.00017708 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2022-09-07 13:01 | 2022-09-07 14:15 | 11 | 1:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P22090700244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-09-07 | 814 | keep | 0 | Sep | 2022 | 0.00055441 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2022-09-07 13:03 | 2022-09-07 16:10 | 2391 | 3:07 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA LEVANTAR 1 FASE PRIMARIA Y CERRO INTERRUPTOR LLEVA 200 CLIENTES DEL 1908-03 | S22090700359 | New_Event | Primary Wire Break | Include | Include | Equipment | 187 | 2022-09-07 | 447117 | keep | 0 | Sep | 2022 | 0.30453 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
SAN JUAN | 2022-09-07 13:03 | 2022-09-07 16:10 | 200 | 3:07 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA Y CERRO INTERRUPTOR SU CARGA POR EL 1343-05 | S22090700359 | New_Event | Primary Wire Break | Include | Include | Equipment | 187 | 2022-09-07 | 37400 | keep | 0 | Sep | 2022 | 0.025473 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2022-09-07 13:03 | 2022-09-07 13:39 | 6 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXIONES EN PEDESTAL Y CONEXIONES EN TRANSFORMADOR | P22090700242 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2022-09-07 | 216 | keep | 0 | Sep | 2022 | 0.00014712 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-09-07 13:04 | 2022-09-07 13:11 | 1902 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22090700243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-07 | 13314 | keep | 0 | Sep | 2022 | 0.0090681 | 0.0012954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-09-07 13:04 | 2022-09-07 13:11 | 970 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22090700243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-07 | 6790 | keep | 0 | Sep | 2022 | 0.0046246 | 0.00066066 | Sustained | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2022-09-07 13:04 | 2022-09-07 13:11 | 3003 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22090700243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-07 | 21021 | keep | 0 | Sep | 2022 | 0.014317 | 0.0020453 | Sustained | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2022-09-07 13:04 | 2022-09-07 13:11 | 2343 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22090700241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-07 | 16401 | keep | 0 | Sep | 2022 | 0.011171 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2022-09-07 13:04 | 2022-09-07 13:11 | 1830 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22090700241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-07 | 12810 | keep | 0 | Sep | 2022 | 0.0087248 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2022-09-07 13:04 | 2022-09-07 13:11 | 710 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22090700241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-07 | 4970 | keep | 0 | Sep | 2022 | 0.003385 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2022-09-07 13:04 | 2022-09-07 13:11 | 1197 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R22090700241 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2022-09-07 | 8379 | keep | 0 | Sep | 2022 | 0.0057069 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
CANOVANAS | 2022-09-07 13:04 | 2022-09-07 13:06 | 3012 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE CERRO POR CONTROL | R22090700254 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2022-09-07 | 6024 | keep | 0 | Sep | 2022 | 0.0041029 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
BAYAMON | 2022-09-07 13:06 | 2022-09-07 14:03 | 15 | 0:57 | P | MAL TIEMPO/RAYOS | 1 X 25 EN C/L MAL TIEMPO RAYOS | B22090700208 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 57 | 2022-09-07 | 855 | keep | 0 | Sep | 2022 | 0.00058234 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-09-07 13:07 | 2022-09-07 14:45 | 1 | 1:38 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22090700095 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 98 | 2022-09-07 | 98 | keep | 0 | Sep | 2022 | 6.6747e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-07 13:10 | 2022-09-07 14:17 | 1 | 1:07 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L RAYOS | B22090700209 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 67 | 2022-09-07 | 67 | keep | 0 | Sep | 2022 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-07 13:11 | 2022-09-07 14:30 | 3012 | 1:19 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SE ABRIO MACHETES PARA PROBAR TRAMO Y SE CERRO BKR ENTRO 40% EN SERVICIO | R22090700254 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 79 | 2022-09-07 | 237948 | keep | 0 | Sep | 2022 | 0.16207 | 0.0020515 | Sustained | FALSE | FALSE | Not_TMED_Event | 3012
UTUADO | 2022-09-07 13:15 | 2022-09-07 16:11 | 20 | 2:56 | P | MAL TIEMPO/RAYOS | 1 X 15 EN DOS TRANSFORMADORES Y 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090700081 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 176 | 2022-09-07 | 3520 | keep | 0 | Sep | 2022 | 0.0023975 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-09-07 13:20 | 2022-09-07 13:21 | 1835 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | C22090700291 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 1835 | keep | 0 | Sep | 2022 | 0.0012498 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-07 13:21 | 2022-09-07 14:37 | 40 | 1:16 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R22090700255 | New_Event | Animals | Include | Include | Wildlife | 76 | 2022-09-07 | 3040 | keep | 0 | Sep | 2022 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-07 13:21 | 2022-09-07 18:08 | 9 | 4:47 | P | MAL TIEMPO/RAYOS | 3 X 65 Y 1 X 80 EN CORTE DE LINEA MAL TIEMPO RAYO | C22090700363 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 287 | 2022-09-07 | 2583 | keep | 0 | Sep | 2022 | 0.0017593 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2022-09-07 13:22 | 2022-09-07 14:40 | 1106 | 1:18 | P | DESGANCHE | SE ABRIO MACHETE AVE. DE DIEGO ESQ. EXPRESSO 22 DEL 1346-02 Y SE CERRO MACHETE PR- 21 FTE HOSPITA; ANTES LAS LOMAS 100% DEL 1529-15 Y 50% DE 1346-02 A LAS 14:40 CONTINUAN PATRULLANDO | S22090700409 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-09-07 | 86268 | keep | 0 | Sep | 2022 | 0.058757 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2022-09-07 13:22 | 2022-09-07 14:40 | 1622 | 1:18 | P | DESGANCHE | SE ABRIO MACHETE AVE. DE DIEGO ESQ. EXPRESSO 22 DEL 1346-02 Y SE CERRO MACHETE PR- 21 FTE HOSPITA; ANTES LAS LOMAS 100% DEL 1529-15 Y 50% DE 1346-02 A LAS 14:40 CONTINUAN PATRULLANDO | S22090700409 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-09-07 | 126516 | keep | 0 | Sep | 2022 | 0.086169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 13:26 | 2022-09-07 13:38 | 20 | 0:12 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYOS | B22090700380 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 12 | 2022-09-07 | 240 | keep | 0 | Sep | 2022 | 0.00016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-07 13:26 | 2022-09-07 13:27 | 222 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE 1907-03 LLEVANDO CARGA 1909-09 | S22090700382 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 222 | keep | 0 | Sep | 2022 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2022-09-07 13:26 | 2022-09-07 13:27 | 4456 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE 1907-03 LLEVANDO CARGA 1909-09 | S22090700382 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 4456 | keep | 0 | Sep | 2022 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2022-09-07 13:27 | 2022-09-07 13:35 | 10 | 0:08 | P | MAL TIEMPO/RAYOS | 3 X 100 EN C/L MAL TIEMPO RAYOS | S22090700304 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 8 | 2022-09-07 | 80 | keep | 0 | Sep | 2022 | 5.4488e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-07 13:27 | 2022-09-07 13:35 | 150 | 0:08 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | S22090700382 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 8 | 2022-09-07 | 1200 | keep | 0 | Sep | 2022 | 0.00081731 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-09-07 13:35 | 2022-09-07 13:36 | 222 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 1907-03 LLEVANDO CARGA 1909-09 EN SERVICO MAL TIEMPO RAYO | S22090700000 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 222 | keep | 0 | Sep | 2022 | 0.0001512 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 13:35 | 2022-09-07 13:36 | 4456 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR 1907-03 CARGA 1909-09 | B2303150000X | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 4456 | keep | 0 | Sep | 2022 | 0.003035 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 13:36 | 2022-09-07 13:37 | 2402 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECIERRE LLEVA 1720-10 | B22090700000 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2022-09-07 | 2402 | keep | 0 | Sep | 2022 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2022-09-07 13:36 | 2022-09-07 13:37 | 1 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECIERRE DEL 1709-02 LLEVANDO LA CARGA DEL 1720-08 | B22090700000 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2022-09-07 | 1 | keep | 0 | Sep | 2022 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-07 13:36 | 2022-09-07 15:48 | 10 | 2:12 | P | MAL TIEMPO/RAYOS | 3 X 100 EN C/L MAL TIEMPO RAYOS | S22090700304 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 132 | 2022-09-07 | 1320 | keep | 0 | Sep | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-07 13:36 | 2022-09-07 13:50 | 150 | 0:14 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | S22090700382 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 14 | 2022-09-07 | 2100 | keep | 0 | Sep | 2022 | 0.0014303 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-09-07 13:37 | 2022-09-07 14:06 | 726 | 0:29 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE ALIMENTADOR SE CERRO POR SCADA LLEVA 40% DE SU CARGA Y LLEVA 30% DEL 1346-03SE CERRO POR SCADA EN SERVICIO | S22090700390 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 29 | 2022-09-07 | 21054 | keep | 0 | Sep | 2022 | 0.01434 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2022-09-07 13:37 | 2022-09-07 14:06 | 738 | 0:29 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE ALIMENTADOR 1346-02 PROBO MALO LLEVA 40% DE SU CARGA Y LLEVA 30% DEL 1346-03 | S22090700390 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 29 | 2022-09-07 | 21402 | keep | 0 | Sep | 2022 | 0.014577 | 0.00050265 | Sustained | FALSE | FALSE | Not_TMED_Event | 738
SAN JUAN | 2022-09-07 13:38 | 2022-09-07 17:45 | 4 | 4:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | S22090700412 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 247 | 2022-09-07 | 988 | keep | 0 | Sep | 2022 | 0.00067292 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-09-07 13:38 | 2022-09-07 13:43 | 723 | 0:05 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1711-02 LLEVA CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA MAL TIEMPO RAYOS | B22090700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-09-07 | 3615 | keep | 0 | Sep | 2022 | 0.0024622 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-09-07 13:38 | 2022-09-07 13:43 | 198 | 0:05 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1711-02 LLEVA CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA MAL TIEMPO RAYOS | B22090700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-09-07 | 990 | keep | 0 | Sep | 2022 | 0.00067428 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-09-07 13:38 | 2022-09-07 13:43 | 1976 | 0:05 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1711-02 LLEVA CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA MAL TIEMPO RAYOS | B22090700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 5 | 2022-09-07 | 9880 | keep | 0 | Sep | 2022 | 0.0067292 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
CANOVANAS | 2022-09-07 13:39 | 2022-09-07 15:17 | 40 | 1:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | R22090700221 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 98 | 2022-09-07 | 3920 | keep | 0 | Sep | 2022 | 0.0026699 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 13:39 | 2022-09-07 15:23 | 164 | 1:44 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22090700213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2022-09-07 | 17056 | keep | 0 | Sep | 2022 | 0.011617 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2022-09-07 13:39 | 2022-09-07 13:44 | 1408 | 0:05 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1714-03 LLEVANDO 1714-02 SE CERRO POR SCADA RAYOS | B22090700215 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 5 | 2022-09-07 | 7040 | keep | 0 | Sep | 2022 | 0.0047949 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2022-09-07 13:39 | 2022-09-07 13:44 | 455 | 0:05 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR 1714-03 LLEVANDO 1714-02 SE CERRO POR SCADA RAYOS | B22090700215 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 5 | 2022-09-07 | 2275 | keep | 0 | Sep | 2022 | 0.0015495 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
CANOVANAS | 2022-09-07 13:40 | 2022-09-07 16:28 | 40 | 2:48 | P | CAUSAS EXTERNAS | ABRIO C/L PARA LIBERAR LINEA PRIMARIA DE POSTE SECUNDARIO PARTIDO X CAMION | R22090700266 | New_Event | Damage From Public | Include | Include | Public | 168 | 2022-09-07 | 6720 | keep | 0 | Sep | 2022 | 0.004577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-07 13:42 | 2022-09-07 15:51 | 150 | 2:09 | P | MAL TIEMPO/RAYOS | 2 X 80 Y 1 X 40 EN C/LS RAYOS | R22090700269 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 129 | 2022-09-07 | 19350 | keep | 0 | Sep | 2022 | 0.013179 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-09-07 13:43 | 2022-09-07 17:39 | 20 | 3:56 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO Y SE LEVANTO AEREO PROVISIONAL | B22090700337 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 236 | 2022-09-07 | 4720 | keep | 0 | Sep | 2022 | 0.0032148 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 13:43 | 2022-09-07 15:19 | 20 | 1:36 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYOS | B22090700380 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 96 | 2022-09-07 | 1920 | keep | 0 | Sep | 2022 | 0.0013077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 13:43 | 2022-09-07 18:46 | 80 | 5:03 | P | MAL TIEMPO/RAYOS | 2 X 80 EN C/L MAL TIEMPO RAYOS | S22090700395 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 303 | 2022-09-07 | 24240 | keep | 0 | Sep | 2022 | 0.01651 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-09-07 13:43 | 2022-09-07 13:57 | 1 | 0:14 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | R22090700270 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 14 | 2022-09-07 | 14 | keep | 0 | Sep | 2022 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-07 13:44 | 2022-09-07 17:04 | 50 | 3:20 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 2 X 40 EN C/L MAL TIEMPO RAYOS | B22090700231 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 200 | 2022-09-07 | 10000 | keep | 0 | Sep | 2022 | 0.006811 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-07 13:45 | 2022-09-07 17:00 | 100 | 3:15 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DEL AISLADOR | M22090700111 | New_Event | Primary Wire Break | Include | Include | Equipment | 195 | 2022-09-07 | 19500 | keep | 0 | Sep | 2022 | 0.013281 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-07 13:45 | 2022-09-07 14:40 | 100 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA REPARAR | M22090300063 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 55 | 2022-09-07 | 5500 | keep | 0 | Sep | 2022 | 0.003746 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 13:47 | 2022-09-07 13:55 | 80 | 0:08 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | B22090700222 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 8 | 2022-09-07 | 640 | keep | 0 | Sep | 2022 | 0.0004359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2022-09-07 13:47 | 2022-09-07 18:35 | 55 | 4:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P22090700266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2022-09-07 | 15840 | keep | 0 | Sep | 2022 | 0.010789 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
GUAYAMA | 2022-09-07 13:47 | 2022-09-07 14:49 | 8 | 1:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA AVERIADA | P22090700267 | New_Event | Secondary Wire Break | Include | Include | Equipment | 62 | 2022-09-07 | 496 | keep | 0 | Sep | 2022 | 0.00033782 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-07 13:48 | 2022-09-07 16:00 | 3 | 2:12 | P | DESGANCHE | 1 X 50 EN C/L | R22090700278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2022-09-07 | 396 | keep | 0 | Sep | 2022 | 0.00026971 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2022-09-07 13:52 | 2022-09-07 16:33 | 15 | 2:41 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR REMPLAZAR XMR QUEMADO X RAYO 75 KVA X 75 KVA | R22090700282 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 161 | 2022-09-07 | 2415 | keep | 0 | Sep | 2022 | 0.0016448 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2022-09-07 13:59 | 2022-09-07 15:04 | 30 | 1:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L FUERTES LLUVIAS | R22090700291 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 65 | 2022-09-07 | 1950 | keep | 0 | Sep | 2022 | 0.0013281 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-07 14:01 | 2022-09-07 16:44 | 14 | 2:43 | P | SECUNDARIA/DESGANCHE | SE DESGANCHO SECUNDARIA Y SE REPUSO 1 X 10 EN XMR | B22090700212 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 163 | 2022-09-07 | 2282 | keep | 0 | Sep | 2022 | 0.0015543 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2022-09-07 14:01 | 2022-09-07 17:12 | 65 | 3:11 | P | DESGANCHE | 3 X 80 EN C/L DESGANCHE | B22090700230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2022-09-07 | 12415 | keep | 0 | Sep | 2022 | 0.0084558 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-09-07 14:03 | 2022-09-07 15:08 | 3597 | 1:05 | T | DESGANCHE | DISPARO DE BKR SE REALIZO DESGANCHE CON VARETA Y SE CERRO POR CONTROL | B22090700232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2022-09-07 | 233805 | keep | 0 | Sep | 2022 | 0.15924 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2022-09-07 14:06 | 2022-09-07 21:44 | 90 | 7:38 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | B22090700292 | New_Event | Vegetation Contact | Include | Include | Vegetation | 458 | 2022-09-07 | 41220 | keep | 0 | Sep | 2022 | 0.028075 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-09-07 14:06 | 2022-09-07 20:31 | 100 | 6:25 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22090700233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 385 | 2022-09-07 | 38500 | keep | 0 | Sep | 2022 | 0.026222 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-07 14:10 | 2022-09-07 17:26 | 80 | 3:16 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO RAYOS | B22090700241 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 196 | 2022-09-07 | 15680 | keep | 0 | Sep | 2022 | 0.01068 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-07 14:11 | 2022-09-07 14:12 | 5252 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE MAL TIEMPO RAYOS | B22090700244 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-07 | 5252 | keep | 0 | Sep | 2022 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2022-09-07 14:11 | 2022-09-07 14:12 | 1210 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE MAL TIEMPO RAYOS | B22090700244 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 1210 | keep | 0 | Sep | 2022 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2022-09-07 14:12 | 2022-09-07 17:52 | 1 | 3:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE LINEA A CAJA EN RISER | B22090700427 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 220 | 2022-09-07 | 220 | keep | 0 | Sep | 2022 | 0.00014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-09-07 14:12 | 2022-09-07 16:18 | 50 | 2:06 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA SAFADA DEL AISLADOR | A22090700099 | New_Event | Primary Wire Break | Include | Include | Equipment | 126 | 2022-09-07 | 6300 | keep | 0 | Sep | 2022 | 0.0042909 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-09-07 14:18 | 2022-09-07 14:19 | 2132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR CARGA POR 8801-03 | A22090700151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 2132 | keep | 0 | Sep | 2022 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-07 14:18 | 2022-09-07 14:19 | 1976 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR LLEVA CARGA DE 8801-01 | A22090700151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 1976 | keep | 0 | Sep | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
UTUADO | 2022-09-07 14:19 | 2022-09-07 16:00 | 120 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22090700103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2022-09-07 | 12120 | keep | 0 | Sep | 2022 | 0.0082549 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-09-07 14:20 | 2022-09-07 14:36 | 1067 | 0:16 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE AVERIADO | C22090700167 | Partial_restoration | Switch Failure | Include | Include | Equipment | 16 | 2022-09-07 | 17072 | keep | 0 | Sep | 2022 | 0.011628 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 14:21 | 2022-09-07 14:22 | 1070 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE MAL TIEMPO RAYOS | B22090700000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 1070 | keep | 0 | Sep | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
VEGA BAJA | 2022-09-07 14:22 | 2022-09-07 14:26 | 80 | 0:04 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | A22090700118 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 4 | 2022-09-07 | 320 | keep | 0 | Sep | 2022 | 0.00021795 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-07 14:23 | 2022-09-07 17:19 | 60 | 2:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | S22090700442 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2022-09-07 | 10560 | keep | 0 | Sep | 2022 | 0.0071924 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 2791 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36100 | A22090700115 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 2791 | keep | 0 | Sep | 2022 | 0.0019009 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 1464 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36100 | A22090700115 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1464 | keep | 0 | Sep | 2022 | 0.00099712 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 759 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 36100 | A22090700115 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 759 | keep | 0 | Sep | 2022 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 1500 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36100 | A22090700115 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1500 | keep | 0 | Sep | 2022 | 0.0010216 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 2132 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36100 CARGA POR 8801-03 | A22090700114 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 2132 | keep | 0 | Sep | 2022 | 0.0014521 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 2366 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36100 | A22090700114 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 2366 | keep | 0 | Sep | 2022 | 0.0016115 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 1976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 36100 LLEVA CARGA DE 8801-01 | A22090700114 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1976 | keep | 0 | Sep | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-09-07 14:26 | 2022-09-07 14:27 | 3688 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERE DE LINEA 36100 | A22090700114 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 3688 | keep | 0 | Sep | 2022 | 0.0025119 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700265 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 3070 | keep | 0 | Sep | 2022 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700265 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 2735 | keep | 0 | Sep | 2022 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700265 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1070 | keep | 0 | Sep | 2022 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700270 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1647 | keep | 0 | Sep | 2022 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700270 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 3295 | keep | 0 | Sep | 2022 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700270 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1180 | keep | 0 | Sep | 2022 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700273 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 320 | keep | 0 | Sep | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2022-09-07 14:26 | 2022-09-07 14:27 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | B22090700273 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 2234 | keep | 0 | Sep | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
VEGA BAJA | 2022-09-07 14:27 | 2022-09-07 21:35 | 20 | 7:08 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | A22090700108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 428 | 2022-09-07 | 8560 | keep | 0 | Sep | 2022 | 0.0058302 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-07 14:27 | 2022-09-07 16:23 | 80 | 1:56 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | A22090700118 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 116 | 2022-09-07 | 9280 | keep | 0 | Sep | 2022 | 0.0063206 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2022-09-07 14:28 | 2022-09-07 14:29 | 619 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL INTERRUPTOR | A22090700152 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2022-09-07 | 619 | keep | 0 | Sep | 2022 | 0.0004216 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
SAN JUAN | 2022-09-07 14:29 | 2022-09-07 18:45 | 100 | 4:16 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA RAYOS | S22090700447 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 256 | 2022-09-07 | 25600 | keep | 0 | Sep | 2022 | 0.017436 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-09-07 14:30 | 2022-09-07 15:06 | 1807 | 0:36 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO BAJANTE PRIMARIO PARTIDO Y DISCOS ROTOS ENTRO 50% EN SERVICIO | R22090700254 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 36 | 2022-09-07 | 65052 | keep | 0 | Sep | 2022 | 0.044307 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2022-09-07 14:31 | 2022-09-07 14:32 | 619 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DEL INTERRUPTOR | A22090700153 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2022-09-07 | 619 | keep | 0 | Sep | 2022 | 0.0004216 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2022-09-07 14:32 | 2022-09-07 17:54 | 75 | 3:22 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES QUEMADOS | A22090700164 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 202 | 2022-09-07 | 15150 | keep | 0 | Sep | 2022 | 0.010319 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2022-09-07 14:33 | 2022-09-07 18:24 | 6 | 3:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR, SE REMPLAZO CAJA Y SE REPARO SECUNDARIA | S22090700450 | New_Event | Cutout Failure | Include | Include | Equipment | 231 | 2022-09-07 | 1386 | keep | 0 | Sep | 2022 | 0.000944 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-09-07 14:36 | 2022-09-07 14:42 | 2900 | 0:06 | T | EXCAVACIONES | DISPARO DE BKR POR AVERRIA SOTERRADA CAUSADO POR CONTRATISTA EXTERNO | C22090700167 | New_Event | Excavation | Include | Include | Public | 6 | 2022-09-07 | 17400 | keep | 0 | Sep | 2022 | 0.011851 | 0.0019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 2900
ARECIBO | 2022-09-07 14:39 | 2022-09-07 17:21 | 70 | 2:42 | P | ARBOL SOBRE LINEA | 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LA LINEA | A22090700120 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 162 | 2022-09-07 | 11340 | keep | 0 | Sep | 2022 | 0.0077236 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2022-09-07 14:40 | 2022-09-07 15:31 | 553 | 0:51 | P | DESGANCHE | SE RETIRO RAMA FRENTE A LA PANADERIA LA HACIRENDA Y SE CERRO MACHETE ENTRO EL 50% EN SERVICIO | S22090700409 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 51 | 2022-09-07 | 28203 | keep | 0 | Sep | 2022 | 0.019209 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-07 14:40 | 2022-09-07 14:57 | 2 | 0:17 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYOS | R22090700318 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 17 | 2022-09-07 | 34 | keep | 0 | Sep | 2022 | 2.3157e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
UTUADO | 2022-09-07 14:40 | 2022-09-07 15:41 | 1 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES SECUNDARIAS | A22090700123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2022-09-07 | 61 | keep | 0 | Sep | 2022 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-07 14:42 | 2022-09-07 14:59 | 1067 | 0:17 | P | EXCAVACIONES | SE SECCIONALIZO MACHETE AVERRIADO | C22090700167 | Partial_restoration | Excavation | Include | Include | Public | 17 | 2022-09-07 | 18139 | keep | 0 | Sep | 2022 | 0.012354 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 14:42 | 2022-09-07 20:20 | 175 | 5:38 | P | MAL TIEMPO/RAYOS | 3 X 80 EN CORTES DE LINEA Y 3 X 15 EN TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A22090700124 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 338 | 2022-09-07 | 59150 | keep | 0 | Sep | 2022 | 0.040287 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
VEGA BAJA | 2022-09-07 14:43 | 2022-09-07 14:44 | 1310 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE MAL TIEMPO RAYOS | B22090700000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-07 | 1310 | keep | 0 | Sep | 2022 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2022-09-07 14:45 | 2022-09-07 18:34 | 20 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR Y 1 X 40 EN C/L RAYO | B22090700301 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2022-09-07 | 4580 | keep | 0 | Sep | 2022 | 0.0031194 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-07 14:46 | 2022-09-07 19:40 | 12 | 4:54 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REPARO BAJANTE SECUNDARIO Y SE DESGANCHO | S22090700462 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 294 | 2022-09-07 | 3528 | keep | 0 | Sep | 2022 | 0.0024029 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-09-07 14:49 | 2022-09-07 17:49 | 50 | 3:00 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | S22090700467 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2022-09-07 | 9000 | keep | 0 | Sep | 2022 | 0.0061299 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2022-09-07 14:55 | 2022-09-07 17:40 | 10 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090700134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2022-09-07 | 1650 | keep | 0 | Sep | 2022 | 0.0011238 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-07 14:55 | 2022-09-07 17:21 | 5 | 2:26 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | B22090700311 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 146 | 2022-09-07 | 730 | keep | 0 | Sep | 2022 | 0.0004972 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-09-07 14:59 | 2022-09-08 14:09 | 4 | 23:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50KVA | S22090700475 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1390 | 2022-09-07 | 5560 | keep | 0 | Sep | 2022 | 0.0037869 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-07 14:59 | 2022-09-07 19:38 | 80 | 4:39 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA RAYOS | S22090700476 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 279 | 2022-09-07 | 22320 | keep | 0 | Sep | 2022 | 0.015202 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-09-07 14:59 | 2022-09-07 15:21 | 2900 | 0:22 | T | EXCAVACIONES | SE DISPARO BKR POR AVERIA SOTERRADA | C22090700167 | Additional_clients | Excavation | Include | Include | Public | 22 | 2022-09-07 | 63800 | keep | 0 | Sep | 2022 | 0.043454 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-07 15:00 | 2022-09-07 16:30 | 16 | 1:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TRANSFORMADOR CON ESCAPE DE ACEITE 75 KVA X 75 KVA | M22090700113 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2022-09-07 | 1440 | keep | 0 | Sep | 2022 | 0.00098078 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-09-07 15:00 | 2022-09-07 16:46 | 20 | 1:46 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L MAL TIEMPO RAYOS | B22090700317 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 106 | 2022-09-07 | 2120 | keep | 0 | Sep | 2022 | 0.0014439 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-07 15:01 | 2022-09-07 16:42 | 327 | 1:41 | T | DESGANCHE | RECERRO INTERRUPTOR SE DEJO FUERA, HIZO LAS TRES OPERACIONES. SE RETIRO RAMA DE LA LINEA CON VARETA CERRADO POR CONTROL | C22090700351 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-09-07 | 33027 | keep | 0 | Sep | 2022 | 0.022495 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
BAYAMON | 2022-09-07 15:01 | 2022-09-07 18:04 | 106 | 3:03 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B22090700321 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2022-09-07 | 19398 | keep | 0 | Sep | 2022 | 0.013212 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
CANOVANAS | 2022-09-07 15:06 | 2022-09-07 16:25 | 1506 | 1:19 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE PRIMARIO PARTIDO Y DISCOS ROTOS ENTRO 100% EN SERVICIO | R22090700254 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 79 | 2022-09-07 | 118974 | keep | 0 | Sep | 2022 | 0.081033 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-07 15:07 | 2022-09-07 18:01 | 2 | 2:54 | P | DESGANCHE | 1 X 10 EN TRANSFORMAOR SE REEMPLAZO PORTAFUSIBLE Y SE DESGANCHO | C22090700356 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-09-07 | 348 | keep | 0 | Sep | 2022 | 0.00023702 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-09-07 15:10 | 2022-09-07 16:52 | 30 | 1:42 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR Y 1 X 30 EN C/L MAL TIEMPO RAYOS | B22090700333 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2022-09-07 | 3060 | keep | 0 | Sep | 2022 | 0.0020842 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-09-07 15:12 | 2022-09-07 18:20 | 170 | 3:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 30 Y 2 X 50 EN CORTE DE LINEA Y 4 X 15 EN TRANSFORMADOR | A22090700146 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 188 | 2022-09-07 | 31960 | keep | 0 | Sep | 2022 | 0.021768 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
AGUADILLA | 2022-09-07 15:15 | 2022-09-07 16:12 | 30 | 0:57 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M22090700150 | New_Event | Animals | Include | Include | Wildlife | 57 | 2022-09-07 | 1710 | keep | 0 | Sep | 2022 | 0.0011647 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2022-09-07 15:18 | 2022-09-07 15:20 | 1131 | 0:02 | T | ERROR HUMANO | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA, PERSONAL TRABAJANDO CAUSO DISPARO SE CERRO POR CONTROL | C22090700366 | New_Event | Human Error | Include | Include | Other | 2 | 2022-09-07 | 2262 | keep | 0 | Sep | 2022 | 0.0015406 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
BARRANQUITAS | 2022-09-07 15:20 | 2022-09-07 16:56 | 9 | 1:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C22090700302 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 96 | 2022-09-07 | 864 | keep | 0 | Sep | 2022 | 0.00058847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-07 15:21 | 2022-09-07 16:08 | 1750 | 0:47 | P | EXCAVACIONES | SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA SOTERRADA | C22090700167 | Partial_restoration | Excavation | Include | Include | Public | 47 | 2022-09-07 | 82250 | keep | 0 | Sep | 2022 | 0.05602 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 15:25 | 2022-09-08 11:15 | 2 | 19:50 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADORES DIFERENTES MAL TIEMPO DESCARGAS ELECTRICAS | A22090700157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1190 | 2022-09-07 | 2380 | keep | 0 | Sep | 2022 | 0.001621 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-09-07 15:25 | 2022-09-07 17:23 | 100 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | A22090700158 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2022-09-07 | 11800 | keep | 0 | Sep | 2022 | 0.0080369 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-07 15:26 | 2022-09-07 20:06 | 6 | 4:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BARRAS EN PEDESTAL | B22090600112 | New_Event | Secondary Wire Break | Include | Include | Equipment | 280 | 2022-09-07 | 1680 | keep | 0 | Sep | 2022 | 0.0011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2022-09-07 15:27 | 2022-09-07 16:45 | 80 | 1:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22090700152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-09-07 | 6240 | keep | 0 | Sep | 2022 | 0.00425 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-09-07 15:27 | 2022-09-07 18:15 | 50 | 2:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090700153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2022-09-07 | 8400 | keep | 0 | Sep | 2022 | 0.0057212 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-07 15:29 | 2022-09-07 19:19 | 69 | 3:50 | P | DESGANCHE | DESGANCHE 1 X 15 EN XMR Y 1 X 50 EN C/L | B22090700347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 230 | 2022-09-07 | 15870 | keep | 0 | Sep | 2022 | 0.010809 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
CANOVANAS | 2022-09-07 15:31 | 2022-09-08 09:20 | 6 | 17:49 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | R22090700348 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1069 | 2022-09-07 | 6414 | keep | 0 | Sep | 2022 | 0.0043685 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-09-07 15:31 | 2022-09-07 21:07 | 6 | 5:36 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22090700165 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 336 | 2022-09-07 | 2016 | keep | 0 | Sep | 2022 | 0.0013731 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-09-07 15:32 | 2022-09-07 17:30 | 2 | 1:58 | P | DESGANCHE | 1 X 20 EN MONTURA TRIFASICA SE RETIRO ENREDADERA | P22090700300 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-09-07 | 236 | keep | 0 | Sep | 2022 | 0.00016074 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-09-07 15:33 | 2022-09-07 16:51 | 14 | 1:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO XMR Y SE LE INSTALO CAJA PRIMARIA A XMR AUTO PROTEGIDO COMO MEDIDA DE PROTECCION | B22090700352 | New_Event | Secondary Wire Break | Include | Include | Equipment | 78 | 2022-09-07 | 1092 | keep | 0 | Sep | 2022 | 0.00074376 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2022-09-07 15:38 | 2022-09-07 17:11 | 60 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090700167 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2022-09-07 | 5580 | keep | 0 | Sep | 2022 | 0.0038005 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-07 15:41 | 2022-09-08 10:15 | 54 | 18:34 | P | DESGANCHE | 1 X 100 1 X 80 EN C/L DESGANCHE SE RETEZO LINEA Y SE REMPLAZO AISLADOR | B22090700360 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1114 | 2022-09-07 | 60156 | keep | 0 | Sep | 2022 | 0.040972 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
FAJARDO | 2022-09-07 15:47 | 2022-09-07 18:56 | 4 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR LLUVIAS | R22090700355 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2022-09-07 | 756 | keep | 0 | Sep | 2022 | 0.00051491 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2022-09-07 15:48 | 2022-09-07 15:49 | 1253 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090700163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1253 | keep | 0 | Sep | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-09-07 15:48 | 2022-09-07 15:49 | 1266 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090700163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1266 | keep | 0 | Sep | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-09-07 15:48 | 2022-09-07 15:49 | 411 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090700163 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 411 | keep | 0 | Sep | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2022-09-07 15:48 | 2022-09-07 15:49 | 1617 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22090700164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1617 | keep | 0 | Sep | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-09-07 15:48 | 2022-09-07 15:49 | 1017 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22090700164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 1017 | keep | 0 | Sep | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-09-07 15:48 | 2022-09-07 15:49 | 828 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERE DE LINEA 2000 | M22090700164 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 828 | keep | 0 | Sep | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-09-07 15:48 | 2022-09-07 15:49 | 974 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090700166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-07 | 974 | keep | 0 | Sep | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
BARRANQUITAS | 2022-09-07 15:51 | 2022-09-08 06:38 | 37 | 14:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C22090700387 | New_Event | Vegetation Contact | Include | Include | Vegetation | 887 | 2022-09-07 | 32819 | keep | 0 | Sep | 2022 | 0.022353 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2022-09-07 15:54 | 2022-09-07 16:22 | 353 | 0:28 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR PARA CERRAR PUENTE PRIMARIO | S22090700517 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 28 | 2022-09-07 | 9884 | keep | 0 | Sep | 2022 | 0.0067319 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-07 15:58 | 2022-09-07 21:51 | 40 | 5:53 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L SE SECCIONALIZO TRANSFORMADOR QUEMADO POR RAYO | R22090700362 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 353 | 2022-09-07 | 14120 | keep | 0 | Sep | 2022 | 0.0096171 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-07 15:59 | 2022-09-07 19:48 | 7 | 3:49 | P | MAL TIEMPO/RAYOS | 2 X 15 EN XMR MAL TIEMPO RAYO | B22090700380 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2022-09-07 | 1603 | keep | 0 | Sep | 2022 | 0.0010918 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2022-09-07 16:02 | 2022-09-08 10:29 | 8 | 18:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | C22090700393 | New_Event | Cutout Failure | Include | Include | Equipment | 1107 | 2022-09-07 | 8856 | keep | 0 | Sep | 2022 | 0.0060318 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2022-09-07 16:03 | 2022-09-07 17:15 | 70 | 1:12 | P | DESGANCHE | 1 X 30 // 1 X 100 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090700138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2022-09-07 | 5040 | keep | 0 | Sep | 2022 | 0.0034327 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2022-09-07 16:05 | 2022-09-07 17:33 | 80 | 1:28 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22090700385 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2022-09-07 | 7040 | keep | 0 | Sep | 2022 | 0.0047949 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2022-09-07 16:08 | 2022-09-07 17:10 | 1123 | 1:02 | P | EXCAVACIONES | SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA SOTERRADA | C22090700167 | Partial_restoration | Excavation | Include | Include | Public | 62 | 2022-09-07 | 69626 | keep | 0 | Sep | 2022 | 0.047422 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-07 16:09 | 2022-09-07 18:42 | 80 | 2:33 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090700180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 153 | 2022-09-07 | 12240 | keep | 0 | Sep | 2022 | 0.0083366 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2022-09-07 16:12 | 2022-09-07 17:15 | 5 | 1:03 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYO | R22090700368 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 63 | 2022-09-07 | 315 | keep | 0 | Sep | 2022 | 0.00021455 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-09-07 16:21 | 2022-09-07 17:25 | 50 | 1:04 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PALOMA CRUZO FASE | P22090700308 | New_Event | Animals | Include | Include | Wildlife | 64 | 2022-09-07 | 3200 | keep | 0 | Sep | 2022 | 0.0021795 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-09-07 16:27 | 2022-09-08 09:15 | 150 | 16:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | M22090700175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1008 | 2022-09-07 | 151200 | keep | 0 | Sep | 2022 | 0.10298 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2022-09-07 16:28 | 2022-09-07 18:15 | 40 | 1:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22090700176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2022-09-07 | 4280 | keep | 0 | Sep | 2022 | 0.0029151 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-07 16:36 | 2022-09-07 17:09 | 5 | 0:33 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y SE REALIZO DESGANCHE SECUNDARIO | B22090700131 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 33 | 2022-09-07 | 165 | keep | 0 | Sep | 2022 | 0.00011238 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-09-07 16:44 | 2022-09-07 18:16 | 84 | 1:32 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYOS | B22090700409 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 92 | 2022-09-07 | 7728 | keep | 0 | Sep | 2022 | 0.0052635 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
FAJARDO | 2022-09-07 16:49 | 2022-09-07 18:04 | 65 | 1:15 | P | MAL TIEMPO/RAYOS | 1 X 30 Y 1 X 40 EN C/LS RAYOS | R22090700375 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2022-09-07 | 4875 | keep | 0 | Sep | 2022 | 0.0033203 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-09-07 16:50 | 2022-09-07 17:30 | 15 | 0:40 | P | MAL TIEMPO/RAYOS | 1 X 25 EN C/L MAL TIEMPO RAYOS | B22090700208 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 40 | 2022-09-07 | 600 | keep | 0 | Sep | 2022 | 0.00040866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-07 16:57 | 2022-09-07 19:00 | 30 | 2:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN RISER LLUVIAS | R22090700377 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 123 | 2022-09-07 | 3690 | keep | 0 | Sep | 2022 | 0.0025132 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-07 17:02 | 2022-09-07 19:15 | 44 | 2:13 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 25 EN C/L RAYOS | B22090700419 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 133 | 2022-09-07 | 5852 | keep | 0 | Sep | 2022 | 0.0039858 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2022-09-07 17:03 | 2022-09-07 19:31 | 119 | 2:28 | P | DESGANCHE | 1 X 50 EN C/L SE RETIRO RAMA SOBRE LINEA | B22090700420 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-09-07 | 17612 | keep | 0 | Sep | 2022 | 0.011995 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
BAYAMON | 2022-09-07 17:07 | 2022-09-07 17:08 | 3438 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE MAL TIEMPO LLUVIAS | B22090700421 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-07 | 3438 | keep | 0 | Sep | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
CAGUAS | 2022-09-07 17:10 | 2022-09-07 17:38 | 1123 | 0:28 | P | EXCAVACIONES | SE DEJO AVERRIA SOTERRADA SECCIONALIZADA Y SE TRANSFIRIO LA CARGA AL CONVERTIDOR DEL 3301-01 100% EN SERVICIO | C22090700167 | Partial_restoration | Excavation | Include | Include | Public | 28 | 2022-09-07 | 31444 | keep | 0 | Sep | 2022 | 0.021416 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-07 17:13 | 2022-09-07 18:15 | 4 | 1:02 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | B22090700426 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 62 | 2022-09-07 | 248 | keep | 0 | Sep | 2022 | 0.00016891 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2022-09-07 17:15 | 2022-09-07 20:00 | 120 | 2:45 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA Y SE REALIZO DESGANCHE | A22090700208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2022-09-07 | 19800 | keep | 0 | Sep | 2022 | 0.013486 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2022-09-07 17:16 | 2022-09-07 19:30 | 35 | 2:14 | P | ARBOL SOBRE LINEA | SE RETEZO LINEA PRIMARIA Y SE REMOVIO ARBOL SOBRE LAS LINEAS | A22090700211 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 134 | 2022-09-07 | 4690 | keep | 0 | Sep | 2022 | 0.0031943 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2022-09-07 17:20 | 2022-09-07 18:01 | 20 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETE PARA REPARAR PUENTE Y FIJAR LINEA FTE. INTERAMERICANA | S22090700444 | New_Event | Primary Wire Break | Include | Include | Equipment | 41 | 2022-09-07 | 820 | keep | 0 | Sep | 2022 | 0.0005585 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2022-09-07 17:24 | 2022-09-07 21:10 | 8 | 3:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M22090700191 | New_Event | Primary Wire Break | Include | Include | Equipment | 226 | 2022-09-07 | 1808 | keep | 0 | Sep | 2022 | 0.0012314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-07 17:28 | 2022-09-07 19:42 | 30 | 2:14 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN XMR DESGANCHE | R22090700382 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 134 | 2022-09-07 | 4020 | keep | 0 | Sep | 2022 | 0.002738 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-07 17:31 | 2022-09-07 20:07 | 15 | 2:36 | P | DESGANCHE | DESGANCHE Y 1 X 40 EN C/L | B22090700438 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2022-09-07 | 2340 | keep | 0 | Sep | 2022 | 0.0015938 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-09-07 17:35 | 2022-09-07 19:15 | 25 | 1:40 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR IGUANA | C22090700418 | New_Event | Animals | Include | Include | Wildlife | 100 | 2022-09-07 | 2500 | keep | 0 | Sep | 2022 | 0.0017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2022-09-07 17:51 | 2022-09-07 20:09 | 1650 | 2:18 | T | MAL TIEMPO/RAYOS | DISPARO DE ALIMENTADOR POR FUERTE LLUVIA Y DESCARGAS ELECTRICAS EN EL AREA | P22090700326 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 138 | 2022-09-07 | 227700 | keep | 0 | Sep | 2022 | 0.15509 | 0.0011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 1650
CANOVANAS | 2022-09-07 17:53 | 2022-09-07 20:36 | 7 | 2:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN XMR SE REMPLAZO CAJA PARTIDA | R22090700386 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2022-09-07 | 1141 | keep | 0 | Sep | 2022 | 0.00077713 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-09-07 17:53 | 2022-09-07 20:51 | 25 | 2:58 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO TRAMO AVERIADO POR POSTE PARTIDO PARA TRABAJAR EN PROXIMO DIA | A22090700221 | New_Event | Primary Pole Failure | Include | Include | Equipment | 178 | 2022-09-07 | 4450 | keep | 0 | Sep | 2022 | 0.0030309 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2022-09-07 17:54 | 2022-09-07 19:01 | 619 | 1:07 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR PARA REEMPLAZO DE MACHETES SE CERRO POR SCADA | A22090700222 | Additional_clients | Switch Failure | Include | Include | Equipment | 67 | 2022-09-07 | 41473 | keep | 0 | Sep | 2022 | 0.028247 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-07 18:00 | 2022-09-07 19:25 | 8 | 1:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | M22090700203 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-09-07 | 680 | keep | 0 | Sep | 2022 | 0.00046314 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-07 18:12 | 2022-09-08 11:10 | 50 | 16:58 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 37.5KVA | M22090700205 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1018 | 2022-09-07 | 50900 | keep | 0 | Sep | 2022 | 0.034668 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-07 18:14 | 2022-09-07 19:17 | 10 | 1:03 | P | MAL TIEMPO/RAYOS | 2 X 40 EN C/L MAL TIEMPO RAYOS | B22090700458 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 63 | 2022-09-07 | 630 | keep | 0 | Sep | 2022 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-09-07 18:28 | 2022-09-08 10:09 | 8 | 15:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR TOMAS EN PEDESTAL | R22090700391 | New_Event | Secondary Wire Break | Include | Include | Equipment | 941 | 2022-09-07 | 7528 | keep | 0 | Sep | 2022 | 0.0051273 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2022-09-07 18:28 | 2022-09-07 18:39 | 1 | 0:11 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 25 AMP | C22090700428 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2022-09-07 | 11 | keep | 0 | Sep | 2022 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-07 18:28 | 2022-09-07 20:17 | 11 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO PORTAFUSIBLE | B22090700461 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2022-09-07 | 1199 | keep | 0 | Sep | 2022 | 0.00081663 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2022-09-07 18:30 | 2022-09-07 20:46 | 4 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA EN PEDESTAL | R22090700394 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2022-09-07 | 544 | keep | 0 | Sep | 2022 | 0.00037052 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2022-09-07 18:34 | 2022-09-08 11:00 | 25 | 16:26 | P | DESGANCHE | 1 X 40 EN C/L Y 1 X 15 EN XMR DESGANCHE | R22090700394 | New_Event | Vegetation Contact | Include | Include | Vegetation | 986 | 2022-09-07 | 24650 | keep | 0 | Sep | 2022 | 0.016789 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2022-09-07 18:40 | 2022-09-08 11:01 | 100 | 16:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 50 EN CORTE DE LINEA | P22090700344 | New_Event | Cutout Failure | Include | Include | Equipment | 981 | 2022-09-07 | 98100 | keep | 0 | Sep | 2022 | 0.066815 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-09-07 18:46 | 2022-09-07 19:16 | 9 | 0:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN XMR FUERTES LLUVIAS | R22090700397 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 30 | 2022-09-07 | 270 | keep | 0 | Sep | 2022 | 0.0001839 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2022-09-07 18:47 | 2022-09-07 23:50 | 74 | 5:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22090700349 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2022-09-07 | 22422 | keep | 0 | Sep | 2022 | 0.015272 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
HUMACAO | 2022-09-07 18:48 | 2022-09-07 20:50 | 6 | 2:02 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | C22090700433 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 122 | 2022-09-07 | 732 | keep | 0 | Sep | 2022 | 0.00049856 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-09-07 18:49 | 2022-09-08 11:35 | 150 | 16:46 | P | DESGANCHE | SE HIZO DESGANCHE Y SE CERRARON PUENTES EN PRIMARIA | P22090700350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1006 | 2022-09-07 | 150900 | keep | 0 | Sep | 2022 | 0.10278 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2022-09-07 18:51 | 2022-09-08 07:30 | 188 | 12:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22090700434 | New_Event | Vegetation Contact | Include | Include | Vegetation | 759 | 2022-09-07 | 142692 | keep | 0 | Sep | 2022 | 0.097187 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
BAYAMON | 2022-09-07 19:04 | 2022-09-07 20:37 | 16 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN RISER A TRANSFORMADOR LLUVIAS | B22090700471 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2022-09-07 | 1488 | keep | 0 | Sep | 2022 | 0.0010135 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2022-09-07 19:09 | 2022-09-07 20:40 | 8 | 1:31 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | B22090700473 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-09-07 | 728 | keep | 0 | Sep | 2022 | 0.00049584 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-07 19:19 | 2022-09-07 20:43 | 7 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR FUERTES LLUVIAS | R22090700404 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2022-09-07 | 588 | keep | 0 | Sep | 2022 | 0.00040048 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-09-07 19:58 | 2022-09-08 19:58 | 50 | 24:00 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE HIZO DESGANCHE Y SE INSTALO RIGIDO | S22090700581 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1440 | 2022-09-07 | 72000 | keep | 0 | Sep | 2022 | 0.049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-09-07 20:01 | 2022-09-07 22:52 | 100 | 2:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22090700232 | New_Event | Cutout Failure | Include | Include | Equipment | 171 | 2022-09-07 | 17100 | keep | 0 | Sep | 2022 | 0.011647 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-09-07 20:07 | 2022-09-07 23:45 | 150 | 3:38 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | P22090700389 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2022-09-07 | 32700 | keep | 0 | Sep | 2022 | 0.022272 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-09-07 20:07 | 2022-09-07 20:50 | 110 | 0:43 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR DESGANCHE | P22090700390 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-09-07 | 4730 | keep | 0 | Sep | 2022 | 0.0032216 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
GUAYAMA | 2022-09-07 20:21 | 2022-09-08 12:44 | 1 | 16:23 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22090700393 | New_Event | Vegetation Contact | Include | Include | Vegetation | 983 | 2022-09-07 | 983 | keep | 0 | Sep | 2022 | 0.00066952 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2022-09-07 20:31 | 2022-09-07 21:11 | 43 | 0:40 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P22090700395 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2022-09-07 | 1720 | keep | 0 | Sep | 2022 | 0.0011715 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2022-09-07 20:53 | 2022-09-08 12:36 | 61 | 15:43 | P | DESGANCHE | 2 X 50 EN C/L SE EALIZO DESGANCHE | B22090700495 | New_Event | Vegetation Contact | Include | Include | Vegetation | 943 | 2022-09-07 | 57523 | keep | 0 | Sep | 2022 | 0.039179 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2022-09-07 20:58 | 2022-09-07 21:00 | 2891 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R22090700418 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-07 | 5782 | keep | 0 | Sep | 2022 | 0.0039381 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
VEGA BAJA | 2022-09-07 21:07 | 2022-09-08 13:10 | 6 | 16:03 | P | MAL TIEMPO/RAYOS | TRANSFORMADOR AVERIADO DE 25 KVA POR 25 KVA | A22090700165 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 963 | 2022-09-07 | 5778 | keep | 0 | Sep | 2022 | 0.0039354 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-09-07 21:22 | 2022-09-07 22:37 | 100 | 1:15 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | M22090700265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2022-09-07 | 7500 | keep | 0 | Sep | 2022 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-09-07 21:48 | 2022-09-07 21:49 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22090700422 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-07 | 4188 | keep | 0 | Sep | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
BARRANQUITAS | 2022-09-07 21:49 | 2022-09-08 17:20 | 8 | 19:31 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE, SE LEVANTO ALAMBRE NEUTRAL Y DOS CAJAS PRIMARIA DE TRANSFORMADORES | C22090700499 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1171 | 2022-09-07 | 9368 | keep | 0 | Sep | 2022 | 0.0063805 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-07 21:51 | 2022-09-08 11:36 | 4 | 13:45 | P | MAL TIEMPO/RAYOS | SE REMPLAZO XMR AVERIADO POR RAYO DE 25 KVA X 25 KVA | R22090700362 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 825 | 2022-09-07 | 3300 | keep | 0 | Sep | 2022 | 0.0022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-07 21:57 | 2022-09-08 06:05 | 500 | 8:08 | P | CABLE SOTERRADO AVERIADO | 1 X 200 EN CORTE DE LINEA POR SOBRECARGA LLEVA LA CARGA DEL 3103-04 POR AVERIA EN RISER DEL TRONCAL | C22090700498 | New_Event | UG Cable Fault | Include | Include | Equipment | 488 | 2022-09-07 | 244000 | keep | 0 | Sep | 2022 | 0.16619 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
VEGA BAJA | 2022-09-07 21:57 | 2022-09-08 08:45 | 50 | 10:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE PRIMARIO | A22090700257 | New_Event | Primary Wire Break | Include | Include | Equipment | 648 | 2022-09-07 | 32400 | keep | 0 | Sep | 2022 | 0.022067 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-07 22:10 | 2022-09-09 13:28 | 10 | 39:18 | P | CONDUCTOR ROTO O ABIERTO | SE ELIMINO ALAMBRE VACANTE Y SE CERRO TRANSFORMADOR | S22090700581 | New_Event | Primary Wire Break | Include | Include | Equipment | 2358 | 2022-09-07 | 23580 | keep | 0 | Sep | 2022 | 0.01606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2022-09-07 23:18 | 2022-09-08 07:17 | 30 | 7:59 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO HACIA CAJA DE RISER | C22090700431 | New_Event | Primary Wire Break | Include | Include | Equipment | 479 | 2022-09-07 | 14370 | keep | 0 | Sep | 2022 | 0.0097873 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-07 23:22 | 2022-09-08 11:27 | 125 | 12:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B22090700511 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 725 | 2022-09-07 | 90625 | keep | 0 | Sep | 2022 | 0.061724 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2022-09-07 23:27 | 2022-09-08 08:30 | 20 | 9:03 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE ELIMINO PARARRAYO | A22090700260 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 543 | 2022-09-07 | 10860 | keep | 0 | Sep | 2022 | 0.0073967 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-07 23:28 | 2022-09-08 06:38 | 702 | 7:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 3 CAJAS PRIMARIAS EN C/L | B22090700154 | New_Event | Cutout Failure | Include | Include | Equipment | 430 | 2022-09-07 | 301860 | keep | 0 | Sep | 2022 | 0.2056 | 0.00047813 | Sustained | FALSE | FALSE | Not_TMED_Event | 702
UTUADO | 2022-09-08 00:37 | 2022-09-08 11:14 | 30 | 10:37 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 637 | 2022-09-08 | 19110 | keep | 0 | Sep | 2022 | 0.013016 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2022-09-08 02:38 | 2022-09-08 04:50 | 2844 | 2:12 | T | ARBOL SOBRE LINEA | ALIMENTADOR FUERA DE SERVICIO POR ARBOL SOBRE LINEA | P22090800012 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 132 | 2022-09-08 | 375408 | keep | 0 | Sep | 2022 | 0.25569 | 0.001937 | Sustained | FALSE | FALSE | Not_TMED_Event | 2844
AGUADILLA | 2022-09-08 03:10 | 2022-09-08 05:30 | 22 | 2:20 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M22090800004 | New_Event | Animals | Include | Include | Wildlife | 140 | 2022-09-08 | 3080 | keep | 0 | Sep | 2022 | 0.0020978 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
GUAYAMA | 2022-09-08 04:50 | 2022-09-08 09:27 | 956 | 4:37 | P | ARBOL SOBRE LINEA | SE HIZO DESGANCHE Y SE LEVANTARON 2 ALAMBRES PRIMARIOS SE CERRARON PUENTES 2 X 140 EN CORTE DE LINEA | P22090800023 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 277 | 2022-09-08 | 264812 | keep | 0 | Sep | 2022 | 0.18036 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-08 05:01 | 2022-09-08 09:55 | 100 | 4:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA REALIZAR DESGANCHE | M22090800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2022-09-08 | 29400 | keep | 0 | Sep | 2022 | 0.020024 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2022-09-08 05:25 | 2022-09-08 09:30 | 100 | 4:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M22090800008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 245 | 2022-09-08 | 24500 | keep | 0 | Sep | 2022 | 0.016687 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2022-09-08 06:08 | 2022-09-08 08:40 | 8 | 2:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CL MAL TIEMPO LLUVIA | B22090800030 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 152 | 2022-09-08 | 1216 | keep | 0 | Sep | 2022 | 0.00082821 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2022-09-08 06:09 | 2022-09-08 16:50 | 1 | 10:41 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C22090800036 | New_Event | Service Transformer Failure | Include | Include | Equipment | 641 | 2022-09-08 | 641 | keep | 0 | Sep | 2022 | 0.00043658 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2022-09-08 06:30 | 2022-09-08 14:50 | 30 | 8:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090800006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 500 | 2022-09-08 | 15000 | keep | 0 | Sep | 2022 | 0.010216 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2022-09-08 06:35 | 2022-09-08 08:38 | 100 | 2:03 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA SE ENDEREZO POSTE PRIMARIO Y 1 X 65 EN CORTE DE LINEA | P22090800033 | New_Event | Primary Wire Break | Include | Include | Equipment | 123 | 2022-09-08 | 12300 | keep | 0 | Sep | 2022 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-08 06:38 | 2022-09-08 06:52 | 2861 | 0:14 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA REEMPLAZO 3 CAJAS PRIMARIAS EN C/L PRICIPAL | B22090800032 | Additional_clients | Cutout Failure | Include | Include | Equipment | 14 | 2022-09-08 | 40054 | keep | 0 | Sep | 2022 | 0.027281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 06:45 | 2022-09-08 10:21 | 10 | 3:36 | P | ANIMAL | 1 X 20 EN RISER CRUCE POR AVE Y SE LE DIO MANTENIMIENTO AL XMR | B22090800039 | New_Event | Animals | Include | Include | Wildlife | 216 | 2022-09-08 | 2160 | keep | 0 | Sep | 2022 | 0.0014712 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-08 06:45 | 2022-09-08 13:13 | 60 | 6:28 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SU AVERIA NUEVA DEL T-311 @ T-310 | B22090800033 | New_Event | UG Cable Fault | Include | Include | Equipment | 388 | 2022-09-08 | 23280 | keep | 0 | Sep | 2022 | 0.015856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-08 06:53 | 2022-09-08 15:45 | 20 | 8:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 SUM-20 EN SU-10 LLUVIA | S22090800007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 532 | 2022-09-08 | 10640 | keep | 0 | Sep | 2022 | 0.0072469 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-08 06:54 | 2022-09-09 11:30 | 40 | 28:36 | P | NO SE REPORTO CAUSA | 1 SUM-20 DE 40AMP EN SU-1 | S22090800626 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1716 | 2022-09-08 | 68640 | keep | 0 | Sep | 2022 | 0.04675 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-09-08 07:00 | 2022-09-08 15:46 | 12 | 8:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADORES LLUVIA | S22090800008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 526 | 2022-09-08 | 6312 | keep | 0 | Sep | 2022 | 0.0042991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-09-08 07:08 | 2022-09-08 07:09 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B22090800034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 325 | keep | 0 | Sep | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CAGUAS | 2022-09-08 07:18 | 2022-09-08 07:19 | 1378 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO INTERRUPTOR EN SERVICIO | C22090800043 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 1378 | keep | 0 | Sep | 2022 | 0.00093855 | 0.00093855 | Momentary | FALSE | FALSE | Not_TMED_Event | 1378
CAGUAS | 2022-09-08 07:19 | 2022-09-08 17:08 | 35 | 9:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 SMU 20 DE 100 AMP. MAL TIEMPO LLUVIA | C22090800057 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 589 | 2022-09-08 | 20615 | keep | 0 | Sep | 2022 | 0.014041 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2022-09-08 07:24 | 2022-09-08 19:00 | 12 | 11:36 | P | TRANSFORMADOR AVERIADO | REMPLAZAR TRANSFORMADOR AVERIADO DE 25 KVA POR 37.5 KVA | A22090800012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 696 | 2022-09-08 | 8352 | keep | 0 | Sep | 2022 | 0.0056885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-09-08 07:27 | 2022-09-08 14:59 | 15 | 7:32 | P | ANIMAL | 1 X 30 EN C/L AVE CRUZO LINEAS | B22090800040 | New_Event | Animals | Include | Include | Wildlife | 452 | 2022-09-08 | 6780 | keep | 0 | Sep | 2022 | 0.0046178 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-08 07:35 | 2022-09-08 09:55 | 20 | 2:20 | P | NO SE REPORTO CAUSA | 2 X 50 EN CL | S22090800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2022-09-08 | 2800 | keep | 0 | Sep | 2022 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2022-09-08 07:35 | 2022-09-08 10:35 | 179 | 3:00 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C22090800047 | New_Event | Animals | Include | Include | Wildlife | 180 | 2022-09-08 | 32220 | keep | 0 | Sep | 2022 | 0.021945 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2022-09-08 07:45 | 2022-09-08 13:15 | 300 | 5:30 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA POR DESGANCHE | P22090800054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 330 | 2022-09-08 | 99000 | keep | 0 | Sep | 2022 | 0.067428 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2022-09-08 07:48 | 2022-09-08 12:32 | 12 | 4:44 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR REMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA Y CAJA | R22090800006 | New_Event | Service Transformer Failure | Include | Include | Equipment | 284 | 2022-09-08 | 3408 | keep | 0 | Sep | 2022 | 0.0023212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-09-08 07:53 | 2022-09-08 12:50 | 80 | 4:57 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE EN VARIOS PUNTOS | B22090800043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 297 | 2022-09-08 | 23760 | keep | 0 | Sep | 2022 | 0.016183 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-08 07:56 | 2022-09-08 11:15 | 15 | 3:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L LLUVIA FUERTE | B22090800044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 199 | 2022-09-08 | 2985 | keep | 0 | Sep | 2022 | 0.0020331 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-08 07:59 | 2022-09-09 12:45 | 6 | 28:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 XMR SE REMPLAZO 200 PIES DE SECUNDARIA | B22090800045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1726 | 2022-09-08 | 10356 | keep | 0 | Sep | 2022 | 0.0070534 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2022-09-08 08:00 | 2022-09-08 14:07 | 1 | 6:07 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 KVA POR 37.5 KVA | A22090800014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 367 | 2022-09-08 | 367 | keep | 0 | Sep | 2022 | 0.00024996 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-09-08 08:03 | 2022-09-08 10:27 | 16 | 2:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | C22090800050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2022-09-08 | 2304 | keep | 0 | Sep | 2022 | 0.0015692 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-09-08 08:06 | 2022-09-08 12:07 | 15 | 4:01 | P | DESGANCHE | 1 X 80 EN C/L Y SE REALIZO DESGANCHE | S22090800016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-09-08 | 3615 | keep | 0 | Sep | 2022 | 0.0024622 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-08 08:09 | 2022-09-08 13:47 | 25 | 5:38 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L Y 1 X 10 EN XMR | R22090800011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 338 | 2022-09-08 | 8450 | keep | 0 | Sep | 2022 | 0.0057553 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-09-08 08:10 | 2022-09-08 11:13 | 2 | 3:03 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L MAL TIEMPO RAYOS | R22090800012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 183 | 2022-09-08 | 366 | keep | 0 | Sep | 2022 | 0.00024928 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2022-09-08 08:12 | 2022-09-08 15:52 | 12 | 7:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR PUENTES REPARAR SECUNDARIA SOLO SE AFECTAN CLIENTES DEL TRANSFORMADOR | A22090800017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 460 | 2022-09-08 | 5520 | keep | 0 | Sep | 2022 | 0.0037596 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-09-08 08:16 | 2022-09-08 12:13 | 7 | 3:57 | P | TRANSFORMADOR AVERIADO | SE ELIMINO TRANSFORMADOR AVERIADO TRASPATIO Y SE PASO CARGA A XMR QUE ESTABA EN LA CALLE QUE SOLO DABA A PARQUE PASIVO | B22090800047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 237 | 2022-09-08 | 1659 | keep | 0 | Sep | 2022 | 0.0011299 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-09-08 08:18 | 2022-09-08 14:24 | 1 | 6:06 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M22090800016 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 366 | 2022-09-08 | 366 | keep | 0 | Sep | 2022 | 0.00024928 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-09-08 08:21 | 2022-09-08 08:22 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22090800053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 551 | keep | 0 | Sep | 2022 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
BAYAMON | 2022-09-08 08:28 | 2022-09-08 15:50 | 30 | 7:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 CL LLUVIA | B22090800049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 442 | 2022-09-08 | 13260 | keep | 0 | Sep | 2022 | 0.0090313 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-08 08:43 | 2022-09-08 09:27 | 60 | 0:44 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | B22090800022 | New_Event | Animals | Include | Include | Wildlife | 44 | 2022-09-08 | 2640 | keep | 0 | Sep | 2022 | 0.0017981 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2022-09-08 08:46 | 2022-09-08 10:36 | 10 | 1:50 | P | PROBLEMA DEL CLIENTE | 2 X 80 EN C/L SE DEJO CLIENTE PRIVADO EDIFICIO PRISM LOTE 5 B1 FUERA POR AVERRIA INTERNA PROA | R22090800016 | New_Event | Customer-Related Interruption | Include | Include | Public | 110 | 2022-09-08 | 1100 | keep | 0 | Sep | 2022 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-08 09:05 | 2022-09-08 11:05 | 20 | 2:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR PRIMARIO | C22090800061 | New_Event | Primary Wire Break | Include | Include | Equipment | 120 | 2022-09-08 | 2400 | keep | 0 | Sep | 2022 | 0.0016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2022-09-08 09:05 | 2022-09-08 13:35 | 30 | 4:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A22090800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-09-08 | 8100 | keep | 0 | Sep | 2022 | 0.0055169 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-09-08 09:11 | 2022-09-08 16:45 | 8 | 7:34 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A22090800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 454 | 2022-09-08 | 3632 | keep | 0 | Sep | 2022 | 0.0024737 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-09-08 09:15 | 2022-09-08 09:45 | 2 | 0:30 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO PALMA DE LA LINEA | M22090800020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 30 | 2022-09-08 | 60 | keep | 0 | Sep | 2022 | 4.0866e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2022-09-08 09:17 | 2022-09-08 11:30 | 57 | 2:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN LA SALIDA DE RISER | C22090800059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2022-09-08 | 7581 | keep | 0 | Sep | 2022 | 0.0051634 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
GUAYAMA | 2022-09-08 09:25 | 2022-09-08 12:46 | 1 | 3:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | P22090800077 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 201 | 2022-09-08 | 201 | keep | 0 | Sep | 2022 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2022-09-08 09:34 | 2022-09-08 13:05 | 2 | 3:31 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22090800025 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 211 | 2022-09-08 | 422 | keep | 0 | Sep | 2022 | 0.00028742 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2022-09-08 09:41 | 2022-09-08 13:09 | 1 | 3:28 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L MAL TIEMPO RAYOS | B22090800057 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 208 | 2022-09-08 | 208 | keep | 0 | Sep | 2022 | 0.00014167 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-08 09:42 | 2022-09-08 14:50 | 175 | 5:08 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S22090800032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2022-09-08 | 53900 | keep | 0 | Sep | 2022 | 0.036711 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CANOVANAS | 2022-09-08 10:02 | 2022-09-08 22:48 | 230 | 12:46 | P | CABLE SOTERRADO AVERIADO | 3 X 100 EN SU - 27 REMPLAZO CAJAS SECAS | R22090800022 | New_Event | UG Cable Fault | Include | Include | Equipment | 766 | 2022-09-08 | 176180 | keep | 0 | Sep | 2022 | 0.12 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
CANOVANAS | 2022-09-08 10:02 | 2022-09-10 15:51 | 2 | 53:49 | P | CABLE SOTERRADO AVERIADO | SE REEMPLAZO CABLE SOTERRADO DE MH 10 A XMR | R22090800022 | New_Event | UG Cable Fault | Include | Include | Equipment | 3229 | 2022-09-08 | 6458 | keep | 0 | Sep | 2022 | 0.0043985 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-09-08 10:04 | 2022-09-09 09:11 | 10 | 23:07 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | S22090800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1387 | 2022-09-08 | 13870 | keep | 0 | Sep | 2022 | 0.0094468 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-09-08 10:11 | 2022-09-08 11:04 | 4 | 0:53 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO RAYOS | R22090800024 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 53 | 2022-09-08 | 212 | keep | 0 | Sep | 2022 | 0.00014439 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-09-08 10:12 | 2022-09-08 12:07 | 3114 | 1:55 | T | DESGANCHE | SE HIZO DESGANCHE MASIVO Y SE PUSO EN SERVICIO INTERRUPTOR | P22090800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2022-09-08 | 358110 | keep | 0 | Sep | 2022 | 0.24391 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
MAYAGÃœEZ | 2022-09-08 10:12 | 2022-09-08 11:13 | 4381 | 1:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR POR MACHETE SOLIDO QUEMADO SE SECCIONALIZO | M22090800048 | New_Event | Switch Failure | Include | Include | Equipment | 61 | 2022-09-08 | 267241 | keep | 0 | Sep | 2022 | 0.18202 | 0.0029839 | Sustained | FALSE | FALSE | Not_TMED_Event | 4381
AGUADILLA | 2022-09-08 10:14 | 2022-09-08 13:00 | 20 | 2:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22090800029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 166 | 2022-09-08 | 3320 | keep | 0 | Sep | 2022 | 0.0022612 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-09-08 10:18 | 2022-09-08 14:38 | 6 | 4:20 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 75 KVA X 75 KVA Y CAJA | R22090800025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 260 | 2022-09-08 | 1560 | keep | 0 | Sep | 2022 | 0.0010625 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-09-08 10:22 | 2022-09-08 16:19 | 5 | 5:57 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO SECUNDARIA | R22090800027 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 357 | 2022-09-08 | 1785 | keep | 0 | Sep | 2022 | 0.0012158 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-09-08 10:34 | 2022-09-08 16:43 | 100 | 6:09 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN CABLE SOTERRADO | B22090800063 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 369 | 2022-09-08 | 36900 | keep | 0 | Sep | 2022 | 0.025132 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-08 10:46 | 2022-09-08 18:00 | 15 | 7:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 50KVA | S22090800048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 434 | 2022-09-08 | 6510 | keep | 0 | Sep | 2022 | 0.0044339 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-08 10:58 | 2022-09-08 11:54 | 8 | 0:56 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | R22090800033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2022-09-08 | 448 | keep | 0 | Sep | 2022 | 0.00030513 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-08 11:00 | 2022-09-08 14:35 | 18 | 3:35 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZAR POSTE SECUNDARIO ROTO | M22090800110 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 215 | 2022-09-08 | 3870 | keep | 0 | Sep | 2022 | 0.0026358 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2022-09-08 11:03 | 2022-09-08 17:50 | 1 | 6:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C22090800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2022-09-08 | 407 | keep | 0 | Sep | 2022 | 0.00027721 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-08 11:04 | 2022-09-08 11:47 | 1 | 0:43 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22090800013 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 43 | 2022-09-08 | 43 | keep | 0 | Sep | 2022 | 2.9287e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-08 11:11 | 2022-09-08 14:13 | 149 | 3:02 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090800084 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 182 | 2022-09-08 | 27118 | keep | 0 | Sep | 2022 | 0.01847 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
HUMACAO | 2022-09-08 11:12 | 2022-09-08 14:03 | 1 | 2:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE QUEMADO | C22090800085 | New_Event | Cutout Failure | Include | Include | Equipment | 171 | 2022-09-08 | 171 | keep | 0 | Sep | 2022 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-08 11:18 | 2022-09-08 11:22 | 20 | 0:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22090800022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2022-09-08 | 80 | keep | 0 | Sep | 2022 | 5.4488e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-09-08 11:23 | 2022-09-08 13:21 | 150 | 1:58 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R22090800037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2022-09-08 | 17700 | keep | 0 | Sep | 2022 | 0.012055 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-09-08 11:26 | 2022-09-08 12:56 | 2 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR Y SE REPARO SECUNDARIA | C22090800087 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2022-09-08 | 180 | keep | 0 | Sep | 2022 | 0.0001226 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2022-09-08 11:34 | 2022-09-08 15:00 | 15 | 3:26 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA Y LINEA SECUNDARIA | M22090800127 | New_Event | Primary Wire Break | Include | Include | Equipment | 206 | 2022-09-08 | 3090 | keep | 0 | Sep | 2022 | 0.0021046 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-08 11:39 | 2022-09-08 15:48 | 160 | 4:09 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE 1 X 80 EN CORTE DE LINEA | S22090800062 | New_Event | Primary Wire Break | Include | Include | Equipment | 249 | 2022-09-08 | 39840 | keep | 0 | Sep | 2022 | 0.027135 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BAYAMON | 2022-09-08 11:39 | 2022-09-08 11:40 | 603 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 9206-08 Y LLEVA EL 9206-09 | B2209080075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 603 | keep | 0 | Sep | 2022 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2022-09-08 11:39 | 2022-09-08 11:40 | 6 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 9206-08 Y LLEVA EL 9206-09 | B2209080075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 6 | keep | 0 | Sep | 2022 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2022-09-08 11:41 | 2022-09-08 15:33 | 8 | 3:52 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR Y EL OTRO TRANSFOMADOR DE LA LINEA ESTA QUEMADO MAL TIEMPO RAYO | C22090800089 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 232 | 2022-09-08 | 1856 | keep | 0 | Sep | 2022 | 0.0012641 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-09-08 11:43 | 2022-09-08 12:46 | 1 | 1:03 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C22090800090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-09-08 | 63 | keep | 0 | Sep | 2022 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-08 11:49 | 2022-09-08 11:50 | 1448 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE BKR | R22090800042 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-08 | 1448 | keep | 0 | Sep | 2022 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
CANOVANAS | 2022-09-08 11:50 | 2022-09-08 15:50 | 58 | 4:00 | P | CONDUCTOR ROTO O ABIERTO | LEVANTO CONDUCTOR | R22090800056 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 240 | 2022-09-08 | 13920 | keep | 0 | Sep | 2022 | 0.0094808 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2022-09-08 11:53 | 2022-09-08 14:24 | 15 | 2:31 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | B22090800077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2022-09-08 | 2265 | keep | 0 | Sep | 2022 | 0.0015427 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-08 11:57 | 2022-09-08 18:24 | 1 | 6:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | R22090800044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 387 | 2022-09-08 | 387 | keep | 0 | Sep | 2022 | 0.00026358 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-08 12:00 | 2022-09-08 12:02 | 1964 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 60% DEL 1110-03 | S22090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-08 | 3928 | keep | 0 | Sep | 2022 | 0.0026753 | 0.0013377 | Momentary | FALSE | FALSE | Not_TMED_Event | 1964
SAN JUAN | 2022-09-08 12:00 | 2022-09-08 12:02 | 915 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 60% DE SU CARGA ESTA POR 1106-04 | S22090800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-08 | 1830 | keep | 0 | Sep | 2022 | 0.0012464 | 0.0006232 | Momentary | FALSE | FALSE | Not_TMED_Event | 915
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 12:10 | 2791 | 0:08 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-08 | 22328 | keep | 0 | Sep | 2022 | 0.015207 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 12:10 | 1464 | 0:08 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-08 | 11712 | keep | 0 | Sep | 2022 | 0.007977 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 12:10 | 759 | 0:08 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-08 | 6072 | keep | 0 | Sep | 2022 | 0.0041356 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 12:10 | 1500 | 0:08 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 8 | 2022-09-08 | 12000 | keep | 0 | Sep | 2022 | 0.0081731 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 14:07 | 2132 | 2:05 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-09-08 | 266500 | keep | 0 | Sep | 2022 | 0.18151 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 14:07 | 2366 | 2:05 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-09-08 | 295750 | keep | 0 | Sep | 2022 | 0.20143 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 14:07 | 1976 | 2:05 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-09-08 | 247000 | keep | 0 | Sep | 2022 | 0.16823 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-09-08 12:02 | 2022-09-08 14:07 | 3688 | 2:05 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090800042 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 125 | 2022-09-08 | 461000 | keep | 0 | Sep | 2022 | 0.31399 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
SAN JUAN | 2022-09-08 12:06 | 2022-09-08 12:59 | 10 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S22090800069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2022-09-08 | 530 | keep | 0 | Sep | 2022 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-08 12:18 | 2022-09-08 12:19 | 2708 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | R22090800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-08 | 2708 | keep | 0 | Sep | 2022 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2022-09-08 12:19 | 2022-09-08 15:01 | 126 | 2:42 | P | DESGANCHE | 2 X 65 Y 1 X 80 EN C/LS | R22090800051 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-09-08 | 20412 | keep | 0 | Sep | 2022 | 0.013903 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
BARRANQUITAS | 2022-09-08 12:23 | 2022-09-09 12:09 | 15 | 23:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO DE TRANSFORMADOR DE 50KVA X 50KVA | C22090800094 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1426 | 2022-09-08 | 21390 | keep | 0 | Sep | 2022 | 0.014569 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2022-09-08 12:26 | 2022-09-08 14:15 | 26 | 1:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22090800051 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 109 | 2022-09-08 | 2834 | keep | 0 | Sep | 2022 | 0.0019302 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-09-08 12:31 | 2022-09-08 16:00 | 10 | 3:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO TRAMO SECUNDARIO | S22090800076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 209 | 2022-09-08 | 2090 | keep | 0 | Sep | 2022 | 0.0014235 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-08 12:32 | 2022-09-08 12:35 | 4085 | 0:03 | T | TRANSFORMADOR AVERIADO | DISPARO DE BKR SE CERRO POR CONTROL | R22090800059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3 | 2022-09-08 | 12255 | keep | 0 | Sep | 2022 | 0.0083468 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2022-09-08 12:35 | 2022-09-08 15:46 | 12 | 3:11 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR REMPLAZO XMR QUEMADO DE 50 KVA X 50 KVA Y CAJA | R22090800006 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 191 | 2022-09-08 | 2292 | keep | 0 | Sep | 2022 | 0.0015611 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2022-09-08 12:37 | 2022-09-08 14:34 | 25 | 1:57 | P | DESGANCHE | 1 X 30 EN C/L | R22090800063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-09-08 | 2925 | keep | 0 | Sep | 2022 | 0.0019922 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2022-09-08 12:45 | 2022-09-08 16:48 | 30 | 4:03 | P | DESGANCHE | 1 X 30 EN C/L | R22090800066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2022-09-08 | 7290 | keep | 0 | Sep | 2022 | 0.0049652 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-08 12:45 | 2022-09-08 15:33 | 85 | 2:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA FUERTE VIENTO | M22090800174 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 168 | 2022-09-08 | 14280 | keep | 0 | Sep | 2022 | 0.009726 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BARRANQUITAS | 2022-09-08 12:46 | 2022-09-08 14:00 | 1 | 1:14 | P | TRANSFORMADOR AVERIADO | 2 X 10 EN BANCO DE TRANSFORMADOR TIENE TRANSFORMADOR AVERIADO | C22090800099 | New_Event | Service Transformer Failure | Include | Include | Equipment | 74 | 2022-09-08 | 74 | keep | 0 | Sep | 2022 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-08 12:52 | 2022-09-08 15:41 | 133 | 2:49 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | B22090800080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 169 | 2022-09-08 | 22477 | keep | 0 | Sep | 2022 | 0.015309 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
BAYAMON | 2022-09-08 12:55 | 2022-09-08 12:56 | 3941 | 0:01 | T | NO SE REPORTO CAUSA | EN SERVICIO | B22090800081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 3941 | keep | 0 | Sep | 2022 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2022-09-08 12:59 | 2022-09-08 13:01 | 2617 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLUVIA FUERTE | B22090800083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-08 | 5234 | keep | 0 | Sep | 2022 | 0.0035649 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2022-09-08 13:00 | 2022-09-08 14:22 | 573 | 1:22 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1704-04 LLEVANDO CARGA 1704-05 SE CERRO POR SCADA ABRIENDO MACHETES N/O CONTRA 1704-05 POR RAMA CRUZANDO LINEAS | B22090800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2022-09-08 | 46986 | keep | 0 | Sep | 2022 | 0.032002 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2022-09-08 13:00 | 2022-09-08 14:41 | 1313 | 1:41 | T | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS Y SE CERRO MACHETES N/O CONTRA 1704-04 | B22090800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2022-09-08 | 132613 | keep | 0 | Sep | 2022 | 0.090322 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
BARRANQUITAS | 2022-09-08 13:01 | 2022-09-08 14:30 | 33 | 1:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE LEVANTO NEUTRAL PRIMARIO | C22090800101 | New_Event | Primary Wire Break | Include | Include | Equipment | 89 | 2022-09-08 | 2937 | keep | 0 | Sep | 2022 | 0.0020004 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:08 | 959 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-09-08 | 5754 | keep | 0 | Sep | 2022 | 0.003919 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:08 | 1382 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-09-08 | 8292 | keep | 0 | Sep | 2022 | 0.0056476 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:08 | 663 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800187 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2022-09-08 | 3978 | keep | 0 | Sep | 2022 | 0.0027094 | 0.00045157 | Sustained | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:06 | 1514 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 6056 | keep | 0 | Sep | 2022 | 0.0041247 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:06 | 1105 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800159 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 4420 | keep | 0 | Sep | 2022 | 0.0030104 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:06 | 4176 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 16704 | keep | 0 | Sep | 2022 | 0.011377 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:06 | 252 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 1008 | keep | 0 | Sep | 2022 | 0.00068654 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:06 | 2147 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 8588 | keep | 0 | Sep | 2022 | 0.0058492 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-09-08 13:02 | 2022-09-08 13:06 | 2858 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 11432 | keep | 0 | Sep | 2022 | 0.0077863 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2022-09-08 13:03 | 2022-09-08 13:06 | 1048 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLUVIA FUERTE | B22090800094 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2022-09-08 | 3144 | keep | 0 | Sep | 2022 | 0.0021414 | 0.00071379 | Momentary | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2022-09-08 13:03 | 2022-09-08 13:11 | 478 | 0:08 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO INTERRUPTOR 1705-01 LLEVANDO CARGA 1705-03 SE CERRO POR SCADA LLUVIA FUERTE | B22090800093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 8 | 2022-09-08 | 3824 | keep | 0 | Sep | 2022 | 0.0026045 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2022-09-08 13:03 | 2022-09-08 13:11 | 949 | 0:08 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO INTERRUPTOR 1705-01 LLEVANDO CARGA 1705-03 SE CERRO POR SCADA LLUVIA FUERTE | B22090800093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 8 | 2022-09-08 | 7592 | keep | 0 | Sep | 2022 | 0.0051709 | 0.00064636 | Sustained | FALSE | FALSE | Not_TMED_Event | 949
BAYAMON | 2022-09-08 13:03 | 2022-09-08 13:09 | 74 | 0:06 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO INTERRUPTOR SE CERRO POR SCADA LLUVIA FUERTE | B22090800095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 6 | 2022-09-08 | 444 | keep | 0 | Sep | 2022 | 0.00030241 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
BAYAMON | 2022-09-08 13:07 | 2022-09-08 15:54 | 80 | 2:47 | P | DESGANCHE | 2 X 100 1 X 50 EN C/L SE DESGANCHO | B22090800103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2022-09-08 | 13360 | keep | 0 | Sep | 2022 | 0.0090994 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-08 13:08 | 2022-09-08 13:56 | 1514 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800159 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-09-08 | 72672 | keep | 0 | Sep | 2022 | 0.049497 | 0.0010312 | Sustained | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2022-09-08 13:08 | 2022-09-08 13:56 | 1105 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800159 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-09-08 | 53040 | keep | 0 | Sep | 2022 | 0.036125 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2022-09-08 13:08 | 2022-09-08 13:56 | 4176 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800134 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-09-08 | 200448 | keep | 0 | Sep | 2022 | 0.13652 | 0.0028443 | Sustained | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2022-09-08 13:08 | 2022-09-08 13:56 | 252 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800134 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-09-08 | 12096 | keep | 0 | Sep | 2022 | 0.0082385 | 0.00017164 | Sustained | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2022-09-08 13:08 | 2022-09-08 13:56 | 2147 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800134 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-09-08 | 103056 | keep | 0 | Sep | 2022 | 0.070191 | 0.0014623 | Sustained | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2022-09-08 13:08 | 2022-09-08 13:56 | 2858 | 0:48 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800139 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 48 | 2022-09-08 | 137184 | keep | 0 | Sep | 2022 | 0.093435 | 0.0019466 | Sustained | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 1935 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGAO | B22090800162 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 3870 | keep | 0 | Sep | 2022 | 0.0026358 | 0.0013179 | Momentary | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 3 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGAO | B22090800162 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 6 | keep | 0 | Sep | 2022 | 4.0866e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 61 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGAO | B22090800162 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 122 | keep | 0 | Sep | 2022 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 1501 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGAO | B22090800162 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 3002 | keep | 0 | Sep | 2022 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 546 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUARAGAO | B22090800162 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 1092 | keep | 0 | Sep | 2022 | 0.00074376 | 0.00037188 | Momentary | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 959 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUAYNABO | S22090800094 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 1918 | keep | 0 | Sep | 2022 | 0.0013063 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 1297 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUAYNABO | S22090800094 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 2594 | keep | 0 | Sep | 2022 | 0.0017668 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 451 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUAYNABO | S22090800094 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 902 | keep | 0 | Sep | 2022 | 0.00061435 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 1264 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUAYNABO | S22090800094 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 2528 | keep | 0 | Sep | 2022 | 0.0017218 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2022-09-08 13:12 | 2022-09-08 13:14 | 620 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA GUAYNABO | S22090800094 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2022-09-08 | 1240 | keep | 0 | Sep | 2022 | 0.00084456 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2022-09-08 13:13 | 2022-09-09 19:30 | 12 | 30:17 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO HACIA T-310 | B22090800033 | New_Event | UG Cable Fault | Include | Include | Equipment | 1817 | 2022-09-08 | 21804 | keep | 0 | Sep | 2022 | 0.014851 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2022-09-08 13:13 | 2022-09-08 13:14 | 6136 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE LLUVIA FUERTE | B22090800000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 6136 | keep | 0 | Sep | 2022 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
BAYAMON | 2022-09-08 13:14 | 2022-09-08 13:56 | 959 | 0:42 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800187 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-09-08 | 40278 | keep | 0 | Sep | 2022 | 0.027433 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 13:14 | 2022-09-08 13:56 | 1382 | 0:42 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800187 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-09-08 | 58044 | keep | 0 | Sep | 2022 | 0.039534 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 13:14 | 2022-09-08 13:56 | 663 | 0:42 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B22090800187 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 42 | 2022-09-08 | 27846 | keep | 0 | Sep | 2022 | 0.018966 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-08 13:20 | 2022-09-08 14:53 | 315 | 1:33 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE PATRULLO NO SE CONSIGUIO CAUSA SE CERRO BKR POR SCADA | C22090800105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2022-09-08 | 29295 | keep | 0 | Sep | 2022 | 0.019953 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
MAYAGÃœEZ | 2022-09-08 13:36 | 2022-09-08 13:37 | 1825 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | M22090800190 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 1825 | keep | 0 | Sep | 2022 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2022-09-08 13:40 | 2022-09-08 15:58 | 437 | 2:18 | T | CABLE SOTERRADO AVERIADO | DISPARO SE ENCONTRO SALIDA QUEMADA 1530-7 Y SE PASO CARGA AL 1526-02 | S22090800095 | New_Event | UG Cable Fault | Include | Include | Equipment | 138 | 2022-09-08 | 60306 | keep | 0 | Sep | 2022 | 0.041074 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
SAN JUAN | 2022-09-08 13:40 | 2022-09-08 15:58 | 643 | 2:18 | T | CABLE SOTERRADO AVERIADO | DISPARO SE ENCONTRO SALIDA QUEMADA Y SE PASO CARGA AL 1531-01 | S22090800095 | New_Event | UG Cable Fault | Include | Include | Equipment | 138 | 2022-09-08 | 88734 | keep | 0 | Sep | 2022 | 0.060436 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
CANOVANAS | 2022-09-08 13:41 | 2022-09-08 15:48 | 8 | 2:07 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO SECUNDARIA | R22090800101 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 127 | 2022-09-08 | 1016 | keep | 0 | Sep | 2022 | 0.00069199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2022-09-08 13:45 | 2022-09-08 16:46 | 65 | 3:01 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C22090800116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-09-08 | 11765 | keep | 0 | Sep | 2022 | 0.0080131 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2022-09-08 13:47 | 2022-09-08 14:46 | 2466 | 0:59 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL 50% EN SERVICIO | S22090800102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2022-09-08 | 145494 | keep | 0 | Sep | 2022 | 0.099095 | 0.0016796 | Sustained | FALSE | FALSE | Not_TMED_Event | 2466
SAN JUAN | 2022-09-08 13:51 | 2022-09-08 13:52 | 675 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% POR EL 1345-02 | S22090800102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 675 | keep | 0 | Sep | 2022 | 0.00045974 | 0.00045974 | Momentary | FALSE | FALSE | Not_TMED_Event | 675
BAYAMON | 2022-09-08 13:52 | 2022-09-08 13:54 | 723 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA LLUVIA FUERTE | B22090800226 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-08 | 1446 | keep | 0 | Sep | 2022 | 0.00098486 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2022-09-08 13:52 | 2022-09-08 13:54 | 198 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA LLUVIA FUERTE | B22090800226 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-08 | 396 | keep | 0 | Sep | 2022 | 0.00026971 | 0.00013486 | Momentary | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2022-09-08 13:52 | 2022-09-08 13:54 | 1976 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 1711-02 LLEVANDO CARGA 1711-05 Y 10% 1711-04 SE CERRO POR SCADA LLUVIA FUERTE | B22090800226 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-08 | 3952 | keep | 0 | Sep | 2022 | 0.0026917 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-09-08 13:56 | 2022-09-08 14:44 | 5191 | 0:48 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL 10% EN SERVICIO | B22090800081 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 48 | 2022-09-08 | 249168 | keep | 0 | Sep | 2022 | 0.16971 | 0.0035356 | Sustained | FALSE | FALSE | Not_TMED_Event | 5191
HUMACAO | 2022-09-08 14:03 | 2022-09-08 14:04 | 71 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090800120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 71 | keep | 0 | Sep | 2022 | 4.8358e-05 | 4.8358e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 71
VEGA BAJA | 2022-09-08 14:07 | 2022-09-08 14:48 | 10 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR POR SECUNDARIA AVERIADA ENERGIZADA | A22090800005 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2022-09-08 | 410 | keep | 0 | Sep | 2022 | 0.00027925 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-08 14:09 | 2022-09-08 14:14 | 1799 | 0:05 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 40% DEL 1204-04 LLEVA 60% 1204-03 Y LLEVA 20% DEL 1303-02 LLUVIA FUERTE | S22090800107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-09-08 | 8995 | keep | 0 | Sep | 2022 | 0.0061265 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
SAN JUAN | 2022-09-08 14:09 | 2022-09-08 14:14 | 487 | 0:05 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DEL 1206-04 LLEVA 20% DEL 1303-02 LLUVIA FUERTE | S22090800107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-09-08 | 2435 | keep | 0 | Sep | 2022 | 0.0016585 | 0.00033169 | Momentary | FALSE | FALSE | Not_TMED_Event | 487
SAN JUAN | 2022-09-08 14:09 | 2022-09-08 14:10 | 1058 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3200 LLEVANDO CARGA 1348-08 20% 1336-08 | S22090800107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 1058 | keep | 0 | Sep | 2022 | 0.0007206 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2022-09-08 14:09 | 2022-09-08 14:10 | 250 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3200 LLEVANDO CARGA 20% 1348-06 | S22090800107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 250 | keep | 0 | Sep | 2022 | 0.00017027 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2022-09-08 14:09 | 2022-09-08 14:10 | 1290 | 0:01 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3200 LLEVANDO CARGA 1348-08 20% 1336-08 | S22090800107 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 1290 | keep | 0 | Sep | 2022 | 0.00087861 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2022-09-08 14:10 | 2022-09-08 15:50 | 4 | 1:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50KVA | S22090700475 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 100 | 2022-09-08 | 400 | keep | 0 | Sep | 2022 | 0.00027244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-08 14:11 | 2022-09-08 20:08 | 100 | 5:57 | P | DESGANCHE | 3 X 65 EN CORTE DE LINEA DESGANCHE DE BAMBUA | C22090800119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 357 | 2022-09-08 | 35700 | keep | 0 | Sep | 2022 | 0.024315 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-08 14:12 | 2022-09-08 14:13 | 1225 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 1203-03 EN SERVICIO MAL TIEMPO LLUVIA | S22090800112 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 1225 | keep | 0 | Sep | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-09-08 14:12 | 2022-09-08 14:13 | 616 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO EN SERVICIO CARGA POR EL 1203-01 | S22090800112 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 616 | keep | 0 | Sep | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-09-08 14:12 | 2022-09-08 14:17 | 135 | 0:05 | T | MAL TIEMPO/LLUVIA O VIENTO | SE PROBO POR CONTROL QUEDO EN SERVICIO MAL TIEMPO CARGA POR EL 1401-08 | S22090800120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-09-08 | 675 | keep | 0 | Sep | 2022 | 0.00045974 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2022-09-08 14:12 | 2022-09-08 14:17 | 135 | 0:05 | T | MAL TIEMPO/LLUVIA O VIENTO | SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-05 MAL TIEMPO LLUVIA | S22090800120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2022-09-08 | 675 | keep | 0 | Sep | 2022 | 0.00045974 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
ARECIBO | 2022-09-08 14:12 | 2022-09-08 15:40 | 10 | 1:28 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLACION | A22090800075 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 88 | 2022-09-08 | 880 | keep | 0 | Sep | 2022 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-08 14:13 | 2022-09-08 15:27 | 6 | 1:14 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR POR AVE | M22090800200 | New_Event | Animals | Include | Include | Wildlife | 74 | 2022-09-08 | 444 | keep | 0 | Sep | 2022 | 0.00030241 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2022-09-08 14:13 | 2022-09-08 16:35 | 15 | 2:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BARRA EN PEDESTAL | B22090800000 | New_Event | Secondary Wire Break | Include | Include | Equipment | 142 | 2022-09-08 | 2130 | keep | 0 | Sep | 2022 | 0.0014507 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-08 14:18 | 2022-09-08 14:22 | 1225 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090800357 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 4900 | keep | 0 | Sep | 2022 | 0.0033374 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-09-08 14:18 | 2022-09-08 14:20 | 1452 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090800357 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-08 | 2904 | keep | 0 | Sep | 2022 | 0.0019779 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2022-09-08 14:18 | 2022-09-08 14:22 | 616 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22090800357 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2022-09-08 | 2464 | keep | 0 | Sep | 2022 | 0.0016782 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-09-08 14:18 | 2022-09-08 14:20 | 3432 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 PORTATIL 22 | S22090800357 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-08 | 6864 | keep | 0 | Sep | 2022 | 0.004675 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-09-08 14:18 | 2022-09-08 14:20 | 414 | 0:02 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 PORTATIL 22 | S22090800357 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2022-09-08 | 828 | keep | 0 | Sep | 2022 | 0.00056395 | 0.00028197 | Momentary | FALSE | FALSE | Not_TMED_Event | 414
SAN JUAN | 2022-09-08 14:21 | 2022-09-08 17:11 | 514 | 2:50 | T | DESGANCHE | DISPARO SE ABRIO N/O SE REALIZO DESGANCHE CON VARETA Y SE CERRO N/O 100% EN SERVICIO SU CARGA POR 1520-05 | S22090800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-09-08 | 87380 | keep | 0 | Sep | 2022 | 0.059514 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2022-09-08 14:21 | 2022-09-08 17:11 | 752 | 2:50 | T | DESGANCHE | DISPARO SE ABRIO N/O SE REALIZO DESGANCHE CON VARETA Y SE CERRO N/O 100% EN SERVICIO SU CARGA POR 1520-05 | S22090800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-09-08 | 127840 | keep | 0 | Sep | 2022 | 0.087071 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2022-09-08 14:21 | 2022-09-08 15:04 | 68 | 0:43 | T | DESGANCHE | DISPARO LLEVA 1520-04 Y 1520-01 SE ABRIO N/O Y SE CERRO 1520-05 | S22090800082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2022-09-08 | 2924 | keep | 0 | Sep | 2022 | 0.0019915 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2022-09-08 14:22 | 2022-09-08 14:23 | 8679 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR 1206-03 LLEVANDO 85% 1204-05 10% DEL 1206-3 X 1620-02 MAL TIEMPO LLUVIA | S22090800143 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 8679 | keep | 0 | Sep | 2022 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2022-09-08 14:22 | 2022-09-08 14:23 | 3720 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 85% DE 1204-05 10% DEL 1206-3 X 1620-02 | S22090800143 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 3720 | keep | 0 | Sep | 2022 | 0.0025337 | 0.0025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 3720
BAYAMON | 2022-09-08 14:23 | 2022-09-08 19:25 | 80 | 5:02 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B22090800246 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2022-09-08 | 24160 | keep | 0 | Sep | 2022 | 0.016455 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-08 14:24 | 2022-09-08 14:25 | 1225 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLEVA 1203-03 EN SERVICIO MAL TIEMPO LLUVIA | S22209080000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 1225 | keep | 0 | Sep | 2022 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2022-09-08 14:24 | 2022-09-08 14:25 | 616 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO CARGA POR EL 1203-01 CLIMA MAL TIEMPO LLUVIA | S22209080000 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 616 | keep | 0 | Sep | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
BAYAMON | 2022-09-08 14:25 | 2022-09-08 23:18 | 80 | 8:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIAS | B22090800247 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 533 | 2022-09-08 | 42640 | keep | 0 | Sep | 2022 | 0.029042 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-09-08 14:32 | 2022-09-08 17:04 | 60 | 2:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M22090800202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2022-09-08 | 9120 | keep | 0 | Sep | 2022 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-08 14:33 | 2022-09-08 14:39 | 207 | 0:06 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 1336-09 SE CERRO POR SCADA LLUVIA FUERTE | S22090800000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 6 | 2022-09-08 | 1242 | keep | 0 | Sep | 2022 | 0.00084592 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
VEGA BAJA | 2022-09-08 14:34 | 2022-09-08 17:35 | 30 | 3:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A22090800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2022-09-08 | 5430 | keep | 0 | Sep | 2022 | 0.0036983 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2022-09-08 14:35 | 2022-09-08 21:39 | 2 | 7:04 | P | DESGANCHE | SE SECCIONALIZO LINEA PRIMARIA PARA DESGANCHE GOI BY-220908-05 | B22090800000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 424 | 2022-09-08 | 848 | keep | 0 | Sep | 2022 | 0.00057757 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2022-09-08 14:37 | 2022-09-08 20:39 | 122 | 6:02 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO RAYOS | S22090800174 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 362 | 2022-09-08 | 44164 | keep | 0 | Sep | 2022 | 0.03008 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
SAN JUAN | 2022-09-08 14:39 | 2022-09-08 17:27 | 1483 | 2:48 | P | DESCONECTIVO DEFECTUOSO | AL CERRAR POLE BKR. DISPARO 1336-9 Y SE CERRO POR SCADA PERO SE ABRIO POR MACHETE QUEMADO 30% POR 1336-08 | S22090800258 | New_Event | Switch Failure | Include | Include | Equipment | 168 | 2022-09-08 | 249144 | keep | 0 | Sep | 2022 | 0.16969 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-09-08 14:39 | 2022-09-08 17:27 | 1531 | 2:48 | P | DESCONECTIVO DEFECTUOSO | AL CERRAR POLE BKR. DISPARO 1336-9 Y SE CERRO POR SCADA PERO SE ABRIO POR MACHETE QUEMADO 15% POR 1336-08 | S22090800258 | New_Event | Switch Failure | Include | Include | Equipment | 168 | 2022-09-08 | 257208 | keep | 0 | Sep | 2022 | 0.17518 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
BAYAMON | 2022-09-08 14:44 | 2022-09-08 15:44 | 778 | 1:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR 15% EN SERVICIO ADICIONAL | B22090800081 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 60 | 2022-09-08 | 46680 | keep | 0 | Sep | 2022 | 0.031794 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 14:46 | 2022-09-08 15:34 | 1233 | 0:48 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES Y ENTRO 25% ADICIONAL | S22090800102 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 48 | 2022-09-08 | 59184 | keep | 0 | Sep | 2022 | 0.04031 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 14:48 | 2022-09-08 18:20 | 75 | 3:32 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYOS | B22090800274 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 212 | 2022-09-08 | 15900 | keep | 0 | Sep | 2022 | 0.010829 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2022-09-08 14:52 | 2022-09-08 19:35 | 60 | 4:43 | P | NO SE REPORTO CAUSA | 1 X 80 1 X 65 EN RISER | B22090800279 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 283 | 2022-09-08 | 16980 | keep | 0 | Sep | 2022 | 0.011565 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-08 14:52 | 2022-09-08 18:50 | 40 | 3:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090800084 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 238 | 2022-09-08 | 9520 | keep | 0 | Sep | 2022 | 0.006484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-09-08 14:57 | 2022-09-08 17:10 | 60 | 2:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090800086 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 133 | 2022-09-08 | 7980 | keep | 0 | Sep | 2022 | 0.0054351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2022-09-08 15:04 | 2022-09-08 15:52 | 3654 | 0:48 | T | ARBOL SOBRE LINEA | SE ABRIO MACHETES SECCIONALIZAR ARBOL SOBRE LINEAS | A22090800090 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 48 | 2022-09-08 | 175392 | keep | 0 | Sep | 2022 | 0.11946 | 0.0024887 | Sustained | FALSE | FALSE | Not_TMED_Event | 3654
UTUADO | 2022-09-08 15:10 | 2022-09-08 16:30 | 1 | 1:20 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22090800091 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 80 | 2022-09-08 | 80 | keep | 0 | Sep | 2022 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-08 15:11 | 2022-09-08 15:22 | 168 | 0:11 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO 1345-02 LLEVA PARTE 1330-04 SE CERRO POR SCADA LLUVIA FUERTE | S22090800000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2022-09-08 | 1848 | keep | 0 | Sep | 2022 | 0.0012587 | 0.00011442 | Sustained | FALSE | FALSE | Not_TMED_Event | 168
SAN JUAN | 2022-09-08 15:11 | 2022-09-08 15:22 | 435 | 0:11 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO 1345-02 LLEVA PARTE 1330-04 SE CERRO POR SCADA LLUVIA FUERTE | S22090800000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2022-09-08 | 4785 | keep | 0 | Sep | 2022 | 0.003259 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2022-09-08 15:11 | 2022-09-09 10:40 | 20 | 19:29 | P | DESGANCHE | DESGANCHE Y FIJO PUENTE DE LINEA A CAJA | S22090800268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1169 | 2022-09-08 | 23380 | keep | 0 | Sep | 2022 | 0.015924 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-08 15:14 | 2022-09-08 18:20 | 12 | 3:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EN TRANSFORMADOR TOMA CRUZADA DE PULL OUT VACANTE | C22090800132 | New_Event | Secondary Wire Break | Include | Include | Equipment | 186 | 2022-09-08 | 2232 | keep | 0 | Sep | 2022 | 0.0015202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-09-08 15:19 | 2022-09-08 20:00 | 4 | 4:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | R22090800128 | New_Event | Cutout Failure | Include | Include | Equipment | 281 | 2022-09-08 | 1124 | keep | 0 | Sep | 2022 | 0.00076555 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-09-08 15:23 | 2022-09-09 03:31 | 100 | 12:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN AEREO PROVISIONAL POR LLUVIA | B22090800318 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 728 | 2022-09-08 | 72800 | keep | 0 | Sep | 2022 | 0.049584 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-08 15:26 | 2022-09-10 15:55 | 10 | 48:29 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 KVA | B22090800322 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2909 | 2022-09-08 | 29090 | keep | 0 | Sep | 2022 | 0.019813 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2022-09-08 15:30 | 2022-09-08 19:20 | 7 | 3:50 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR LIQUEO ACEITE DE 25 KVA POR 25 KVA | A22090800104 | New_Event | Service Transformer Failure | Include | Include | Equipment | 230 | 2022-09-08 | 1610 | keep | 0 | Sep | 2022 | 0.0010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2022-09-08 15:34 | 2022-09-08 16:12 | 616 | 0:38 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES Y ENTRO 25% ADICIONAL PARA EL 100% | S22090800102 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 38 | 2022-09-08 | 23408 | keep | 0 | Sep | 2022 | 0.015943 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-08 15:36 | 2022-09-08 18:34 | 189 | 2:58 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | C22090800139 | New_Event | Primary Wire Break | Include | Include | Equipment | 178 | 2022-09-08 | 33642 | keep | 0 | Sep | 2022 | 0.022913 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
BAYAMON | 2022-09-08 15:36 | 2022-09-09 12:05 | 30 | 20:29 | P | MAL TIEMPO/LLUVIA O VIENTO | POSTE VIRADO POR DESPRENDIMIENTO DEL TERENO 1 X 30 EN C/L | B22090800330 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1229 | 2022-09-08 | 36870 | keep | 0 | Sep | 2022 | 0.025112 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-08 15:37 | 2022-09-08 15:38 | 828 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 60% POR EL 1206-04 | S22090800112 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 828 | keep | 0 | Sep | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
SAN JUAN | 2022-09-08 15:37 | 2022-09-08 15:38 | 1977 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR 40% DE SU CARGA POR EL 1206-04 | S22090800112 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-08 | 1977 | keep | 0 | Sep | 2022 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
MAYAGÃœEZ | 2022-09-08 15:39 | 2022-09-08 18:30 | 1 | 2:51 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO SE ENCONTRO CAUSA | M22090800215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 171 | 2022-09-08 | 171 | keep | 0 | Sep | 2022 | 0.00011647 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-08 15:44 | 2022-09-08 16:59 | 3374 | 1:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR 65% EN SERVICIO ADICIONAL | B22090800081 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 75 | 2022-09-08 | 253050 | keep | 0 | Sep | 2022 | 0.17235 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-08 15:47 | 2022-09-08 20:40 | 12 | 4:53 | P | SECUNDARIA/DESGANCHE | 1 X 5 EN XMR DESGANCHE SECUNDARIO | R22090800138 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 293 | 2022-09-08 | 3516 | keep | 0 | Sep | 2022 | 0.0023947 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-09-08 15:52 | 2022-09-08 16:02 | 1 | 0:10 | P | NO SE REPORTO CAUSA | 2 X 15 EN RISER / NO SE REPORTO CAUSA | M22090800205 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2022-09-08 | 10 | keep | 0 | Sep | 2022 | 6.811e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-08 15:52 | 2022-09-08 18:48 | 1825 | 2:56 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA Y SE LEVANTO LINEA PRIMARIA SE CERRARON MACHETES | A22090800124 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 176 | 2022-09-08 | 321200 | keep | 0 | Sep | 2022 | 0.21877 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 15:55 | 2022-09-09 11:23 | 15 | 19:28 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR | B22090800364 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1168 | 2022-09-08 | 17520 | keep | 0 | Sep | 2022 | 0.011933 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-08 15:59 | 2022-09-09 05:48 | 10 | 13:49 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | S22090800365 | New_Event | Service Transformer Failure | Include | Include | Equipment | 829 | 2022-09-08 | 8290 | keep | 0 | Sep | 2022 | 0.0056463 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-08 16:05 | 2022-09-08 19:30 | 4 | 3:25 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A22090800120 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 205 | 2022-09-08 | 820 | keep | 0 | Sep | 2022 | 0.0005585 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2022-09-08 16:12 | 2022-09-08 16:39 | 80 | 0:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S22090800102 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 27 | 2022-09-08 | 2160 | keep | 0 | Sep | 2022 | 0.0014712 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2022-09-08 16:24 | 2022-09-08 16:52 | 29 | 0:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU | C22090800143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2022-09-08 | 812 | keep | 0 | Sep | 2022 | 0.00055305 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2022-09-08 16:25 | 2022-09-10 15:30 | 15 | 47:05 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO @ T-30 | B22090800395 | New_Event | UG Cable Fault | Include | Include | Equipment | 2825 | 2022-09-08 | 42375 | keep | 0 | Sep | 2022 | 0.028861 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-08 16:29 | 2022-09-08 16:32 | 4232 | 0:03 | P | DESCONECTIVO DEFECTUOSO | AL CERRAR POLE BKR. DISPARO 1336-9 Y SE CERRO POR SCADA PERO SE ABRIO POR MACHETE QUEMADO | S22090800258 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2022-09-08 | 12696 | keep | 0 | Sep | 2022 | 0.0086472 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
SAN JUAN | 2022-09-08 16:29 | 2022-09-08 16:50 | 207 | 0:21 | T | DESCONECTIVO DEFECTUOSO | DISPARO AL CERRAR POLE BKR. DEL 1336-08 SE ABRIO N/O Y SE NORMALIZO CARGA | S22090800258 | New_Event | Switch Failure | Include | Include | Equipment | 21 | 2022-09-08 | 4347 | keep | 0 | Sep | 2022 | 0.0029607 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2022-09-08 16:31 | 2022-09-09 12:53 | 40 | 20:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S22090800429 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1222 | 2022-09-08 | 48880 | keep | 0 | Sep | 2022 | 0.033292 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-09-08 16:32 | 2022-09-08 17:27 | 4232 | 0:55 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y SE CERRO POLE BKR Y SE NORMALIZO CARGAS LLEVA 80% DE SU CARGA | S22090800258 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 55 | 2022-09-08 | 232760 | keep | 0 | Sep | 2022 | 0.15853 | 0.0028824 | Sustained | FALSE | FALSE | Not_TMED_Event | 4232
HUMACAO | 2022-09-08 16:33 | 2022-09-08 18:16 | 12 | 1:43 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CRUCE POR AVE | C22090800146 | New_Event | Animals | Include | Include | Wildlife | 103 | 2022-09-08 | 1236 | keep | 0 | Sep | 2022 | 0.00084183 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2022-09-08 16:38 | 2022-09-08 16:39 | 2713 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M22090800221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 2713 | keep | 0 | Sep | 2022 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
CAGUAS | 2022-09-08 16:47 | 2022-09-08 21:47 | 104 | 5:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22090800208 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 300 | 2022-09-08 | 31200 | keep | 0 | Sep | 2022 | 0.02125 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
SAN JUAN | 2022-09-08 16:51 | 2022-09-08 18:28 | 80 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | S22090800465 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2022-09-08 | 7760 | keep | 0 | Sep | 2022 | 0.0052853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2022-09-08 16:58 | 2022-09-09 00:22 | 40 | 7:24 | P | TRANSFORMADOR AVERIADO | 1X50 EN RISER Y SE REMPLAZO BUSHING SENCILLO POR DOBLE-BUSHING EN EL T-8 | S22090800480 | New_Event | Service Transformer Failure | Include | Include | Equipment | 444 | 2022-09-08 | 17760 | keep | 0 | Sep | 2022 | 0.012096 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-08 16:59 | 2022-09-08 19:08 | 519 | 2:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y SE REMPLAZO AISLADOR 10% EN SERVICIO ADICIONAL VER GOI BY-220908-03 | B22090800081 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 129 | 2022-09-08 | 66951 | keep | 0 | Sep | 2022 | 0.0456 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-08 17:11 | 2022-09-08 18:15 | 200 | 1:04 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO RAYOS | S22090800501 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 64 | 2022-09-08 | 12800 | keep | 0 | Sep | 2022 | 0.008718 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2022-09-08 17:16 | 2022-09-08 19:18 | 180 | 2:02 | P | MAL TIEMPO/RAYOS | 1 X 80 Y 2 X 100 EN CORTE DE LINEA MAL TIEMPO RAYOS | S22090800510 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 122 | 2022-09-08 | 21960 | keep | 0 | Sep | 2022 | 0.014957 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
SAN JUAN | 2022-09-08 17:19 | 2022-09-09 10:54 | 35 | 17:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 50 EN CORTE DE LINEA | S22090800518 | New_Event | Cutout Failure | Include | Include | Equipment | 1055 | 2022-09-08 | 36925 | keep | 0 | Sep | 2022 | 0.025149 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2022-09-08 17:26 | 2022-09-09 01:59 | 83 | 8:33 | P | MAL TIEMPO/RAYOS | 1X65 EN C/L RAYOS | B22090800464 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 513 | 2022-09-08 | 42579 | keep | 0 | Sep | 2022 | 0.029 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
SAN JUAN | 2022-09-08 17:27 | 2022-09-09 02:05 | 150 | 8:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3X80 EN RISER, 2X65 EN SU-2 SE REMPLAZARON (2) CAJAS PRIMARIAS DE RISER @ SU-1 | S22090800258 | New_Event | Cutout Failure | Include | Include | Equipment | 518 | 2022-09-08 | 77700 | keep | 0 | Sep | 2022 | 0.052921 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-09-08 17:30 | 2022-09-08 23:09 | 100 | 5:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIAS | B22090800468 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 339 | 2022-09-08 | 33900 | keep | 0 | Sep | 2022 | 0.023089 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-08 17:33 | 2022-09-08 20:00 | 60 | 2:27 | P | MAL TIEMPO/RAYOS | 1 X 50 1 X 40 1 X 20 DESCARGAS ELECTRICAS | B22090800470 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 147 | 2022-09-08 | 8820 | keep | 0 | Sep | 2022 | 0.0060073 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-08 17:35 | 2022-09-08 17:36 | 1253 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 1253 | keep | 0 | Sep | 2022 | 0.00085341 | 0.00085341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1253
MAYAGÃœEZ | 2022-09-08 17:35 | 2022-09-08 17:36 | 1266 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 1266 | keep | 0 | Sep | 2022 | 0.00086227 | 0.00086227 | Momentary | FALSE | FALSE | Not_TMED_Event | 1266
MAYAGÃœEZ | 2022-09-08 17:35 | 2022-09-08 17:36 | 411 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 411 | keep | 0 | Sep | 2022 | 0.00027993 | 0.00027993 | Momentary | FALSE | FALSE | Not_TMED_Event | 411
AGUADILLA | 2022-09-08 17:35 | 2022-09-08 17:36 | 1617 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 1617 | keep | 0 | Sep | 2022 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2022-09-08 17:35 | 2022-09-08 17:36 | 1017 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 1017 | keep | 0 | Sep | 2022 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2022-09-08 17:35 | 2022-09-08 17:36 | 828 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 828 | keep | 0 | Sep | 2022 | 0.00056395 | 0.00056395 | Momentary | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2022-09-08 17:35 | 2022-09-08 17:36 | 863 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800231 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 863 | keep | 0 | Sep | 2022 | 0.00058779 | 0.00058779 | Momentary | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2022-09-08 17:35 | 2022-09-08 17:36 | 309 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800231 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 309 | keep | 0 | Sep | 2022 | 0.00021046 | 0.00021046 | Momentary | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2022-09-08 17:35 | 2022-09-08 17:36 | 176 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800231 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 176 | keep | 0 | Sep | 2022 | 0.00011987 | 0.00011987 | Momentary | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2022-09-08 17:35 | 2022-09-08 17:36 | 974 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2000 | M22090800232 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-08 | 974 | keep | 0 | Sep | 2022 | 0.00066339 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
SAN JUAN | 2022-09-08 17:41 | 2022-09-09 11:06 | 40 | 17:25 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA RAYOS | S22090800557 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1045 | 2022-09-08 | 41800 | keep | 0 | Sep | 2022 | 0.02847 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-09-08 17:43 | 2022-09-08 22:19 | 30 | 4:36 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN CORTE DE LINEA SE DEJO SECCIONALIZADO PARA TRABAJAR MAÃ‘ANA | M22090800234 | New_Event | UG Cable Fault | Include | Include | Equipment | 276 | 2022-09-08 | 8280 | keep | 0 | Sep | 2022 | 0.0056395 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2022-09-08 17:47 | 2022-09-08 18:45 | 1 | 0:58 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE ENCONTRO CAUSA | M22090800235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2022-09-08 | 58 | keep | 0 | Sep | 2022 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-08 17:47 | 2022-09-08 19:30 | 10 | 1:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B22090800482 | New_Event | Secondary Wire Break | Include | Include | Equipment | 103 | 2022-09-08 | 1030 | keep | 0 | Sep | 2022 | 0.00070153 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-08 17:49 | 2022-09-09 09:53 | 12 | 16:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIAS | B22090800485 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 964 | 2022-09-08 | 11568 | keep | 0 | Sep | 2022 | 0.0078789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-09-08 17:55 | 2022-09-08 20:29 | 50 | 2:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REMPLAZO CAJA AVERIADA | C22090800163 | New_Event | Cutout Failure | Include | Include | Equipment | 154 | 2022-09-08 | 7700 | keep | 0 | Sep | 2022 | 0.0052444 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-09-08 18:08 | 2022-09-08 19:50 | 55 | 1:42 | P | DESGANCHE | 1X65 EN CORTE DE LINEA POR DESGANCHE | P22090800279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2022-09-08 | 5610 | keep | 0 | Sep | 2022 | 0.0038209 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
UTUADO | 2022-09-08 18:13 | 2022-09-08 20:15 | 40 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A22090800145 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2022-09-08 | 4880 | keep | 0 | Sep | 2022 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-09-08 18:17 | 2022-09-08 23:02 | 227 | 4:45 | P | MAL TIEMPO/RAYOS | 2 X 80 EN C/L RAYOS | S22090800591 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 285 | 2022-09-08 | 64695 | keep | 0 | Sep | 2022 | 0.044063 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
CANOVANAS | 2022-09-08 18:18 | 2022-09-08 19:44 | 40 | 1:26 | P | DESGANCHE | 1 X 40 EN C/L | R22090800167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2022-09-08 | 3440 | keep | 0 | Sep | 2022 | 0.002343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2022-09-08 18:25 | 2022-09-08 18:38 | 1117 | 0:13 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO SE ABRIO PARA NORMALIZAR NO FASEA GOI CG-220907-01B | C22090800167 | New_Event | UG Cable Fault | Include | Include | Equipment | 13 | 2022-09-08 | 14521 | keep | 0 | Sep | 2022 | 0.0098902 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
HUMACAO | 2022-09-08 18:26 | 2022-09-08 19:36 | 284 | 1:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C22090800166 | New_Event | Cutout Failure | Include | Include | Equipment | 70 | 2022-09-08 | 19880 | keep | 0 | Sep | 2022 | 0.01354 | 0.00019343 | Sustained | FALSE | FALSE | Not_TMED_Event | 284
SAN JUAN | 2022-09-08 18:33 | 2022-09-08 21:42 | 816 | 3:09 | P | MAL TIEMPO/RAYOS | 1 X 100 1 X 80 Y 1 X 65 EN CORTE DE LINEA DIFERENTES MAL TIEMPO RAYOS | S22090800605 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 189 | 2022-09-08 | 154224 | keep | 0 | Sep | 2022 | 0.10504 | 0.00055577 | Sustained | FALSE | FALSE | Not_TMED_Event | 816
AGUADILLA | 2022-09-08 18:36 | 2022-09-08 20:45 | 20 | 2:09 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M22090800239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2022-09-08 | 2580 | keep | 0 | Sep | 2022 | 0.0017572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-08 18:47 | 2022-09-08 20:23 | 10 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22090800148 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2022-09-08 | 960 | keep | 0 | Sep | 2022 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-08 18:56 | 2022-09-08 18:57 | 676 | 0:01 | T | ANIMAL | RECERRO INTERRUPTOR EN SERVICIO | C22090800191 | New_Event | Animals | Include | Include | Wildlife | 1 | 2022-09-08 | 676 | keep | 0 | Sep | 2022 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2022-09-08 18:57 | 2022-09-09 07:11 | 52 | 12:14 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | C22090800196 | 1st_after_momentary | Animals | Include | Include | Wildlife | 734 | 2022-09-08 | 38168 | keep | 0 | Sep | 2022 | 0.025996 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
SAN JUAN | 2022-09-08 18:59 | 2022-09-09 12:19 | 15 | 17:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO T-13 Y SE ENERGIZO SE DEJO N/O EN T-12 | S22090800632 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1040 | 2022-09-08 | 15600 | keep | 0 | Sep | 2022 | 0.010625 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2022-09-08 19:10 | 2022-09-09 08:45 | 75 | 13:35 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | B22090800541 | New_Event | Primary Wire Break | Include | Include | Equipment | 815 | 2022-09-08 | 61125 | keep | 0 | Sep | 2022 | 0.041632 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2022-09-08 19:13 | 2022-09-08 20:17 | 1500 | 1:04 | P | DESCONECTIVO DEFECTUOSO | MACHETES DE SALIDA QUEMADOS | A22090800158 | New_Event | Switch Failure | Include | Include | Equipment | 64 | 2022-09-08 | 96000 | keep | 0 | Sep | 2022 | 0.065385 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
BAYAMON | 2022-09-08 19:13 | 2022-09-08 21:16 | 187 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 140 EN C/L RAYOS | B22090800546 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-09-08 | 23001 | keep | 0 | Sep | 2022 | 0.015666 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
AGUADILLA | 2022-09-08 19:15 | 2022-09-08 20:40 | 40 | 1:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA / NO SE ENCONTRO CAUSA | M22090800242 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2022-09-08 | 3400 | keep | 0 | Sep | 2022 | 0.0023157 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2022-09-08 19:16 | 2022-09-08 20:50 | 1 | 1:34 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A22090800161 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 94 | 2022-09-08 | 94 | keep | 0 | Sep | 2022 | 6.4023e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-08 19:40 | 2022-09-08 20:50 | 18 | 1:10 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090800207 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 70 | 2022-09-08 | 1260 | keep | 0 | Sep | 2022 | 0.00085818 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-09-08 19:46 | 2022-09-08 21:44 | 3 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | A22090800203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2022-09-08 | 354 | keep | 0 | Sep | 2022 | 0.00024111 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2022-09-08 19:56 | 2022-09-09 15:40 | 133 | 19:44 | P | DESGANCHE | DESGANCHE SE REPARO BUSHING 1 X 50 EN CORTE DE LINEA SE CAMBIO CAJA PRIMARIA DEL TRANSFORMADOR | S22090800669 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1184 | 2022-09-08 | 157472 | keep | 0 | Sep | 2022 | 0.10725 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
FAJARDO | 2022-09-08 19:59 | 2022-09-08 20:00 | 1902 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090800174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 1902 | keep | 0 | Sep | 2022 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2022-09-08 20:02 | 2022-09-08 21:44 | 40 | 1:42 | P | CONDUCTOR ROTO O ABIERTO | FIJO BAJANTE DE CAJA A LINEA NO FUNDIO | R22090800175 | New_Event | Primary Wire Break | Include | Include | Equipment | 102 | 2022-09-08 | 4080 | keep | 0 | Sep | 2022 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2022-09-08 20:03 | 2022-09-09 01:29 | 15 | 5:26 | P | MAL TIEMPO/RAYOS | 1X65 EN C/L POR RAYOS | B22090800602 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 326 | 2022-09-08 | 4890 | keep | 0 | Sep | 2022 | 0.0033306 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-08 20:03 | 2022-09-09 10:15 | 15 | 14:12 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYO | B22090800603 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 852 | 2022-09-08 | 12780 | keep | 0 | Sep | 2022 | 0.0087044 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-09-08 20:07 | 2022-09-08 21:46 | 90 | 1:39 | P | SOBRECARGA | 1 X 100 EN CORTE DE LINEA POR CARGA | M22090800264 | New_Event | Trip Due To Overload | Include | Include | Other | 99 | 2022-09-08 | 8910 | keep | 0 | Sep | 2022 | 0.0060686 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2022-09-08 20:17 | 2022-09-08 21:11 | 4607 | 0:54 | T | DESCONECTIVO DEFECTUOSO | SE INSTALO PUENTE PORTATIL EN MACHETE AVERIADO Y SE CERRO INTERRUPTOR | A22090800235 | Additional_clients | Switch Failure | Include | Include | Equipment | 54 | 2022-09-08 | 248778 | keep | 0 | Sep | 2022 | 0.16944 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 20:26 | 2022-09-09 05:00 | 53 | 8:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L POR LLUVIA | B22090800619 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 514 | 2022-09-08 | 27242 | keep | 0 | Sep | 2022 | 0.018554 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
PONCE | 2022-09-08 20:50 | 2022-09-08 20:53 | 3114 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR SCADA | P22090800314 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-08 | 9342 | keep | 0 | Sep | 2022 | 0.0063628 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2022-09-08 20:57 | 2022-09-09 06:19 | 40 | 9:22 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B22090800631 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2022-09-08 | 22480 | keep | 0 | Sep | 2022 | 0.015311 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2022-09-08 20:59 | 2022-09-08 21:00 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C22090800219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 2450 | keep | 0 | Sep | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
BAYAMON | 2022-09-08 21:07 | 2022-09-08 22:33 | 150 | 1:26 | P | MAL TIEMPO/RAYOS | 1X80 DEL SU-6 @ RISER, 1X65 EN RISER CALLE 16, 1X40 EN PROVISIONAL AEREO CALLE 16, 1X30 OTRO PROVISIONAL AEREO CALLE 15, 1X15 EN XMR CALLE 15, 1X15 EN PM CALLE 15 POR TORMENTA ELECTRICA | B22090800637 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 86 | 2022-09-08 | 12900 | keep | 0 | Sep | 2022 | 0.0087861 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2022-09-08 21:26 | 2022-09-09 00:22 | 220 | 2:56 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P22090800324 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2022-09-08 | 38720 | keep | 0 | Sep | 2022 | 0.026372 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
MAYAGÃœEZ | 2022-09-08 21:30 | 2022-09-08 22:39 | 15 | 1:09 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | M22090800318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-09-08 | 1035 | keep | 0 | Sep | 2022 | 0.00070493 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-08 21:38 | 2022-09-09 01:50 | 82 | 4:12 | P | DESGANCHE | 1 X 50 EN C/L | R22090800190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2022-09-08 | 20664 | keep | 0 | Sep | 2022 | 0.014074 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
CAGUAS | 2022-09-08 21:38 | 2022-09-09 01:25 | 100 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L LLUVIAS | C22090800235 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2022-09-08 | 22700 | keep | 0 | Sep | 2022 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-09-08 21:47 | 2022-09-09 08:57 | 30 | 11:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22090800239 | New_Event | Cutout Failure | Include | Include | Equipment | 670 | 2022-09-08 | 20100 | keep | 0 | Sep | 2022 | 0.01369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-08 21:53 | 2022-09-09 14:57 | 20 | 17:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA EN VARIOS PUNTOS | S22090800688 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1024 | 2022-09-08 | 20480 | keep | 0 | Sep | 2022 | 0.013949 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-08 21:55 | 2022-09-08 23:41 | 283 | 1:46 | T | NO SE REPORTO CAUSA | DISPARO SE SECCIONALIZO EL BKR | C22090800244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 106 | 2022-09-08 | 29998 | keep | 0 | Sep | 2022 | 0.020432 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
SAN JUAN | 2022-09-08 22:00 | 2022-09-09 12:26 | 24 | 14:26 | P | DESGANCHE | SE HIZO DESGANCHE Y SE FIJO PUENTE DE LINEA A CAJA | S22090800705 | New_Event | Vegetation Contact | Include | Include | Vegetation | 866 | 2022-09-08 | 20784 | keep | 0 | Sep | 2022 | 0.014156 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2022-09-08 22:05 | 2022-09-09 09:45 | 12 | 11:40 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO EVENTO TRANSFERIDO DE CAGUAS | C22090800250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 700 | 2022-09-08 | 8400 | keep | 0 | Sep | 2022 | 0.0057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-09-08 22:10 | 2022-09-09 15:06 | 50 | 16:56 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO RAYOS | S22090800709 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1016 | 2022-09-08 | 50800 | keep | 0 | Sep | 2022 | 0.0346 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-08 22:13 | 2022-09-09 00:17 | 10 | 2:04 | P | NO SE REPORTO CAUSA | 1X8 EN T-30 | S22090800710 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2022-09-08 | 1240 | keep | 0 | Sep | 2022 | 0.00084456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-08 22:19 | 2022-09-09 20:16 | 15 | 21:57 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO Y SE CERRO PM#4 | M22090800234 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1317 | 2022-09-08 | 19755 | keep | 0 | Sep | 2022 | 0.013455 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-08 22:28 | 2022-09-09 09:10 | 40 | 10:42 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22090800665 | New_Event | Vegetation Contact | Include | Include | Vegetation | 642 | 2022-09-08 | 25680 | keep | 0 | Sep | 2022 | 0.017491 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-09-08 22:30 | 2022-09-08 23:58 | 200 | 1:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M22090800326 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2022-09-08 | 17600 | keep | 0 | Sep | 2022 | 0.011987 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2022-09-08 22:52 | 2022-09-09 14:50 | 50 | 15:58 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22090800196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 958 | 2022-09-08 | 47900 | keep | 0 | Sep | 2022 | 0.032624 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2022-09-08 23:00 | 2022-09-09 11:00 | 40 | 12:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN SWIT UNIT SE REPARO BASE DE PORTA FUSIBLE | P22090800340 | New_Event | Cutout Failure | Include | Include | Equipment | 720 | 2022-09-08 | 28800 | keep | 0 | Sep | 2022 | 0.019616 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-08 23:05 | 2022-09-09 03:23 | 129 | 4:18 | P | PARARRAYOS DEFECTUOSO | 1 X 80 SE REPARO BAJANTE PRIMARIO Y SE REMPLAZO PARARRAYO | C22090800269 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 258 | 2022-09-08 | 33282 | keep | 0 | Sep | 2022 | 0.022668 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
SAN JUAN | 2022-09-08 23:24 | 2022-09-09 17:10 | 10 | 17:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA RAMA SOBRE LINEA | S22090800724 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1066 | 2022-09-08 | 10660 | keep | 0 | Sep | 2022 | 0.0072605 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2022-09-08 23:25 | 2022-09-08 23:26 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22090800272 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-08 | 2203 | keep | 0 | Sep | 2022 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
GUAYAMA | 2022-09-08 23:30 | 2022-09-09 10:49 | 4 | 11:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22090800342 | New_Event | Secondary Wire Break | Include | Include | Equipment | 679 | 2022-09-08 | 2716 | keep | 0 | Sep | 2022 | 0.0018499 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2022-09-08 23:41 | 2022-09-08 23:47 | 32 | 0:06 | P | NO SE REPORTO CAUSA | EN SERVICIO NO CAUSA | C22090800244 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 6 | 2022-09-08 | 192 | keep | 0 | Sep | 2022 | 0.00013077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-08 23:45 | 2022-09-09 10:26 | 20 | 10:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | R22090800203 | New_Event | Cutout Failure | Include | Include | Equipment | 641 | 2022-09-08 | 12820 | keep | 0 | Sep | 2022 | 0.0087316 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-08 23:50 | 2022-09-09 08:05 | 40 | 8:15 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA / DESCARGAS ELECTRICAS | M22090800261 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 495 | 2022-09-08 | 19800 | keep | 0 | Sep | 2022 | 0.013486 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2022-09-09 00:59 | 2022-09-09 01:22 | 1483 | 0:23 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 20% DE SU CARGA POR PORTATIL 1348-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 SE CERRO POR CONTROL LUEGO DE VERIFICAR PERSONAL FUERA DE LA LINEA | S22090900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-09-09 | 34109 | keep | 0 | Sep | 2022 | 0.023231 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2022-09-09 00:59 | 2022-09-09 01:22 | 1531 | 0:23 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 20% DE SU CARGA POR PORTATIL 1348-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 SE CERRO POR CONTROL LUEGO DE VERIFICAR PERSONAL FUERA DE LA LINEA | S22090900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-09-09 | 35213 | keep | 0 | Sep | 2022 | 0.023983 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2022-09-09 00:59 | 2022-09-09 01:22 | 4232 | 0:23 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 20% DE SU CARGA POR PORTATIL 1348-08 LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 SE CERRO POR CONTROL LUEGO DE VERIFICAR PERSONAL FUERA DE LA LINEA | S22090900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2022-09-09 | 97336 | keep | 0 | Sep | 2022 | 0.066295 | 0.0028824 | Sustained | FALSE | FALSE | Not_TMED_Event | 4232
VEGA BAJA | 2022-09-09 01:11 | 2022-09-09 06:30 | 300 | 5:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22090900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2022-09-09 | 95700 | keep | 0 | Sep | 2022 | 0.065181 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2022-09-09 01:35 | 2022-09-09 09:10 | 30 | 7:35 | P | NO SE REPORTO CAUSA | 1 X 25 EN C/L | B22090900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 455 | 2022-09-09 | 13650 | keep | 0 | Sep | 2022 | 0.009297 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2022-09-09 01:39 | 2022-09-09 04:16 | 4027 | 2:37 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL NO SE ENCONTRO CAUSA | B22090900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-09-09 | 632239 | keep | 0 | Sep | 2022 | 0.43062 | 0.0027428 | Sustained | FALSE | FALSE | Not_TMED_Event | 4027
BARRANQUITAS | 2022-09-09 01:52 | 2022-09-09 17:05 | 72 | 15:13 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO PARARRAYO | C22090900007 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 913 | 2022-09-09 | 65736 | keep | 0 | Sep | 2022 | 0.044772 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2022-09-09 01:56 | 2022-09-09 01:59 | 1695 | 0:03 | P | NO SE REPORTO CAUSA | SE CERRO POR CONTROL 30% DE SU CARGA TRANSFERIDO AL 1346-02 | S22090900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-09 | 5085 | keep | 0 | Sep | 2022 | 0.0034634 | 0.0011545 | Momentary | FALSE | FALSE | Not_TMED_Event | 1695
BAYAMON | 2022-09-09 02:02 | 2022-09-09 10:00 | 10 | 7:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EM XMR LLUVIA | B22090900005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 478 | 2022-09-09 | 4780 | keep | 0 | Sep | 2022 | 0.0032556 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-09 02:29 | 2022-09-09 08:30 | 40 | 6:01 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R22090900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2022-09-09 | 14440 | keep | 0 | Sep | 2022 | 0.009835 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-09 03:23 | 2022-09-09 03:24 | 1565 | 0:01 | T | PARARRAYOS DEFECTUOSO | DISPARO NO RECIERRA CERRADO X CONTROL | C22090900010 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2022-09-09 | 1565 | keep | 0 | Sep | 2022 | 0.0010659 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-09 03:24 | 2022-09-09 14:06 | 129 | 10:42 | P | PARARRAYOS DEFECTUOSO | 1 X 80 SE REPARO BAJANTE PRIMARIO Y SE REMPLAZO PARARRAYO | C22090800269 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 642 | 2022-09-09 | 82818 | keep | 0 | Sep | 2022 | 0.056407 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
HUMACAO | 2022-09-09 04:00 | 2022-09-09 04:02 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO NO RECIERRA | C22090900014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-09 | 4252 | keep | 0 | Sep | 2022 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2022-09-09 04:26 | 2022-09-09 10:21 | 18 | 5:55 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | B22090900022 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 355 | 2022-09-09 | 6390 | keep | 0 | Sep | 2022 | 0.0043522 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2022-09-09 04:57 | 2022-09-09 09:22 | 6 | 4:25 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R22090900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 265 | 2022-09-09 | 1590 | keep | 0 | Sep | 2022 | 0.0010829 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2022-09-09 05:27 | 2022-09-09 06:11 | 150 | 0:44 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P22090900039 | New_Event | Animals | Include | Include | Wildlife | 44 | 2022-09-09 | 6600 | keep | 0 | Sep | 2022 | 0.0044952 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2022-09-09 05:48 | 2022-09-09 07:14 | 1860 | 1:26 | T | NO SE REPORTO CAUSA | SE PATRULLO NO SE REPORTO CAUSA SE BORRARON LAS BANDERAS Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S22090900071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2022-09-09 | 159960 | keep | 0 | Sep | 2022 | 0.10895 | 0.0012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 1860
BAYAMON | 2022-09-09 05:52 | 2022-09-09 11:40 | 20 | 5:48 | P | MAL TIEMPO/RAYOS | 1 X 15 1 X 15 EN XMR RAYOS | B22090900028 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 348 | 2022-09-09 | 6960 | keep | 0 | Sep | 2022 | 0.0047404 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-09 06:38 | 2022-09-09 11:02 | 10 | 4:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR PORTAFUSIBLE | B22090900084 | New_Event | Cutout Failure | Include | Include | Equipment | 264 | 2022-09-09 | 2640 | keep | 0 | Sep | 2022 | 0.0017981 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-09 06:40 | 2022-09-09 13:00 | 200 | 6:20 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA DESGANCHE | S22090900076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2022-09-09 | 76000 | keep | 0 | Sep | 2022 | 0.051763 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-09-09 06:42 | 2022-09-09 09:50 | 12 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 20 EN PROVISIONAL AERIO | B22090900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-09-09 | 2256 | keep | 0 | Sep | 2022 | 0.0015366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-09-09 07:04 | 2022-09-09 12:40 | 4 | 5:36 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO SECUNDARIA | P22090900058 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 336 | 2022-09-09 | 1344 | keep | 0 | Sep | 2022 | 0.00091539 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2022-09-09 07:10 | 2022-09-09 11:39 | 10 | 4:29 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22090900014 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 269 | 2022-09-09 | 2690 | keep | 0 | Sep | 2022 | 0.0018321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-09 07:14 | 2022-09-09 12:27 | 10 | 5:13 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | S22090800365 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 313 | 2022-09-09 | 3130 | keep | 0 | Sep | 2022 | 0.0021318 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-09 07:15 | 2022-09-09 16:19 | 1 | 9:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 25KVA X 37.5KVA | M22090900010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 544 | 2022-09-09 | 544 | keep | 0 | Sep | 2022 | 0.00037052 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-09 07:27 | 2022-09-09 16:00 | 15 | 8:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE XMR | B22090900038 | New_Event | Primary Wire Break | Include | Include | Equipment | 513 | 2022-09-09 | 7695 | keep | 0 | Sep | 2022 | 0.005241 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-09-09 07:32 | 2022-09-09 17:55 | 356 | 10:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C22090900037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 623 | 2022-09-09 | 221788 | keep | 0 | Sep | 2022 | 0.15106 | 0.00024247 | Sustained | FALSE | FALSE | Not_TMED_Event | 356
BARRANQUITAS | 2022-09-09 07:36 | 2022-09-09 09:30 | 10 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONECTORES SECUNDARIOS | C22090900038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2022-09-09 | 1140 | keep | 0 | Sep | 2022 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-09 07:40 | 2022-09-09 15:14 | 50 | 7:34 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B22090900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 454 | 2022-09-09 | 22700 | keep | 0 | Sep | 2022 | 0.015461 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2022-09-09 07:46 | 2022-09-09 10:55 | 60 | 3:09 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEA | R22090900011 | New_Event | Animals | Include | Include | Wildlife | 189 | 2022-09-09 | 11340 | keep | 0 | Sep | 2022 | 0.0077236 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2022-09-09 07:57 | 2022-09-09 14:30 | 15 | 6:33 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A22090900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 393 | 2022-09-09 | 5895 | keep | 0 | Sep | 2022 | 0.0040151 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-09 08:04 | 2022-09-09 12:20 | 75 | 4:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | B22090900047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 256 | 2022-09-09 | 19200 | keep | 0 | Sep | 2022 | 0.013077 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2022-09-09 08:05 | 2022-09-09 10:48 | 50 | 2:43 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R22090900014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2022-09-09 | 8150 | keep | 0 | Sep | 2022 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-09-09 08:11 | 2022-09-09 12:40 | 10 | 4:29 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C22090900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2022-09-09 | 2690 | keep | 0 | Sep | 2022 | 0.0018321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2022-09-09 08:13 | 2022-09-09 12:21 | 1 | 4:08 | P | ANIMAL | 2 X 30 EN RISER CRUCE POR IGUANA | R22090900013 | New_Event | Animals | Include | Include | Wildlife | 248 | 2022-09-09 | 248 | keep | 0 | Sep | 2022 | 0.00016891 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 08:16 | 2791 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090900035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 8373 | keep | 0 | Sep | 2022 | 0.0057028 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 08:16 | 1464 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090900035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 4392 | keep | 0 | Sep | 2022 | 0.0029914 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 08:16 | 759 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090900035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 2277 | keep | 0 | Sep | 2022 | 0.0015509 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 08:16 | 1500 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22090900035 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 4500 | keep | 0 | Sep | 2022 | 0.0030649 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 10:03 | 2132 | 1:50 | S | LINEA DE TRANSMISION 115KV | CERRADA LINEA 36100 RESTABLECIDO EL SERVICIO | A22090900041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 110 | 2022-09-09 | 234520 | keep | 0 | Sep | 2022 | 0.15973 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 10:03 | 2366 | 1:50 | S | LINEA DE TRANSMISION 115KV | CERRADA LINEA 36100 RESTABLECIDO EL SERVICIO | A22090900041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 110 | 2022-09-09 | 260260 | keep | 0 | Sep | 2022 | 0.17726 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 10:03 | 1976 | 1:50 | S | LINEA DE TRANSMISION 115KV | CERRADA LINEA 36100 RESTABLECIDO EL SERVICIO | A22090900041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 110 | 2022-09-09 | 217360 | keep | 0 | Sep | 2022 | 0.14804 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-09-09 08:13 | 2022-09-09 10:03 | 3688 | 1:50 | S | LINEA DE TRANSMISION 115KV | CERRADA LINEA 36100 RESTABLECIDO EL SERVICIO | A22090900041 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 110 | 2022-09-09 | 405680 | keep | 0 | Sep | 2022 | 0.27631 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
PONCE | 2022-09-09 08:22 | 2022-09-09 08:23 | 732 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22090900091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-09 | 732 | keep | 0 | Sep | 2022 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
CANOVANAS | 2022-09-09 08:50 | 2022-09-09 11:19 | 30 | 2:29 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R22090900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2022-09-09 | 4470 | keep | 0 | Sep | 2022 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-09 08:59 | 2022-09-09 15:16 | 10 | 6:17 | P | CAUSAS EXTERNAS | CONTRATISTA PRIVADO HALO CABLE SOTERRADO CON EXCAVADORA Y SACO PISTOLA DE BUSHING XMR, SE LLEVO PISTOLA A BUSHING | R22090900023 | New_Event | Damage From Public | Include | Include | Public | 377 | 2022-09-09 | 3770 | keep | 0 | Sep | 2022 | 0.0025677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-09 09:05 | 2022-09-09 15:30 | 7 | 6:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | S22090900109 | New_Event | Cutout Failure | Include | Include | Equipment | 385 | 2022-09-09 | 2695 | keep | 0 | Sep | 2022 | 0.0018356 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-09-09 09:10 | 2022-09-09 09:11 | 2791 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090900066 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-09 | 2791 | keep | 0 | Sep | 2022 | 0.0019009 | 0.0019009 | Momentary | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2022-09-09 09:10 | 2022-09-09 09:11 | 1464 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090900066 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-09 | 1464 | keep | 0 | Sep | 2022 | 0.00099712 | 0.00099712 | Momentary | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2022-09-09 09:10 | 2022-09-09 09:11 | 759 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090900066 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-09 | 759 | keep | 0 | Sep | 2022 | 0.00051695 | 0.00051695 | Momentary | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2022-09-09 09:10 | 2022-09-09 09:11 | 1500 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 | A22090900066 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-09 | 1500 | keep | 0 | Sep | 2022 | 0.0010216 | 0.0010216 | Momentary | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2022-09-09 09:16 | 2022-09-09 11:30 | 3 | 2:14 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR DE 25KVA X 25KVA | C22090900060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 134 | 2022-09-09 | 402 | keep | 0 | Sep | 2022 | 0.0002738 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-09-09 09:26 | 2022-09-09 09:28 | 3296 | 0:02 | T | PARARRAYOS DEFECTUOSO | DISPARO DE BREAKER SE CERRO POR CONTROL | C22090900063 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2022-09-09 | 6592 | keep | 0 | Sep | 2022 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2022-09-09 09:28 | 2022-09-09 13:31 | 10 | 4:03 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO Y BAJANTE PRIMARIO | C22090900088 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 243 | 2022-09-09 | 2430 | keep | 0 | Sep | 2022 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-09 09:32 | 2022-09-09 09:40 | 12 | 0:08 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA DESCONECTAR CLIENTE | B22090900068 | New_Event | Customer-Related Interruption | Include | Include | Public | 8 | 2022-09-09 | 96 | keep | 0 | Sep | 2022 | 6.5385e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-09-09 09:38 | 2022-09-09 15:32 | 100 | 5:54 | P | NO SE REPORTO CAUSA | 1 X 100 EN SU-1 1 X 25 EN SU-9 | S22090900112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 354 | 2022-09-09 | 35400 | keep | 0 | Sep | 2022 | 0.024111 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2022-09-09 09:41 | 2022-09-09 14:21 | 1 | 4:40 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22090900069 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 280 | 2022-09-09 | 280 | keep | 0 | Sep | 2022 | 0.00019071 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-09-09 09:50 | 2022-09-09 09:51 | 1444 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6014-02 EL CUAL ESTA LLEVANDO LA CARGA DEL 6014-01 | M22090900028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-09 | 1444 | keep | 0 | Sep | 2022 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-09-09 09:50 | 2022-09-09 09:51 | 3630 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE LE HIZO PRUEBA POR SCADA Y QUEDO EN SERVICIO | M22090900028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-09 | 3630 | keep | 0 | Sep | 2022 | 0.0024724 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
SAN JUAN | 2022-09-09 10:00 | 2022-09-09 13:21 | 8 | 3:21 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | S22090900174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2022-09-09 | 1608 | keep | 0 | Sep | 2022 | 0.0010952 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-09-09 10:06 | 2022-09-09 14:34 | 50 | 4:28 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C22090900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2022-09-09 | 13400 | keep | 0 | Sep | 2022 | 0.0091267 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2022-09-09 10:06 | 2022-09-09 13:16 | 8 | 3:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P22090900011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 190 | 2022-09-09 | 1520 | keep | 0 | Sep | 2022 | 0.0010353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2022-09-09 11:19 | 2022-09-10 13:06 | 15 | 25:47 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR DE 50KVA X 50KVA | C22090900080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1547 | 2022-09-09 | 23205 | keep | 0 | Sep | 2022 | 0.015805 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-09 11:25 | 2022-09-09 12:00 | 3 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS | R22090800180 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2022-09-09 | 105 | keep | 0 | Sep | 2022 | 7.1515e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2022-09-09 11:33 | 2022-09-09 11:42 | 1 | 0:09 | P | ANIMAL | 2 X 40 EN RISER AVE CRUZO LINEAS | P22090900128 | New_Event | Animals | Include | Include | Wildlife | 9 | 2022-09-09 | 9 | keep | 0 | Sep | 2022 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-09-09 11:36 | 2022-09-09 17:25 | 50 | 5:49 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22090900042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2022-09-09 | 17450 | keep | 0 | Sep | 2022 | 0.011885 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-09 11:39 | 2022-09-17 13:01 | 6 | 193:22 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE ROMPIO ACERA PARA REMPLAZAR BARRAS DE PEDESTAL | C22090900087 | New_Event |  |  |  |  | 11602 | 2022-09-09 | 69612 | keep | 0 | Sep | 2022 | 0.047412 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2022-09-09 11:54 | 2022-09-09 13:01 | 12 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON BARRAS EN PEDESTAL | R22090900051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2022-09-09 | 804 | keep | 0 | Sep | 2022 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2022-09-09 12:00 | 2022-09-09 17:13 | 46 | 5:13 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO RAYOS | S22090900268 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 313 | 2022-09-09 | 14398 | keep | 0 | Sep | 2022 | 0.0098064 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
MAYAGÃœEZ | 2022-09-09 12:06 | 2022-09-09 12:08 | 372 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6008-03 EL CUAL ESTA LLEVANDO LA CARGA DEL6008-02 | M22090900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-09 | 744 | keep | 0 | Sep | 2022 | 0.00050674 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
HUMACAO | 2022-09-09 12:15 | 2022-09-09 15:33 | 1 | 3:18 | P | MAL TIEMPO/RAYOS | 2 X 10 EN BANCO XMR MAL TIEMPO RAYOS | C22090900096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 198 | 2022-09-09 | 198 | keep | 0 | Sep | 2022 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2022-09-09 12:15 | 2022-09-09 14:25 | 1 | 2:10 | P | ANIMAL | 1 X 15 EN RISER CRUCE POR AVE | C22090900095 | New_Event | Animals | Include | Include | Wildlife | 130 | 2022-09-09 | 130 | keep | 0 | Sep | 2022 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-09 12:31 | 2022-09-09 13:40 | 1 | 1:09 | P | NO SE REPORTO CAUSA | 2 X 20 EN BANCO DE XMR | B22090900098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2022-09-09 | 69 | keep | 0 | Sep | 2022 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-09 12:44 | 2022-09-09 12:45 | 534 | 0:01 | T | DESGANCHE | RECERRO SU CARGA POR 1519-05 | S22090900192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-09 | 534 | keep | 0 | Sep | 2022 | 0.0003637 | 0.0003637 | Momentary | FALSE | FALSE | Not_TMED_Event | 534
SAN JUAN | 2022-09-09 12:44 | 2022-09-09 12:45 | 558 | 0:01 | T | DESGANCHE | RECERRO LLEVA 1519-01 | S22090900192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-09 | 558 | keep | 0 | Sep | 2022 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
SAN JUAN | 2022-09-09 12:45 | 2022-09-09 15:58 | 15 | 3:13 | P | DESGANCHE | 2 X 100 EN C/L SE DESGANCHE | S22090900200 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 193 | 2022-09-09 | 2895 | keep | 0 | Sep | 2022 | 0.0019718 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-09 12:57 | 2022-09-09 18:56 | 20 | 5:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN RISER SE REMPLAZO CAJA QUEMADA | S22090900195 | New_Event | Cutout Failure | Include | Include | Equipment | 359 | 2022-09-09 | 7180 | keep | 0 | Sep | 2022 | 0.0048903 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2022-09-09 13:00 | 2022-09-09 15:40 | 200 | 2:40 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE | S22090900108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2022-09-09 | 32000 | keep | 0 | Sep | 2022 | 0.021795 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2022-09-09 13:00 | 2022-09-09 17:10 | 80 | 4:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22090900106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 250 | 2022-09-09 | 20000 | keep | 0 | Sep | 2022 | 0.013622 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2022-09-09 13:02 | 2022-09-09 13:03 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | EN SERVICIO | R22090900056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-09 | 4188 | keep | 0 | Sep | 2022 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
AGUADILLA | 2022-09-09 13:02 | 2022-09-09 17:00 | 80 | 3:58 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M22090900178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2022-09-09 | 19040 | keep | 0 | Sep | 2022 | 0.012968 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2022-09-09 13:03 | 2022-09-09 15:35 | 75 | 2:32 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | A22090900095 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 152 | 2022-09-09 | 11400 | keep | 0 | Sep | 2022 | 0.0077645 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2022-09-09 13:05 | 2022-09-09 17:06 | 15 | 4:01 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYOS | B22090900102 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 241 | 2022-09-09 | 3615 | keep | 0 | Sep | 2022 | 0.0024622 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2022-09-09 13:14 | 2022-09-09 17:15 | 25 | 4:01 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 37.5 KVA A 2.4KV AVERIADO POR UNO IGUAL CAPACIDAD | P22090900140 | New_Event | Service Transformer Failure | Include | Include | Equipment | 241 | 2022-09-09 | 6025 | keep | 0 | Sep | 2022 | 0.0041036 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2022-09-09 13:16 | 2022-09-09 16:00 | 180 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA 1 X 80 EN CORTE DE LINEA | P22090900142 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2022-09-09 | 29520 | keep | 0 | Sep | 2022 | 0.020106 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
YAUCO | 2022-09-09 13:25 | 2022-09-09 14:20 | 10 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA 1 X 10 EN TRANSFORMADOR | P22090900147 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2022-09-09 | 550 | keep | 0 | Sep | 2022 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-09-09 13:34 | 2022-09-09 16:45 | 30 | 3:11 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CONVERTIDO 1 X 15 EN TRANSFORMADOR Y SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR DESCARGA ELECTRICA CAYO EN EL AREA Y CAUSO ESTAS AVERIAS | A22090900098 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 191 | 2022-09-09 | 5730 | keep | 0 | Sep | 2022 | 0.0039027 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2022-09-09 13:34 | 2022-09-09 13:37 | 934 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090900102 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 2802 | keep | 0 | Sep | 2022 | 0.0019084 | 0.00063614 | Momentary | FALSE | FALSE | Not_TMED_Event | 934
UTUADO | 2022-09-09 13:34 | 2022-09-09 13:37 | 4 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090900102 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 12 | keep | 0 | Sep | 2022 | 8.1731e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2022-09-09 13:34 | 2022-09-09 13:37 | 1479 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090900102 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 4437 | keep | 0 | Sep | 2022 | 0.003022 | 0.0010073 | Momentary | FALSE | FALSE | Not_TMED_Event | 1479
UTUADO | 2022-09-09 13:34 | 2022-09-09 13:37 | 1841 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090900103 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 5523 | keep | 0 | Sep | 2022 | 0.0037617 | 0.0012539 | Momentary | FALSE | FALSE | Not_TMED_Event | 1841
UTUADO | 2022-09-09 13:34 | 2022-09-09 13:37 | 1950 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36400 | A22090900103 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2022-09-09 | 5850 | keep | 0 | Sep | 2022 | 0.0039844 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
UTUADO | 2022-09-09 13:36 | 2022-09-09 13:38 | 1527 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | A22090900099 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2022-09-09 | 3054 | keep | 0 | Sep | 2022 | 0.0020801 | 0.00104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2022-09-09 13:38 | 2022-09-09 19:02 | 300 | 5:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | A22090900101 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 324 | 2022-09-09 | 97200 | keep | 0 | Sep | 2022 | 0.066202 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
FAJARDO | 2022-09-09 13:45 | 2022-09-09 14:13 | 10 | 0:28 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | R22090900061 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 28 | 2022-09-09 | 280 | keep | 0 | Sep | 2022 | 0.00019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-09-09 14:12 | 2022-09-09 16:40 | 30 | 2:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A22090900109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-09-09 | 4440 | keep | 0 | Sep | 2022 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2022-09-09 14:18 | 2022-09-09 16:30 | 1 | 2:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REEMPLAZO CAJA PRIMARIA | R22090900065 | New_Event | Cutout Failure | Include | Include | Equipment | 132 | 2022-09-09 | 132 | keep | 0 | Sep | 2022 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2022-09-09 14:22 | 2022-09-09 15:48 | 60 | 1:26 | P | PARARRAYOS DEFECTUOSO | 1 X 65 Y 1 X 80 EN CORTE DE LINEA SE RETIRO PARARRAYOS AVERIADOS | M22090900066 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 86 | 2022-09-09 | 5160 | keep | 0 | Sep | 2022 | 0.0035145 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-09 14:23 | 2022-09-09 16:00 | 12 | 1:37 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | B22090900107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2022-09-09 | 1164 | keep | 0 | Sep | 2022 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2022-09-09 14:30 | 2022-09-09 15:00 | 45 | 0:30 | P | CABLE SOTERRADO AVERIADO | TRABAJAR DESCONECTANDO PROVICIONAL AEREO EN T#25 | P22090900162 | New_Event | UG Cable Fault | Include | Include | Equipment | 30 | 2022-09-09 | 1350 | keep | 0 | Sep | 2022 | 0.00091948 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2022-09-09 14:30 | 2022-09-09 18:42 | 20 | 4:12 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR RAYO | M22090900070 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 252 | 2022-09-09 | 5040 | keep | 0 | Sep | 2022 | 0.0034327 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2022-09-09 14:34 | 2022-09-09 20:45 | 8 | 6:11 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO POSTE PRIMARIO PODRIDO PARTIDO | C22090900116 | New_Event | Primary Pole Failure | Include | Include | Equipment | 371 | 2022-09-09 | 2968 | keep | 0 | Sep | 2022 | 0.0020215 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2022-09-09 14:35 | 2022-09-09 18:33 | 15 | 3:58 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR RAYOS | M22090900072 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 238 | 2022-09-09 | 3570 | keep | 0 | Sep | 2022 | 0.0024315 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2022-09-09 14:36 | 2022-09-09 17:59 | 60 | 3:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | M22090900073 | New_Event | Cutout Failure | Include | Include | Equipment | 203 | 2022-09-09 | 12180 | keep | 0 | Sep | 2022 | 0.0082957 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2022-09-09 14:40 | 2022-09-09 17:46 | 70 | 3:06 | P | CAUSAS EXTERNAS | 1 X 80 Y 1 X 100 EN CORTE DE LINEA POR IMPACTO DE AUTO | M22090900076 | New_Event | Damage From Public | Include | Include | Public | 186 | 2022-09-09 | 13020 | keep | 0 | Sep | 2022 | 0.0088679 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:12 | 1924 | 0:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900190 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 30 | 2022-09-09 | 57720 | keep | 0 | Sep | 2022 | 0.039313 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:12 | 968 | 0:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900190 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 30 | 2022-09-09 | 29040 | keep | 0 | Sep | 2022 | 0.019779 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:12 | 680 | 0:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900190 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 30 | 2022-09-09 | 20400 | keep | 0 | Sep | 2022 | 0.013894 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:12 | 2246 | 0:30 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900190 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 30 | 2022-09-09 | 67380 | keep | 0 | Sep | 2022 | 0.045892 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:05 | 1569 | 0:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-09-09 | 36087 | keep | 0 | Sep | 2022 | 0.024579 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:05 | 2309 | 0:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-09-09 | 53107 | keep | 0 | Sep | 2022 | 0.036171 | 0.0015726 | Sustained | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:05 | 2179 | 0:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-09-09 | 50117 | keep | 0 | Sep | 2022 | 0.034134 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2022-09-09 14:42 | 2022-09-09 15:05 | 2440 | 0:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 | P22090900193 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 23 | 2022-09-09 | 56120 | keep | 0 | Sep | 2022 | 0.038223 | 0.0016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 2440
CANOVANAS | 2022-09-09 15:02 | 2022-09-09 15:50 | 10 | 0:48 | P | DESGANCHE | 1 X 10 EN XMR SE RETIRO ENREDADERA CRUZANDO CAJA PRIMARIA XMR | R22090900071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2022-09-09 | 480 | keep | 0 | Sep | 2022 | 0.00032693 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-09 15:06 | 2022-09-09 15:07 | 1225 | 0:01 | T | MAL TIEMPO/RAYOS | RECERRO LLEVA 1203-03 | S22090900000 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-09 | 1225 | keep | 0 | Sep | 2022 | 0.00083434 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-09 15:06 | 2022-09-09 15:07 | 616 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO CARGA POR 1203-01 | S22090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-09 | 616 | keep | 0 | Sep | 2022 | 0.00041955 | 0.00041955 | Momentary | FALSE | FALSE | Not_TMED_Event | 616
SAN JUAN | 2022-09-09 15:07 | 2022-09-09 18:40 | 50 | 3:33 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO RAYOS | S22090800709 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 213 | 2022-09-09 | 10650 | keep | 0 | Sep | 2022 | 0.0072537 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2022-09-09 15:07 | 2022-09-09 18:14 | 50 | 3:07 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M22090900085 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 187 | 2022-09-09 | 9350 | keep | 0 | Sep | 2022 | 0.0063682 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2022-09-09 15:09 | 2022-09-09 17:26 | 20 | 2:17 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | A22090900129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2022-09-09 | 2740 | keep | 0 | Sep | 2022 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2022-09-09 15:21 | 2022-09-09 16:44 | 15 | 1:23 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R22090900073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2022-09-09 | 1245 | keep | 0 | Sep | 2022 | 0.00084796 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2022-09-09 15:23 | 2022-09-09 20:58 | 35 | 5:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22090900198 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 335 | 2022-09-09 | 11725 | keep | 0 | Sep | 2022 | 0.0079858 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2022-09-09 15:29 | 2022-09-09 17:59 | 40 | 2:30 | P | DESGANCHE | SE REEMPLAZO 1X50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA PRIMARIA | M22090900054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2022-09-09 | 6000 | keep | 0 | Sep | 2022 | 0.0040866 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-09-09 15:29 | 2022-09-09 17:12 | 60 | 1:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | M22090900095 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 103 | 2022-09-09 | 6180 | keep | 0 | Sep | 2022 | 0.0042092 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2022-09-09 15:35 | 2022-09-09 17:02 | 10 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CONECTORES DE BAJANTE A SECUNDARIA | C22090900135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2022-09-09 | 870 | keep | 0 | Sep | 2022 | 0.00059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2022-09-09 15:40 | 2022-09-09 19:57 | 200 | 4:17 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE | S22090900108 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 257 | 2022-09-09 | 51400 | keep | 0 | Sep | 2022 | 0.035008 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2022-09-09 15:43 | 2022-09-09 19:46 | 8 | 4:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO PUENTE | M22090900106 | New_Event | Primary Wire Break | Include | Include | Equipment | 243 | 2022-09-09 | 1944 | keep | 0 | Sep | 2022 | 0.001324 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2022-09-09 15:48 | 2022-09-09 15:57 | 1444 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL EN EL CAMPO Y SE CERRO INTERRUPTOR | M22090900125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2022-09-09 | 12996 | keep | 0 | Sep | 2022 | 0.0088515 | 0.0009835 | Sustained | FALSE | FALSE | Not_TMED_Event | 1444
MAYAGÃœEZ | 2022-09-09 15:48 | 2022-09-09 15:57 | 3630 | 0:09 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL EN EL CAMPO Y SE CERRO INTERRUPTOR | M22090900125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 9 | 2022-09-09 | 32670 | keep | 0 | Sep | 2022 | 0.022251 | 0.0024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2022-09-09 15:57 | 2022-09-10 12:45 | 300 | 20:48 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22090900137 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1248 | 2022-09-09 | 374400 | keep | 0 | Sep | 2022 | 0.255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-09 16:09 | 2022-09-09 17:50 | 68 | 1:41 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22090900147 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 101 | 2022-09-09 | 6868 | keep | 0 | Sep | 2022 | 0.0046778 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
CANOVANAS | 2022-09-09 16:32 | 2022-09-09 17:56 | 50 | 1:24 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE PRIMARIO Y CAJA PRIMARIA | R22090900078 | New_Event | Primary Wire Break | Include | Include | Equipment | 84 | 2022-09-09 | 4200 | keep | 0 | Sep | 2022 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-09-09 16:41 | 2022-09-09 18:33 | 173 | 1:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C22090900158 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 112 | 2022-09-09 | 19376 | keep | 0 | Sep | 2022 | 0.013197 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
SAN JUAN | 2022-09-09 16:43 | 2022-09-09 16:45 | 5619 | 0:02 | P | MAL TIEMPO/RAYOS | DISPARO 90% POR 1620-03 MAL TIEMPO RAYOS | S22090900258 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2 | 2022-09-09 | 11238 | keep | 0 | Sep | 2022 | 0.0076542 | 0.0038271 | Momentary | FALSE | FALSE | Not_TMED_Event | 5619
SAN JUAN | 2022-09-09 16:43 | 2022-09-09 16:45 | 362 | 0:02 | P | MAL TIEMPO/RAYOS | DISPARO 90% POR 1620-03 MAL TIEMPO RAYOS | S22090900258 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2 | 2022-09-09 | 724 | keep | 0 | Sep | 2022 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2022-09-09 16:43 | 2022-09-09 16:45 | 36 | 0:02 | T | MAL TIEMPO/RAYOS | DISPARO SU CARGA POR 1620-03 MAL TIEMPO RAYOS | S22090900258 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2 | 2022-09-09 | 72 | keep | 0 | Sep | 2022 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2022-09-09 16:43 | 2022-09-09 16:45 | 1073 | 0:02 | T | MAL TIEMPO/RAYOS | DISPARO LLEVA 1620-01 LLEVA 90% DEL 1336-07 LLEVA 90% DEL 1336-10 SE PROBO QUEDO EN SERVICIO MAL TIEMPO RAYOS | S22090900258 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2 | 2022-09-09 | 2146 | keep | 0 | Sep | 2022 | 0.0014616 | 0.00073082 | Momentary | FALSE | FALSE | Not_TMED_Event | 1073
SAN JUAN | 2022-09-09 16:51 | 2022-09-09 16:53 | 225 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO CARGA X 1303-05 SE PROBO QUEDO EN SERVICIO | S22090900000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-09 | 450 | keep | 0 | Sep | 2022 | 0.00030649 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2022-09-09 16:51 | 2022-09-09 16:53 | 870 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO LLEVA 1303-04 SE PROBO QUEDO EN SERVICIO | S22090900000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2022-09-09 | 1740 | keep | 0 | Sep | 2022 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2022-09-09 16:57 | 2022-09-09 19:00 | 114 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYO | B22090900124 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2022-09-09 | 14022 | keep | 0 | Sep | 2022 | 0.0095503 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
VEGA BAJA | 2022-09-09 17:14 | 2022-09-09 19:36 | 200 | 2:22 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA CAIDA SOBRE LAS LINEAS | A22090900153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2022-09-09 | 28400 | keep | 0 | Sep | 2022 | 0.019343 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2022-09-09 17:15 | 2022-09-09 18:32 | 100 | 1:17 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22090900155 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 77 | 2022-09-09 | 7700 | keep | 0 | Sep | 2022 | 0.0052444 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2022-09-09 17:16 | 2022-09-10 09:38 | 12 | 16:22 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B22090900125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 982 | 2022-09-09 | 11784 | keep | 0 | Sep | 2022 | 0.008026 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2022-09-09 17:21 | 2022-09-09 18:31 | 75 | 1:10 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA PAJARO CRUZO FASE | P22090900225 | New_Event | Animals | Include | Include | Wildlife | 70 | 2022-09-09 | 5250 | keep | 0 | Sep | 2022 | 0.0035758 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2022-09-09 17:23 | 2022-09-10 10:05 | 3 | 16:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22090900160 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1002 | 2022-09-09 | 3006 | keep | 0 | Sep | 2022 | 0.0020474 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2022-09-09 17:32 | 2022-09-10 12:00 | 19 | 18:28 | P | DESGANCHE | 2 X 80 Y 1 X 100 EN C/L DESGANCHE | C22090900168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1108 | 2022-09-09 | 21052 | keep | 0 | Sep | 2022 | 0.014338 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
UTUADO | 2022-09-09 17:38 | 2022-09-10 10:00 | 4 | 16:22 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22090900172 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 982 | 2022-09-09 | 3928 | keep | 0 | Sep | 2022 | 0.0026753 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-09 17:50 | 2022-09-09 18:26 | 16 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA REPARAR BAJANTE SECUNDARIO Y VARIAS TOMAS | S22090900272 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2022-09-09 | 576 | keep | 0 | Sep | 2022 | 0.00039231 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2022-09-09 17:57 | 2022-09-09 18:00 | 143 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 80% DEL 1404-07 | S22090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-09 | 429 | keep | 0 | Sep | 2022 | 0.00029219 | 9.7397e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2022-09-09 17:57 | 2022-09-09 18:00 | 1085 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO 80% POR 1404-06 | S22090900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2022-09-09 | 3255 | keep | 0 | Sep | 2022 | 0.002217 | 0.00073899 | Momentary | FALSE | FALSE | Not_TMED_Event | 1085
CAGUAS | 2022-09-09 18:11 | 2022-09-09 19:14 | 203 | 1:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C22090900173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2022-09-09 | 12789 | keep | 0 | Sep | 2022 | 0.0087105 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
ARECIBO | 2022-09-09 18:26 | 2022-09-09 20:44 | 25 | 2:18 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A22090900194 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 138 | 2022-09-09 | 3450 | keep | 0 | Sep | 2022 | 0.0023498 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-09-09 18:28 | 2022-09-10 04:46 | 80 | 10:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M22090900177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 618 | 2022-09-09 | 49440 | keep | 0 | Sep | 2022 | 0.033673 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2022-09-09 18:32 | 2022-09-09 21:30 | 15 | 2:58 | P | MAL TIEMPO/RAYOS | 1 X 15 EN RISER POR RAYOS | M22090900180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 178 | 2022-09-09 | 2670 | keep | 0 | Sep | 2022 | 0.0018185 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-09 18:33 | 2022-09-09 19:20 | 11 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRA EN PEDESTAL | R22090900083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2022-09-09 | 517 | keep | 0 | Sep | 2022 | 0.00035213 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2022-09-09 18:37 | 2022-09-11 10:21 | 1 | 39:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A22090900198 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2384 | 2022-09-09 | 2384 | keep | 0 | Sep | 2022 | 0.0016237 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-09-09 18:42 | 2022-09-10 11:43 | 3 | 17:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C22090900179 | New_Event | Cutout Failure | Include | Include | Equipment | 1021 | 2022-09-09 | 3063 | keep | 0 | Sep | 2022 | 0.0020862 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2022-09-09 18:44 | 2022-09-09 20:23 | 200 | 1:39 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | R22090900086 | New_Event | Animals | Include | Include | Wildlife | 99 | 2022-09-09 | 19800 | keep | 0 | Sep | 2022 | 0.013486 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-09-09 18:49 | 2022-09-09 19:56 | 26 | 1:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN TRANSFORMADOR FUSIBLE CORROIDO | P22090900235 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2022-09-09 | 1742 | keep | 0 | Sep | 2022 | 0.0011865 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
SAN JUAN | 2022-09-09 18:56 | 2022-09-09 18:59 | 3708 | 0:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRE INTERRUPTOR A PETICION F. FEBRES CONECTOR QUEMANDOSE RISER AVE. ASHFORD #1510 SE ABRE POR SEGURIDAD | S22090900000 | Additional_clients | Cutout Failure | Include | Include | Equipment | 3 | 2022-09-09 | 11124 | keep | 0 | Sep | 2022 | 0.0075765 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-09 18:57 | 2022-09-10 00:45 | 4 | 5:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIAS Y VIENTOS FUERTES | M22090900188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 348 | 2022-09-09 | 1392 | keep | 0 | Sep | 2022 | 0.00094808 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2022-09-09 18:59 | 2022-09-09 19:41 | 20 | 0:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN RISER SE REMPLAZO CAJA QUEMADA | S22090900195 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 42 | 2022-09-09 | 840 | keep | 0 | Sep | 2022 | 0.00057212 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-09 18:59 | 2022-09-09 19:01 | 1403 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C22090900181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-09 | 2806 | keep | 0 | Sep | 2022 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
SAN JUAN | 2022-09-09 19:03 | 2022-09-09 22:47 | 60 | 3:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X100 EN C/L Y 1X80 EN RISER POR LLUVIA | S22090900315 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 224 | 2022-09-09 | 13440 | keep | 0 | Sep | 2022 | 0.0091539 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-09 19:11 | 2022-09-09 20:59 | 50 | 1:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS | S22090900319 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 108 | 2022-09-09 | 5400 | keep | 0 | Sep | 2022 | 0.0036779 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2022-09-09 19:21 | 2022-09-10 15:48 | 23 | 20:27 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C22090900183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1227 | 2022-09-09 | 28221 | keep | 0 | Sep | 2022 | 0.019221 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
MAYAGÃœEZ | 2022-09-09 19:33 | 2022-09-09 22:31 | 3 | 2:58 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REFIRIO SITUACION DE DESGANCHE | M22090900193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2022-09-09 | 534 | keep | 0 | Sep | 2022 | 0.0003637 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2022-09-09 19:36 | 2022-09-10 08:13 | 7 | 12:37 | P | ANIMAL | 1 X15 EN XMR AVE CRUZO LINEAS | P22090900239 | New_Event | Animals | Include | Include | Wildlife | 757 | 2022-09-09 | 5299 | keep | 0 | Sep | 2022 | 0.0036091 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2022-09-09 19:36 | 2022-09-09 19:42 | 2132 | 0:06 | T | DESGANCHE | SE ABRIO EL INTERRUPTOR 8801-03 A PETICION DE JUAN CARLOS RESTO PARA PODER RETIRAR UNA RAMA MUY GRANDE DE ARBOL QUE CAYO SOBRE LAS TRES FASES Y ESTABA A PUNTO DE ROMPERLAS SE RETIRO LA RAMA Y SE CERRO EL INTERRUPTOR LLEVA LA CARGA DEL 8801-01 | A22090900229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-09-09 | 12792 | keep | 0 | Sep | 2022 | 0.0087126 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-09 19:36 | 2022-09-09 19:42 | 1976 | 0:06 | T | DESGANCHE | SE ABRIO EL INTERRUPTOR 8801-03 A PETICION DE JUAN CARLOS RESTO PARA PODER RETIRAR UNA RAMA MUY GRANDE DE ARBOL QUE CAYO SOBRE LAS TRES FASES Y ESTABA A PUNTO DE ROMPERLAS SE RETIRO LA RAMA Y SE CERRO EL INTERRUPTOR LLEVA LA CARGA DEL 8801-01 | A22090900229 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 6 | 2022-09-09 | 11856 | keep | 0 | Sep | 2022 | 0.0080751 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2022-09-09 19:42 | 2022-09-09 19:59 | 200 | 0:17 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA CAIDA SOBRE LAS LINEAS | A22090900153 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 17 | 2022-09-09 | 3400 | keep | 0 | Sep | 2022 | 0.0023157 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-09 19:47 | 2022-09-10 12:46 | 10 | 16:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S22090900333 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1019 | 2022-09-09 | 10190 | keep | 0 | Sep | 2022 | 0.0069404 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2022-09-09 19:50 | 2022-09-09 21:23 | 436 | 1:33 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA | C22090900185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-09-09 | 40548 | keep | 0 | Sep | 2022 | 0.027617 | 0.00029696 | Sustained | FALSE | FALSE | Not_TMED_Event | 436
BAYAMON | 2022-09-09 20:01 | 2022-09-09 23:20 | 200 | 3:19 | P | DESGANCHE | 1X200 EN C/L SE REFIRIO PARA DESGANCHE | B22090900140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2022-09-09 | 39800 | keep | 0 | Sep | 2022 | 0.027108 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2022-09-09 20:41 | 2022-09-10 19:30 | 178 | 22:49 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA PARTIDA | P22090900244 | New_Event | Primary Wire Break | Include | Include | Equipment | 1369 | 2022-09-09 | 243682 | keep | 0 | Sep | 2022 | 0.16597 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
AGUADILLA | 2022-09-09 20:45 | 2022-09-09 21:54 | 2 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A22090900167 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2022-09-09 | 138 | keep | 0 | Sep | 2022 | 9.3991e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2022-09-09 20:47 | 2022-09-09 23:48 | 100 | 3:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R22090900107 | New_Event | Cutout Failure | Include | Include | Equipment | 181 | 2022-09-09 | 18100 | keep | 0 | Sep | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2022-09-09 21:06 | 2022-09-09 23:37 | 200 | 2:31 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO (RADIAL) | S22090900348 | New_Event | Primary Wire Break | Include | Include | Equipment | 151 | 2022-09-09 | 30200 | keep | 0 | Sep | 2022 | 0.020569 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2022-09-09 21:10 | 2022-09-09 21:11 | 2450 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO INTERRUPTOR EN SERVICIO | C22090900257 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-09 | 2450 | keep | 0 | Sep | 2022 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2022-09-09 21:11 | 2022-09-09 22:52 | 50 | 1:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | C22090900291 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 101 | 2022-09-09 | 5050 | keep | 0 | Sep | 2022 | 0.0034395 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2022-09-09 21:15 | 2022-09-10 09:58 | 60 | 12:43 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | C22090900260 | New_Event | Primary Wire Break | Include | Include | Equipment | 763 | 2022-09-09 | 45780 | keep | 0 | Sep | 2022 | 0.031181 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-09 21:18 | 2022-09-10 00:51 | 100 | 3:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN C/L SE REMPLAZO PORTAFUSIBLE | S22090900358 | New_Event | Cutout Failure | Include | Include | Equipment | 213 | 2022-09-09 | 21300 | keep | 0 | Sep | 2022 | 0.014507 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2022-09-09 21:56 | 2022-09-10 07:05 | 70 | 9:09 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22090900294 | New_Event | Vegetation Contact | Include | Include | Vegetation | 549 | 2022-09-09 | 38430 | keep | 0 | Sep | 2022 | 0.026174 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2022-09-09 21:57 | 2022-09-10 14:50 | 3 | 16:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE A CAJA DE TRANSFORMADOR | A22090900233 | New_Event | Primary Wire Break | Include | Include | Equipment | 1013 | 2022-09-09 | 3039 | keep | 0 | Sep | 2022 | 0.0020698 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2022-09-09 22:29 | 2022-09-11 06:20 | 80 | 31:51 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO | M22090900215 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1911 | 2022-09-09 | 152880 | keep | 0 | Sep | 2022 | 0.10413 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2022-09-09 22:39 | 2022-09-10 11:37 | 1 | 12:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A22090900234 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 778 | 2022-09-09 | 778 | keep | 0 | Sep | 2022 | 0.00052989 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2022-09-09 22:52 | 2022-09-10 09:51 | 80 | 10:59 | P | PROBLEMA DEL CLIENTE | 1 X 100 EN SU 27 CONTAMINACION EN SUBESTACION DE CONDOMINIO | R22090900112 | New_Event | Customer-Related Interruption | Include | Include | Public | 659 | 2022-09-09 | 52720 | keep | 0 | Sep | 2022 | 0.035907 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2022-09-09 22:52 | 2022-09-09 23:23 | 200 | 0:31 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO | C22090900291 | New_Event | Primary Wire Break | Include | Include | Equipment | 31 | 2022-09-09 | 6200 | keep | 0 | Sep | 2022 | 0.0042228 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2022-09-09 23:31 | 2022-09-10 01:14 | 573 | 1:43 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1704-04 QUE LLEVA LA CARGA DEL 1704-05 SE DESGANCHO ARBOL (A VARETA) DESDE EL SUELO MEDIANTE SWITCHING-FORM BY-220910-01 Y SE CERRO POR CONTROL | B22090900167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-09-09 | 59019 | keep | 0 | Sep | 2022 | 0.040198 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2022-09-09 23:31 | 2022-09-10 01:14 | 1313 | 1:43 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1704-04 QUE LLEVA LA CARGA DEL 1704-05 SE DESGANCHO ARBOL (A VARETA) DESDE EL SUELO MEDIANTE SWITCHING-FORM BY-220910-01 Y SE CERRO POR CONTROL | B22090900167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2022-09-09 | 135239 | keep | 0 | Sep | 2022 | 0.092111 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
UTUADO | 2022-09-09 23:41 | 2022-09-10 15:07 | 10 | 15:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | A22090900235 | New_Event | Service Transformer Failure | Include | Include | Equipment | 926 | 2022-09-09 | 9260 | keep | 0 | Sep | 2022 | 0.0063069 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2022-09-10 00:03 | 2022-09-10 16:15 | 40 | 16:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | A22091000002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 972 | 2022-09-10 | 38880 | keep | 0 | Sep | 2022 | 0.026481 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2022-09-10 00:10 | 2022-09-11 17:54 | 40 | 41:44 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO POSTE PARTIDO | M22091000436 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2504 | 2022-09-10 | 100160 | keep | 0 | Sep | 2022 | 0.068219 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2022-09-10 00:17 | 2022-09-10 01:43 | 1834 | 1:26 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO | C22091000002 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 86 | 2022-09-10 | 157724 | keep | 0 | Sep | 2022 | 0.10743 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2022-09-10 01:43 | 2022-09-10 02:25 | 1467 | 0:42 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO HACIA MH2 | C22091000002 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 42 | 2022-09-10 | 61614 | keep | 0 | Sep | 2022 | 0.041965 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-10 02:21 | 2022-09-10 15:09 | 100 | 12:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | C22091000009 | New_Event | Cutout Failure | Include | Include | Equipment | 768 | 2022-09-10 | 76800 | keep | 0 | Sep | 2022 | 0.052308 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2022-09-10 02:25 | 2022-09-10 02:26 | 1834 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA | C22091000002 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2022-09-10 | 1834 | keep | 0 | Sep | 2022 | 0.0012491 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2022-09-10 02:26 | 2022-09-10 09:31 | 112 | 7:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S22091000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2022-09-10 | 47600 | keep | 0 | Sep | 2022 | 0.03242 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
BARRANQUITAS | 2022-09-10 02:26 | 2022-09-10 03:05 | 1100 | 0:39 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | ABIERTO DEL MH1 HACIA MH2 Y ABIERTO MH4 HACIA MH2 | C22091000002 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 39 | 2022-09-10 | 42900 | keep | 0 | Sep | 2022 | 0.029219 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
BARRANQUITAS | 2022-09-10 02:42 | 2022-09-10 13:40 | 11 | 10:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C22091000012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 658 | 2022-09-10 | 7238 | keep | 0 | Sep | 2022 | 0.0049298 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-09-10 03:05 | 2022-09-10 03:15 | 1834 | 0:10 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO SE VERIFICO PERSONAL FUERA | C22091000002 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 10 | 2022-09-10 | 18340 | keep | 0 | Sep | 2022 | 0.012491 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-10 03:15 | 2022-09-10 04:25 | 550 | 1:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | MH2 VACCUUM SWITCH AVERIADO SIGUEN FUERA 40 CLIENTES | C22091000002 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 70 | 2022-09-10 | 38500 | keep | 0 | Sep | 2022 | 0.026222 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-10 04:25 | 2022-09-10 17:30 | 40 | 13:05 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO EL MH2 VACCUUM SWITCH AVERIADO 100% EN SERVICIO | C22091000002 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 785 | 2022-09-10 | 31400 | keep | 0 | Sep | 2022 | 0.021386 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-10 05:14 | 2022-09-10 18:34 | 60 | 13:20 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SE LEVANTO CONDUCTORES Y SE REEMPLAZO XMR 25KVA X 35 KVA | R22091000004 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 800 | 2022-09-10 | 48000 | keep | 0 | Sep | 2022 | 0.032693 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2022-09-10 06:47 | 2022-09-10 09:55 | 18 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | S22091000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2022-09-10 | 3384 | keep | 0 | Sep | 2022 | 0.0023048 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2022-09-10 06:51 | 2022-09-10 14:19 | 120 | 7:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 Y 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A22091000009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 448 | 2022-09-10 | 53760 | keep | 0 | Sep | 2022 | 0.036616 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2022-09-10 07:24 | 2022-09-10 09:14 | 20 | 1:50 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R22091000006 | New_Event | Animals | Include | Include | Wildlife | 110 | 2022-09-10 | 2200 | keep | 0 | Sep | 2022 | 0.0014984 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2022-09-10 07:24 | 2022-09-10 08:42 | 8 | 1:18 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22091000038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2022-09-10 | 624 | keep | 0 | Sep | 2022 | 0.000425 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2022-09-10 07:33 | 2022-09-10 08:35 | 1 | 1:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REMPLAZO PORTAFUSIBLE | B22091000017 | New_Event | Cutout Failure | Include | Include | Equipment | 62 | 2022-09-10 | 62 | keep | 0 | Sep | 2022 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2022-09-10 07:40 | 2022-09-10 10:50 | 34 | 3:10 | P | ANIMAL | 1 X 20 EN C/L Y 1 X 40 EN C/L CRUCE POR AVE | C22091000042 | New_Event | Animals | Include | Include | Wildlife | 190 | 2022-09-10 | 6460 | keep | 0 | Sep | 2022 | 0.0043999 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CAGUAS | 2022-09-10 07:43 | 2022-09-10 10:48 | 11 | 3:05 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C22091000043 | New_Event | Animals | Include | Include | Wildlife | 185 | 2022-09-10 | 2035 | keep | 0 | Sep | 2022 | 0.001386 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2022-09-10 07:57 | 2022-09-10 17:06 | 11 | 9:09 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE SECUNDARIO | C22091000050 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 549 | 2022-09-10 | 6039 | keep | 0 | Sep | 2022 | 0.0041131 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2022-09-10 08:01 | 2022-09-10 11:38 | 29 | 3:37 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C22091000068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2022-09-10 | 6293 | keep | 0 | Sep | 2022 | 0.0042861 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2022-09-10 08:08 | 2022-09-10 10:50 | 18 | 2:42 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B22091000019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2022-09-10 | 2916 | keep | 0 | Sep | 2022 | 0.0019861 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2022-09-10 08:11 | 2022-09-10 16:12 | 6 | 8:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO 25KVA X 25KVA | R22091000011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 481 | 2022-09-10 | 2886 | keep | 0 | Sep | 2022 | 0.0019656 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2022-09-10 08:24 | 2022-09-10 10:00 | 1 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C22091000059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2022-09-10 | 96 | keep | 0 | Sep | 2022 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2022-09-10 08:42 | 2022-09-10 08:44 | 2192 | 0:02 | T | DESGANCHE | DISPARO DE BKR SE CERRO POR CONTROL | C22091000064 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2022-09-10 | 4384 | keep | 0 | Sep | 2022 | 0.0029859 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-10 08:44 | 2022-09-10 12:17 | 80 | 3:33 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE Y TAMBIEN SE REPARON CONEXIONES SECUNDARIAS | S22091000014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2022-09-10 | 17040 | keep | 0 | Sep | 2022 | 0.011606 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2022-09-10 08:44 | 2022-09-10 18:40 | 8 | 9:56 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C22091000038 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 596 | 2022-09-10 | 4768 | keep | 0 | Sep | 2022 | 0.0032475 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2022-09-10 08:52 | 2022-09-10 08:53 | 1173 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN C/L | P22091000051 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2022-09-10 | 1173 | keep | 0 | Sep | 2022 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
AGUADILLA | 2022-09-10 09:04 | 2022-09-10 12:05 | 100 | 3:01 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000028 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 181 | 2022-09-10 | 18100 | keep | 0 | Sep | 2022 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2022-09-10 09:06 | 2022-09-10 16:20 | 20 | 7:14 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA REQUIERE DESGANCHE | M22091000029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2022-09-10 | 8680 | keep | 0 | Sep | 2022 | 0.0059119 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2022-09-10 09:07 | 2022-09-10 09:08 | 2888 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR NO RECIERRA SE REALIZA PRUEBA Y QUEDA EN SERVICIO | A22091000029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2022-09-10 | 2888 | keep | 0 | Sep | 2022 | 0.001967 | 0.001967 | Momentary | FALSE | FALSE | Not_TMED_Event | 2888
VEGA BAJA | 2022-09-10 09:08 | 2022-09-10 12:23 | 350 | 3:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN C/L SE REMPLAZO AISLADOR | A22091000040 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 195 | 2022-09-10 | 68250 | keep | 0 | Sep | 2022 | 0.046485 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BARRANQUITAS | 2022-09-10 09:10 | 2022-09-10 14:17 | 44 | 5:07 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C22091000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2022-09-10 | 13508 | keep | 0 | Sep | 2022 | 0.0092002 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2022-09-10 09:12 | 2022-09-10 09:13 | 1976 | 0:01 | T | LINEA DE TRANSMISION 115KV | SE ABRIO INTERRUPTOR PARA PODER ABRIR MACHETES SOLIDOS QUE TENIA COLMENA DE AVEJAS ESTO ES PARA PODER REALIZAR DESGANCHE MASIVO EN LINEA 36100 Y DISTRIBUCION DEBAJO | A22091000049 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-10 | 1976 | keep | 0 | Sep | 2022 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2022-09-10 09:13 | 2022-09-10 11:50 | 1 | 2:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE XMR | B22091000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2022-09-10 | 157 | keep | 0 | Sep | 2022 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2022-09-10 09:13 | 2022-09-10 10:43 | 800 | 1:30 | P | LINEA DE TRANSMISION 115KV | VIA LIBRE DE EMERGENCIA PARA PODER REALIZAR DESGANCHE EN LINEA 36100 DISTRIBUCION DEBAJO | A22091000046 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 90 | 2022-09-10 | 72000 | keep | 0 | Sep | 2022 | 0.049039 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
CAGUAS | 2022-09-10 09:28 | 2022-09-11 08:59 | 10 | 23:31 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR DE 75KVA X 75KVA | C22091000076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1411 | 2022-09-10 | 14110 | keep | 0 | Sep | 2022 | 0.0096103 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-09-10 09:48 | 2022-09-10 12:07 | 10 | 2:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R22091000022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-09-10 | 1390 | keep | 0 | Sep | 2022 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2022-09-10 09:48 | 2022-09-10 12:00 | 10 | 2:12 | P | CABLE SOTERRADO AVERIADO | SE ABRIO XMR PARA DESCONECTAR RISER DE PROVISIONAL AEREO | P22091000058 | New_Event | UG Cable Fault | Include | Include | Equipment | 132 | 2022-09-10 | 1320 | keep | 0 | Sep | 2022 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2022-09-10 10:00 | 2022-09-10 15:23 | 150 | 5:23 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA REMPLAZO DE POSTE | M22091000043 | New_Event | Primary Pole Failure | Include | Include | Equipment | 323 | 2022-09-10 | 48450 | keep | 0 | Sep | 2022 | 0.032999 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-09-10 10:04 | 2022-09-10 11:32 | 15 | 1:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22091000023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 88 | 2022-09-10 | 1320 | keep | 0 | Sep | 2022 | 0.00089905 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2022-09-10 10:08 | 2022-09-10 12:35 | 40 | 2:27 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22091000045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2022-09-10 | 5880 | keep | 0 | Sep | 2022 | 0.0040048 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-10 10:11 | 2022-09-10 11:15 | 3046 | 1:04 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO INTERRUPTOR 1646-03 SECCIONALIZANDO ALIMENTADOR . 40 % ALIMENTADOR EN SERVICIO Y FUERA CARGA DE 15% 1647-09 | R22091000026 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 64 | 2022-09-10 | 194944 | keep | 0 | Sep | 2022 | 0.13278 | 0.0020746 | Sustained | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2022-09-10 10:11 | 2022-09-10 11:48 | 308 | 1:37 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO DE RISER HACIA SU 1A SECCIONALIZANDO DE SU A HACIA SU AA 70% 1646-03 EN SERVICIO Y 15% 1647-09 EN SERVICIO | R22091000026 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 97 | 2022-09-10 | 29876 | keep | 0 | Sep | 2022 | 0.020348 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-09-10 10:30 | 2022-09-10 12:17 | 10 | 1:47 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR CON DERRAME DE ACEITE | B22091000025 | New_Event | Service Transformer Failure | Include | Include | Equipment | 107 | 2022-09-10 | 1070 | keep | 0 | Sep | 2022 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2022-09-10 10:31 | 2022-09-10 11:20 | 12 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22090900138 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2022-09-10 | 588 | keep | 0 | Sep | 2022 | 0.00040048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 2791 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000071 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 360039 | keep | 0 | Sep | 2022 | 0.24522 | 0.0019009 | Sustained | FALSE | FALSE | Not_TMED_Event | 2791
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 1464 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000071 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 188856 | keep | 0 | Sep | 2022 | 0.12863 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 759 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000071 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 97911 | keep | 0 | Sep | 2022 | 0.066687 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 1500 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000071 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 193500 | keep | 0 | Sep | 2022 | 0.13179 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 2132 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000072 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 275028 | keep | 0 | Sep | 2022 | 0.18732 | 0.0014521 | Sustained | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 2366 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000072 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 305214 | keep | 0 | Sep | 2022 | 0.20788 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 1976 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000072 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 254904 | keep | 0 | Sep | 2022 | 0.17361 | 0.0013458 | Sustained | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2022-09-10 10:43 | 2022-09-10 12:52 | 3688 | 2:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 | A22091000072 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 129 | 2022-09-10 | 475752 | keep | 0 | Sep | 2022 | 0.32403 | 0.0025119 | Sustained | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2022-09-10 10:50 | 2022-09-10 12:02 | 10 | 1:12 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA CONECTAR TOMA DE CLIENTE NUEVO | B22091000026 | New_Event |  |  |  |  | 72 | 2022-09-10 | 720 | keep | 0 | Sep | 2022 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2022-09-10 11:07 | 2022-09-10 14:16 | 11 | 3:09 | P | DESGANCHE | 1 X 20 EN AEREO PROVISIONAL SE DESGANCHO | R22091000060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2022-09-10 | 2079 | keep | 0 | Sep | 2022 | 0.001416 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2022-09-10 11:15 | 2022-09-10 11:31 | 1827 | 0:16 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR AL REALIZAR OPERACIONES PARA SECCIONALIZAR MACHETE QUEMADO EN SU AA | R22091000026 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 16 | 2022-09-10 | 29232 | keep | 0 | Sep | 2022 | 0.01991 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-10 11:19 | 2022-09-10 14:10 | 25 | 2:51 | P | SOBRECARGA | 1 X 65 EN CORTE DE LINEA SE INDICA QUE SOBRECARGA | M22091000060 | New_Event | Trip Due To Overload | Include | Include | Other | 171 | 2022-09-10 | 4275 | keep | 0 | Sep | 2022 | 0.0029117 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-09-10 11:31 | 2022-09-10 11:38 | 3046 | 0:07 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA. 40% EN SERVICIO 1646-03 Y FUERA 15% 1647-09 | R22091000026 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 7 | 2022-09-10 | 21322 | keep | 0 | Sep | 2022 | 0.014522 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-10 11:32 | 2022-09-10 12:29 | 296 | 0:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22091000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2022-09-10 | 16872 | keep | 0 | Sep | 2022 | 0.011491 | 0.0002016 | Sustained | FALSE | FALSE | Not_TMED_Event | 296
ARECIBO | 2022-09-10 11:35 | 2022-09-10 14:25 | 15 | 2:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A22091000091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 170 | 2022-09-10 | 2550 | keep | 0 | Sep | 2022 | 0.0017368 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2022-09-10 11:38 | 2022-09-10 11:48 | 1827 | 0:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CERRO DE RISER HACIA SU 1A SECCIONALIZANDO DE SU A HACIA SU AA 70% 1646-03 EN SERVICIO Y 15% 1647-09 EN SERVICIO | R22091000026 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 10 | 2022-09-10 | 18270 | keep | 0 | Sep | 2022 | 0.012444 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2022-09-10 11:43 | 2022-09-10 20:30 | 1 | 8:47 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO 2 TRANSFORMADOR AVERIADOS DE 37.5KVA X 37.5KVA EN BANCO TRIFASICO | C22090900179 | New_Event | Service Transformer Failure | Include | Include | Equipment | 527 | 2022-09-10 | 527 | keep | 0 | Sep | 2022 | 0.00035894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-10 11:47 | 2022-09-10 16:00 | 12 | 4:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22091000034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 253 | 2022-09-10 | 3036 | keep | 0 | Sep | 2022 | 0.0020678 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2022-09-10 11:48 | 2022-09-10 12:03 | 914 | 0:15 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO DE SU 1B HACIA SU AA POR MACHETE QUEMADO Y SE CERRO N/O CONTRA 2404-06 PASANDO 30% DE LA CARGA 1646-03. 100% EN SERVICIO | R22091000026 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 15 | 2022-09-10 | 13710 | keep | 0 | Sep | 2022 | 0.0093378 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2022-09-10 11:50 | 2022-09-10 12:50 | 15 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M22090600399 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-09-10 | 900 | keep | 0 | Sep | 2022 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-10 11:56 | 2022-09-10 14:24 | 621 | 2:28 | P | DESGANCHE | 1 X 100 EN C/L SE DESGANCHO | B22091000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2022-09-10 | 91908 | keep | 0 | Sep | 2022 | 0.062598 | 0.00042296 | Sustained | FALSE | FALSE | Not_TMED_Event | 621
BAYAMON | 2022-09-10 12:02 | 2022-09-10 12:03 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22091000039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 2234 | keep | 0 | Sep | 2022 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2022-09-10 12:03 | 2022-09-10 13:40 | 10 | 1:37 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA CONECTAR TOMA DE CLIENTE NUEVO | B22091000026 | Partial_restoration |  |  |  |  | 97 | 2022-09-10 | 970 | keep | 0 | Sep | 2022 | 0.00066066 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-10 12:06 | 2022-09-10 14:15 | 20 | 2:09 | P | NO SE REPORTO CAUSA | 1 X 40 EN PROVISIONAL AEREO | B22091000040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2022-09-10 | 2580 | keep | 0 | Sep | 2022 | 0.0017572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2022-09-10 12:10 | 2022-09-10 16:00 | 1000 | 3:50 | P | MAL TIEMPO/RAYOS | SE CERRO RECLOSER MAL TIEMPO DESCARGAS ELECTRICAS | M22091000082 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 230 | 2022-09-10 | 230000 | keep | 0 | Sep | 2022 | 0.15665 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
HUMACAO | 2022-09-10 12:20 | 2022-09-10 14:20 | 37 | 2:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN C/L SE REEMPLAZO AISLADOR PARTIDO | C22091000118 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2022-09-10 | 4440 | keep | 0 | Sep | 2022 | 0.0030241 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
FAJARDO | 2022-09-10 12:21 | 2022-09-10 18:10 | 20 | 5:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 C/L SE REEMPLAZO AISLADOR | R22091000091 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 349 | 2022-09-10 | 6980 | keep | 0 | Sep | 2022 | 0.004754 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-10 12:33 | 2022-09-10 15:58 | 22 | 3:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA | B22091000043 | New_Event | Cutout Failure | Include | Include | Equipment | 205 | 2022-09-10 | 4510 | keep | 0 | Sep | 2022 | 0.0030717 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2022-09-10 12:33 | 2022-09-10 14:46 | 18 | 2:13 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR RAYOS | B22091000044 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 133 | 2022-09-10 | 2394 | keep | 0 | Sep | 2022 | 0.0016305 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BAYAMON | 2022-09-10 12:35 | 2022-09-10 14:55 | 50 | 2:20 | P | ARBOL SOBRE LINEA | SE ABRIO C/L PARA RETIRAR ARBOL DE LA LINEA | B22091000045 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 140 | 2022-09-10 | 7000 | keep | 0 | Sep | 2022 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-10 12:36 | 2022-09-10 15:07 | 150 | 2:31 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PARARRAYO Y BAJANTE DE LINEA A CAJA | S22091000034 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 151 | 2022-09-10 | 22650 | keep | 0 | Sep | 2022 | 0.015427 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2022-09-10 12:43 | 2022-09-10 14:40 | 95 | 1:57 | P | MAL TIEMPO/RAYOS | 2 X 65 EN C/L RAYOS | B22091000046 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2022-09-10 | 11115 | keep | 0 | Sep | 2022 | 0.0075704 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2022-09-10 12:44 | 2022-09-10 16:45 | 15 | 4:01 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO | S22091000038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2022-09-10 | 3615 | keep | 0 | Sep | 2022 | 0.0024622 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-10 12:51 | 2022-09-10 18:42 | 364 | 5:51 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE HIZO DESGANCHE 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | S22091000041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2022-09-10 | 127764 | keep | 0 | Sep | 2022 | 0.087019 | 0.00024792 | Sustained | FALSE | FALSE | Not_TMED_Event | 364
VEGA BAJA | 2022-09-10 12:52 | 2022-09-10 18:30 | 800 | 5:38 | P | LINEA DE TRANSMISION 115KV | VIA LIBRE DE EMERGENCIA PARA PODER REALIZAR DESGANCHE EN LINEA 36100 DISTRIBUCION DEBAJO | A22091000046 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 338 | 2022-09-10 | 270400 | keep | 0 | Sep | 2022 | 0.18417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2022-09-10 12:58 | 2022-09-10 12:59 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22091000129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 1709 | keep | 0 | Sep | 2022 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
SAN JUAN | 2022-09-10 13:05 | 2022-09-10 13:06 | 3432 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECERRO 20% DE SU CARGA POR EL 1303-02. LLEVA 10% DEL 1204-03 | S22091000000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-10 | 3432 | keep | 0 | Sep | 2022 | 0.0023375 | 0.0023375 | Momentary | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-09-10 13:05 | 2022-09-10 13:06 | 138 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECERRO 10% DE SU CARGA ESTA POR 1204-02 | S22091000000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-10 | 138 | keep | 0 | Sep | 2022 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2022-09-10 13:05 | 2022-09-10 13:06 | 3955 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO LLEVA 80% DE SU CARGA LLEVA 10% 1204-03 | S22091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 3955 | keep | 0 | Sep | 2022 | 0.0026937 | 0.0026937 | Momentary | FALSE | FALSE | Not_TMED_Event | 3955
BAYAMON | 2022-09-10 13:05 | 2022-09-10 18:16 | 1 | 5:11 | P | DESGANCHE | 1 X 15 EN C/L DESGANCHE | S22091000050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2022-09-10 | 311 | keep | 0 | Sep | 2022 | 0.00021182 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2022-09-10 13:06 | 2022-09-10 15:37 | 60 | 2:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | S22091000052 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 151 | 2022-09-10 | 9060 | keep | 0 | Sep | 2022 | 0.0061707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2022-09-10 13:07 | 2022-09-10 13:08 | 2605 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22091000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 2605 | keep | 0 | Sep | 2022 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
MAYAGÃœEZ | 2022-09-10 13:07 | 2022-09-10 14:15 | 90 | 1:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22091000070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2022-09-10 | 6120 | keep | 0 | Sep | 2022 | 0.0041683 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2022-09-10 13:10 | 2022-09-10 15:23 | 50 | 2:13 | P | TERMINACION SOTERRADA AVERIADA | 1 X 65 EN C/L SE DIO MANTENIMIENTO A PISTOLA EN XMR SUMERGIBLE | B22091000052 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 133 | 2022-09-10 | 6650 | keep | 0 | Sep | 2022 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-09-10 13:10 | 2022-09-10 16:00 | 45 | 2:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22091000073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2022-09-10 | 7650 | keep | 0 | Sep | 2022 | 0.0052104 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2022-09-10 13:10 | 2022-09-10 16:00 | 1000 | 2:50 | P | MAL TIEMPO/RAYOS | SE CERRO RECLOSER MAL TIEMPO DESCARGAS ELECTRICAS | M22091000082 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 170 | 2022-09-10 | 170000 | keep | 0 | Sep | 2022 | 0.11579 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
AGUADILLA | 2022-09-10 13:10 | 2022-09-11 15:24 | 30 | 26:14 | P | ARBOL SOBRE LINEA | SE ABRE CORTE DE LINEA, SE DESGANCHA ARBOL SOBRE LINEA, 1 X 20 EN TRANSFORMADOR Y SE REPARO SECUNDARIA PARTIDA POR ARBOL | M22091000072 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1574 | 2022-09-10 | 47220 | keep | 0 | Sep | 2022 | 0.032161 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2022-09-10 13:12 | 2022-09-10 15:41 | 742 | 2:29 | T | MAL TIEMPO/RAYOS | DISPARO SE PATRULLO SE ABRIO MACHETE MALL OF SAN JUAN SE CERRO INTERRUPTOR SIN CARGA SE PATRULLO MAL TIEMPO/ RAYOS Y SE CERRO MACHETE 100% EN SERVICIO | S22091000096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 149 | 2022-09-10 | 110558 | keep | 0 | Sep | 2022 | 0.075301 | 0.00050537 | Sustained | FALSE | FALSE | Not_TMED_Event | 742
SAN JUAN | 2022-09-10 13:13 | 2022-09-10 13:14 | 262 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22091000069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-10 | 262 | keep | 0 | Sep | 2022 | 0.00017845 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2022-09-10 13:13 | 2022-09-10 13:14 | 296 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22091000069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-10 | 296 | keep | 0 | Sep | 2022 | 0.0002016 | 0.0002016 | Momentary | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2022-09-10 13:13 | 2022-09-10 13:14 | 79 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22091000069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-10 | 79 | keep | 0 | Sep | 2022 | 5.3807e-05 | 5.3807e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2022-09-10 13:13 | 2022-09-10 13:14 | 1129 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22091000069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-10 | 1129 | keep | 0 | Sep | 2022 | 0.00076896 | 0.00076896 | Momentary | FALSE | FALSE | Not_TMED_Event | 1129
SAN JUAN | 2022-09-10 13:13 | 2022-09-10 13:14 | 1573 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3600 | S22091000069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2022-09-10 | 1573 | keep | 0 | Sep | 2022 | 0.0010714 | 0.0010714 | Momentary | FALSE | FALSE | Not_TMED_Event | 1573
SAN JUAN | 2022-09-10 13:16 | 2022-09-10 14:31 | 3432 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | RECERRO QUEDO ABIERTO SE ENCONTRO LINEA EN EL PISO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 60% EN SERVICIO Y LLEVA 10% DEL 1204-03 | S22091000061 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 75 | 2022-09-10 | 257400 | keep | 0 | Sep | 2022 | 0.17531 | 0.0023375 | Sustained | FALSE | FALSE | Not_TMED_Event | 3432
SAN JUAN | 2022-09-10 13:16 | 2022-09-10 14:31 | 138 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | RECERRO QUEDO ABIERTO SE ENCONTRO LINEA EN EL PISO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 10% POR 1204-02 | S22091000061 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 75 | 2022-09-10 | 10350 | keep | 0 | Sep | 2022 | 0.0070493 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
BAYAMON | 2022-09-10 13:16 | 2022-09-10 13:17 | 4431 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO | B22091000059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 4431 | keep | 0 | Sep | 2022 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
MAYAGÃœEZ | 2022-09-10 13:25 | 2022-09-10 15:30 | 50 | 2:05 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000076 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 125 | 2022-09-10 | 6250 | keep | 0 | Sep | 2022 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2022-09-10 13:29 | 2022-09-10 16:33 | 60 | 3:04 | P | MAL TIEMPO/RAYOS | 1 X 100 1 X 20 EN C/L RAYOS | B22091000065 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 184 | 2022-09-10 | 11040 | keep | 0 | Sep | 2022 | 0.0075193 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2022-09-10 13:36 | 2022-09-10 21:08 | 15 | 7:32 | P | MAL TIEMPO/RAYOS | 1 X 15 Y 1 X 20 EN XMR MAL TIEMPO RAYOS | C22091000140 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 452 | 2022-09-10 | 6780 | keep | 0 | Sep | 2022 | 0.0046178 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-10 13:37 | 2022-09-10 13:38 | 3438 | 0:01 | T | CABLE SOTERRADO AVERIADO | RECERRO | B22091000067 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2022-09-10 | 3438 | keep | 0 | Sep | 2022 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
CANOVANAS | 2022-09-10 13:38 | 2022-09-10 13:39 | 2132 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO 70% DE SU CARGA Y 15% DE 1647-09 SE ENCONTRO PUENTE ABIERTO EN MACHETE. HUBO EVENTO DE RAYOS Y LLUVIA | R22091000026 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-10 | 2132 | keep | 0 | Sep | 2022 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
CANOVANAS | 2022-09-10 13:38 | 2022-09-10 13:39 | 308 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO 70% DE SU CARGA Y 15% DE 1647-09 LLUVIA FUERTE | R22091000026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2022-09-10 | 308 | keep | 0 | Sep | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2022-09-10 13:38 | 2022-09-10 16:25 | 40 | 2:47 | P | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO FASE DE RISER AVERIADA, SE CAMBIARON DE FASE LOS XMR SIN SERVICIO Y SE REFIERE PARA REPARAR TRAMO | B22091000073 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 167 | 2022-09-10 | 6680 | keep | 0 | Sep | 2022 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2022-09-10 13:39 | 2022-09-10 16:26 | 711 | 2:47 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO EN MACHETE LUEGO DE EVENTO DE MAL TIEMPO. RAYOS Y LLUVIA | R22091000133 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 167 | 2022-09-10 | 118737 | keep | 0 | Sep | 2022 | 0.080871 | 0.00048426 | Sustained | FALSE | FALSE | Not_TMED_Event | 711
BAYAMON | 2022-09-10 13:41 | 2022-09-10 13:42 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B22091000068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 325 | keep | 0 | Sep | 2022 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CAGUAS | 2022-09-10 13:43 | 2022-09-10 13:44 | 4390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C22091000143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 4390 | keep | 0 | Sep | 2022 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
MAYAGÃœEZ | 2022-09-10 13:53 | 2022-09-10 16:45 | 80 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000087 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2022-09-10 | 13760 | keep | 0 | Sep | 2022 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2022-09-10 14:01 | 2022-09-10 21:25 | 100 | 7:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | S22091000335 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 444 | 2022-09-10 | 44400 | keep | 0 | Sep | 2022 | 0.030241 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2022-09-10 14:01 | 2022-09-10 19:00 | 137 | 4:59 | P | MAL TIEMPO/RAYOS | 1 X 100 1 X 80 EN CORTE DE LINEA 2 X 10 EN YTRANSFORMADOR POR DESCARGA ELECTRICA | P22091000111 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 299 | 2022-09-10 | 40963 | keep | 0 | Sep | 2022 | 0.0279 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2022-09-10 14:06 | 2022-09-10 17:30 | 150 | 3:24 | P | TRANSFORMADOR AVERIADO | T-5 AVERIADO ( SE DEJO ABIERTO DE PROVISIONAL A T-5 Y SE REPUSO 1 X 100 Y 1 X 80 EN CORTE DE LINEA | S22091000105 | New_Event | Service Transformer Failure | Include | Include | Equipment | 204 | 2022-09-10 | 30600 | keep | 0 | Sep | 2022 | 0.020842 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2022-09-10 14:07 | 2022-09-10 14:08 | 2302 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE MAL TIEMPO | C22091000143 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-10 | 2302 | keep | 0 | Sep | 2022 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2022-09-10 14:08 | 2022-09-10 21:59 | 12 | 7:51 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO RAYOS | C22091000186 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 471 | 2022-09-10 | 5652 | keep | 0 | Sep | 2022 | 0.0038496 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2022-09-10 14:17 | 2022-09-10 14:18 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P22091000114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 3718 | keep | 0 | Sep | 2022 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2022-09-10 14:24 | 2022-09-10 15:30 | 17 | 1:06 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA ENDEREZARLO | B22091000072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 66 | 2022-09-10 | 1122 | keep | 0 | Sep | 2022 | 0.00076419 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2022-09-10 14:26 | 2022-09-10 15:40 | 309 | 1:14 | T | DESGANCHE | SE RETIRO BAMBUAS CAIDAS SOBRE EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M22091000106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2022-09-10 | 22866 | keep | 0 | Sep | 2022 | 0.015574 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
PONCE | 2022-09-10 14:29 | 2022-09-10 16:18 | 58 | 1:49 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P22091000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2022-09-10 | 6322 | keep | 0 | Sep | 2022 | 0.0043059 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
ARECIBO | 2022-09-10 14:29 | 2022-09-10 16:02 | 30 | 1:33 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA POR DESGANCHE | A22091000150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2022-09-10 | 2790 | keep | 0 | Sep | 2022 | 0.0019003 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-10 14:30 | 2022-09-11 11:00 | 150 | 20:30 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M22091000107 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1230 | 2022-09-10 | 184500 | keep | 0 | Sep | 2022 | 0.12566 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-09-10 14:30 | 2022-09-10 17:05 | 7 | 2:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | A22091000151 | New_Event | Service Transformer Failure | Include | Include | Equipment | 155 | 2022-09-10 | 1085 | keep | 0 | Sep | 2022 | 0.00073899 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2022-09-10 14:31 | 2022-09-10 17:14 | 929 | 2:43 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE | S22091000061 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 163 | 2022-09-10 | 151427 | keep | 0 | Sep | 2022 | 0.10314 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-10 14:32 | 2022-09-10 14:33 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R22091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 3464 | keep | 0 | Sep | 2022 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
SAN JUAN | 2022-09-10 14:44 | 2022-09-10 14:45 | 727 | 0:01 | T | DESGANCHE | RECERRO | S2209100000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2022-09-10 | 727 | keep | 0 | Sep | 2022 | 0.00049516 | 0.00049516 | Momentary | FALSE | FALSE | Not_TMED_Event | 727
SAN JUAN | 2022-09-10 14:45 | 2022-09-10 18:20 | 150 | 3:35 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE | S22091000147 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 215 | 2022-09-10 | 32250 | keep | 0 | Sep | 2022 | 0.021965 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2022-09-10 14:50 | 2022-09-10 20:45 | 25 | 5:55 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22091000157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 355 | 2022-09-10 | 8875 | keep | 0 | Sep | 2022 | 0.0060447 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2022-09-10 14:51 | 2022-09-10 17:15 | 50 | 2:24 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000122 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 144 | 2022-09-10 | 7200 | keep | 0 | Sep | 2022 | 0.0049039 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2022-09-10 14:55 | 2022-09-10 19:52 | 6 | 4:57 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO RAYOS | C22091000148 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 297 | 2022-09-10 | 1782 | keep | 0 | Sep | 2022 | 0.0012137 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2022-09-10 15:02 | 2022-09-10 19:25 | 60 | 4:23 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 263 | 2022-09-10 | 15780 | keep | 0 | Sep | 2022 | 0.010748 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-10 15:13 | 2022-09-10 21:00 | 150 | 5:47 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000143 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 347 | 2022-09-10 | 52050 | keep | 0 | Sep | 2022 | 0.035451 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2022-09-10 15:13 | 2022-09-10 19:25 | 50 | 4:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA 1 X 50 EN CORTE DE LINEA | P22091000133 | New_Event | Cutout Failure | Include | Include | Equipment | 252 | 2022-09-10 | 12600 | keep | 0 | Sep | 2022 | 0.0085818 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2022-09-10 15:17 | 2022-09-10 20:00 | 50 | 4:43 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000147 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 283 | 2022-09-10 | 14150 | keep | 0 | Sep | 2022 | 0.0096375 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2022-09-10 15:23 | 2022-09-10 15:32 | 1717 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22091000137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-09-10 | 15453 | keep | 0 | Sep | 2022 | 0.010525 | 0.0011694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1717
PONCE | 2022-09-10 15:23 | 2022-09-10 15:32 | 974 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22091000137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-09-10 | 8766 | keep | 0 | Sep | 2022 | 0.0059705 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2022-09-10 15:23 | 2022-09-10 15:32 | 1905 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22091000137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-09-10 | 17145 | keep | 0 | Sep | 2022 | 0.011677 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
PONCE | 2022-09-10 15:23 | 2022-09-10 15:32 | 1262 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22091000137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-09-10 | 11358 | keep | 0 | Sep | 2022 | 0.0077359 | 0.00085954 | Sustained | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2022-09-10 15:23 | 2022-09-10 15:32 | 200 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22091000137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-09-10 | 1800 | keep | 0 | Sep | 2022 | 0.001226 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2022-09-10 15:23 | 2022-09-10 15:32 | 222 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22091000138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-09-10 | 1998 | keep | 0 | Sep | 2022 | 0.0013608 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
PONCE | 2022-09-10 15:23 | 2022-09-10 15:32 | 537 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 300 | P22091000138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2022-09-10 | 4833 | keep | 0 | Sep | 2022 | 0.0032917 | 0.00036575 | Sustained | FALSE | FALSE | Not_TMED_Event | 537
ARECIBO | 2022-09-10 15:24 | 2022-09-10 17:21 | 120 | 1:57 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A22091000167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2022-09-10 | 14040 | keep | 0 | Sep | 2022 | 0.0095626 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2022-09-10 15:27 | 2022-09-10 17:26 | 182 | 1:59 | P | DESGANCHE | 1 X 10 EN XMR 1 X 100 EN C/L DESGANCHE | C22091000155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2022-09-10 | 21658 | keep | 0 | Sep | 2022 | 0.014751 | 0.00012396 | Sustained | FALSE | FALSE | Not_TMED_Event | 182
AGUADILLA | 2022-09-10 15:27 | 2022-09-10 17:30 | 40 | 2:03 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 65 EN CORTE DE LINEA SE RETEZO LINEA ARRIADA | M22091000167 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 123 | 2022-09-10 | 4920 | keep | 0 | Sep | 2022 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-09-10 15:30 | 2022-09-10 17:25 | 3 | 1:55 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22091000170 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 115 | 2022-09-10 | 345 | keep | 0 | Sep | 2022 | 0.00023498 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2022-09-10 15:31 | 2022-09-10 17:50 | 40 | 2:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M22091000174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2022-09-10 | 5560 | keep | 0 | Sep | 2022 | 0.0037869 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2022-09-10 15:36 | 2022-09-10 17:20 | 100 | 1:44 | P | MAL TIEMPO/RAYOS | 2 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000181 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2022-09-10 | 10400 | keep | 0 | Sep | 2022 | 0.0070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2022-09-10 15:38 | 2022-09-10 16:30 | 130 | 0:52 | P | DESGANCHE | 1 X 65 EN C/L SE REALIZO DESGANCHE | R22091000137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2022-09-10 | 6760 | keep | 0 | Sep | 2022 | 0.0046042 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2022-09-10 15:39 | 2022-09-10 20:09 | 154 | 4:30 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S22091000163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2022-09-10 | 41580 | keep | 0 | Sep | 2022 | 0.02832 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
PONCE | 2022-09-10 15:40 | 2022-09-10 15:41 | 2163 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE POR DESCARGA ELECTRICA | P22091000147 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2022-09-10 | 2163 | keep | 0 | Sep | 2022 | 0.0014732 | 0.0014732 | Momentary | FALSE | FALSE | Not_TMED_Event | 2163
MAYAGÃœEZ | 2022-09-10 15:43 | 2022-09-10 19:00 | 25 | 3:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000200 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 197 | 2022-09-10 | 4925 | keep | 0 | Sep | 2022 | 0.0033544 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2022-09-10 15:46 | 2022-09-10 20:36 | 44 | 4:50 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | R22091000141 | New_Event | Animals | Include | Include | Wildlife | 290 | 2022-09-10 | 12760 | keep | 0 | Sep | 2022 | 0.0086908 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
AGUADILLA | 2022-09-10 15:47 | 2022-09-11 11:35 | 60 | 19:48 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M22091000206 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1188 | 2022-09-10 | 71280 | keep | 0 | Sep | 2022 | 0.048548 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2022-09-10 15:47 | 2022-09-10 17:40 | 20 | 1:53 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000205 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 113 | 2022-09-10 | 2260 | keep | 0 | Sep | 2022 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2022-09-10 15:47 | 2022-09-10 20:06 | 30 | 4:19 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | A22091000173 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 259 | 2022-09-10 | 7770 | keep | 0 | Sep | 2022 | 0.0052921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2022-09-10 15:51 | 2022-09-10 19:51 | 10 | 4:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA EN PEDESTAL | C22091000163 | New_Event | Secondary Wire Break | Include | Include | Equipment | 240 | 2022-09-10 | 2400 | keep | 0 | Sep | 2022 | 0.0016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2022-09-10 15:52 | 2022-09-10 16:58 | 130 | 1:06 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A22091000177 | New_Event | Animals | Include | Include | Wildlife | 66 | 2022-09-10 | 8580 | keep | 0 | Sep | 2022 | 0.0058438 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2022-09-10 15:53 | 2022-09-10 18:20 | 10 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A22091000178 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2022-09-10 | 1470 | keep | 0 | Sep | 2022 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2022-09-10 15:54 | 2022-09-10 17:00 | 5 | 1:06 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M22091000220 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 66 | 2022-09-10 | 330 | keep | 0 | Sep | 2022 | 0.00022476 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2022-09-10 15:56 | 2022-09-10 19:11 | 19 | 3:15 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR 37.5 KVA AVERIADO SE LE DA SERVICIO A LOS CLIENTES PROVICIONALMENTE DE OTRA LINEA SECUNDARIA | P22091000153 | New_Event | Service Transformer Failure | Include | Include | Equipment | 195 | 2022-09-10 | 3705 | keep | 0 | Sep | 2022 | 0.0025235 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
AGUADILLA | 2022-09-10 16:05 | 2022-09-11 01:14 | 40 | 9:09 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M22091000234 | New_Event | Primary Wire Break | Include | Include | Equipment | 549 | 2022-09-10 | 21960 | keep | 0 | Sep | 2022 | 0.014957 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2022-09-10 16:12 | 2022-09-10 19:04 | 5 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A22091000183 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2022-09-10 | 860 | keep | 0 | Sep | 2022 | 0.00058574 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2022-09-10 16:17 | 2022-09-10 16:18 | 742 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S22091000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 742 | keep | 0 | Sep | 2022 | 0.00050537 | 0.00050537 | Momentary | FALSE | FALSE | Not_TMED_Event | 742
PONCE | 2022-09-10 16:18 | 2022-09-11 10:12 | 20 | 17:54 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P22091000163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1074 | 2022-09-10 | 21480 | keep | 0 | Sep | 2022 | 0.01463 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2022-09-10 16:23 | 2022-09-10 19:00 | 15 | 2:37 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO DE POSTE EN MALAS CONDICIONES | B22091000078 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 157 | 2022-09-10 | 2355 | keep | 0 | Sep | 2022 | 0.001604 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2022-09-10 16:25 | 2022-09-11 21:27 | 95 | 29:02 | P | CABLE SOTERRADO AVERIADO | SE PREPARO PROVISIONAL AEREO | B22091000087 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1742 | 2022-09-10 | 165490 | keep | 0 | Sep | 2022 | 0.11271 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-10 16:26 | 2022-09-10 16:27 | 2132 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR LLEVANDO 70% DE SU CARGA Y 15% DE 1647-09. 30% 1646-03 POR 2404-06 | R22091000133 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-10 | 2132 | keep | 0 | Sep | 2022 | 0.0014521 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2022-09-10 16:26 | 2022-09-10 16:27 | 308 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR LLEVANDO 70% DE SU CARGA Y 15% DE 1647-09. 30% 1646-03 POR 2404-06 | R22091000133 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2022-09-10 | 308 | keep | 0 | Sep | 2022 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2022-09-10 16:27 | 2022-09-10 19:15 | 711 | 2:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN MACHETE Y SE REEMPLAZO MACHETE | R22091000133 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 168 | 2022-09-10 | 119448 | keep | 0 | Sep | 2022 | 0.081355 | 0.00048426 | Sustained | FALSE | FALSE | Not_TMED_Event | 711
MAYAGÃœEZ | 2022-09-10 16:29 | 2022-09-10 18:00 | 50 | 1:31 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M22091000262 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2022-09-10 | 4550 | keep | 0 | Sep | 2022 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2022-09-10 16:32 | 2022-09-11 15:54 | 5 | 23:22 | P | TRANSFORMADOR AVERIADO | 2X15 EN XMR SE REMPLAZO XMR 50KVA - X - 50KVA @ 13KV | S22091000205 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1402 | 2022-09-10 | 7010 | keep | 0 | Sep | 2022 | 0.0047745 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2022-09-10 16:40 | 2022-09-10 17:40 | 15 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B22091000083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2022-09-10 | 900 | keep | 0 | Sep | 2022 | 0.00061299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2022-09-10 16:48 | 2022-09-10 16:50 | 271 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S22091000219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2022-09-10 | 542 | keep | 0 | Sep | 2022 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
ARECIBO | 2022-09-10 17:06 | 2022-09-10 18:08 | 100 | 1:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO FUERTE | A22091000190 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 62 | 2022-09-10 | 6200 | keep | 0 | Sep | 2022 | 0.0042228 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2022-09-10 17:08 | 2022-09-10 19:48 | 80 | 2:40 | P | MAL TIEMPO/RAYOS | 1 X 40 1 X 50 Y 1 X 65 EN C/L RAYO | R22091000174 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 160 | 2022-09-10 | 12800 | keep | 0 | Sep | 2022 | 0.008718 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2022-09-10 17:28 | 2022-09-10 20:50 | 7 | 3:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EN TRANSFORMADOR SE REPARO SECUNDARIA | M22091000304 | New_Event | Secondary Wire Break | Include | Include | Equipment | 202 | 2022-09-10 | 1414 | keep | 0 | Sep | 2022 | 0.00096307 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2022-09-10 17:29 | 2022-09-10 20:30 | 125 | 3:01 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000305 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 181 | 2022-09-10 | 22625 | keep | 0 | Sep | 2022 | 0.01541 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2022-09-10 17:30 | 2022-09-11 01:21 | 20 | 7:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO EL T-5 | S22091000105 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 471 | 2022-09-10 | 9420 | keep | 0 | Sep | 2022 | 0.0064159 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2022-09-10 17:30 | 2022-09-10 17:31 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B22091000093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2022-09-10 | 320 | keep | 0 | Sep | 2022 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
MAYAGÃœEZ | 2022-09-10 17:35 | 2022-09-10 18:45 | 7 | 1:10 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M2209100308 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 70 | 2022-09-10 | 490 | keep | 0 | Sep | 2022 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2022-09-10 17:38 | 2022-09-10 19:36 | 49 | 1:58 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA DESCARGA ELECTRICA | P22091000176 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 118 | 2022-09-10 | 5782 | keep | 0 | Sep | 2022 | 0.0039381 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
VEGA BAJA | 2022-09-10 17:41 | 2022-09-11 10:05 | 25 | 16:24 | P | ARBOL SOBRE LINEA | 2 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A22091000204 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 984 | 2022-09-10 | 24600 | keep | 0 | Sep | 2022 | 0.016755 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2022-09-10 17:43 | 2022-09-10 18:35 | 30 | 0:52 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | B22091000095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 52 | 2022-09-10 | 1560 | keep | 0 | Sep | 2022 | 0.0010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2022-09-10 17:45 | 2022-09-11 12:47 | 1 | 19:02 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN TRANSFORMADOR SE RETIRO BEJUCO DEL TRANSFORMADOR | M22091000312 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1142 | 2022-09-10 | 1142 | keep | 0 | Sep | 2022 | 0.00077781 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2022-09-10 17:46 | 2022-09-10 19:23 | 742 | 1:37 | T | DESCONECTIVO DEFECTUOSO | SE REMPLAZO 2 MACHETES QUEMADO SE ABRIO MACHETE PARA SECCIONALIZAR TRAMO 90% EN SERVICIO | S22091000260 | New_Event | Switch Failure | Include | Include | Equipment | 97 | 2022-09-10 | 71974 | keep | 0 | Sep | 2022 | 0.049021 | 0.00050537 | Sustained | FALSE | FALSE | Not_TMED_Event | 742
HUMACAO | 2022-09-10 17:46 | 2022-09-10 18:56 | 4 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C22091000185 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2022-09-10 | 280 | keep | 0 | Sep | 2022 | 0.00019071 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2022-09-10 17:51 | 2022-09-10 20:45 | 173 | 2:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA | P22091000181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2022-09-10 | 30102 | keep | 0 | Sep | 2022 | 0.020502 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
AGUADILLA | 2022-09-10 17:53 | 2022-09-10 19:25 | 30 | 1:32 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M22091000315 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 92 | 2022-09-10 | 2760 | keep | 0 | Sep | 2022 | 0.0018798 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30