GUAYAMA | 2023-03-29 17:31 | 2023-03-29 18:47 | 5 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA EN TRANSFORMADOR 1 X 15 | P23032900117 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2023-03-29 | 380 | keep | 0 | Mar | 2023 | 0.00025882 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-29 17:35 | 2023-03-29 17:36 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 931 CLIENTES DEL 2402-02 | R23032900305 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-29 | 1648 | keep | 0 | Mar | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-03-29 17:35 | 2023-03-29 17:36 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 2302-03 | R23032900305 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-29 | 931 | keep | 0 | Mar | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
SAN JUAN | 2023-03-29 17:49 | 2023-03-29 21:13 | 278 | 3:24 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | S23032900296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-03-29 | 56712 | keep | 0 | Mar | 2023 | 0.038626 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
BARRANQUITAS | 2023-03-29 17:57 | 2023-03-29 18:43 | 10 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO CAJA PRIMARIA DEL TRANSFORMADOR Y SE DIERON CONECTORES EN BAJANTE SECUNDARIO | C23032900154 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-03-29 | 460 | keep | 0 | Mar | 2023 | 0.0003133 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-29 18:12 | 2023-03-29 20:54 | 80 | 2:42 | P | ANIMAL | 1X65 EN C/L CRUCE POR AVE | B23032900218 | New_Event | Animals | Include | Include | Wildlife | 162 | 2023-03-29 | 12960 | keep | 0 | Mar | 2023 | 0.008827 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-03-29 18:33 | 2023-03-29 21:56 | 15 | 3:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA A @ LINEA EN XMR NO FUNDIO | B23032900230 | New_Event | Primary Wire Break | Include | Include | Equipment | 203 | 2023-03-29 | 3045 | keep | 0 | Mar | 2023 | 0.0020739 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-03-29 18:48 | 2023-03-29 20:44 | 64 | 1:56 | P | CONDUCTOR ROTO O ABIERTO | SE DESPEGO BAJANTE QUEMADO DE MACHETE | R23032900309 | New_Event | Primary Wire Break | Include | Include | Equipment | 116 | 2023-03-29 | 7424 | keep | 0 | Mar | 2023 | 0.0050565 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
VEGA BAJA | 2023-03-29 19:02 | 2023-03-30 11:30 | 14 | 16:28 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | A23032900196 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 988 | 2023-03-29 | 13832 | keep | 0 | Mar | 2023 | 0.0094209 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-03-29 20:54 | 2023-03-30 11:48 | 3 | 14:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23032900138 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 894 | 2023-03-29 | 2682 | keep | 0 | Mar | 2023 | 0.0018267 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-03-29 21:15 | 2023-03-30 08:27 | 30 | 11:12 | P | ANIMAL | 1 X 30 EN C/L 1 X 10 EN XMR CRUCE X REPTIL | C23032900167 | New_Event | Animals | Include | Include | Wildlife | 672 | 2023-03-29 | 20160 | keep | 0 | Mar | 2023 | 0.013731 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-03-29 21:43 | 2023-03-30 00:39 | 190 | 2:56 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23032900169 | New_Event | Animals | Include | Include | Wildlife | 176 | 2023-03-29 | 33440 | keep | 0 | Mar | 2023 | 0.022776 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
VEGA BAJA | 2023-03-29 22:22 | 2023-03-30 17:31 | 20 | 19:09 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23032900255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1149 | 2023-03-29 | 22980 | keep | 0 | Mar | 2023 | 0.015652 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-03-30 00:51 | 2023-03-30 09:40 | 40 | 8:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | M23033000001 | New_Event | Cutout Failure | Include | Include | Equipment | 529 | 2023-03-30 | 21160 | keep | 0 | Mar | 2023 | 0.014412 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-30 02:21 | 2023-03-30 02:22 | 652 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B2303300000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-30 | 652 | keep | 0 | Mar | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
AGUADILLA | 2023-03-30 02:26 | 2023-03-30 06:30 | 200 | 4:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 140 EN CORTE DE LINEA SE ABRIO PUENTES PRIMARIOS PARA SECCIONALIZAR POSTES PRIMARIOS AVERIADOS | M23033000002 | New_Event | Primary Pole Failure | Include | Include | Equipment | 244 | 2023-03-30 | 48800 | keep | 0 | Mar | 2023 | 0.033237 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-03-30 02:27 | 2023-03-30 02:29 | 652 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO CERRADO POR CONTROL | B2303300000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2023-03-30 | 1304 | keep | 0 | Mar | 2023 | 0.00088815 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
ARECIBO | 2023-03-30 02:38 | 2023-03-30 02:39 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23033100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-30 | 1227 | keep | 0 | Mar | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-03-30 02:40 | 2023-03-30 10:27 | 40 | 7:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA POR AISLADOR PARTIDO | A23033000001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 467 | 2023-03-30 | 18680 | keep | 0 | Mar | 2023 | 0.012723 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-03-30 02:51 | 2023-03-30 04:10 | 652 | 1:19 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTORES PRIMARIOS PARTIDOS EN CONVENTIDOR 25% EN SERVICIO | B2303300000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 79 | 2023-03-30 | 51508 | keep | 0 | Mar | 2023 | 0.035082 | 0.00044407 | Sustained | FALSE | FALSE | Not_TMED_Event | 652
CAGUAS | 2023-03-30 02:52 | 2023-03-30 07:44 | 50 | 4:52 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23033000002 | New_Event | Animals | Include | Include | Wildlife | 292 | 2023-03-30 | 14600 | keep | 0 | Mar | 2023 | 0.009944 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-03-30 03:31 | 2023-03-30 12:03 | 54 | 8:32 | P | CABLE SOTERRADO AVERIADO | 1X30 DE SU-4 @ T-40 AVERIA DE T-40 @ T-41 Y T-41 @ T-42 QUEDAN FUERA 39 CLIENTES | B23033000007 | New_Event | UG Cable Fault | Include | Include | Equipment | 512 | 2023-03-30 | 27648 | keep | 0 | Mar | 2023 | 0.018831 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BAYAMON | 2023-03-30 04:10 | 2023-03-30 05:25 | 489 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | BY-230330-01 SE SECCIONALIZO TRAMO PARA TRANSFERIR CARGA AL 9202-03 85% EN SERVICIO | B23033000005 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 75 | 2023-03-30 | 36675 | keep | 0 | Mar | 2023 | 0.024979 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-30 05:25 | 2023-03-30 20:34 | 97 | 15:09 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO CONDUCTOR PRIMARIO PARTIDO EN CONVERTIDOR MEDIANTE G.O.I. BY-230330-01 EN SERVICIO TOTAL | B23033000005 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 909 | 2023-03-30 | 88173 | keep | 0 | Mar | 2023 | 0.060054 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-03-30 06:27 | 2023-03-30 14:07 | 15 | 7:40 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | A23033000003 | New_Event | Animals | Include | Include | Wildlife | 460 | 2023-03-30 | 6900 | keep | 0 | Mar | 2023 | 0.0046996 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-03-30 06:30 | 2023-03-30 19:30 | 100 | 13:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZARON 3 POSTES PARTIDOS, SE REPARARON LINEAS PRIMARIAS Y SE CERRO PUENTES | M23033000002 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 780 | 2023-03-30 | 78000 | keep | 0 | Mar | 2023 | 0.053125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-30 07:11 | 2023-03-30 09:44 | 47 | 2:33 | P | ANIMAL | 1 X 50 EN C/L CRUCE X IGUANA | R23033000002 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-03-30 | 7191 | keep | 0 | Mar | 2023 | 0.0048978 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2023-03-30 07:17 | 2023-03-30 13:05 | 40 | 5:48 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23033000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2023-03-30 | 13920 | keep | 0 | Mar | 2023 | 0.0094808 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-03-30 07:26 | 2023-03-30 13:45 | 6 | 6:19 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN XMR PARA CERRAR PUENTE PRIMARIO DE LINEA @ CAJA | B23033000013 | New_Event | Primary Wire Break | Include | Include | Equipment | 379 | 2023-03-30 | 2274 | keep | 0 | Mar | 2023 | 0.0015488 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-30 07:27 | 2023-03-30 07:29 | 3005 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23033000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-30 | 6010 | keep | 0 | Mar | 2023 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
VEGA BAJA | 2023-03-30 07:54 | 2023-03-30 07:59 | 4027 | 0:05 | S | DESCONECTIVO DEFECTUOSO | MACHETES AVERIADOS EN 9105-06 AL OPERAR SE LLEVO LA BARRA DE DISTRIBUCION Y AFECTO LA CARGA DE LA 9101-00- SE CERRO POR CONTROL | B23033000021 | New_Event | Switch Failure | Include | Include | Equipment | 5 | 2023-03-30 | 20135 | keep | 0 | Mar | 2023 | 0.013714 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-03-30 07:54 | 2023-03-30 07:59 | 2468 | 0:05 | S | DESCONECTIVO DEFECTUOSO | MACHETES AVERIADOS EN 9105-06 AL OPERAR SE LLEVO LA BARRA DE DISTRIBUCION Y AFECTO LA CARGA DE LA 9101-00- SE CERRO POR CONTROL | B23033000021 | New_Event | Switch Failure | Include | Include | Equipment | 5 | 2023-03-30 | 12340 | keep | 0 | Mar | 2023 | 0.0084047 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-03-30 07:54 | 2023-03-30 07:59 | 1494 | 0:05 | S | CABLE SOTERRADO AVERIADO | MACHETES AVERIADO EN 9105-06 AL OPERAR SE LLEVO LA BARRA DE DISTRIBUCION Y AFECTO LA CARGA DE LA 9101-00- SE CERRO POR CONTROL | B23033000021 | New_Event | UG Cable Fault | Include | Include | Equipment | 5 | 2023-03-30 | 7470 | keep | 0 | Mar | 2023 | 0.0050878 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-03-30 07:54 | 2023-03-30 14:48 | 1310 | 6:54 | S | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON (2) MACHETES PRIMARIOS QUEMADOS EN 9105-06 QUE AL OPERAR SE LLEVO LA BARRA DE DISTRIBUCION MEDIANTE GOI 230330-02 Y SE CERRO POR CONTROL | B23033000017 | New_Event | Switch Failure | Include | Include | Equipment | 414 | 2023-03-30 | 542340 | keep | 0 | Mar | 2023 | 0.36939 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2023-03-30 07:54 | 2023-03-30 11:03 | 215 | 3:09 | S | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO AVERIA POR (2) MACHETES QUEMADOS EN 9105-06 QUE AL OPERAR SE LLEVO LA BARRA DE DISTRIBUCION - GOI BY-230330-02 - Y SE CERRO POR CONTROL | B23033000017 | New_Event | Switch Failure | Include | Include | Equipment | 189 | 2023-03-30 | 40635 | keep | 0 | Mar | 2023 | 0.027676 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-03-30 07:54 | 2023-03-30 11:04 | 1 | 3:10 | S | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO AVERIA POR (2) MACHETES QUEMADOS EN 9105-06 QUE AL OPERAR SE LLEVO LA BARRA DE DISTRIBUCION - GOI BY-230330-02 - Y SE CERRO POR CONTROL | B23033000017 | New_Event | Switch Failure | Include | Include | Equipment | 190 | 2023-03-30 | 190 | keep | 0 | Mar | 2023 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-30 08:27 | 2023-03-30 08:29 | 1483 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 30% DE LA CARGA POR EL 1336-08 SE CERRO POR SCADA | S23033000058 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-30 | 2966 | keep | 0 | Mar | 2023 | 0.0020201 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-03-30 08:27 | 2023-03-30 08:29 | 1531 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 15% DE LA CARGA POR EL 1336-08 SE CERRO POR SCADA | S23033000058 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-30 | 3062 | keep | 0 | Mar | 2023 | 0.0020855 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-03-30 08:27 | 2023-03-30 16:08 | 312 | 7:41 | P | CRUCETA DEFECTUOSA O AVERIADA | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% 1204-04 LLEVA 15% 1204-05 LLEVA 5% 1336-07 SE SECCIONALIZO AVERIA EN EL 1336-07 SE REMPLAZO CRUCETA PARTIDA Y ENTRO EL 5% EN SERVICIO MEDIANTE GOI SJ-230330-01 | S23033000058 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 461 | 2023-03-30 | 143832 | keep | 0 | Mar | 2023 | 0.097963 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-03-30 08:27 | 2023-03-30 08:29 | 4232 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR LLEVA 30% DE LA CARGA DEL 1204-04 LLEVA 15% DE LA CARGA DEL 1204-05 LLEVA 5% DE LA CARGA DEL 1336-07 SE SECCIONALIZO AVERIA EN EL 1336-07 Y SE CERRO POR SCADA LLEVA 80% DE SU CARGA | S23033000058 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-30 | 8464 | keep | 0 | Mar | 2023 | 0.0057648 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
BAYAMON | 2023-03-30 08:28 | 2023-03-30 12:30 | 50 | 4:02 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA CERRAR PUENTE PRIMARIO DE LINEA @ LINEA | B23033000023 | New_Event | Primary Wire Break | Include | Include | Equipment | 242 | 2023-03-30 | 12100 | keep | 0 | Mar | 2023 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-03-30 08:33 | 2023-03-30 10:00 | 75 | 1:27 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23033000020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-03-30 | 6525 | keep | 0 | Mar | 2023 | 0.0044441 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-03-30 08:37 | 2023-03-30 15:27 | 20 | 6:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X25 EN C/L SE REMPLAZO AISLADOR | B23033000027 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 410 | 2023-03-30 | 8200 | keep | 0 | Mar | 2023 | 0.005585 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-30 08:43 | 2023-03-30 10:57 | 250 | 2:14 | P | ANIMAL | 1 X 80 EN CL CRUCE DE FASE POR IGUANA | M23033000025 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-03-30 | 33500 | keep | 0 | Mar | 2023 | 0.022817 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2023-03-30 08:49 | 2023-03-30 11:04 | 27 | 2:15 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23033000018 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-03-30 | 3645 | keep | 0 | Mar | 2023 | 0.0024826 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BARRANQUITAS | 2023-03-30 08:50 | 2023-03-30 12:16 | 79 | 3:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23033000019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2023-03-30 | 16274 | keep | 0 | Mar | 2023 | 0.011084 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
AGUADILLA | 2023-03-30 08:55 | 2023-03-30 08:56 | 595 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR TIENE LA CARGA DEL 7902-02 | M23033000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-30 | 595 | keep | 0 | Mar | 2023 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2023-03-30 08:55 | 2023-03-30 08:56 | 51 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 7902-01 CON CARGA DEL 7902-02 | M23033000029 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-30 | 51 | keep | 0 | Mar | 2023 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-03-30 08:58 | 2023-03-30 10:00 | 1 | 1:02 | P | ANIMAL | 1X10 EN XMR CRUCE POR IGUANA | B23033000034 | New_Event | Animals | Include | Include | Wildlife | 62 | 2023-03-30 | 62 | keep | 0 | Mar | 2023 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 11:46 | 849 | 2:47 | S | NO SE REPORTO CAUSA | SE ENCONTRO FUSIBLE FUNDIDO EN LA ALTA SE REALIZARON OPERACIONES PARA TRANSFERIR LA CARGA SJ-230330-02 CONSERVACION DE SUBESTACIONES NO INFORMO AVERIA | S23033000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-03-30 | 141783 | keep | 0 | Mar | 2023 | 0.096568 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 12:07 | 893 | 3:08 | S | NO SE REPORTO CAUSA | SE ENCONTRO FUSIBLE FUNDIDO EN LA ALTA SE REALIZARON OPERACIONES PARA TRANSFERIR LA CARGA SJ-230330-02 CONSERVACION DE SUBESTACIONES NO INFORMO AVERIA | S23033000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-03-30 | 167884 | keep | 0 | Mar | 2023 | 0.11435 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 12:07 | 602 | 3:08 | S | NO SE REPORTO CAUSA | SE ENCONTRO FUSIBLE FUNDIDO EN LA ALTA SE REALIZARON OPERACIONES PARA TRANSFERIR LA CARGA SJ-230330-02 CONSERVACION DE SUBESTACIONES NO INFORMO AVERIA | S23033000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-03-30 | 113176 | keep | 0 | Mar | 2023 | 0.077084 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 13:14 | 43 | 4:15 | S | NO SE REPORTO CAUSA | SE ENCONTRO FUSIBLE FUNDIDO EN LA ALTA SE REALIZARON OPERACIONES PARA TRANSFERIR LA CARGA SJ-230330-02 CONSERVACION DE SUBESTACIONES NO INFORMO AVERIA | S23033000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 255 | 2023-03-30 | 10965 | keep | 0 | Mar | 2023 | 0.0074682 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 09:01 | 297 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 20% DE SU CARGA POR EL 1338-02 | S2303300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-30 | 594 | keep | 0 | Mar | 2023 | 0.00040457 | 0.00020229 | Momentary | FALSE | FALSE | Not_TMED_Event | 297
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 09:01 | 721 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 SUB. 1418 QUINTANA FUNDIÃ“ UN FUSIBLE. | S23033000022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-30 | 1442 | keep | 0 | Mar | 2023 | 0.00098214 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 09:01 | 325 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 SUB. 1418 QUINTANA FUNDIÃ“ UN FUSIBLE. | S23033000022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-30 | 650 | keep | 0 | Mar | 2023 | 0.00044271 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 09:01 | 600 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 SUB. 1418 QUINTANA FUNDIÃ“ UN FUSIBLE. | S23033000022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-30 | 1200 | keep | 0 | Mar | 2023 | 0.00081731 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 09:01 | 267 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 SUB. 1418 QUINTANA FUNDIÃ“ UN FUSIBLE. | S23033000022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-30 | 534 | keep | 0 | Mar | 2023 | 0.0003637 | 0.00018185 | Momentary | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2023-03-30 08:59 | 2023-03-30 09:01 | 621 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7200 SUB. 1418 QUINTANA FUNDIÃ“ UN FUSIBLE. | S23033000022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-03-30 | 1242 | keep | 0 | Mar | 2023 | 0.00084592 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
CANOVANAS | 2023-03-30 09:02 | 2023-03-30 13:04 | 15 | 4:02 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR 1X25 EN C/L | R23033000010 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 242 | 2023-03-30 | 3630 | keep | 0 | Mar | 2023 | 0.0024724 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-03-30 09:18 | 2023-03-30 11:08 | 1 | 1:50 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA IGUANA | M23033000034 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-03-30 | 110 | keep | 0 | Mar | 2023 | 7.492e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-30 09:26 | 2023-03-30 09:27 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1118-10 SE CERRO POR SCADA 20% DEL 1111-01 POR 1118-10 | S2303300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-30 | 513 | keep | 0 | Mar | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-03-30 09:26 | 2023-03-30 09:27 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA LLEVA 20% DEL 1111-01 | S2303300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-30 | 2782 | keep | 0 | Mar | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2023-03-30 09:26 | 2023-03-30 14:44 | 10 | 5:18 | P | PROBLEMA DEL CLIENTE | 1X100 EN RISER Y 1X65 EN TRANSCLOSURE PRIVADO | B23033000040 | New_Event | Customer-Related Interruption | Include | Include | Public | 318 | 2023-03-30 | 3180 | keep | 0 | Mar | 2023 | 0.0021659 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-03-30 09:34 | 2023-03-30 10:27 | 128 | 0:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPAZARON DOS CAJAS PRIMARIAS Y 2 X100 EN C/L | R23033000016 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2023-03-30 | 6784 | keep | 0 | Mar | 2023 | 0.0046206 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
SAN JUAN | 2023-03-30 09:38 | 2023-03-30 13:24 | 45 | 3:46 | P | DESGANCHE | 2 X 50 EN C/L SE REALIZO DESGANCHE | S23033000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2023-03-30 | 10170 | keep | 0 | Mar | 2023 | 0.0069267 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-03-30 09:54 | 2023-03-30 10:15 | 20 | 0:21 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REPARO SECUNDARIA Y SE REALIZO DESGANCHE SECUNDARIO | B23033000046 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 21 | 2023-03-30 | 420 | keep | 0 | Mar | 2023 | 0.00028606 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-30 09:56 | 2023-03-30 09:59 | 837 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 1401-07 SE CERRO POR SCADA | S23033000051 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-03-30 | 2511 | keep | 0 | Mar | 2023 | 0.0017102 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-03-30 09:56 | 2023-03-30 09:59 | 908 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1401-06 SE CERRO POR SCADA | S23033000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-03-30 | 2724 | keep | 0 | Mar | 2023 | 0.0018553 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2023-03-30 09:59 | 2023-03-30 13:18 | 10 | 3:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA PARTIDA TRASPATIO | B23033000049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 199 | 2023-03-30 | 1990 | keep | 0 | Mar | 2023 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-03-30 10:07 | 2023-03-30 11:30 | 20 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIO | C23033000032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2023-03-30 | 1660 | keep | 0 | Mar | 2023 | 0.0011306 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-03-30 10:22 | 2023-03-30 10:23 | 2708 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23033000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-30 | 2708 | keep | 0 | Mar | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
FAJARDO | 2023-03-30 10:27 | 2023-03-30 10:28 | 956 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R23033000024 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-30 | 956 | keep | 0 | Mar | 2023 | 0.00065113 | 0.00065113 | Momentary | FALSE | FALSE | Not_TMED_Event | 956
FAJARDO | 2023-03-30 10:28 | 2023-03-30 10:33 | 128 | 0:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPAZARON DOS CAJAS PRIMARIAS Y 2 X100 EN C/L | R23033000016 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 5 | 2023-03-30 | 640 | keep | 0 | Mar | 2023 | 0.0004359 | 8.718e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 128
GUAYAMA | 2023-03-30 10:30 | 2023-03-30 15:39 | 12 | 5:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO SECUNDARIA QUEMADA | P23033000031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 309 | 2023-03-30 | 3708 | keep | 0 | Mar | 2023 | 0.0025255 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-03-30 10:31 | 2023-03-30 19:54 | 2 | 9:23 | P | TRANSFORMADOR AVERIADO | 1 X 8 EN XMR SE REMPLAZO XMR 25KVA X 25KVA | B23033000054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 563 | 2023-03-30 | 1126 | keep | 0 | Mar | 2023 | 0.00076691 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-03-30 10:32 | 2023-03-30 10:33 | 4085 | 0:01 | T | DESGANCHE | RECIERRE | R23033000026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-30 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
FAJARDO | 2023-03-30 10:33 | 2023-03-30 10:34 | 956 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R23033000027 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2023-03-30 | 956 | keep | 0 | Mar | 2023 | 0.00065113 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-30 10:33 | 2023-03-30 12:34 | 15 | 2:01 | P | DESGANCHE | 1 X 100 EM C/L Y DESGANCHE | R23033000028 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-03-30 | 1815 | keep | 0 | Mar | 2023 | 0.0012362 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-03-30 10:34 | 2023-03-30 11:53 | 128 | 1:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPAZARON DOS CAJAS PRIMARIAS Y 2 X100 EN C/L | R23033000016 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 79 | 2023-03-30 | 10112 | keep | 0 | Mar | 2023 | 0.0068872 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BAYAMON | 2023-03-30 10:39 | 2023-03-30 23:14 | 4 | 12:35 | P | CAUSAS EXTERNAS | 1 X 20 EN RISER CARRO IMPACTO POSTE | B23033000012 | New_Event | Damage From Public | Include | Include | Public | 755 | 2023-03-30 | 3020 | keep | 0 | Mar | 2023 | 0.0020569 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-30 10:41 | 2023-03-30 11:51 | 1 | 1:10 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R23033000029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2023-03-30 | 70 | keep | 0 | Mar | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-03-30 10:42 | 2023-03-30 12:01 | 8 | 1:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER POR SULFATADO EL FUSIBLE | A23033000030 | New_Event | Cutout Failure | Include | Include | Equipment | 79 | 2023-03-30 | 632 | keep | 0 | Mar | 2023 | 0.00043045 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-03-30 10:45 | 2023-03-30 18:43 | 4 | 7:58 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR POR PROBLEMAS DE VOLTAJE NO PUDIERON REPARAR LA CONDICION SE REFIERE A REMPLAZAR EL TRNSFORMADOR DE 25KVA | S23033000071 | New_Event | Service Transformer Failure | Include | Include | Equipment | 478 | 2023-03-30 | 1912 | keep | 0 | Mar | 2023 | 0.0013023 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-03-30 10:50 | 2023-03-30 13:08 | 1 | 2:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA | R23033000034 | New_Event | Cutout Failure | Include | Include | Equipment | 138 | 2023-03-30 | 138 | keep | 0 | Mar | 2023 | 9.3991e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-30 10:51 | 2023-03-30 15:45 | 38 | 4:54 | P | ANIMAL | 1 X 65 EN AEREO PROVISIONAL CRUCE X AVE | S23033000077 | New_Event | Animals | Include | Include | Wildlife | 294 | 2023-03-30 | 11172 | keep | 0 | Mar | 2023 | 0.0076092 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-03-30 11:04 | 2023-03-30 14:11 | 65 | 3:07 | P | CAUSAS EXTERNAS | 2X65 EN C/L PERSONAL AJENO A LUMA REALIZANDO DESGANCHE | S23033000086 | New_Event | Damage From Public | Include | Include | Public | 187 | 2023-03-30 | 12155 | keep | 0 | Mar | 2023 | 0.0082787 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2023-03-30 11:12 | 2023-03-30 17:58 | 2450 | 6:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 12600 POT HEAD AVERIADO | C23033000046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 406 | 2023-03-30 | 994700 | keep | 0 | Mar | 2023 | 0.67749 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-03-30 11:12 | 2023-03-30 17:58 | 640 | 6:46 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 12600 POTHEAD AVERIADO | C23033000046 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 406 | 2023-03-30 | 259840 | keep | 0 | Mar | 2023 | 0.17698 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
CANOVANAS | 2023-03-30 11:18 | 2023-03-30 15:01 | 13 | 3:43 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | R23033000035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2023-03-30 | 2899 | keep | 0 | Mar | 2023 | 0.0019745 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2023-03-30 11:43 | 2023-03-30 11:47 | 3114 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR NO SE ENCONTRO CAUSA | P23033000048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-03-30 | 12456 | keep | 0 | Mar | 2023 | 0.0084837 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2023-03-30 11:50 | 2023-03-30 12:30 | 10 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES EN LINEA SECUNDARIA | P23033000050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-03-30 | 400 | keep | 0 | Mar | 2023 | 0.00027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-30 11:57 | 2023-03-30 21:56 | 20 | 9:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | A23033000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 599 | 2023-03-30 | 11980 | keep | 0 | Mar | 2023 | 0.0081595 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-30 12:08 | 2023-03-30 15:50 | 20 | 3:42 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S23033000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-03-30 | 4440 | keep | 0 | Mar | 2023 | 0.0030241 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-30 12:26 | 2023-03-30 12:33 | 1784 | 0:07 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CORROBORO PERSONAL FUERA Y SE CERRO POR CONTROL | B2303300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-03-30 | 12488 | keep | 0 | Mar | 2023 | 0.0085055 | 0.0012151 | Sustained | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-03-30 12:26 | 2023-03-30 12:33 | 453 | 0:07 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CORROBORO PERSONAL FUERA Y SE CERRO POR CONTROL | B2303300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-03-30 | 3171 | keep | 0 | Mar | 2023 | 0.0021598 | 0.00030854 | Sustained | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-03-30 12:26 | 2023-03-30 12:33 | 186 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CORROBORO PERSONAL FUERA Y SE CERRO POR CONTROL | B2303300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-03-30 | 1302 | keep | 0 | Mar | 2023 | 0.00088679 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
BARRANQUITAS | 2023-03-30 12:28 | 2023-03-30 14:00 | 60 | 1:32 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | C23033000071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-03-30 | 5520 | keep | 0 | Mar | 2023 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-30 12:30 | 2023-03-30 16:33 | 10 | 4:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA | B23033000080 | New_Event | Secondary Wire Break | Include | Include | Equipment | 243 | 2023-03-30 | 2430 | keep | 0 | Mar | 2023 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-03-30 12:54 | 2023-03-31 14:19 | 4 | 25:25 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL Y SE REPARO LINEA PRIMARIA | M23033000118 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1525 | 2023-03-30 | 6100 | keep | 0 | Mar | 2023 | 0.0041547 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-03-30 13:09 | 2023-03-30 15:15 | 30 | 2:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23033000057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-03-30 | 3780 | keep | 0 | Mar | 2023 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-30 13:12 | 2023-03-30 21:08 | 40 | 7:56 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B23033000089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 476 | 2023-03-30 | 19040 | keep | 0 | Mar | 2023 | 0.012968 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-03-30 13:17 | 2023-03-30 17:04 | 12 | 3:47 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZAR POSTE SECUNDARIO PARTIDO | S23033000133 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 227 | 2023-03-30 | 2724 | keep | 0 | Mar | 2023 | 0.0018553 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-03-30 13:33 | 2023-03-30 15:00 | 25 | 1:27 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA CAMION CRUZO LINEAS | M23033000096 | New_Event | Damage From Public | Include | Include | Public | 87 | 2023-03-30 | 2175 | keep | 0 | Mar | 2023 | 0.0014814 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-03-30 13:45 | 2023-03-30 19:37 | 250 | 5:52 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 Y 1 X 80 EN CORTE DE LINEA POR LINEA CRUZADA | A23033000067 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 352 | 2023-03-30 | 88000 | keep | 0 | Mar | 2023 | 0.059936 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-03-30 13:51 | 2023-03-30 15:45 | 1 | 1:54 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | S23033000143 | New_Event | Animals | Include | Include | Wildlife | 114 | 2023-03-30 | 114 | keep | 0 | Mar | 2023 | 7.7645e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-03-30 13:52 | 2023-03-30 17:56 | 5 | 4:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | R23033000052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 244 | 2023-03-30 | 1220 | keep | 0 | Mar | 2023 | 0.00083094 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-30 14:04 | 2023-03-30 14:45 | 1 | 0:41 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 80 EN RISER CONTAMINACION EN TRANSCLOSURE | R23033000053 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 41 | 2023-03-30 | 41 | keep | 0 | Mar | 2023 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-30 14:09 | 2023-03-30 14:10 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23033000098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-30 | 27 | keep | 0 | Mar | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-03-30 14:17 | 2023-03-30 15:47 | 8 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL ABIERTO EN SECUNDARIA NO FUNDIO | B23033000100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-03-30 | 720 | keep | 0 | Mar | 2023 | 0.00049039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-03-30 14:30 | 2023-03-30 18:00 | 12 | 3:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXIONES Y SE REEMPLAZO VARIOS TRAMOS DE SECUNDARIAS | A23033000082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 210 | 2023-03-30 | 2520 | keep | 0 | Mar | 2023 | 0.0017164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-03-30 14:42 | 2023-03-30 18:06 | 20 | 3:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA NO FUNDIO | C23033000105 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2023-03-30 | 4080 | keep | 0 | Mar | 2023 | 0.0027789 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-03-30 14:51 | 2023-03-30 17:24 | 30 | 2:33 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | S23033000154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-03-30 | 4590 | keep | 0 | Mar | 2023 | 0.0031262 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-03-30 15:15 | 2023-03-30 16:15 | 38 | 1:00 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA (NO SE QUEDARON CLIENTES SIN SERVICIO CON LA LINEA SECCIONALIZADA) | M23033000111 | New_Event | Primary Wire Break | Include | Include | Equipment | 60 | 2023-03-30 | 2280 | keep | 0 | Mar | 2023 | 0.0015529 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-03-30 15:20 | 2023-03-30 19:50 | 11 | 4:30 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | S23033000159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-03-30 | 2970 | keep | 0 | Mar | 2023 | 0.0020229 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-03-30 15:29 | 2023-03-30 21:27 | 16 | 5:58 | P | ANIMAL | 1X40 EN C/L CRUCE POR IGUANA | B23033000113 | New_Event | Animals | Include | Include | Wildlife | 358 | 2023-03-30 | 5728 | keep | 0 | Mar | 2023 | 0.0039013 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2023-03-30 15:29 | 2023-03-30 17:22 | 166 | 1:53 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA SE ABRIO PUENTE PARA REEMPLAZO DE POSTE IMPACTADO POR CAMION SOLO QUEDAN 15 CLIENTES | R23033000072 | New_Event | Damage From Public | Include | Include | Public | 113 | 2023-03-30 | 18758 | keep | 0 | Mar | 2023 | 0.012776 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
VEGA BAJA | 2023-03-30 15:33 | 2023-03-30 18:23 | 100 | 2:50 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B23033000114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2023-03-30 | 17000 | keep | 0 | Mar | 2023 | 0.011579 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-30 15:37 | 2023-03-30 16:04 | 10 | 0:27 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR Y SE REMPLAZO PUENTE DE LINEA A CAJA | S23033000168 | New_Event | Primary Wire Break | Include | Include | Equipment | 27 | 2023-03-30 | 270 | keep | 0 | Mar | 2023 | 0.0001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-30 15:37 | 2023-03-30 17:43 | 2 | 2:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23033000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-03-30 | 252 | keep | 0 | Mar | 2023 | 0.00017164 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-03-30 15:44 | 2023-03-30 18:23 | 5 | 2:39 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23033000118 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-03-30 | 795 | keep | 0 | Mar | 2023 | 0.00054147 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-03-30 16:02 | 2023-03-30 21:49 | 85 | 5:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO PORTAFUSIBLE Y 1 X 30 EN RISER | S23033000175 | New_Event | Cutout Failure | Include | Include | Equipment | 347 | 2023-03-30 | 29495 | keep | 0 | Mar | 2023 | 0.020089 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-03-30 16:05 | 2023-03-30 17:17 | 6 | 1:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X30 EN C/L SE REMPLAZO CAJA PRIMARIA | B23033000123 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2023-03-30 | 432 | keep | 0 | Mar | 2023 | 0.00029423 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-03-30 16:17 | 2023-03-30 18:11 | 22 | 1:54 | P | DESGANCHE | 1 X 40 EN C/L | C23033000130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-03-30 | 2508 | keep | 0 | Mar | 2023 | 0.0017082 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
PONCE | 2023-03-30 16:17 | 2023-03-30 18:11 | 17 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTE SECUNDARIO Y SE REPARO SECUNDARIA EN VARIOS PUNTOS | P23033000098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2023-03-30 | 1938 | keep | 0 | Mar | 2023 | 0.00132 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
PONCE | 2023-03-30 16:41 | 2023-03-30 16:42 | 2446 | 0:01 | T | ANIMAL | EXPLOSION FUE EN PATIO DE LA TECNICA Y PERSONAL VIERON EL CRUCE DE LA IGUANA EN LAS FASES | P23033000103 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-03-30 | 2446 | keep | 0 | Mar | 2023 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
FAJARDO | 2023-03-30 17:22 | 2023-03-30 21:29 | 15 | 4:07 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PRIMARIO PARTIDO POR IMPACTO DE CAMION , SE CERRO PUENTE EN LINEA MONOFASICA SIN CARGA | R23033000072 | Partial_restoration | Damage From Public | Include | Include | Public | 247 | 2023-03-30 | 3705 | keep | 0 | Mar | 2023 | 0.0025235 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-03-30 17:28 | 2023-03-31 13:18 | 17 | 19:50 | P | TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO TERMINACION SE REEMPLAZO TRANSFORMADOR 100 KVA A 2.4KV 1 X 80 EN RISER | P23033000105 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1190 | 2023-03-30 | 20230 | keep | 0 | Mar | 2023 | 0.013779 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
AGUADILLA | 2023-03-30 17:31 | 2023-03-30 20:10 | 400 | 2:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23033000140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2023-03-30 | 63600 | keep | 0 | Mar | 2023 | 0.043318 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2023-03-30 17:33 | 2023-03-30 19:25 | 17 | 1:52 | P | CONDUCTOR ARRIADO O CRUZADO | ABRIO C/L PARA RETEZAR LINEAS | C23033000139 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 112 | 2023-03-30 | 1904 | keep | 0 | Mar | 2023 | 0.0012968 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-03-30 17:40 | 2023-03-30 21:20 | 100 | 3:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23033000141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-03-30 | 22000 | keep | 0 | Mar | 2023 | 0.014984 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-03-30 18:00 | 2023-03-30 18:34 | 1 | 0:34 | P | PROBLEMA DEL CLIENTE | 1X25 DE RISER @ BANCO DE XMRS REQUIERE MANTENIMIENTO | S23033000192 | New_Event | Customer-Related Interruption | Include | Include | Public | 34 | 2023-03-30 | 34 | keep | 0 | Mar | 2023 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-30 18:05 | 2023-03-30 18:55 | 30 | 0:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R23033000078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2023-03-30 | 1500 | keep | 0 | Mar | 2023 | 0.0010216 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-30 18:10 | 2023-03-30 19:31 | 100 | 1:21 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR RAMA | A23033000131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-03-30 | 8100 | keep | 0 | Mar | 2023 | 0.0055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-03-30 18:52 | 2023-03-30 19:57 | 25 | 1:05 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | R23033000082 | New_Event | Animals | Include | Include | Wildlife | 65 | 2023-03-30 | 1625 | keep | 0 | Mar | 2023 | 0.0011068 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-03-30 18:55 | 2023-03-30 20:42 | 132 | 1:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | R23033000078 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 107 | 2023-03-30 | 14124 | keep | 0 | Mar | 2023 | 0.0096198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-03-30 19:04 | 2023-03-30 19:05 | 4085 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R23033000083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-30 | 4085 | keep | 0 | Mar | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-03-30 19:05 | 2023-03-30 20:37 | 117 | 1:32 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R23033000084 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-03-30 | 10764 | keep | 0 | Mar | 2023 | 0.0073313 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
AGUADILLA | 2023-03-30 19:06 | 2023-03-30 22:09 | 100 | 3:03 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA Y 2 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23033000148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-03-30 | 18300 | keep | 0 | Mar | 2023 | 0.012464 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-03-30 19:16 | 2023-03-30 20:58 | 3 | 1:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA | R23033000092 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2023-03-30 | 306 | keep | 0 | Mar | 2023 | 0.00020842 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-03-30 19:30 | 2023-03-31 07:29 | 78 | 11:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23033000156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 719 | 2023-03-30 | 56082 | keep | 0 | Mar | 2023 | 0.038197 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 293 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000221 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 1172 | keep | 0 | Mar | 2023 | 0.00079824 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 761 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000221 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 3044 | keep | 0 | Mar | 2023 | 0.0020733 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 451 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000221 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 1804 | keep | 0 | Mar | 2023 | 0.0012287 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 922 | 0:04 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 INTERRUPTOR 1401-08 LLEVA LA CARGA DEL 1346-05 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 3688 | keep | 0 | Mar | 2023 | 0.0025119 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 837 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 3348 | keep | 0 | Mar | 2023 | 0.0022803 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 908 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 3632 | keep | 0 | Mar | 2023 | 0.0024737 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 135 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 LLEVA LA CARGA DEL 1346-05 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 540 | keep | 0 | Mar | 2023 | 0.00036779 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 1 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 4 | keep | 0 | Mar | 2023 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 1498 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 5992 | keep | 0 | Mar | 2023 | 0.0040811 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 164 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 656 | keep | 0 | Mar | 2023 | 0.0004468 | 0.0001117 | Momentary | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 533 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 2132 | keep | 0 | Mar | 2023 | 0.0014521 | 0.00036302 | Momentary | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 451 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 1804 | keep | 0 | Mar | 2023 | 0.0012287 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 766 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 3064 | keep | 0 | Mar | 2023 | 0.0020869 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 427 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000228 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 1708 | keep | 0 | Mar | 2023 | 0.0011633 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 716 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000228 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 2864 | keep | 0 | Mar | 2023 | 0.0019507 | 0.00048766 | Momentary | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 867 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000228 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 3468 | keep | 0 | Mar | 2023 | 0.002362 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2023-03-30 19:57 | 2023-03-30 20:01 | 353 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8900 AL CERRAR EL MOD 10125 REPARTO METRO PARA PROBAR TRAMO LINEA 10100 DISPARA LINEA 8900 DEBIDO A PARARRAYO AVERIADO EN LINEA 10100 | S23033000228 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-03-30 | 1412 | keep | 0 | Mar | 2023 | 0.00096171 | 0.00024043 | Momentary | FALSE | FALSE | Not_TMED_Event | 353
YAUCO | 2023-03-30 20:03 | 2023-03-30 20:39 | 100 | 0:36 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LINEAS | M23033000172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-03-30 | 3600 | keep | 0 | Mar | 2023 | 0.0024519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-03-30 21:10 | 2023-03-31 08:55 | 7 | 11:45 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE | M23033000180 | New_Event | Animals | Include | Include | Wildlife | 705 | 2023-03-30 | 4935 | keep | 0 | Mar | 2023 | 0.0033612 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-03-30 22:01 | 2023-03-31 17:34 | 7 | 19:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR/LEVANTAR CONDUCTOR SECUNDARIO DEL SUELO NO FUNDIO | S23033000242 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1173 | 2023-03-30 | 8211 | keep | 0 | Mar | 2023 | 0.0055925 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-03-30 22:09 | 2023-03-31 08:32 | 13 | 10:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR PORTAFUSIBLE CON CONTAMINACION | C23033000164 | New_Event | Cutout Failure | Include | Include | Equipment | 623 | 2023-03-30 | 8099 | keep | 0 | Mar | 2023 | 0.0055162 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-03-30 22:20 | 2023-03-31 14:34 | 2 | 16:14 | P | ANIMAL | 1X100 EN C/L CRUCE POR AVE | S23033000229 | New_Event | Animals | Include | Include | Wildlife | 974 | 2023-03-30 | 1948 | keep | 0 | Mar | 2023 | 0.0013268 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-03-30 22:56 | 2023-03-31 18:58 | 186 | 20:02 | P | LINEA DE TRANSMISION 38KV | 2 X 100 EN C/ L SE RETIRO CONDUCTOR DE 38KV SOBRE ALIMENTADOR | S23033000243 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1202 | 2023-03-30 | 223572 | keep | 0 | Mar | 2023 | 0.15227 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
CANOVANAS | 2023-03-30 22:58 | 2023-03-30 22:59 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2303300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-30 | 7621 | keep | 0 | Mar | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-03-30 23:11 | 2023-03-31 10:30 | 100 | 11:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO CAJA QUEMADA | R23033000098 | New_Event | Cutout Failure | Include | Include | Equipment | 679 | 2023-03-30 | 67900 | keep | 0 | Mar | 2023 | 0.046246 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-31 00:35 | 2023-03-31 00:37 | 119 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL 75% POR 1011-05 | S2303310000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-03-31 | 238 | keep | 0 | Mar | 2023 | 0.0001621 | 8.105e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 119
SAN JUAN | 2023-03-31 00:35 | 2023-03-31 00:37 | 719 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 75% DEL 1011-02 | S2303310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-31 | 1438 | keep | 0 | Mar | 2023 | 0.00097942 | 0.00048971 | Momentary | FALSE | FALSE | Not_TMED_Event | 719
BAYAMON | 2023-03-31 01:21 | 2023-03-31 01:22 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2303310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 2402 | keep | 0 | Mar | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-03-31 01:22 | 2023-03-31 03:02 | 10 | 1:40 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23033100002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 100 | 2023-03-31 | 1000 | keep | 0 | Mar | 2023 | 0.0006811 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-03-31 02:46 | 2023-03-31 12:50 | 200 | 10:04 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR AVERIADO | A23033100002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 604 | 2023-03-31 | 120800 | keep | 0 | Mar | 2023 | 0.082276 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-03-31 04:57 | 2023-03-31 07:31 | 11 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23033100002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2023-03-31 | 1694 | keep | 0 | Mar | 2023 | 0.0011538 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-03-31 05:18 | 2023-03-31 05:19 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23033100011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 308 | keep | 0 | Mar | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
UTUADO | 2023-03-31 06:53 | 2023-03-31 12:44 | 3 | 5:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE CAJAS EN TRANSFORMADOR PARA CERRAR PUENTE SECUNDARIO | A23033100014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 351 | 2023-03-31 | 1053 | keep | 0 | Mar | 2023 | 0.00071719 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-03-31 07:19 | 2023-03-31 07:20 | 1702 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECERRO INTERRUPTOR EN SERVICIO | C23033100004 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-03-31 | 1702 | keep | 0 | Mar | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-03-31 07:20 | 2023-03-31 13:12 | 70 | 5:52 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO EN TRONCAL | C23033100016 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 352 | 2023-03-31 | 24640 | keep | 0 | Mar | 2023 | 0.016782 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-03-31 08:00 | 2023-03-31 08:50 | 10 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23033100011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-03-31 | 500 | keep | 0 | Mar | 2023 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-03-31 08:01 | 2023-03-31 12:39 | 30 | 4:38 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA POR MAQUINARIA | A23033100018 | New_Event | Damage From Public | Include | Include | Public | 278 | 2023-03-31 | 8340 | keep | 0 | Mar | 2023 | 0.0056803 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-03-31 08:27 | 2023-03-31 12:20 | 15 | 3:53 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE PRIMARIO | B23033100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-03-31 | 3495 | keep | 0 | Mar | 2023 | 0.0023804 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-03-31 08:27 | 2023-03-31 08:28 | 1397 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23033100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 1397 | keep | 0 | Mar | 2023 | 0.00095149 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
FAJARDO | 2023-03-31 08:38 | 2023-03-31 11:00 | 20 | 2:22 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23033100015 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-03-31 | 2840 | keep | 0 | Mar | 2023 | 0.0019343 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-03-31 08:48 | 2023-03-31 13:00 | 60 | 4:12 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23033100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-03-31 | 15120 | keep | 0 | Mar | 2023 | 0.010298 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-03-31 08:55 | 2023-03-31 10:00 | 7 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR REP SECUNDARIA | B23033100019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-03-31 | 455 | keep | 0 | Mar | 2023 | 0.0003099 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-03-31 08:58 | 2023-03-31 12:47 | 18 | 3:49 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23033100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-03-31 | 4122 | keep | 0 | Mar | 2023 | 0.0028075 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-03-31 09:12 | 2023-03-31 17:08 | 1 | 7:56 | P | NO SE REPORTO CAUSA | 2X40 EN C/L 2X25 EN MONTURA DE XMRS | S23033100015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 476 | 2023-03-31 | 476 | keep | 0 | Mar | 2023 | 0.0003242 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-31 09:14 | 2023-03-31 13:30 | 693 | 4:16 | T | MAL TIEMPO/LLUVIA O VIENTO | SE REEMPLAZO AISLADORES PARTIDOS DEBIDO A VIENTO FUERTE | M23033100012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 256 | 2023-03-31 | 177408 | keep | 0 | Mar | 2023 | 0.12083 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
CAGUAS | 2023-03-31 09:35 | 2023-03-31 10:06 | 20 | 0:31 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | C23033100006 | New_Event | Animals | Include | Include | Wildlife | 31 | 2023-03-31 | 620 | keep | 0 | Mar | 2023 | 0.00042228 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-03-31 09:38 | 2023-03-31 09:39 | 2096 | 0:01 | T | DESGANCHE | RECIERRE | B2303310000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-03-31 | 2096 | keep | 0 | Mar | 2023 | 0.0014276 | 0.0014276 | Momentary | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2023-03-31 09:39 | 2023-03-31 11:44 | 50 | 2:05 | P | DESGANCHE | 2 X 65 EN C/L SE DESGANCHO | B23033100030 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-03-31 | 6250 | keep | 0 | Mar | 2023 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-03-31 10:26 | 2023-03-31 10:38 | 7 | 0:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR SECUNDARIA | C23033100036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 12 | 2023-03-31 | 84 | keep | 0 | Mar | 2023 | 5.7212e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-03-31 10:32 | 2023-03-31 15:02 | 5 | 4:30 | P | DESGANCHE | 1 X 25 EN CONVERTIDOR DESGANCHE | A23033100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-03-31 | 1350 | keep | 0 | Mar | 2023 | 0.00091948 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-03-31 10:35 | 2023-03-31 14:50 | 22 | 4:15 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR 50 KVA X 50 KVA AVERIADO Y CAJA | R23033100027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 255 | 2023-03-31 | 5610 | keep | 0 | Mar | 2023 | 0.0038209 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2023-03-31 10:47 | 2023-03-31 12:31 | 29 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | R23033100029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-03-31 | 3016 | keep | 0 | Mar | 2023 | 0.0020542 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2023-03-31 11:04 | 2023-03-31 11:05 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23033100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 2039 | keep | 0 | Mar | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
FAJARDO | 2023-03-31 11:11 | 2023-03-31 11:59 | 50 | 0:48 | P | ANIMAL | 1 X 50 EN RISER CRUCE X AVE | R23033100034 | New_Event | Animals | Include | Include | Wildlife | 48 | 2023-03-31 | 2400 | keep | 0 | Mar | 2023 | 0.0016346 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-03-31 11:14 | 2023-03-31 11:16 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23033100051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-03-31 | 4252 | keep | 0 | Mar | 2023 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BARRANQUITAS | 2023-03-31 11:18 | 2023-03-31 12:34 | 9 | 1:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR XMR PARA REPARAR Y RELOCALIZAR SECUNDARIAS PARA EVITAR DESGANCHE DE BAMBUAS | C23033100029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 76 | 2023-03-31 | 684 | keep | 0 | Mar | 2023 | 0.00046587 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-03-31 11:25 | 2023-03-31 15:00 | 60 | 3:35 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M23033100035 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 215 | 2023-03-31 | 12900 | keep | 0 | Mar | 2023 | 0.0087861 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-31 11:41 | 2023-03-31 16:16 | 12 | 4:35 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23033100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-03-31 | 3300 | keep | 0 | Mar | 2023 | 0.0022476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-03-31 11:41 | 2023-03-31 13:58 | 145 | 2:17 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23033100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-03-31 | 19865 | keep | 0 | Mar | 2023 | 0.01353 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
BARRANQUITAS | 2023-03-31 11:43 | 2023-03-31 14:40 | 71 | 2:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C23033100058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2023-03-31 | 12567 | keep | 0 | Mar | 2023 | 0.0085593 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
CANOVANAS | 2023-03-31 11:48 | 2023-03-31 14:19 | 1 | 2:31 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R23033100039 | New_Event | Animals | Include | Include | Wildlife | 151 | 2023-03-31 | 151 | keep | 0 | Mar | 2023 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-03-31 12:03 | 2023-03-31 17:43 | 39 | 5:40 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AERIO HACIA T-41 Y SE REPARO CABLE SOTERADO DEL T-41 AL T-42 | B23033000007 | New_Event | UG Cable Fault | Include | Include | Equipment | 340 | 2023-03-31 | 13260 | keep | 0 | Mar | 2023 | 0.0090313 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
YAUCO | 2023-03-31 12:05 | 2023-03-31 17:21 | 20 | 5:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR Y SE FIJO BAJANTE DE BUSHING PRIMARIO | P23033100041 | New_Event | Primary Wire Break | Include | Include | Equipment | 316 | 2023-03-31 | 6320 | keep | 0 | Mar | 2023 | 0.0043045 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-03-31 12:05 | 2023-03-31 12:06 | 2697 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR REALIZA TRES OPERACIONES Y QUEDA EN SERVICIO | A23033100058 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-31 | 2697 | keep | 0 | Mar | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-03-31 12:09 | 2023-03-31 13:17 | 2697 | 1:08 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE ABREN MACHETES Y REALIZA PRUEBA A INTERRUPTOR QUEDANDO EN SERVICIO | A23033100059 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 68 | 2023-03-31 | 183396 | keep | 0 | Mar | 2023 | 0.12491 | 0.0018369 | Sustained | FALSE | FALSE | Not_TMED_Event | 2697
FAJARDO | 2023-03-31 12:10 | 2023-03-31 14:17 | 6 | 2:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO Y NEUTRAL PRIMARIO | R23033100041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 127 | 2023-03-31 | 762 | keep | 0 | Mar | 2023 | 0.00051899 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-03-31 12:36 | 2023-03-31 12:37 | 1730 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23033100049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 1730 | keep | 0 | Mar | 2023 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
BAYAMON | 2023-03-31 12:38 | 2023-03-31 13:42 | 138 | 1:04 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B23033100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-03-31 | 8832 | keep | 0 | Mar | 2023 | 0.0060154 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
ARECIBO | 2023-03-31 12:40 | 2023-03-31 15:26 | 100 | 2:46 | P | DESGANCHE | 1 X 140 EN CL DESGANCHE | A23033100069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-03-31 | 16600 | keep | 0 | Mar | 2023 | 0.011306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-03-31 13:10 | 2023-03-31 23:54 | 400 | 10:44 | P | DESGANCHE | SJ-230331-01 SE SECCIONALIZO TRAMO PARA REALIZAR DESGANCHE PRIMARIO | S23033100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2023-03-31 | 257600 | keep | 0 | Mar | 2023 | 0.17545 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-03-31 13:17 | 2023-03-31 14:50 | 1 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23033100053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-03-31 | 93 | keep | 0 | Mar | 2023 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-03-31 13:17 | 2023-03-31 14:24 | 1348 | 1:07 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR Y SE CIERRAN MACHETES | A23033100079 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 67 | 2023-03-31 | 90316 | keep | 0 | Mar | 2023 | 0.061514 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-03-31 13:28 | 2023-03-31 13:29 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23033100056 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 2039 | keep | 0 | Mar | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2023-03-31 13:29 | 2023-03-31 14:13 | 39 | 0:44 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA POR IMPACTO DE CAMION A POSTE | P23033100034 | New_Event | Damage From Public | Include | Include | Public | 44 | 2023-03-31 | 1716 | keep | 0 | Mar | 2023 | 0.0011688 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2023-03-31 13:33 | 2023-03-31 21:49 | 60 | 8:16 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE CAJA @ LINEA NO FUNDIO | S23033100042 | New_Event | Primary Wire Break | Include | Include | Equipment | 496 | 2023-03-31 | 29760 | keep | 0 | Mar | 2023 | 0.020269 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-03-31 13:37 | 2023-03-31 15:15 | 10 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN CL NO SE REPORTA CAUSA | A23033100083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2023-03-31 | 980 | keep | 0 | Mar | 2023 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-03-31 14:18 | 2023-03-31 17:23 | 100 | 3:05 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | B23033100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-03-31 | 18500 | keep | 0 | Mar | 2023 | 0.0126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-03-31 14:20 | 2023-03-31 16:46 | 50 | 2:26 | P | DESGANCHE | 1 X 40 EN C/L Y DSGANCHE | B23033100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-03-31 | 7300 | keep | 0 | Mar | 2023 | 0.004972 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-03-31 14:34 | 2023-03-31 14:35 | 386 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23033100053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 386 | keep | 0 | Mar | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
SAN JUAN | 2023-03-31 14:35 | 2023-03-31 18:30 | 2 | 3:55 | P | ANIMAL | 1X100 EN C/L CRUCE POR AVE | S23033000229 | Partial_restoration | Animals | Include | Include | Wildlife | 235 | 2023-03-31 | 470 | keep | 0 | Mar | 2023 | 0.00032011 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-03-31 14:44 | 2023-03-31 15:11 | 7 | 0:27 | P | DESGANCHE | 1 X 40 EN C/L | B23033100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2023-03-31 | 189 | keep | 0 | Mar | 2023 | 0.00012873 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-03-31 14:46 | 2023-03-31 18:16 | 15 | 3:30 | P | DESGANCHE | 2 X 20 EN CONVERTIDOR DESGANCHE | A23033100095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-03-31 | 3150 | keep | 0 | Mar | 2023 | 0.0021455 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-03-31 14:49 | 2023-03-31 15:39 | 7 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BAJANTES SECUNDARIOS QUEMADOS Y SE CERRO MONTURA | P23033100068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-03-31 | 350 | keep | 0 | Mar | 2023 | 0.00023838 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-03-31 15:00 | 2023-03-31 17:23 | 12 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR PORTA FUSIBLE AVERIADO | A23033100100 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2023-03-31 | 1716 | keep | 0 | Mar | 2023 | 0.0011688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-03-31 15:03 | 2023-03-31 15:04 | 234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA LA CARGA DEL 2 | P23033100073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 234 | keep | 0 | Mar | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-03-31 15:03 | 2023-03-31 15:04 | 2468 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23033100073 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-03-31 | 2468 | keep | 0 | Mar | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
AGUADILLA | 2023-03-31 15:07 | 2023-03-31 15:08 | 693 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA PUENTE ABIERTO A LA SALIDA DEL ALIMENTADOR | M23033100074 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-31 | 693 | keep | 0 | Mar | 2023 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2023-03-31 15:08 | 2023-03-31 15:24 | 231 | 0:16 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO A LA SALIDA DEL ALIMENTADOR | M23033100085 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 16 | 2023-03-31 | 3696 | keep | 0 | Mar | 2023 | 0.0025173 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
CANOVANAS | 2023-03-31 15:11 | 2023-03-31 18:26 | 2 | 3:15 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE | R23033100054 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 195 | 2023-03-31 | 390 | keep | 0 | Mar | 2023 | 0.00026563 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-03-31 15:21 | 2023-03-31 16:19 | 1 | 0:58 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE X AVE | S23033100060 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-03-31 | 58 | keep | 0 | Mar | 2023 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-03-31 15:24 | 2023-03-31 15:25 | 693 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR PUENTE ABIERTO A LA SALIDA DEL ALIMENTADOR | M23033100077 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-31 | 693 | keep | 0 | Mar | 2023 | 0.000472 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-03-31 15:25 | 2023-03-31 15:28 | 231 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO A LA SALIDA DEL ALIMENTADOR | M23033100085 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 3 | 2023-03-31 | 693 | keep | 0 | Mar | 2023 | 0.000472 | 0.00015733 | Momentary | FALSE | FALSE | Not_TMED_Event | 231
AGUADILLA | 2023-03-31 15:28 | 2023-03-31 15:29 | 693 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR PUENTE ABIERTO A LA SALIDA DEL ALIMENTADOR | M23033100078 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-03-31 | 693 | keep | 0 | Mar | 2023 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2023-03-31 15:29 | 2023-03-31 15:42 | 231 | 0:13 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO A LA SALIDA DEL ALIMENTADOR | M23033100085 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 13 | 2023-03-31 | 3003 | keep | 0 | Mar | 2023 | 0.0020453 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
MAYAGÃœEZ | 2023-03-31 15:34 | 2023-04-01 08:55 | 50 | 17:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTES VIENTOS | M23033100079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1041 | 2023-03-31 | 52050 | keep | 0 | Mar | 2023 | 0.035451 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-03-31 15:42 | 2023-03-31 17:45 | 693 | 2:03 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO SE CERRO INTERRUPTOR | M23033100085 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 123 | 2023-03-31 | 85239 | keep | 0 | Mar | 2023 | 0.058056 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-03-31 15:43 | 2023-03-31 17:25 | 40 | 1:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL VIENTOS | A23033100114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 102 | 2023-03-31 | 4080 | keep | 0 | Mar | 2023 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-03-31 15:45 | 2023-03-31 15:47 | 1494 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE REALIZA PRUEBA A INTERRUPTOR Y QUEDO EN SERVICIO | A23033100113 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2023-03-31 | 2988 | keep | 0 | Mar | 2023 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-03-31 15:47 | 2023-03-31 19:00 | 200 | 3:13 | P | DESCONECTIVO DEFECTUOSO | 3 X 100 EN CL SE REMPLAZO UNA CAJA Y UN MACHETE | A23033100120 | New_Event | Switch Failure | Include | Include | Equipment | 193 | 2023-03-31 | 38600 | keep | 0 | Mar | 2023 | 0.02629 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-03-31 15:48 | 2023-03-31 16:51 | 2 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR BAJANTE SECUNDARIO | C23033100094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2023-03-31 | 126 | keep | 0 | Mar | 2023 | 8.5818e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-03-31 15:52 | 2023-03-31 19:15 | 11 | 3:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A23033100124 | New_Event | Cutout Failure | Include | Include | Equipment | 203 | 2023-03-31 | 2233 | keep | 0 | Mar | 2023 | 0.0015209 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-03-31 15:54 | 2023-03-31 17:30 | 4 | 1:36 | P | TRANSFORMADOR AVERIADO | SE ABRIO EN XMR PARA REMPLAZO DE XMR 25KVA X 25KVA | S23033100063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 96 | 2023-03-31 | 384 | keep | 0 | Mar | 2023 | 0.00026154 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-03-31 15:54 | 2023-03-31 15:55 | 1952 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23033100081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 1952 | keep | 0 | Mar | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
CAGUAS | 2023-03-31 15:56 | 2023-03-31 18:30 | 51 | 2:34 | P | CABLE SOTERRADO AVERIADO | 1 SMU 20 DE 40 AMP. EN SU-1 A AVERIA NUEVA DEL T-3 AL T-18, AVERIA VIEJA DEL T-18 AL SU-2A | C23033100095 | New_Event | UG Cable Fault | Include | Include | Equipment | 154 | 2023-03-31 | 7854 | keep | 0 | Mar | 2023 | 0.0053493 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
YAUCO | 2023-03-31 16:46 | 2023-03-31 19:25 | 90 | 2:39 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS EVENTO CON MAYAGÃœEZ | M23303100094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2023-03-31 | 14310 | keep | 0 | Mar | 2023 | 0.0097465 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2023-03-31 17:14 | 2023-03-31 19:57 | 10 | 2:43 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO A CAJA DE TRANSFORMADOR | A23033100155 | New_Event | Primary Wire Break | Include | Include | Equipment | 163 | 2023-03-31 | 1630 | keep | 0 | Mar | 2023 | 0.0011102 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-03-31 17:23 | 2023-03-31 19:32 | 8 | 2:09 | P | ANIMAL | 1 X 10 EN XMRCRUCE X AVE | B23033100116 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-03-31 | 1032 | keep | 0 | Mar | 2023 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-03-31 17:33 | 2023-03-31 18:51 | 11 | 1:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRA DE NEUTRAL EN PEDESTAL | R23033100063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 78 | 2023-03-31 | 858 | keep | 0 | Mar | 2023 | 0.00058438 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-03-31 17:45 | 2023-03-31 19:10 | 3 | 1:25 | P | CABLE SOTERRADO AVERIADO | INDICA FOREMAN WILFREDO HERNANDEZ POSIBLE AVERIA SOTERRADA SE PASO LA CARGA AL 7002-02 | M23033100115 | New_Event | UG Cable Fault | Include | Include | Equipment | 85 | 2023-03-31 | 255 | keep | 0 | Mar | 2023 | 0.00017368 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-03-31 17:51 | 2023-03-31 20:47 | 6 | 2:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO XMR Y SE REMPLAZO CAJA PRIMARIA | B23033100118 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2023-03-31 | 1056 | keep | 0 | Mar | 2023 | 0.00071924 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-03-31 17:55 | 2023-03-31 18:18 | 8 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23033100012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-03-31 | 184 | keep | 0 | Mar | 2023 | 0.00012532 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-03-31 18:15 | 2023-04-01 08:15 | 24 | 14:00 | P | NO SE REPORTO CAUSA | CERRAR CORTE DE LINEA | P23033100111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 840 | 2023-03-31 | 20160 | keep | 0 | Mar | 2023 | 0.013731 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2023-03-31 18:30 | 2023-04-01 20:13 | 40 | 25:43 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL DEL SU-1A HACIA T-4 - CG-230401-01B | C23033100120 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1543 | 2023-03-31 | 61720 | keep | 0 | Mar | 2023 | 0.042037 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-03-31 18:51 | 2023-03-31 20:00 | 1 | 1:09 | P | PROBLEMA DEL CLIENTE | DEFECTO INTERIOR SE DEJO RISER ABIERTO Y TAG | P23033100099 | New_Event | Customer-Related Interruption | Include | Include | Public | 69 | 2023-03-31 | 69 | keep | 0 | Mar | 2023 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-03-31 18:58 | 2023-03-31 19:19 | 1106 | 0:21 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CORROBORO PERSONAL FUERA DE LAS LINEAS Y SE CERRO POR CONTROL | S23033100107 | New_Event | Feeder Load Transferred | Include | Include | Other | 21 | 2023-03-31 | 23226 | keep | 0 | Mar | 2023 | 0.015819 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-03-31 18:58 | 2023-03-31 19:19 | 1802 | 0:21 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CORROBORO PERSONAL FUERA DE LAS LINEAS Y SE CERRO POR CONTROL | S23033100107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 21 | 2023-03-31 | 37842 | keep | 0 | Mar | 2023 | 0.025774 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
HUMACAO | 2023-03-31 19:11 | 2023-03-31 19:12 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23033100119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-03-31 | 2126 | keep | 0 | Mar | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
VEGA BAJA | 2023-03-31 19:14 | 2023-03-31 20:04 | 10 | 0:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REMPLAZO PORTAFUSIBLE | B23033100123 | New_Event | Cutout Failure | Include | Include | Equipment | 50 | 2023-03-31 | 500 | keep | 0 | Mar | 2023 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-03-31 19:15 | 2023-04-01 08:35 | 18 | 13:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | P23033100103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 800 | 2023-03-31 | 14400 | keep | 0 | Mar | 2023 | 0.0098078 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-03-31 19:15 | 2023-03-31 19:45 | 10 | 0:30 | P | FUEGO | ABRIR CAJAS TRANSFORMADOR PARA REPARAR SECUNDARIAS QUEMADAS POR FUEGO FORESTAL | M23033100129 | New_Event | Fire | Include | Include | Public | 30 | 2023-03-31 | 300 | keep | 0 | Mar | 2023 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-03-31 19:18 | 2023-04-01 10:43 | 60 | 15:25 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23033100132 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 925 | 2023-03-31 | 55500 | keep | 0 | Mar | 2023 | 0.037801 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-03-31 19:19 | 2023-03-31 22:58 | 186 | 3:39 | P | LINEA DE TRANSMISION 38KV | 2 X 100 EN C/ L SE RETIRO CONDUCTOR DE 38KV SOBRE ALIMENTADOR | S23033000243 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 219 | 2023-03-31 | 40734 | keep | 0 | Mar | 2023 | 0.027744 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-03-31 19:22 | 2023-03-31 21:37 | 321 | 2:15 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | C23033100125 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-03-31 | 43335 | keep | 0 | Mar | 2023 | 0.029515 | 0.00021863 | Sustained | FALSE | FALSE | Not_TMED_Event | 321
BAYAMON | 2023-03-31 19:37 | 2023-03-31 22:38 | 163 | 3:01 | P | CAUSAS EXTERNAS | 1 X 100 Y SE REMOVIO TENSOR | B23033100124 | New_Event | Damage From Public | Include | Include | Public | 181 | 2023-03-31 | 29503 | keep | 0 | Mar | 2023 | 0.020094 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
CAGUAS | 2023-03-31 19:41 | 2023-04-01 07:59 | 52 | 12:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO | C23033100134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 738 | 2023-03-31 | 38376 | keep | 0 | Mar | 2023 | 0.026138 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2023-03-31 19:57 | 2023-03-31 21:00 | 75 | 1:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23033100143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-03-31 | 4725 | keep | 0 | Mar | 2023 | 0.0032182 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-03-31 20:12 | 2023-04-01 10:50 | 6 | 14:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23033100144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 878 | 2023-03-31 | 5268 | keep | 0 | Mar | 2023 | 0.003588 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-03-31 20:24 | 2023-04-01 09:29 | 37 | 13:05 | P | CAUSAS EXTERNAS | 1 X 100 EN CORTE DE LINEA FASE CRUZADA CON TORNILLO DE NEUTRAL SECUNDARIO | P23033100108 | New_Event | Damage From Public | Include | Include | Public | 785 | 2023-03-31 | 29045 | keep | 0 | Mar | 2023 | 0.019782 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
FAJARDO | 2023-03-31 21:17 | 2023-04-01 09:14 | 1 | 11:57 | P | POWER TRANSFORMER AVERIADO | DISPARO DE LOCKOUT, PARRARAYO AVERIADO EN LA ALTA DEL XMR LLEVABA SOLO 1 CLIENTE. SJ-230331-50 | R23033100069 | New_Event | Power Transformer Failure | Include | Include | Equipment | 717 | 2023-03-31 | 717 | keep | 0 | Mar | 2023 | 0.00048835 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-03-31 21:17 | 2023-03-31 23:15 | 2722 | 1:58 | T | POWER TRANSFORMER AVERIADO | DISPARO DE LOCKOUT, PARRARAYO AVERIADO EN LA ALTA DEL XMR SE TRANSFIRIO LA CARGA AL 2006-04 | R23033100069 | New_Event | Power Transformer Failure | Include | Include | Equipment | 118 | 2023-03-31 | 321196 | keep | 0 | Mar | 2023 | 0.21877 | 0.0018539 | Sustained | FALSE | FALSE | Not_TMED_Event | 2722
FAJARDO | 2023-03-31 21:17 | 2023-03-31 23:23 | 1234 | 2:06 | T | POWER TRANSFORMER AVERIADO | DISPARO DE LOCKOUT, PARRARAYO AVERIADO EN LA ALTA DEL XMR SE TRANSFIRIO LA CARGA AL 2003-01 | R23033100069 | New_Event | Power Transformer Failure | Include | Include | Equipment | 126 | 2023-03-31 | 155484 | keep | 0 | Mar | 2023 | 0.1059 | 0.00084047 | Sustained | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2023-03-31 21:17 | 2023-03-31 23:23 | 76 | 2:06 | T | POWER TRANSFORMER AVERIADO | DISPARO DE LOCKOUT, PARRARAYO AVERIADO EN LA ALTA DEL SE TRANSFIRIO LA CARGA AL 2006-04 | R23033100069 | New_Event | Power Transformer Failure | Include | Include | Equipment | 126 | 2023-03-31 | 9576 | keep | 0 | Mar | 2023 | 0.0065222 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
VEGA BAJA | 2023-03-31 22:33 | 2023-04-01 10:13 | 16 | 11:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE REPARARON CONEXIONES SECUNDARIAS | B23033100128 | New_Event | Secondary Wire Break | Include | Include | Equipment | 700 | 2023-03-31 | 11200 | keep | 0 | Mar | 2023 | 0.0076283 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-03-31 23:21 | 2023-04-01 09:21 | 40 | 10:00 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO CON LOAD PICK UP TOOL | C23033100149 | New_Event | Primary Wire Break | Include | Include | Equipment | 600 | 2023-03-31 | 24000 | keep | 0 | Mar | 2023 | 0.016346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-01 01:13 | 2023-04-01 01:38 | 5 | 0:25 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23050100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 25 | 2023-04-01 | 125 | keep | 0 | Apr | 2023 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-04-01 01:14 | 2023-04-01 01:19 | 3114 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL SCADA | P23040100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-01 | 15570 | keep | 0 | Apr | 2023 | 0.010605 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2023-04-01 01:56 | 2023-04-01 03:30 | 70 | 1:34 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23040100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-04-01 | 6580 | keep | 0 | Apr | 2023 | 0.0044816 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-04-01 02:50 | 2023-04-01 04:44 | 26 | 1:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MALTIEMPO LLUVIA | B23040100004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 114 | 2023-04-01 | 2964 | keep | 0 | Apr | 2023 | 0.0020188 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CANOVANAS | 2023-04-01 04:21 | 2023-04-01 09:45 | 15 | 5:24 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23040100002 | New_Event | Animals | Include | Include | Wildlife | 324 | 2023-04-01 | 4860 | keep | 0 | Apr | 2023 | 0.0033101 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-01 04:40 | 2023-04-01 09:21 | 15 | 4:41 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23040100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2023-04-01 | 4215 | keep | 0 | Apr | 2023 | 0.0028708 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-04-01 04:44 | 2023-04-01 09:30 | 30 | 4:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | A23040100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2023-04-01 | 8580 | keep | 0 | Apr | 2023 | 0.0058438 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-01 04:45 | 2023-04-01 04:46 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1909-09 | S2304010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-01 04:45 | 2023-04-01 04:46 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECEEERE CARGA POR 1907-03 | S2304010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-01 | 4456 | keep | 0 | Apr | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CAGUAS | 2023-04-01 04:59 | 2023-04-01 20:08 | 50 | 15:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23040100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 909 | 2023-04-01 | 45450 | keep | 0 | Apr | 2023 | 0.030956 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-01 05:20 | 2023-04-01 08:51 | 46 | 3:31 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23040100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2023-04-01 | 9706 | keep | 0 | Apr | 2023 | 0.0066107 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BARRANQUITAS | 2023-04-01 05:32 | 2023-04-01 10:50 | 50 | 5:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | C23040100008 | New_Event | Primary Wire Break | Include | Include | Equipment | 318 | 2023-04-01 | 15900 | keep | 0 | Apr | 2023 | 0.010829 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-01 05:36 | 2023-04-01 05:37 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23040100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 2126 | keep | 0 | Apr | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-04-01 05:45 | 2023-04-01 11:58 | 20 | 6:13 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23040100011 | New_Event | Animals | Include | Include | Wildlife | 373 | 2023-04-01 | 7460 | keep | 0 | Apr | 2023 | 0.005081 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-01 06:06 | 2023-04-01 09:43 | 114 | 3:37 | P | ANIMAL | 1 X 50, 1 X 65 Y 1 X 80 EN C/L CRUCE X AVE | C23040100012 | New_Event | Animals | Include | Include | Wildlife | 217 | 2023-04-01 | 24738 | keep | 0 | Apr | 2023 | 0.016849 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
MAYAGÃœEZ | 2023-04-01 06:45 | 2023-04-01 13:32 | 7 | 6:47 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | M23040100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 407 | 2023-04-01 | 2849 | keep | 0 | Apr | 2023 | 0.0019404 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-04-01 07:32 | 2023-04-01 07:33 | 1227 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | A23040100010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-01 | 1227 | keep | 0 | Apr | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-04-01 07:33 | 2023-04-01 08:55 | 30 | 1:22 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23040100011 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 82 | 2023-04-01 | 2460 | keep | 0 | Apr | 2023 | 0.0016755 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-01 07:47 | 2023-04-01 07:48 | 1342 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR | C2304010000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-01 | 1342 | keep | 0 | Apr | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2023-04-01 07:48 | 2023-04-01 12:12 | 43 | 4:24 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23040100092 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 264 | 2023-04-01 | 11352 | keep | 0 | Apr | 2023 | 0.0077318 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-04-01 08:00 | 2023-04-01 09:18 | 23 | 1:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMRIA DESGANCHE | S23040100001 | New_Event | Cutout Failure | Include | Include | Equipment | 78 | 2023-04-01 | 1794 | keep | 0 | Apr | 2023 | 0.0012219 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-04-01 08:00 | 2023-04-01 09:33 | 4 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN RISER VIENTO FUERTE | B23040100011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-04-01 | 372 | keep | 0 | Apr | 2023 | 0.00025337 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-04-01 08:00 | 2023-04-01 11:30 | 1 | 3:30 | P | DESGANCHE | 2 X 10 EN CORTE DE LINEA SE RETIRO BAMBUS | A23040100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-04-01 | 210 | keep | 0 | Apr | 2023 | 0.00014303 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-01 08:11 | 2023-04-01 08:12 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040100016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 4132 | keep | 0 | Apr | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
AGUADILLA | 2023-04-01 08:33 | 2023-04-01 13:17 | 40 | 4:44 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CONECTOR DAÃ‘ADO | M23040100009 | New_Event | Primary Wire Break | Include | Include | Equipment | 284 | 2023-04-01 | 11360 | keep | 0 | Apr | 2023 | 0.0077372 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-01 08:36 | 2023-04-01 13:48 | 388 | 5:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 100 EN C/L MAL TIEMPO LLUVIAS | C23040100028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 312 | 2023-04-01 | 121056 | keep | 0 | Apr | 2023 | 0.082451 | 0.00026427 | Sustained | FALSE | FALSE | Not_TMED_Event | 388
CAGUAS | 2023-04-01 08:39 | 2023-04-01 18:18 | 8 | 9:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 25 KVA X 25 KVA | C23040100029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 579 | 2023-04-01 | 4632 | keep | 0 | Apr | 2023 | 0.0031548 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-04-01 08:47 | 2023-04-01 10:18 | 1403 | 1:31 | T | PARARRAYOS DEFECTUOSO | DISPARO DE BKR SE SECICONALIZO Y SE CERRO POR CONTROL 95% EN SERVICIO | C23040100031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 91 | 2023-04-01 | 127673 | keep | 0 | Apr | 2023 | 0.086957 | 0.00095558 | Sustained | FALSE | FALSE | Not_TMED_Event | 1403
ARECIBO | 2023-04-01 08:57 | 2023-04-01 08:58 | 2201 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FALTA PATRULLAR ÃREA QUE REQUIERE PATRULLAJE AÃ‰REO | A23040100019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 2201 | keep | 0 | Apr | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-04-01 08:57 | 2023-04-01 08:58 | 1986 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FALTA PATRULLAR ÃREA QUE REQUIERE PATRULLAJE AÃ‰REO | A23040100019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 1986 | keep | 0 | Apr | 2023 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-04-01 08:57 | 2023-04-01 08:58 | 199 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FALTA PATRULLAR ÃREA QUE REQUIERE PATRULLAJE AÃ‰REO | A23040100019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 199 | keep | 0 | Apr | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-04-01 08:57 | 2023-04-01 08:58 | 24 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 FALTA PATRULLAR ÃREA QUE REQUIERE PATRULLAJE AÃ‰REO | A23040100019 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 24 | keep | 0 | Apr | 2023 | 1.6346e-05 | 1.6346e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 24
ARECIBO | 2023-04-01 09:11 | 2023-04-01 09:12 | 1227 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | A23040100020 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-04-01 | 1227 | keep | 0 | Apr | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-04-01 09:12 | 2023-04-01 11:30 | 25 | 2:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A23040100032 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 138 | 2023-04-01 | 3450 | keep | 0 | Apr | 2023 | 0.0023498 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-04-01 09:15 | 2023-04-01 09:16 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23040100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 1271 | keep | 0 | Apr | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
BARRANQUITAS | 2023-04-01 09:15 | 2023-04-01 13:09 | 120 | 3:54 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C23040100043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-04-01 | 28080 | keep | 0 | Apr | 2023 | 0.019125 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
MAYAGÃœEZ | 2023-04-01 09:20 | 2023-04-01 23:54 | 810 | 14:34 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 POSTE TRANSMISION PARTIDO CON EL ALIMENTADOR 6101-01. SE REMPLAZO POSTE Y SE ENERGIZO EL ALIMENTADOR 6101-01. | M23040100029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 874 | 2023-04-01 | 707940 | keep | 0 | Apr | 2023 | 0.48217 | 0.00055169 | Sustained | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2023-04-01 09:20 | 2023-04-01 15:27 | 1235 | 6:07 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 5600 POSTE DE TRANSMISION PARTIDO CON EL ALIMENTADOR 6101-01 | M23040100029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 367 | 2023-04-01 | 453245 | keep | 0 | Apr | 2023 | 0.3087 | 0.00084115 | Sustained | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2023-04-01 09:20 | 2023-04-01 15:27 | 93 | 6:07 | S | LINEA DE TRANSMISION 38KV | DISAPRO DE LINEA 5600 POSTE DE TRANSMISION PARTIDO CON EL ALIMENTADOR 6101-01 | M23040100029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 367 | 2023-04-01 | 34131 | keep | 0 | Apr | 2023 | 0.023246 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2023-04-01 09:20 | 2023-04-01 15:27 | 1825 | 6:07 | S | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA SUBESTACION PARA ABRIR PUENTE EN LINEA 5600 POR POSTE TRANSMISION PARTIDO CON EL ALIMENTADOR 6101-01 | M23040100029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 367 | 2023-04-01 | 669775 | keep | 0 | Apr | 2023 | 0.45618 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2023-04-01 09:20 | 2023-04-01 15:27 | 3230 | 6:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 SE RETIRO CARGA SUBESTACION | M23040100029 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 367 | 2023-04-01 | 1185410 | keep | 0 | Apr | 2023 | 0.80738 | 0.0021999 | Sustained | FALSE | FALSE | Not_TMED_Event | 3230
FAJARDO | 2023-04-01 09:29 | 2023-04-01 09:30 | 1234 | 0:01 | T | POWER TRANSFORMER AVERIADO | SE HICIERON OPERACIONES CON SJ-230331-50 SE DEVOLVIERON LAS CARGAS ABRIENDO N/O ENTRE 2005-10/2006-04(NO FASEAN) Y SE CERRO BKR 2005-10 | R23033100069 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1 | 2023-04-01 | 1234 | keep | 0 | Apr | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
ARECIBO | 2023-04-01 09:36 | 2023-04-01 14:00 | 40 | 4:24 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR RAMA SOBRE LAS LINEAS | A23040100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2023-04-01 | 10560 | keep | 0 | Apr | 2023 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-04-01 09:46 | 2023-04-01 11:17 | 23 | 1:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON SECUNDARIAS | R23040100013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 91 | 2023-04-01 | 2093 | keep | 0 | Apr | 2023 | 0.0014255 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
ARECIBO | 2023-04-01 09:50 | 2023-04-01 10:12 | 25 | 0:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR CONECTOR CON PUNTO CALIENTE | A23040100029 | New_Event | Primary Wire Break | Include | Include | Equipment | 22 | 2023-04-01 | 550 | keep | 0 | Apr | 2023 | 0.0003746 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-01 09:52 | 2023-04-01 09:53 | 1976 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23040100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 1976 | keep | 0 | Apr | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BARRANQUITAS | 2023-04-01 09:52 | 2023-04-01 15:48 | 111 | 5:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REPARO CORNED BRACKET EN VARIOS PUNTOS | C23040100061 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 356 | 2023-04-01 | 39516 | keep | 0 | Apr | 2023 | 0.026914 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
CANOVANAS | 2023-04-01 09:54 | 2023-04-01 11:20 | 65 | 1:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | R23040100016 | New_Event | Cutout Failure | Include | Include | Equipment | 86 | 2023-04-01 | 5590 | keep | 0 | Apr | 2023 | 0.0038073 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-04-01 09:59 | 2023-04-01 10:32 | 2 | 0:33 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | B23040100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-04-01 | 66 | keep | 0 | Apr | 2023 | 4.4952e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-04-01 10:10 | 2023-04-01 16:50 | 100 | 6:40 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M23040100087 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 400 | 2023-04-01 | 40000 | keep | 0 | Apr | 2023 | 0.027244 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-01 10:18 | 2023-04-01 14:16 | 25 | 3:58 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23040100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-04-01 | 5950 | keep | 0 | Apr | 2023 | 0.0040525 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-01 10:18 | 2023-04-01 13:46 | 25 | 3:28 | P | DESGANCHE | 1 X 65 DESGANCHE Y SE LEVANTO CONDUCTOR | S23040100025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2023-04-01 | 5200 | keep | 0 | Apr | 2023 | 0.0035417 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-01 10:18 | 2023-04-01 11:27 | 71 | 1:09 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO EN EL TRONCAL 100% EN SERVICIO | C23040100031 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 69 | 2023-04-01 | 4899 | keep | 0 | Apr | 2023 | 0.0033367 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
FAJARDO | 2023-04-01 10:38 | 2023-04-01 14:30 | 16 | 3:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23040100022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 232 | 2023-04-01 | 3712 | keep | 0 | Apr | 2023 | 0.0025282 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-04-01 10:55 | 2023-04-01 13:00 | 25 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23040100027 | New_Event | Primary Wire Break | Include | Include | Equipment | 125 | 2023-04-01 | 3125 | keep | 0 | Apr | 2023 | 0.0021284 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-01 11:03 | 2023-04-01 14:45 | 67 | 3:42 | P | CONDUCTOR ROTO O ABIERTO | BY-230401-01 SE SECCIONALIZO ALIMENTADOR POR PUENTES ABIERTOS | B23040100027 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-04-01 | 14874 | keep | 0 | Apr | 2023 | 0.010131 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
ARECIBO | 2023-04-01 11:03 | 2023-04-01 13:40 | 30 | 2:37 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA CAMION ROMPIO TENSOR DE POSTE Y CRUZO FASES | A23040100038 | New_Event | Damage From Public | Include | Include | Public | 157 | 2023-04-01 | 4710 | keep | 0 | Apr | 2023 | 0.003208 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-01 11:07 | 2023-04-01 15:28 | 202 | 4:21 | P | DESGANCHE | 3 X 65 Y 3 X 50 EN C/L DESGANCHE | B23040100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-04-01 | 52722 | keep | 0 | Apr | 2023 | 0.035909 | 0.00013758 | Sustained | FALSE | FALSE | Not_TMED_Event | 202
AGUADILLA | 2023-04-01 11:13 | 2023-04-01 14:35 | 150 | 3:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M23040100112 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 202 | 2023-04-01 | 30300 | keep | 0 | Apr | 2023 | 0.020637 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-01 11:16 | 2023-04-01 11:32 | 1058 | 0:16 | P | TERMINACION SOTERRADA AVERIADA | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA REPARAR TERMINACION SOTERRADA 20% POR EL 1424-08 SJ-230401-01 | S23040100037 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 16 | 2023-04-01 | 16928 | keep | 0 | Apr | 2023 | 0.01153 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-04-01 11:16 | 2023-04-01 11:32 | 1251 | 0:16 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA REPARAR TERMINACION SOTERRADA 80% POR EL 1424-08 SJ-230401-01 | S23040100037 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-04-01 | 20016 | keep | 0 | Apr | 2023 | 0.013633 | 0.00085205 | Sustained | FALSE | FALSE | Not_TMED_Event | 1251
SAN JUAN | 2023-04-01 11:16 | 2023-04-01 11:32 | 278 | 0:16 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA REPARAR TERMINACION SOTERRADA CARGA POR EL 1424-08 SJ-230401-01 | S23040100037 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-04-01 | 4448 | keep | 0 | Apr | 2023 | 0.0030295 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-04-01 11:16 | 2023-04-01 11:32 | 1295 | 0:16 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA REPARAR TERMINACION SOTERRADA CARGA POR EL 1424-08 SJ-230401-01 | S23040100037 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-04-01 | 20720 | keep | 0 | Apr | 2023 | 0.014112 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-04-01 11:16 | 2023-04-01 11:32 | 9 | 0:16 | T | ALIMENTADOR AMARRADO | DISPAARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA REPARAR TERMINACION SOTERRADA LLEVA LA CARGA DEL 1348-07 80% DEL 1348-08 20% DEL 1336-08 LA CARGA DEL 1401-10 SJ-230401-01 | S23040100037 | New_Event | Feeder Load Transferred | Include | Include | Other | 16 | 2023-04-01 | 144 | keep | 0 | Apr | 2023 | 9.8078e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-04-01 11:32 | 2023-04-01 14:56 | 5 | 3:24 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION SOTERRADA EN CAJAS SECAS EN MH-07 SJ-230401-01 | S23040100037 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 204 | 2023-04-01 | 1020 | keep | 0 | Apr | 2023 | 0.00069472 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-01 11:42 | 2023-04-01 19:33 | 1 | 7:51 | P | DESGANCHE | 1 X 10 EN XMR Y SE DESGANCHO | B23040100070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2023-04-01 | 471 | keep | 0 | Apr | 2023 | 0.0003208 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-01 11:46 | 2023-04-01 17:26 | 1 | 5:40 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23040100075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 340 | 2023-04-01 | 340 | keep | 0 | Apr | 2023 | 0.00023157 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-01 11:49 | 2023-04-01 13:39 | 55 | 1:50 | P | DESGANCHE | 1 X 40 EN C/L Y SE RETIRO RAMA | B23040100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-04-01 | 6050 | keep | 0 | Apr | 2023 | 0.0041206 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2023-04-01 12:04 | 2023-04-01 12:05 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA | B2304010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 4431 | keep | 0 | Apr | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-04-01 12:06 | 2023-04-01 16:39 | 34 | 4:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIA | B23040100090 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 273 | 2023-04-01 | 9282 | keep | 0 | Apr | 2023 | 0.0063219 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CANOVANAS | 2023-04-01 12:06 | 2023-04-01 12:54 | 6 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23040100028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2023-04-01 | 288 | keep | 0 | Apr | 2023 | 0.00019616 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-04-01 12:14 | 2023-04-01 12:46 | 23 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES EN LINEA SECUNDARIA | P23040100037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-04-01 | 736 | keep | 0 | Apr | 2023 | 0.00050129 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 959 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 959 | keep | 0 | Apr | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 1382 | keep | 0 | Apr | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 663 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 663 | keep | 0 | Apr | 2023 | 0.00045157 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 1514 | keep | 0 | Apr | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 1105 | keep | 0 | Apr | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 4176 | keep | 0 | Apr | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 252 | keep | 0 | Apr | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 2147 | keep | 0 | Apr | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-04-01 12:29 | 2023-04-01 12:30 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23040100135 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 2858 | keep | 0 | Apr | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-04-01 12:38 | 2023-04-01 15:58 | 143 | 3:20 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23040100123 | New_Event | Animals | Include | Include | Wildlife | 200 | 2023-04-01 | 28600 | keep | 0 | Apr | 2023 | 0.019479 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
BARRANQUITAS | 2023-04-01 12:49 | 2023-04-01 14:14 | 10 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS | C23040100114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2023-04-01 | 850 | keep | 0 | Apr | 2023 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-01 13:04 | 2023-04-01 15:08 | 139 | 2:04 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23040100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-04-01 | 17236 | keep | 0 | Apr | 2023 | 0.011739 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
MAYAGÃœEZ | 2023-04-01 13:05 | 2023-04-01 17:00 | 100 | 3:55 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M23040100139 | New_Event | Animals | Include | Include | Wildlife | 235 | 2023-04-01 | 23500 | keep | 0 | Apr | 2023 | 0.016006 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-01 13:35 | 2023-04-01 15:57 | 1336 | 2:22 | T | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO SE CERRO INTERRUPTOR | M23040100141 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 142 | 2023-04-01 | 189712 | keep | 0 | Apr | 2023 | 0.12921 | 0.00090994 | Sustained | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2023-04-01 14:16 | 2023-04-01 17:15 | 60 | 2:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040100157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-04-01 | 10740 | keep | 0 | Apr | 2023 | 0.007315 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-01 14:19 | 2023-04-01 15:40 | 62 | 1:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23040100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-04-01 | 5022 | keep | 0 | Apr | 2023 | 0.0034205 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-04-01 14:33 | 2023-04-01 17:37 | 138 | 3:04 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23040100165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 184 | 2023-04-01 | 25392 | keep | 0 | Apr | 2023 | 0.017294 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
CANOVANAS | 2023-04-01 14:37 | 2023-04-01 18:39 | 125 | 4:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R23040100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2023-04-01 | 30250 | keep | 0 | Apr | 2023 | 0.020603 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-04-01 14:41 | 2023-04-01 17:06 | 25 | 2:25 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | S23040100056 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-04-01 | 3625 | keep | 0 | Apr | 2023 | 0.002469 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-04-01 14:44 | 2023-04-01 15:34 | 10 | 0:50 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R23040100037 | New_Event | Animals | Include | Include | Wildlife | 50 | 2023-04-01 | 500 | keep | 0 | Apr | 2023 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-01 14:45 | 2023-04-01 16:18 | 310 | 1:33 | P | CONDUCTOR ROTO O ABIERTO | BY-230401-01 SE REPARO PUENTE ABIERTO Y SE CERRO MACHETES | B23040100027 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 93 | 2023-04-01 | 28830 | keep | 0 | Apr | 2023 | 0.019636 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-04-01 14:48 | 2023-04-01 14:49 | 47 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23040100167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 47 | keep | 0 | Apr | 2023 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-04-01 14:57 | 2023-04-01 15:00 | 553 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 60% DE SU CARGA POR EL 1529-15 SE CERRO POR SCADA | S23040100075 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-01 | 1659 | keep | 0 | Apr | 2023 | 0.0011299 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
SAN JUAN | 2023-04-01 14:57 | 2023-04-01 15:00 | 1802 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR LLEVA 60% DEL 1346-02 SE CERRO POR SCADA | S23040100075 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-01 | 5406 | keep | 0 | Apr | 2023 | 0.003682 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2023-04-01 15:00 | 2023-04-01 15:23 | 25 | 0:23 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23040100124 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 23 | 2023-04-01 | 575 | keep | 0 | Apr | 2023 | 0.00039163 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-01 15:01 | 2023-04-01 16:31 | 30 | 1:30 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23040100055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-04-01 | 2700 | keep | 0 | Apr | 2023 | 0.001839 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-01 15:23 | 2023-04-01 15:24 | 553 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 1529-15 SE CERRO POR SCADA | S2304010000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-01 | 553 | keep | 0 | Apr | 2023 | 0.00037665 | 0.00037665 | Momentary | FALSE | FALSE | Not_TMED_Event | 553
SAN JUAN | 2023-04-01 15:23 | 2023-04-01 15:24 | 1802 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR LLEVA 60% DEL 1346-02 | S2304010000X | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-01 | 1802 | keep | 0 | Apr | 2023 | 0.0012273 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-04-01 15:23 | 2023-04-01 15:28 | 47 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO. SE CERRO POR CONTROL SCADA | M23040100174 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-01 | 235 | keep | 0 | Apr | 2023 | 0.00016006 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-04-01 15:24 | 2023-04-01 21:25 | 25 | 6:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23040100124 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 361 | 2023-04-01 | 9025 | keep | 0 | Apr | 2023 | 0.0061469 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-04-01 15:31 | 2023-04-01 16:49 | 1979 | 1:18 | T | CONDUCTOR ARRIADO O CRUZADO | SE PATRULLO COMPLETO Y LO QUE VEN ES QUE HAY MUCHO VIENTO Y LAS LINEAS ARRIADAS SE PEGAN SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23040100053 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 78 | 2023-04-01 | 154362 | keep | 0 | Apr | 2023 | 0.10514 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
AGUADILLA | 2023-04-01 15:31 | 2023-04-01 15:32 | 47 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23040100177 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 47 | keep | 0 | Apr | 2023 | 3.2011e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-04-01 15:32 | 2023-04-01 18:41 | 693 | 3:09 | S | ANIMAL | SE RETIRO IGUANA SOBRE TRANSFORMADOR, SE REMPLAZO FUSIBLE EN LA ALTA Y SE RESTABLECIO CARGA | M23040100234 | New_Event | Animals | Include | Include | Wildlife | 189 | 2023-04-01 | 130977 | keep | 0 | Apr | 2023 | 0.089208 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2023-04-01 15:32 | 2023-04-01 18:41 | 47 | 3:09 | S | ANIMAL | SE RETIRO IGUANA SOBRE TRANSFORMADOR, SE REMPLAZO FUSIBLE EN LA ALTA Y SE RESTABLECIO CARGA | M23040100234 | New_Event | Animals | Include | Include | Wildlife | 189 | 2023-04-01 | 8883 | keep | 0 | Apr | 2023 | 0.0060502 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
AGUADILLA | 2023-04-01 15:32 | 2023-04-01 18:41 | 1256 | 3:09 | S | ANIMAL | SE RETIRO IGUANA SOBRE TRANSFORMADOR, SE REMPLAZO FUSIBLE EN LA ALTA Y SE RESTABLECIO CARGA | M23040100234 | New_Event | Animals | Include | Include | Wildlife | 189 | 2023-04-01 | 237384 | keep | 0 | Apr | 2023 | 0.16168 | 0.00085546 | Sustained | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2023-04-01 15:32 | 2023-04-01 18:41 | 558 | 3:09 | S | ANIMAL | SE RETIRO IGUANA SOBRE TRANSFORMADOR, SE REMPLAZO FUSIBLE EN LA ALTA Y SE RESTABLECIO CARGA | M23040100234 | New_Event | Animals | Include | Include | Wildlife | 189 | 2023-04-01 | 105462 | keep | 0 | Apr | 2023 | 0.07183 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
SAN JUAN | 2023-04-01 15:45 | 2023-04-01 19:33 | 156 | 3:48 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | S23040100088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 228 | 2023-04-01 | 35568 | keep | 0 | Apr | 2023 | 0.024225 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
YAUCO | 2023-04-01 16:00 | 2023-04-01 18:21 | 8 | 2:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE TRANSFORMADOR 1 X 30 | P23040100058 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2023-04-01 | 1128 | keep | 0 | Apr | 2023 | 0.00076828 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-01 16:06 | 2023-04-01 16:10 | 1483 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 30% DE SU CARGA POR EL 1336-08 SE CERRO POR SCADA | S2304010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-04-01 | 5932 | keep | 0 | Apr | 2023 | 0.0040403 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-04-01 16:06 | 2023-04-01 16:10 | 1531 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 15% DE SU CARGA POR EL 1336-08 SE CERRO POR SCADA | S2304010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-04-01 | 6124 | keep | 0 | Apr | 2023 | 0.004171 | 0.0010428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-04-01 16:06 | 2023-04-01 16:10 | 5290 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 30% DEL 1204-04 LLEVA 15% DEL 1204-05 SE CERRO POR SCADA | S2304010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-01 | 21160 | keep | 0 | Apr | 2023 | 0.014412 | 0.003603 | Momentary | FALSE | FALSE | Not_TMED_Event | 5290
MAYAGÃœEZ | 2023-04-01 16:12 | 2023-04-01 20:50 | 75 | 4:38 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M23040100205 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 278 | 2023-04-01 | 20850 | keep | 0 | Apr | 2023 | 0.014201 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2023-04-01 16:27 | 2023-04-02 15:00 | 12 | 22:33 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 2400 VOLT AVERIADO | P23040100060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1353 | 2023-04-01 | 16236 | keep | 0 | Apr | 2023 | 0.011058 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-01 17:08 | 2023-04-01 18:15 | 12 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23040100121 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2023-04-01 | 804 | keep | 0 | Apr | 2023 | 0.0005476 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-04-01 17:11 | 2023-04-01 19:50 | 35 | 2:39 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA GLOBO CRUZO LINEAS | A23040100057 | New_Event | Damage From Public | Include | Include | Public | 159 | 2023-04-01 | 5565 | keep | 0 | Apr | 2023 | 0.0037903 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-04-01 17:42 | 2023-04-01 19:30 | 26 | 1:48 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | B23040100230 | New_Event | Switch Failure | Include | Include | Equipment | 108 | 2023-04-01 | 2808 | keep | 0 | Apr | 2023 | 0.0019125 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2023-04-01 17:43 | 2023-04-01 22:49 | 60 | 5:06 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23040100140 | New_Event | Animals | Include | Include | Wildlife | 306 | 2023-04-01 | 18360 | keep | 0 | Apr | 2023 | 0.012505 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-04-01 17:44 | 2023-04-01 20:00 | 1 | 2:16 | P | ANIMAL | 2 X 15 EN RISER AVE CRUZO RISER | M23040100245 | New_Event | Animals | Include | Include | Wildlife | 136 | 2023-04-01 | 136 | keep | 0 | Apr | 2023 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-01 17:54 | 2023-04-01 18:36 | 7 | 0:42 | P | EXCAVACIONES | 1 X 8 EN TRANSFORMADOR PERITO ELECTRICISTA EN EXCAVACION CRUZO FASE | P23040100078 | New_Event | Excavation | Include | Include | Public | 42 | 2023-04-01 | 294 | keep | 0 | Apr | 2023 | 0.00020024 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-04-01 17:55 | 2023-04-01 21:46 | 76 | 3:51 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA | R23040100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-04-01 | 17556 | keep | 0 | Apr | 2023 | 0.011957 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
PONCE | 2023-04-01 18:03 | 2023-04-02 10:30 | 10 | 16:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO CAJA EN XMR | P23040100084 | New_Event | Cutout Failure | Include | Include | Equipment | 987 | 2023-04-01 | 9870 | keep | 0 | Apr | 2023 | 0.0067224 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-01 18:14 | 2023-04-01 19:14 | 100 | 1:00 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA LINEAS ARRIADAS | P23040100086 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 60 | 2023-04-01 | 6000 | keep | 0 | Apr | 2023 | 0.0040866 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-01 18:41 | 2023-04-02 08:20 | 12 | 13:39 | P | OTRAS CAUSAS | 1 X 20 EN TRANSFORMADOR FUSIBLE PODRIDO | M23040100313 | New_Event | Other Causes | Include | Include | Other | 819 | 2023-04-01 | 9828 | keep | 0 | Apr | 2023 | 0.0066938 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-04-01 18:51 | 2023-04-02 12:30 | 100 | 17:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | M23040100261 | New_Event | Primary Wire Break | Include | Include | Equipment | 1059 | 2023-04-01 | 105900 | keep | 0 | Apr | 2023 | 0.072128 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-01 19:03 | 2023-04-01 20:45 | 15 | 1:42 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23040100062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2023-04-01 | 1530 | keep | 0 | Apr | 2023 | 0.0010421 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-04-01 19:09 | 2023-04-01 23:52 | 230 | 4:43 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 Y 1 X 80 EN C/L SE REEMPLAZO AISLADOR Y PIN POLE TOP | C23040100148 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 283 | 2023-04-01 | 65090 | keep | 0 | Apr | 2023 | 0.044333 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
SAN JUAN | 2023-04-01 20:20 | 2023-04-02 14:24 | 53 | 18:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23040100132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1084 | 2023-04-01 | 57452 | keep | 0 | Apr | 2023 | 0.03913 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2023-04-01 21:43 | 2023-04-02 00:31 | 25 | 2:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X100 EN C/L 1X 15 EN XMR SE ELIMINO CONDUCTOR PRIMARIO QUE ESTABA TOCANDO CAJA PRMARIA | S23040100136 | New_Event | Primary Wire Break | Include | Include | Equipment | 168 | 2023-04-01 | 4200 | keep | 0 | Apr | 2023 | 0.0028606 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-01 21:57 | 2023-04-02 08:51 | 16 | 10:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23040100166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 654 | 2023-04-01 | 10464 | keep | 0 | Apr | 2023 | 0.007127 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-04-01 22:22 | 2023-04-02 08:06 | 16 | 9:44 | P | CABLE SOTERRADO AVERIADO | 1 X 25 EN SU 16 AVERIA NUEVA ENTRE T58 @ T 57 | B23040100264 | New_Event | UG Cable Fault | Include | Include | Equipment | 584 | 2023-04-01 | 9344 | keep | 0 | Apr | 2023 | 0.0063642 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2023-04-01 22:50 | 2023-04-02 12:21 | 10 | 13:31 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN SW SE REPARO BUSCHING EN XMR | P23040100101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 811 | 2023-04-01 | 8110 | keep | 0 | Apr | 2023 | 0.0055237 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-01 23:13 | 2023-04-01 23:14 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23040100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 476 | keep | 0 | Apr | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-04-01 23:13 | 2023-04-01 23:14 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23040100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 1655 | keep | 0 | Apr | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-04-01 23:13 | 2023-04-01 23:14 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23040100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 361 | keep | 0 | Apr | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-04-01 23:13 | 2023-04-01 23:14 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23040100172 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 2842 | keep | 0 | Apr | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-04-01 23:13 | 2023-04-01 23:14 | 1702 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23040100173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-04-01 23:13 | 2023-04-01 23:14 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23040100173 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 918 | keep | 0 | Apr | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-04-01 23:13 | 2023-04-01 23:14 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23040100174 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-01 | 1725 | keep | 0 | Apr | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
HUMACAO | 2023-04-01 23:48 | 2023-04-01 23:50 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23040100176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-01 | 4252 | keep | 0 | Apr | 2023 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2023-04-01 23:50 | 2023-04-01 23:51 | 1097 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23040100317 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-01 | 1097 | keep | 0 | Apr | 2023 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
BAYAMON | 2023-04-02 00:33 | 2023-04-02 00:34 | 4079 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 10 % POR 1801-02 | B2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 4079 | keep | 0 | Apr | 2023 | 0.0027782 | 0.0027782 | Momentary | FALSE | FALSE | Not_TMED_Event | 4079
BARRANQUITAS | 2023-04-02 02:15 | 2023-04-02 09:23 | 39 | 7:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23040200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 428 | 2023-04-02 | 16692 | keep | 0 | Apr | 2023 | 0.011369 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2023-04-02 02:18 | 2023-04-02 02:19 | 138 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1206-04 10% POR 1206-04 | S2304020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-02 | 138 | keep | 0 | Apr | 2023 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-04-02 02:18 | 2023-04-02 02:19 | 1977 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1206-04 40% POR 1206-04 | S2304020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-02 | 1977 | keep | 0 | Apr | 2023 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-04-02 02:18 | 2023-04-02 02:19 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 10 % DEL 1204-03 LLEVA 40% DEL 1204-04 | S2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 1799 | keep | 0 | Apr | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
MAYAGÃœEZ | 2023-04-02 02:23 | 2023-04-02 11:20 | 130 | 8:57 | P | PARARRAYOS DEFECTUOSO | 1 X 100, 1 X 65 Y 2 X 50 EN CORTES DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | M23040200010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 537 | 2023-04-02 | 69810 | keep | 0 | Apr | 2023 | 0.047547 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2023-04-02 03:47 | 2023-04-02 04:57 | 2861 | 1:10 | T | ARBOL SOBRE LINEA | BY-230402-01 SE SECCIONALIZO TRAMO PARA RETIRAR ARBOL SOBRE LINEA 60% EN SERVICIO | B23040200001 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 70 | 2023-04-02 | 200270 | keep | 0 | Apr | 2023 | 0.1364 | 0.0019486 | Sustained | FALSE | FALSE | Not_TMED_Event | 2861
CAGUAS | 2023-04-02 04:21 | 2023-04-02 04:22 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2023-04-02 04:57 | 2023-04-02 06:44 | 1144 | 1:47 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEAS BY-230402-01 | B23040200001 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 107 | 2023-04-02 | 122408 | keep | 0 | Apr | 2023 | 0.083372 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-02 05:26 | 2023-04-02 10:06 | 30 | 4:40 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040200001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-04-02 | 8400 | keep | 0 | Apr | 2023 | 0.0057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-02 05:28 | 2023-04-02 16:54 | 10 | 11:26 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN XMR Y DEAGANCHE SECUNDARIO | S23040200005 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 686 | 2023-04-02 | 6860 | keep | 0 | Apr | 2023 | 0.0046723 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-02 06:54 | 2023-04-02 06:55 | 1615 | 0:01 | T | ANIMAL | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2304020000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-02 | 1615 | keep | 0 | Apr | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-04-02 06:55 | 2023-04-02 09:21 | 121 | 2:26 | P | ANIMAL | 1 X 25 EN RISER Y 2 X 80 EN C/L REMPLAZO CAJA QUEMADA X AVE | R23040200003 | 1st_after_momentary | Animals | Include | Include | Wildlife | 146 | 2023-04-02 | 17666 | keep | 0 | Apr | 2023 | 0.012032 | 8.2413e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 121
SAN JUAN | 2023-04-02 06:58 | 2023-04-02 13:26 | 15 | 6:28 | P | DESGANCHE | 1 X 25 EN SU-12 SE REALIZO DESGANCHE | S23040200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2023-04-02 | 5820 | keep | 0 | Apr | 2023 | 0.003964 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-04-02 07:01 | 2023-04-02 10:40 | 50 | 3:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23040200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2023-04-02 | 10950 | keep | 0 | Apr | 2023 | 0.007458 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-02 07:05 | 2023-04-02 18:45 | 21 | 11:40 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23040200010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 700 | 2023-04-02 | 14700 | keep | 0 | Apr | 2023 | 0.010012 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CAGUAS | 2023-04-02 07:34 | 2023-04-02 07:35 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 6197 | keep | 0 | Apr | 2023 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
BAYAMON | 2023-04-02 07:37 | 2023-04-02 07:38 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23040200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2023-04-02 07:47 | 2023-04-02 11:07 | 761 | 3:20 | T | DESGANCHE | DISPARO DE INTERRUPTOR LLEVA EL 1421-01 SE RETIRO RAMA DE LINEA Y SE CERRO POR SCADA | S23040200102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-04-02 | 152200 | keep | 0 | Apr | 2023 | 0.10366 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2023-04-02 07:47 | 2023-04-02 11:07 | 1498 | 3:20 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 1310-04 SE RETIRO RAMA DE LINEA Y SE CERRO POR SCADA | S23040200102 | New_Event | Feeder Load Transferred | Include | Include | Other | 200 | 2023-04-02 | 299600 | keep | 0 | Apr | 2023 | 0.20406 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-04-02 07:54 | 2023-04-02 11:00 | 200 | 3:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 140 EN C/L SE REEMPLAZO AISLADOR ROTO Y SE SUBIO LINEA | B23040200014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 186 | 2023-04-02 | 37200 | keep | 0 | Apr | 2023 | 0.025337 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-02 07:57 | 2023-04-02 09:32 | 30 | 1:35 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | B23040200015 | New_Event | Animals | Include | Include | Wildlife | 95 | 2023-04-02 | 2850 | keep | 0 | Apr | 2023 | 0.0019411 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-04-02 08:00 | 2023-04-02 08:01 | 2450 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 12600 QUE ESTA POR EL 5350 FUSIBLES FUNDIDOS EN SUBESTACIÃ“N 2675 MICROSOFT | C23040200011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-02 | 2450 | keep | 0 | Apr | 2023 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-04-02 08:00 | 2023-04-02 08:01 | 640 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 12600 QUE ESTA POR EL 5350 FUSIBLES FUNDIDOS EN SUBESTACIÃ“N 2675 MICROSOFT | C23040200011 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-02 | 640 | keep | 0 | Apr | 2023 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
BAYAMON | 2023-04-02 08:06 | 2023-04-02 18:26 | 5 | 10:20 | P | CABLE SOTERRADO AVERIADO | BY-230402-02 SE REPARO TRAMO SOTTERRADO DE T58 @T 57 | B23040100264 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 620 | 2023-04-02 | 3100 | keep | 0 | Apr | 2023 | 0.0021114 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-02 08:08 | 2023-04-02 08:09 | 2704 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 2704 | keep | 0 | Apr | 2023 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2023-04-02 08:15 | 2023-04-02 09:08 | 15 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO Y CONECTORES | B23040200018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-04-02 | 795 | keep | 0 | Apr | 2023 | 0.00054147 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-02 08:17 | 2023-04-02 18:47 | 13 | 10:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO PM 75KVA X 50KVA Y 1 X 50 EN RISER | S23040200048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 630 | 2023-04-02 | 8190 | keep | 0 | Apr | 2023 | 0.0055782 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-04-02 09:05 | 2023-04-02 10:28 | 20 | 1:23 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA POR PALOMA QUE CRUZO LINEAS | A23040200005 | New_Event | Animals | Include | Include | Wildlife | 83 | 2023-04-02 | 1660 | keep | 0 | Apr | 2023 | 0.0011306 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-04-02 09:06 | 2023-04-02 10:30 | 11 | 1:24 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHE Y SE REEMPLAZO SECUNDARIA AVERIADA POR ARBOL | C23040200013 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 84 | 2023-04-02 | 924 | keep | 0 | Apr | 2023 | 0.00062933 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-04-02 09:15 | 2023-04-02 10:10 | 6 | 0:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 37.5KVA CON ESCAPE DE ACEITE | M23040200060 | New_Event | Service Transformer Failure | Include | Include | Equipment | 55 | 2023-04-02 | 330 | keep | 0 | Apr | 2023 | 0.00022476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-02 09:35 | 2023-04-02 11:02 | 50 | 1:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPPLAZO CAJA PRIMARIA EN C/L INTERMEDIO Y 1 X 65 EN C/L PRINCIPAL | B23040200038 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2023-04-02 | 4350 | keep | 0 | Apr | 2023 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-02 09:38 | 2023-04-02 09:39 | 1342 | 0:01 | T | ANIMAL | RECIERRE | C2304020000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-02 | 1342 | keep | 0 | Apr | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2023-04-02 09:39 | 2023-04-02 11:41 | 60 | 2:02 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C23040200018 | 1st_after_momentary | Animals | Include | Include | Wildlife | 122 | 2023-04-02 | 7320 | keep | 0 | Apr | 2023 | 0.0049856 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-02 09:41 | 2023-04-02 17:26 | 4 | 7:45 | P | DESGANCHE | 2 X 65 EN XC/L DESGANCHE | S23040200106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2023-04-02 | 1860 | keep | 0 | Apr | 2023 | 0.0012668 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-02 09:41 | 2023-04-02 13:19 | 1 | 3:38 | P | ANIMAL | SE RETIRO RATON 2 X 40 SMU20 EN GABINETE Y 2 X 50 EN RISER | B23040200039 | New_Event | Animals | Include | Include | Wildlife | 218 | 2023-04-02 | 218 | keep | 0 | Apr | 2023 | 0.00014848 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-02 10:12 | 2023-04-02 11:44 | 60 | 1:32 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23040200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-04-02 | 5520 | keep | 0 | Apr | 2023 | 0.0037596 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-02 10:16 | 2023-04-02 12:12 | 40 | 1:56 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN C/L REMPLAZO PARARRAYO | R23040200009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 116 | 2023-04-02 | 4640 | keep | 0 | Apr | 2023 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-04-02 10:20 | 2023-04-02 11:17 | 16 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | M23040200090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-04-02 | 912 | keep | 0 | Apr | 2023 | 0.00062116 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-04-02 11:28 | 2023-04-02 14:50 | 100 | 3:22 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23040200126 | New_Event | Primary Wire Break | Include | Include | Equipment | 202 | 2023-04-02 | 20200 | keep | 0 | Apr | 2023 | 0.013758 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-02 11:31 | 2023-04-02 15:33 | 50 | 4:02 | P | ANIMAL | 1 X 50 EN C/L CRUCE DE IGUANA | S23040200176 | New_Event | Animals | Include | Include | Wildlife | 242 | 2023-04-02 | 12100 | keep | 0 | Apr | 2023 | 0.0082413 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-02 11:34 | 2023-04-02 15:37 | 1483 | 4:03 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO TRAMO Y SE REEMPLAZO MACHETE QUEMADO Y AISLADORES 30% DE SU CARGA POR EL 1336-08 SJ-230402-02 | S23040200271 | New_Event | Feeder Load Transferred | Include | Include | Other | 243 | 2023-04-02 | 360369 | keep | 0 | Apr | 2023 | 0.24545 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-04-02 11:34 | 2023-04-02 15:37 | 1531 | 4:03 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO TRAMO Y SE REEMPLAZO MACHETE QUEMADO Y AISLADORES 15% DE SU CARGA POR EL 1336-08 SJ-230402-02 | S23040200271 | New_Event | Feeder Load Transferred | Include | Include | Other | 243 | 2023-04-02 | 372033 | keep | 0 | Apr | 2023 | 0.25339 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-04-02 11:34 | 2023-04-02 15:37 | 5290 | 4:03 | T | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO TRAMO Y SE REEMPLAZO MACHETE QUEMADO Y AISLADORES LLEVA 30% DEL 1204-04 15% DEL 1204-05 SJ-230402-02 | S23040200271 | New_Event | Switch Failure | Include | Include | Equipment | 243 | 2023-04-02 | 1285470 | keep | 0 | Apr | 2023 | 0.87553 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
MAYAGÃœEZ | 2023-04-02 11:40 | 2023-04-02 12:40 | 295 | 1:00 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEAS PRIMARIAS | M23040200137 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 60 | 2023-04-02 | 17700 | keep | 0 | Apr | 2023 | 0.012055 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
SAN JUAN | 2023-04-02 11:50 | 2023-04-02 11:52 | 1106 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 60% DE LA CARGA POR EL 1529-15 SE CERRO POR SCADA | S2304020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-02 | 2212 | keep | 0 | Apr | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-04-02 11:50 | 2023-04-02 11:52 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 60% DEL 1346-02 SE CERRO POR SCADA | S2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-02 | 3604 | keep | 0 | Apr | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2023-04-02 12:12 | 2023-04-03 10:11 | 30 | 21:59 | P | DESGANCHE | SE ABRIO EN C/L (RADIAL) PARA REALIZAR DESGANCHE/CERRAR PUENTE PRIMARIO ABIERTO | S23040200259 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1319 | 2023-04-02 | 39570 | keep | 0 | Apr | 2023 | 0.026951 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-02 12:12 | 2023-04-03 17:26 | 50 | 29:14 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE RETESO LINEA | S23040200260 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1754 | 2023-04-02 | 87700 | keep | 0 | Apr | 2023 | 0.059732 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-02 12:16 | 2023-04-02 15:17 | 1 | 3:01 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 20 EN CORTE DE LINEA LINEAS PRIMARIAS ARRIADAS | A23040200026 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 181 | 2023-04-02 | 181 | keep | 0 | Apr | 2023 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-02 12:25 | 2023-04-02 14:33 | 235 | 2:08 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL Y SE CERRO PUENTES | B23040200093 | New_Event | Primary Wire Break | Include | Include | Equipment | 128 | 2023-04-02 | 30080 | keep | 0 | Apr | 2023 | 0.020487 | 0.00016006 | Sustained | FALSE | FALSE | Not_TMED_Event | 235
BAYAMON | 2023-04-02 12:29 | 2023-04-02 12:47 | 10 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23040200052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-04-02 | 180 | keep | 0 | Apr | 2023 | 0.0001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-04-02 12:30 | 2023-04-02 12:45 | 6 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23040200025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-04-02 | 90 | keep | 0 | Apr | 2023 | 6.1299e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-02 13:06 | 2023-04-02 13:37 | 50 | 0:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23040200030 | New_Event | Cutout Failure | Include | Include | Equipment | 31 | 2023-04-02 | 1550 | keep | 0 | Apr | 2023 | 0.0010557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-02 13:29 | 2023-04-02 14:21 | 37 | 0:52 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23040200096 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-04-02 | 1924 | keep | 0 | Apr | 2023 | 0.0013104 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2023-04-02 13:43 | 2023-04-02 18:04 | 1 | 4:21 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN RISER 1 X 80 SMU-20 POR CONTAMINACION | B23040200100 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 261 | 2023-04-02 | 261 | keep | 0 | Apr | 2023 | 0.00017777 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-02 13:52 | 2023-04-02 15:40 | 20 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 30 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23040200151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-04-02 | 2160 | keep | 0 | Apr | 2023 | 0.0014712 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-02 14:39 | 2023-04-02 17:02 | 23 | 2:23 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23040200100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-04-02 | 3289 | keep | 0 | Apr | 2023 | 0.0022401 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-04-02 14:45 | 2023-04-02 19:59 | 40 | 5:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PARTIDA NO FUNDIO | B23040200107 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2023-04-02 | 12560 | keep | 0 | Apr | 2023 | 0.0085546 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-02 14:58 | 2023-04-02 17:42 | 8 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | A23040200036 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2023-04-02 | 1312 | keep | 0 | Apr | 2023 | 0.0008936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-04-02 15:45 | 2023-04-02 17:48 | 21 | 2:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23040200105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-04-02 | 2583 | keep | 0 | Apr | 2023 | 0.0017593 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-04-02 15:56 | 2023-04-02 17:24 | 100 | 1:28 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | S23040200670 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-04-02 | 8800 | keep | 0 | Apr | 2023 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-04-02 16:21 | 2023-04-02 17:57 | 10 | 1:36 | P | ANIMAL | 1 X 15 EN XMR CRUCE X LAGARTO | C23040200106 | New_Event | Animals | Include | Include | Wildlife | 96 | 2023-04-02 | 960 | keep | 0 | Apr | 2023 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-02 16:26 | 2023-04-02 18:34 | 386 | 2:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO TRAMO PARA REEMPLAZAR AISLADOR | S23040200686 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 128 | 2023-04-02 | 49408 | keep | 0 | Apr | 2023 | 0.033652 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
GUAYAMA | 2023-04-02 16:51 | 2023-04-02 17:34 | 80 | 0:43 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | P23040200072 | New_Event | Animals | Include | Include | Wildlife | 43 | 2023-04-02 | 3440 | keep | 0 | Apr | 2023 | 0.002343 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-02 16:58 | 2023-04-02 17:00 | 1106 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 60% DE SU CARGA POR EL 1529-15 SE CERRO POR SCADA | S2304020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-02 | 2212 | keep | 0 | Apr | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-04-02 16:58 | 2023-04-02 17:00 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 60% DEL 1346-02 SE CERRO POR SCADA | S2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-02 | 3604 | keep | 0 | Apr | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
MAYAGÃœEZ | 2023-04-02 17:12 | 2023-04-02 19:45 | 75 | 2:33 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23040200169 | New_Event | Primary Wire Break | Include | Include | Equipment | 153 | 2023-04-02 | 11475 | keep | 0 | Apr | 2023 | 0.0078156 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-04-02 17:12 | 2023-04-02 18:40 | 100 | 1:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23040200163 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 88 | 2023-04-02 | 8800 | keep | 0 | Apr | 2023 | 0.0059936 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-02 17:14 | 2023-04-03 14:47 | 12 | 21:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER SE REMPLAZO CAJA | S23040200720 | New_Event | Cutout Failure | Include | Include | Equipment | 1293 | 2023-04-02 | 15516 | keep | 0 | Apr | 2023 | 0.010568 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-02 17:24 | 2023-04-03 14:42 | 200 | 21:18 | P | ANIMAL | SE DESGANCHO Y SE RETIRO IGUANA SE REMPLAZO 2 CAJA 100AMP 3 X 100 EN RISER Y SE CERRO PUENTE | S23040200724 | New_Event | Animals | Include | Include | Wildlife | 1278 | 2023-04-02 | 255600 | keep | 0 | Apr | 2023 | 0.17409 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-04-02 18:00 | 2023-04-02 18:52 | 15 | 0:52 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23040200114 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-04-02 | 780 | keep | 0 | Apr | 2023 | 0.00053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-04-02 18:12 | 2023-04-02 18:13 | 725 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 725 | keep | 0 | Apr | 2023 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CAGUAS | 2023-04-02 18:14 | 2023-04-02 20:10 | 60 | 1:56 | P | ANIMAL | 1 X 50, 2 X 65 EN C/L Y 3 X 80 EN RISER CRUCE POR AVE | C23040200118 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-04-02 | 6960 | keep | 0 | Apr | 2023 | 0.0047404 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-04-02 18:25 | 2023-04-02 20:12 | 10 | 1:47 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23040200128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-04-02 | 1070 | keep | 0 | Apr | 2023 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-02 18:29 | 2023-04-02 20:58 | 40 | 2:29 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23040200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-04-02 | 5960 | keep | 0 | Apr | 2023 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-04-02 18:31 | 2023-04-02 20:10 | 30 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 25 EN CONVERTIDOR NO SE REPORTO CAUSA | A23040200048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-04-02 | 2970 | keep | 0 | Apr | 2023 | 0.0020229 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-02 18:34 | 2023-04-02 20:33 | 26 | 1:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO TRAMO Y SE REEMPLAZO AISLADOR SJ-230402-03 | S23040200762 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 119 | 2023-04-02 | 3094 | keep | 0 | Apr | 2023 | 0.0021073 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-02 18:42 | 2023-04-02 20:35 | 150 | 1:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | A23040200050 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 113 | 2023-04-02 | 16950 | keep | 0 | Apr | 2023 | 0.011545 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-02 18:57 | 2023-04-03 17:41 | 12 | 22:44 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA DESGANCHE | S23040200748 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1364 | 2023-04-02 | 16368 | keep | 0 | Apr | 2023 | 0.011148 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-02 19:41 | 2023-04-03 01:37 | 213 | 5:56 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONLIZO HACIA POSTE PARTIDO FUE REFERIDO A CONSTRUCCION 3 CLIENTES QUEDARON SIN SERVICIO | B23040200145 | New_Event | Primary Pole Failure | Include | Include | Equipment | 356 | 2023-04-02 | 75828 | keep | 0 | Apr | 2023 | 0.051646 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
PONCE | 2023-04-02 19:46 | 2023-04-03 08:27 | 12 | 12:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO EN XMR | P23040200086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 761 | 2023-04-02 | 9132 | keep | 0 | Apr | 2023 | 0.0062198 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-02 20:17 | 2023-04-03 10:22 | 180 | 14:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C23040200150 | New_Event | Cutout Failure | Include | Include | Equipment | 845 | 2023-04-02 | 152100 | keep | 0 | Apr | 2023 | 0.10359 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
CANOVANAS | 2023-04-02 20:41 | 2023-04-02 20:42 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23040200066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CAGUAS | 2023-04-02 20:58 | 2023-04-03 08:02 | 65 | 11:04 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA, CRUCE POR AVE. | C23040200152 | New_Event | Animals | Include | Include | Wildlife | 664 | 2023-04-02 | 43160 | keep | 0 | Apr | 2023 | 0.029396 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-04-02 21:18 | 2023-04-03 11:22 | 14 | 14:04 | P | DESGANCHE | SE REALIZO DESGANCHE 2 X 40 EN C/L | S23040200772 | New_Event | Vegetation Contact | Include | Include | Vegetation | 844 | 2023-04-02 | 11816 | keep | 0 | Apr | 2023 | 0.0080478 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-04-02 21:34 | 2023-04-02 21:35 | 2900 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23040200160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-02 | 2900 | keep | 0 | Apr | 2023 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
SAN JUAN | 2023-04-02 21:53 | 2023-04-02 23:44 | 4398 | 1:51 | T | CONDUCTOR ROTO O ABIERTO | SJ-230402-04 SE REPARO PUENTE DE LINEA A RISER Y SE INSTALO AISLADOR 20% EN SERVICIO | S23040200776 | New_Event | Primary Wire Break | Include | Include | Equipment | 111 | 2023-04-02 | 488178 | keep | 0 | Apr | 2023 | 0.3325 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2023-04-02 23:44 | 2023-04-03 00:56 | 3518 | 1:12 | P | CONDUCTOR ROTO O ABIERTO | SJ-230402-04 SE REPARO PUENTE DE LINEA A RISER Y SE INSTALO AISLADOR 100% EN SERVICIO | S23040200776 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 72 | 2023-04-02 | 253296 | keep | 0 | Apr | 2023 | 0.17252 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-03 01:37 | 2023-04-03 18:13 | 3 | 16:36 | P | CONDUCTOR ROTO O ABIERTO | SE INSTALO POSTE PRIMARIO, SE SUBIO CONDUCTOR Y SE CERRO PUENTE CON VOLTAJE SIN CARGA | B23040200145 | New_Event | Primary Wire Break | Include | Include | Equipment | 996 | 2023-04-03 | 2988 | keep | 0 | Apr | 2023 | 0.0020351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-04-03 01:55 | 2023-04-03 01:57 | 125 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2304030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-03 | 250 | keep | 0 | Apr | 2023 | 0.00017027 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
VEGA BAJA | 2023-04-03 02:46 | 2023-04-03 08:40 | 30 | 5:54 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23040300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2023-04-03 | 10620 | keep | 0 | Apr | 2023 | 0.0072332 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-04-03 04:11 | 2023-04-03 04:12 | 1394 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 2005-07 Y 2005-08 | R2304030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 1394 | keep | 0 | Apr | 2023 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2023-04-03 04:11 | 2023-04-03 04:12 | 424 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 2003-01 LLEVA 2005-07 Y 2005-08 | R2304030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-03 | 424 | keep | 0 | Apr | 2023 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
FAJARDO | 2023-04-03 04:11 | 2023-04-03 04:12 | 240 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 2003-01 LLEVA 2005-07 Y 2005-08 | R2304030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-03 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 0.00016346 | Momentary | FALSE | FALSE | Not_TMED_Event | 240
SAN JUAN | 2023-04-03 04:18 | 2023-04-03 04:19 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 75 % DEL 1203-03 | S2304030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 1225 | keep | 0 | Apr | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-04-03 04:18 | 2023-04-03 04:19 | 462 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL 75% POR 1203-01 | S2304030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-03 | 462 | keep | 0 | Apr | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
CANOVANAS | 2023-04-03 05:16 | 2023-04-03 09:17 | 35 | 4:01 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESPEJE DE LINEA | R23040300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2023-04-03 | 8435 | keep | 0 | Apr | 2023 | 0.005745 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-04-03 05:36 | 2023-04-03 07:39 | 10 | 2:03 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23040300003 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-04-03 | 1230 | keep | 0 | Apr | 2023 | 0.00083775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-03 05:52 | 2023-04-03 05:54 | 2092 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE BKR LLEVA 1619-02 LLEVA EL 42% DEL 1336-06 SE CERRO POR CONTROL | R2304030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-03 | 4184 | keep | 0 | Apr | 2023 | 0.0028497 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
ARECIBO | 2023-04-03 06:13 | 2023-04-03 10:45 | 1 | 4:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23040300003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2023-04-03 | 272 | keep | 0 | Apr | 2023 | 0.00018526 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-04-03 06:21 | 2023-04-03 07:57 | 87 | 1:36 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN C/L SE SECCIONALIZO POSTE PRIMARIO PARTIDO | R23040300012 | New_Event | Primary Pole Failure | Include | Include | Equipment | 96 | 2023-04-03 | 8352 | keep | 0 | Apr | 2023 | 0.0056885 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
BAYAMON | 2023-04-03 06:34 | 2023-04-03 09:39 | 70 | 3:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN C/L Y 1 X 50 EN C/L POR MAL TIEMPO VIENTO | B23040300002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 185 | 2023-04-03 | 12950 | keep | 0 | Apr | 2023 | 0.0088202 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-04-03 06:40 | 2023-04-03 10:36 | 21 | 3:56 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23040300004 | New_Event | Animals | Include | Include | Wildlife | 236 | 2023-04-03 | 4956 | keep | 0 | Apr | 2023 | 0.0033755 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CANOVANAS | 2023-04-03 06:53 | 2023-04-03 07:27 | 10 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTES SECUNDARIO | R23040200068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-04-03 | 340 | keep | 0 | Apr | 2023 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-03 07:04 | 2023-04-03 09:20 | 12 | 2:16 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | M23040300003 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 136 | 2023-04-03 | 1632 | keep | 0 | Apr | 2023 | 0.0011115 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-03 07:14 | 2023-04-03 15:24 | 8 | 8:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C23040300010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 490 | 2023-04-03 | 3920 | keep | 0 | Apr | 2023 | 0.0026699 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-03 07:49 | 2023-04-03 10:13 | 7 | 2:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | B23040300009 | New_Event | Primary Wire Break | Include | Include | Equipment | 144 | 2023-04-03 | 1008 | keep | 0 | Apr | 2023 | 0.00068654 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-03 07:57 | 2023-04-03 08:14 | 15 | 0:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR CONECTORES SECUNDARIOS | B23040300010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 17 | 2023-04-03 | 255 | keep | 0 | Apr | 2023 | 0.00017368 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-04-03 07:57 | 2023-04-03 14:55 | 10 | 6:58 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO PARTIDO | R23040300012 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 418 | 2023-04-03 | 4180 | keep | 0 | Apr | 2023 | 0.002847 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-03 08:01 | 2023-04-03 12:45 | 80 | 4:44 | P | NO SE REPORTO CAUSA | 2 X 65 EN RISER NO CAUSA | C23040300018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2023-04-03 | 22720 | keep | 0 | Apr | 2023 | 0.015474 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-03 08:06 | 2023-04-03 10:17 | 149 | 2:11 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | R23040300022 | New_Event | Animals | Include | Include | Wildlife | 131 | 2023-04-03 | 19519 | keep | 0 | Apr | 2023 | 0.013294 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
VEGA BAJA | 2023-04-03 08:08 | 2023-04-03 18:02 | 8 | 9:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A23040300027 | New_Event | Cutout Failure | Include | Include | Equipment | 594 | 2023-04-03 | 4752 | keep | 0 | Apr | 2023 | 0.0032366 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-03 08:29 | 2023-04-03 08:30 | 125 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2304030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 125 | keep | 0 | Apr | 2023 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2023-04-03 08:34 | 2023-04-03 13:15 | 2 | 4:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE LINEA A RISER | A23040300011 | New_Event | Primary Wire Break | Include | Include | Equipment | 281 | 2023-04-03 | 562 | keep | 0 | Apr | 2023 | 0.00038278 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-04-03 08:38 | 2023-04-03 09:28 | 3 | 0:50 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | P23040300015 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 50 | 2023-04-03 | 150 | keep | 0 | Apr | 2023 | 0.00010216 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-04-03 08:46 | 2023-04-03 15:49 | 17 | 7:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L PIN POLE TOP PARTIDO | B23040300015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 423 | 2023-04-03 | 7191 | keep | 0 | Apr | 2023 | 0.0048978 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-04-03 08:56 | 2023-04-03 21:34 | 10 | 12:38 | P | NO SE REPORTO CAUSA | 2 X 100 Y 1 X 100 EN CORTE DE LINEA NO CAUSA | S23040300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 758 | 2023-04-03 | 7580 | keep | 0 | Apr | 2023 | 0.0051627 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-03 09:05 | 2023-04-03 11:45 | 5 | 2:40 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23040300028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2023-04-03 | 800 | keep | 0 | Apr | 2023 | 0.00054488 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-04-03 09:42 | 2023-04-03 13:57 | 34 | 4:15 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO | C23040300040 | New_Event | Primary Wire Break | Include | Include | Equipment | 255 | 2023-04-03 | 8670 | keep | 0 | Apr | 2023 | 0.0059051 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
AGUADILLA | 2023-04-03 10:20 | 2023-04-03 11:50 | 10 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE Y SECUNDARIA | A23040300029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-04-03 | 900 | keep | 0 | Apr | 2023 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-03 10:22 | 2023-04-03 10:24 | 1106 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CERRO POR CONTROL | S2304030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-03 | 2212 | keep | 0 | Apr | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-04-03 10:22 | 2023-04-03 10:24 | 1802 | 0:02 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE CERRO POR CONTROL | S2304030000X | New_Event | Primary To Primary Contact | Include | Include | Equipment | 2 | 2023-04-03 | 3604 | keep | 0 | Apr | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
VEGA BAJA | 2023-04-03 10:46 | 2023-04-03 13:57 | 6 | 3:11 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | B23040300034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-04-03 | 1146 | keep | 0 | Apr | 2023 | 0.00078054 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-04-03 10:51 | 2023-04-03 11:40 | 1 | 0:49 | P | OTRAS CAUSAS | 1 X 20 EN TRANSFORMADOR FUSIBLE PODRIDO | A23040300040 | New_Event | Other Causes | Include | Include | Other | 49 | 2023-04-03 | 49 | keep | 0 | Apr | 2023 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-03 11:01 | 2023-04-03 12:48 | 9 | 1:47 | P | ANIMAL | 1 X 15 EN PROVICIONAL AEREO CRUCE POR AVE | B23040300072 | New_Event | Animals | Include | Include | Wildlife | 107 | 2023-04-03 | 963 | keep | 0 | Apr | 2023 | 0.00065589 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2023-04-03 11:01 | 2023-04-03 12:41 | 144 | 1:40 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23040300056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-04-03 | 14400 | keep | 0 | Apr | 2023 | 0.0098078 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2023-04-03 11:13 | 2023-04-03 19:00 | 10 | 7:47 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | S23040300060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 467 | 2023-04-03 | 4670 | keep | 0 | Apr | 2023 | 0.0031807 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-03 11:27 | 2023-04-03 15:38 | 1844 | 4:11 | P | ALIMENTADOR AMARRADO | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO MACHETE SERVICIO 60% POR 1529-15 | S23040300061 | New_Event | Feeder Load Transferred | Include | Include | Other | 251 | 2023-04-03 | 462844 | keep | 0 | Apr | 2023 | 0.31524 | 0.0012559 | Sustained | FALSE | FALSE | Not_TMED_Event | 1844
SAN JUAN | 2023-04-03 11:27 | 2023-04-03 12:22 | 1802 | 0:55 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE INTERRUPTOR 1529-15 LLEVA 60% DEL 1346-02 SE ABRIO AMARRE PARA SECCIONALIZAR ARBOL SOBRE LINEAS SWITCHING-FORM SJ-230403-01 | S23040300061 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 55 | 2023-04-03 | 99110 | keep | 0 | Apr | 2023 | 0.067503 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
CANOVANAS | 2023-04-03 11:43 | 2023-04-03 11:44 | 1613 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23040300042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 1613 | keep | 0 | Apr | 2023 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
AGUADILLA | 2023-04-03 12:10 | 2023-04-03 12:11 | 47 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23040300047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 47 | keep | 0 | Apr | 2023 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
AGUADILLA | 2023-04-03 12:15 | 2023-04-03 13:30 | 10 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23040300033 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-04-03 | 750 | keep | 0 | Apr | 2023 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-04-03 12:16 | 2023-04-04 12:24 | 8 | 24:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES EN LINEA SECUNDARIA QUEMADOS | R23040300045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1448 | 2023-04-03 | 11584 | keep | 0 | Apr | 2023 | 0.0078898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-03 12:30 | 2023-04-03 14:31 | 50 | 2:01 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C23040300068 | New_Event | Animals | Include | Include | Wildlife | 121 | 2023-04-03 | 6050 | keep | 0 | Apr | 2023 | 0.0041206 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-03 12:32 | 2023-04-03 12:48 | 1802 | 0:16 | T | CONDUCTOR ARRIADO O CRUZADO | SE VOLVIO A DISPARAR, SE RETIRARON VARIAS RAMAS A VARETA (DESDE EL SUELO) MEDIANTE SWITCHING FORM SJ-230403-01 PERO AUN ASI SE DISPARO NUEVAMENTE | S23040300061 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 16 | 2023-04-03 | 28832 | keep | 0 | Apr | 2023 | 0.019637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-03 12:37 | 2023-04-03 15:55 | 45 | 3:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M23040300055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 198 | 2023-04-03 | 8910 | keep | 0 | Apr | 2023 | 0.0060686 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
YAUCO | 2023-04-03 12:40 | 2023-04-03 12:55 | 1 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M23040300054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-04-03 | 15 | keep | 0 | Apr | 2023 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-03 12:42 | 2023-04-03 15:15 | 25 | 2:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23040300052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-04-03 | 3825 | keep | 0 | Apr | 2023 | 0.0026052 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-03 12:48 | 2023-04-03 15:38 | 901 | 2:50 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO MACHETE 100% EN SERVICIO LLEVA 60% DEL 1346-02 | S23040300061 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 170 | 2023-04-03 | 153170 | keep | 0 | Apr | 2023 | 0.10432 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-03 12:56 | 2023-04-03 18:45 | 107 | 5:49 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | P23040300065 | New_Event | Primary Wire Break | Include | Include | Equipment | 349 | 2023-04-03 | 37343 | keep | 0 | Apr | 2023 | 0.025434 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
BARRANQUITAS | 2023-04-03 13:01 | 2023-04-03 15:50 | 42 | 2:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REEMPLAZO AISLADOR ROTO | C23040300072 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 169 | 2023-04-03 | 7098 | keep | 0 | Apr | 2023 | 0.0048344 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2023-04-03 13:09 | 2023-04-03 16:20 | 1 | 3:11 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23040300088 | New_Event | Animals | Include | Include | Wildlife | 191 | 2023-04-03 | 191 | keep | 0 | Apr | 2023 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-03 13:19 | 2023-04-03 13:20 | 2720 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | A23040300060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 2720 | keep | 0 | Apr | 2023 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
AGUADILLA | 2023-04-03 13:24 | 2023-04-03 18:17 | 47 | 4:53 | T | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETES Y SE CERRO INTERRUPTOR | M23040300064 | New_Event | Switch Failure | Include | Include | Equipment | 293 | 2023-04-03 | 13771 | keep | 0 | Apr | 2023 | 0.0093794 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2023-04-03 13:28 | 2023-04-03 16:40 | 25 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | 2 X 30 EN C/L SE REEMPLAZO PUENTE PRIMARIO | B23040300092 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2023-04-03 | 4800 | keep | 0 | Apr | 2023 | 0.0032693 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-03 13:34 | 2023-04-03 21:13 | 10 | 7:39 | P | NO SE REPORTO CAUSA | 2 X 80 Y 1 X 65 EN CORTE DE LINEA NO CAUSA | S23040300124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 459 | 2023-04-03 | 4590 | keep | 0 | Apr | 2023 | 0.0031262 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-03 13:34 | 2023-04-03 17:16 | 70 | 3:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR FUERTE VIENTO | M23040300066 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 222 | 2023-04-03 | 15540 | keep | 0 | Apr | 2023 | 0.010584 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-04-03 13:44 | 2023-04-03 13:45 | 4027 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 4027 | keep | 0 | Apr | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-04-03 13:56 | 2023-04-03 19:09 | 50 | 5:13 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23040300094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2023-04-03 | 15650 | keep | 0 | Apr | 2023 | 0.010659 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-03 13:58 | 2023-04-03 17:50 | 291 | 3:52 | T | ARBOL SOBRE LINEA | DISPARO SE PATRULLO SE RETIRO ARBOL SOBRE LINEA Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S23040300135 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 232 | 2023-04-03 | 67512 | keep | 0 | Apr | 2023 | 0.045982 | 0.0001982 | Sustained | FALSE | FALSE | Not_TMED_Event | 291
VEGA BAJA | 2023-04-03 14:00 | 2023-04-03 15:24 | 80 | 1:24 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L SE RETIRO GUY CRUZADO EN LINEA PRIMARIA | B23040300103 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 84 | 2023-04-03 | 6720 | keep | 0 | Apr | 2023 | 0.004577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-03 14:20 | 2023-04-03 16:38 | 30 | 2:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONECTORES QUEMADOS | B23040300100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 138 | 2023-04-03 | 4140 | keep | 0 | Apr | 2023 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-03 14:48 | 2023-04-03 15:59 | 3871 | 1:11 | T | CAUSAS EXTERNAS | DISPARO DE BKR SE REALIZO DESGANCHE CON VARETA DESDE EL SUELO Y SE CERRO POR CONTROL 100% EN SERVICIO. PERSONAL AJENO A LUMA DEJO CAER RAMA SOBRE LA LINEA. SE CERRO POR CONTROL. | B23040300111 | New_Event | Damage From Public | Include | Include | Public | 71 | 2023-04-03 | 274841 | keep | 0 | Apr | 2023 | 0.18719 | 0.0026365 | Sustained | FALSE | FALSE | Not_TMED_Event | 3871
MAYAGÃœEZ | 2023-04-03 14:50 | 2023-04-03 15:15 | 20 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTES SECUNDARIOS | M23040300068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-04-03 | 500 | keep | 0 | Apr | 2023 | 0.00034055 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-03 14:51 | 2023-04-03 17:45 | 40 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER 1 X 10 EN XMR | S23040300167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2023-04-03 | 6960 | keep | 0 | Apr | 2023 | 0.0047404 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-04-03 15:00 | 2023-04-03 16:38 | 5 | 1:38 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE DESCRUZO LINEA SECUNDARIA EN POSTE DE METAL | C23040300082 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 98 | 2023-04-03 | 490 | keep | 0 | Apr | 2023 | 0.00033374 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-03 15:03 | 2023-04-03 19:44 | 110 | 4:41 | P | ARBOL SOBRE LINEA | 1 X 50 EN C/L SE RETIRO ARBOL SOBRE LA LINEA, SE LEVANTO CONDUCTOR DEL SUELO | B23040300118 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 281 | 2023-04-03 | 30910 | keep | 0 | Apr | 2023 | 0.021053 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
VEGA BAJA | 2023-04-03 15:05 | 2023-04-03 16:42 | 9 | 1:37 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23040300085 | New_Event | Animals | Include | Include | Wildlife | 97 | 2023-04-03 | 873 | keep | 0 | Apr | 2023 | 0.0005946 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-04-03 15:26 | 2023-04-03 18:30 | 150 | 3:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 2 X 100 1 X 30 Y 1 X 65 EN DISTINTOS CORTES DE LINEA POR LLUVIA Y VIENTO | M23040300084 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 184 | 2023-04-03 | 27600 | keep | 0 | Apr | 2023 | 0.018798 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-04-03 15:29 | 2023-04-03 18:45 | 70 | 3:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M23040300087 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 196 | 2023-04-03 | 13720 | keep | 0 | Apr | 2023 | 0.0093446 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-04-03 15:36 | 2023-04-03 17:11 | 167 | 1:35 | S | LINEA DE TRANSMISION 38KV | LINEA 4700 FUERA DE SERVICIO NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS | P23040300113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 95 | 2023-04-03 | 15865 | keep | 0 | Apr | 2023 | 0.010806 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
PONCE | 2023-04-03 15:36 | 2023-04-03 17:11 | 26 | 1:35 | S | LINEA DE TRANSMISION 38KV | LINEA 4700 FUERA DE SERVICIO NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS | P23040300113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 95 | 2023-04-03 | 2470 | keep | 0 | Apr | 2023 | 0.0016823 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
UTUADO | 2023-04-03 15:36 | 2023-04-03 17:57 | 3502 | 2:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS | A23040300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2023-04-03 | 493782 | keep | 0 | Apr | 2023 | 0.33631 | 0.0023852 | Sustained | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2023-04-03 15:36 | 2023-04-03 17:57 | 1241 | 2:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS | A23040300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2023-04-03 | 174981 | keep | 0 | Apr | 2023 | 0.11918 | 0.00084524 | Sustained | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2023-04-03 15:36 | 2023-04-03 17:57 | 650 | 2:21 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4700 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS | A23040300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 141 | 2023-04-03 | 91650 | keep | 0 | Apr | 2023 | 0.062422 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
MAYAGÃœEZ | 2023-04-03 15:39 | 2023-04-03 17:02 | 281 | 1:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS, LINEA 8100 DISPARA AL TRANSFERIR ADJUNTAS | M23040300096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 83 | 2023-04-03 | 23323 | keep | 0 | Apr | 2023 | 0.015885 | 0.00019139 | Sustained | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2023-04-03 15:39 | 2023-04-03 17:02 | 1252 | 1:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS, LINEA 8100 DISPARA AL TRANSFERIR ADJUNTAS | M23040300096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 83 | 2023-04-03 | 103916 | keep | 0 | Apr | 2023 | 0.070777 | 0.00085273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2023-04-03 15:39 | 2023-04-03 17:02 | 595 | 1:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS, LINEA 8100 DISPARA AL TRANSFERIR ADJUNTAS | M23040300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 83 | 2023-04-03 | 49385 | keep | 0 | Apr | 2023 | 0.033636 | 0.00040525 | Sustained | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2023-04-03 15:39 | 2023-04-03 17:02 | 51 | 1:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS, LINEA 8100 DISPARA AL TRANSFERIR ADJUNTAS | M23040300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 83 | 2023-04-03 | 4233 | keep | 0 | Apr | 2023 | 0.0028831 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2023-04-03 15:39 | 2023-04-03 17:02 | 721 | 1:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS, LINEA 8100 DISPARA AL TRANSFERIR ADJUNTAS | M23040300098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 83 | 2023-04-03 | 59843 | keep | 0 | Apr | 2023 | 0.040759 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2023-04-03 15:39 | 2023-04-03 17:02 | 1382 | 1:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS, LINEA 8100 DISPARA AL TRANSFERIR ADJUNTAS | A23040300137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 83 | 2023-04-03 | 114706 | keep | 0 | Apr | 2023 | 0.078126 | 0.00094127 | Sustained | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2023-04-03 15:39 | 2023-04-03 17:02 | 654 | 1:23 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 8100 NIDO CON PARTES METÃLICAS EN BARRA 38KV ADJUNTAS, LINEA 8100 DISPARA AL TRANSFERIR ADJUNTAS | A23040300137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 83 | 2023-04-03 | 54282 | keep | 0 | Apr | 2023 | 0.036971 | 0.00044544 | Sustained | FALSE | FALSE | Not_TMED_Event | 654
YAUCO | 2023-04-03 15:48 | 2023-04-03 15:49 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040300112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 179 | keep | 0 | Apr | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2023-04-03 15:55 | 2023-04-03 17:07 | 58 | 1:12 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA | P23040300099 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 72 | 2023-04-03 | 4176 | keep | 0 | Apr | 2023 | 0.0028443 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
BAYAMON | 2023-04-03 15:59 | 2023-04-03 17:04 | 1290 | 1:05 | P | CAUSAS EXTERNAS | SE ENCONTRO PUENTE ABIERTO Y MACHETE QUEMADO CERCA DE LA SALIDA DEL ALIMENTADOR | B23040300160 | Partial_restoration | Damage From Public | Include | Include | Public | 65 | 2023-04-03 | 83850 | keep | 0 | Apr | 2023 | 0.05711 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-03 16:02 | 2023-04-03 16:03 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040300120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 2067 | keep | 0 | Apr | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
BAYAMON | 2023-04-03 16:05 | 2023-04-04 01:42 | 149 | 9:37 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23040300204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 577 | 2023-04-03 | 85973 | keep | 0 | Apr | 2023 | 0.058556 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
SAN JUAN | 2023-04-03 16:09 | 2023-04-03 16:11 | 1106 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 60% POR 1529-15 | S23040300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-03 | 2212 | keep | 0 | Apr | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-04-03 16:09 | 2023-04-03 16:11 | 1802 | 0:02 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 60% DEL 1346-02 | S23040300000 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 2 | 2023-04-03 | 3604 | keep | 0 | Apr | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2023-04-03 16:10 | 2023-04-03 18:31 | 30 | 2:21 | P | DESGANCHE | 1 X 50 EN C/L Y 1 X 10 EN XMR DESGANCHE | B23040300146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-04-03 | 4230 | keep | 0 | Apr | 2023 | 0.002881 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-03 16:27 | 2023-04-03 16:28 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040300130 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 2067 | keep | 0 | Apr | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2023-04-03 16:33 | 2023-04-03 16:34 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040300133 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 2067 | keep | 0 | Apr | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
BARRANQUITAS | 2023-04-03 16:53 | 2023-04-03 18:17 | 66 | 1:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23040300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-04-03 | 5544 | keep | 0 | Apr | 2023 | 0.003776 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
CAGUAS | 2023-04-03 16:54 | 2023-04-03 18:37 | 6 | 1:43 | P | CAUSAS EXTERNAS | 2 X 10 EN TRANSFORMADOR CAMION PRIVADO DERRIBO TOMA SECUNDARIA | C23040300104 | New_Event | Damage From Public | Include | Include | Public | 103 | 2023-04-03 | 618 | keep | 0 | Apr | 2023 | 0.00042092 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-03 17:04 | 2023-04-03 17:05 | 3871 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE DE INTERRUPTOR | B2304030000X | Additional_clients | Damage From Public | Include | Include | Public | 1 | 2023-04-03 | 3871 | keep | 0 | Apr | 2023 | 0.0026365 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-03 17:05 | 2023-04-03 19:42 | 1290 | 2:37 | P | CAUSAS EXTERNAS | SE ENCONTRO PUENTE ABIERTO Y MACHETE QUEMADO | B23040300160 | 1st_after_momentary | Damage From Public | Include | Include | Public | 157 | 2023-04-03 | 202530 | keep | 0 | Apr | 2023 | 0.13794 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
MAYAGÃœEZ | 2023-04-03 17:30 | 2023-04-03 19:44 | 150 | 2:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA POR VIENTOS | M23040300149 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 134 | 2023-04-03 | 20100 | keep | 0 | Apr | 2023 | 0.01369 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-04-03 17:40 | 2023-04-04 08:02 | 20 | 14:22 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23040300205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 862 | 2023-04-03 | 17240 | keep | 0 | Apr | 2023 | 0.011742 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-03 18:00 | 2023-04-03 22:39 | 358 | 4:39 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN C/L Y 1 X100 EN C/L SE LEVANTO CONDUCTOR DEL SUELO | S23040300255 | New_Event | Primary Wire Break | Include | Include | Equipment | 279 | 2023-04-03 | 99882 | keep | 0 | Apr | 2023 | 0.068029 | 0.00024383 | Sustained | FALSE | FALSE | Not_TMED_Event | 358
AGUADILLA | 2023-04-03 18:04 | 2023-04-04 09:31 | 4 | 15:27 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE NECESITA DESGANCHE PRIMARIO | M23040300169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 927 | 2023-04-03 | 3708 | keep | 0 | Apr | 2023 | 0.0025255 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-04-03 18:11 | 2023-04-03 19:49 | 70 | 1:38 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTES DE LINEA | C23040300119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-04-03 | 6860 | keep | 0 | Apr | 2023 | 0.0046723 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-04-03 18:17 | 2023-04-03 21:41 | 20 | 3:24 | P | CRUCETA DEFECTUOSA O AVERIADA | REEMPLAZAR CRUZETAS Y RETEZAR LINEA PRIMARIA | M23040300176 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 204 | 2023-04-03 | 4080 | keep | 0 | Apr | 2023 | 0.0027789 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-04-03 18:54 | 2023-04-03 20:28 | 91 | 1:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE SAFADO HACIA CAJA | C23040300122 | New_Event | Primary Wire Break | Include | Include | Equipment | 94 | 2023-04-03 | 8554 | keep | 0 | Apr | 2023 | 0.0058261 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
CANOVANAS | 2023-04-03 19:00 | 2023-04-03 19:01 | 2092 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 1619-02 | R2304030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-03 | 2092 | keep | 0 | Apr | 2023 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
SAN JUAN | 2023-04-03 19:01 | 2023-04-04 09:39 | 20 | 14:38 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | S23040300265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 878 | 2023-04-03 | 17560 | keep | 0 | Apr | 2023 | 0.01196 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-03 19:13 | 2023-04-03 21:32 | 100 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA POR VIENTO | M23040300183 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-04-03 | 13900 | keep | 0 | Apr | 2023 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-04-03 19:19 | 2023-04-03 20:39 | 7 | 1:20 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A23040300164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-04-03 | 560 | keep | 0 | Apr | 2023 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-03 19:42 | 2023-04-03 19:45 | 3871 | 0:03 | T | CAUSAS EXTERNAS | SE ABRIO A PETICION DEL PERSONAL DE CAMPO PARA ABRIR MACHETES SOLDADOS E INCOMODOS Y SECCIONALIZAR LA AVERIA CERCA LA SALIDA DEL ALIMENTADOR. SE CERRO POR CONTROL 1% EN SERVICIO (40 CLIENTES) | B2304030000X | Additional_clients | Damage From Public | Include | Include | Public | 3 | 2023-04-03 | 11613 | keep | 0 | Apr | 2023 | 0.0079096 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-03 19:45 | 2023-04-03 22:51 | 3831 | 3:06 | P | CAUSAS EXTERNAS | SE REEMPLAZO PUENTE ABIERTO Y MACHETE QUEMADO Y SE ENERGIZO 100% EN SERVICIO | B23040300160 | 1st_after_momentary | Damage From Public | Include | Include | Public | 186 | 2023-04-03 | 712566 | keep | 0 | Apr | 2023 | 0.48533 | 0.0026093 | Sustained | FALSE | FALSE | Not_TMED_Event | 3831
VEGA BAJA | 2023-04-03 20:42 | 2023-04-04 08:46 | 8 | 12:04 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | B23040300404 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 724 | 2023-04-03 | 5792 | keep | 0 | Apr | 2023 | 0.0039449 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-03 22:23 | 2023-04-04 12:42 | 8 | 14:19 | P | TRANSFORMADOR AVERIADO | 2 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR BUSHING AVERIADO | S23040300082 | New_Event | Service Transformer Failure | Include | Include | Equipment | 859 | 2023-04-03 | 6872 | keep | 0 | Apr | 2023 | 0.0046805 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-04-03 22:59 | 2023-04-04 09:45 | 60 | 10:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040300202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 646 | 2023-04-03 | 38760 | keep | 0 | Apr | 2023 | 0.026399 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-04-04 00:58 | 2023-04-04 00:59 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23040400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 4381 | keep | 0 | Apr | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
GUAYAMA | 2023-04-04 01:11 | 2023-04-04 09:55 | 25 | 8:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | P23040400001 | New_Event | Primary Wire Break | Include | Include | Equipment | 524 | 2023-04-04 | 13100 | keep | 0 | Apr | 2023 | 0.0089224 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-04-04 05:50 | 2023-04-04 09:07 | 10 | 3:17 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | R23040400001 | New_Event | Animals | Include | Include | Wildlife | 197 | 2023-04-04 | 1970 | keep | 0 | Apr | 2023 | 0.0013418 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-04 06:15 | 2023-04-04 10:55 | 30 | 4:40 | P | DESGANCHE | 2 X 50 EN CL DESGANCHE | A23040400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-04-04 | 8400 | keep | 0 | Apr | 2023 | 0.0057212 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-04 06:38 | 2023-04-04 06:39 | 776 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23040400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 776 | keep | 0 | Apr | 2023 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
ARECIBO | 2023-04-04 06:52 | 2023-04-04 09:40 | 100 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER NO SE REPORTO CAUSA | A23040400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-04-04 | 16800 | keep | 0 | Apr | 2023 | 0.011442 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-04 07:18 | 2023-04-04 09:04 | 1 | 1:46 | P | ANIMAL | 1X10 EN BANCO DE XMRS CRUCE POR AVE | R23040400002 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-04-04 | 106 | keep | 0 | Apr | 2023 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-04 07:35 | 2023-04-04 13:04 | 47 | 5:29 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 40 EN CORTE DE LINEA SE LEVANTO POSTE Y LINEAS PRIMARIAS | P23040400004 | New_Event | Primary Pole Failure | Include | Include | Equipment | 329 | 2023-04-04 | 15463 | keep | 0 | Apr | 2023 | 0.010532 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
PONCE | 2023-04-04 08:10 | 2023-04-04 08:11 | 23 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040400007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 23 | keep | 0 | Apr | 2023 | 1.5665e-05 | 1.5665e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 23
HUMACAO | 2023-04-04 08:29 | 2023-04-04 13:08 | 80 | 4:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 Y 1 X 40 EN C/LS SE LEVANTO CONDUCTOR | C23040400009 | New_Event | Primary Wire Break | Include | Include | Equipment | 279 | 2023-04-04 | 22320 | keep | 0 | Apr | 2023 | 0.015202 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-04-04 08:48 | 2023-04-04 18:00 | 1 | 9:12 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 40 EN CL LINEA PRIMARIA ARIADA | P23040400015 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 552 | 2023-04-04 | 552 | keep | 0 | Apr | 2023 | 0.00037596 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-04 08:52 | 2023-04-04 10:25 | 5 | 1:33 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR CRUCE POR AVE | A23040400021 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-04-04 | 465 | keep | 0 | Apr | 2023 | 0.00031671 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-04 09:08 | 2023-04-04 11:48 | 1 | 2:40 | P | ANIMAL | 1 X 10 EN MONTURA XMR CRUCE POR AVE | B23040400044 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-04-04 | 160 | keep | 0 | Apr | 2023 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-04 09:22 | 2023-04-04 10:35 | 6 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA SE REPARAR SECUNDARIA | C23040400018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-04-04 | 438 | keep | 0 | Apr | 2023 | 0.00029832 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-04 09:27 | 2023-04-04 12:57 | 25 | 3:30 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23040400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-04-04 | 5250 | keep | 0 | Apr | 2023 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-04 09:53 | 2023-04-04 11:48 | 1 | 1:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23040400023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2023-04-04 | 115 | keep | 0 | Apr | 2023 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-04 09:57 | 2023-04-04 13:55 | 15 | 3:58 | P | CONDUCTOR ROTO O ABIERTO | SE FIJA BAJANTE DE LINEA PRIMARIA A CAJA EN TRANSFORMADOR | A23040400029 | New_Event | Primary Wire Break | Include | Include | Equipment | 238 | 2023-04-04 | 3570 | keep | 0 | Apr | 2023 | 0.0024315 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-04-04 09:58 | 2023-04-04 10:03 | 796 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-04 LLEVA 16% DEL 1336-06 SE CERRO POR CONTROL | S23040400036 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-04 | 3980 | keep | 0 | Apr | 2023 | 0.0027108 | 0.00054215 | Momentary | FALSE | FALSE | Not_TMED_Event | 796
CANOVANAS | 2023-04-04 09:58 | 2023-04-04 10:03 | 172 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVA 16% DEL 1336-06 SE CERRO POR CONTROL | S23040400036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-04 | 860 | keep | 0 | Apr | 2023 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2023-04-04 10:33 | 2023-04-04 14:15 | 1 | 3:42 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGACHE | M23040400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-04-04 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-04 10:34 | 2023-04-04 12:30 | 200 | 1:56 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M23040400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 116 | 2023-04-04 | 23200 | keep | 0 | Apr | 2023 | 0.015801 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-04 10:40 | 2023-04-04 10:41 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE 9202-03 | B23040400036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 308 | keep | 0 | Apr | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-04-04 10:40 | 2023-04-04 10:41 | 698 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9202-02 LLEVANDO PARTE 9202-03 | B23040400036 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 698 | keep | 0 | Apr | 2023 | 0.0004754 | 0.0004754 | Momentary | FALSE | FALSE | Not_TMED_Event | 698
MAYAGÃœEZ | 2023-04-04 10:41 | 2023-04-04 16:01 | 20 | 5:20 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA POR LINEA CRUZADA | M23040400042 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 320 | 2023-04-04 | 6400 | keep | 0 | Apr | 2023 | 0.004359 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-04 11:11 | 2023-04-04 13:57 | 100 | 2:46 | P | DESGANCHE | 1 X 80 EN C/L | C23040400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-04-04 | 16600 | keep | 0 | Apr | 2023 | 0.011306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-04-04 11:13 | 2023-04-04 11:50 | 10 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR MONTURA PARA REPARAR SECUNDARIA | P23040400038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-04-04 | 370 | keep | 0 | Apr | 2023 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-04 11:14 | 2023-04-04 13:36 | 69 | 2:22 | P | ANIMAL | 1 X 50 Y 1 X 40 EN C/L CRUCE POR AVE SE REALIZO COORDINACION DE FUSIBLES | B23040400043 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-04-04 | 9798 | keep | 0 | Apr | 2023 | 0.0066734 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2023-04-04 11:23 | 2023-04-04 16:24 | 13 | 5:01 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU-2 SE SECCIONALIZO AVERIA SOTERRADA QUEDA T-8 SIN SERVICIO | B23040400046 | New_Event | UG Cable Fault | Include | Include | Equipment | 301 | 2023-04-04 | 3913 | keep | 0 | Apr | 2023 | 0.0026651 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2023-04-04 11:26 | 2023-04-04 13:09 | 4 | 1:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA | C23040400041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 103 | 2023-04-04 | 412 | keep | 0 | Apr | 2023 | 0.00028061 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-04-04 11:28 | 2023-04-05 13:34 | 10 | 26:06 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO Y TAMBIEN SE DIERON CONECTORES EN NEUTRAL DEL SISTEMA | C23040400146 | New_Event | Primary Wire Break | Include | Include | Equipment | 1566 | 2023-04-04 | 15660 | keep | 0 | Apr | 2023 | 0.010666 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-04 11:31 | 2023-04-04 11:32 | 3701 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040400046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 3701 | keep | 0 | Apr | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
ARECIBO | 2023-04-04 11:47 | 2023-04-04 11:56 | 1 | 0:09 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER NO SE ENCONTRO CAUSA | A23040400042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-04-04 | 9 | keep | 0 | Apr | 2023 | 6.1299e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-04 11:50 | 2023-04-04 15:14 | 3 | 3:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 3 X 50 EN CORTE DE LINEA Y SE REEMPLAZO AISLA | M23040400048 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 204 | 2023-04-04 | 612 | keep | 0 | Apr | 2023 | 0.00041683 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-04-04 11:54 | 2023-04-04 13:26 | 7 | 1:32 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR TRAMO SECUNDARIO Y REALIZAR DESGANCHE SECUNDARIO | C23040400053 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 92 | 2023-04-04 | 644 | keep | 0 | Apr | 2023 | 0.00043863 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-04-04 11:56 | 2023-04-04 13:55 | 60 | 1:59 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESPEJE DE LINEA | S23040400091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-04-04 | 7140 | keep | 0 | Apr | 2023 | 0.004863 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-04-04 11:58 | 2023-04-04 15:35 | 55 | 3:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23040400043 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 217 | 2023-04-04 | 11935 | keep | 0 | Apr | 2023 | 0.0081289 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BARRANQUITAS | 2023-04-04 12:11 | 2023-04-04 16:40 | 35 | 4:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L LEVANTO CONDUCTOR | C23040400058 | New_Event | Primary Wire Break | Include | Include | Equipment | 269 | 2023-04-04 | 9415 | keep | 0 | Apr | 2023 | 0.0064125 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
ARECIBO | 2023-04-04 12:15 | 2023-04-04 14:25 | 20 | 2:10 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEA | A23040400044 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 130 | 2023-04-04 | 2600 | keep | 0 | Apr | 2023 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-04 12:32 | 2023-04-04 12:33 | 1452 | 0:01 | T | DESGANCHE | RECERRO | S23040400000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-04 | 1452 | keep | 0 | Apr | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
ARECIBO | 2023-04-04 12:32 | 2023-04-04 17:40 | 100 | 5:08 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | A23040400046 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 308 | 2023-04-04 | 30800 | keep | 0 | Apr | 2023 | 0.020978 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-04 12:33 | 2023-04-04 15:35 | 7 | 3:02 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | S23040400113 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-04-04 | 1274 | keep | 0 | Apr | 2023 | 0.00086772 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-04 12:37 | 2023-04-04 13:57 | 2 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONEXIONES SECUNDARIAS | S23040400099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-04-04 | 160 | keep | 0 | Apr | 2023 | 0.00010898 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-04 12:38 | 2023-04-04 15:02 | 135 | 2:24 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L VEHICULO IMPACTO POSTE Y CRUZO LAS LINEAS | B23040400058 | New_Event | Damage From Public | Include | Include | Public | 144 | 2023-04-04 | 19440 | keep | 0 | Apr | 2023 | 0.01324 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-04-04 12:39 | 2023-04-04 12:41 | 1106 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO 60% 1529-15 | S23040400000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-04 | 2212 | keep | 0 | Apr | 2023 | 0.0015066 | 0.00075329 | Momentary | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-04-04 12:39 | 2023-04-04 12:41 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 60% DEL 1346-02 | S23040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-04 | 3604 | keep | 0 | Apr | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
AGUADILLA | 2023-04-04 12:44 | 2023-04-04 18:35 | 80 | 5:51 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | M23040400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 351 | 2023-04-04 | 28080 | keep | 0 | Apr | 2023 | 0.019125 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-04 12:49 | 2023-04-04 14:30 | 9 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR SE REMPLAZO BARRA PEDESTAL | S23040400112 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2023-04-04 | 909 | keep | 0 | Apr | 2023 | 0.00061912 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-04-04 12:50 | 2023-04-04 12:51 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 931 CLIENTES DEL 2402-02 | R23040400019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-04 12:50 | 2023-04-04 12:51 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 2302-03 | R23040400019 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 931 | keep | 0 | Apr | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
BARRANQUITAS | 2023-04-04 12:57 | 2023-04-04 16:10 | 12 | 3:13 | P | TRANSFORMADOR AVERIADO | REEMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C23040400067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 193 | 2023-04-04 | 2316 | keep | 0 | Apr | 2023 | 0.0015774 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-04-04 12:58 | 2023-04-04 13:15 | 4 | 0:17 | P | CONDUCTOR ROTO O ABIERTO | SE ABREN CAJAS EN TRANSFORMADOR PARA REMPLAZAR BAJANTE PRIMARIO | A23040400052 | New_Event | Primary Wire Break | Include | Include | Equipment | 17 | 2023-04-04 | 68 | keep | 0 | Apr | 2023 | 4.6314e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-04-04 12:59 | 2023-04-04 15:22 | 9 | 2:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONDUCTOR SECUNDARIO | B23040400060 | New_Event | Secondary Wire Break | Include | Include | Equipment | 143 | 2023-04-04 | 1287 | keep | 0 | Apr | 2023 | 0.00087657 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2023-04-04 13:08 | 2023-04-04 17:30 | 50 | 4:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23040400054 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 262 | 2023-04-04 | 13100 | keep | 0 | Apr | 2023 | 0.0089224 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-04-04 13:14 | 2023-04-04 14:50 | 5 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BARRAS QUEMADAS EN PEDESTAL SECUNDARIO | R23040400021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-04-04 | 480 | keep | 0 | Apr | 2023 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-04-04 13:17 | 2023-04-04 15:02 | 1106 | 1:45 | P | ALIMENTADOR AMARRADO | DISPARO 1529-15 SE ENCONTRO SPACEADORES DEL 1526-1 Y 5 AVERIADO CUANDO DABA VIENTO CRUZABA FASE EL 1529-15 SE ABRIO N/O SE PASO 60% DEL 1346-2 A SU BKR. | S23040400128 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 105 | 2023-04-04 | 116130 | keep | 0 | Apr | 2023 | 0.079096 | 0.00075329 | Sustained | FALSE | FALSE | Not_TMED_Event | 1106
SAN JUAN | 2023-04-04 13:17 | 2023-04-04 15:08 | 1802 | 1:51 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO 1529-15 SE ENCONTRO SPACEADORES DEL 1526-1 Y 5 AVERIADO CUANDO DABA VIENTO CRUZABA FASE EL 1529-15 SE ABRIO N/O SE PASO 60% DEL 1346-2 A SU BKR. Y SE CERRO INTERRUPTOR 100% EN SERVICIO | S23040400128 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 111 | 2023-04-04 | 200022 | keep | 0 | Apr | 2023 | 0.13623 | 0.0012273 | Sustained | FALSE | FALSE | Not_TMED_Event | 1802
BAYAMON | 2023-04-04 13:30 | 2023-04-04 17:28 | 18 | 3:58 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA TRANSFERIR LINEAS SECUNDARIA A POSTE EXISTENTE | B23040400064 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 238 | 2023-04-04 | 4284 | keep | 0 | Apr | 2023 | 0.0029178 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-04-04 13:46 | 2023-04-04 16:41 | 100 | 2:55 | P | DESGANCHE | 1 X 100 EN C/L | C23040400076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-04-04 | 17500 | keep | 0 | Apr | 2023 | 0.011919 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-04 14:01 | 2023-04-04 19:20 | 10 | 5:19 | P | CRUCETA DEFECTUOSA O AVERIADA | 3 X 10 EN TRANSFORMADOR SE ABRE MONTURA TRIFASICA Y SE REEMPLAZA CRUCETA PRIMARIA | M23040400079 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 319 | 2023-04-04 | 3190 | keep | 0 | Apr | 2023 | 0.0021727 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-04 14:05 | 2023-04-04 16:27 | 10 | 2:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR Y SE CERRO PUENTE DE LINEA A CAJA | B23040400067 | New_Event | Primary Wire Break | Include | Include | Equipment | 142 | 2023-04-04 | 1420 | keep | 0 | Apr | 2023 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-04 14:07 | 2023-04-04 14:08 | 1284 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2304040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 1284 | keep | 0 | Apr | 2023 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
MAYAGÃœEZ | 2023-04-04 14:18 | 2023-04-04 17:41 | 80 | 3:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CL SE REMPLAZO CAJA PRIMARIA | M23040400074 | New_Event | Cutout Failure | Include | Include | Equipment | 203 | 2023-04-04 | 16240 | keep | 0 | Apr | 2023 | 0.011061 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-04-04 14:18 | 2023-04-04 18:10 | 125 | 3:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR VIENTOS | M23040400075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 232 | 2023-04-04 | 29000 | keep | 0 | Apr | 2023 | 0.019752 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2023-04-04 14:26 | 2023-04-04 16:25 | 40 | 1:59 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23040400064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-04-04 | 4760 | keep | 0 | Apr | 2023 | 0.003242 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-04-04 14:29 | 2023-04-04 14:33 | 3296 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23040400080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-04 | 13184 | keep | 0 | Apr | 2023 | 0.0089796 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
PONCE | 2023-04-04 14:34 | 2023-04-04 16:10 | 25 | 1:36 | P | ANIMAL | 1 X 65 EN CL CRUCE DE FASE PRIMARIA POR IGUANA | P23040400065 | New_Event | Animals | Include | Include | Wildlife | 96 | 2023-04-04 | 2400 | keep | 0 | Apr | 2023 | 0.0016346 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-04 14:37 | 2023-04-05 14:25 | 15 | 23:48 | P | DESGANCHE | SE REMPLAZO CRUZETA Y DESGANCHE 1 X 50 EN C/L | C23040400081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1428 | 2023-04-04 | 21420 | keep | 0 | Apr | 2023 | 0.014589 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-04-04 14:43 | 2023-04-04 16:18 | 14 | 1:35 | P | ANIMAL | 1 X 50 EN CL 1 X 100 CL CRUCE DE FASE PRIMARIAS POR AVE | P23040400066 | New_Event | Animals | Include | Include | Wildlife | 95 | 2023-04-04 | 1330 | keep | 0 | Apr | 2023 | 0.00090586 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2023-04-04 14:49 | 2023-04-04 17:58 | 12 | 3:09 | P | EXCAVACIONES | 1 X 18 NX REALIZAN EXCAVACION Y CRUZAN TOMAS SOTERRADAS | P23040400068 | New_Event | Excavation | Include | Include | Public | 189 | 2023-04-04 | 2268 | keep | 0 | Apr | 2023 | 0.0015447 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-04-04 14:53 | 2023-04-04 18:09 | 15 | 3:16 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | P23040400070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-04-04 | 2940 | keep | 0 | Apr | 2023 | 0.0020024 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-04-04 14:54 | 2023-04-04 16:55 | 25 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23040400060 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-04-04 | 3025 | keep | 0 | Apr | 2023 | 0.0020603 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-04-04 15:08 | 2023-04-04 15:16 | 3 | 0:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA NEUTRAL SECUNDARIA | R23040400028 | New_Event | Secondary Wire Break | Include | Include | Equipment | 8 | 2023-04-04 | 24 | keep | 0 | Apr | 2023 | 1.6346e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-04-04 15:14 | 2023-04-04 15:40 | 1923 | 0:26 | T | ARBOL SOBRE LINEA | AVERIA DE ARBOL SOBRE LINEA Y CONDUCTOR ROTO. SE REALIZA PRUEBA EN EL CAMPO YA QUE NO CERRO POR CONTROL Y AL PROBAR MALO NO ABRIO POR CAPACITOR TRIP AVERIADO PASANDO AVERIA A LOS FUSIBLES DE ALTA DEL TRANSFORMADOR | A23040400065 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 26 | 2023-04-04 | 49998 | keep | 0 | Apr | 2023 | 0.034053 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
HUMACAO | 2023-04-04 15:16 | 2023-04-04 16:38 | 34 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOPR Y SE REEMPLAZO BAJANTES SECUNDARIOS Y BAJO TAP DEL 4 @ 3 QUEDO EN 125/250V | C23040400090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-04-04 | 2788 | keep | 0 | Apr | 2023 | 0.0018989 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2023-04-04 15:22 | 2023-04-04 17:26 | 30 | 2:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23040400177 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2023-04-04 | 3720 | keep | 0 | Apr | 2023 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-04 15:23 | 2023-04-04 15:24 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO PARTE DE LA CARGA DEL 2402-02 | R23040400029 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-04 15:23 | 2023-04-04 15:24 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE PARTE DE LA CARGA POR EL 2302-03 | R23040400029 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 931 | keep | 0 | Apr | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
CAGUAS | 2023-04-04 15:28 | 2023-04-04 17:14 | 6 | 1:46 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | ABRIO XMR PARA REPARAR SECUNDARIA CRUZADA | C23040400094 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 106 | 2023-04-04 | 636 | keep | 0 | Apr | 2023 | 0.00043318 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-04 15:40 | 2023-04-05 22:10 | 2231 | 30:30 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | INFORMA LEONARDO MODESTO QUE SE ENERGIZO PORTATIL #3, SE LE INSTALO CAPACITOR TRIP DEVICE A INTERRUPTORES 8401-02 Y 8401-04. LA CARGA DEL INTERRUPTOR 8401-01 SE PASO AL 8401-02 Y LA CARGA DEL 8401-03 SE PASO AL 8401-04. | A23040400110 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1830 | 2023-04-04 | 4082730 | keep | 0 | Apr | 2023 | 2.7807 | 0.0015195 | Sustained | FALSE | FALSE | Not_TMED_Event | 2231
VEGA BAJA | 2023-04-04 15:40 | 2023-04-05 22:10 | 1923 | 30:30 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | INFORMA LEONARDO MODESTO QUE SE ENERGIZO PORTATIL #3, SE LE INSTALO CAPACITOR TRIP DEVICE A INTERRUPTORES 8401-02 Y 8401-04. LA CARGA DEL 8401-01 SE PASO AL 8401-02 SE CORRIGIO AVERIA EN 8401-02 Y SE ENERGIZO | A23040400110 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1830 | 2023-04-04 | 3519090 | keep | 0 | Apr | 2023 | 2.3968 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-04-04 15:40 | 2023-04-05 22:10 | 1066 | 30:30 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | INFORMA LEONARDO MODESTO QUE SE ENERGIZO PORTATIL #3, SE LE INSTALO CAPACITOR TRIP DEVICE A INTERRUPTORES 8401-02 Y 8401-04. LA CARGA DEL INTERRUPTOR 8401-01 SE PASO AL 8401-02 Y LA CARGA DEL 8401-03 SE PASO AL 8401-04. | A23040400110 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1830 | 2023-04-04 | 1950780 | keep | 0 | Apr | 2023 | 1.3287 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
VEGA BAJA | 2023-04-04 15:40 | 2023-04-05 22:10 | 141 | 30:30 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | INFORMA LEONARDO MODESTO QUE SE ENERGIZO PORTATIL #3, SE LE INSTALO CAPACITOR TRIP DEVICE A INTERRUPTORES 8401-02 Y 8401-04. LA CARGA DEL INTERRUPTOR 8401-01 SE PASO AL 8401-02 Y LA CARGA DEL 8401-03 SE PASO AL 8401-04. | A23040400110 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1830 | 2023-04-04 | 258030 | keep | 0 | Apr | 2023 | 0.17574 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
VEGA BAJA | 2023-04-04 15:40 | 2023-04-04 15:42 | 2107 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-14700 EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-04 | 4214 | keep | 0 | Apr | 2023 | 0.0028701 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-04-04 15:40 | 2023-04-04 15:42 | 308 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-14700 EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-04 | 616 | keep | 0 | Apr | 2023 | 0.00041955 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-04-04 15:40 | 2023-04-04 15:42 | 2697 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-14700 EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-04 | 5394 | keep | 0 | Apr | 2023 | 0.0036738 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-04-04 15:40 | 2023-04-04 15:42 | 67 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-14700 EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-04 | 134 | keep | 0 | Apr | 2023 | 9.1267e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2023-04-04 15:41 | 2023-04-04 15:44 | 2777 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-2200 DE MANATI A BARCELONETA EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-04 | 8331 | keep | 0 | Apr | 2023 | 0.0056742 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2023-04-04 15:41 | 2023-04-04 15:52 | 2 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO L-2200 DE MANATI A BARCELONETA EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-04-04 | 22 | keep | 0 | Apr | 2023 | 1.4984e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-04-04 15:41 | 2023-04-04 15:44 | 2839 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-2200 DE MANATI A BARCELONETA EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-04 | 8517 | keep | 0 | Apr | 2023 | 0.0058009 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
VEGA BAJA | 2023-04-04 15:41 | 2023-04-04 15:44 | 1160 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-2200 DE MANATI A BARCELONETA EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-04 | 3480 | keep | 0 | Apr | 2023 | 0.0023702 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
VEGA BAJA | 2023-04-04 15:41 | 2023-04-04 15:44 | 1860 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO L-2200 DE MANATI A BARCELONETA EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-04 | 5580 | keep | 0 | Apr | 2023 | 0.0038005 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2023-04-04 15:42 | 2023-04-04 15:44 | 1879 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO L-2200 DE MANATI A BARCELONETA EN BACK UP DEBIDO A AVERIA EN SUBESTACION 8401-00 Y FUSIBLES DE 38KV | A23040400101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-04 | 3758 | keep | 0 | Apr | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
YAUCO | 2023-04-04 15:46 | 2023-04-04 17:46 | 50 | 2:00 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23040400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-04-04 | 6000 | keep | 0 | Apr | 2023 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-04 15:54 | 2023-04-04 18:32 | 50 | 2:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | S23040400180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-04-04 | 7900 | keep | 0 | Apr | 2023 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-04 15:54 | 2023-04-04 15:55 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO PARTE DE LA CARGA DEL 2402-02 | R23040400032 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-04 15:54 | 2023-04-04 15:55 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE PARTE DE LA CARGA POR EL 2302-03 | R23040400032 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 931 | keep | 0 | Apr | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
BAYAMON | 2023-04-04 16:08 | 2023-04-04 18:46 | 755 | 2:38 | P | DESGANCHE | 1 X 100 EN C/L DESGANCJE | B23040400091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-04-04 | 119290 | keep | 0 | Apr | 2023 | 0.081248 | 0.00051423 | Sustained | FALSE | FALSE | Not_TMED_Event | 755
BAYAMON | 2023-04-04 16:15 | 2023-04-05 12:09 | 3 | 19:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 RBA EN SU 4 Y 1 X 25 EN SU 3 LLUVIA FUERTE | B23040400092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1194 | 2023-04-04 | 3582 | keep | 0 | Apr | 2023 | 0.0024397 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-04 16:17 | 2023-04-05 12:58 | 18 | 20:41 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE REPARO PUENTE PRIMARIO DE CAJA A XMR 1 X 15 EN TRANSFORMADOR | B23040400094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1241 | 2023-04-04 | 22338 | keep | 0 | Apr | 2023 | 0.015214 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-04-04 16:21 | 2023-04-04 18:30 | 60 | 2:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23040400122 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 129 | 2023-04-04 | 7740 | keep | 0 | Apr | 2023 | 0.0052717 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-04 16:24 | 2023-04-04 18:43 | 8 | 2:19 | P | CABLE SOTERRADO AVERIADO | SE ENERGIZO CERRANDO DE SU-2 A T-8 Y SE DEJO SECCIONALIZADA AVERIA DEL T-7 AL T-8 | B23040400046 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 139 | 2023-04-04 | 1112 | keep | 0 | Apr | 2023 | 0.00075738 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-04-04 16:30 | 2023-04-04 17:47 | 19 | 1:17 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA CRUCE CON AVE | R23040400035 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-04-04 | 1463 | keep | 0 | Apr | 2023 | 0.00099644 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2023-04-04 16:45 | 2023-04-04 19:08 | 100 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA POR VIENTOS | M23040400110 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2023-04-04 | 14300 | keep | 0 | Apr | 2023 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-04-04 16:49 | 2023-04-04 17:10 | 4 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C23040400105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-04-04 | 84 | keep | 0 | Apr | 2023 | 5.7212e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-04-04 17:01 | 2023-04-04 20:10 | 1417 | 3:09 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SIN RTU INFORMAN POR FUERTES VIENTOS | M23040400131 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2023-04-04 | 267813 | keep | 0 | Apr | 2023 | 0.18241 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
BARRANQUITAS | 2023-04-04 17:02 | 2023-04-04 18:46 | 1 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | C23040400107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-04-04 | 104 | keep | 0 | Apr | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-04 17:03 | 2023-04-04 18:10 | 3 | 1:07 | P | ANIMAL | 1 X 10 EN RISER POR AVE | M23040400117 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-04-04 | 201 | keep | 0 | Apr | 2023 | 0.0001369 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-04 17:09 | 2023-04-04 17:10 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO PARTE DE LA CARGA DEL 2402-02 | R23040400038 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-04 17:09 | 2023-04-04 17:10 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE PARTE DE LA CARGA POR EL 2302-03 | R23040400038 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 931 | keep | 0 | Apr | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
CANOVANAS | 2023-04-04 18:07 | 2023-04-04 19:52 | 54 | 1:45 | P | PROBLEMA DEL CLIENTE | 2 X 80 Y 2 X 65 EN CORTES DE LINEA PROBLEMA INTERIOR EN BOMBAS AAA | R23040400039 | New_Event | Customer-Related Interruption | Include | Include | Public | 105 | 2023-04-04 | 5670 | keep | 0 | Apr | 2023 | 0.0038618 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
ARECIBO | 2023-04-04 18:07 | 2023-04-04 20:59 | 10 | 2:52 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR POR SECUNDARIA CRUZADA POR ARBOL | M23040400147 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 172 | 2023-04-04 | 1720 | keep | 0 | Apr | 2023 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-04 18:10 | 2023-04-04 18:13 | 1356 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23040400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-04 | 4068 | keep | 0 | Apr | 2023 | 0.0027707 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
SAN JUAN | 2023-04-04 18:43 | 2023-04-05 01:35 | 100 | 6:52 | P | DESGANCHE | 1 X 80 Y 1 X 100 EN C/L DESGANCHE | S23040400213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2023-04-04 | 41200 | keep | 0 | Apr | 2023 | 0.028061 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-04 18:44 | 2023-04-05 15:48 | 100 | 21:04 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23040400053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1264 | 2023-04-04 | 126400 | keep | 0 | Apr | 2023 | 0.08609 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-04-04 18:48 | 2023-04-05 11:09 | 100 | 16:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIAS | C23040400115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 981 | 2023-04-04 | 98100 | keep | 0 | Apr | 2023 | 0.066815 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-04 18:49 | 2023-04-04 18:50 | 2708 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE LLEVANDO LA CARGA DEL 2302-02 | R23040400050 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 2708 | keep | 0 | Apr | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-04-04 18:49 | 2023-04-04 18:50 | 2524 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE CARGA POR EL 2302-01 | R23040400050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 2524 | keep | 0 | Apr | 2023 | 0.0017191 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2023-04-04 18:50 | 2023-04-05 00:15 | 40 | 5:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTO | R23040400071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 325 | 2023-04-04 | 13000 | keep | 0 | Apr | 2023 | 0.0088542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-04 18:54 | 2023-04-04 18:55 | 3046 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE LLEVANDO LA CARGA DEL 1647-10 | R23040400057 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-04-04 | 3046 | keep | 0 | Apr | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-04-04 18:54 | 2023-04-04 18:55 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE CARGA POR EL 1646-03 | R23040400057 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 61 | keep | 0 | Apr | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-04-04 18:55 | 2023-04-04 21:01 | 125 | 2:06 | P | TERMINACION SOTERRADA AVERIADA | 1 X 25 EN RISER Y 1 X 65 EN CORTE DE LINEA SE REEMPLAZO TERMINACION QUEMADA | R23040400059 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 126 | 2023-04-04 | 15750 | keep | 0 | Apr | 2023 | 0.010727 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2023-04-04 19:16 | 2023-04-05 09:10 | 100 | 13:54 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M23040400161 | New_Event | Primary Wire Break | Include | Include | Equipment | 834 | 2023-04-04 | 83400 | keep | 0 | Apr | 2023 | 0.056803 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-04 19:20 | 2023-04-04 22:50 | 133 | 3:30 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE DEJO TRAMO SECCIONALIZADO PARA PERSONAL DE DESGANCHE LO TRABAJE MAÃ‘ANA | R23040400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-04-04 | 27930 | keep | 0 | Apr | 2023 | 0.019023 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
AGUADILLA | 2023-04-04 19:34 | 2023-04-05 16:24 | 154 | 20:50 | S | POWER TRANSFORMER AVERIADO | SE INSTALA SUBESTACION PORTATIL 5 DEBIDO A TRANSFORMADOR DE SUBESTACION 7201-00 AVERIADO | M23040400219 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1250 | 2023-04-04 | 192500 | keep | 0 | Apr | 2023 | 0.13111 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2023-04-04 19:34 | 2023-04-05 16:24 | 1261 | 20:50 | S | POWER TRANSFORMER AVERIADO | SE INSTALA SUBESTACION PORTATIL 5 DEBIDO A TRANSFORMADOR DE SUBESTACION 7201-00 AVERIADO | M23040400219 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1250 | 2023-04-04 | 1576250 | keep | 0 | Apr | 2023 | 1.0736 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2023-04-04 19:34 | 2023-04-05 16:24 | 3894 | 20:50 | S | POWER TRANSFORMER AVERIADO | SE INSTALA SUBESTACION PORTATIL 5 DEBIDO A TRANSFORMADOR DE SUBESTACION 7201-00 AVERIADO | M23040400219 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1250 | 2023-04-04 | 4867500 | keep | 0 | Apr | 2023 | 3.3152 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2023-04-04 19:34 | 2023-04-05 16:24 | 997 | 20:50 | S | POWER TRANSFORMER AVERIADO | SE INSTALA SUBESTACION PORTATIL 5 DEBIDO A TRANSFORMADOR DE SUBESTACION 7201-00 AVERIADO | M23040400219 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1250 | 2023-04-04 | 1246250 | keep | 0 | Apr | 2023 | 0.84882 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-04-04 19:34 | 2023-04-05 16:24 | 1497 | 20:50 | S | POWER TRANSFORMER AVERIADO | SE INSTALA SUBESTACION PORTATIL 5 DEBIDO A TRANSFORMADOR DE SUBESTACION 7201-00 AVERIADO | M23040400219 | New_Event | Power Transformer Failure | Include | Include | Equipment | 1250 | 2023-04-04 | 1871250 | keep | 0 | Apr | 2023 | 1.2745 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
CANOVANAS | 2023-04-04 19:42 | 2023-04-04 23:50 | 20 | 4:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23040400079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-04-04 | 4960 | keep | 0 | Apr | 2023 | 0.0033782 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-04 19:44 | 2023-04-05 09:15 | 15 | 13:31 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARARON CONEXIONES SECUNDARIAS | A23040400172 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 811 | 2023-04-04 | 12165 | keep | 0 | Apr | 2023 | 0.0082855 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-04-04 19:56 | 2023-04-05 09:46 | 4 | 13:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X10 EN MONTURA DE XMRS POR LLUVIAS | C23040400134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 830 | 2023-04-04 | 3320 | keep | 0 | Apr | 2023 | 0.0022612 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-04-04 20:05 | 2023-04-05 01:21 | 131 | 5:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | R23040400091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 316 | 2023-04-04 | 41396 | keep | 0 | Apr | 2023 | 0.028195 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
AGUADILLA | 2023-04-04 20:10 | 2023-04-04 21:05 | 300 | 0:55 | P | MAL TIEMPO/LLUVIA O VIENTO | CERRAR POLE BREAKER 7903-06A | M23040400131 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 55 | 2023-04-04 | 16500 | keep | 0 | Apr | 2023 | 0.011238 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-04 20:16 | 2023-04-05 09:45 | 60 | 13:29 | P | DESGANCHE | 1 X 80 EN C/L | R23040400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 809 | 2023-04-04 | 48540 | keep | 0 | Apr | 2023 | 0.03306 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-04-04 20:36 | 2023-04-05 07:18 | 8 | 10:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X25 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23040400138 | New_Event | Cutout Failure | Include | Include | Equipment | 642 | 2023-04-04 | 5136 | keep | 0 | Apr | 2023 | 0.0034981 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-04-04 20:41 | 2023-04-04 23:07 | 481 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | 3 X 65 Y Y 3 X 100 EN C/L SE LLEVO LINEA A AISLADOR | R23040400115 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2023-04-04 | 70226 | keep | 0 | Apr | 2023 | 0.047831 | 0.00032761 | Sustained | FALSE | FALSE | Not_TMED_Event | 481
BAYAMON | 2023-04-04 20:48 | 2023-04-04 21:54 | 627 | 1:06 | P | ANIMAL | 1 X 50 EN RISER 1 X 65 EN RISER 1 X 80 EN C/L CRUCE POR AVE | B23040400131 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-04-04 | 41382 | keep | 0 | Apr | 2023 | 0.028185 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
AGUADILLA | 2023-04-04 20:57 | 2023-04-05 10:20 | 10 | 13:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR POR PORTAFUSIBLE AVERIADO | A23040400185 | New_Event | Cutout Failure | Include | Include | Equipment | 803 | 2023-04-04 | 8030 | keep | 0 | Apr | 2023 | 0.0054692 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-04 21:18 | 2023-04-05 01:26 | 40 | 4:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER Y 1 X 80 EN C/L SE REEMPLAZO DE CAJA PRIMARIA | B23040400135 | New_Event | Cutout Failure | Include | Include | Equipment | 248 | 2023-04-04 | 9920 | keep | 0 | Apr | 2023 | 0.0067565 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-04 21:20 | 2023-04-05 17:18 | 80 | 19:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A23040400187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1198 | 2023-04-04 | 95840 | keep | 0 | Apr | 2023 | 0.065276 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-04 21:43 | 2023-04-05 01:03 | 54 | 3:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | R23040400134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-04-04 | 10800 | keep | 0 | Apr | 2023 | 0.0073558 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
ARECIBO | 2023-04-04 21:53 | 2023-04-04 22:24 | 50 | 0:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A23040400193 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 31 | 2023-04-04 | 1550 | keep | 0 | Apr | 2023 | 0.0010557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-04 21:57 | 2023-04-04 22:50 | 1588 | 0:53 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1716-03 SE SECCIONALIZO PARA REALIZAR DESGANCHE 80% EN SERVICIO DEL 1716-03 Y 100% 1711-01 Y 100% 1711-03 | B23040400145 | New_Event | Feeder Load Transferred | Include | Include | Other | 53 | 2023-04-04 | 84164 | keep | 0 | Apr | 2023 | 0.057324 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-04 21:57 | 2023-04-04 22:50 | 13 | 0:53 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1716-03 SE SECCIONALIZO PARA REALIZAR DESGANCHE 80% EN SERVICIO DEL 1716-03 Y 100% 1711-01 Y 100% 1711-03 | B23040400145 | New_Event | Feeder Load Transferred | Include | Include | Other | 53 | 2023-04-04 | 689 | keep | 0 | Apr | 2023 | 0.00046927 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-04 21:57 | 2023-04-04 22:50 | 1812 | 0:53 | T | DESGANCHE | DISPARO DE BKR SE SECCIONALIZO PARA REALIZAR DESGANCHE 80% EN SERVICIO DEL 1716-03 Y 100% 1711-01 Y 100% 1711-03 | B23040400145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2023-04-04 | 96036 | keep | 0 | Apr | 2023 | 0.06541 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
ARECIBO | 2023-04-04 22:02 | 2023-04-04 22:03 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23040400197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 1227 | keep | 0 | Apr | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
CANOVANAS | 2023-04-04 22:05 | 2023-04-05 11:19 | 10 | 13:14 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | R23040400137 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 794 | 2023-04-04 | 7940 | keep | 0 | Apr | 2023 | 0.0054079 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-04 22:08 | 2023-04-04 22:09 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23040400200 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 1227 | keep | 0 | Apr | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
VEGA BAJA | 2023-04-04 22:09 | 2023-04-04 22:10 | 4027 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE VEGA ALTA CABLERIA CT BKR 0050 | B23040400153 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-04-04 | 4027 | keep | 0 | Apr | 2023 | 0.0027428 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-04-04 22:09 | 2023-04-04 22:10 | 2468 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE VEGA ALTA CABLERIA CT BKR 0050 | B23040400153 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-04-04 | 2468 | keep | 0 | Apr | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-04-04 22:09 | 2023-04-04 22:10 | 1494 | 0:01 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE VEGA ALTA CABLERIA CT BKR 0050 | B23040400153 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 1 | 2023-04-04 | 1494 | keep | 0 | Apr | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-04-04 22:09 | 2023-04-04 22:13 | 1310 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE 0050 Y BARRA DE VEGA ALTA CABLERIA CT BKR 0050 | B23040400152 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-04-04 | 5240 | keep | 0 | Apr | 2023 | 0.0035689 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2023-04-04 22:09 | 2023-04-05 00:28 | 215 | 2:19 | T | ANIMAL | DISPARO DE BKR SE LLEVO EL BKR 0050. SE SECCIONALIZO EL ALIMENTADOR 40% EN SERVICIO BY-230404-04 | B23040400152 | New_Event | Animals | Include | Include | Wildlife | 139 | 2023-04-04 | 29885 | keep | 0 | Apr | 2023 | 0.020355 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-04-04 22:09 | 2023-04-04 22:13 | 1 | 0:04 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE 0050 Y DISPARO DE BARRA DE VEGA ALTA CABLERIA CT BKR 0050 | B23040400152 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 4 | 2023-04-04 | 4 | keep | 0 | Apr | 2023 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-04 22:11 | 2023-04-05 02:52 | 1185 | 4:41 | S | POWER TRANSFORMER AVERIADO | SE DESCONECTO PARARRAYO AVERIDO DEL TRANSFORMADOR DE LA SUBESTACION 8002-00 CON EL GOI AR-230405-01 QUE OCACIONO DISPARO DE LA LINEA 6900 | A23040500006 | New_Event | Power Transformer Failure | Include | Include | Equipment | 281 | 2023-04-04 | 332985 | keep | 0 | Apr | 2023 | 0.22679 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2023-04-04 22:24 | 2023-04-04 22:25 | 2201 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23040400207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-04 | 2201 | keep | 0 | Apr | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-04-04 22:25 | 2023-04-05 02:53 | 50 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A23040400193 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-04-04 | 13400 | keep | 0 | Apr | 2023 | 0.0091267 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-04 22:29 | 2023-04-05 10:18 | 10 | 11:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P23040400130 | New_Event | Cutout Failure | Include | Include | Equipment | 709 | 2023-04-04 | 7090 | keep | 0 | Apr | 2023 | 0.004829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-04 22:29 | 2023-04-05 12:29 | 40 | 14:00 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO NEUTRAL PRIMARIO ABIERTO | A23040400210 | New_Event | Primary Wire Break | Include | Include | Equipment | 840 | 2023-04-04 | 33600 | keep | 0 | Apr | 2023 | 0.022885 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-04 22:50 | 2023-04-04 23:14 | 363 | 0:24 | P | DESGANCHE | SE REALIZA DESGANCHE CON VARETA | B23040400145 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 24 | 2023-04-04 | 8712 | keep | 0 | Apr | 2023 | 0.0059337 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-04 22:50 | 2023-04-05 10:45 | 134 | 11:55 | P | DESGANCHE | SE REALIZO DESGANCHE Y CERRO MACHETES | R23040400069 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 715 | 2023-04-04 | 95810 | keep | 0 | Apr | 2023 | 0.065256 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-04 22:55 | 2023-04-04 22:56 | 1243 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1204-01 LLEVA 90% DE CARGA DEL 1204-03 | S2304040000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-04 | 1243 | keep | 0 | Apr | 2023 | 0.0008466 | 0.0008466 | Momentary | FALSE | FALSE | Not_TMED_Event | 1243
CANOVANAS | 2023-04-04 22:55 | 2023-04-05 00:26 | 319 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTO | R23040400150 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2023-04-04 | 29029 | keep | 0 | Apr | 2023 | 0.019772 | 0.00021727 | Sustained | FALSE | FALSE | Not_TMED_Event | 319
BAYAMON | 2023-04-04 23:14 | 2023-04-04 23:16 | 1588 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1716-03 SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL 80% EN SERVICIO DEL 1716-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-04 | 3176 | keep | 0 | Apr | 2023 | 0.0021632 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-04 23:14 | 2023-04-04 23:16 | 13 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1716-03 SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL 80% EN SERVICIO DEL 1716-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-04 | 26 | keep | 0 | Apr | 2023 | 1.7708e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-04 23:14 | 2023-04-04 23:16 | 1812 | 0:02 | T | DESGANCHE | DISPARO DE BKR 1716-03 SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL 80% EN SERVICIO DEL 1716-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-04 | 3624 | keep | 0 | Apr | 2023 | 0.0024683 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-04 23:16 | 2023-04-04 23:48 | 363 | 0:32 | P | DESGANCHE | SE REALIZA DESGANCHE CON VARETA | B23040400145 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 32 | 2023-04-04 | 11616 | keep | 0 | Apr | 2023 | 0.0079116 | 0.00024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 363
BAYAMON | 2023-04-04 23:34 | 2023-04-05 03:00 | 488 | 3:26 | P | ANIMAL | 2 X 65 EN C/L Y SE CERRO PUENTE DE CAJA A LINEA A CAUSA DE CRUCE X AVE | B23040400269 | New_Event | Animals | Include | Include | Wildlife | 206 | 2023-04-04 | 100528 | keep | 0 | Apr | 2023 | 0.068469 | 0.00033237 | Sustained | FALSE | FALSE | Not_TMED_Event | 488
BAYAMON | 2023-04-04 23:48 | 2023-04-04 23:50 | 1588 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1716-03 AL CERRAR LOS MACHETES SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL 80% EN SERVICIO DEL 1716-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-04 | 3176 | keep | 0 | Apr | 2023 | 0.0021632 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-04 23:48 | 2023-04-04 23:50 | 13 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1716-03 AL CERRAR LOS MACHETES SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL 80% EN SERVICIO DEL 1716-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-04 | 26 | keep | 0 | Apr | 2023 | 1.7708e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-04 23:48 | 2023-04-04 23:50 | 1812 | 0:02 | T | DESGANCHE | DISPARO DE BKR 1716-03 AL CERRAR LOS MACHETES SE VERIFICO PERSONAL FUERA SE CERRO POR CONTROL 80% EN SERVICIO DEL 1716-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-04 | 3624 | keep | 0 | Apr | 2023 | 0.0024683 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-04 23:50 | 2023-04-04 23:54 | 363 | 0:04 | P | DESGANCHE | SE RETIRO RAMAS SOBRE LA LINEA Y SE REEMPLAZO MACHETE QUEMADO | B23040400145 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-04-04 | 1452 | keep | 0 | Apr | 2023 | 0.00098895 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
BAYAMON | 2023-04-04 23:54 | 2023-04-05 00:04 | 1588 | 0:10 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR 1716-03 A PETICION DE GIOVANI RIVERA POR MACHETE PRENDIDO EN FUEGO SE SECCIONALIZO Y SE CERRO POR CONTROL 75% EN SERVICIO DEL 1619-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 10 | 2023-04-04 | 15880 | keep | 0 | Apr | 2023 | 0.010816 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-04 23:54 | 2023-04-05 00:04 | 13 | 0:10 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR 1716-03 A PETICION DE GIOVANI RIVERA POR MACHETE PRENDIDO EN FUEGO SE SECCIONALIZO Y SE CERRO POR CONTROL 75% EN SERVICIO DEL 1619-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 10 | 2023-04-04 | 130 | keep | 0 | Apr | 2023 | 8.8542e-05 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-04 23:54 | 2023-04-05 00:04 | 1812 | 0:10 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR A PETICION DE GIOVANI RIVERA POR MACHETE PRENDIDO EN FUEGO SE SECCIONALIZO Y SE CERRO POR CONTROL 75% EN SERVICIO DEL 1619-03, 100% 1711-01 Y 100% 1711-03 | B23040400145 | New_Event | Switch Failure | Include | Include | Equipment | 10 | 2023-04-04 | 18120 | keep | 0 | Apr | 2023 | 0.012341 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
SAN JUAN | 2023-04-05 00:03 | 2023-04-05 00:04 | 154 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1342-04 80% X 1345-02 Y LLEVA 25% 1203-03 | S2304050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-05 | 154 | keep | 0 | Apr | 2023 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
SAN JUAN | 2023-04-05 00:03 | 2023-04-05 00:04 | 78 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1342-04 80% X 1345-02 Y LLEVA 25% 1203-03 | S2304050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 78 | keep | 0 | Apr | 2023 | 5.3125e-05 | 5.3125e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 78
BAYAMON | 2023-04-05 00:04 | 2023-04-05 00:59 | 453 | 0:55 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO Y SE CERRARON MACHETES 80% EN SERVICIO | B23040400145 | Partial_restoration | Switch Failure | Include | Include | Equipment | 55 | 2023-04-05 | 24915 | keep | 0 | Apr | 2023 | 0.016969 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-05 00:04 | 2023-04-05 00:05 | 3597 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 9405-05 LLEVA EL 1719-15 | B2304050000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-05 | 3597 | keep | 0 | Apr | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-04-05 00:04 | 2023-04-05 00:05 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 9405-05 LLEVA EL 1719-15 | B2304050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 3511 | keep | 0 | Apr | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
VEGA BAJA | 2023-04-05 00:28 | 2023-04-05 01:05 | 129 | 0:37 | P | ANIMAL | SE RETIRO NIDO DE AVE CRUZANDO MACHETE CON VARETA 80% EN SERVICIO BY-230404-04 | B23040400152 | Partial_restoration | Animals | Include | Include | Wildlife | 37 | 2023-04-05 | 4773 | keep | 0 | Apr | 2023 | 0.0032509 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-05 00:47 | 2023-04-05 02:52 | 458 | 2:05 | S | POWER TRANSFORMER AVERIADO | SE DESCONECTO PARARRAYO AVERIDO DEL TRANSFORMADOR DE LA SUBESTACION 8002-00 CON EL GOI AR-230405-01 QUE OCACIONO DISPARO DE LA LINEA 6900 | A23040500006 | New_Event | Power Transformer Failure | Include | Include | Equipment | 125 | 2023-04-05 | 57250 | keep | 0 | Apr | 2023 | 0.038993 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2023-04-05 00:47 | 2023-04-05 02:52 | 437 | 2:05 | S | POWER TRANSFORMER AVERIADO | SE DESCONECTO PARARRAYO AVERIDAO DEL TRANSFORMADOR DE LA SUBESTACION 8002-00 CON EL GOI AR-230405-01 QUE OCACIONO DISPARO DE LA LINEA 6900 | A23040500006 | New_Event | Power Transformer Failure | Include | Include | Equipment | 125 | 2023-04-05 | 54625 | keep | 0 | Apr | 2023 | 0.037205 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2023-04-05 00:47 | 2023-04-05 02:52 | 63 | 2:05 | S | POWER TRANSFORMER AVERIADO | SE DESCONECTO PARARRAYO AVERIDO DEL TRANSFORMADOR DE LA SUBESTACION 8002-00 CON EL GOI AR-230405-01 QUE OCACIONO DISPARO DE LA LINEA 6900 | A23040500006 | New_Event | Power Transformer Failure | Include | Include | Equipment | 125 | 2023-04-05 | 7875 | keep | 0 | Apr | 2023 | 0.0053636 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2023-04-05 00:47 | 2023-04-05 02:52 | 232 | 2:05 | S | POWER TRANSFORMER AVERIADO | SE DESCONECTO PARARRAYO AVERIDO DEL TRANSFORMADOR DE LA SUBESTACION 8002-00 CON EL GOI AR-230405-01 QUE OCACIONO DISPARO DE LA LINEA 6900 | A23040500006 | New_Event | Power Transformer Failure | Include | Include | Equipment | 125 | 2023-04-05 | 29000 | keep | 0 | Apr | 2023 | 0.019752 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
CANOVANAS | 2023-04-05 00:50 | 2023-04-05 00:51 | 3464 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO INTERRUPTOR EN SERVICIO | R23040500005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-05 | 3464 | keep | 0 | Apr | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2023-04-05 00:51 | 2023-04-05 02:05 | 429 | 1:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23040500007 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 74 | 2023-04-05 | 31746 | keep | 0 | Apr | 2023 | 0.021622 | 0.00029219 | Sustained | FALSE | FALSE | Not_TMED_Event | 429
BAYAMON | 2023-04-05 00:59 | 2023-04-05 01:07 | 363 | 0:08 | P | DESCONECTIVO DEFECTUOSO | SE CERRARON MACHETES 100% EN SERVICIO | B23040400145 | Partial_restoration | Switch Failure | Include | Include | Equipment | 8 | 2023-04-05 | 2904 | keep | 0 | Apr | 2023 | 0.0019779 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-05 01:05 | 2023-04-05 01:38 | 43 | 0:33 | P | ANIMAL | 1 X 100 EN C/L PRINCIPAL 100% EN SERVICIO BY-230404-04 CRUCE POR NIDO DE AVE | B23040400152 | Partial_restoration | Animals | Include | Include | Wildlife | 33 | 2023-04-05 | 1419 | keep | 0 | Apr | 2023 | 0.00096647 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-05 01:26 | 2023-04-05 01:27 | 1362 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR RELACIONADO AL EVENTO B23030400135 | B2304050000X | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2023-04-05 | 1362 | keep | 0 | Apr | 2023 | 0.00092765 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-05 01:27 | 2023-04-05 01:55 | 40 | 0:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN RISER Y 1 X 80 EN C/L SE REEMPLAZO DE CAJA PRIMARIA | B23040400135 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 28 | 2023-04-05 | 1120 | keep | 0 | Apr | 2023 | 0.00076283 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-05 01:49 | 2023-04-05 01:50 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 4304 | keep | 0 | Apr | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
SAN JUAN | 2023-04-05 02:14 | 2023-04-05 02:15 | 1105 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2304050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 1105 | keep | 0 | Apr | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2023-04-05 02:15 | 2023-04-05 02:16 | 1105 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2304050000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 1105 | keep | 0 | Apr | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
SAN JUAN | 2023-04-05 03:11 | 2023-04-05 11:46 | 40 | 8:35 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA DESGANCHE ARBOL SOBRE LINEA | S23040500008 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 515 | 2023-04-05 | 20600 | keep | 0 | Apr | 2023 | 0.014031 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-05 03:48 | 2023-04-05 07:05 | 100 | 3:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN RISER PORTAFUSIBLE CONTAMINADO | R23040500019 | New_Event | Cutout Failure | Include | Include | Equipment | 197 | 2023-04-05 | 19700 | keep | 0 | Apr | 2023 | 0.013418 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-05 04:00 | 2023-04-05 04:01 | 603 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR LLEVA 9206-09 | B23040500030 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-05 | 603 | keep | 0 | Apr | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-04-05 04:00 | 2023-04-05 04:01 | 6 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-08 LLEVA 9206-09 | B23040500030 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-05 | 6 | keep | 0 | Apr | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-05 04:01 | 2023-04-05 07:08 | 116 | 3:07 | P | ANIMAL | 1 X 80 EN C/L AVE CRUZO LINEAS | B23040500031 | 1st_after_momentary | Animals | Include | Include | Wildlife | 187 | 2023-04-05 | 21692 | keep | 0 | Apr | 2023 | 0.014774 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
BAYAMON | 2023-04-05 04:12 | 2023-04-05 04:13 | 163 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9203-03 17% X 9202-02 Y LLEVA 20% DEL 9201-01 | B23040500032 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-05 | 163 | keep | 0 | Apr | 2023 | 0.00011102 | 0.00011102 | Momentary | FALSE | FALSE | Not_TMED_Event | 163
BAYAMON | 2023-04-05 04:12 | 2023-04-05 04:13 | 1929 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 17% X 9202-02 Y LLEVA 20% DEL 9201-01 | B23040500032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 1929 | keep | 0 | Apr | 2023 | 0.0013138 | 0.0013138 | Momentary | FALSE | FALSE | Not_TMED_Event | 1929
CAGUAS | 2023-04-05 04:59 | 2023-04-05 05:00 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 853 | keep | 0 | Apr | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
SAN JUAN | 2023-04-05 05:02 | 2023-04-05 15:58 | 80 | 10:56 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE HIZO DESGANCHE | S23040500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 656 | 2023-04-05 | 52480 | keep | 0 | Apr | 2023 | 0.035744 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-04-05 06:39 | 2023-04-05 06:40 | 3701 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | C23040500006 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-05 | 3701 | keep | 0 | Apr | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2023-04-05 06:40 | 2023-04-05 09:00 | 360 | 2:20 | P | CONDUCTOR ROTO O ABIERTO | SE RETIRO BAJANTE PRIMARIO VACANTE/SE ENERGIZO TRIP SAVER PARA COMPLETAR LA TRIFASICA | C23040500007 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 140 | 2023-04-05 | 50400 | keep | 0 | Apr | 2023 | 0.034327 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
BAYAMON | 2023-04-05 06:46 | 2023-04-05 09:37 | 9 | 2:51 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN XMR SE ELIMINO PARARRAYO | B23040500040 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 171 | 2023-04-05 | 1539 | keep | 0 | Apr | 2023 | 0.0010482 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-04-05 06:49 | 2023-04-05 10:00 | 2219 | 3:11 | P | DESGANCHE | DISPARO PB-3A SE SECCIONALIZO TRAMO Y SE CERRO PB-3A | S23040500055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-04-05 | 423829 | keep | 0 | Apr | 2023 | 0.28867 | 0.0015114 | Sustained | FALSE | FALSE | Not_TMED_Event | 2219
CAGUAS | 2023-04-05 06:55 | 2023-04-05 11:14 | 60 | 4:19 | P | ANIMAL | 1X80 EN C/L Y 2X50 EN OTRO C/L CRUCE POR AVE | C23040500010 | New_Event | Animals | Include | Include | Wildlife | 259 | 2023-04-05 | 15540 | keep | 0 | Apr | 2023 | 0.010584 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-05 07:16 | 2023-04-05 13:13 | 36 | 5:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN SU-2 SE DESCONTAMINO PORTAFUSIBLE | R23040500033 | New_Event | Cutout Failure | Include | Include | Equipment | 357 | 2023-04-05 | 12852 | keep | 0 | Apr | 2023 | 0.0087534 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2023-04-05 07:18 | 2023-04-05 07:20 | 4027 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VEGA ALTA TC CABLERIA CT BKR 0050 | B23040500049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-04-05 | 8054 | keep | 0 | Apr | 2023 | 0.0054855 | 0.0027428 | Momentary | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-04-05 07:18 | 2023-04-05 07:20 | 2468 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VEGA ALTA TC CABLERIA CT BKR 0050 | B23040500049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-04-05 | 4936 | keep | 0 | Apr | 2023 | 0.0033619 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-04-05 07:18 | 2023-04-05 07:20 | 1494 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VEGA ALTA TC CABLERIA CT BKR 0050 | B23040500049 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-04-05 | 2988 | keep | 0 | Apr | 2023 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-04-05 07:18 | 2023-04-05 13:22 | 1310 | 6:04 | S | DISPARO DE BARRA DE TRANSMISION | SE REPARO PUENTE CT DE BKR 0050 CABLERIA CT BKR 0050 | B23040500044 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 364 | 2023-04-05 | 476840 | keep | 0 | Apr | 2023 | 0.32477 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2023-04-05 07:18 | 2023-04-05 13:22 | 215 | 6:04 | S | DISPARO DE BARRA DE TRANSMISION | SE REPARO PUENTE CT DE BKR 0050 CABLERIA CT BKR 0050 | B23040500044 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 364 | 2023-04-05 | 78260 | keep | 0 | Apr | 2023 | 0.053303 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-04-05 07:18 | 2023-04-05 13:22 | 1 | 6:04 | S | DISPARO DE BARRA DE TRANSMISION | SE REPARO PUENTE CT DE BKR 0050 CABLERIA CT BKR 0050 | B23040500044 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 364 | 2023-04-05 | 364 | keep | 0 | Apr | 2023 | 0.00024792 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-05 07:20 | 2023-04-05 09:19 | 30 | 1:59 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | C23040500017 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-04-05 | 3570 | keep | 0 | Apr | 2023 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-05 07:28 | 2023-04-05 07:29 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23040500021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
ARECIBO | 2023-04-05 07:35 | 2023-04-05 12:06 | 5 | 4:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A23040500027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 271 | 2023-04-05 | 1355 | keep | 0 | Apr | 2023 | 0.00092288 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-04-05 07:45 | 2023-04-05 10:23 | 26 | 2:38 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23040500030 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-04-05 | 4108 | keep | 0 | Apr | 2023 | 0.0027979 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
ARECIBO | 2023-04-05 07:45 | 2023-04-05 11:50 | 15 | 4:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR PORTAFUSIBLE PARTIDO | A23040500029 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2023-04-05 | 3675 | keep | 0 | Apr | 2023 | 0.002503 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-04-05 08:11 | 2023-04-05 09:38 | 5 | 1:27 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | R23040500035 | New_Event | Animals | Include | Include | Wildlife | 87 | 2023-04-05 | 435 | keep | 0 | Apr | 2023 | 0.00029628 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-04-05 08:13 | 2023-04-05 13:25 | 150 | 5:12 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE CERRO MACHETES | M23040500024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 312 | 2023-04-05 | 46800 | keep | 0 | Apr | 2023 | 0.031875 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-04-05 08:20 | 2023-04-05 08:21 | 1702 | 0:01 | T | ANIMAL | RECERRO | C23040500036 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-05 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-04-05 08:29 | 2023-04-05 12:21 | 80 | 3:52 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | C23040500043 | New_Event | Animals | Include | Include | Wildlife | 232 | 2023-04-05 | 18560 | keep | 0 | Apr | 2023 | 0.012641 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-05 08:31 | 2023-04-05 08:33 | 2364 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23004050000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-05 | 4728 | keep | 0 | Apr | 2023 | 0.0032202 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
AGUADILLA | 2023-04-05 08:33 | 2023-04-05 12:15 | 60 | 3:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS | M23040500037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-04-05 | 13320 | keep | 0 | Apr | 2023 | 0.0090722 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-05 08:36 | 2023-04-05 08:37 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23040500037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2023-04-05 08:47 | 2023-04-05 08:49 | 837 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL CARGA DEL 1401-06 POR EL 1401-07 | S23040500090 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-05 | 1674 | keep | 0 | Apr | 2023 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-04-05 08:47 | 2023-04-05 08:49 | 908 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA CARGA DEL 1401-06 | S23040500090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-05 | 1816 | keep | 0 | Apr | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2023-04-05 08:50 | 2023-04-05 12:01 | 48 | 3:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | B23040500069 | New_Event | Cutout Failure | Include | Include | Equipment | 191 | 2023-04-05 | 9168 | keep | 0 | Apr | 2023 | 0.0062443 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2023-04-05 08:51 | 2023-04-05 08:52 | 57 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | S2304050000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-05 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-04-05 08:52 | 2023-04-05 14:52 | 2 | 6:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS Y VIENTO | S23040500172 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 360 | 2023-04-05 | 720 | keep | 0 | Apr | 2023 | 0.00049039 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-05 09:00 | 2023-04-05 09:04 | 651 | 0:04 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | B2304050000X | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2023-04-05 | 2604 | keep | 0 | Apr | 2023 | 0.0017736 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
CANOVANAS | 2023-04-05 09:00 | 2023-04-05 10:49 | 7 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R23040500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-04-05 | 763 | keep | 0 | Apr | 2023 | 0.00051968 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-04-05 09:02 | 2023-04-05 10:00 | 5 | 0:58 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASES | M23040500055 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-04-05 | 290 | keep | 0 | Apr | 2023 | 0.00019752 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-04-05 09:03 | 2023-04-05 14:54 | 10 | 5:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REEMPLAZO CAJA PRIMARIA | R23040500042 | New_Event | Cutout Failure | Include | Include | Equipment | 351 | 2023-04-05 | 3510 | keep | 0 | Apr | 2023 | 0.0023906 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-05 09:04 | 2023-04-05 13:38 | 100 | 4:34 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN GABINETE Y 1 X 100 EN RISER | B23040500118 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 274 | 2023-04-05 | 27400 | keep | 0 | Apr | 2023 | 0.018662 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-05 09:13 | 2023-04-05 10:51 | 26 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER LLUVIA FUERTE | B23040500075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2023-04-05 | 2548 | keep | 0 | Apr | 2023 | 0.0017354 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2023-04-05 09:15 | 2023-04-05 13:35 | 107 | 4:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN PROVISIONAL 1 X 50 EN CORTE DE LINEA MAL TIEMPO | B23040500077 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 260 | 2023-04-05 | 27820 | keep | 0 | Apr | 2023 | 0.018948 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
SAN JUAN | 2023-04-05 09:16 | 2023-04-05 12:29 | 10 | 3:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | S23040500108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 193 | 2023-04-05 | 1930 | keep | 0 | Apr | 2023 | 0.0013145 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-05 09:17 | 2023-04-05 11:23 | 1 | 2:06 | P | DESGANCHE | 1X10 EN XMR DESGANCHE PRIMARIO | C23040500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-04-05 | 126 | keep | 0 | Apr | 2023 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-05 09:21 | 2023-04-05 11:28 | 603 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIAS | C23040500063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2023-04-05 | 76581 | keep | 0 | Apr | 2023 | 0.052159 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
VEGA BAJA | 2023-04-05 09:25 | 2023-04-05 13:15 | 190 | 3:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23040500086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2023-04-05 | 43700 | keep | 0 | Apr | 2023 | 0.029764 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
AGUADILLA | 2023-04-05 09:33 | 2023-04-05 11:09 | 1 | 1:36 | P | DESGANCHE | 1 X 25 EN CL DESGANCHE | M23040500044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-04-05 | 96 | keep | 0 | Apr | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-05 09:37 | 2023-04-05 09:38 | 2610 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23040500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 2610 | keep | 0 | Apr | 2023 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
GUAYAMA | 2023-04-05 09:45 | 2023-04-05 14:03 | 1 | 4:18 | P | NO SE REPORTO CAUSA | 2 X 10 EN XMR NO SE REPORTO CAUSA | P23040500051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2023-04-05 | 258 | keep | 0 | Apr | 2023 | 0.00017572 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-05 09:50 | 2023-04-05 12:39 | 12 | 2:49 | P | MAL TIEMPO/RAYOS | 1X10 EN XMR POR LLUVIAS | C23040500095 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 169 | 2023-04-05 | 2028 | keep | 0 | Apr | 2023 | 0.0013813 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-04-05 09:52 | 2023-04-05 15:41 | 80 | 5:49 | P | DESGANCHE | 1 X 100 EN CL BAMBUS | M23040500052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2023-04-05 | 27920 | keep | 0 | Apr | 2023 | 0.019016 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-05 09:54 | 2023-04-05 12:41 | 30 | 2:47 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L AEREO PROVISIONAL Y SE LEVANTO CONDUCTOR | B23040500100 | New_Event | Primary Wire Break | Include | Include | Equipment | 167 | 2023-04-05 | 5010 | keep | 0 | Apr | 2023 | 0.0034123 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-05 09:58 | 2023-04-05 11:16 | 1 | 1:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO ABIERTO @ LA ENTRADA DE XMR NO FUNDIO | C23040500109 | New_Event | Primary Wire Break | Include | Include | Equipment | 78 | 2023-04-05 | 78 | keep | 0 | Apr | 2023 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-05 09:59 | 2023-04-05 10:15 | 1 | 0:16 | P | CAUSAS EXTERNAS | 1 X 20 EN BANCO XMR SE ENCONTRO TAPE CRUZANDO LINEA | B23040500113 | New_Event | Damage From Public | Include | Include | Public | 16 | 2023-04-05 | 16 | keep | 0 | Apr | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-05 09:59 | 2023-04-05 12:25 | 10 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE EN CL | M23040500056 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2023-04-05 | 1460 | keep | 0 | Apr | 2023 | 0.0009944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-05 10:00 | 2023-04-05 12:56 | 12 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA MAL TIEMPO | S23040500126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2023-04-05 | 2112 | keep | 0 | Apr | 2023 | 0.0014385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-05 10:00 | 2023-04-05 12:12 | 220 | 2:12 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE Y SE CERRO MACHETE | S23040500128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-04-05 | 29040 | keep | 0 | Apr | 2023 | 0.019779 | 0.00014984 | Sustained | FALSE | FALSE | Not_TMED_Event | 220
CANOVANAS | 2023-04-05 10:00 | 2023-04-05 16:46 | 26 | 6:46 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE CON CULEBRA | R23040500050 | New_Event | Animals | Include | Include | Wildlife | 406 | 2023-04-05 | 10556 | keep | 0 | Apr | 2023 | 0.0071896 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BARRANQUITAS | 2023-04-05 10:00 | 2023-04-05 12:58 | 60 | 2:58 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | C23040500112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-04-05 | 10680 | keep | 0 | Apr | 2023 | 0.0072741 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-04-05 10:00 | 2023-04-05 10:01 | 2201 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23040500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 2201 | keep | 0 | Apr | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
BARRANQUITAS | 2023-04-05 10:10 | 2023-04-05 16:20 | 75 | 6:10 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA REPARAR CONDUCTOR PRIMARIO ROTO CG-230405-01 | C23040500118 | New_Event | Primary Wire Break | Include | Include | Equipment | 370 | 2023-04-05 | 27750 | keep | 0 | Apr | 2023 | 0.0189 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-04-05 10:15 | 2023-04-05 10:16 | 4533 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 4533 | keep | 0 | Apr | 2023 | 0.0030874 | 0.0030874 | Momentary | FALSE | FALSE | Not_TMED_Event | 4533
SAN JUAN | 2023-04-05 10:16 | 2023-04-05 14:30 | 7 | 4:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 3 X 80 EN CORTE DE LINEA MAL TIEMPO | S23040500130 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 254 | 2023-04-05 | 1778 | keep | 0 | Apr | 2023 | 0.001211 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-05 10:16 | 2023-04-05 12:55 | 1 | 2:39 | P | CAUSAS EXTERNAS | 1 X 20 EN BANCO XMR SE ENCONTRO TAPE CRUZANDO LINEA | B23040500113 | New_Event | Damage From Public | Include | Include | Public | 159 | 2023-04-05 | 159 | keep | 0 | Apr | 2023 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-05 10:21 | 2023-04-05 10:22 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
ARECIBO | 2023-04-05 10:25 | 2023-04-05 12:59 | 100 | 2:34 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040500083 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 154 | 2023-04-05 | 15400 | keep | 0 | Apr | 2023 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-05 10:45 | 2023-04-05 16:13 | 48 | 5:28 | P | ANIMAL | 1 X 65, Y 1 X 40 EN CORTES DE LINEA, 1 X 50 EN RISER Y 1 X 15 EN TRANSFORMADOR CRUCE POR AVE. | C23040500128 | New_Event | Animals | Include | Include | Wildlife | 328 | 2023-04-05 | 15744 | keep | 0 | Apr | 2023 | 0.010723 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
AGUADILLA | 2023-04-05 10:50 | 2023-04-05 14:00 | 8 | 3:10 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REMPLAZO BAJANTE SECUNDARIO | M23040500068 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 190 | 2023-04-05 | 1520 | keep | 0 | Apr | 2023 | 0.0010353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-05 11:02 | 2023-04-05 17:28 | 19 | 6:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B23040500130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 386 | 2023-04-05 | 7334 | keep | 0 | Apr | 2023 | 0.0049952 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-04-05 11:03 | 2023-04-05 16:02 | 632 | 4:59 | P | CABLE SOTERRADO AVERIADO | BY-230405-02 SE REPARO CABLE SOTERRADO AVERIADO EN SU-1 | B23040500133 | New_Event | UG Cable Fault | Include | Include | Equipment | 299 | 2023-04-05 | 188968 | keep | 0 | Apr | 2023 | 0.12871 | 0.00043045 | Sustained | FALSE | FALSE | Not_TMED_Event | 632
BAYAMON | 2023-04-05 11:08 | 2023-04-05 13:00 | 76 | 1:52 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23040500137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-04-05 | 8512 | keep | 0 | Apr | 2023 | 0.0057975 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
ARECIBO | 2023-04-05 11:10 | 2023-04-05 14:39 | 35 | 3:29 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A23040500100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-04-05 | 7315 | keep | 0 | Apr | 2023 | 0.0049822 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2023-04-05 11:18 | 2023-04-05 14:27 | 25 | 3:09 | P | SOBRECARGA | 3 X 50 EN CORTE4 DE LINEA POR SOBRE CARGA | A23040500104 | New_Event | Trip Due To Overload | Include | Include | Other | 189 | 2023-04-05 | 4725 | keep | 0 | Apr | 2023 | 0.0032182 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-05 11:23 | 2023-04-05 13:52 | 25 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | S23040500166 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2023-04-05 | 3725 | keep | 0 | Apr | 2023 | 0.0025371 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-04-05 11:23 | 2023-04-05 11:59 | 1863 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500119 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 67068 | keep | 0 | Apr | 2023 | 0.04568 | 0.0012689 | Sustained | FALSE | FALSE | Not_TMED_Event | 1863
PONCE | 2023-04-05 11:23 | 2023-04-05 11:59 | 708 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500119 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 25488 | keep | 0 | Apr | 2023 | 0.01736 | 0.00048222 | Sustained | FALSE | FALSE | Not_TMED_Event | 708
YAUCO | 2023-04-05 11:23 | 2023-04-05 11:59 | 502 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 18072 | keep | 0 | Apr | 2023 | 0.012309 | 0.00034191 | Sustained | FALSE | FALSE | Not_TMED_Event | 502
YAUCO | 2023-04-05 11:23 | 2023-04-05 11:59 | 2747 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 98892 | keep | 0 | Apr | 2023 | 0.067355 | 0.001871 | Sustained | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2023-04-05 11:23 | 2023-04-05 11:59 | 1587 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 57132 | keep | 0 | Apr | 2023 | 0.038912 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
YAUCO | 2023-04-05 11:23 | 2023-04-05 11:59 | 2671 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 96156 | keep | 0 | Apr | 2023 | 0.065491 | 0.0018192 | Sustained | FALSE | FALSE | Not_TMED_Event | 2671
YAUCO | 2023-04-05 11:23 | 2023-04-05 11:59 | 508 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 18288 | keep | 0 | Apr | 2023 | 0.012456 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-04-05 11:23 | 2023-04-05 11:59 | 64 | 0:36 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 FLASHOVER EN AUXILIAR 0521 COSTA SUR | P23040500122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 36 | 2023-04-05 | 2304 | keep | 0 | Apr | 2023 | 0.0015692 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
CAGUAS | 2023-04-05 11:30 | 2023-04-05 16:10 | 181 | 4:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23040500151 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 280 | 2023-04-05 | 50680 | keep | 0 | Apr | 2023 | 0.034518 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
PONCE | 2023-04-05 11:33 | 2023-04-05 13:42 | 1 | 2:09 | P | MAL TIEMPO/RAYOS | 2 X 40 EN C/L MAL TIEMPO RAYOS | P23040500096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 129 | 2023-04-05 | 129 | keep | 0 | Apr | 2023 | 8.7861e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-05 11:37 | 2023-04-05 11:38 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 2402 | keep | 0 | Apr | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
CAGUAS | 2023-04-05 11:37 | 2023-04-05 12:27 | 100 | 0:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIAS | C23040500154 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 50 | 2023-04-05 | 5000 | keep | 0 | Apr | 2023 | 0.0034055 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-04-05 11:38 | 2023-04-05 16:10 | 40 | 4:32 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500081 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 272 | 2023-04-05 | 10880 | keep | 0 | Apr | 2023 | 0.0074103 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-05 11:39 | 2023-04-05 14:26 | 149 | 2:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS FUERTES | B23040500162 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 167 | 2023-04-05 | 24883 | keep | 0 | Apr | 2023 | 0.016948 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
SAN JUAN | 2023-04-05 11:45 | 2023-04-05 11:48 | 1825 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040500175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 5475 | keep | 0 | Apr | 2023 | 0.003729 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-04-05 11:45 | 2023-04-05 11:48 | 47 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040500175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 141 | keep | 0 | Apr | 2023 | 9.6034e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-04-05 11:45 | 2023-04-05 11:48 | 315 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040500175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 945 | keep | 0 | Apr | 2023 | 0.00064364 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-04-05 11:45 | 2023-04-05 11:48 | 2 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040500175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 6 | keep | 0 | Apr | 2023 | 4.0866e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-05 11:45 | 2023-04-05 11:48 | 2391 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040500175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 7173 | keep | 0 | Apr | 2023 | 0.0048855 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2023-04-05 11:45 | 2023-04-05 11:49 | 2276 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040500160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-05 | 9104 | keep | 0 | Apr | 2023 | 0.0062007 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-04-05 11:45 | 2023-04-05 11:49 | 777 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040500160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-05 | 3108 | keep | 0 | Apr | 2023 | 0.0021168 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-04-05 11:45 | 2023-04-05 11:49 | 12 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040500160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-05 | 48 | keep | 0 | Apr | 2023 | 3.2693e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-05 11:45 | 2023-04-05 11:49 | 1290 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040500160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-05 | 5160 | keep | 0 | Apr | 2023 | 0.0035145 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
VEGA BAJA | 2023-04-05 11:46 | 2023-04-05 12:13 | 3157 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 SUBESTACION 8602-00 AFECTADA | A23040500141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2023-04-05 | 85239 | keep | 0 | Apr | 2023 | 0.058056 | 0.0021502 | Sustained | FALSE | FALSE | Not_TMED_Event | 3157
VEGA BAJA | 2023-04-05 11:46 | 2023-04-05 12:13 | 35 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 SUBESTACION 8602-00 AFECTADA | A23040500141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2023-04-05 | 945 | keep | 0 | Apr | 2023 | 0.00064364 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-04-05 11:46 | 2023-04-05 12:13 | 2916 | 0:27 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 SUBESTACION 8602-00 AFECTADA | A23040500141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 27 | 2023-04-05 | 78732 | keep | 0 | Apr | 2023 | 0.053624 | 0.0019861 | Sustained | FALSE | FALSE | Not_TMED_Event | 2916
GUAYAMA | 2023-04-05 11:49 | 2023-04-05 13:07 | 50 | 1:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO FUERTES LLUVIAS | P23040500124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 78 | 2023-04-05 | 3900 | keep | 0 | Apr | 2023 | 0.0026563 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-04-05 11:50 | 2023-04-05 11:51 | 494 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040500126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 494 | keep | 0 | Apr | 2023 | 0.00033646 | 0.00033646 | Momentary | FALSE | FALSE | Not_TMED_Event | 494
UTUADO | 2023-04-05 11:52 | 2023-04-05 16:42 | 5 | 4:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR POR MAL TIEMPO | A23040500125 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 290 | 2023-04-05 | 1450 | keep | 0 | Apr | 2023 | 0.00098759 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-04-05 11:55 | 2023-04-05 14:30 | 10 | 2:35 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ELIMINO POSTE SECUNDARIO PARTIDO | P23040500131 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 155 | 2023-04-05 | 1550 | keep | 0 | Apr | 2023 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-05 11:58 | 2023-04-05 11:59 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23040500059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-05 12:00 | 2023-04-05 14:03 | 150 | 2:03 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | R23040500060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-04-05 | 18450 | keep | 0 | Apr | 2023 | 0.012566 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-04-05 12:00 | 2023-04-05 20:35 | 400 | 8:35 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA Y SE CERRO PUENTE | A23040500142 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 515 | 2023-04-05 | 206000 | keep | 0 | Apr | 2023 | 0.14031 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-04-05 12:03 | 2023-04-05 15:48 | 48 | 3:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS Y VIENTO | B23040500170 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 225 | 2023-04-05 | 10800 | keep | 0 | Apr | 2023 | 0.0073558 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
ARECIBO | 2023-04-05 12:06 | 2023-04-05 14:00 | 20 | 1:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23040500146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-04-05 | 2280 | keep | 0 | Apr | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-05 12:10 | 2023-04-05 13:07 | 14 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES SECUNDARIO | S23040500083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-04-05 | 798 | keep | 0 | Apr | 2023 | 0.00054351 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-04-05 12:12 | 2023-04-05 14:13 | 12 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CORTE DE LINEA POR MAL TIEMPO | A23040500155 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-04-05 | 1452 | keep | 0 | Apr | 2023 | 0.00098895 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-04-05 12:15 | 2023-04-05 19:46 | 200 | 7:31 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23040500144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 451 | 2023-04-05 | 90200 | keep | 0 | Apr | 2023 | 0.061435 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-04-05 12:18 | 2023-04-05 12:21 | 3046 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | R23040500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-05 | 9138 | keep | 0 | Apr | 2023 | 0.0062239 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
BARRANQUITAS | 2023-04-05 12:23 | 2023-04-05 14:58 | 125 | 2:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA, MAL TIEMPO LLUVIA | C23040500179 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 155 | 2023-04-05 | 19375 | keep | 0 | Apr | 2023 | 0.013196 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
YAUCO | 2023-04-05 12:23 | 2023-04-05 12:24 | 1339 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA POR 6601-02 | M23040500107 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-05 | 1339 | keep | 0 | Apr | 2023 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-04-05 12:23 | 2023-04-05 12:24 | 470 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040500107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 470 | keep | 0 | Apr | 2023 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-04-05 12:23 | 2023-04-05 12:24 | 2483 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M23040500108 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-05 | 2483 | keep | 0 | Apr | 2023 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-04-05 12:24 | 2023-04-05 16:42 | 125 | 4:18 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500117 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 258 | 2023-04-05 | 32250 | keep | 0 | Apr | 2023 | 0.021965 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
AGUADILLA | 2023-04-05 12:24 | 2023-04-05 12:25 | 1827 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M23040500109 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-05 | 1827 | keep | 0 | Apr | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-04-05 12:25 | 2023-04-05 19:17 | 25 | 6:52 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23030500298 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 412 | 2023-04-05 | 10300 | keep | 0 | Apr | 2023 | 0.0070153 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-04-05 12:26 | 2023-04-05 14:18 | 1 | 1:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23040500150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-04-05 | 112 | keep | 0 | Apr | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-05 12:27 | 2023-04-05 13:07 | 9 | 0:40 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | C23040500184 | New_Event | Animals | Include | Include | Wildlife | 40 | 2023-04-05 | 360 | keep | 0 | Apr | 2023 | 0.00024519 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
ARECIBO | 2023-04-05 12:28 | 2023-04-05 16:17 | 80 | 3:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | A23040500171 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 229 | 2023-04-05 | 18320 | keep | 0 | Apr | 2023 | 0.012478 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-05 12:36 | 2023-04-05 15:44 | 111 | 3:08 | P | DESGANCHE | DESPEJE DE LINEA 1 X 65 EN CORTE DE LINEA | S23040500190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-04-05 | 20868 | keep | 0 | Apr | 2023 | 0.014213 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
VEGA BAJA | 2023-04-05 12:43 | 2023-04-05 18:01 | 119 | 5:18 | P | DESGANCHE | 1 X 30 Y 1 X 65 EN C/L DESGANCHE | B23040500208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2023-04-05 | 37842 | keep | 0 | Apr | 2023 | 0.025774 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
AGUADILLA | 2023-04-05 12:45 | 2023-04-05 12:46 | 693 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA CICLO DE RECIERRE Y QUEDA EN SERVICIO | M23040500140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 693 | keep | 0 | Apr | 2023 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
BAYAMON | 2023-04-05 12:48 | 2023-04-05 14:19 | 60 | 1:31 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN C/L SE REALIZO DESGANCHE | B23040500209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-04-05 | 5460 | keep | 0 | Apr | 2023 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-04-05 12:55 | 2023-04-05 14:30 | 50 | 1:35 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYO | A23040500185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 95 | 2023-04-05 | 4750 | keep | 0 | Apr | 2023 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-05 12:56 | 2023-04-05 16:05 | 7 | 3:09 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | C23040500188 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 189 | 2023-04-05 | 1323 | keep | 0 | Apr | 2023 | 0.00090109 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-04-05 12:57 | 2023-04-05 21:01 | 60 | 8:04 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR Y 1 X 30 Y 1X 40 EN CORTE DE LINEA POR RAYOS | A23040500186 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 484 | 2023-04-05 | 29040 | keep | 0 | Apr | 2023 | 0.019779 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-04-05 13:00 | 2023-04-05 15:28 | 100 | 2:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN C/L | P23040500171 | New_Event | Primary Wire Break | Include | Include | Equipment | 148 | 2023-04-05 | 14800 | keep | 0 | Apr | 2023 | 0.01008 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-04-05 13:00 | 2023-04-05 15:00 | 50 | 2:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA | A23040500180 | New_Event | Primary Wire Break | Include | Include | Equipment | 120 | 2023-04-05 | 6000 | keep | 0 | Apr | 2023 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-04-05 13:02 | 2023-04-05 13:26 | 15 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO PEDESTAL Y BARRAS SECUNDARIAS | P23040500173 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-04-05 | 360 | keep | 0 | Apr | 2023 | 0.00024519 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-04-05 13:07 | 2023-04-05 13:08 | 3131 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040500080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 3131 | keep | 0 | Apr | 2023 | 0.0021325 | 0.0021325 | Momentary | FALSE | FALSE | Not_TMED_Event | 3131
BARRANQUITAS | 2023-04-05 13:08 | 2023-04-05 16:13 | 9 | 3:05 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | C23040500184 | Partial_restoration | Animals | Include | Include | Wildlife | 185 | 2023-04-05 | 1665 | keep | 0 | Apr | 2023 | 0.001134 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-05 13:09 | 2023-04-05 15:16 | 25 | 2:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C23040500195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-04-05 | 3175 | keep | 0 | Apr | 2023 | 0.0021625 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-04-05 13:12 | 2023-04-05 15:52 | 33 | 2:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23040500196 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 160 | 2023-04-05 | 5280 | keep | 0 | Apr | 2023 | 0.0035962 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-04-05 13:35 | 2023-04-05 16:16 | 1 | 2:41 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23040500230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-04-05 | 161 | keep | 0 | Apr | 2023 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-05 13:38 | 2023-04-05 17:23 | 2 | 3:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO RISER Y SE CERRO PUENTE DE LINEA A CAJA 2 X 80 EN RISER | B23040500247 | New_Event | Primary Wire Break | Include | Include | Equipment | 225 | 2023-04-05 | 450 | keep | 0 | Apr | 2023 | 0.00030649 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-04-05 13:52 | 2023-04-05 16:55 | 2533 | 3:03 | P | DESGANCHE | SE CERRO INTELIRUPTER SE RETIRO RAMAS SOBRE LAS LINEAS 6014-02A | M23040500289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-04-05 | 463539 | keep | 0 | Apr | 2023 | 0.31571 | 0.0017252 | Sustained | FALSE | FALSE | Not_TMED_Event | 2533
HUMACAO | 2023-04-05 13:58 | 2023-04-05 16:43 | 1 | 2:45 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C23040500210 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-04-05 | 165 | keep | 0 | Apr | 2023 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-05 13:59 | 2023-04-05 15:02 | 1 | 1:03 | P | DESGANCHE | 1 X 15 EN MONTURA 1 X 25 EN C/L | B23040500240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-04-05 | 63 | keep | 0 | Apr | 2023 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-05 13:59 | 2023-04-05 16:28 | 30 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTES LLUVIA | M23040500303 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2023-04-05 | 4470 | keep | 0 | Apr | 2023 | 0.0030445 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-05 14:09 | 2023-04-05 21:35 | 13 | 7:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MMAL TIEMPO LLUVIA | S23040500224 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 446 | 2023-04-05 | 5798 | keep | 0 | Apr | 2023 | 0.003949 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2023-04-05 14:10 | 2023-04-05 14:30 | 50 | 0:20 | P | ANIMAL | 1 X 20 Y 1 X 30 EN CORTES DE LINEA CRUCE CON AVE | R23040500076 | New_Event | Animals | Include | Include | Wildlife | 20 | 2023-04-05 | 1000 | keep | 0 | Apr | 2023 | 0.0006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-05 14:23 | 2023-04-05 16:45 | 1 | 2:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN RISER MAL TIEMPO LLUVIA | C23040500219 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 142 | 2023-04-05 | 142 | keep | 0 | Apr | 2023 | 9.6716e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-05 14:26 | 2023-04-05 17:14 | 58 | 2:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIA Y VIENTOS FUERTES | S23040500228 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 168 | 2023-04-05 | 9744 | keep | 0 | Apr | 2023 | 0.0066366 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
CAGUAS | 2023-04-05 14:29 | 2023-04-05 15:42 | 218 | 1:13 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23040500222 | New_Event | Animals | Include | Include | Wildlife | 73 | 2023-04-05 | 15914 | keep | 0 | Apr | 2023 | 0.010839 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
CANOVANAS | 2023-04-05 14:34 | 2023-04-05 18:54 | 100 | 4:20 | P | ANIMAL | 1 X 65 Y 1 X 40 EN CORTES DE LINEA CRUCE CON AVE | R23040500079 | New_Event | Animals | Include | Include | Wildlife | 260 | 2023-04-05 | 26000 | keep | 0 | Apr | 2023 | 0.017708 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-05 14:36 | 2023-04-05 15:45 | 10 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO BAJANTE SECUNDARIO | B23040500254 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-04-05 | 690 | keep | 0 | Apr | 2023 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-04-05 14:38 | 2023-04-05 17:35 | 60 | 2:57 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500350 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 177 | 2023-04-05 | 10620 | keep | 0 | Apr | 2023 | 0.0072332 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-04-05 14:40 | 2023-04-05 17:38 | 65 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN FUERTES LLUVIAS | M23040500353 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-04-05 | 11570 | keep | 0 | Apr | 2023 | 0.0078803 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-04-05 14:43 | 2023-04-05 16:48 | 6 | 2:05 | P | DESGANCHE | RAMAS SOBRE LINEAS Y CONDUCTOR EN EL SUELO | S23040500232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-04-05 | 750 | keep | 0 | Apr | 2023 | 0.00051082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-05 14:44 | 2023-04-05 17:50 | 50 | 3:06 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040500361 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-04-05 | 9300 | keep | 0 | Apr | 2023 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-05 14:47 | 2023-04-05 21:34 | 15 | 6:47 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO NO CERRO ORDEN DATOS SE RECOPILARON DEL OMS | S23040500234 | New_Event | Primary Wire Break | Include | Include | Equipment | 407 | 2023-04-05 | 6105 | keep | 0 | Apr | 2023 | 0.0041581 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-05 15:10 | 2023-04-05 21:00 | 28 | 5:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER MAL TIEMPO LLUVIA | S23040500238 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 350 | 2023-04-05 | 9800 | keep | 0 | Apr | 2023 | 0.0066747 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2023-04-05 15:16 | 2023-04-05 16:14 | 10 | 0:58 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA DESGANCHE SECUNDARIO | B23040500237 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 58 | 2023-04-05 | 580 | keep | 0 | Apr | 2023 | 0.00039504 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-05 15:22 | 2023-04-05 17:15 | 40 | 1:53 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA | C23040500240 | New_Event | Primary Wire Break | Include | Include | Equipment | 113 | 2023-04-05 | 4520 | keep | 0 | Apr | 2023 | 0.0030786 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-04-05 15:23 | 2023-04-05 19:24 | 70 | 4:01 | P | MAL TIEMPO/RAYOS | 1 X 80 CL DESCARGAS ELECTRICAS | M23040500400 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 241 | 2023-04-05 | 16870 | keep | 0 | Apr | 2023 | 0.01149 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2023-04-05 15:31 | 2023-04-05 18:20 | 100 | 2:49 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500415 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 169 | 2023-04-05 | 16900 | keep | 0 | Apr | 2023 | 0.011511 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-04-05 15:35 | 2023-04-05 18:48 | 10 | 3:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | P23040500224 | New_Event | Secondary Wire Break | Include | Include | Equipment | 193 | 2023-04-05 | 1930 | keep | 0 | Apr | 2023 | 0.0013145 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-05 15:40 | 2023-04-06 09:20 | 1 | 17:40 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23040500424 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1060 | 2023-04-05 | 1060 | keep | 0 | Apr | 2023 | 0.00072196 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-05 15:45 | 2023-04-05 17:05 | 3 | 1:20 | P | CAUSAS EXTERNAS | CAMION IMPACTO SECUNDARIA, SE ABRIO XMR Y SE REPARO SECUNDARIA AVERIADA | S23040500125 | New_Event | Damage From Public | Include | Include | Public | 80 | 2023-04-05 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-04-05 15:51 | 2023-04-05 18:04 | 50 | 2:13 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR AVE | C23040500245 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-04-05 | 6650 | keep | 0 | Apr | 2023 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-04-05 16:00 | 2023-04-06 00:02 | 80 | 8:02 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETAS PARTIDAS 1 X 80 EN CORTE DE LINEA | P23040500236 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 482 | 2023-04-05 | 38560 | keep | 0 | Apr | 2023 | 0.026263 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-05 16:08 | 2023-04-05 19:51 | 106 | 3:43 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B23040500293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2023-04-05 | 23638 | keep | 0 | Apr | 2023 | 0.0161 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
MAYAGÃœEZ | 2023-04-05 16:09 | 2023-04-05 17:30 | 80 | 1:21 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500476 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 81 | 2023-04-05 | 6480 | keep | 0 | Apr | 2023 | 0.0044135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2023-04-05 16:34 | 2023-04-05 23:02 | 300 | 6:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA 1 X 140 | P23040500139 | New_Event | Primary Wire Break | Include | Include | Equipment | 388 | 2023-04-05 | 116400 | keep | 0 | Apr | 2023 | 0.07928 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2023-04-05 16:35 | 2023-04-05 20:20 | 18 | 3:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R23040500085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 225 | 2023-04-05 | 4050 | keep | 0 | Apr | 2023 | 0.0027584 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
VEGA BAJA | 2023-04-05 16:43 | 2023-04-05 16:58 | 215 | 0:15 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR CONTROL | B23040500280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2023-04-05 | 3225 | keep | 0 | Apr | 2023 | 0.0021965 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-04-05 16:48 | 2023-04-05 18:53 | 50 | 2:05 | P | DESGANCHE | 2 X 100 EN CORTES DE LINEA SE ABRIO CORTE DE LINEA TOTAL PARA SECCIONALIZAR CONDUCTOR EN EL SUELO | S23040500232 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-04-05 | 6250 | keep | 0 | Apr | 2023 | 0.0042568 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-05 16:48 | 2023-04-05 21:51 | 10 | 5:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REPARO SECUNDARIA | P23040500253 | New_Event | Secondary Wire Break | Include | Include | Equipment | 303 | 2023-04-05 | 3030 | keep | 0 | Apr | 2023 | 0.0020637 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-05 17:07 | 2023-04-06 08:13 | 80 | 15:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN C/L LLUVIAS | B23040500285 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 906 | 2023-04-05 | 72480 | keep | 0 | Apr | 2023 | 0.049366 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-04-05 17:17 | 2023-04-05 18:34 | 7 | 1:17 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | C23040500268 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2023-04-05 | 539 | keep | 0 | Apr | 2023 | 0.00036711 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-05 17:19 | 2023-04-05 19:22 | 7 | 2:03 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR SE REEMPLAZO MICARTA | B23040500287 | New_Event | Service Transformer Failure | Include | Include | Equipment | 123 | 2023-04-05 | 861 | keep | 0 | Apr | 2023 | 0.00058642 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-04-05 17:35 | 2023-04-06 10:32 | 8 | 16:57 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO CAJA PRIMARIA Y SE CERRO PUENTE | C23040500270 | New_Event | Primary Wire Break | Include | Include | Equipment | 1017 | 2023-04-05 | 8136 | keep | 0 | Apr | 2023 | 0.0055414 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-04-05 17:38 | 2023-04-06 10:49 | 50 | 17:11 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CL DESCARGAS ELECTRICAS | M23040500563 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1031 | 2023-04-05 | 51550 | keep | 0 | Apr | 2023 | 0.03511 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-04-05 17:40 | 2023-04-05 18:31 | 10 | 0:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO CAJA EN XMR | P23040500270 | New_Event | Cutout Failure | Include | Include | Equipment | 51 | 2023-04-05 | 510 | keep | 0 | Apr | 2023 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-05 17:51 | 2023-04-05 21:03 | 60 | 3:12 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CL DESCARGAS ELECTRICAS | M23040500577 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 192 | 2023-04-05 | 11520 | keep | 0 | Apr | 2023 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-04-05 17:55 | 2023-04-05 19:10 | 70 | 1:15 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23040500581 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-04-05 | 5250 | keep | 0 | Apr | 2023 | 0.0035758 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-04-05 18:28 | 2023-04-05 19:26 | 32 | 0:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23040500279 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 58 | 2023-04-05 | 1856 | keep | 0 | Apr | 2023 | 0.0012641 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
VEGA BAJA | 2023-04-05 18:29 | 2023-04-05 20:34 | 40 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 N C/L LLUVIAS Y VIENTO FUERTE | B23040500295 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-04-05 | 5000 | keep | 0 | Apr | 2023 | 0.0034055 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-05 18:32 | 2023-04-05 20:23 | 142 | 1:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA EVENTO ATENDIDO POR SJ Y TRANSFERIDO A CANOVANAS | S23040500261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-04-05 | 15762 | keep | 0 | Apr | 2023 | 0.010735 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
YAUCO | 2023-04-05 18:48 | 2023-04-05 19:32 | 50 | 0:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23040500610 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 44 | 2023-04-05 | 2200 | keep | 0 | Apr | 2023 | 0.0014984 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-05 18:49 | 2023-04-05 20:17 | 70 | 1:28 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500611 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 88 | 2023-04-05 | 6160 | keep | 0 | Apr | 2023 | 0.0041955 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-04-05 18:53 | 2023-04-10 21:20 | 6 | 122:27 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE LEVANTO PRIMARIA Y SE CERRO PUENTE PRIMARIO SE HABIA SECCIONALIZADO EVENTO RELACIONADO S23040500232 CLIENTES FUERA DESDE 4/5/23 Y SE CULMINO EL 04/10/23 | S23041000169 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 7347 | 2023-04-05 | 44082 | keep | 0 | Apr | 2023 | 0.030024 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-05 19:06 | 2023-04-05 21:10 | 20 | 2:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23040500625 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 124 | 2023-04-05 | 2480 | keep | 0 | Apr | 2023 | 0.0016891 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-04-05 19:14 | 2023-04-05 20:56 | 100 | 1:42 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CL DESCARGAS ELECTRICAS | P23040500305 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2023-04-05 | 10200 | keep | 0 | Apr | 2023 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-04-05 19:14 | 2023-04-05 22:30 | 30 | 3:16 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500629 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 196 | 2023-04-05 | 5880 | keep | 0 | Apr | 2023 | 0.0040048 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-05 19:16 | 2023-04-06 09:34 | 10 | 14:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DEL TRANSFORMADOR | M23040500633 | New_Event | Primary Wire Break | Include | Include | Equipment | 858 | 2023-04-05 | 8580 | keep | 0 | Apr | 2023 | 0.0058438 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-05 19:17 | 2023-04-05 19:18 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23040500634 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 1827 | keep | 0 | Apr | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-04-05 19:18 | 2023-04-05 19:50 | 25 | 0:32 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040500298 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 32 | 2023-04-05 | 800 | keep | 0 | Apr | 2023 | 0.00054488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-05 19:21 | 2023-04-06 07:15 | 8 | 11:54 | P | OTRAS CAUSAS | 1 X 10 EN XMR FUSIBLE FATIGADO | C23040500283 | New_Event | Other Causes | Include | Include | Other | 714 | 2023-04-05 | 5712 | keep | 0 | Apr | 2023 | 0.0038904 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-04-05 19:21 | 2023-04-06 08:12 | 6 | 12:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIAS | B23040500298 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 771 | 2023-04-05 | 4626 | keep | 0 | Apr | 2023 | 0.0031507 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-04-05 19:22 | 2023-04-05 20:55 | 50 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23040500640 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-04-05 | 4650 | keep | 0 | Apr | 2023 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-04-05 19:24 | 2023-04-05 19:42 | 18 | 0:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R23040500093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2023-04-05 | 324 | keep | 0 | Apr | 2023 | 0.00022067 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-04-05 20:08 | 2023-04-05 20:09 | 138 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 10% POR 1206-03 | S23040500000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-05 | 138 | keep | 0 | Apr | 2023 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-04-05 20:08 | 2023-04-05 20:09 | 1977 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 40% POR 1206-03 | S23040500000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-05 | 1977 | keep | 0 | Apr | 2023 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-04-05 20:08 | 2023-04-05 20:09 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 10% DEL 1204-03 Y 40% DEL 1204-04 | S23040500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-05 | 4133 | keep | 0 | Apr | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
YAUCO | 2023-04-05 20:29 | 2023-04-06 09:44 | 2 | 13:15 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CL LINEA CRUZADA | M23040500677 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 795 | 2023-04-05 | 1590 | keep | 0 | Apr | 2023 | 0.0010829 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-04-05 20:44 | 2023-04-05 21:50 | 70 | 1:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23040500685 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 66 | 2023-04-05 | 4620 | keep | 0 | Apr | 2023 | 0.0031467 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-04-05 21:36 | 2023-04-07 20:30 | 10 | 46:54 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO AEREO PROVISIONAL HACIA T-108 TRASPATIO | R23040500101 | New_Event | UG Cable Fault | Include | Include | Equipment | 2814 | 2023-04-05 | 28140 | keep | 0 | Apr | 2023 | 0.019166 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-05 21:50 | 2023-04-06 09:30 | 30 | 11:40 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23040500694 | New_Event | Vegetation Contact | Include | Include | Vegetation | 700 | 2023-04-05 | 21000 | keep | 0 | Apr | 2023 | 0.014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-05 22:23 | 2023-04-05 22:26 | 3157 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A23040500337 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 9471 | keep | 0 | Apr | 2023 | 0.0064507 | 0.0021502 | Momentary | FALSE | FALSE | Not_TMED_Event | 3157
VEGA BAJA | 2023-04-05 22:23 | 2023-04-05 22:26 | 35 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A23040500337 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 105 | keep | 0 | Apr | 2023 | 7.1515e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-04-05 22:23 | 2023-04-05 22:26 | 2916 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 11400 | A23040500337 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-05 | 8748 | keep | 0 | Apr | 2023 | 0.0059582 | 0.0019861 | Momentary | FALSE | FALSE | Not_TMED_Event | 2916
SAN JUAN | 2023-04-05 22:33 | 2023-04-06 12:42 | 11 | 14:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23040500293 | New_Event | Secondary Wire Break | Include | Include | Equipment | 849 | 2023-04-05 | 9339 | keep | 0 | Apr | 2023 | 0.0063608 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-04-05 22:54 | 2023-04-06 10:20 | 100 | 11:26 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23040500348 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 686 | 2023-04-05 | 68600 | keep | 0 | Apr | 2023 | 0.046723 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-05 23:15 | 2023-04-06 08:40 | 8 | 9:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23040500354 | New_Event | Primary Wire Break | Include | Include | Equipment | 565 | 2023-04-05 | 4520 | keep | 0 | Apr | 2023 | 0.0030786 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-04-05 23:40 | 2023-04-06 00:07 | 150 | 0:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P23040500348 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 27 | 2023-04-05 | 4050 | keep | 0 | Apr | 2023 | 0.0027584 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-04-06 00:23 | 2023-04-06 11:47 | 20 | 11:24 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A23040600002 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 684 | 2023-04-06 | 13680 | keep | 0 | Apr | 2023 | 0.0093174 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-06 02:15 | 2023-04-06 02:16 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
CANOVANAS | 2023-04-06 02:32 | 2023-04-06 19:21 | 37 | 16:49 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | R23040600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1009 | 2023-04-06 | 37333 | keep | 0 | Apr | 2023 | 0.025427 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
BAYAMON | 2023-04-06 02:39 | 2023-04-06 02:40 | 2402 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | B23040600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-06 | 2402 | keep | 0 | Apr | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
CANOVANAS | 2023-04-06 03:00 | 2023-04-06 03:01 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23040600002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-06 03:06 | 2023-04-06 03:07 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23040600006 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2023-04-06 03:10 | 2023-04-06 13:23 | 13 | 10:13 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23040600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 613 | 2023-04-06 | 7969 | keep | 0 | Apr | 2023 | 0.0054276 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-04-06 03:15 | 2023-04-06 11:30 | 16 | 8:15 | P | SECUNDARIA/DESGANCHE | 1 X 25 XMR DESGANCHE | S23040600007 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 495 | 2023-04-06 | 7920 | keep | 0 | Apr | 2023 | 0.0053943 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-04-06 03:28 | 2023-04-06 08:40 | 50 | 5:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23040600007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 312 | 2023-04-06 | 15600 | keep | 0 | Apr | 2023 | 0.010625 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-06 03:30 | 2023-04-06 12:07 | 96 | 8:37 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | S23040600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2023-04-06 | 49632 | keep | 0 | Apr | 2023 | 0.033804 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
VEGA BAJA | 2023-04-06 03:59 | 2023-04-06 04:00 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B23040600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 4702 | keep | 0 | Apr | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
HUMACAO | 2023-04-06 04:00 | 2023-04-06 04:01 | 800 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 800 CLIENTES POR EL 3205-07. | C23040600001 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-06 | 800 | keep | 0 | Apr | 2023 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
CAGUAS | 2023-04-06 04:00 | 2023-04-06 04:01 | 3026 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 1608 CLIENTES POR EL 3201-01. LLEVA 800 CLIENTES DEL 2603-08 | C23040600001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 3026 | keep | 0 | Apr | 2023 | 0.002061 | 0.002061 | Momentary | FALSE | FALSE | Not_TMED_Event | 3026
CANOVANAS | 2023-04-06 04:13 | 2023-04-06 12:32 | 40 | 8:19 | P | DESGANCHE | 1X50 EN C/L | R23040600008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 499 | 2023-04-06 | 19960 | keep | 0 | Apr | 2023 | 0.013595 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-04-06 04:22 | 2023-04-06 11:56 | 25 | 7:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS | P23040600015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 454 | 2023-04-06 | 11350 | keep | 0 | Apr | 2023 | 0.0077304 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-06 05:03 | 2023-04-06 09:35 | 40 | 4:32 | P | DESGANCHE | 1 X 40 EN C/L | C23040600002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2023-04-06 | 10880 | keep | 0 | Apr | 2023 | 0.0074103 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-06 05:07 | 2023-04-07 07:32 | 13 | 26:25 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23040600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1585 | 2023-04-06 | 20605 | keep | 0 | Apr | 2023 | 0.014034 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-04-06 05:25 | 2023-04-06 15:45 | 20 | 10:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23040600010 | New_Event | Cutout Failure | Include | Include | Equipment | 620 | 2023-04-06 | 12400 | keep | 0 | Apr | 2023 | 0.0084456 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-06 05:26 | 2023-04-06 08:29 | 10 | 3:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR PORTAFUSIBLE QUEMADO | C23040600003 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2023-04-06 | 1830 | keep | 0 | Apr | 2023 | 0.0012464 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-06 06:00 | 2023-04-06 10:20 | 40 | 4:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE MASIVO | A23040600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2023-04-06 | 10400 | keep | 0 | Apr | 2023 | 0.0070834 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-04-06 06:03 | 2023-04-06 10:03 | 40 | 4:00 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO Y ELIMINO PARARRAYO VACANTE CRUZADO Y REMPLAZO AISLADOR | C23040600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2023-04-06 | 9600 | keep | 0 | Apr | 2023 | 0.0065385 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-06 06:05 | 2023-04-06 18:37 | 20 | 12:32 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR Y 1 X 25 EN C/L MAL TIEMPO RAYOS | B23040600043 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 752 | 2023-04-06 | 15040 | keep | 0 | Apr | 2023 | 0.010244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-06 06:06 | 2023-04-06 06:08 | 171 | 0:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1110-05 LLEVA 1102-02, 03 | S23040600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 342 | keep | 0 | Apr | 2023 | 0.00023293 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2023-04-06 06:06 | 2023-04-06 06:08 | 1837 | 0:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1110-05 LLEVA 1102-02, 03 | S23040600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 3674 | keep | 0 | Apr | 2023 | 0.0025023 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
SAN JUAN | 2023-04-06 06:06 | 2023-04-06 06:08 | 218 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S23040600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 436 | keep | 0 | Apr | 2023 | 0.00029696 | 0.00014848 | Momentary | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2023-04-06 06:06 | 2023-04-06 06:08 | 455 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S23040600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 910 | keep | 0 | Apr | 2023 | 0.0006198 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2023-04-06 06:06 | 2023-04-06 06:08 | 1526 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 | S23040600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 3052 | keep | 0 | Apr | 2023 | 0.0020787 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
SAN JUAN | 2023-04-06 06:06 | 2023-04-06 06:08 | 283 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6700 1110-05 LLEVA 1102-02, 03 | S23040600017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 566 | keep | 0 | Apr | 2023 | 0.0003855 | 0.00019275 | Momentary | FALSE | FALSE | Not_TMED_Event | 283
BAYAMON | 2023-04-06 06:18 | 2023-04-06 07:33 | 14 | 1:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | B23040600047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 75 | 2023-04-06 | 1050 | keep | 0 | Apr | 2023 | 0.00071515 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-04-06 06:20 | 2023-04-06 06:21 | 2407 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23040600017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 2407 | keep | 0 | Apr | 2023 | 0.0016394 | 0.0016394 | Momentary | FALSE | FALSE | Not_TMED_Event | 2407
AGUADILLA | 2023-04-06 06:21 | 2023-04-06 10:46 | 1827 | 4:25 | T | CONDUCTOR ARRIADO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS EN TRONCAL DEL ALIMENTADOR | M23040600016 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 265 | 2023-04-06 | 484155 | keep | 0 | Apr | 2023 | 0.32976 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2023-04-06 06:47 | 2023-04-06 11:25 | 1 | 4:38 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REPARO BARRA PRIMARIA DEL SU-2 @ TRANSCLOSURE BOMBAS A.A.A. MEDIANTE G.O.I. SJ-230406-50 | R23040600011 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 278 | 2023-04-06 | 278 | keep | 0 | Apr | 2023 | 0.00018934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-04-06 07:00 | 2023-04-06 08:10 | 30 | 1:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23040600026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 70 | 2023-04-06 | 2100 | keep | 0 | Apr | 2023 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-04-06 07:07 | 2023-04-06 12:30 | 20 | 5:23 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040600022 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 323 | 2023-04-06 | 6460 | keep | 0 | Apr | 2023 | 0.0043999 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-04-06 07:19 | 2023-04-06 15:40 | 125 | 8:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR Y SE CERRO PUENTE PRIMARIO | M23040600026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 501 | 2023-04-06 | 62625 | keep | 0 | Apr | 2023 | 0.042654 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
ARECIBO | 2023-04-06 07:19 | 2023-04-06 12:30 | 5 | 5:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO BAJANTE DE LINEA A CAJA | A23040600025 | New_Event | Primary Wire Break | Include | Include | Equipment | 311 | 2023-04-06 | 1555 | keep | 0 | Apr | 2023 | 0.0010591 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-04-06 07:22 | 2023-04-06 12:50 | 50 | 5:28 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2023-04-06 | 16400 | keep | 0 | Apr | 2023 | 0.01117 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-06 07:27 | 2023-04-06 08:20 | 15 | 0:53 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR CULEBRA | B23040600067 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-04-06 | 795 | keep | 0 | Apr | 2023 | 0.00054147 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-06 07:27 | 2023-04-06 10:45 | 10 | 3:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO CONECTORES SECUNDARIOS | B23040600068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 198 | 2023-04-06 | 1980 | keep | 0 | Apr | 2023 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-06 07:28 | 2023-04-06 09:29 | 10 | 2:01 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | B23040600070 | New_Event | Animals | Include | Include | Wildlife | 121 | 2023-04-06 | 1210 | keep | 0 | Apr | 2023 | 0.00082413 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-04-06 07:33 | 2023-04-06 15:30 | 12 | 7:57 | P | TRANSFORMADOR AVERIADO | SE INSTALO 150 PIES DE SECUNDARIA EN OTRO XMR YA QUE HAY XMR AVERIADO | P23040600032 | New_Event | Service Transformer Failure | Include | Include | Equipment | 477 | 2023-04-06 | 5724 | keep | 0 | Apr | 2023 | 0.0038986 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-04-06 07:33 | 2023-04-06 07:34 | 1047 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23040600032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1047 | keep | 0 | Apr | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
YAUCO | 2023-04-06 07:37 | 2023-04-07 11:03 | 125 | 27:26 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 Y 2 X 50 EN CORTES DE LINEA SE REPARO PUENTE PRIMARIO | M23040600033 | New_Event | Primary Wire Break | Include | Include | Equipment | 1646 | 2023-04-06 | 205750 | keep | 0 | Apr | 2023 | 0.14014 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
GUAYAMA | 2023-04-06 07:41 | 2023-04-06 12:52 | 6 | 5:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REMPLAZO CAJA EN XMR | P23040600036 | New_Event | Cutout Failure | Include | Include | Equipment | 311 | 2023-04-06 | 1866 | keep | 0 | Apr | 2023 | 0.0012709 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-06 07:54 | 2023-04-06 07:55 | 1835 | 0:01 | T | ANIMAL | RECIERRE | C23040600007 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-06 | 1835 | keep | 0 | Apr | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2023-04-06 07:55 | 2023-04-06 10:25 | 80 | 2:30 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C23040600008 | 1st_after_momentary | Animals | Include | Include | Wildlife | 150 | 2023-04-06 | 12000 | keep | 0 | Apr | 2023 | 0.0081731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-04-06 07:56 | 2023-04-06 15:56 | 4 | 8:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS | B23040600077 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 480 | 2023-04-06 | 1920 | keep | 0 | Apr | 2023 | 0.0013077 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-06 08:06 | 2023-04-06 13:46 | 100 | 5:40 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO SPAN CON VOLTAGE SIN CARGA | B23040600087 | New_Event | Primary Wire Break | Include | Include | Equipment | 340 | 2023-04-06 | 34000 | keep | 0 | Apr | 2023 | 0.023157 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-06 08:08 | 2023-04-06 08:09 | 215 | 0:01 | T | DESGANCHE | DISPARO SE CERRO POR SCADA | B23040600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-06 | 215 | keep | 0 | Apr | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-04-06 08:09 | 2023-04-06 09:50 | 115 | 1:41 | P | DESGANCHE | 1 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA Y 1 X 80 EN PM DESGANCHE | B23040600091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-04-06 | 11615 | keep | 0 | Apr | 2023 | 0.0079109 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
UTUADO | 2023-04-06 08:10 | 2023-04-06 09:00 | 40 | 0:50 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23040600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-04-06 | 2000 | keep | 0 | Apr | 2023 | 0.0013622 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-06 08:18 | 2023-04-06 14:30 | 120 | 6:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23040600049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 372 | 2023-04-06 | 44640 | keep | 0 | Apr | 2023 | 0.030404 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-04-06 08:19 | 2023-04-06 15:07 | 214 | 6:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23040600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 408 | 2023-04-06 | 87312 | keep | 0 | Apr | 2023 | 0.059468 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
YAUCO | 2023-04-06 08:19 | 2023-04-06 14:38 | 25 | 6:19 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR RAYOS | M23040600048 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 379 | 2023-04-06 | 9475 | keep | 0 | Apr | 2023 | 0.0064534 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-06 08:24 | 2023-04-06 12:05 | 100 | 3:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN LA SALIDA DEL CONVERTIDOR FUERTES LLUVIA | C23040600011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 221 | 2023-04-06 | 22100 | keep | 0 | Apr | 2023 | 0.015052 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-04-06 08:25 | 2023-04-06 12:51 | 6 | 4:26 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | P23040600051 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 266 | 2023-04-06 | 1596 | keep | 0 | Apr | 2023 | 0.001087 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-06 08:29 | 2023-04-06 11:18 | 25 | 2:49 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040600055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-04-06 | 4225 | keep | 0 | Apr | 2023 | 0.0028776 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-06 08:32 | 2023-04-06 11:25 | 25 | 2:53 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23040600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-04-06 | 4325 | keep | 0 | Apr | 2023 | 0.0029457 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-04-06 08:36 | 2023-04-06 09:00 | 50 | 0:24 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P23040600017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 24 | 2023-04-06 | 1200 | keep | 0 | Apr | 2023 | 0.00081731 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-06 08:40 | 2023-04-06 08:41 | 1261 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040600014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1261 | keep | 0 | Apr | 2023 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
SAN JUAN | 2023-04-06 08:49 | 2023-04-06 09:27 | 36 | 0:38 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23040600067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2023-04-06 | 1368 | keep | 0 | Apr | 2023 | 0.00093174 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
CAGUAS | 2023-04-06 08:56 | 2023-04-06 14:49 | 249 | 5:53 | P | CONDUCTOR ROTO O ABIERTO | 2 X 200 EN CORTE DE LINEA SE CERRO PUENTE ABIERTO | C23040600017 | New_Event | Primary Wire Break | Include | Include | Equipment | 353 | 2023-04-06 | 87897 | keep | 0 | Apr | 2023 | 0.059866 | 0.00016959 | Sustained | FALSE | FALSE | Not_TMED_Event | 249
BAYAMON | 2023-04-06 09:06 | 2023-04-06 09:53 | 13 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23040600109 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-04-06 | 611 | keep | 0 | Apr | 2023 | 0.00041615 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-04-06 09:10 | 2023-04-06 10:51 | 1 | 1:41 | P | NO SE REPORTO CAUSA | 2X10 EN BANCO DE XMRS | R23040600026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2023-04-06 | 101 | keep | 0 | Apr | 2023 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-06 09:14 | 2023-04-06 17:27 | 2 | 8:13 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23040600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 493 | 2023-04-06 | 986 | keep | 0 | Apr | 2023 | 0.00067156 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-04-06 09:26 | 2023-04-06 17:10 | 1 | 7:44 | P | DESGANCHE | 2 X 10 EN BANCO DE TRANSFORMADORES SE REALIZO DESGANCHE PRIMARIO Y SE REPARO NEUTRAL PRIMARIO | R23040600033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 464 | 2023-04-06 | 464 | keep | 0 | Apr | 2023 | 0.00031603 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-06 09:26 | 2023-04-06 09:28 | 5663 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1717-02 QUE LLEVA 95% DEL 1713-05 POR 1717-02 | B23040600120 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-06 | 11326 | keep | 0 | Apr | 2023 | 0.0077141 | 0.003857 | Momentary | FALSE | FALSE | Not_TMED_Event | 5663
BAYAMON | 2023-04-06 09:26 | 2023-04-06 09:28 | 911 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA LLEVA 95% DEL 1713-05 | B23040600120 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-06 | 1822 | keep | 0 | Apr | 2023 | 0.001241 | 0.00062048 | Momentary | FALSE | FALSE | Not_TMED_Event | 911
HUMACAO | 2023-04-06 09:29 | 2023-04-06 14:58 | 1 | 5:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTE DE LINEA SE REEMPLAZARON CAJAS QUEMADAS | C23040600031 | New_Event | Cutout Failure | Include | Include | Equipment | 329 | 2023-04-06 | 329 | keep | 0 | Apr | 2023 | 0.00022408 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-06 09:36 | 2023-04-06 12:41 | 2450 | 3:05 | S | ANIMAL | SE REMPLAZO LAS CAJAS DE LA MEDICION REMOTA QUEMADAS EN CRUCE X AVE Y SE REPUSO 3 X 125 S/S | C23040600038 | New_Event | Animals | Include | Include | Wildlife | 185 | 2023-04-06 | 453250 | keep | 0 | Apr | 2023 | 0.30871 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-04-06 09:36 | 2023-04-06 12:41 | 640 | 3:05 | S | ANIMAL | SE REMPLAZO LAS CAJAS DE LA MEDICION REMOTA QUEMADAS EN CRUCE X AVE Y SE REPUSO 3 X 125 S/S | C23040600038 | New_Event | Animals | Include | Include | Wildlife | 185 | 2023-04-06 | 118400 | keep | 0 | Apr | 2023 | 0.080642 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
MAYAGÃœEZ | 2023-04-06 09:39 | 2023-04-06 09:40 | 2713 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR | M23040600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-06 | 2713 | keep | 0 | Apr | 2023 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
BAYAMON | 2023-04-06 09:40 | 2023-04-06 09:41 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 3871 | keep | 0 | Apr | 2023 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
MAYAGÃœEZ | 2023-04-06 09:40 | 2023-04-06 12:25 | 75 | 2:45 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | M23040600090 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-04-06 | 12375 | keep | 0 | Apr | 2023 | 0.0084286 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-04-06 09:42 | 2023-04-06 14:20 | 200 | 4:38 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA POR RAYOS | M23040600079 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 278 | 2023-04-06 | 55600 | keep | 0 | Apr | 2023 | 0.037869 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-06 09:45 | 2023-04-06 09:46 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304060000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 3871 | keep | 0 | Apr | 2023 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
CAGUAS | 2023-04-06 09:50 | 2023-04-06 11:05 | 43 | 1:15 | P | ANIMAL | 1 X 40 EN C/L CRUCE X REPTIL | C23040600043 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-04-06 | 3225 | keep | 0 | Apr | 2023 | 0.0021965 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
MAYAGÃœEZ | 2023-04-06 09:50 | 2023-04-06 11:00 | 5 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23040600046 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-04-06 | 350 | keep | 0 | Apr | 2023 | 0.00023838 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-04-06 09:50 | 2023-04-06 15:00 | 4 | 5:10 | P | DESGANCHE | 3 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040600099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-04-06 | 1240 | keep | 0 | Apr | 2023 | 0.00084456 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-04-06 09:50 | 2023-04-06 09:51 | 215 | 0:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23040600132 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-06 | 215 | keep | 0 | Apr | 2023 | 0.00014644 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-06 09:51 | 2023-04-06 10:40 | 115 | 0:49 | P | DESGANCHE | 1 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA Y 1 X 80 EN PM DESGANCHE | B23040600091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 49 | 2023-04-06 | 5635 | keep | 0 | Apr | 2023 | 0.003838 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CAGUAS | 2023-04-06 09:52 | 2023-04-06 09:53 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040600045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1709 | keep | 0 | Apr | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2023-04-06 09:53 | 2023-04-06 09:54 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040600049 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1709 | keep | 0 | Apr | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
BARRANQUITAS | 2023-04-06 09:53 | 2023-04-06 11:19 | 10 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23040600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-04-06 | 860 | keep | 0 | Apr | 2023 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-06 09:54 | 2023-04-06 14:55 | 80 | 5:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23040600102 | New_Event | Cutout Failure | Include | Include | Equipment | 301 | 2023-04-06 | 24080 | keep | 0 | Apr | 2023 | 0.016401 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-04-06 10:03 | 2023-04-06 10:04 | 1843 | 0:01 | T | DESGANCHE | RECIERRE | C23040600053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-06 | 1843 | keep | 0 | Apr | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
SAN JUAN | 2023-04-06 10:04 | 2023-04-06 13:31 | 27 | 3:27 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHE Y SE REPARO SECUNDARIA | S23040600088 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 207 | 2023-04-06 | 5589 | keep | 0 | Apr | 2023 | 0.0038066 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BARRANQUITAS | 2023-04-06 10:04 | 2023-04-06 12:02 | 40 | 1:58 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHO Y ELIMINO PARARRAYO VACANTE CRUZADO Y REMPLAZO AISLADOR | C23040600005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-04-06 | 4720 | keep | 0 | Apr | 2023 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-06 10:07 | 2023-04-06 12:45 | 100 | 2:38 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040600114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 158 | 2023-04-06 | 15800 | keep | 0 | Apr | 2023 | 0.010761 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-04-06 10:13 | 2023-04-06 13:11 | 50 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C23040600064 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-04-06 | 8900 | keep | 0 | Apr | 2023 | 0.0060617 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-06 10:14 | 2023-04-06 12:00 | 25 | 1:46 | P | DESGANCHE | SE REPARO BAJANTE DE LINEA A CAJA Y DESGANCHE | B23040600144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-04-06 | 2650 | keep | 0 | Apr | 2023 | 0.0018049 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-06 10:18 | 2023-04-06 10:19 | 2635 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 2635 | keep | 0 | Apr | 2023 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2023-04-06 10:21 | 2023-04-06 13:50 | 30 | 3:29 | P | CAUSAS EXTERNAS | 1 X 30 EN C/L CRUCE X CARPA | C23040600070 | New_Event | Damage From Public | Include | Include | Public | 209 | 2023-04-06 | 6270 | keep | 0 | Apr | 2023 | 0.0042705 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-06 10:22 | 2023-04-06 14:14 | 133 | 3:52 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTES DE LINEA | C23040600072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-04-06 | 30856 | keep | 0 | Apr | 2023 | 0.021016 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
HUMACAO | 2023-04-06 10:23 | 2023-04-06 11:29 | 50 | 1:06 | P | ANIMAL | 1 X 50 EN C/L CRUCE X REPTIL | C23040600074 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-04-06 | 3300 | keep | 0 | Apr | 2023 | 0.0022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-06 10:26 | 2023-04-06 14:12 | 25 | 3:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER 1 X 30 EN C/L LLUVIAS | B23040600147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 226 | 2023-04-06 | 5650 | keep | 0 | Apr | 2023 | 0.0038482 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-04-06 10:27 | 2023-04-06 17:36 | 12 | 7:09 | P | DESGANCHE | 1 X 50 EN RISER | R23040600043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2023-04-06 | 5148 | keep | 0 | Apr | 2023 | 0.0035063 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-04-06 10:27 | 2023-04-06 12:19 | 70 | 1:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA | C23040600077 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 112 | 2023-04-06 | 7840 | keep | 0 | Apr | 2023 | 0.0053398 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2023-04-06 10:31 | 2023-04-06 10:32 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1400 LINEA 1400 ALIMENTA RADIAL A YAUCO 1 | A23040600217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-06 | 1382 | keep | 0 | Apr | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2023-04-06 10:31 | 2023-04-06 10:32 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1400 LINEA 1400 ALIMENTA RADIAL A YAUCO 1 | A23040600217 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-06 | 654 | keep | 0 | Apr | 2023 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
BARRANQUITAS | 2023-04-06 10:33 | 2023-04-06 14:30 | 56 | 3:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23040600080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2023-04-06 | 13272 | keep | 0 | Apr | 2023 | 0.0090395 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
VEGA BAJA | 2023-04-06 10:40 | 2023-04-06 10:42 | 215 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23040600157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-06 | 430 | keep | 0 | Apr | 2023 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2023-04-06 10:40 | 2023-04-06 12:04 | 108 | 1:24 | P | DESGANCHE | 1 X50 EN C/L DESGANCHE | B23040600155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-04-06 | 9072 | keep | 0 | Apr | 2023 | 0.0061789 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
VEGA BAJA | 2023-04-06 10:42 | 2023-04-06 12:38 | 115 | 1:56 | P | DESGANCHE | 1 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA Y 1 X 80 EN PM DESGANCHE | B23040600091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-04-06 | 13340 | keep | 0 | Apr | 2023 | 0.0090858 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
BARRANQUITAS | 2023-04-06 10:43 | 2023-04-06 14:09 | 76 | 3:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUVIAS | C23040600082 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 206 | 2023-04-06 | 15656 | keep | 0 | Apr | 2023 | 0.010663 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CAGUAS | 2023-04-06 10:48 | 2023-04-06 13:26 | 1 | 2:38 | P | ANIMAL | 1 X 80 EN C/L CRUCE X REPTIL | C23040600091 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-04-06 | 158 | keep | 0 | Apr | 2023 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-06 10:48 | 2023-04-06 13:00 | 100 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN RISER | P23040600103 | New_Event | Primary Wire Break | Include | Include | Equipment | 132 | 2023-04-06 | 13200 | keep | 0 | Apr | 2023 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-06 10:48 | 2023-04-06 12:53 | 153 | 2:05 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | B23040600163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-04-06 | 19125 | keep | 0 | Apr | 2023 | 0.013026 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
UTUADO | 2023-04-06 10:50 | 2023-04-06 14:00 | 60 | 3:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23040600150 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 190 | 2023-04-06 | 11400 | keep | 0 | Apr | 2023 | 0.0077645 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-04-06 10:51 | 2023-04-06 10:52 | 1952 | 0:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSA | P23040600111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1952 | keep | 0 | Apr | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
PONCE | 2023-04-06 10:51 | 2023-04-06 10:52 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | NO SE REPORTO CAUSA | P23040600110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 2113 | keep | 0 | Apr | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
VEGA BAJA | 2023-04-06 10:51 | 2023-04-06 20:20 | 100 | 9:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23040600148 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 569 | 2023-04-06 | 56900 | keep | 0 | Apr | 2023 | 0.038754 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-06 10:53 | 2023-04-06 20:00 | 15 | 9:07 | P | SECUNDARIA/OTROS | SE ABRE MONTURA DE TRANSFORMADOR PARA REPARA SECUNDARIAS | M23040600121 | New_Event |  |  |  |  | 547 | 2023-04-06 | 8205 | keep | 0 | Apr | 2023 | 0.0055884 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-04-06 11:04 | 2023-04-06 12:15 | 10 | 1:11 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23040600128 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 71 | 2023-04-06 | 710 | keep | 0 | Apr | 2023 | 0.00048358 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-06 11:05 | 2023-04-06 12:23 | 80 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 140 DE RISER @ SU-C | R23040600050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2023-04-06 | 6240 | keep | 0 | Apr | 2023 | 0.00425 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-04-06 11:05 | 2023-04-06 11:30 | 8 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23040600163 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-04-06 | 200 | keep | 0 | Apr | 2023 | 0.00013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-04-06 11:06 | 2023-04-06 13:51 | 100 | 2:45 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23040600119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-04-06 | 16500 | keep | 0 | Apr | 2023 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-04-06 11:08 | 2023-04-06 18:00 | 50 | 6:52 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23040600120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2023-04-06 | 20600 | keep | 0 | Apr | 2023 | 0.014031 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-04-06 11:09 | 2023-04-06 17:58 | 100 | 6:49 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | P23040600122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 409 | 2023-04-06 | 40900 | keep | 0 | Apr | 2023 | 0.027857 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-04-06 11:09 | 2023-04-06 13:45 | 882 | 2:36 | T | DESGANCHE | SE CERRO INTERRUPTOR SE DEJO CORTE DE LINEA ABIERTO PARA REALIZAR DESGANCHE | A23040600169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-04-06 | 137592 | keep | 0 | Apr | 2023 | 0.093713 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
AGUADILLA | 2023-04-06 11:11 | 2023-04-06 13:30 | 60 | 2:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040600132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-04-06 | 8340 | keep | 0 | Apr | 2023 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-04-06 11:15 | 2023-04-06 11:32 | 5 | 0:17 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23040600133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 17 | 2023-04-06 | 85 | keep | 0 | Apr | 2023 | 5.7893e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-04-06 11:18 | 2023-04-06 13:55 | 100 | 2:37 | P | MAL TIEMPO/RAYOS | 2 X 100 EN C/L MAL TIEMPO RAYOS | P23040600139 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 157 | 2023-04-06 | 15700 | keep | 0 | Apr | 2023 | 0.010693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-04-06 11:18 | 2023-04-06 21:05 | 15 | 9:47 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A23040600184 | New_Event | Primary Wire Break | Include | Include | Equipment | 587 | 2023-04-06 | 8805 | keep | 0 | Apr | 2023 | 0.005997 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-06 11:21 | 2023-04-06 13:27 | 1 | 2:06 | P | DESGANCHE | 1 X 80 EN C/L | C23040600143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-04-06 | 126 | keep | 0 | Apr | 2023 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-06 11:24 | 2023-04-06 14:39 | 1 | 3:15 | P | SECUNDARIA/DESGANCHE | 2 X 15 EN EN BANCO Y DESGANCHE SECUNDARIO | S23040600099 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 195 | 2023-04-06 | 195 | keep | 0 | Apr | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-04-06 11:24 | 2023-04-06 11:25 | 1830 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 2201-04 LLEVA LA CARGA DEL 2201-02 | R23040600059 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-06 | 1830 | keep | 0 | Apr | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-04-06 11:24 | 2023-04-06 11:25 | 1197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 2201-04 LLEVA LA CARGA DEL 2201-02 | R23040600059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1197 | keep | 0 | Apr | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
FAJARDO | 2023-04-06 11:28 | 2023-04-06 12:03 | 1830 | 0:35 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR CARGA POR EL 2201-04 SE SECCIONALIZO MACHETES QUEMADO EN SERVICIO 50% SJ-230406-52 | R23040600061 | New_Event | Switch Failure | Include | Include | Equipment | 35 | 2023-04-06 | 64050 | keep | 0 | Apr | 2023 | 0.043624 | 0.0012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-04-06 11:28 | 2023-04-06 12:03 | 1197 | 0:35 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 2201-04 LLEVA LA CARGA DEL 2201-02 SE SECCIONALIZO MACHETES QUEMADOS, 2201-02 50% EN SERVICIO | R23040600061 | New_Event | Feeder Load Transferred | Include | Include | Other | 35 | 2023-04-06 | 41895 | keep | 0 | Apr | 2023 | 0.028534 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
YAUCO | 2023-04-06 11:28 | 2023-04-06 17:00 | 100 | 5:32 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | P23040600150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 332 | 2023-04-06 | 33200 | keep | 0 | Apr | 2023 | 0.022612 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-06 11:28 | 2023-04-06 15:11 | 74 | 3:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 40 EN C/L Y SE REPARO SECUNDARIA | B23040600175 | New_Event | Secondary Wire Break | Include | Include | Equipment | 223 | 2023-04-06 | 16502 | keep | 0 | Apr | 2023 | 0.011239 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
MAYAGÃœEZ | 2023-04-06 11:31 | 2023-04-06 11:32 | 281 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1400 LINEA 1400 ALIMENTA RADIAL A YAUCO 1 | M23040600139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-06 | 281 | keep | 0 | Apr | 2023 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2023-04-06 11:31 | 2023-04-06 11:32 | 1252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1400 LINEA 1400 ALIMENTA RADIAL A YAUCO 1 | M23040600139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-06 | 1252 | keep | 0 | Apr | 2023 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2023-04-06 11:31 | 2023-04-06 11:32 | 595 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1400 LINEA 1400 ALIMENTA RADIAL A YAUCO 1 | M23040600141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-06 | 595 | keep | 0 | Apr | 2023 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2023-04-06 11:31 | 2023-04-06 11:32 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1400 LINEA 1400 ALIMENTA RADIAL A YAUCO 1 | M23040600141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-06 | 51 | keep | 0 | Apr | 2023 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2023-04-06 11:31 | 2023-04-06 11:32 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1400 LINEA 1400 ALIMENTA RADIAL A YAUCO 1 | M23040600141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-06 | 721 | keep | 0 | Apr | 2023 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
YAUCO | 2023-04-06 11:32 | 2023-04-06 19:32 | 40 | 8:00 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23040600155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2023-04-06 | 19200 | keep | 0 | Apr | 2023 | 0.013077 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-06 11:33 | 2023-04-06 13:44 | 25 | 2:11 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y SDESGANCHE SECUNDARIO | B23040600182 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 131 | 2023-04-06 | 3275 | keep | 0 | Apr | 2023 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-04-06 11:33 | 2023-04-06 17:00 | 40 | 5:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | P23040600156 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 327 | 2023-04-06 | 13080 | keep | 0 | Apr | 2023 | 0.0089087 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-04-06 11:34 | 2023-04-06 11:35 | 1475 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | P23040600157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-06 | 1475 | keep | 0 | Apr | 2023 | 0.0010046 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
BAYAMON | 2023-04-06 11:35 | 2023-04-06 13:06 | 50 | 1:31 | P | DESGANCHE | DESGANCHE Y 1 X 65 EN C/L | S23040600102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-04-06 | 4550 | keep | 0 | Apr | 2023 | 0.003099 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-04-06 11:35 | 2023-04-06 13:46 | 50 | 2:11 | P | MAL TIEMPO/RAYOS | 2 X 65 EN C/L MAL TIEMPO RAYOS | P23040600175 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 131 | 2023-04-06 | 6550 | keep | 0 | Apr | 2023 | 0.0044612 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-04-06 11:38 | 2023-04-06 13:00 | 6 | 1:22 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23040600142 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 82 | 2023-04-06 | 492 | keep | 0 | Apr | 2023 | 0.0003351 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-04-06 11:40 | 2023-04-06 16:38 | 50 | 4:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | P23040600160 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 298 | 2023-04-06 | 14900 | keep | 0 | Apr | 2023 | 0.010148 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-04-06 11:54 | 2023-04-06 14:40 | 30 | 2:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040600242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-04-06 | 4980 | keep | 0 | Apr | 2023 | 0.0033919 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-06 11:57 | 2023-04-06 13:35 | 10 | 1:38 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN C/L LINEAS SE CRUZARON | S23040600108 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 98 | 2023-04-06 | 980 | keep | 0 | Apr | 2023 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-04-06 11:57 | 2023-04-07 11:51 | 41 | 23:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | P23040600182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1434 | 2023-04-06 | 58794 | keep | 0 | Apr | 2023 | 0.040044 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
MAYAGÃœEZ | 2023-04-06 11:57 | 2023-04-06 11:59 | 1117 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M23040600151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
MAYAGÃœEZ | 2023-04-06 11:57 | 2023-04-06 11:59 | 1671 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M23040600151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 3342 | keep | 0 | Apr | 2023 | 0.0022762 | 0.0011381 | Momentary | FALSE | FALSE | Not_TMED_Event | 1671
MAYAGÃœEZ | 2023-04-06 11:57 | 2023-04-06 11:59 | 527 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M23040600151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 1054 | keep | 0 | Apr | 2023 | 0.00071787 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2023-04-06 11:57 | 2023-04-06 11:59 | 671 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1200 | M23040600151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-06 | 1342 | keep | 0 | Apr | 2023 | 0.00091403 | 0.00045702 | Momentary | FALSE | FALSE | Not_TMED_Event | 671
UTUADO | 2023-04-06 11:57 | 2023-04-06 14:50 | 40 | 2:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040600244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-04-06 | 6920 | keep | 0 | Apr | 2023 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-06 12:02 | 2023-04-06 12:30 | 35 | 0:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | A23040600248 | New_Event | Primary Wire Break | Include | Include | Equipment | 28 | 2023-04-06 | 980 | keep | 0 | Apr | 2023 | 0.00066747 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2023-04-06 12:03 | 2023-04-06 12:36 | 915 | 0:33 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETES QUEMADOS Y SE CERRO N/O DEL 2201-02 CON EL 2201-04 85% EN SERVICIO SJ-230406-52 | R23040600061 | Partial_restoration | Switch Failure | Include | Include | Equipment | 33 | 2023-04-06 | 30195 | keep | 0 | Apr | 2023 | 0.020566 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-06 12:09 | 2023-04-06 13:40 | 1 | 1:31 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER HACIA TRANSFORMADOR PRIVADO | R23040600108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2023-04-06 | 91 | keep | 0 | Apr | 2023 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-06 12:09 | 2023-04-06 12:12 | 4381 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE REALIZO PRUEBA Y QUEDO EN SERVICIO | M23040600169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2023-04-06 | 13143 | keep | 0 | Apr | 2023 | 0.0089516 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
YAUCO | 2023-04-06 12:11 | 2023-04-06 19:36 | 70 | 7:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L MAL TIEMPO LLUVIAS | P23040600190 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 445 | 2023-04-06 | 31150 | keep | 0 | Apr | 2023 | 0.021216 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-04-06 12:12 | 2023-04-06 16:40 | 200 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN CORTE DE LINEA POR MAL TIEMPO | M23040600305 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-04-06 | 53600 | keep | 0 | Apr | 2023 | 0.036507 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-04-06 12:15 | 2023-04-06 14:19 | 50 | 2:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE DE ARBOL | M23040600185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-04-06 | 6200 | keep | 0 | Apr | 2023 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-04-06 12:18 | 2023-04-06 15:23 | 250 | 3:05 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | P23040600193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-04-06 | 46250 | keep | 0 | Apr | 2023 | 0.031501 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-04-06 12:22 | 2023-04-06 13:00 | 5 | 0:38 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | B23040600205 | New_Event | Primary Wire Break | Include | Include | Equipment | 38 | 2023-04-06 | 190 | keep | 0 | Apr | 2023 | 0.00012941 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-04-06 12:27 | 2023-04-06 14:52 | 3 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO QUEMADO | C23040600134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-04-06 | 435 | keep | 0 | Apr | 2023 | 0.00029628 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-04-06 12:36 | 2023-04-06 17:55 | 137 | 5:19 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO 6 MACHETES QUEMADOS Y PARARRAYOS 100% EN SERVICIO SJ-230406-52 | R23040600061 | Partial_restoration | Switch Failure | Include | Include | Equipment | 319 | 2023-04-06 | 43703 | keep | 0 | Apr | 2023 | 0.029766 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-04-06 12:41 | 2023-04-06 14:49 | 100 | 2:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23040600273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-04-06 | 12800 | keep | 0 | Apr | 2023 | 0.008718 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-04-06 12:44 | 2023-04-06 17:12 | 250 | 4:28 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA | C23040600140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-04-06 | 67000 | keep | 0 | Apr | 2023 | 0.045633 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-04-06 12:44 | 2023-04-06 12:50 | 6 | 0:06 | P | MAL TIEMPO/LLUVIA O VIENTO | MAL TIEMPO LLUVIAS 1 X 15 EN XMR | B23040600215 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 6 | 2023-04-06 | 36 | keep | 0 | Apr | 2023 | 2.4519e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-04-06 12:45 | 2023-04-06 15:40 | 50 | 2:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23040600231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-04-06 | 8750 | keep | 0 | Apr | 2023 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-04-06 12:47 | 2023-04-06 14:38 | 25 | 1:51 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR RAYO | M23040600292 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 111 | 2023-04-06 | 2775 | keep | 0 | Apr | 2023 | 0.00189 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-06 12:50 | 2023-04-06 12:51 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO 50% POR 1909-07 | B2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 766 | keep | 0 | Apr | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
UTUADO | 2023-04-06 12:50 | 2023-04-06 14:53 | 18 | 2:03 | P | CONDUCTOR ARRIADO O CRUZADO | CERRAR CORTE DE LINEA ABIERTO DE EMERGENCIA LINEAS CRUZADAS | A23040600300 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 123 | 2023-04-06 | 2214 | keep | 0 | Apr | 2023 | 0.0015079 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2023-04-06 13:02 | 2023-04-06 16:25 | 50 | 3:23 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040600289 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 203 | 2023-04-06 | 10150 | keep | 0 | Apr | 2023 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-06 13:03 | 2023-04-06 13:04 | 302 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 302 | keep | 0 | Apr | 2023 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
GUAYAMA | 2023-04-06 13:03 | 2023-04-06 16:41 | 15 | 3:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR | P23040600247 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 218 | 2023-04-06 | 3270 | keep | 0 | Apr | 2023 | 0.0022272 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-06 13:06 | 2023-04-06 13:07 | 302 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2304060000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 302 | keep | 0 | Apr | 2023 | 0.00020569 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2023-04-06 13:08 | 2023-04-06 14:27 | 302 | 1:19 | T | NO SE REPORTO CAUSA | SE CERRO POR PARTES QUEDO 100% EN SERVICIO NO SE ENCONTRO CAUSA BY-230406-01 | B23040600232 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 79 | 2023-04-06 | 23858 | keep | 0 | Apr | 2023 | 0.01625 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
SAN JUAN | 2023-04-06 13:11 | 2023-04-06 14:56 | 1187 | 1:45 | P | DESGANCHE | DISPARO PB-3 SE ABRIO MACHETE PARA SECCIONALIZAR Y DISPARO BKR. | S23040600117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-04-06 | 124635 | keep | 0 | Apr | 2023 | 0.084888 | 0.00080846 | Sustained | FALSE | FALSE | Not_TMED_Event | 1187
YAUCO | 2023-04-06 13:20 | 2023-04-06 17:26 | 50 | 4:06 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | P23040600260 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 246 | 2023-04-06 | 12300 | keep | 0 | Apr | 2023 | 0.0083775 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-04-06 13:25 | 2023-04-06 14:45 | 16 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REPARAR SOTERRADO SECUNDARIA AVERIADA | A23040600091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-04-06 | 1280 | keep | 0 | Apr | 2023 | 0.0008718 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-04-06 13:32 | 2023-04-06 17:47 | 80 | 4:15 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA POR RAYOS | M23040600365 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 255 | 2023-04-06 | 20400 | keep | 0 | Apr | 2023 | 0.013894 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-04-06 13:33 | 2023-04-06 14:26 | 1 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | REPARAR BAJANTE DE RISER | M23040600367 | New_Event | Primary Wire Break | Include | Include | Equipment | 53 | 2023-04-06 | 53 | keep | 0 | Apr | 2023 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-06 13:36 | 2023-04-06 16:01 | 90 | 2:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA POR MAL TIEMPO | M23040600369 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 145 | 2023-04-06 | 13050 | keep | 0 | Apr | 2023 | 0.0088883 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
UTUADO | 2023-04-06 13:45 | 2023-04-06 19:15 | 25 | 5:30 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO CORTE DE LINEA | A23040600323 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 330 | 2023-04-06 | 8250 | keep | 0 | Apr | 2023 | 0.005619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-06 13:57 | 2023-04-06 13:59 | 726 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 1346-04 | S2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-06 | 1452 | keep | 0 | Apr | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-04-06 13:57 | 2023-04-06 13:59 | 3932 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL CARGA X 1303-03 | S2304060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-06 | 7864 | keep | 0 | Apr | 2023 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
MAYAGÃœEZ | 2023-04-06 14:00 | 2023-04-06 15:50 | 30 | 1:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE CORTE DE LINEA Y SE REEMPLAZO POSTE PRIMARIO | M23040600397 | New_Event | Primary Pole Failure | Include | Include | Equipment | 110 | 2023-04-06 | 3300 | keep | 0 | Apr | 2023 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-06 14:12 | 2023-04-06 14:13 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
SAN JUAN | 2023-04-06 14:13 | 2023-04-06 14:44 | 255 | 0:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 CABLE SOTERRADO AVERIADO | S23040600186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2023-04-06 | 7905 | keep | 0 | Apr | 2023 | 0.0053841 | 0.00017368 | Sustained | FALSE | FALSE | Not_TMED_Event | 255
SAN JUAN | 2023-04-06 14:13 | 2023-04-06 14:44 | 928 | 0:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 CABLE SOTERRADO AVERIADO | S23040600186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2023-04-06 | 28768 | keep | 0 | Apr | 2023 | 0.019594 | 0.00063206 | Sustained | FALSE | FALSE | Not_TMED_Event | 928
SAN JUAN | 2023-04-06 14:13 | 2023-04-06 14:44 | 200 | 0:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 CABLE SOTERRADO AVERIADO | S23040600186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2023-04-06 | 6200 | keep | 0 | Apr | 2023 | 0.0042228 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-04-06 14:13 | 2023-04-06 14:44 | 185 | 0:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 CABLE SOTERRADO AVERIADO | S23040600186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2023-04-06 | 5735 | keep | 0 | Apr | 2023 | 0.0039061 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
SAN JUAN | 2023-04-06 14:13 | 2023-04-06 14:44 | 73 | 0:31 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6600 CABLE SOTERRADO AVERIADO | S23040600186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 31 | 2023-04-06 | 2263 | keep | 0 | Apr | 2023 | 0.0015413 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
BAYAMON | 2023-04-06 14:14 | 2023-04-06 16:34 | 114 | 2:20 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L SE RETEZO LINEA | B23040600262 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 140 | 2023-04-06 | 15960 | keep | 0 | Apr | 2023 | 0.01087 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
HUMACAO | 2023-04-06 14:16 | 2023-04-06 14:17 | 3833 | 0:01 | T | DESGANCHE | RECIERRE | C23040600167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-06 | 3833 | keep | 0 | Apr | 2023 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2023-04-06 14:17 | 2023-04-06 16:35 | 400 | 2:18 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA | C23040600176 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-04-06 | 55200 | keep | 0 | Apr | 2023 | 0.037596 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-04-06 14:36 | 2023-04-06 16:07 | 60 | 1:31 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23040600273 | New_Event | Animals | Include | Include | Wildlife | 91 | 2023-04-06 | 5460 | keep | 0 | Apr | 2023 | 0.0037188 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-04-06 14:38 | 2023-04-06 17:25 | 500 | 2:47 | P | MAL TIEMPO/RAYOS | 3 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040600340 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 167 | 2023-04-06 | 83500 | keep | 0 | Apr | 2023 | 0.056871 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BARRANQUITAS | 2023-04-06 14:43 | 2023-04-06 16:46 | 53 | 2:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIAS | C23040600183 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 123 | 2023-04-06 | 6519 | keep | 0 | Apr | 2023 | 0.0044401 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2023-04-06 14:56 | 2023-04-06 15:35 | 3957 | 0:39 | T | DESGANCHE | DISPARO ALIMENTADOR AL CERRAR PB-3 SE ABRIO DE NUEVO Y SE CERRO INTERRUPTOR 20% EN SERVICIO | S23040600117 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 39 | 2023-04-06 | 154323 | keep | 0 | Apr | 2023 | 0.10511 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-06 14:56 | 2023-04-06 15:15 | 10 | 0:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN TRANSFORMADOR | A23040600342 | New_Event | Primary Wire Break | Include | Include | Equipment | 19 | 2023-04-06 | 190 | keep | 0 | Apr | 2023 | 0.00012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-06 15:00 | 2023-04-06 15:58 | 33 | 0:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO PUENTE Y SE REMPLAZO CAJA PRIMARIA | S23040600211 | New_Event | Cutout Failure | Include | Include | Equipment | 58 | 2023-04-06 | 1914 | keep | 0 | Apr | 2023 | 0.0013036 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2023-04-06 15:21 | 2023-04-06 17:01 | 30 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M23040600505 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2023-04-06 | 3000 | keep | 0 | Apr | 2023 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-04-06 15:23 | 2023-04-06 18:20 | 250 | 2:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040600347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2023-04-06 | 44250 | keep | 0 | Apr | 2023 | 0.030138 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2023-04-06 15:25 | 2023-04-06 16:16 | 4 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BARRA EN PEDESTAL | R23040600121 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2023-04-06 | 204 | keep | 0 | Apr | 2023 | 0.00013894 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-06 15:35 | 2023-04-06 15:44 | 3165 | 0:09 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETE Y PB-3 100% EN SERVICIO | S23040600117 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 9 | 2023-04-06 | 28485 | keep | 0 | Apr | 2023 | 0.019401 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-06 15:42 | 2023-04-06 17:35 | 150 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN C/L MAL TIEMPO LLUVIAS | B23040600304 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2023-04-06 | 16950 | keep | 0 | Apr | 2023 | 0.011545 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-06 15:42 | 2023-04-06 17:05 | 1 | 1:23 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | B23040600303 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2023-04-06 | 83 | keep | 0 | Apr | 2023 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-06 15:48 | 2023-04-06 15:49 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1909-09 | B2304060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-06 15:48 | 2023-04-06 15:49 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR CARGA POR EL 1907-03 | B2304060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-06 | 4456 | keep | 0 | Apr | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
VEGA BAJA | 2023-04-06 15:48 | 2023-04-06 18:18 | 8 | 2:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR LLUVIAS | B23040600309 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 150 | 2023-04-06 | 1200 | keep | 0 | Apr | 2023 | 0.00081731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-04-06 15:56 | 2023-04-06 16:51 | 100 | 0:55 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE | R23040600144 | New_Event | Animals | Include | Include | Wildlife | 55 | 2023-04-06 | 5500 | keep | 0 | Apr | 2023 | 0.003746 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-04-06 15:57 | 2023-04-06 17:42 | 50 | 1:45 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C23040600206 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-04-06 | 5250 | keep | 0 | Apr | 2023 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-04-06 16:09 | 2023-04-07 15:10 | 14 | 23:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE TANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | A23040600361 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1381 | 2023-04-06 | 19334 | keep | 0 | Apr | 2023 | 0.013168 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-04-06 16:23 | 2023-04-06 16:24 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040600218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-06 | 1271 | keep | 0 | Apr | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
SAN JUAN | 2023-04-06 16:30 | 2023-04-06 19:00 | 8 | 2:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA LEVANTAR SECUNDARIA | S23040600266 | New_Event | Secondary Wire Break | Include | Include | Equipment | 150 | 2023-04-06 | 1200 | keep | 0 | Apr | 2023 | 0.00081731 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-04-06 16:42 | 2023-04-07 10:55 | 15 | 18:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | M23040600595 | New_Event | Cutout Failure | Include | Include | Equipment | 1093 | 2023-04-06 | 16395 | keep | 0 | Apr | 2023 | 0.011167 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-06 16:44 | 2023-04-06 20:07 | 50 | 3:23 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23040600231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-04-06 | 10150 | keep | 0 | Apr | 2023 | 0.0069131 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-06 16:51 | 2023-04-06 19:26 | 7 | 2:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO VIENTO | S23040600234 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 155 | 2023-04-06 | 1085 | keep | 0 | Apr | 2023 | 0.00073899 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-04-06 16:53 | 2023-04-06 20:50 | 2952 | 3:57 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR SIN RTU | M23040600611 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 237 | 2023-04-06 | 699624 | keep | 0 | Apr | 2023 | 0.47651 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
PONCE | 2023-04-06 17:00 | 2023-04-06 18:56 | 56 | 1:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN C/L SE REMPLAZO AISLADOR | P23040600349 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 116 | 2023-04-06 | 6496 | keep | 0 | Apr | 2023 | 0.0044244 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
MAYAGÃœEZ | 2023-04-06 17:07 | 2023-04-06 17:44 | 100 | 0:37 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA POR MAL TIEMPO RAYOS | M23040600628 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 37 | 2023-04-06 | 3700 | keep | 0 | Apr | 2023 | 0.0025201 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-04-06 17:11 | 2023-04-06 17:36 | 20 | 0:25 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M23040600630 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 25 | 2023-04-06 | 500 | keep | 0 | Apr | 2023 | 0.00034055 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 396 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2772 | keep | 0 | Apr | 2023 | 0.001888 | 0.00026971 | Sustained | FALSE | FALSE | Not_TMED_Event | 396
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 119 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 833 | keep | 0 | Apr | 2023 | 0.00056735 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 290 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2030 | keep | 0 | Apr | 2023 | 0.0013826 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 390 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2730 | keep | 0 | Apr | 2023 | 0.0018594 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 719 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 5033 | keep | 0 | Apr | 2023 | 0.003428 | 0.00048971 | Sustained | FALSE | FALSE | Not_TMED_Event | 719
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 67 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 469 | keep | 0 | Apr | 2023 | 0.00031943 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 1 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 7 | keep | 0 | Apr | 2023 | 4.7677e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 275 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 1925 | keep | 0 | Apr | 2023 | 0.0013111 | 0.0001873 | Sustained | FALSE | FALSE | Not_TMED_Event | 275
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 142 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 994 | keep | 0 | Apr | 2023 | 0.00067701 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 45 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600281 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 315 | keep | 0 | Apr | 2023 | 0.00021455 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 93 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE CERRO POR CONTROL BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600287 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 651 | keep | 0 | Apr | 2023 | 0.00044339 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 418 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE CERRO POR CONTROL BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600287 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2926 | keep | 0 | Apr | 2023 | 0.0019929 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 295 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE CERRO POR CONTROL BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600287 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2065 | keep | 0 | Apr | 2023 | 0.0014065 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 948 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE CERRO POR CONTROL BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600287 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 6636 | keep | 0 | Apr | 2023 | 0.0045197 | 0.00064568 | Sustained | FALSE | FALSE | Not_TMED_Event | 948
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 350 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S2304060000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2450 | keep | 0 | Apr | 2023 | 0.0016687 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 215 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S2304060000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 1505 | keep | 0 | Apr | 2023 | 0.001025 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 262 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S2304060000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 1834 | keep | 0 | Apr | 2023 | 0.0012491 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 90 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE 1100-05 LLEVA 1102-02,03,05 BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S2304060000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 630 | keep | 0 | Apr | 2023 | 0.00042909 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 171 | 0:07 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE CERRO POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 1197 | keep | 0 | Apr | 2023 | 0.00081527 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 1837 | 0:07 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE CERRO POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 12859 | keep | 0 | Apr | 2023 | 0.0087582 | 0.0012512 | Sustained | FALSE | FALSE | Not_TMED_Event | 1837
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 600 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE ENERGIZO NUEVAMENTE PARTE DEL 1105-01 POR 1113-03 BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600275 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 4200 | keep | 0 | Apr | 2023 | 0.0028606 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 308 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE ENERGIZO NUEVAMENTE 1105-02 LLEVA 1133-04 BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600275 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2156 | keep | 0 | Apr | 2023 | 0.0014684 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 559 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE ENERGIZO NUEVAMENTE CARGA POR 1105-05 BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600275 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 3913 | keep | 0 | Apr | 2023 | 0.0026651 | 0.00038073 | Sustained | FALSE | FALSE | Not_TMED_Event | 559
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 370 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 SE ENERGIZO NUEVAMENTE 1105-05 LLEVA 1105-04 BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600275 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2590 | keep | 0 | Apr | 2023 | 0.001764 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 218 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 1526 | keep | 0 | Apr | 2023 | 0.0010394 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 455 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 3185 | keep | 0 | Apr | 2023 | 0.0021693 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 1526 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 10682 | keep | 0 | Apr | 2023 | 0.0072755 | 0.0010394 | Sustained | FALSE | FALSE | Not_TMED_Event | 1526
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 283 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 CERRADA POR CCE BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600283 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 1981 | keep | 0 | Apr | 2023 | 0.0013493 | 0.00019275 | Sustained | FALSE | FALSE | Not_TMED_Event | 283
SAN JUAN | 2023-04-06 17:17 | 2023-04-06 17:24 | 333 | 0:07 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3300 1105-02 LLEVA 1133-04 BKR 3390 VIADUCTO NO ABRE EN DISPARO DE LINEA. DISPARA BARRA #2 38KV VIADUCTO TC. BKR 5030 MIRAMAR ABRE EN EVENTO Y SE APAGA BARRA 38KV COVADONGA. | S23040600275 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-04-06 | 2331 | keep | 0 | Apr | 2023 | 0.0015876 | 0.0002268 | Sustained | FALSE | FALSE | Not_TMED_Event | 333
PONCE | 2023-04-06 17:29 | 2023-04-06 20:23 | 50 | 2:54 | P | ANIMAL | 1 X 40 EN C/L ANIMAL CRUZO LINEAS | P23040600360 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-04-06 | 8700 | keep | 0 | Apr | 2023 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-04-06 17:36 | 2023-04-06 17:45 | 1339 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600910 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 12051 | keep | 0 | Apr | 2023 | 0.0082079 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-04-06 17:36 | 2023-04-06 17:45 | 470 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600910 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 4230 | keep | 0 | Apr | 2023 | 0.002881 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-04-06 17:36 | 2023-04-06 17:45 | 2483 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600910 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 22347 | keep | 0 | Apr | 2023 | 0.01522 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-04-06 17:36 | 2023-04-06 17:45 | 2190 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600910 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 19710 | keep | 0 | Apr | 2023 | 0.013424 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-04-06 17:36 | 2023-04-06 17:45 | 3006 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600916 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 27054 | keep | 0 | Apr | 2023 | 0.018426 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-04-06 17:36 | 2023-04-06 17:45 | 179 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600916 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 1611 | keep | 0 | Apr | 2023 | 0.0010972 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:45 | 107 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600910 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 963 | keep | 0 | Apr | 2023 | 0.00065589 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:45 | 1666 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600910 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 14994 | keep | 0 | Apr | 2023 | 0.010212 | 0.0011347 | Sustained | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:45 | 4387 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600910 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 39483 | keep | 0 | Apr | 2023 | 0.026892 | 0.002988 | Sustained | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:46 | 2073 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M23040600944 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-04-06 | 20730 | keep | 0 | Apr | 2023 | 0.014119 | 0.0014119 | Sustained | FALSE | FALSE | Not_TMED_Event | 2073
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:46 | 637 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M23040600944 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-04-06 | 6370 | keep | 0 | Apr | 2023 | 0.0043386 | 0.00043386 | Sustained | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:46 | 1491 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M23040600944 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-04-06 | 14910 | keep | 0 | Apr | 2023 | 0.010155 | 0.0010155 | Sustained | FALSE | FALSE | Not_TMED_Event | 1491
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:45 | 3147 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600917 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 28323 | keep | 0 | Apr | 2023 | 0.019291 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:45 | 4304 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13400 | M23040600917 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-04-06 | 38736 | keep | 0 | Apr | 2023 | 0.026383 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:46 | 4892 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M23040600946 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-04-06 | 48920 | keep | 0 | Apr | 2023 | 0.033319 | 0.0033319 | Sustained | FALSE | FALSE | Not_TMED_Event | 4892
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:46 | 160 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13500 | M23040600946 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-04-06 | 1600 | keep | 0 | Apr | 2023 | 0.0010898 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
MAYAGÃœEZ | 2023-04-06 17:36 | 2023-04-06 17:38 | 1097 | 0:02 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR | M23040601012 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 2 | 2023-04-06 | 2194 | keep | 0 | Apr | 2023 | 0.0014943 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-06 17:38 | 2023-04-06 18:40 | 20 | 1:02 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M23040600630 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 62 | 2023-04-06 | 1240 | keep | 0 | Apr | 2023 | 0.00084456 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-06 17:38 | 2023-04-06 17:39 | 3458 | 0:01 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR | M23040601014 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-06 | 3458 | keep | 0 | Apr | 2023 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
MAYAGÃœEZ | 2023-04-06 17:47 | 2023-04-06 17:48 | 990 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR MAL TIEMPO EN EL AREA | M23040600749 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-06 | 990 | keep | 0 | Apr | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2023-04-06 17:50 | 2023-04-06 17:51 | 990 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR MAL TIEMPO EN EL AREA | M23040600749 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-06 | 990 | keep | 0 | Apr | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2023-04-06 17:55 | 2023-04-06 19:17 | 990 | 1:22 | T | MAL TIEMPO/LLUVIA O VIENTO | SE PATRULLO Y NO SE ENCONTRO CAUSA RECIERRE DE INTERRUPTOR MAL TIEMPO EN EL AREA | M23040600749 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 82 | 2023-04-06 | 81180 | keep | 0 | Apr | 2023 | 0.055291 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
VEGA BAJA | 2023-04-06 18:05 | 2023-04-06 23:19 | 139 | 5:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS VIENTOS | B23040600342 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 314 | 2023-04-06 | 43646 | keep | 0 | Apr | 2023 | 0.029727 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
ARECIBO | 2023-04-06 18:15 | 2023-04-07 12:29 | 12 | 18:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23040600399 | New_Event | Cutout Failure | Include | Include | Equipment | 1094 | 2023-04-06 | 13128 | keep | 0 | Apr | 2023 | 0.0089414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-04-06 18:26 | 2023-04-07 01:28 | 60 | 7:02 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23040600791 | New_Event | Vegetation Contact | Include | Include | Vegetation | 422 | 2023-04-06 | 25320 | keep | 0 | Apr | 2023 | 0.017245 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-06 18:51 | 2023-04-07 08:27 | 175 | 13:36 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23040600311 | New_Event | Primary Wire Break | Include | Include | Equipment | 816 | 2023-04-06 | 142800 | keep | 0 | Apr | 2023 | 0.09726 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2023-04-06 19:01 | 2023-04-06 22:36 | 50 | 3:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEAS POR LLUVIA Y VIENTO | M23040600855 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 215 | 2023-04-06 | 10750 | keep | 0 | Apr | 2023 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-06 19:04 | 2023-04-07 00:37 | 76 | 5:33 | S | DISPARO DE BARRA DE TRANSMISION | SE TRANSFIRIO LA CARGA AL 1100-02 POR AUXILIAR DE BARRA 38KV AVERIADO SJ-230406-02 | S23040600277 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 333 | 2023-04-06 | 25308 | keep | 0 | Apr | 2023 | 0.017237 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
SAN JUAN | 2023-04-06 19:04 | 2023-04-07 00:37 | 1079 | 5:33 | S | DISPARO DE BARRA DE TRANSMISION | SE TRANSFIRIO LA CARGA AL 1100-02 POR AUXILIAR DE BARRA 38KV AVERIADO SJ-230406-02 | S23040600277 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 333 | 2023-04-06 | 359307 | keep | 0 | Apr | 2023 | 0.24472 | 0.0007349 | Sustained | FALSE | FALSE | Not_TMED_Event | 1079
UTUADO | 2023-04-06 19:13 | 2023-04-07 13:58 | 20 | 18:45 | P | MAL TIEMPO/RAYOS | 3 X 15 EN TRAMSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23040600453 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1125 | 2023-04-06 | 22500 | keep | 0 | Apr | 2023 | 0.015325 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-04-06 19:16 | 2023-04-06 20:36 | 100 | 1:20 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23040600386 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2023-04-06 | 8000 | keep | 0 | Apr | 2023 | 0.0054488 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-06 19:19 | 2023-04-06 20:12 | 6 | 0:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 Y 2 X 10 EN TRANSFORMADOR POR MAL TIEMPO | M23040600881 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 53 | 2023-04-06 | 318 | keep | 0 | Apr | 2023 | 0.00021659 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-06 19:37 | 2023-04-06 20:50 | 50 | 1:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | M23040600923 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 73 | 2023-04-06 | 3650 | keep | 0 | Apr | 2023 | 0.002486 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-06 19:50 | 2023-04-07 07:44 | 7 | 11:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR REPARO SECUNDARIA | C23040600230 | New_Event | Secondary Wire Break | Include | Include | Equipment | 714 | 2023-04-06 | 4998 | keep | 0 | Apr | 2023 | 0.0034041 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-04-06 19:57 | 2023-04-06 22:35 | 50 | 2:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M23040600961 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 158 | 2023-04-06 | 7900 | keep | 0 | Apr | 2023 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-06 20:05 | 2023-04-06 21:14 | 10 | 1:09 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DESGANCHE SECUNDARIO Y REPARAR LA SECUNDARIA | R23040600150 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 69 | 2023-04-06 | 690 | keep | 0 | Apr | 2023 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-06 20:07 | 2023-04-06 20:40 | 40 | 0:33 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZA BAJANTE PRIMARIO | M23040600978 | New_Event | Primary Wire Break | Include | Include | Equipment | 33 | 2023-04-06 | 1320 | keep | 0 | Apr | 2023 | 0.00089905 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-06 20:08 | 2023-04-07 09:20 | 50 | 13:12 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23040600231 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 792 | 2023-04-06 | 39600 | keep | 0 | Apr | 2023 | 0.026971 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-06 20:12 | 2023-04-06 23:20 | 40 | 3:08 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN CORTE DE LINEA SE DEJO ABIERTO TRANSFORMADOR CRUZADO | A23040600465 | New_Event | Service Transformer Failure | Include | Include | Equipment | 188 | 2023-04-06 | 7520 | keep | 0 | Apr | 2023 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-04-06 20:13 | 2023-04-07 07:42 | 33 | 11:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P23040600402 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 689 | 2023-04-06 | 22737 | keep | 0 | Apr | 2023 | 0.015486 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
VEGA BAJA | 2023-04-06 20:38 | 2023-04-07 09:20 | 20 | 12:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A23040600072 | New_Event | Primary Wire Break | Include | Include | Equipment | 762 | 2023-04-06 | 15240 | keep | 0 | Apr | 2023 | 0.01038 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-04-06 20:40 | 2023-04-07 00:10 | 150 | 3:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN MACHETE | M23040601023 | New_Event | Primary Wire Break | Include | Include | Equipment | 210 | 2023-04-06 | 31500 | keep | 0 | Apr | 2023 | 0.021455 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2023-04-06 21:06 | 2023-04-07 12:17 | 7 | 15:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23040600374 | New_Event | Cutout Failure | Include | Include | Equipment | 911 | 2023-04-06 | 6377 | keep | 0 | Apr | 2023 | 0.0043433 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-04-06 21:10 | 2023-04-07 13:30 | 1 | 16:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23040600475 | New_Event | Primary Wire Break | Include | Include | Equipment | 980 | 2023-04-06 | 980 | keep | 0 | Apr | 2023 | 0.00066747 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-06 21:34 | 2023-04-06 21:36 | 4381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M23040601060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-06 | 8762 | keep | 0 | Apr | 2023 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2023-04-06 21:49 | 2023-04-07 11:21 | 6 | 13:32 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR Y SE DEJO TOMA DE CLIENTE FUERA PROA | S23040600402 | New_Event | Customer-Related Interruption | Include | Include | Public | 812 | 2023-04-06 | 4872 | keep | 0 | Apr | 2023 | 0.0033183 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-06 22:13 | 2023-04-07 10:00 | 50 | 11:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040601077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 707 | 2023-04-06 | 35350 | keep | 0 | Apr | 2023 | 0.024077 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-06 22:19 | 2023-04-06 22:21 | 4381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23040601086 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-06 | 8762 | keep | 0 | Apr | 2023 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2023-04-06 22:42 | 2023-04-07 10:40 | 40 | 11:58 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040601096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 718 | 2023-04-06 | 28720 | keep | 0 | Apr | 2023 | 0.019561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-04-06 23:11 | 2023-04-07 02:39 | 3565 | 3:28 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CG-230406-01 SE REEMPLAZARON CAJAS QUEMADAS EN TRONCAL LLEVANDO PARTE DE LA CARGA DEL 9602-04 | C23040600238 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2023-04-06 | 741520 | keep | 0 | Apr | 2023 | 0.50505 | 0.0024281 | Sustained | FALSE | FALSE | Not_TMED_Event | 3565
BARRANQUITAS | 2023-04-06 23:11 | 2023-04-07 02:39 | 200 | 3:28 | P | ALIMENTADOR AMARRADO | PARTE DE LA CARGA POR EL 3502-02 | C23040600238 | New_Event | Feeder Load Transferred | Include | Include | Other | 208 | 2023-04-06 | 41600 | keep | 0 | Apr | 2023 | 0.028334 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-04-06 23:19 | 2023-04-07 09:30 | 80 | 10:11 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23040601108 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 611 | 2023-04-06 | 48880 | keep | 0 | Apr | 2023 | 0.033292 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-04-06 23:20 | 2023-04-08 17:05 | 12 | 41:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 50 KVA X 50 KVA RELACIONADO A EVENTO A23040600465 SE DEJO XMER ABIERTO POR ESTAR AVERIADO | A23040800049 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 2505 | 2023-04-06 | 30060 | keep | 0 | Apr | 2023 | 0.020474 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-06 23:38 | 2023-04-07 08:04 | 50 | 8:26 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR EN TRAMO RADIAL | B23040600370 | New_Event | Primary Wire Break | Include | Include | Equipment | 506 | 2023-04-06 | 25300 | keep | 0 | Apr | 2023 | 0.017232 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-06 23:50 | 2023-04-07 13:18 | 40 | 13:28 | P | PARARRAYOS DEFECTUOSO | 3 X 40 EN CORTE DE LINEA SE REMPLAZO PARARRAYOS DEFECTUOSO | A23040600358 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 808 | 2023-04-06 | 32320 | keep | 0 | Apr | 2023 | 0.022013 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-06 23:53 | 2023-04-07 10:00 | 100 | 10:07 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040601129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 607 | 2023-04-06 | 60700 | keep | 0 | Apr | 2023 | 0.041342 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-07 00:08 | 2023-04-07 00:09 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23040700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1859 | keep | 0 | Apr | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
SAN JUAN | 2023-04-07 00:37 | 2023-04-08 11:05 | 375 | 34:28 | P | ERROR HUMANO | SE CERRO MACHETES HACIA CARGA DEL 1107-05 FUERA DESDE QUE SE TRANSFIRIO SUBESTACION EL DIA 6 DE ABRIL DEL 2023 | S23040800214 | New_Event | Human Error | Include | Include | Other | 2068 | 2023-04-07 | 775500 | keep | 0 | Apr | 2023 | 0.52819 | 0.00025541 | Sustained | FALSE | FALSE | Not_TMED_Event | 375
CAGUAS | 2023-04-07 01:00 | 2023-04-07 11:17 | 35 | 10:17 | P | DESGANCHE | 1 X 50 EN C/L | C23040700008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 617 | 2023-04-07 | 21595 | keep | 0 | Apr | 2023 | 0.014708 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-04-07 01:15 | 2023-04-07 09:42 | 106 | 8:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L REEMPLAZO PIN POLE TOP | C23040700009 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 507 | 2023-04-07 | 53742 | keep | 0 | Apr | 2023 | 0.036603 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
VEGA BAJA | 2023-04-07 01:41 | 2023-04-07 01:42 | 2107 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23040700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2107 | keep | 0 | Apr | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
SAN JUAN | 2023-04-07 01:44 | 2023-04-07 06:27 | 727 | 4:43 | P | ALIMENTADOR AMARRADO | CON SJ-230407-01. SE REMPLAZO MACHETE QUEMADO. Y SE CERRO AMARRE CONTRA 1336-10 QUE ESTA A SU VEZ POR 1620-01. ENTRO UN 90% EN SERVICIO Y ENTRO 18% DEL 1206-03 QUE ESTA POR 1620-02 | S23040700004 | New_Event | Feeder Load Transferred | Include | Include | Other | 283 | 2023-04-07 | 205741 | keep | 0 | Apr | 2023 | 0.14013 | 0.00049516 | Sustained | FALSE | FALSE | Not_TMED_Event | 727
SAN JUAN | 2023-04-07 01:44 | 2023-04-07 05:25 | 3718 | 3:41 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE BKR SE HICIERON OPERACIONES CON SJ-230407-01. SE SECCIONALIZO AVERIA DE MACHETES QUEMADOS. ENTRO UN 40% EN SERVICIO. LLEVA 18% DEL 1206-03 | S23040700004 | New_Event | Switch Failure | Include | Include | Equipment | 221 | 2023-04-07 | 821678 | keep | 0 | Apr | 2023 | 0.55964 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
SAN JUAN | 2023-04-07 03:02 | 2023-04-07 10:36 | 60 | 7:34 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE CERRO CORTE DE LINEA NO FUNDIO | S23040700013 | New_Event | Primary Wire Break | Include | Include | Equipment | 454 | 2023-04-07 | 27240 | keep | 0 | Apr | 2023 | 0.018553 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-04-07 03:18 | 2023-04-07 03:19 | 1228 | 0:01 | T | DESGANCHE | RECIERRE | C23040700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-07 | 1228 | keep | 0 | Apr | 2023 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2023-04-07 03:19 | 2023-04-07 08:28 | 155 | 5:09 | P | DESGANCHE | 1 X 80 EN C/L | C23040700015 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 309 | 2023-04-07 | 47895 | keep | 0 | Apr | 2023 | 0.032621 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
SAN JUAN | 2023-04-07 05:25 | 2023-04-07 06:27 | 2230 | 1:02 | P | DESCONECTIVO DEFECTUOSO | CON SJ-230407-01. SE REMPLAZO MACHETE QUEMADO. Y SE CERRO AMARRE CONTRA 1336-10 QUE ESTA A SU VEZ POR 1620-01. ENTRO UN 90% EN SERVICIO Y ENTRO 18% DEL 1206-03 | S23040700004 | Partial_restoration | Switch Failure | Include | Include | Equipment | 62 | 2023-04-07 | 138260 | keep | 0 | Apr | 2023 | 0.094168 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-07 05:52 | 2023-04-07 05:53 | 1681 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL BKR 1303-01 LLEVA EL 1346-06 | S23040700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1681 | keep | 0 | Apr | 2023 | 0.0011449 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-04-07 05:52 | 2023-04-07 05:53 | 1598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL BKR 1303-01 LLEVA EL 1346-06 | S23040700018 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 1598 | keep | 0 | Apr | 2023 | 0.0010884 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
CAGUAS | 2023-04-07 06:13 | 2023-04-07 13:45 | 51 | 7:32 | P | DESCONECTIVO DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE INSTALO PUENTE PORTATIL EN MACHETE QUEMADO HASTA QUE EL DISTRITO REPARE | C23040700016 | New_Event | Switch Failure | Include | Include | Equipment | 452 | 2023-04-07 | 23052 | keep | 0 | Apr | 2023 | 0.015701 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-04-07 06:24 | 2023-04-07 06:25 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR RECERRO LLEVA 75% DEL 1718-03 | B2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-04-07 06:24 | 2023-04-07 06:25 | 1953 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR RECERRO 75% DE SU CARGA POR EL 1713-04 | B2304070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 1953 | keep | 0 | Apr | 2023 | 0.0013302 | 0.0013302 | Momentary | FALSE | FALSE | Not_TMED_Event | 1953
SAN JUAN | 2023-04-07 06:27 | 2023-04-07 06:32 | 297 | 0:05 | P | DESCONECTIVO DEFECTUOSO | CON SJ-230407-01. ENTRO UN 98% SE CERRO MACHETES HACIA SAN MARTIN QUEDA CARGA DE SU-19 FUERA Y SECCIONALIZADA | S23040700004 | Partial_restoration | Switch Failure | Include | Include | Equipment | 5 | 2023-04-07 | 1485 | keep | 0 | Apr | 2023 | 0.0010114 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-07 06:32 | 2023-04-07 13:24 | 74 | 6:52 | P | DESCONECTIVO DEFECTUOSO | SJ-230407-01 SE REPARO PIN HOLE EN RISER HACIA SU-9 | S23040700004 | Partial_restoration | Switch Failure | Include | Include | Equipment | 412 | 2023-04-07 | 30488 | keep | 0 | Apr | 2023 | 0.020765 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-07 06:46 | 2023-04-07 09:29 | 84 | 2:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 80 EN C/L | B23040700012 | New_Event | Cutout Failure | Include | Include | Equipment | 163 | 2023-04-07 | 13692 | keep | 0 | Apr | 2023 | 0.0093256 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
GUAYAMA | 2023-04-07 06:46 | 2023-04-07 09:30 | 45 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA 1 X 65 EN CORTE DE LINEA | P23040700066 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2023-04-07 | 7380 | keep | 0 | Apr | 2023 | 0.0050265 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-04-07 07:01 | 2023-04-07 18:15 | 5 | 11:14 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA X 25 KVA | C23040700018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 674 | 2023-04-07 | 3370 | keep | 0 | Apr | 2023 | 0.0022953 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-04-07 07:01 | 2023-04-07 15:09 | 44 | 8:08 | P | SOBRECARGA | 1 X 80 Y 1 X 50 EN CORTES DE LINEA SE COORDINO FUSIBLES | C23040700075 | New_Event | Trip Due To Overload | Include | Include | Other | 488 | 2023-04-07 | 21472 | keep | 0 | Apr | 2023 | 0.014624 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2023-04-07 07:06 | 2023-04-07 07:08 | 3157 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23040700025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-07 | 6314 | keep | 0 | Apr | 2023 | 0.0043004 | 0.0021502 | Momentary | FALSE | FALSE | Not_TMED_Event | 3157
VEGA BAJA | 2023-04-07 07:06 | 2023-04-07 07:08 | 35 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23040700025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-07 | 70 | keep | 0 | Apr | 2023 | 4.7677e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-04-07 07:06 | 2023-04-07 07:08 | 2916 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23040700025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-07 | 5832 | keep | 0 | Apr | 2023 | 0.0039721 | 0.0019861 | Momentary | FALSE | FALSE | Not_TMED_Event | 2916
BAYAMON | 2023-04-07 07:07 | 2023-04-07 08:34 | 961 | 1:27 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | B23040700015 | New_Event | Animals | Include | Include | Wildlife | 87 | 2023-04-07 | 83607 | keep | 0 | Apr | 2023 | 0.056944 | 0.00065453 | Sustained | FALSE | FALSE | Not_TMED_Event | 961
MAYAGÃœEZ | 2023-04-07 07:11 | 2023-04-07 07:12 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 6802-04 ACACIAS 13 KV NO RECERRO SE CERRO POR CONTROL SCADA | M23040700063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 4381 | keep | 0 | Apr | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CANOVANAS | 2023-04-07 07:14 | 2023-04-07 09:32 | 42 | 2:18 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTES DE LINEA | R23040700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-04-07 | 5796 | keep | 0 | Apr | 2023 | 0.0039476 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
MAYAGÃœEZ | 2023-04-07 07:38 | 2023-04-07 12:10 | 80 | 4:32 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700077 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 272 | 2023-04-07 | 21760 | keep | 0 | Apr | 2023 | 0.014821 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-07 07:45 | 2023-04-07 07:46 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1615 | keep | 0 | Apr | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-04-07 08:04 | 2023-04-07 08:05 | 2179 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | R23040700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2179 | keep | 0 | Apr | 2023 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
VEGA BAJA | 2023-04-07 08:04 | 2023-04-07 08:07 | 3076 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE DISPARO INTERRUPTOR A PETICION DE VICTOR QUINONEZ PARA SECCIONALIZAR TRAMO Y LEBANTAR CONDUCTOR | B23040600370 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-07 | 9228 | keep | 0 | Apr | 2023 | 0.0062851 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-07 08:07 | 2023-04-07 14:38 | 50 | 6:31 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR EN TRAMO RADIAL | B23040600370 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 391 | 2023-04-07 | 19550 | keep | 0 | Apr | 2023 | 0.013315 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-07 08:16 | 2023-04-07 14:45 | 6 | 6:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN C/L SE LEVANTO CONDUCTOR PRIMARIO AREA PERTENECE A MONACILLOS | S23040700031 | New_Event | Primary Wire Break | Include | Include | Equipment | 389 | 2023-04-07 | 2334 | keep | 0 | Apr | 2023 | 0.0015897 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-07 08:17 | 2023-04-07 09:27 | 12 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REEMPLAZAR BARRAS DE PEDESTAL | C23040700024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-04-07 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-04-07 08:19 | 2023-04-07 16:38 | 10 | 8:19 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A23040700044 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 499 | 2023-04-07 | 4990 | keep | 0 | Apr | 2023 | 0.0033987 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-07 08:34 | 2023-04-07 12:03 | 100 | 3:29 | P | DESGANCHE | 2 X 80 EN C/L | C23040700029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-04-07 | 20900 | keep | 0 | Apr | 2023 | 0.014235 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-07 08:40 | 2023-04-07 08:41 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23040700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 3464 | keep | 0 | Apr | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2023-04-07 08:41 | 2023-04-07 08:47 | 229 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1619-02 LLEVA 42% DE LA CARGA DEL 1336-06 | R23040700029 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-04-07 | 1374 | keep | 0 | Apr | 2023 | 0.00093583 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
CANOVANAS | 2023-04-07 08:41 | 2023-04-07 08:47 | 2531 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE PROBO QUEDO EN SERVICIO 50% POR 1619-02 | S23040700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-07 | 15186 | keep | 0 | Apr | 2023 | 0.010343 | 0.0017239 | Sustained | FALSE | FALSE | Not_TMED_Event | 2531
YAUCO | 2023-04-07 08:56 | 2023-04-07 11:58 | 30 | 3:02 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA POR RAYOS | M23040700149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 182 | 2023-04-07 | 5460 | keep | 0 | Apr | 2023 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-07 08:58 | 2023-04-07 18:17 | 10 | 9:19 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23040700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 559 | 2023-04-07 | 5590 | keep | 0 | Apr | 2023 | 0.0038073 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-07 08:59 | 2023-04-07 10:15 | 10 | 1:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE PRIMARIO | M23040700153 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2023-04-07 | 760 | keep | 0 | Apr | 2023 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-07 09:00 | 2023-04-07 09:01 | 2435 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR CARGA POR EL 1909-08 | B2304070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-07 09:00 | 2023-04-07 09:01 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 1907-05 | B2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2956 | keep | 0 | Apr | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CANOVANAS | 2023-04-07 09:02 | 2023-04-07 11:07 | 80 | 2:05 | P | DESGANCHE | 2X100 EN C/L DESGANCHE | R23040700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-04-07 | 10000 | keep | 0 | Apr | 2023 | 0.006811 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-04-07 09:06 | 2023-04-07 10:46 | 67 | 1:40 | P | ANIMAL | 1 X 40 Y 1 X 50 EN C/LS CRUCE X AVE | C23040700045 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-04-07 | 6700 | keep | 0 | Apr | 2023 | 0.0045633 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
MAYAGÃœEZ | 2023-04-07 09:20 | 2023-04-07 11:47 | 12 | 2:27 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040700179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-04-07 | 1764 | keep | 0 | Apr | 2023 | 0.0012015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-07 09:22 | 2023-04-07 12:56 | 150 | 3:34 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER Y 1 X80 EN C/L 1 X65 EN SU | B23040700055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 214 | 2023-04-07 | 32100 | keep | 0 | Apr | 2023 | 0.021863 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-07 09:28 | 2023-04-07 09:30 | 316 | 0:02 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO Y SE CERRO POR SCADA 1117-09 LLEVA 25% DEL 1119-02 Y LLEVA 25% DEL 1119-04 | S23040700040 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-04-07 | 632 | keep | 0 | Apr | 2023 | 0.00043045 | 0.00021523 | Momentary | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2023-04-07 09:28 | 2023-04-07 09:30 | 215 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO Y SE CERRO POR SCADA 1117-09 LLEVA 25% DEL 1119-02 Y LLEVA 25% DEL 1119-04 | S23040700040 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-07 | 430 | keep | 0 | Apr | 2023 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-04-07 09:28 | 2023-04-07 09:30 | 680 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE 1117-09 QUE LLEVA 25% DEL 1119-04 | S23040700040 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-07 | 1360 | keep | 0 | Apr | 2023 | 0.00092629 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
SAN JUAN | 2023-04-07 09:30 | 2023-04-07 12:26 | 42 | 2:56 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 3 SMU-20 DE 20AMP CONTAMINACION EN SU | S23040700040 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 176 | 2023-04-07 | 7392 | keep | 0 | Apr | 2023 | 0.0050347 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
MAYAGÃœEZ | 2023-04-07 09:31 | 2023-04-07 11:21 | 1600 | 1:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PARTIDO, SE REMPLAZO CAJA QUEMADA Y SE CERRO MACHETES | M23040700189 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 110 | 2023-04-07 | 176000 | keep | 0 | Apr | 2023 | 0.11987 | 0.0010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1600
AGUADILLA | 2023-04-07 09:31 | 2023-04-07 14:50 | 1483 | 5:19 | S | OTRAS CAUSAS | SE REMPLAZO 2 FUSIBLE EN LA ALTA DEL TRANSFORMADOR EN LAS FASES 2 Y 3 DE 65 AMP VSS INFORMO MIGUEL RAMOS QUE SE ELIMINO UNA BARRA QUE ESTABA CRUZANDO A TIERRA ESTA LE DABA SERVICIO A UNOS PTS QUE ESTAN DESHABILITADOS | A23040700070 | New_Event | Other Causes | Include | Include | Other | 319 | 2023-04-07 | 473077 | keep | 0 | Apr | 2023 | 0.32221 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
AGUADILLA | 2023-04-07 09:31 | 2023-04-07 14:50 | 89 | 5:19 | S | OTRAS CAUSAS | SE REMPLAZO 2 FUSIBLE EN LA ALTA DEL TRANSFORMADOR EN LAS FASES 2 Y 3 DE 65 AMP VSS INFORMO MIGUEL RAMOS QUE SE ELIMINO UNA BARRA QUE ESTABA CRUZANDO A TIERRA ESTA LE DABA SERVICIO A UNOS PTS QUE ESTAN DESHABILITADOS | A23040700070 | New_Event | Other Causes | Include | Include | Other | 319 | 2023-04-07 | 28391 | keep | 0 | Apr | 2023 | 0.019337 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
MAYAGÃœEZ | 2023-04-07 09:34 | 2023-04-07 10:50 | 40 | 1:16 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700190 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 76 | 2023-04-07 | 3040 | keep | 0 | Apr | 2023 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-07 09:35 | 2023-04-07 19:47 | 1 | 10:12 | P | NO SE REPORTO CAUSA | 1 X 100 EN CL | S23040700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 612 | 2023-04-07 | 612 | keep | 0 | Apr | 2023 | 0.00041683 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-04-07 09:35 | 2023-04-07 11:42 | 10 | 2:07 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE BUSHING SECUNDARIO EN XMR | R23040700049 | New_Event | Service Transformer Failure | Include | Include | Equipment | 127 | 2023-04-07 | 1270 | keep | 0 | Apr | 2023 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-07 09:35 | 2023-04-07 11:17 | 100 | 1:42 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23040700056 | New_Event | Animals | Include | Include | Wildlife | 102 | 2023-04-07 | 10200 | keep | 0 | Apr | 2023 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-04-07 10:00 | 2023-04-07 10:48 | 3 | 0:48 | P | DESGANCHE | 1 X 25 EN C/L | C23040700062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-04-07 | 144 | keep | 0 | Apr | 2023 | 9.8078e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-07 10:08 | 2023-04-07 11:24 | 114 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIAS | R23040700054 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2023-04-07 | 8664 | keep | 0 | Apr | 2023 | 0.005901 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
AGUADILLA | 2023-04-07 10:15 | 2023-04-07 11:00 | 1 | 0:45 | P | MAL TIEMPO/RAYOS | 1 X 65 EN RISER MAL TIEMPO DESCARGAS ELECTRICAS | M23040700219 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 45 | 2023-04-07 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-07 10:27 | 2023-04-07 12:49 | 49 | 2:22 | P | DESGANCHE | 1 X 65 EN C/L | C23040700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-04-07 | 6958 | keep | 0 | Apr | 2023 | 0.0047391 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
BAYAMON | 2023-04-07 10:31 | 2023-04-07 12:55 | 35 | 2:24 | P | DESGANCHE | 1 X 65 EN C/L Y DESGANCHE | B23040700068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-04-07 | 5040 | keep | 0 | Apr | 2023 | 0.0034327 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-04-07 10:36 | 2023-04-07 11:40 | 40 | 1:04 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700231 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 64 | 2023-04-07 | 2560 | keep | 0 | Apr | 2023 | 0.0017436 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-07 10:59 | 2023-04-07 14:04 | 36 | 3:05 | P | DESGANCHE | 2 X 65 EN CORTES DE LINEA | R23040700064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-04-07 | 6660 | keep | 0 | Apr | 2023 | 0.0045361 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
FAJARDO | 2023-04-07 11:00 | 2023-04-07 15:01 | 10 | 4:01 | P | NO SE REPORTO CAUSA | 1 X 18 EN TRANSFORMADOR | R23040700070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 241 | 2023-04-07 | 2410 | keep | 0 | Apr | 2023 | 0.0016414 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-07 11:06 | 2023-04-07 11:07 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23040700061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
FAJARDO | 2023-04-07 11:08 | 2023-04-07 11:56 | 70 | 0:48 | P | DESGANCHE | 1X25 EN C/L DESGANCHE | R23040700065 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-04-07 | 3360 | keep | 0 | Apr | 2023 | 0.0022885 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2023-04-07 11:10 | 2023-04-07 15:12 | 150 | 4:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 Y 1 X 80 EN CORTES DE LINEA SE REEMPLAZARON CAJAS QUEMADAS | R23040700067 | New_Event | Cutout Failure | Include | Include | Equipment | 242 | 2023-04-07 | 36300 | keep | 0 | Apr | 2023 | 0.024724 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-04-07 11:14 | 2023-04-07 15:18 | 11 | 4:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R23040700071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-04-07 | 2684 | keep | 0 | Apr | 2023 | 0.0018281 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-04-07 11:15 | 2023-04-07 11:16 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23040700073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-07 11:17 | 2023-04-07 12:49 | 30 | 1:32 | P | DESGANCHE | 1X40 EN C/L 1X30 EN OTRO C/L DESGANCHE | R23040700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-04-07 | 2760 | keep | 0 | Apr | 2023 | 0.0018798 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-07 11:21 | 2023-04-07 11:22 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23040700075 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2023-04-07 11:23 | 2023-04-07 11:27 | 225 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO BKR 1303-04 CERRADO POR SCADA | S2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-07 | 900 | keep | 0 | Apr | 2023 | 0.00061299 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
CANOVANAS | 2023-04-07 11:24 | 2023-04-07 11:25 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | R23040700077 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-07 11:27 | 2023-04-07 11:28 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23040700078 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
VEGA BAJA | 2023-04-07 11:29 | 2023-04-07 14:25 | 20 | 2:56 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTES SECUNDARIOS Y SE REALIZO DESGANCHE | A23040600201 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 176 | 2023-04-07 | 3520 | keep | 0 | Apr | 2023 | 0.0023975 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-07 11:30 | 2023-04-07 11:34 | 4291 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO 1204-02 SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | S2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-07 | 17164 | keep | 0 | Apr | 2023 | 0.01169 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2023-04-07 11:30 | 2023-04-07 11:32 | 315 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | B2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-07 | 630 | keep | 0 | Apr | 2023 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
PONCE | 2023-04-07 11:30 | 2023-04-07 13:52 | 57 | 2:22 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE CORRGIO CRUCE EN LINEA PRIMARIA | P23040700131 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 142 | 2023-04-07 | 8094 | keep | 0 | Apr | 2023 | 0.0055128 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-04-07 11:32 | 2023-04-07 11:35 | 1588 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL CARGA POR EL 1716-03 | B230407000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-07 | 4764 | keep | 0 | Apr | 2023 | 0.0032447 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-07 11:32 | 2023-04-07 11:35 | 723 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL CARGA POR EL 1716-03 | B230407000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-07 | 2169 | keep | 0 | Apr | 2023 | 0.0014773 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-04-07 11:32 | 2023-04-07 11:35 | 1812 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA LA CARGA DEL 1711-01 Y 1711-02 | B230407000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-07 | 5436 | keep | 0 | Apr | 2023 | 0.0037024 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2023-04-07 11:32 | 2023-04-07 11:33 | 4431 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | B2304070000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-07 | 4431 | keep | 0 | Apr | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-04-07 11:34 | 2023-04-07 11:36 | 1784 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 90% DE SU CARGA POR EL 1801-02 | B2304070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-07 | 3568 | keep | 0 | Apr | 2023 | 0.0024301 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-04-07 11:34 | 2023-04-07 11:36 | 453 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 10% DE SU CARGA POR EL 1801-02 | B2304070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-07 | 906 | keep | 0 | Apr | 2023 | 0.00061707 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-04-07 11:34 | 2023-04-07 11:37 | 4431 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2304070000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-04-07 | 13293 | keep | 0 | Apr | 2023 | 0.0090538 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-04-07 11:34 | 2023-04-07 11:36 | 186 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 | B2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-07 | 372 | keep | 0 | Apr | 2023 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
VEGA BAJA | 2023-04-07 11:35 | 2023-04-07 14:30 | 500 | 2:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 Y 2 X 100 EN DISTINTOS CORTES DE LINEAS POR LLUVIA Y VIENTO | A23040700080 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 175 | 2023-04-07 | 87500 | keep | 0 | Apr | 2023 | 0.059596 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2023-04-07 11:39 | 2023-04-07 11:41 | 4431 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2304070000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-07 | 8862 | keep | 0 | Apr | 2023 | 0.0060359 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
SAN JUAN | 2023-04-07 11:41 | 2023-04-07 13:45 | 89 | 2:04 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23040700074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-04-07 | 11036 | keep | 0 | Apr | 2023 | 0.0075166 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
SAN JUAN | 2023-04-07 11:45 | 2023-04-07 11:46 | 770 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | R23040700081 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-07 | 770 | keep | 0 | Apr | 2023 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2023-04-07 11:46 | 2023-04-07 12:29 | 443 | 0:43 | P | CONDUCTOR ROTO O ABIERTO | SE PATRULLO SE ENCONTRO ALAMBRE EN EL PSIO SE VA A SECCIONALIZAR | R23040700086 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 43 | 2023-04-07 | 19049 | keep | 0 | Apr | 2023 | 0.012974 | 0.00030173 | Sustained | FALSE | FALSE | Not_TMED_Event | 443
BAYAMON | 2023-04-07 11:46 | 2023-04-07 11:47 | 57 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | B2304070000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-07 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-04-07 11:48 | 2023-04-07 13:03 | 4431 | 1:15 | T | DESGANCHE | DISPARO SE RETIRO RAMA SOBRE LINEAS | B23040700238 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-04-07 | 332325 | keep | 0 | Apr | 2023 | 0.22635 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
CANOVANAS | 2023-04-07 11:55 | 2023-04-07 16:13 | 60 | 4:18 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN CORTES DE LINEA SE LEVANTO CONDUCTORES DEL SUELO | R23040700082 | New_Event | Primary Wire Break | Include | Include | Equipment | 258 | 2023-04-07 | 15480 | keep | 0 | Apr | 2023 | 0.010543 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-07 11:56 | 2023-04-07 13:32 | 238 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR Y 1 X 40 EN C/L MAL TIEMPO LLUVIAS | B23040700120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2023-04-07 | 22848 | keep | 0 | Apr | 2023 | 0.015562 | 0.0001621 | Sustained | FALSE | FALSE | Not_TMED_Event | 238
FAJARDO | 2023-04-07 11:56 | 2023-04-07 16:37 | 30 | 4:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 Y 1 X 30 EN CORTES DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA QUEMADA | R23040700085 | New_Event | Cutout Failure | Include | Include | Equipment | 281 | 2023-04-07 | 8430 | keep | 0 | Apr | 2023 | 0.0057416 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-04-07 11:56 | 2023-04-07 11:57 | 508 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVANDO CARGA DE 5402-02 | P23040700143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 508 | keep | 0 | Apr | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-04-07 11:56 | 2023-04-07 11:57 | 64 | 0:01 | T | ALIMENTADOR AMARRADO | RECIRRE | P23040700143 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 64 | keep | 0 | Apr | 2023 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
YAUCO | 2023-04-07 11:58 | 2023-04-07 17:25 | 1268 | 5:27 | S | PROTECCION DEFECTUOSA | SE IDENTIFICO FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR (38KV) INTERRUPTORES 6501-2 Y 6501-04 NO OPERARON EN AVERIA (MAL TIEMPO EN EL AREA) | M23040700450 | New_Event | Protection Miscoordination | Include | Include | Other | 327 | 2023-04-07 | 414636 | keep | 0 | Apr | 2023 | 0.28241 | 0.00086363 | Sustained | FALSE | FALSE | Not_TMED_Event | 1268
YAUCO | 2023-04-07 11:58 | 2023-04-07 17:25 | 2064 | 5:27 | S | PROTECCION DEFECTUOSA | SE IDENTIFICO FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR (38KV) INTERRUPTORES 6501-2 Y 6501-04 NO OPERARON EN AVERIA (MAL TIEMPO EN EL AREA) | M23040700450 | New_Event | Protection Miscoordination | Include | Include | Other | 327 | 2023-04-07 | 674928 | keep | 0 | Apr | 2023 | 0.45969 | 0.0014058 | Sustained | FALSE | FALSE | Not_TMED_Event | 2064
YAUCO | 2023-04-07 11:58 | 2023-04-07 17:25 | 3036 | 5:27 | S | PROTECCION DEFECTUOSA | SE IDENTIFICO FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR (38KV) INTERRUPTORES 6501-2 Y 6501-04 NO OPERARON EN AVERIA (MAL TIEMPO EN EL AREA) | M23040700450 | New_Event | Protection Miscoordination | Include | Include | Other | 327 | 2023-04-07 | 992772 | keep | 0 | Apr | 2023 | 0.67617 | 0.0020678 | Sustained | FALSE | FALSE | Not_TMED_Event | 3036
YAUCO | 2023-04-07 11:58 | 2023-04-07 17:25 | 2952 | 5:27 | S | PROTECCION DEFECTUOSA | SE IDENTIFICO FUSIBLE FUNDIDO EN LA ALTA DEL TRANSFORMADOR (38KV) INTERRUPTORES 6501-2 Y 6501-04 NO OPERARON EN AVERIA (MAL TIEMPO EN EL AREA) | M23040700450 | New_Event | Protection Miscoordination | Include | Include | Other | 327 | 2023-04-07 | 965304 | keep | 0 | Apr | 2023 | 0.65746 | 0.0020106 | Sustained | FALSE | FALSE | Not_TMED_Event | 2952
FAJARDO | 2023-04-07 12:01 | 2023-04-07 12:32 | 65 | 0:31 | P | DESGANCHE | 1 X 40 Y 1 X 30 EN CORTES DE LINEA | R23040700090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-04-07 | 2015 | keep | 0 | Apr | 2023 | 0.0013724 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-04-07 12:04 | 2023-04-07 14:10 | 2402 | 2:06 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-04-07 | 302652 | keep | 0 | Apr | 2023 | 0.20613 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-04-07 12:04 | 2023-04-07 14:39 | 30 | 2:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES LLUVIAS | B23040700138 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 155 | 2023-04-07 | 4650 | keep | 0 | Apr | 2023 | 0.0031671 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-07 12:08 | 2023-04-07 15:36 | 50 | 3:28 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | S23040700101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2023-04-07 | 10400 | keep | 0 | Apr | 2023 | 0.0070834 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-07 12:08 | 2023-04-07 17:40 | 100 | 5:32 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 Y1 X 140 EN CORTE DE LINEA SE RETEZO PRIMARIA | M23040700274 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 332 | 2023-04-07 | 33200 | keep | 0 | Apr | 2023 | 0.022612 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-07 12:11 | 2023-04-07 14:35 | 400 | 2:24 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700279 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 144 | 2023-04-07 | 57600 | keep | 0 | Apr | 2023 | 0.039231 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2023-04-07 12:14 | 2023-04-07 16:32 | 15 | 4:18 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23040700108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2023-04-07 | 3870 | keep | 0 | Apr | 2023 | 0.0026358 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-04-07 12:16 | 2023-04-07 15:11 | 39 | 2:55 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO | R23040700096 | New_Event | Primary Wire Break | Include | Include | Equipment | 175 | 2023-04-07 | 6825 | keep | 0 | Apr | 2023 | 0.0046485 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
SAN JUAN | 2023-04-07 12:18 | 2023-04-07 14:42 | 20 | 2:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA RELOCALIZAR LINEA SECUNADARIA | S23040700110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 144 | 2023-04-07 | 2880 | keep | 0 | Apr | 2023 | 0.0019616 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-07 12:20 | 2023-04-07 17:00 | 100 | 4:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADOR | M23040700302 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 280 | 2023-04-07 | 28000 | keep | 0 | Apr | 2023 | 0.019071 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-07 12:22 | 2023-04-07 14:20 | 239 | 1:58 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | B23040700193 | New_Event | Animals | Include | Include | Wildlife | 118 | 2023-04-07 | 28202 | keep | 0 | Apr | 2023 | 0.019208 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
BAYAMON | 2023-04-07 12:22 | 2023-04-07 12:23 | 3070 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE | B2304070000X | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-07 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-04-07 12:23 | 2023-04-08 09:52 | 2 | 21:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L SE REPORTA MAL TIEMPO LLUVIA | S23040700114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1289 | 2023-04-07 | 2578 | keep | 0 | Apr | 2023 | 0.0017559 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-07 12:23 | 2023-04-07 15:03 | 45 | 2:40 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYOS | B23040700245 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 160 | 2023-04-07 | 7200 | keep | 0 | Apr | 2023 | 0.0049039 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-04-07 12:23 | 2023-04-07 13:48 | 41 | 1:25 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L MAL TIEMPO RAYOS | B23040700218 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 85 | 2023-04-07 | 3485 | keep | 0 | Apr | 2023 | 0.0023736 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
MAYAGÃœEZ | 2023-04-07 12:25 | 2023-04-07 12:26 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23040700326 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
AGUADILLA | 2023-04-07 12:25 | 2023-04-07 12:26 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23040700319 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1192 | keep | 0 | Apr | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
BAYAMON | 2023-04-07 12:27 | 2023-04-07 16:04 | 1408 | 3:37 | T | OTRAS CAUSAS | CARGA POR EL 1714-03 PROBLEMAS EN LOS DPU | B23040700214 | New_Event | Other Causes | Include | Include | Other | 217 | 2023-04-07 | 305536 | keep | 0 | Apr | 2023 | 0.2081 | 0.00095898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2023-04-07 12:27 | 2023-04-07 16:04 | 455 | 3:37 | S | OTRAS CAUSAS | SE REEMPLAZARON 2 FUSIBLES EN LA ALTA 125 STANDARD SE REPARO CIRCUITOR DE POWER DE LOS DPU DE LOS INTERRUPTORES | B23040700214 | New_Event | Other Causes | Include | Include | Other | 217 | 2023-04-07 | 98735 | keep | 0 | Apr | 2023 | 0.067248 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
BAYAMON | 2023-04-07 12:27 | 2023-04-07 16:04 | 878 | 3:37 | S | OTRAS CAUSAS | SE REEMPLAZARON 2 FUSIBLES EN LA ALTA 125 STANDARD SE REPARO CIRCUITOR DE POWER DE LOS DPU DE LOS INTERRUPTORES | B23040700214 | New_Event | Other Causes | Include | Include | Other | 217 | 2023-04-07 | 190526 | keep | 0 | Apr | 2023 | 0.12977 | 0.000598 | Sustained | FALSE | FALSE | Not_TMED_Event | 878
SAN JUAN | 2023-04-07 12:29 | 2023-04-07 13:13 | 770 | 0:44 | T | CONDUCTOR ROTO O ABIERTO | SJ-230407-02 SE ABRIO INTERRUPTOR POR CONTROL SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO N/O CONTRA 1301-01 | S23040700118 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 44 | 2023-04-07 | 33880 | keep | 0 | Apr | 2023 | 0.023076 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-07 12:31 | 2023-04-07 14:24 | 151 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P23040700161 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2023-04-07 | 17063 | keep | 0 | Apr | 2023 | 0.011622 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
MAYAGÃœEZ | 2023-04-07 12:33 | 2023-04-07 15:20 | 40 | 2:47 | P | MAL TIEMPO/RAYOS | 1 X 50 Y 1 X 40 EN CORTE DE LINEA POR RAYOS | M23040700335 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 167 | 2023-04-07 | 6680 | keep | 0 | Apr | 2023 | 0.0045497 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-07 12:36 | 2023-04-07 14:27 | 50 | 1:51 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA POR RAYOS | M23040700341 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 111 | 2023-04-07 | 5550 | keep | 0 | Apr | 2023 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-07 12:37 | 2023-04-07 14:07 | 9 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE DESCONTAMINO TERMINACION SULFATADA | R23040700103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-04-07 | 810 | keep | 0 | Apr | 2023 | 0.00055169 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-04-07 12:38 | 2023-04-07 12:39 | 3786 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1718-03 LLEVA EL 65% DEL 1710-05 | B2304070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 3786 | keep | 0 | Apr | 2023 | 0.0025786 | 0.0025786 | Momentary | FALSE | FALSE | Not_TMED_Event | 3786
BAYAMON | 2023-04-07 12:38 | 2023-04-07 12:39 | 651 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 75% POR EL 1713-04 LLEVA 65% DEL 1710-05 LLEVA EL 1719-19 | C2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 651 | keep | 0 | Apr | 2023 | 0.00044339 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2023-04-07 12:38 | 2023-04-07 12:39 | 2617 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE CARGA POR EL 1718-03 | B2304070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 2617 | keep | 0 | Apr | 2023 | 0.0017824 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2023-04-07 12:40 | 2023-04-07 16:28 | 120 | 3:48 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | B23040700230 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-04-07 | 27360 | keep | 0 | Apr | 2023 | 0.018635 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-04-07 12:40 | 2023-04-07 16:43 | 5 | 4:03 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23040700344 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-04-07 | 1215 | keep | 0 | Apr | 2023 | 0.00082753 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-04-07 12:43 | 2023-04-07 12:44 | 1245 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23040700353 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1245 | keep | 0 | Apr | 2023 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
SAN JUAN | 2023-04-07 12:48 | 2023-04-07 14:56 | 94 | 2:08 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | S23040700128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-04-07 | 12032 | keep | 0 | Apr | 2023 | 0.0081949 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
FAJARDO | 2023-04-07 12:54 | 2023-04-07 16:11 | 6 | 3:17 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR | R23040700106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2023-04-07 | 1182 | keep | 0 | Apr | 2023 | 0.00080505 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-04-07 12:55 | 2023-04-07 12:56 | 1644 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA | A23040700108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1644 | keep | 0 | Apr | 2023 | 0.0011197 | 0.0011197 | Momentary | FALSE | FALSE | Not_TMED_Event | 1644
VEGA BAJA | 2023-04-07 12:56 | 2023-04-07 19:47 | 3 | 6:51 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR Y 1 X 25 EN C/L | B23040700251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 411 | 2023-04-07 | 1233 | keep | 0 | Apr | 2023 | 0.00083979 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-04-07 12:59 | 2023-04-08 13:00 | 50 | 24:01 | P | SECUNDARIA/DESGANCHE | 2 X 40 EN CORTE DE LINEA SE DESGANCHO EN LINEA SECUNDARIAS | M23040700389 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1441 | 2023-04-07 | 72050 | keep | 0 | Apr | 2023 | 0.049073 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-07 13:05 | 2023-04-07 14:38 | 80 | 1:33 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO RAYOS | M23040700404 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2023-04-07 | 7440 | keep | 0 | Apr | 2023 | 0.0050674 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-04-07 13:05 | 2023-04-07 15:57 | 200 | 2:52 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR POR RAYOS | M23040700401 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2023-04-07 | 34400 | keep | 0 | Apr | 2023 | 0.02343 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-07 13:08 | 2023-04-07 14:59 | 79 | 1:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | B23040700258 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 111 | 2023-04-07 | 8769 | keep | 0 | Apr | 2023 | 0.0059725 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2023-04-07 13:13 | 2023-04-07 16:17 | 231 | 3:04 | P | CONDUCTOR ROTO O ABIERTO | SJ-230407-02 SE LEVANTO PRIMARIA Y SE NORMALIZO CARGAS | S23040700118 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 184 | 2023-04-07 | 42504 | keep | 0 | Apr | 2023 | 0.028949 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-07 13:13 | 2023-04-08 09:39 | 40 | 20:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040700118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1226 | 2023-04-07 | 49040 | keep | 0 | Apr | 2023 | 0.033401 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-04-07 13:14 | 2023-04-07 15:32 | 5 | 2:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P23040700191 | New_Event | Primary Wire Break | Include | Include | Equipment | 138 | 2023-04-07 | 690 | keep | 0 | Apr | 2023 | 0.00046996 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-04-07 13:15 | 2023-04-07 13:26 | 1 | 0:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIAS | R23040700111 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2023-04-07 | 11 | keep | 0 | Apr | 2023 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-07 13:17 | 2023-04-07 17:05 | 200 | 3:48 | P | MAL TIEMPO/RAYOS | 1 X 50, 1 X 65 Y 1 X 100CORTE DE LINEA POR RAYOS | M23040700432 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 228 | 2023-04-07 | 45600 | keep | 0 | Apr | 2023 | 0.031058 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-04-07 13:22 | 2023-04-07 15:21 | 10 | 1:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA QUEMADA EN RISER | R23040700115 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2023-04-07 | 1190 | keep | 0 | Apr | 2023 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-04-07 13:25 | 2023-04-07 16:03 | 5 | 2:38 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMA PEGANDO CON EL BUSHING DEL TRANSFORMADOR | A23040700127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-04-07 | 790 | keep | 0 | Apr | 2023 | 0.00053807 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-04-07 13:33 | 2023-04-07 13:34 | 643 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE 1530-09 LLEVA 1530-07 | S23040700142 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 643 | keep | 0 | Apr | 2023 | 0.00043794 | 0.00043794 | Momentary | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2023-04-07 13:33 | 2023-04-07 13:34 | 1310 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE 1530-09 LLEVA 1530-07 | S23040700142 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-07 | 1310 | keep | 0 | Apr | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2023-04-07 13:33 | 2023-04-07 18:03 | 10 | 4:30 | P | DESGANCHE | 1 X 20 Y DESGANCHE | S23040700141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-04-07 | 2700 | keep | 0 | Apr | 2023 | 0.001839 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-07 13:41 | 2023-04-07 18:42 | 150 | 5:01 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA POR RAYOS | M23040700467 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 301 | 2023-04-07 | 45150 | keep | 0 | Apr | 2023 | 0.030751 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-04-07 13:45 | 2023-04-08 11:40 | 8 | 21:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23040700280 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1315 | 2023-04-07 | 10520 | keep | 0 | Apr | 2023 | 0.0071651 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-04-07 13:52 | 2023-04-07 13:53 | 2132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23040700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2132 | keep | 0 | Apr | 2023 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
CAGUAS | 2023-04-07 13:56 | 2023-04-07 16:05 | 149 | 2:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN RISER MAL TIEMPO LLUVIA | C23040700096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 129 | 2023-04-07 | 19221 | keep | 0 | Apr | 2023 | 0.013091 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
VEGA BAJA | 2023-04-07 14:01 | 2023-04-07 14:02 | 2132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23060700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2132 | keep | 0 | Apr | 2023 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
SAN JUAN | 2023-04-07 14:06 | 2023-04-07 14:07 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1118-10 QUE LLEVA 20% DEL 1111-01 CERRADO POR CONTROL | S2304070000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-07 | 513 | keep | 0 | Apr | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-04-07 14:06 | 2023-04-07 14:07 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1118-10 QUE LLEVA 20% DEL 1111-01 CERRADO POR CONTROL | S2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2782 | keep | 0 | Apr | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2023-04-07 14:10 | 2023-04-07 17:01 | 2162 | 2:51 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-04-07 | 369702 | keep | 0 | Apr | 2023 | 0.2518 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-07 14:18 | 2023-04-07 14:19 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1825 | keep | 0 | Apr | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
UTUADO | 2023-04-07 14:19 | 2023-04-08 09:50 | 2 | 19:31 | P | DESGANCHE | 1 X 10 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040700152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1171 | 2023-04-07 | 2342 | keep | 0 | Apr | 2023 | 0.0015951 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-04-07 14:20 | 2023-04-07 17:55 | 39 | 3:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P23040700146 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 215 | 2023-04-07 | 8385 | keep | 0 | Apr | 2023 | 0.005711 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
YAUCO | 2023-04-07 14:24 | 2023-04-07 15:24 | 55 | 1:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P23040700227 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 60 | 2023-04-07 | 3300 | keep | 0 | Apr | 2023 | 0.0022476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-07 14:25 | 2023-04-07 14:55 | 15 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL SECUNDARIO, NO SE PUDO BAJAR TAP ESTA EN EL ULTIMO TAP. SE RECOMIENDA REEMPLAZO DEL TRANSFORMADOR | C23040700098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-04-07 | 450 | keep | 0 | Apr | 2023 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-04-07 14:28 | 2023-04-07 17:05 | 40 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M23040700513 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2023-04-07 | 6280 | keep | 0 | Apr | 2023 | 0.0042773 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-07 14:32 | 2023-04-07 20:39 | 500 | 6:07 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA SE RETIRO PALMA CAIDA SOBRE LAS LINEAS SE REPARO LINEA PRIMARIA ROTA Y SE REMPLAZO PORTAFUSIBLES AVERIADO | A23040700155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2023-04-07 | 183500 | keep | 0 | Apr | 2023 | 0.12498 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2023-04-07 14:58 | 2023-04-07 16:45 | 2 | 1:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A23040700161 | New_Event | Primary Wire Break | Include | Include | Equipment | 107 | 2023-04-07 | 214 | keep | 0 | Apr | 2023 | 0.00014575 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 1357 | 0:20 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY GIS 5% POR 1404-07 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700194 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 27140 | keep | 0 | Apr | 2023 | 0.018485 | 0.00092425 | Sustained | FALSE | FALSE | Not_TMED_Event | 1357
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 1058 | 0:05 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC 20% POR 1424-08 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 5290 | keep | 0 | Apr | 2023 | 0.003603 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 976 | 0:05 | P | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC 80% POR 1424-08 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 4880 | keep | 0 | Apr | 2023 | 0.0033237 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 278 | 0:05 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY GIS CARGA POR 1424-08 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 1390 | keep | 0 | Apr | 2023 | 0.00094672 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 1295 | 0:05 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC CARGA POR 1424-08 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 6475 | keep | 0 | Apr | 2023 | 0.0044101 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 143 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700194 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 2860 | keep | 0 | Apr | 2023 | 0.0019479 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 1357 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC LLEVA 5% DEL 1112-04 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700194 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 27140 | keep | 0 | Apr | 2023 | 0.018485 | 0.00092425 | Sustained | FALSE | FALSE | Not_TMED_Event | 1357
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 328 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700194 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 6560 | keep | 0 | Apr | 2023 | 0.004468 | 0.0002234 | Sustained | FALSE | FALSE | Not_TMED_Event | 328
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 242 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC 20% POR 1401-07 30% POR 1420-04 LLEVA 1420-05 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700194 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 4840 | keep | 0 | Apr | 2023 | 0.0032965 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 23 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700175 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 253 | keep | 0 | Apr | 2023 | 0.00017232 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 530 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700175 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 5830 | keep | 0 | Apr | 2023 | 0.0039708 | 0.00036098 | Sustained | FALSE | FALSE | Not_TMED_Event | 530
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 37 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700175 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 407 | keep | 0 | Apr | 2023 | 0.00027721 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 929 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700175 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 10219 | keep | 0 | Apr | 2023 | 0.0069601 | 0.00063274 | Sustained | FALSE | FALSE | Not_TMED_Event | 929
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 21 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700175 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 231 | keep | 0 | Apr | 2023 | 0.00015733 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:09 | 262 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC LLEVA 1416-04 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700181 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-07 | 2096 | keep | 0 | Apr | 2023 | 0.0014276 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:09 | 296 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC LLEVA 1416-03 LLEVA 1418-05 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700181 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-07 | 2368 | keep | 0 | Apr | 2023 | 0.0016128 | 0.0002016 | Sustained | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:09 | 79 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC CARGA POR 1416-02 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700181 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-07 | 632 | keep | 0 | Apr | 2023 | 0.00043045 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:09 | 1129 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC CARGA POR 1416-01 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700181 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-07 | 9032 | keep | 0 | Apr | 2023 | 0.0061517 | 0.00076896 | Sustained | FALSE | FALSE | Not_TMED_Event | 1129
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:09 | 1573 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY GIS AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700181 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-07 | 12584 | keep | 0 | Apr | 2023 | 0.0085709 | 0.0010714 | Sustained | FALSE | FALSE | Not_TMED_Event | 1573
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 849 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 16980 | keep | 0 | Apr | 2023 | 0.011565 | 0.00057825 | Sustained | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 893 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 17860 | keep | 0 | Apr | 2023 | 0.012164 | 0.00060822 | Sustained | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 602 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 12040 | keep | 0 | Apr | 2023 | 0.0082004 | 0.00041002 | Sustained | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 43 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 860 | keep | 0 | Apr | 2023 | 0.00058574 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 1389 | 0:20 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700173 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 27780 | keep | 0 | Apr | 2023 | 0.018921 | 0.00094604 | Sustained | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:21 | 4 | 0:20 | T | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC CARGA POR 1404-09 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700194 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 20 | 2023-04-07 | 80 | keep | 0 | Apr | 2023 | 5.4488e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 673 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700180 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 3365 | keep | 0 | Apr | 2023 | 0.0022919 | 0.00045838 | Momentary | FALSE | FALSE | Not_TMED_Event | 673
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 372 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700180 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 1860 | keep | 0 | Apr | 2023 | 0.0012668 | 0.00025337 | Momentary | FALSE | FALSE | Not_TMED_Event | 372
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 732 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700180 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 3660 | keep | 0 | Apr | 2023 | 0.0024928 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 721 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 3605 | keep | 0 | Apr | 2023 | 0.0024553 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 325 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 1625 | keep | 0 | Apr | 2023 | 0.0011068 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 600 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY GIS AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 3000 | keep | 0 | Apr | 2023 | 0.0020433 | 0.00040866 | Momentary | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 267 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 1335 | keep | 0 | Apr | 2023 | 0.00090926 | 0.00018185 | Momentary | FALSE | FALSE | Not_TMED_Event | 267
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 621 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700174 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 3105 | keep | 0 | Apr | 2023 | 0.0021148 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 2203 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 11015 | keep | 0 | Apr | 2023 | 0.0075023 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 246 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 1230 | keep | 0 | Apr | 2023 | 0.00083775 | 0.00016755 | Momentary | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:06 | 9 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC LLEVA 100% 1348-07 LLEVA 80% 1346-06 LLEVA 20% 1336-08 AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. LLEVA 1401-10 | S23040700178 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-07 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 514 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700192 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 5654 | keep | 0 | Apr | 2023 | 0.0038509 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 681 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700192 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 7491 | keep | 0 | Apr | 2023 | 0.0051021 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 752 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700192 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 8272 | keep | 0 | Apr | 2023 | 0.005634 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2023-04-07 15:01 | 2023-04-07 15:12 | 68 | 0:11 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 2 HATO REY TC AVERIA EN BUS SUPPORT BAJA DEL BANCO #1 115/38KV HATO REY TC, ESTA AFECTO BUS SUPPORT BAJA BANCO #2 115/38KV. | S23040700192 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 11 | 2023-04-07 | 748 | keep | 0 | Apr | 2023 | 0.00050946 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
CANOVANAS | 2023-04-07 15:31 | 2023-04-07 18:20 | 1 | 2:49 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE CORTE DE LINEA | R23040700125 | New_Event | Primary Wire Break | Include | Include | Equipment | 169 | 2023-04-07 | 169 | keep | 0 | Apr | 2023 | 0.00011511 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-07 15:49 | 2023-04-07 18:55 | 60 | 3:06 | P | MAL TIEMPO/RAYOS | 1 X 80 Y 2 X 65 EN C/L MAL TIEMPO RAYOS | B23040700338 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 186 | 2023-04-07 | 11160 | keep | 0 | Apr | 2023 | 0.007601 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-04-07 15:49 | 2023-04-07 17:37 | 200 | 1:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO LLUVIAS | B23040700377 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 108 | 2023-04-07 | 21600 | keep | 0 | Apr | 2023 | 0.014712 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-07 16:03 | 2023-04-07 20:36 | 362 | 4:33 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA CON VOLTAJE SIN CARGA | S23040700219 | New_Event | Primary Wire Break | Include | Include | Equipment | 273 | 2023-04-07 | 98826 | keep | 0 | Apr | 2023 | 0.06731 | 0.00024656 | Sustained | FALSE | FALSE | Not_TMED_Event | 362
AGUADILLA | 2023-04-07 16:07 | 2023-04-07 19:55 | 100 | 3:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M23040700573 | New_Event | Primary Wire Break | Include | Include | Equipment | 228 | 2023-04-07 | 22800 | keep | 0 | Apr | 2023 | 0.015529 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-07 16:11 | 2023-04-07 18:30 | 150 | 2:19 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA POR RAYO | M23040700575 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 139 | 2023-04-07 | 20850 | keep | 0 | Apr | 2023 | 0.014201 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-04-07 16:12 | 2023-04-07 20:01 | 40 | 3:49 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA POR RAYOS | M23040700183 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 229 | 2023-04-07 | 9160 | keep | 0 | Apr | 2023 | 0.0062388 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-07 16:14 | 2023-04-07 21:45 | 57 | 5:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23040700364 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2023-04-07 | 18867 | keep | 0 | Apr | 2023 | 0.01285 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
CANOVANAS | 2023-04-07 16:30 | 2023-04-07 17:23 | 26 | 0:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS | R23040700135 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 53 | 2023-04-07 | 1378 | keep | 0 | Apr | 2023 | 0.00093855 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2023-04-07 16:31 | 2023-04-07 18:24 | 27 | 1:53 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE PRIMARIO DE LINEA A CAJA DE TRANSFORMADOR | C23040700113 | New_Event | Primary Wire Break | Include | Include | Equipment | 113 | 2023-04-07 | 3051 | keep | 0 | Apr | 2023 | 0.002078 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-04-07 16:36 | 2023-04-07 19:22 | 13 | 2:46 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR SE REEMPLAZO XMR DE 37.5KVA POR UNO DE IGUAL CAPACIDAD | R23040700136 | New_Event | Service Transformer Failure | Include | Include | Equipment | 166 | 2023-04-07 | 2158 | keep | 0 | Apr | 2023 | 0.0014698 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-07 16:40 | 2023-04-07 17:05 | 9 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23040700384 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-04-07 | 225 | keep | 0 | Apr | 2023 | 0.00015325 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-04-07 16:51 | 2023-04-07 16:52 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23040700201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2697 | keep | 0 | Apr | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
BAYAMON | 2023-04-07 17:01 | 2023-04-07 17:03 | 2402 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-07 | 4804 | keep | 0 | Apr | 2023 | 0.003272 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-07 17:03 | 2023-04-07 17:26 | 1922 | 0:23 | P | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | New_Event | Switch Failure | Include | Include | Equipment | 23 | 2023-04-07 | 44206 | keep | 0 | Apr | 2023 | 0.030109 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
YAUCO | 2023-04-07 17:07 | 2023-04-07 21:50 | 80 | 4:43 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700620 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 283 | 2023-04-07 | 22640 | keep | 0 | Apr | 2023 | 0.01542 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-04-07 17:14 | 2023-04-07 18:49 | 140 | 1:35 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA | C23040700115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-04-07 | 13300 | keep | 0 | Apr | 2023 | 0.0090586 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
YAUCO | 2023-04-07 17:25 | 2023-04-07 18:20 | 30 | 0:55 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA POR RAYOS | M23040700149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 55 | 2023-04-07 | 1650 | keep | 0 | Apr | 2023 | 0.0011238 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-07 17:26 | 2023-04-07 17:45 | 961 | 0:19 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-04-07 | 18259 | keep | 0 | Apr | 2023 | 0.012436 | 0.00065453 | Sustained | FALSE | FALSE | Not_TMED_Event | 961
BAYAMON | 2023-04-07 17:45 | 2023-04-07 17:46 | 2402 | 0:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-07 | 2402 | keep | 0 | Apr | 2023 | 0.001636 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-07 17:46 | 2023-04-07 18:08 | 961 | 0:22 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-04-07 | 21142 | keep | 0 | Apr | 2023 | 0.0144 | 0.00065453 | Sustained | FALSE | FALSE | Not_TMED_Event | 961
BAYAMON | 2023-04-07 17:49 | 2023-04-07 17:52 | 1408 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION PARA ABRIR MACHETE Y SECCIONALIZAR CONDUCTOR EN EL SUELO BY-230407-03 CARGA POR EL 1714-03 | B23040700432 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-07 | 4224 | keep | 0 | Apr | 2023 | 0.0028769 | 0.00095898 | Momentary | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2023-04-07 17:49 | 2023-04-07 17:52 | 455 | 0:03 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR A PETICION PARA ABRIR MACHETE Y SECCIONALIZAR CONDUCTOR EN EL SUELO BY-230407-03 LLEVA LA CARGA DEL 1714-02 | B23040700432 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-07 | 1365 | keep | 0 | Apr | 2023 | 0.0009297 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
BAYAMON | 2023-04-07 17:52 | 2023-04-07 18:25 | 1197 | 0:33 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO Y SE REALIZARON OPERACION PARA DAR SERVICIO BY-230407-03 CARGA POR EL 1714-03 | B23040700432 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 33 | 2023-04-07 | 39501 | keep | 0 | Apr | 2023 | 0.026904 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
PONCE | 2023-04-07 17:56 | 2023-04-07 17:57 | 485 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040700259 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 485 | keep | 0 | Apr | 2023 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
VEGA BAJA | 2023-04-07 18:05 | 2023-04-07 18:50 | 400 | 0:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA POR LLUVIA Y VIENTO | A23040700242 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 45 | 2023-04-07 | 18000 | keep | 0 | Apr | 2023 | 0.01226 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-04-07 18:08 | 2023-04-07 18:12 | 2402 | 0:04 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 | B23040700140 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-04-07 | 9608 | keep | 0 | Apr | 2023 | 0.006544 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-07 18:12 | 2023-04-07 19:10 | 480 | 0:58 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO BY-230407-02 SE REEMPLAZARON MACHETES Y SE REALIZO DESGANCHE PRIMARIO | B23040700140 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-04-07 | 27840 | keep | 0 | Apr | 2023 | 0.018962 | 0.00032693 | Sustained | FALSE | FALSE | Not_TMED_Event | 480
BAYAMON | 2023-04-07 18:25 | 2023-04-08 16:46 | 211 | 22:21 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO Y LEVANTO CONDUCTOR PRIMARIO BY-230407-03 CARGA POR EL 1714-03 | B23040700432 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1341 | 2023-04-07 | 282951 | keep | 0 | Apr | 2023 | 0.19272 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-04-07 18:41 | 2023-04-07 20:25 | 84 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CORTE DE LINEA POR PUENTE ABIERTO SE TRABAJAR MAÃ‘ANA QUEDARON 30 CLIENTES | C23040700125 | New_Event | Primary Wire Break | Include | Include | Equipment | 104 | 2023-04-07 | 8736 | keep | 0 | Apr | 2023 | 0.00595 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
SAN JUAN | 2023-04-07 18:51 | 2023-04-07 18:52 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 4291 | keep | 0 | Apr | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2023-04-07 18:54 | 2023-04-07 18:55 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 5252 | keep | 0 | Apr | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
YAUCO | 2023-04-07 18:59 | 2023-04-07 19:23 | 10 | 0:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P23040700260 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 24 | 2023-04-07 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-07 19:03 | 2023-04-08 03:04 | 80 | 8:01 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700686 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 481 | 2023-04-07 | 38480 | keep | 0 | Apr | 2023 | 0.026209 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-07 19:04 | 2023-04-07 22:51 | 144 | 3:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | B23040700444 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 227 | 2023-04-07 | 32688 | keep | 0 | Apr | 2023 | 0.022264 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
BAYAMON | 2023-04-07 19:04 | 2023-04-07 19:05 | 172 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23040700654 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 172 | keep | 0 | Apr | 2023 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2023-04-07 19:08 | 2023-04-07 22:40 | 463 | 3:32 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE CERRO PUENTE DE CAJA A LINEA | C23040700136 | New_Event | Primary Wire Break | Include | Include | Equipment | 212 | 2023-04-07 | 98156 | keep | 0 | Apr | 2023 | 0.066854 | 0.00031535 | Sustained | FALSE | FALSE | Not_TMED_Event | 463
MAYAGÃœEZ | 2023-04-07 19:09 | 2023-04-08 14:12 | 85 | 19:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA PUENTE PRIMARIO ROTO | M23040700692 | New_Event | Primary Wire Break | Include | Include | Equipment | 1143 | 2023-04-07 | 97155 | keep | 0 | Apr | 2023 | 0.066172 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2023-04-07 19:12 | 2023-04-07 19:13 | 2379 | 0:01 | T | ANIMAL | RECIERRE | P23040700261 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-07 | 2379 | keep | 0 | Apr | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2023-04-07 19:13 | 2023-04-07 22:04 | 100 | 2:51 | P | ANIMAL | 1 X 100 2 X 65 EN DIFERENTES CORTES DE LINEA POR ANIMAL | P23040700271 | 1st_after_momentary | Animals | Include | Include | Wildlife | 171 | 2023-04-07 | 17100 | keep | 0 | Apr | 2023 | 0.011647 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-07 19:13 | 2023-04-07 19:15 | 2610 | 0:02 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23040700447 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-07 | 5220 | keep | 0 | Apr | 2023 | 0.0035553 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
PONCE | 2023-04-07 19:20 | 2023-04-07 19:23 | 5063 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL SCADA | P23040700264 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-07 | 15189 | keep | 0 | Apr | 2023 | 0.010345 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
MAYAGÃœEZ | 2023-04-07 19:20 | 2023-04-08 16:30 | 50 | 21:10 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMA | M23040700699 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1270 | 2023-04-07 | 63500 | keep | 0 | Apr | 2023 | 0.04325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-04-07 19:27 | 2023-04-07 22:59 | 30 | 3:32 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA POR DESCARGAS ELECTRICAS | M23040700706 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 212 | 2023-04-07 | 6360 | keep | 0 | Apr | 2023 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-07 19:30 | 2023-04-08 00:13 | 174 | 4:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | B23040700453 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 283 | 2023-04-07 | 49242 | keep | 0 | Apr | 2023 | 0.033539 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
MAYAGÃœEZ | 2023-04-07 19:31 | 2023-04-08 12:56 | 60 | 17:25 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA ROEDOR CRUZO LINEAS | M23040700708 | New_Event | Animals | Include | Include | Wildlife | 1045 | 2023-04-07 | 62700 | keep | 0 | Apr | 2023 | 0.042705 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-04-07 19:31 | 2023-04-07 19:32 | 3000 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | B2304070000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-07 | 3000 | keep | 0 | Apr | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2023-04-07 19:32 | 2023-04-07 21:44 | 6 | 2:12 | P | MAL TIEMPO/RAYOS | 1 X 20 EN XMR RAYOS | B23040700454 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 132 | 2023-04-07 | 792 | keep | 0 | Apr | 2023 | 0.00053943 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-07 19:32 | 2023-04-07 22:12 | 12 | 2:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO | B23040700456 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 160 | 2023-04-07 | 1920 | keep | 0 | Apr | 2023 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-07 19:36 | 2023-04-08 10:47 | 12 | 15:11 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR IGUANA | S23040700305 | New_Event | Animals | Include | Include | Wildlife | 911 | 2023-04-07 | 10932 | keep | 0 | Apr | 2023 | 0.0074457 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-04-07 19:38 | 2023-04-08 06:26 | 40 | 10:48 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L RAYOS | C23040700140 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 648 | 2023-04-07 | 25920 | keep | 0 | Apr | 2023 | 0.017654 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-04-07 19:38 | 2023-04-08 12:50 | 35 | 17:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P23040700270 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1032 | 2023-04-07 | 36120 | keep | 0 | Apr | 2023 | 0.024601 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-04-07 19:49 | 2023-04-07 21:30 | 71 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23040700145 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2023-04-07 | 7171 | keep | 0 | Apr | 2023 | 0.0048841 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
MAYAGÃœEZ | 2023-04-07 19:50 | 2023-04-08 09:45 | 80 | 13:55 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700726 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 835 | 2023-04-07 | 66800 | keep | 0 | Apr | 2023 | 0.045497 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-04-07 19:57 | 2023-04-08 00:45 | 70 | 4:48 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M23040700739 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2023-04-07 | 20160 | keep | 0 | Apr | 2023 | 0.013731 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-04-07 20:07 | 2023-04-07 23:40 | 722 | 3:33 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23040700164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-04-07 | 153786 | keep | 0 | Apr | 2023 | 0.10474 | 0.00049175 | Sustained | FALSE | FALSE | Not_TMED_Event | 722
FAJARDO | 2023-04-07 20:16 | 2023-04-08 12:12 | 10 | 15:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 50KVA | R23040700148 | New_Event | Service Transformer Failure | Include | Include | Equipment | 956 | 2023-04-07 | 9560 | keep | 0 | Apr | 2023 | 0.0065113 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-07 20:17 | 2023-04-08 16:30 | 1 | 20:13 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRCIAS | M23040700750 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1213 | 2023-04-07 | 1213 | keep | 0 | Apr | 2023 | 0.00082617 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-07 20:25 | 2023-04-08 10:33 | 50 | 14:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L SE REPARO BAJANTE DE LINEA A CAJA | C23040700125 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 848 | 2023-04-07 | 42400 | keep | 0 | Apr | 2023 | 0.028878 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-07 20:32 | 2023-04-08 10:50 | 20 | 14:18 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700756 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 858 | 2023-04-07 | 17160 | keep | 0 | Apr | 2023 | 0.011688 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-07 20:45 | 2023-04-07 20:46 | 2610 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B2304070000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-07 | 2610 | keep | 0 | Apr | 2023 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
BAYAMON | 2023-04-07 21:00 | 2023-04-08 16:52 | 33 | 19:52 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L MAL TIEMPO RAYO | B23040700475 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1192 | 2023-04-07 | 39336 | keep | 0 | Apr | 2023 | 0.026792 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
MAYAGÃœEZ | 2023-04-07 21:12 | 2023-04-08 10:48 | 1 | 13:36 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS RELACIONADO A EVENTO M23040700767 QUE CERRARON | M23040800049 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 816 | 2023-04-07 | 816 | keep | 0 | Apr | 2023 | 0.00055577 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-07 21:29 | 2023-04-07 23:49 | 60 | 2:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M23040700787 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 140 | 2023-04-07 | 8400 | keep | 0 | Apr | 2023 | 0.0057212 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-04-07 21:30 | 2023-04-08 12:10 | 35 | 14:40 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040700301 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 880 | 2023-04-07 | 30800 | keep | 0 | Apr | 2023 | 0.020978 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-04-07 21:46 | 2023-04-08 12:04 | 1 | 14:18 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO CAJA | A23040700303 | New_Event | Animals | Include | Include | Wildlife | 858 | 2023-04-07 | 858 | keep | 0 | Apr | 2023 | 0.00058438 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-07 21:49 | 2023-04-07 21:50 | 2610 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B2304070000X | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-07 | 2610 | keep | 0 | Apr | 2023 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2023-04-07 21:52 | 2023-04-07 22:35 | 2610 | 0:43 | T | DESGANCHE | DISPARO DE INTERRUPTOR PROBO MALO BY-230407-04 SE SECCIONALIZO TRAMO PARA REALIZAR DESGANCHE A VARETA DE PISO. 90% EN SERVICIO | B23040700490 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 43 | 2023-04-07 | 112230 | keep | 0 | Apr | 2023 | 0.076439 | 0.0017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 2610
CAGUAS | 2023-04-07 21:57 | 2023-04-08 08:52 | 80 | 10:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN RISER FUERTES LLUVIAS | C23040700153 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 655 | 2023-04-07 | 52400 | keep | 0 | Apr | 2023 | 0.035689 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-07 22:19 | 2023-04-08 02:20 | 430 | 4:01 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23040700150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2023-04-07 | 103630 | keep | 0 | Apr | 2023 | 0.070582 | 0.00029287 | Sustained | FALSE | FALSE | Not_TMED_Event | 430
VEGA BAJA | 2023-04-07 22:35 | 2023-04-08 00:57 | 261 | 2:22 | P | DESGANCHE | DISPARO DE INTERRUPTOR PROBO MALO BY-230407-04 SE REALIZO DESGANCHE A VARETA DE PISO. ENTRO EL 10% QUE FALTABA. 100% EN SERVICIO | B23040700490 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-04-07 | 37062 | keep | 0 | Apr | 2023 | 0.025243 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-07 22:45 | 2023-04-07 22:46 | 1250 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040700171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1250 | keep | 0 | Apr | 2023 | 0.00085137 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
AGUADILLA | 2023-04-07 22:49 | 2023-04-08 08:55 | 6 | 10:06 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23040700782 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 606 | 2023-04-07 | 3636 | keep | 0 | Apr | 2023 | 0.0024765 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-04-07 22:55 | 2023-04-07 22:56 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040700175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 853 | keep | 0 | Apr | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
MAYAGÃœEZ | 2023-04-07 22:58 | 2023-04-07 22:59 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040700783 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1825 | keep | 0 | Apr | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
AGUADILLA | 2023-04-07 23:02 | 2023-04-08 12:00 | 20 | 12:58 | P | MAL TIEMPO/RAYOS | 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23040700017 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 778 | 2023-04-07 | 15560 | keep | 0 | Apr | 2023 | 0.010598 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-07 23:06 | 2023-04-08 12:50 | 10 | 13:44 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23040700309 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 824 | 2023-04-07 | 8240 | keep | 0 | Apr | 2023 | 0.0056122 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-07 23:14 | 2023-04-07 23:15 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23040700152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 2039 | keep | 0 | Apr | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
PONCE | 2023-04-07 23:25 | 2023-04-07 23:26 | 948 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23040700297 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-07 | 948 | keep | 0 | Apr | 2023 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
PONCE | 2023-04-07 23:25 | 2023-04-07 23:26 | 7 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23040700297 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-07 | 7 | keep | 0 | Apr | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-04-07 23:25 | 2023-04-07 23:26 | 114 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23040700297 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-07 | 114 | keep | 0 | Apr | 2023 | 7.7645e-05 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
PONCE | 2023-04-07 23:25 | 2023-04-07 23:26 | 2113 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23040700297 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-07 | 2113 | keep | 0 | Apr | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2023-04-07 23:25 | 2023-04-07 23:26 | 1478 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23040700297 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-07 | 1478 | keep | 0 | Apr | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
PONCE | 2023-04-07 23:25 | 2023-04-07 23:26 | 396 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE | P23040700297 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-07 | 396 | keep | 0 | Apr | 2023 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
BAYAMON | 2023-04-07 23:27 | 2023-04-08 09:48 | 24 | 10:21 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B23040700563 | New_Event | Vegetation Contact | Include | Include | Vegetation | 621 | 2023-04-07 | 14904 | keep | 0 | Apr | 2023 | 0.010151 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BARRANQUITAS | 2023-04-07 23:31 | 2023-04-08 13:26 | 35 | 13:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C23040700178 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 835 | 2023-04-07 | 29225 | keep | 0 | Apr | 2023 | 0.019905 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-04-07 23:37 | 2023-04-07 23:38 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040700180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2023-04-07 23:54 | 2023-04-07 23:55 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S2304070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-07 | 1615 | keep | 0 | Apr | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
HUMACAO | 2023-04-07 23:57 | 2023-04-07 23:58 | 2873 | 0:01 | T | MAL TIEMPO/RAYOS | RECERRO INTERRUPTOR EN SERVICIO | C23040700188 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-07 | 2873 | keep | 0 | Apr | 2023 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
HUMACAO | 2023-04-07 23:58 | 2023-04-08 08:43 | 41 | 8:45 | P | MAL TIEMPO/RAYOS | 1X65 EN C/L POR RAYO | C23040700184 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 525 | 2023-04-07 | 21525 | keep | 0 | Apr | 2023 | 0.014661 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
HUMACAO | 2023-04-07 23:59 | 2023-04-08 07:37 | 280 | 7:38 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 2 X 80 Y 1 X 100 EN C/LS REMPLAZO LIGADURA LEVANTO CONDUCTOR Y REMPLAZO CAJA AVERIADA | C23040700187 | New_Event | Primary Wire Break | Include | Include | Equipment | 458 | 2023-04-07 | 128240 | keep | 0 | Apr | 2023 | 0.087344 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
HUMACAO | 2023-04-08 | 2023-04-08 12:48 | 80 | 12:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES LLUVIAS | C23040800001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 768 | 2023-04-08 | 61440 | keep | 0 | Apr | 2023 | 0.041847 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-04-08 | 2023-04-08 00:01 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040800002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 676 | keep | 0 | Apr | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
SAN JUAN | 2023-04-08 00:05 | 2023-04-08 00:07 | 4291 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL | S2304080000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-04-08 | 8582 | keep | 0 | Apr | 2023 | 0.0058452 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
HUMACAO | 2023-04-08 00:18 | 2023-04-08 12:15 | 25 | 11:57 | P | DESGANCHE | 1 X 40 EN C/L | C23040800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 717 | 2023-04-08 | 17925 | keep | 0 | Apr | 2023 | 0.012209 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-08 00:19 | 2023-04-08 14:11 | 13 | 13:52 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23040800008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 832 | 2023-04-08 | 10816 | keep | 0 | Apr | 2023 | 0.0073667 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:34 | 693 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2810 HOSP. DTTO. CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800030 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-04-08 | 4158 | keep | 0 | Apr | 2023 | 0.002832 | 0.000472 | Sustained | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:34 | 47 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2810 HOSP. DTTO. CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800030 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-04-08 | 282 | keep | 0 | Apr | 2023 | 0.00019207 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:34 | 1256 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2810 HOSP. DTTO. CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800030 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-04-08 | 7536 | keep | 0 | Apr | 2023 | 0.0051327 | 0.00085546 | Sustained | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:34 | 558 | 0:06 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2810 HOSP. DTTO. CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800030 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 6 | 2023-04-08 | 3348 | keep | 0 | Apr | 2023 | 0.0022803 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:36 | 1192 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800032 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-08 | 9536 | keep | 0 | Apr | 2023 | 0.0064949 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:36 | 3041 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800032 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-08 | 24328 | keep | 0 | Apr | 2023 | 0.01657 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:36 | 390 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800032 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-08 | 3120 | keep | 0 | Apr | 2023 | 0.002125 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:36 | 650 | 0:08 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800032 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 8 | 2023-04-08 | 5200 | keep | 0 | Apr | 2023 | 0.0035417 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 569 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800027 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 2845 | keep | 0 | Apr | 2023 | 0.0019377 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 1245 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800027 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 6225 | keep | 0 | Apr | 2023 | 0.0042398 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 1155 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800027 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 5775 | keep | 0 | Apr | 2023 | 0.0039333 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 867 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800028 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 4335 | keep | 0 | Apr | 2023 | 0.0029525 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 257 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800028 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 1285 | keep | 0 | Apr | 2023 | 0.00087521 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 1336 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800028 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 6680 | keep | 0 | Apr | 2023 | 0.0045497 | 0.00090994 | Momentary | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 3315 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800029 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 16575 | keep | 0 | Apr | 2023 | 0.011289 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:33 | 1718 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV OPERO BKR 2510 SAN SEBASTIAN CON DISPARO BARRA #1 38KV VICTORIA TC | M23040800029 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-04-08 | 8590 | keep | 0 | Apr | 2023 | 0.0058506 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:35 | 154 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-04-08 | 1078 | keep | 0 | Apr | 2023 | 0.00073422 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:35 | 1261 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-04-08 | 8827 | keep | 0 | Apr | 2023 | 0.006012 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:35 | 3894 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-04-08 | 27258 | keep | 0 | Apr | 2023 | 0.018565 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:35 | 997 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-04-08 | 6979 | keep | 0 | Apr | 2023 | 0.0047534 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-04-08 00:28 | 2023-04-08 00:35 | 1497 | 0:07 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA VICTORIA 38KV | M23040800031 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 7 | 2023-04-08 | 10479 | keep | 0 | Apr | 2023 | 0.0071372 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
BARRANQUITAS | 2023-04-08 00:30 | 2023-04-08 04:24 | 3463 | 3:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETES DE BARRA DE INSPECCION QUE ESTABAN CALENTANDO, TIENE AISLADOR ROTO. | C23040800026 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 234 | 2023-04-08 | 810342 | keep | 0 | Apr | 2023 | 0.55192 | 0.0023586 | Sustained | FALSE | FALSE | Not_TMED_Event | 3463
CANOVANAS | 2023-04-08 00:47 | 2023-04-08 02:18 | 68 | 1:31 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | R23040800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-04-08 | 6188 | keep | 0 | Apr | 2023 | 0.0042146 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2023-04-08 00:49 | 2023-04-08 12:23 | 14 | 11:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | B23040800009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 694 | 2023-04-08 | 9716 | keep | 0 | Apr | 2023 | 0.0066175 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-04-08 00:56 | 2023-04-08 09:37 | 14 | 8:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23040800014 | New_Event | Cutout Failure | Include | Include | Equipment | 521 | 2023-04-08 | 7294 | keep | 0 | Apr | 2023 | 0.0049679 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-04-08 01:05 | 2023-04-08 01:06 | 2141 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040800042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 2141 | keep | 0 | Apr | 2023 | 0.0014582 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
PONCE | 2023-04-08 01:11 | 2023-04-08 03:28 | 1746 | 2:17 | T | TERMINACION SOTERRADA AVERIADA | SE ABRE MACHETES EN CALLE CRISTOBAL COLON Y SE LE DA PRUEBA Y QUEDA EN SERVICIO FID 1000110566 Y SE AMARRA CON EL 5018-04 DEJANDO EL CASCO URBANO FUERA | P23040800015 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 137 | 2023-04-08 | 239202 | keep | 0 | Apr | 2023 | 0.16292 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
CAGUAS | 2023-04-08 01:20 | 2023-04-08 01:21 | 3495 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SOLO LLEVA EL 80% DE SU CARGA | C2303090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 3495 | keep | 0 | Apr | 2023 | 0.0023804 | 0.0023804 | Momentary | FALSE | FALSE | Not_TMED_Event | 3495
SAN JUAN | 2023-04-08 01:23 | 2023-04-08 14:03 | 225 | 12:40 | T | DESGANCHE | SJ-230408-01 SE REMPLAZO MACHETES, AISLADOR Y SE RETIRO BAMBUAS 75% EN SERVICIO | S23040800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 760 | 2023-04-08 | 171000 | keep | 0 | Apr | 2023 | 0.11647 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
HUMACAO | 2023-04-08 01:34 | 2023-04-08 01:35 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 3 | keep | 0 | Apr | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-04-08 01:36 | 2023-04-08 01:37 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040800046 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 676 | keep | 0 | Apr | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CANOVANAS | 2023-04-08 01:37 | 2023-04-08 01:38 | 424 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE LLUVIA FUERTE | R23040800003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-08 | 424 | keep | 0 | Apr | 2023 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
GUAYAMA | 2023-04-08 01:38 | 2023-04-08 01:39 | 1730 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040800022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 1730 | keep | 0 | Apr | 2023 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
CAGUAS | 2023-04-08 01:43 | 2023-04-08 09:33 | 60 | 7:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES LLUVIAS | C23040800050 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 470 | 2023-04-08 | 28200 | keep | 0 | Apr | 2023 | 0.019207 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-04-08 01:54 | 2023-04-08 04:47 | 3041 | 2:53 | T | PROBLEMA DEL CLIENTE | SE ABRIO MACHETE PARA SECCIONALIZAR ALIMENTADOR Y SE CERRO EL INTERRUPTOR SE ENCONTRO AVERIA EN RISER CON PROBLEMA INTERNO DEL CLIENTE | M23040800049 | New_Event | Customer-Related Interruption | Include | Include | Public | 173 | 2023-04-08 | 526093 | keep | 0 | Apr | 2023 | 0.35832 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
GUAYAMA | 2023-04-08 01:59 | 2023-04-08 10:43 | 55 | 8:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P23040800027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 524 | 2023-04-08 | 28820 | keep | 0 | Apr | 2023 | 0.019629 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CANOVANAS | 2023-04-08 02:10 | 2023-04-08 02:11 | 1026 | 0:01 | T | CONDUCTOR ARRIADO O CRUZADO | RECERRO INTERRUPTOR EN SERVICIO | R23040800004 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1 | 2023-04-08 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-08 02:13 | 2023-04-08 03:41 | 1026 | 1:28 | T | CONDUCTOR ARRIADO O CRUZADO | MUCHA LLUVIA Y SE DESPEGO BAJANTE DE PARARRAYO CON VARETA, CERRADO POR CONTROL | R23040800005 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 88 | 2023-04-08 | 90288 | keep | 0 | Apr | 2023 | 0.061495 | 0.0006988 | Sustained | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-08 02:18 | 2023-04-08 02:19 | 5062 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 5062 | keep | 0 | Apr | 2023 | 0.0034477 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
CANOVANAS | 2023-04-08 02:19 | 2023-04-08 12:08 | 68 | 9:49 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | R23040800001 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 589 | 2023-04-08 | 40052 | keep | 0 | Apr | 2023 | 0.027279 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 02:20 | 2023-04-08 02:21 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 5252 | keep | 0 | Apr | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
CAGUAS | 2023-04-08 02:28 | 2023-04-08 02:29 | 2178 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C2304080000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-08 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CANOVANAS | 2023-04-08 02:37 | 2023-04-08 02:38 | 1862 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE LLUVIA FUERTE | R23040800008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-08 | 1862 | keep | 0 | Apr | 2023 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
BARRANQUITAS | 2023-04-08 02:39 | 2023-04-08 02:40 | 1131 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040800063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 1131 | keep | 0 | Apr | 2023 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
BAYAMON | 2023-04-08 02:45 | 2023-04-08 11:54 | 40 | 9:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | B23040800016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 549 | 2023-04-08 | 21960 | keep | 0 | Apr | 2023 | 0.014957 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-08 02:47 | 2023-04-08 02:50 | 363 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL 90% POR EL 1620-01 | S2304080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-08 | 1089 | keep | 0 | Apr | 2023 | 0.00074171 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
SAN JUAN | 2023-04-08 02:47 | 2023-04-08 02:50 | 36 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL LLEVANDO 90% DEL 1336-10 LLEVANDO 60% 1620-02 LLUVIA FUERTE | S2304080000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2023-04-08 | 108 | keep | 0 | Apr | 2023 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-04-08 02:47 | 2023-04-08 02:50 | 2231 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL 60% POR EL 1620-01 | S2304080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-08 | 6693 | keep | 0 | Apr | 2023 | 0.0045586 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
HUMACAO | 2023-04-08 02:47 | 2023-04-08 02:48 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23040800065 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 676 | keep | 0 | Apr | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2023-04-08 02:50 | 2023-04-08 14:51 | 7 | 12:01 | P | MAL TIEMPO/RAYOS | 1X10 EN XMR POR RAYO | C23040800066 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 721 | 2023-04-08 | 5047 | keep | 0 | Apr | 2023 | 0.0034375 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-08 02:51 | 2023-04-08 08:53 | 23 | 6:02 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN C/L POR FASE ARRIADA TOCANDO POSTE | B23040800017 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 362 | 2023-04-08 | 8326 | keep | 0 | Apr | 2023 | 0.0056708 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2023-04-08 03:02 | 2023-04-08 06:57 | 2178 | 3:55 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR | C23040800067 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-04-08 | 511830 | keep | 0 | Apr | 2023 | 0.34861 | 0.0014834 | Sustained | FALSE | FALSE | Not_TMED_Event | 2178
MAYAGÃœEZ | 2023-04-08 03:04 | 2023-04-08 03:05 | 4304 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DE INTERRUPTOR | M23040800053 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-08 | 4304 | keep | 0 | Apr | 2023 | 0.0029314 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-08 03:05 | 2023-04-08 09:32 | 80 | 6:27 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23040700686 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 387 | 2023-04-08 | 30960 | keep | 0 | Apr | 2023 | 0.021087 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-08 03:10 | 2023-04-08 03:13 | 867 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE CERRO POR CONTROL LLUVIA FUERTE | S2304080000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2023-04-08 | 2601 | keep | 0 | Apr | 2023 | 0.0017715 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
PONCE | 2023-04-08 03:28 | 2023-04-08 04:02 | 318 | 0:34 | T | TERMINACION SOTERRADA AVERIADA | SE ABRE MACHETES EN CALLE CRISTOBAL COLON Y SE LE DA PRUEBA Y QUEDA EN SERVICIO FID 1000110566 Y SE AMARRA CON EL 5018-04 DEJANDO EL CASCO URBANO FUERA | P23040800015 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 34 | 2023-04-08 | 10812 | keep | 0 | Apr | 2023 | 0.007364 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-08 03:35 | 2023-04-08 05:01 | 9 | 1:26 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA CRUZADA | P23040800035 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 86 | 2023-04-08 | 774 | keep | 0 | Apr | 2023 | 0.00052717 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2023-04-08 04:02 | 2023-04-08 09:26 | 479 | 5:24 | P | TERMINACION SOTERRADA AVERIADA | MACHETES ABIERTOS SECCIONALIZANDO AVERIA SOTERRADA EM MH#6 | P23040800054 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 324 | 2023-04-08 | 155196 | keep | 0 | Apr | 2023 | 0.1057 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-08 04:08 | 2023-04-08 08:44 | 33 | 4:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | P23040800046 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2023-04-08 | 9108 | keep | 0 | Apr | 2023 | 0.0062034 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
VEGA BAJA | 2023-04-08 04:19 | 2023-04-08 04:21 | 2610 | 0:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR SE CERRO POR CONTROL | B23040800019 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2023-04-08 | 5220 | keep | 0 | Apr | 2023 | 0.0035553 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
PONCE | 2023-04-08 04:38 | 2023-04-08 18:40 | 80 | 14:02 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS ARRIADAS | P23040800051 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 842 | 2023-04-08 | 67360 | keep | 0 | Apr | 2023 | 0.045879 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-04-08 04:38 | 2023-04-08 04:40 | 2610 | 0:02 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE BKR SE CERRO POR CONTROL | B23040800023 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 2 | 2023-04-08 | 5220 | keep | 0 | Apr | 2023 | 0.0035553 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
YAUCO | 2023-04-08 04:40 | 2023-04-08 04:41 | 508 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040800052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 508 | keep | 0 | Apr | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-04-08 04:40 | 2023-04-08 04:41 | 64 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23040800052 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-08 | 64 | keep | 0 | Apr | 2023 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
VEGA BAJA | 2023-04-08 04:41 | 2023-04-08 05:38 | 2610 | 0:57 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONAR TRAMO BY-230408-01 | B23040800031 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 57 | 2023-04-08 | 148770 | keep | 0 | Apr | 2023 | 0.10133 | 0.0017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 2610
MAYAGÃœEZ | 2023-04-08 04:45 | 2023-04-08 12:40 | 20 | 7:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040800067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2023-04-08 | 9500 | keep | 0 | Apr | 2023 | 0.0064704 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-08 04:47 | 2023-04-08 10:55 | 641 | 6:08 | P | PROBLEMA DEL CLIENTE | SE DESCONECTO RISER CON PROBLEMA INTERNO DEL CLIENTE Y SE CERRO MACHETES | M23040800049 | Partial_restoration | Customer-Related Interruption | Include | Include | Public | 368 | 2023-04-08 | 235888 | keep | 0 | Apr | 2023 | 0.16066 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-08 04:51 | 2023-04-08 07:13 | 1905 | 2:22 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE ALIMENTADOR POR LINEA PRIMARIA CRUZADA | P23040800057 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 142 | 2023-04-08 | 270510 | keep | 0 | Apr | 2023 | 0.18424 | 0.0012975 | Sustained | FALSE | FALSE | Not_TMED_Event | 1905
GUAYAMA | 2023-04-08 05:01 | 2023-04-08 05:02 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040800061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 4132 | keep | 0 | Apr | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2023-04-08 05:02 | 2023-04-08 12:15 | 9 | 7:13 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA ALAMBRE PRIMARIO CRUZADO | P23040800035 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 433 | 2023-04-08 | 3897 | keep | 0 | Apr | 2023 | 0.0026542 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-08 05:07 | 2023-04-08 09:22 | 95 | 4:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA RMA SOBRE LINEA | P23040800063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2023-04-08 | 24225 | keep | 0 | Apr | 2023 | 0.0165 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2023-04-08 05:09 | 2023-04-08 11:30 | 1337 | 6:21 | T | CONDUCTOR ARRIADO O CRUZADO | LINEAS CRUZADAS SE ABRIO MACHETES PARA SECCIONALIZAR Y CERRAR EL INTERRUPTOR | M23040800141 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 381 | 2023-04-08 | 509397 | keep | 0 | Apr | 2023 | 0.34695 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-04-08 05:14 | 2023-04-08 15:14 | 10 | 10:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M23040800072 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 600 | 2023-04-08 | 6000 | keep | 0 | Apr | 2023 | 0.0040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-08 05:15 | 2023-04-08 05:18 | 1447 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVANDO LA CARGA DEL 1419-09 SE CERRO POR CONTROL | S2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-08 | 4341 | keep | 0 | Apr | 2023 | 0.0029566 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2023-04-08 05:15 | 2023-04-08 05:18 | 266 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO CARGA POR EL 1112-04 SE CERRO POR CONTROL | S2304080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-08 | 798 | keep | 0 | Apr | 2023 | 0.00054351 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
BAYAMON | 2023-04-08 05:17 | 2023-04-08 11:45 | 72 | 6:28 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23040800028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2023-04-08 | 27936 | keep | 0 | Apr | 2023 | 0.019027 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2023-04-08 05:28 | 2023-04-08 05:29 | 341 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 341 | keep | 0 | Apr | 2023 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
VEGA BAJA | 2023-04-08 05:38 | 2023-04-08 06:03 | 131 | 0:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONAR TRAMO BY-230408-01 | B23040800031 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 25 | 2023-04-08 | 3275 | keep | 0 | Apr | 2023 | 0.0022306 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-08 05:40 | 2023-04-08 08:15 | 1615 | 2:35 | T | DESGANCHE | SE SECCIONALIZO PARA DESGANCHE MEDIANTE G.O.I. SJ-230408-50 - 70% EN SERVICIO | R23040800022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-04-08 | 250325 | keep | 0 | Apr | 2023 | 0.1705 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2023-04-08 05:43 | 2023-04-08 05:44 | 4291 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE LLUVIA FUERTE | S2304080000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-08 | 4291 | keep | 0 | Apr | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
VEGA BAJA | 2023-04-08 06:03 | 2023-04-08 07:28 | 2610 | 1:25 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONAR TRAMO BY-230408-01 | B23040800031 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 85 | 2023-04-08 | 221850 | keep | 0 | Apr | 2023 | 0.1511 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-08 06:06 | 2023-04-08 09:20 | 248 | 3:14 | P | DESGANCHE | 1 X 65 EN C/L SE RETIRO RAMA | S23040800063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-04-08 | 48112 | keep | 0 | Apr | 2023 | 0.032769 | 0.00016891 | Sustained | FALSE | FALSE | Not_TMED_Event | 248
CANOVANAS | 2023-04-08 06:29 | 2023-04-08 09:02 | 51 | 2:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X200 EN C/L PRINCIPAL POR LLUVIAS | R23040800026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 153 | 2023-04-08 | 7803 | keep | 0 | Apr | 2023 | 0.0053146 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
CAGUAS | 2023-04-08 06:29 | 2023-04-08 10:00 | 40 | 3:31 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L DESPEGO BAJANTE DE LINEA A CAJA DEL PARARRAYO | C23040800158 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 211 | 2023-04-08 | 8440 | keep | 0 | Apr | 2023 | 0.0057484 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-04-08 06:34 | 2023-04-08 06:36 | 2192 | 0:02 | T | PARARRAYOS DEFECTUOSO | DISPARO CERRADO X CONTROL | C2304080000X | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2023-04-08 | 4384 | keep | 0 | Apr | 2023 | 0.0029859 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
BARRANQUITAS | 2023-04-08 06:36 | 2023-04-08 10:07 | 44 | 3:31 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN C/L ELIMINO PARARRAYO CRUZADO | C23040800180 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 211 | 2023-04-08 | 9284 | keep | 0 | Apr | 2023 | 0.0063233 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2023-04-08 06:42 | 2023-04-08 09:14 | 116 | 2:32 | P | DESGANCHE | 2 X 80 EN SU Y DESGANCHE | S23040800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-04-08 | 17632 | keep | 0 | Apr | 2023 | 0.012009 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
HUMACAO | 2023-04-08 06:52 | 2023-04-08 14:35 | 277 | 7:43 | P | CONDUCTOR ROTO O ABIERTO | LEVANTO CONDUCTORES Y CERRO MACHETES | C23040800183 | New_Event | Primary Wire Break | Include | Include | Equipment | 463 | 2023-04-08 | 128251 | keep | 0 | Apr | 2023 | 0.087351 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
BAYAMON | 2023-04-08 06:54 | 2023-04-08 12:43 | 18 | 5:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L Y SE REPARO BAJANTE | B23040800045 | New_Event | Primary Wire Break | Include | Include | Equipment | 349 | 2023-04-08 | 6282 | keep | 0 | Apr | 2023 | 0.0042786 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-04-08 06:57 | 2023-04-08 07:56 | 1307 | 0:59 | P | DESGANCHE | SE REALIZO DESGANCHE Y CERRO MACHETES | C23040800191 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-04-08 | 77113 | keep | 0 | Apr | 2023 | 0.052521 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-08 07:04 | 2023-04-08 11:32 | 132 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 65 EN C/S LLUVIAS FUERTES | C23040800197 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-04-08 | 35376 | keep | 0 | Apr | 2023 | 0.024094 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
HUMACAO | 2023-04-08 07:06 | 2023-04-08 11:49 | 150 | 4:43 | P | DESGANCHE | 1 X 65 2 X 40 Y 1 X 30 DESGANCHE Y REEMPLAZO PIN POLE TOP | C23040800199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-04-08 | 42450 | keep | 0 | Apr | 2023 | 0.028913 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-08 07:15 | 2023-04-08 07:16 | 3597 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9405-05 LLEVA EL 1719-15 | B2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 3597 | keep | 0 | Apr | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
CANOVANAS | 2023-04-08 07:19 | 2023-04-08 12:46 | 12 | 5:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X15 DE AEREO PROVISIONAL @ T-75 POR LLUVIAS | R23040800057 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 327 | 2023-04-08 | 3924 | keep | 0 | Apr | 2023 | 0.0026726 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-08 07:20 | 2023-04-08 07:21 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9405-05 LLEVA EL 1719-15 | B2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 3511 | keep | 0 | Apr | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
VEGA BAJA | 2023-04-08 07:28 | 2023-04-08 08:15 | 1305 | 0:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONAR TRAMO BY-230408-01 | B23040800031 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 47 | 2023-04-08 | 61335 | keep | 0 | Apr | 2023 | 0.041775 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-08 07:32 | 2023-04-08 09:45 | 1 | 2:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 37.5 KVA X 37.5 KVA | A23040800010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 133 | 2023-04-08 | 133 | keep | 0 | Apr | 2023 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-08 07:38 | 2023-04-08 13:11 | 1400 | 5:33 | P | DESGANCHE | 2 X 140 1 X 200 1 X 50 Y 1 X 65 EN C/LS DESGANCHO Y FIJO CONDUCTOR | C23040800218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2023-04-08 | 466200 | keep | 0 | Apr | 2023 | 0.31753 | 0.00095353 | Sustained | FALSE | FALSE | Not_TMED_Event | 1400
CAGUAS | 2023-04-08 07:47 | 2023-04-08 20:12 | 100 | 12:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS FUERTES | C23040800230 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 745 | 2023-04-08 | 74500 | keep | 0 | Apr | 2023 | 0.050742 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-08 07:54 | 2023-04-08 12:42 | 18 | 4:48 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | S23040800114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 288 | 2023-04-08 | 5184 | keep | 0 | Apr | 2023 | 0.0035308 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2023-04-08 07:57 | 2023-04-10 11:22 | 3 | 51:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. SJ-230410-50 | R23040800075 | New_Event | Primary Wire Break | Include | Include | Equipment | 3085 | 2023-04-08 | 9255 | keep | 0 | Apr | 2023 | 0.0063035 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-04-08 07:59 | 2023-04-08 13:19 | 152 | 5:20 | P | DESGANCHE | 1 X 65 EN C/L | C23040800244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-04-08 | 48640 | keep | 0 | Apr | 2023 | 0.033128 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
BAYAMON | 2023-04-08 08:01 | 2023-04-08 15:30 | 152 | 7:29 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23040800064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2023-04-08 | 68248 | keep | 0 | Apr | 2023 | 0.046483 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
BARRANQUITAS | 2023-04-08 08:03 | 2023-04-08 09:38 | 54 | 1:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR Y LEVANTO CONDUCTOR | C23040800247 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 95 | 2023-04-08 | 5130 | keep | 0 | Apr | 2023 | 0.003494 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2023-04-08 08:06 | 2023-04-08 11:49 | 25 | 3:43 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23040800120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2023-04-08 | 5575 | keep | 0 | Apr | 2023 | 0.0037971 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-04-08 08:12 | 2023-04-08 08:13 | 2178 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C23040800256 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-08 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BARRANQUITAS | 2023-04-08 08:14 | 2023-04-08 12:12 | 80 | 3:58 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHO Y REEMPLAZO CAJA AVERIADA | C23040800257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-04-08 | 19040 | keep | 0 | Apr | 2023 | 0.012968 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-08 08:15 | 2023-04-08 08:52 | 484 | 0:37 | P | DESGANCHE | SE SECCIONALIZO PREVIAMENTE POR DESGANCHE MEDIANTE G.O.I. SJ-230408-50 PERO EL INTERRUPTOR SE VOLVIO A DISPARAR DURANTE LAS OPERACIONES | R23040800022 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-04-08 | 17908 | keep | 0 | Apr | 2023 | 0.012197 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-08 08:15 | 2023-04-08 08:23 | 2610 | 0:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONAR TRAMO BY-230408-01 | B23040800031 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2023-04-08 | 20880 | keep | 0 | Apr | 2023 | 0.014221 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-08 08:19 | 2023-04-08 12:53 | 1 | 4:34 | P | NO SE REPORTO CAUSA | 1X100 Y 1 X 80 EN CORTES DE LINEA | R23040800091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2023-04-08 | 274 | keep | 0 | Apr | 2023 | 0.00018662 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-08 08:23 | 2023-04-08 09:30 | 1305 | 1:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONAR TRAMO Y SE REEMPLAZO AISLADOR QUEMADO BY-230408-01 | B23040800031 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 67 | 2023-04-08 | 87435 | keep | 0 | Apr | 2023 | 0.059552 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 08:24 | 2023-04-08 23:02 | 102 | 14:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO FUERTES VIENTOS | B23040800079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 878 | 2023-04-08 | 89556 | keep | 0 | Apr | 2023 | 0.060996 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
BAYAMON | 2023-04-08 08:35 | 2023-04-08 08:36 | 1210 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 1210 | keep | 0 | Apr | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BARRANQUITAS | 2023-04-08 08:43 | 2023-04-08 13:54 | 50 | 5:11 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L ELIMINO PARARRAYO CRUZADO | C23040800296 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 311 | 2023-04-08 | 15550 | keep | 0 | Apr | 2023 | 0.010591 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-08 08:44 | 2023-04-08 15:40 | 200 | 6:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M23040800140 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 416 | 2023-04-08 | 83200 | keep | 0 | Apr | 2023 | 0.056667 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-04-08 08:52 | 2023-04-08 08:57 | 1615 | 0:05 | T | DESGANCHE | INTERRUPTOR SE VOLVIO A DISPARAR SE SECCIONALIZO NUEVAMENTE POR DESGANCHE EN OTRO PUNTO MEDIANTE G.O.I. SJ-230408-50 - 70% EN SERVICIO | R23040800022 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 5 | 2023-04-08 | 8075 | keep | 0 | Apr | 2023 | 0.0054998 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 08:52 | 2023-04-08 12:20 | 2435 | 3:28 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 208 | 2023-04-08 | 506480 | keep | 0 | Apr | 2023 | 0.34496 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-08 08:52 | 2023-04-08 12:20 | 2956 | 3:28 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | New_Event | Feeder Load Transferred | Include | Include | Other | 208 | 2023-04-08 | 614848 | keep | 0 | Apr | 2023 | 0.41877 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
CANOVANAS | 2023-04-08 08:57 | 2023-04-08 09:34 | 484 | 0:37 | P | DESGANCHE | SE CERRO MACHETE EN OTRO PUNTO MEDIANTE G.O.I. SJ-230408-50 MIENTRAS SE CONTINUAN LOS TRABAJOS DE DESGANCHE - 90% EN SERVICIO | R23040800022 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-04-08 | 17908 | keep | 0 | Apr | 2023 | 0.012197 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-08 09:02 | 2023-04-08 09:03 | 3464 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO LLUVIA FUERTE | R23040800122 | Additional_clients | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-08 | 3464 | keep | 0 | Apr | 2023 | 0.0023593 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-08 09:02 | 2023-04-08 12:35 | 350 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X 100 EN C/L MAL TIEMPO LLUVIA | B23040800124 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2023-04-08 | 74550 | keep | 0 | Apr | 2023 | 0.050776 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2023-04-08 09:03 | 2023-04-08 14:16 | 80 | 5:13 | P | PROBLEMA DEL CLIENTE | 1X100 EN C/L POR AVERIA INTERNA DEL CLIENTE | S23040800171 | New_Event | Customer-Related Interruption | Include | Include | Public | 313 | 2023-04-08 | 25040 | keep | 0 | Apr | 2023 | 0.017055 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-08 09:03 | 2023-04-08 11:58 | 51 | 2:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X200 EN C/L PRINCIPAL POR LLUVIAS | R23040800026 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 175 | 2023-04-08 | 8925 | keep | 0 | Apr | 2023 | 0.0060788 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-04-08 09:15 | 2023-04-08 14:10 | 20 | 4:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23040800140 | New_Event | Secondary Wire Break | Include | Include | Equipment | 295 | 2023-04-08 | 5900 | keep | 0 | Apr | 2023 | 0.0040185 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-04-08 09:26 | 2023-04-08 09:27 | 1746 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | AVERIA EN MH#6 | P23040800160 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-04-08 | 1746 | keep | 0 | Apr | 2023 | 0.0011892 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-08 09:27 | 2023-04-08 11:09 | 100 | 1:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L FUERTES LLUVIAS | C23040800359 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 102 | 2023-04-08 | 10200 | keep | 0 | Apr | 2023 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-04-08 09:27 | 2023-04-08 14:55 | 25 | 5:28 | P | TERMINACION SOTERRADA AVERIADA | TERMINACION AVERIADA VS#83 AL VS#6 | P23040800162 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 328 | 2023-04-08 | 8200 | keep | 0 | Apr | 2023 | 0.005585 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-04-08 09:30 | 2023-04-08 11:51 | 88 | 2:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P23040800161 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 141 | 2023-04-08 | 12408 | keep | 0 | Apr | 2023 | 0.008451 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
SAN JUAN | 2023-04-08 09:33 | 2023-04-09 02:30 | 189 | 16:57 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | S23040800195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1017 | 2023-04-08 | 192213 | keep | 0 | Apr | 2023 | 0.13092 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
CANOVANAS | 2023-04-08 09:34 | 2023-04-08 11:11 | 161 | 1:37 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO, SE REMPLAZARON (2) PARARRAYOS Y SE ELIMINARON OTROS (2) PARARRAYOS PRIVADOS ADICIONALES MEDIANTE G.O.I. SJ-230408-50 - EN SERVICIO 100% | R23040800022 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-04-08 | 15617 | keep | 0 | Apr | 2023 | 0.010637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-08 09:51 | 2023-04-08 13:33 | 43 | 3:42 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN C/L DESENREDO LINEAS | C23040800396 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 222 | 2023-04-08 | 9546 | keep | 0 | Apr | 2023 | 0.0065017 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
HUMACAO | 2023-04-08 09:51 | 2023-04-08 16:32 | 100 | 6:41 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L Y 2 X 10 EN XMRS RAYOS | C23040800395 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 401 | 2023-04-08 | 40100 | keep | 0 | Apr | 2023 | 0.027312 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-08 09:54 | 2023-04-08 14:33 | 21 | 4:39 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | ABRIO XMR PARA SECCIONALIZAR POSTES SECUNDARIOS EN EL SUELO | C23040800405 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 279 | 2023-04-08 | 5859 | keep | 0 | Apr | 2023 | 0.0039905 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CANOVANAS | 2023-04-08 09:57 | 2023-04-08 16:26 | 8 | 6:29 | P | MAL TIEMPO/RAYOS | 2X15 EN XMR MAL TIEMPO RAYOS | R23040800176 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 389 | 2023-04-08 | 3112 | keep | 0 | Apr | 2023 | 0.0021196 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-04-08 09:57 | 2023-04-08 11:55 | 1 | 1:58 | P | MAL TIEMPO/RAYOS | 2 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23040800169 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 118 | 2023-04-08 | 118 | keep | 0 | Apr | 2023 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-08 10:00 | 2023-04-08 10:01 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23040800173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 1825 | keep | 0 | Apr | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
CAGUAS | 2023-04-08 10:01 | 2023-04-09 09:15 | 85 | 23:14 | P | DESGANCHE | 2 X 65 EN C/L | C23040800410 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1394 | 2023-04-08 | 118490 | keep | 0 | Apr | 2023 | 0.080703 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2023-04-08 10:16 | 2023-04-08 10:17 | 2178 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C23040800421 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-08 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
HUMACAO | 2023-04-08 10:17 | 2023-04-08 10:18 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040800433 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 2450 | keep | 0 | Apr | 2023 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-04-08 10:17 | 2023-04-08 10:20 | 640 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C23040800424 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-08 | 1920 | keep | 0 | Apr | 2023 | 0.0013077 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
CAGUAS | 2023-04-08 10:17 | 2023-04-08 19:40 | 50 | 9:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C23040800649 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 563 | 2023-04-08 | 28150 | keep | 0 | Apr | 2023 | 0.019173 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-04-08 10:18 | 2023-04-08 12:14 | 1 | 1:56 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN RANSFORMADOR BAJANTE PRIMARIO PARTIDO | P23040800177 | New_Event | Primary Wire Break | Include | Include | Equipment | 116 | 2023-04-08 | 116 | keep | 0 | Apr | 2023 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-08 10:19 | 2023-04-08 12:56 | 40 | 2:37 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L DESCARGAS ELECTRICAS | C23040800429 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 157 | 2023-04-08 | 6280 | keep | 0 | Apr | 2023 | 0.0042773 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-08 10:20 | 2023-04-08 19:09 | 5 | 8:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L SE REPORTA MAL TIEMPO LLUVIA | B23040800169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 529 | 2023-04-08 | 2645 | keep | 0 | Apr | 2023 | 0.0018015 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-04-08 10:22 | 2023-04-08 19:51 | 8 | 9:29 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040800031 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 569 | 2023-04-08 | 4552 | keep | 0 | Apr | 2023 | 0.0031003 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-04-08 10:23 | 2023-04-08 10:40 | 35 | 0:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040800032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 17 | 2023-04-08 | 595 | keep | 0 | Apr | 2023 | 0.00040525 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-04-08 10:25 | 2023-04-08 10:27 | 34 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO 1116-02 QUE LLEVA 30% DEL 1115-04 | S2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-08 | 68 | keep | 0 | Apr | 2023 | 4.6314e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
HUMACAO | 2023-04-08 10:26 | 2023-04-08 15:43 | 45 | 5:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 Y 1 X 40 EN C/LS LLUVIAS | C23040800436 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 317 | 2023-04-08 | 14265 | keep | 0 | Apr | 2023 | 0.0097158 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-04-08 10:27 | 2023-04-08 11:12 | 8 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BAJANTE SECUNDARIO | C23040800438 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-08 | 360 | keep | 0 | Apr | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-04-08 10:34 | 2023-04-08 14:40 | 80 | 4:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | M23040800185 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 246 | 2023-04-08 | 19680 | keep | 0 | Apr | 2023 | 0.013404 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-04-08 10:54 | 2023-04-08 13:46 | 107 | 2:52 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | R23040800211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-04-08 | 18404 | keep | 0 | Apr | 2023 | 0.012535 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
SAN JUAN | 2023-04-08 10:55 | 2023-04-08 10:56 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 4291 | keep | 0 | Apr | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
GUAYAMA | 2023-04-08 11:04 | 2023-04-08 13:50 | 25 | 2:46 | P | TRANSFORMADOR AVERIADO | 1 X 80 EN SU#1 MI CARTA QUEMADA EN TRANSFORMADOR #23 | P23040800200 | New_Event | Service Transformer Failure | Include | Include | Equipment | 166 | 2023-04-08 | 4150 | keep | 0 | Apr | 2023 | 0.0028265 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-08 11:05 | 2023-04-08 13:32 | 6 | 2:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y DESGANCHE SECUNDARIO | B23040800189 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 147 | 2023-04-08 | 882 | keep | 0 | Apr | 2023 | 0.00060073 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-08 11:19 | 2023-04-08 15:28 | 386 | 4:09 | T | NO SE REPORTO CAUSA | DISPARO DE BKR NO CERRO POR CONTROL NI EN EL CAMPO SE TRANSFIRIO LA CARGA AL 1908-01 POR B/I | S23040800268 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 249 | 2023-04-08 | 96114 | keep | 0 | Apr | 2023 | 0.065463 | 0.0002629 | Sustained | FALSE | FALSE | Not_TMED_Event | 386
SAN JUAN | 2023-04-08 11:21 | 2023-04-08 11:23 | 2435 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR Y SE CERRO POR SCADA | S23040800270 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-08 | 4870 | keep | 0 | Apr | 2023 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-04-08 11:26 | 2023-04-08 11:33 | 3957 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO HACIENDO OPERACIONES PARA CERRAR CONTRA 1303-04 SE ABRE AMARRE Y SE CIERRA POR SCADA 20% EN SERVICIO DEBIDO A QUE DISPARO EL PB 1908-03A. | S23040800280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-04-08 | 27699 | keep | 0 | Apr | 2023 | 0.018866 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
BAYAMON | 2023-04-08 11:30 | 2023-04-08 18:16 | 2 | 6:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L SE REPORTA MAL TIEMPO LLUVIA | S23040800283 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 406 | 2023-04-08 | 812 | keep | 0 | Apr | 2023 | 0.00055305 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-08 11:30 | 2023-04-08 13:40 | 1266 | 2:10 | P | CONDUCTOR ARRIADO O CRUZADO | SE REPARO LINEAS PRIMARIAS CRUZADAS | M23040800217 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 130 | 2023-04-08 | 164580 | keep | 0 | Apr | 2023 | 0.11209 | 0.00086227 | Sustained | FALSE | FALSE | Not_TMED_Event | 1266
HUMACAO | 2023-04-08 11:32 | 2023-04-08 15:09 | 35 | 3:37 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYOS | C23040800507 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 217 | 2023-04-08 | 7595 | keep | 0 | Apr | 2023 | 0.0051729 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-04-08 11:33 | 2023-04-08 12:55 | 3166 | 1:22 | P | NO SE REPORTO CAUSA | DISPARO DE POLE BREKAER 1908-03A SE PROBO EN EL CAMPO 100% EN SERVICIO | S23040800280 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-04-08 | 259612 | keep | 0 | Apr | 2023 | 0.17682 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-08 11:43 | 2023-04-08 13:22 | 80 | 1:39 | P | MAL TIEMPO/RAYOS | 1 X 40 1 X 30 Y 3 X 15 EN XMRS RAYOS | C23040800518 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 99 | 2023-04-08 | 7920 | keep | 0 | Apr | 2023 | 0.0053943 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-08 11:45 | 2023-04-09 04:13 | 87 | 16:28 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | S23040800324 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 988 | 2023-04-08 | 85956 | keep | 0 | Apr | 2023 | 0.058544 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
CAGUAS | 2023-04-08 11:48 | 2023-04-08 15:40 | 43 | 3:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C23040800522 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 232 | 2023-04-08 | 9976 | keep | 0 | Apr | 2023 | 0.0067946 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2023-04-08 11:53 | 2023-04-08 17:42 | 35 | 5:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS FUERTES | C23040800531 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 349 | 2023-04-08 | 12215 | keep | 0 | Apr | 2023 | 0.0083196 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-04-08 11:57 | 2023-04-08 15:00 | 14 | 3:03 | P | PROBLEMA DEL CLIENTE | 2 X 80 EN SU-10 SE DEJO ABIERTO DE VS DE ATLANTIS HACIA CAJAS SECAS | S23040800347 | New_Event | Customer-Related Interruption | Include | Include | Public | 183 | 2023-04-08 | 2562 | keep | 0 | Apr | 2023 | 0.001745 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2023-04-08 12:01 | 2023-04-08 20:08 | 100 | 8:07 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA POR AVE | P23040800218 | New_Event | Animals | Include | Include | Wildlife | 487 | 2023-04-08 | 48700 | keep | 0 | Apr | 2023 | 0.033169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-04-08 12:01 | 2023-04-08 16:51 | 60 | 4:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | M23040800207 | New_Event | Cutout Failure | Include | Include | Equipment | 290 | 2023-04-08 | 17400 | keep | 0 | Apr | 2023 | 0.011851 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-08 12:09 | 2023-04-08 22:38 | 5 | 10:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA CERRAR PUENTE DE CAJA A TRANSFORMADOR | R23040800239 | New_Event | Secondary Wire Break | Include | Include | Equipment | 629 | 2023-04-08 | 3145 | keep | 0 | Apr | 2023 | 0.002142 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-04-08 12:09 | 2023-04-08 17:47 | 50 | 5:38 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L RAYOS | C23040800541 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 338 | 2023-04-08 | 16900 | keep | 0 | Apr | 2023 | 0.011511 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-04-08 12:13 | 2023-04-08 19:19 | 60 | 7:06 | P | CAUSAS EXTERNAS | GLOBO DE HELIO 1 X 80 EN CORTE DE LINEA | P23040800221 | New_Event | Damage From Public | Include | Include | Public | 426 | 2023-04-08 | 25560 | keep | 0 | Apr | 2023 | 0.017409 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-08 12:14 | 2023-04-08 14:02 | 60 | 1:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 Y 1 X 50 EN CORTES DE LINEA MAL TIEMPO LLUVIA | R23040800242 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 108 | 2023-04-08 | 6480 | keep | 0 | Apr | 2023 | 0.0044135 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-04-08 12:15 | 2023-04-08 16:29 | 40 | 4:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C23040800550 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 254 | 2023-04-08 | 10160 | keep | 0 | Apr | 2023 | 0.0069199 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-08 12:20 | 2023-04-08 13:30 | 1948 | 1:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 70 | 2023-04-08 | 136360 | keep | 0 | Apr | 2023 | 0.092874 | 0.0013268 | Sustained | FALSE | FALSE | Not_TMED_Event | 1948
BAYAMON | 2023-04-08 12:21 | 2023-04-08 16:02 | 91 | 3:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 60 EN C/L MAL TIEMPO LLUVIA | B23040800208 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 221 | 2023-04-08 | 20111 | keep | 0 | Apr | 2023 | 0.013698 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
SAN JUAN | 2023-04-08 12:27 | 2023-04-08 15:40 | 7 | 3:13 | S | AVERIA EN BARRA DE DISTRIBUCION | SUBESTACION FUERA FUNDIO 2 FUSIBLES EN LA ALTA A CAUSA DE CONTAMINACION EN LA UNIT Y EN BARRA DE DISTRIBUCION SE TRANSFIRIO CARGA AL 1525-01 | S23040800461 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 193 | 2023-04-08 | 1351 | keep | 0 | Apr | 2023 | 0.00092016 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-04-08 12:27 | 2023-04-08 15:12 | 277 | 2:45 | S | AVERIA EN BARRA DE DISTRIBUCION | SUBESTACION FUERA FUNDIO 2 FUSIBLES EN LA ALTA A CAUSA DE CONTAMINACION EN LA UNIT Y EN BARRA DE DISTRIBUCION SE TRANSFIRIO CARGA AL 1421-02 | S23040800461 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 165 | 2023-04-08 | 45705 | keep | 0 | Apr | 2023 | 0.031129 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
SAN JUAN | 2023-04-08 12:27 | 2023-04-08 15:12 | 15 | 2:45 | S | AVERIA EN BARRA DE DISTRIBUCION | SUBESTACION FUERA FUNDIO 2 FUSIBLES EN LA ALTA A CAUSA DE CONTAMINACION EN LA UNIT Y EN BARRA DE DISTRIBUCION SE TRANSFIRIO CARGA AL 1421-02 | S23040800461 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 165 | 2023-04-08 | 2475 | keep | 0 | Apr | 2023 | 0.0016857 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-08 12:27 | 2023-04-08 15:49 | 5 | 3:22 | S | AVERIA EN BARRA DE DISTRIBUCION | SUBESTACION FUERA FUNDIO 2 FUSIBLES EN LA ALTA A CAUSA DE CONTAMINACION EN LA UNIT Y EN BARRA DE DISTRIBUCION SE TRANSFIRIO CARGA AL 1421-02 | S23040800461 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 202 | 2023-04-08 | 1010 | keep | 0 | Apr | 2023 | 0.00068791 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-04-08 12:27 | 2023-04-08 22:10 | 125 | 9:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 80 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO PARTIDO | R23040800246 | New_Event | Primary Pole Failure | Include | Include | Equipment | 583 | 2023-04-08 | 72875 | keep | 0 | Apr | 2023 | 0.049635 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-04-08 12:28 | 2023-04-08 18:36 | 17 | 6:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR LLUVIAS | C23040800564 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 368 | 2023-04-08 | 6256 | keep | 0 | Apr | 2023 | 0.0042609 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2023-04-08 12:29 | 2023-04-08 15:31 | 7 | 3:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR LLUVIAS | C23040800565 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 182 | 2023-04-08 | 1274 | keep | 0 | Apr | 2023 | 0.00086772 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-04-08 12:30 | 2023-04-08 17:05 | 1 | 4:35 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040800044 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 275 | 2023-04-08 | 275 | keep | 0 | Apr | 2023 | 0.0001873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-08 12:36 | 2023-04-09 07:07 | 25 | 18:31 | P | DESGANCHE | 1 X 50 EN C/L | C23040800567 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1111 | 2023-04-08 | 27775 | keep | 0 | Apr | 2023 | 0.018917 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-08 12:38 | 2023-04-08 12:39 | 870 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO HACIENDO OPERACIONES PARA CERRAR CONTRA 1303-04 SE ABRIO AMARRE Y SE CERRO POR SCADA | S2304080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-08 | 870 | keep | 0 | Apr | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2023-04-08 12:52 | 2023-04-08 12:53 | 3941 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | B2304080000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-08 | 3941 | keep | 0 | Apr | 2023 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2023-04-08 12:53 | 2023-04-08 20:08 | 1 | 7:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | B23040800229 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 435 | 2023-04-08 | 435 | keep | 0 | Apr | 2023 | 0.00029628 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-08 12:57 | 2023-04-08 13:02 | 796 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-04 LLEVA 16% DEL 1336-06 SE CERRO POR CONTROL | S23040800416 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-08 | 3980 | keep | 0 | Apr | 2023 | 0.0027108 | 0.00054215 | Momentary | FALSE | FALSE | Not_TMED_Event | 796
CANOVANAS | 2023-04-08 12:57 | 2023-04-08 13:02 | 172 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVA 16% DEL 1336-06 SE CERRO POR CONTROL | S23040800416 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-08 | 860 | keep | 0 | Apr | 2023 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
CAGUAS | 2023-04-08 12:58 | 2023-04-08 18:16 | 40 | 5:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L Y 1 X 10 EN XMR LLUVIAS | C23040800576 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 318 | 2023-04-08 | 12720 | keep | 0 | Apr | 2023 | 0.0086635 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-04-08 13:11 | 2023-04-08 14:17 | 200 | 1:06 | P | ANIMAL | 1 X 80 1 X 65 Y 1 X 100 EN C/LS CRUCE X AVE | C23040800585 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-04-08 | 13200 | keep | 0 | Apr | 2023 | 0.0089905 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-04-08 13:13 | 2023-04-08 13:14 | 34 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR 1116-02 (BKR SPARE) LLEVA 30% DE LA CARGA DEL 1115-04 SE CERRO POR CONTROL | S2304080000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 34 | keep | 0 | Apr | 2023 | 2.3157e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
HUMACAO | 2023-04-08 13:17 | 2023-04-08 14:15 | 75 | 0:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 1 X 50 Y 1 X 65 EN C/LS LLUVIAS | C23040800587 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 58 | 2023-04-08 | 4350 | keep | 0 | Apr | 2023 | 0.0029628 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-04-08 13:23 | 2023-04-08 18:49 | 35 | 5:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C23040800594 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 326 | 2023-04-08 | 11410 | keep | 0 | Apr | 2023 | 0.0077713 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-04-08 13:30 | 2023-04-08 14:43 | 1583 | 1:13 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 73 | 2023-04-08 | 115559 | keep | 0 | Apr | 2023 | 0.078707 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-08 13:32 | 2023-04-08 18:45 | 100 | 5:13 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTES DE LINEA DISTINTOS SE RETIRO RAMAS SOBRE LAS LINEAS | A23040800054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2023-04-08 | 31300 | keep | 0 | Apr | 2023 | 0.021318 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-04-08 13:36 | 2023-04-08 15:49 | 41 | 2:13 | P | DESGANCHE | 1 X 80 EN C/L | C23040800607 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-04-08 | 5453 | keep | 0 | Apr | 2023 | 0.003714 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
VEGA BAJA | 2023-04-08 13:38 | 2023-04-08 18:55 | 4 | 5:17 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040800062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2023-04-08 | 1268 | keep | 0 | Apr | 2023 | 0.00086363 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-04-08 13:48 | 2023-04-08 16:43 | 329 | 2:55 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZARON CAJA | C23040800617 | New_Event | Cutout Failure | Include | Include | Equipment | 175 | 2023-04-08 | 57575 | keep | 0 | Apr | 2023 | 0.039214 | 0.00022408 | Sustained | FALSE | FALSE | Not_TMED_Event | 329
HUMACAO | 2023-04-08 13:49 | 2023-04-08 16:08 | 40 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIA | C23040800618 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-04-08 | 5560 | keep | 0 | Apr | 2023 | 0.0037869 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-04-08 13:51 | 2023-04-08 19:59 | 382 | 6:08 | P | ARBOL SOBRE LINEA | 1 X 80 1 X 65 Y 1 X 50 EN C/LS SE RETIRO ARBOL DE LAS LINEAS Y COORDINO LOS FUSIBLES GOI CG-230408-03 | C23040800621 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 368 | 2023-04-08 | 140576 | keep | 0 | Apr | 2023 | 0.095746 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
VEGA BAJA | 2023-04-08 14:01 | 2023-04-08 19:45 | 8 | 5:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA DE TRANSFORMADOR | A23040800070 | New_Event | Primary Wire Break | Include | Include | Equipment | 344 | 2023-04-08 | 2752 | keep | 0 | Apr | 2023 | 0.0018744 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-08 14:03 | 2023-04-08 14:38 | 56 | 0:35 | P | DESGANCHE | SJ-230408-01 SE RETIRO BAMBUA Y SE CERRO MACHETE 100 % EN SERVICO | S23040800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 35 | 2023-04-08 | 1960 | keep | 0 | Apr | 2023 | 0.0013349 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
FAJARDO | 2023-04-08 14:04 | 2023-04-08 15:18 | 3 | 1:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X10 EN XMR MAL TIEMPO LLUVIAS | R23040800272 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 74 | 2023-04-08 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-08 14:05 | 2023-04-08 14:49 | 91 | 0:44 | P | ANIMAL | 1X40 Y 2 X 30 EN CORTES DE LINEA Y 1X15 EN XMR CRUCE POR AVE | R23040800273 | New_Event | Animals | Include | Include | Wildlife | 44 | 2023-04-08 | 4004 | keep | 0 | Apr | 2023 | 0.0027271 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
UTUADO | 2023-04-08 14:09 | 2023-04-08 18:40 | 20 | 4:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LA SALIDA DE CAJA DE CORTE DE LINEA | A23040800074 | New_Event | Primary Wire Break | Include | Include | Equipment | 271 | 2023-04-08 | 5420 | keep | 0 | Apr | 2023 | 0.0036915 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-04-08 14:10 | 2023-04-08 22:32 | 1 | 8:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | C23040800635 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 502 | 2023-04-08 | 502 | keep | 0 | Apr | 2023 | 0.00034191 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-08 14:16 | 2023-04-08 18:44 | 30 | 4:28 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER 1 X 20 EN SU-D | S23040800476 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 268 | 2023-04-08 | 8040 | keep | 0 | Apr | 2023 | 0.005476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-08 14:24 | 2023-04-08 18:32 | 35 | 4:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L MAL TIEMPO LLUVIAS | R23040800277 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 248 | 2023-04-08 | 8680 | keep | 0 | Apr | 2023 | 0.0059119 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-04-08 14:30 | 2023-04-08 16:40 | 4 | 2:10 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO TRANSFORMADOR PARA REMPLAZAR CRUCETA PARTIDA | M23040800168 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 130 | 2023-04-08 | 520 | keep | 0 | Apr | 2023 | 0.00035417 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-04-08 14:38 | 2023-04-08 16:54 | 20 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS FUERTES | C23040800644 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-04-08 | 2720 | keep | 0 | Apr | 2023 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-08 14:41 | 2023-04-08 14:43 | 796 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-04 LLEVA 16% DEL 1336-06 SE CERRO POR CONTROL | S23040800048 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-08 | 1592 | keep | 0 | Apr | 2023 | 0.0010843 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-08 14:41 | 2023-04-08 14:43 | 172 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1620-04 LLEVA 16% DEL 1336-06 SE CERRO POR CONTROL | S23040800048 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-08 | 344 | keep | 0 | Apr | 2023 | 0.0002343 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 14:43 | 2023-04-08 14:45 | 2435 | 0:02 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-04-08 | 4870 | keep | 0 | Apr | 2023 | 0.0033169 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 14:43 | 2023-04-08 14:45 | 2956 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-08 | 5912 | keep | 0 | Apr | 2023 | 0.0040266 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-04-08 14:45 | 2023-04-08 15:32 | 1583 | 0:47 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 47 | 2023-04-08 | 74401 | keep | 0 | Apr | 2023 | 0.050674 | 0.0010782 | Sustained | FALSE | FALSE | Not_TMED_Event | 1583
PONCE | 2023-04-08 14:55 | 2023-04-08 14:56 | 1746 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | DISPARO AL CERRAR DE MH#83 A MH#6 AVERIA EN TERMINACION CONTINUA 4/09/2023 DESDE LAS 14:56 | P23040800269 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-04-08 | 1746 | keep | 0 | Apr | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2023-04-08 14:56 | 2023-04-09 10:38 | 25 | 19:42 | P | TERMINACION SOTERRADA AVERIADA | TERMINACION AVERIADA VS#83 A MH#6 | P23040800162 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 1182 | 2023-04-08 | 29550 | keep | 0 | Apr | 2023 | 0.020126 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-08 15:01 | 2023-04-08 17:10 | 25 | 2:09 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23040800109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-04-08 | 3225 | keep | 0 | Apr | 2023 | 0.0021965 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-08 15:01 | 2023-04-08 16:29 | 39 | 1:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 Y 1 X 50 EN C/L MAL TIEMPO RAYOS | B23040800245 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 88 | 2023-04-08 | 3432 | keep | 0 | Apr | 2023 | 0.0023375 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
HUMACAO | 2023-04-08 15:04 | 2023-04-08 18:06 | 2 | 3:02 | P | PROBLEMA DEL CLIENTE | 1 X 30 EN C/L XMR PRIVADO DEL MUNICIPIO AVERIADO | C23040800651 | New_Event | Customer-Related Interruption | Include | Include | Public | 182 | 2023-04-08 | 364 | keep | 0 | Apr | 2023 | 0.00024792 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-04-08 15:23 | 2023-04-08 16:39 | 17 | 1:16 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X40 EN C/L SE REEMPLAZO AISLADOR | R23040800293 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 76 | 2023-04-08 | 1292 | keep | 0 | Apr | 2023 | 0.00087998 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-04-08 15:25 | 2023-04-08 20:29 | 40 | 5:04 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040800085 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 304 | 2023-04-08 | 12160 | keep | 0 | Apr | 2023 | 0.0082821 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-08 15:26 | 2023-04-08 15:27 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 2466 | keep | 0 | Apr | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
FAJARDO | 2023-04-08 15:27 | 2023-04-08 17:21 | 10 | 1:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X20 EN C/L SE REMPLAZO AISLADOR | R23040800029 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 114 | 2023-04-08 | 1140 | keep | 0 | Apr | 2023 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-08 15:32 | 2023-04-08 16:14 | 2435 | 0:42 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 42 | 2023-04-08 | 102270 | keep | 0 | Apr | 2023 | 0.069656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 15:32 | 2023-04-08 16:14 | 2956 | 0:42 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 42 | 2023-04-08 | 124152 | keep | 0 | Apr | 2023 | 0.084559 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
HUMACAO | 2023-04-08 15:47 | 2023-04-08 16:39 | 25 | 0:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L LLUVIAS FUERTES | C23040800669 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 52 | 2023-04-08 | 1300 | keep | 0 | Apr | 2023 | 0.00088542 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-08 15:53 | 2023-04-08 16:11 | 30 | 0:18 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23040800254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 18 | 2023-04-08 | 540 | keep | 0 | Apr | 2023 | 0.00036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-08 15:55 | 2023-04-08 17:24 | 44 | 1:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE LEVANTO CONDUCTOR | C23040800672 | New_Event | Primary Wire Break | Include | Include | Equipment | 89 | 2023-04-08 | 3916 | keep | 0 | Apr | 2023 | 0.0026672 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
UTUADO | 2023-04-08 16:04 | 2023-04-09 10:30 | 15 | 18:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LINEAS | A23040800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1106 | 2023-04-08 | 16590 | keep | 0 | Apr | 2023 | 0.011299 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-08 16:06 | 2023-04-08 17:18 | 7 | 1:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR LLUVIAS FUERTES | C23040800676 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 72 | 2023-04-08 | 504 | keep | 0 | Apr | 2023 | 0.00034327 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-04-08 16:07 | 2023-04-08 20:48 | 1 | 4:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L MAL TIEMPO LLUVIAS | R23040800300 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 281 | 2023-04-08 | 281 | keep | 0 | Apr | 2023 | 0.00019139 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-08 16:14 | 2023-04-08 18:38 | 1583 | 2:24 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 144 | 2023-04-08 | 227952 | keep | 0 | Apr | 2023 | 0.15526 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-08 16:15 | 2023-04-08 21:00 | 54 | 4:45 | P | CONDUCTOR ROTO O ABIERTO | SJ-230408-05 SE SECCIONALIZO TRAMO PARA LEVANTAR ALAMBRE PRIMARIO | S23040800539 | New_Event | Primary Wire Break | Include | Include | Equipment | 285 | 2023-04-08 | 15390 | keep | 0 | Apr | 2023 | 0.010482 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
GUAYAMA | 2023-04-08 16:21 | 2023-04-08 20:10 | 12 | 3:49 | P | TRANSFORMADOR AVERIADO | SE ABRE CORTE DE LINEA PARA ELIMINAR TRANSFORMADOR AVERIADO Y ARRIMAR LA FASE A OTRO TRANSFORMADOR | P23040800300 | New_Event | Service Transformer Failure | Include | Include | Equipment | 229 | 2023-04-08 | 2748 | keep | 0 | Apr | 2023 | 0.0018717 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-04-08 16:29 | 2023-04-08 17:00 | 20 | 0:31 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23040800262 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 31 | 2023-04-08 | 620 | keep | 0 | Apr | 2023 | 0.00042228 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-08 16:30 | 2023-04-09 09:25 | 3 | 16:55 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040800263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1015 | 2023-04-08 | 3045 | keep | 0 | Apr | 2023 | 0.0020739 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-04-08 16:31 | 2023-04-08 16:32 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040800685 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 2302 | keep | 0 | Apr | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CANOVANAS | 2023-04-08 16:35 | 2023-04-08 21:11 | 14 | 4:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X20 EN XMR MAL TIEMPO LLUVIAS | R23040800308 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 276 | 2023-04-08 | 3864 | keep | 0 | Apr | 2023 | 0.0026318 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-04-08 16:38 | 2023-04-08 16:39 | 222 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO INTERRUPTOR A PETICION DE JESUS TORRES PARA ABRIIR CAJA PRIMARIA ARQUEANDO LLEVA LA CARGA DEL 1909-09 | S23040800544 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-04-08 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-08 16:38 | 2023-04-08 16:39 | 222 | 0:01 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR A PETICION DE JESUS TORRES PARA ABRIIR CAJA PRIMARIA ARQUEANDO LLEVA LA CARGA DEL 1909-09 | S23040800544 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-08 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-08 16:39 | 2023-04-08 17:34 | 1 | 0:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | S23040800544 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 55 | 2023-04-08 | 55 | keep | 0 | Apr | 2023 | 3.746e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-08 16:39 | 2023-04-08 16:40 | 2708 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23040800310 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 2708 | keep | 0 | Apr | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-04-08 16:40 | 2023-04-08 17:41 | 17 | 1:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X40 EN C/L SE REEMPLAZO AISLADOR | R23040800293 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 61 | 2023-04-08 | 1037 | keep | 0 | Apr | 2023 | 0.0007063 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-04-08 16:47 | 2023-04-09 09:11 | 1 | 16:24 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23040800098 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 984 | 2023-04-08 | 984 | keep | 0 | Apr | 2023 | 0.0006702 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-08 16:50 | 2023-04-09 13:00 | 3 | 20:10 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | S23040800549 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1210 | 2023-04-08 | 3630 | keep | 0 | Apr | 2023 | 0.0024724 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-04-08 16:54 | 2023-04-09 09:13 | 10 | 16:19 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHO | C23040800690 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 979 | 2023-04-08 | 9790 | keep | 0 | Apr | 2023 | 0.0066679 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-08 16:57 | 2023-04-08 17:30 | 7 | 0:33 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYO | C23040800692 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 33 | 2023-04-08 | 231 | keep | 0 | Apr | 2023 | 0.00015733 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-08 17:07 | 2023-04-08 17:09 | 651 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | B2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-08 | 1302 | keep | 0 | Apr | 2023 | 0.00088679 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
HUMACAO | 2023-04-08 17:07 | 2023-04-08 18:29 | 20 | 1:22 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYOS | C23040800694 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 82 | 2023-04-08 | 1640 | keep | 0 | Apr | 2023 | 0.001117 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-04-08 17:11 | 2023-04-08 19:40 | 6 | 2:29 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M23040800267 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 149 | 2023-04-08 | 894 | keep | 0 | Apr | 2023 | 0.0006089 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-08 17:12 | 2023-04-09 16:30 | 7 | 23:18 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO RAYOS | S23040800557 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1398 | 2023-04-08 | 9786 | keep | 0 | Apr | 2023 | 0.0066652 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-08 17:25 | 2023-04-08 23:02 | 211 | 5:37 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO DE NUEVO PARA REPARAR PUENTE ABIERTO BY-230407-03 CARGA POR EL 1714-03 | B23040700432 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 337 | 2023-04-08 | 71107 | keep | 0 | Apr | 2023 | 0.048431 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-08 17:36 | 2023-04-08 19:00 | 41 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS FUERTES | C23040800697 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2023-04-08 | 3444 | keep | 0 | Apr | 2023 | 0.0023457 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2023-04-08 17:37 | 2023-04-08 18:53 | 50 | 1:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | C23040800698 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 76 | 2023-04-08 | 3800 | keep | 0 | Apr | 2023 | 0.0025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-08 17:39 | 2023-04-09 11:20 | 150 | 17:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER 2 X 50 EN SU-7 Y 1 X 80 EN OTRO RISER MAL TIEMPO LLUVIA | S23040800561 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1061 | 2023-04-08 | 159150 | keep | 0 | Apr | 2023 | 0.1084 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-04-08 17:46 | 2023-04-08 18:56 | 30 | 1:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L FUERTES LLUVIAS | C23040800699 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 70 | 2023-04-08 | 2100 | keep | 0 | Apr | 2023 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-08 17:46 | 2023-04-09 11:14 | 8 | 17:28 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040800109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2023-04-08 | 8384 | keep | 0 | Apr | 2023 | 0.0057103 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-04-08 17:55 | 2023-04-08 18:40 | 7 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | M23040800246 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-08 | 315 | keep | 0 | Apr | 2023 | 0.00021455 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-04-08 18:18 | 2023-04-08 18:50 | 6 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | M23040800239 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-04-08 | 192 | keep | 0 | Apr | 2023 | 0.00013077 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-08 18:19 | 2023-04-09 10:33 | 10 | 16:14 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR QUEMADO 50 KVA X 25 KVA | C23040800703 | New_Event | Service Transformer Failure | Include | Include | Equipment | 974 | 2023-04-08 | 9740 | keep | 0 | Apr | 2023 | 0.0066339 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-08 18:28 | 2023-04-09 01:10 | 20 | 6:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | M23040800272 | New_Event | Cutout Failure | Include | Include | Equipment | 402 | 2023-04-08 | 8040 | keep | 0 | Apr | 2023 | 0.005476 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-08 18:38 | 2023-04-08 18:45 | 2435 | 0:07 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 7 | 2023-04-08 | 17045 | keep | 0 | Apr | 2023 | 0.011609 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 18:38 | 2023-04-08 18:45 | 2956 | 0:07 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 7 | 2023-04-08 | 20692 | keep | 0 | Apr | 2023 | 0.014093 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 18:45 | 2023-04-08 19:08 | 1583 | 0:23 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 23 | 2023-04-08 | 36409 | keep | 0 | Apr | 2023 | 0.024798 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-08 18:56 | 2023-04-09 11:42 | 4 | 16:46 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR RAYO | C23040800699 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1006 | 2023-04-08 | 4024 | keep | 0 | Apr | 2023 | 0.0027407 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-08 18:57 | 2023-04-08 18:59 | 893 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2304080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-08 | 1786 | keep | 0 | Apr | 2023 | 0.0012164 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2023-04-08 19:00 | 2023-04-08 20:33 | 52 | 1:33 | P | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO EN SOTERRADO T 14 1 X 40 EN C/L 1 X 80 EN C/L | S23040800591 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 93 | 2023-04-08 | 4836 | keep | 0 | Apr | 2023 | 0.0032938 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2023-04-08 19:08 | 2023-04-08 19:10 | 2435 | 0:02 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-04-08 | 4870 | keep | 0 | Apr | 2023 | 0.0033169 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 19:08 | 2023-04-08 19:10 | 2956 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-08 | 5912 | keep | 0 | Apr | 2023 | 0.0040266 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-08 19:08 | 2023-04-08 20:15 | 3 | 1:07 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR RAYO | C23040800708 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 67 | 2023-04-08 | 201 | keep | 0 | Apr | 2023 | 0.0001369 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2023-04-08 19:08 | 2023-04-08 21:04 | 20 | 1:56 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | M23040800273 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-04-08 | 2320 | keep | 0 | Apr | 2023 | 0.0015801 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-08 19:10 | 2023-04-08 20:47 | 277 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIA | B23040800271 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2023-04-08 | 26869 | keep | 0 | Apr | 2023 | 0.0183 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
BAYAMON | 2023-04-08 19:10 | 2023-04-08 21:34 | 1948 | 2:24 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 144 | 2023-04-08 | 280512 | keep | 0 | Apr | 2023 | 0.19106 | 0.0013268 | Sustained | FALSE | FALSE | Not_TMED_Event | 1948
FAJARDO | 2023-04-08 19:10 | 2023-04-08 19:11 | 1902 | 0:01 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 | R23040800326 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 1902 | keep | 0 | Apr | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-04-08 19:10 | 2023-04-08 19:11 | 970 | 0:01 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 | R23040800326 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 970 | keep | 0 | Apr | 2023 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-04-08 19:10 | 2023-04-08 19:11 | 3003 | 0:01 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 | R23040800326 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 3003 | keep | 0 | Apr | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-04-08 19:10 | 2023-04-08 19:11 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 | R23040800327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 2343 | keep | 0 | Apr | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-04-08 19:10 | 2023-04-08 19:11 | 1830 | 0:01 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 | R23040800327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 1830 | keep | 0 | Apr | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-04-08 19:10 | 2023-04-08 19:11 | 710 | 0:01 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 | R23040800327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 710 | keep | 0 | Apr | 2023 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-04-08 19:10 | 2023-04-08 19:11 | 1197 | 0:01 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 | R23040800327 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 1197 | keep | 0 | Apr | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
CANOVANAS | 2023-04-08 19:10 | 2023-04-08 19:11 | 3012 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO POR CONTROL | R23040800321 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 3012 | keep | 0 | Apr | 2023 | 0.0020515 | 0.0020515 | Momentary | FALSE | FALSE | Not_TMED_Event | 3012
SAN JUAN | 2023-04-08 19:13 | 2023-04-09 13:23 | 29 | 18:10 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA PARTIDA Y SE ANCLO LINEA | S23040800596 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1090 | 2023-04-08 | 31610 | keep | 0 | Apr | 2023 | 0.021529 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-04-08 19:17 | 2023-04-09 14:31 | 5 | 19:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SE REMPLAZO PUENTE DE LINEA A CAJA | S23040800601 | New_Event | Cutout Failure | Include | Include | Equipment | 1154 | 2023-04-08 | 5770 | keep | 0 | Apr | 2023 | 0.0039299 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-04-08 19:17 | 2023-04-08 21:40 | 2 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE TRANSFORMADOR PARTIDA 1 X 20 | P23040800339 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2023-04-08 | 286 | keep | 0 | Apr | 2023 | 0.00019479 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-04-08 19:19 | 2023-04-08 21:22 | 50 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L RAYO | C23040800709 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2023-04-08 | 6150 | keep | 0 | Apr | 2023 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-04-08 19:27 | 2023-04-09 08:56 | 65 | 13:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23040800343 | New_Event | Vegetation Contact | Include | Include | Vegetation | 809 | 2023-04-08 | 52585 | keep | 0 | Apr | 2023 | 0.035815 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
ARECIBO | 2023-04-08 19:40 | 2023-04-08 21:08 | 50 | 1:28 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23040800117 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 88 | 2023-04-08 | 4400 | keep | 0 | Apr | 2023 | 0.0029968 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-08 19:59 | 2023-04-09 16:09 | 25 | 20:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23040800623 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1210 | 2023-04-08 | 30250 | keep | 0 | Apr | 2023 | 0.020603 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-04-08 20:10 | 2023-04-08 20:40 | 10 | 0:30 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN TRANSFORMADOR POR PARARRAYO CRUZADO | P23040800350 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 30 | 2023-04-08 | 300 | keep | 0 | Apr | 2023 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-08 20:28 | 2023-04-09 08:35 | 6 | 12:07 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR DE DESCONECTO PARARRAYOS AVERIADO | M23040800280 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 727 | 2023-04-08 | 4362 | keep | 0 | Apr | 2023 | 0.0029709 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-04-08 20:53 | 2023-04-09 00:35 | 12 | 3:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA Y AISLADOR | A23040800126 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2023-04-08 | 2664 | keep | 0 | Apr | 2023 | 0.0018144 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-08 21:34 | 2023-04-08 21:37 | 2435 | 0:03 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 3 | 2023-04-08 | 7305 | keep | 0 | Apr | 2023 | 0.0049754 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-08 21:34 | 2023-04-08 21:37 | 2956 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-08 | 8868 | keep | 0 | Apr | 2023 | 0.00604 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-04-08 21:37 | 2023-04-09 14:47 | 244 | 17:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 1030 | 2023-04-08 | 251320 | keep | 0 | Apr | 2023 | 0.17117 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
VEGA BAJA | 2023-04-08 21:50 | 2023-04-09 07:51 | 7 | 10:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23040800280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 601 | 2023-04-08 | 4207 | keep | 0 | Apr | 2023 | 0.0028654 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-04-08 22:32 | 2023-04-08 22:33 | 637 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040800281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 637 | keep | 0 | Apr | 2023 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
AGUADILLA | 2023-04-08 22:34 | 2023-04-09 08:50 | 40 | 10:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M23040800282 | New_Event | Cutout Failure | Include | Include | Equipment | 616 | 2023-04-08 | 24640 | keep | 0 | Apr | 2023 | 0.016782 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-08 22:43 | 2023-04-09 03:19 | 70 | 4:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUUVIA Y FUERTES VIENTOS | M23040800284 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 276 | 2023-04-08 | 19320 | keep | 0 | Apr | 2023 | 0.013159 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2023-04-08 22:49 | 2023-04-09 10:07 | 40 | 11:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L 1 X 8 Y 1 X 15 EN XMRS LLUVIAS FUERTES | C23040800723 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 678 | 2023-04-08 | 27120 | keep | 0 | Apr | 2023 | 0.018471 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-08 23:01 | 2023-04-08 23:02 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040800286 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-08 | 990 | keep | 0 | Apr | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
CAGUAS | 2023-04-08 23:03 | 2023-04-09 09:30 | 17 | 10:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23040800724 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 627 | 2023-04-08 | 10659 | keep | 0 | Apr | 2023 | 0.0072598 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2023-04-08 23:38 | 2023-04-08 23:39 | 1862 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC | R23040800332 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 1862 | keep | 0 | Apr | 2023 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-04-08 23:38 | 2023-04-08 23:39 | 1613 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC | R23040800332 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 1613 | keep | 0 | Apr | 2023 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-04-08 23:38 | 2023-04-08 23:39 | 1448 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC | R23040800332 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-08 | 1448 | keep | 0 | Apr | 2023 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
ARECIBO | 2023-04-08 23:42 | 2023-04-09 11:25 | 7 | 11:43 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEA SECUNDARIAS | A23040800132 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 703 | 2023-04-08 | 4921 | keep | 0 | Apr | 2023 | 0.0033517 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-04-08 23:51 | 2023-04-09 09:00 | 8 | 9:09 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23040800134 | New_Event | Animals | Include | Include | Wildlife | 549 | 2023-04-08 | 4392 | keep | 0 | Apr | 2023 | 0.0029914 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-04-09 | 2023-04-09 18:09 | 12 | 18:09 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR AVERIADO DE 15KVA X 15KVA | A23040900050 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1089 | 2023-04-09 | 13068 | keep | 0 | Apr | 2023 | 0.0089006 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-09 00:29 | 2023-04-09 07:30 | 50 | 7:01 | P | ARBOL SOBRE LINEA | 1 X 50 EN C/L SE RETIRO ARBOL SOBRE LINEA | B23040900002 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 421 | 2023-04-09 | 21050 | keep | 0 | Apr | 2023 | 0.014337 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-09 00:37 | 2023-04-09 00:38 | 3332 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23040900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 3332 | keep | 0 | Apr | 2023 | 0.0022694 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
BAYAMON | 2023-04-09 00:40 | 2023-04-09 01:07 | 17 | 0:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN C/L MAL TIEMPO FUERTES LLUVIAS | B23040900004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 27 | 2023-04-09 | 459 | keep | 0 | Apr | 2023 | 0.00031262 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2023-04-09 01:06 | 2023-04-09 09:11 | 1 | 8:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | P23040900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 485 | 2023-04-09 | 485 | keep | 0 | Apr | 2023 | 0.00033033 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-09 01:20 | 2023-04-09 04:24 | 404 | 3:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23040900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 184 | 2023-04-09 | 74336 | keep | 0 | Apr | 2023 | 0.05063 | 0.00027516 | Sustained | FALSE | FALSE | Not_TMED_Event | 404
MAYAGÃœEZ | 2023-04-09 01:30 | 2023-04-09 04:47 | 140 | 3:17 | P | MAL TIEMPO/LLUVIA O VIENTO | SE OPERO INTELIRRUPTER 6704-02A POR LLUVIA Y FUERTES VIENTOS | M23040900006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 197 | 2023-04-09 | 27580 | keep | 0 | Apr | 2023 | 0.018785 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
UTUADO | 2023-04-09 02:59 | 2023-04-09 10:28 | 35 | 7:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23040900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2023-04-09 | 15715 | keep | 0 | Apr | 2023 | 0.010703 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-04-09 03:01 | 2023-04-09 03:03 | 222 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1907-03 LLEVA EL 1909-09 | S2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-09 | 444 | keep | 0 | Apr | 2023 | 0.00030241 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-09 03:01 | 2023-04-09 03:03 | 4456 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1907-03 | S2304090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-09 | 8912 | keep | 0 | Apr | 2023 | 0.0060699 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
GUAYAMA | 2023-04-09 03:43 | 2023-04-09 09:12 | 4035 | 5:29 | T | NO SE REPORTO CAUSA | ALIMENTADOR FUERA DE SERVICIO NO DIO INDICACION POR SCADA | P23040900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 329 | 2023-04-09 | 1327515 | keep | 0 | Apr | 2023 | 0.90416 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
AGUADILLA | 2023-04-09 04:04 | 2023-04-09 04:05 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23040900027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 1192 | keep | 0 | Apr | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CAGUAS | 2023-04-09 04:54 | 2023-04-09 04:55 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 918 | keep | 0 | Apr | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-04-09 05:00 | 2023-04-09 09:31 | 117 | 4:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23040900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 271 | 2023-04-09 | 31707 | keep | 0 | Apr | 2023 | 0.021595 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
MAYAGÃœEZ | 2023-04-09 05:17 | 2023-04-09 15:15 | 90 | 9:58 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN CORTE DE LINEA SE RETIRO PARARRAYO CRUZADO | M23040900029 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 598 | 2023-04-09 | 53820 | keep | 0 | Apr | 2023 | 0.036657 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-04-09 05:22 | 2023-04-09 12:15 | 150 | 6:53 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER POR AVERIA SOTERRADA QUEDAN 50 CLIENTES FUERA PROBO MALO DE T-38 AL T-37 AVERIA VIEJA DEL T-35 AL T-36 | B23040900010 | New_Event | UG Cable Fault | Include | Include | Equipment | 413 | 2023-04-09 | 61950 | keep | 0 | Apr | 2023 | 0.042194 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-04-09 05:36 | 2023-04-09 12:07 | 39 | 6:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | C23040900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2023-04-09 | 15249 | keep | 0 | Apr | 2023 | 0.010386 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CANOVANAS | 2023-04-09 06:12 | 2023-04-09 10:50 | 16 | 4:38 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23040900007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2023-04-09 | 4448 | keep | 0 | Apr | 2023 | 0.0030295 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2023-04-09 06:46 | 2023-04-09 10:30 | 1 | 3:44 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR EVENTO TRANSFERIDO DE PONCE | P23040900097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2023-04-09 | 224 | keep | 0 | Apr | 2023 | 0.00015257 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-09 07:18 | 2023-04-09 07:19 | 271 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23040900019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 271 | keep | 0 | Apr | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2023-04-09 07:43 | 2023-04-09 07:44 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 27 | keep | 0 | Apr | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2023-04-09 07:44 | 2023-04-09 07:45 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23040900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 3458 | keep | 0 | Apr | 2023 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
SAN JUAN | 2023-04-09 07:56 | 2023-04-09 07:57 | 271 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23040900026 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 271 | keep | 0 | Apr | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CAGUAS | 2023-04-09 07:59 | 2023-04-09 11:38 | 4 | 3:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIAS | C23040900039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 219 | 2023-04-09 | 876 | keep | 0 | Apr | 2023 | 0.00059664 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-04-09 08:02 | 2023-04-09 12:00 | 20 | 3:58 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L Y 1 X 15 EN XMR | R23040900008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2023-04-09 | 4760 | keep | 0 | Apr | 2023 | 0.003242 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-09 08:10 | 2023-04-09 15:00 | 30 | 6:50 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE PRIMARIO Y SE REPARO SECUNDARIA | B23040900017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 410 | 2023-04-09 | 12300 | keep | 0 | Apr | 2023 | 0.0083775 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-09 08:11 | 2023-04-09 12:29 | 1 | 4:18 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23040900010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2023-04-09 | 258 | keep | 0 | Apr | 2023 | 0.00017572 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-09 08:12 | 2023-04-09 08:13 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040900041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 551 | keep | 0 | Apr | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-04-09 08:33 | 2023-04-09 11:59 | 70 | 3:26 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23040900047 | New_Event | Animals | Include | Include | Wildlife | 206 | 2023-04-09 | 14420 | keep | 0 | Apr | 2023 | 0.0098214 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-04-09 08:36 | 2023-04-09 12:19 | 50 | 3:43 | P | TERMINACION SOTERRADA AVERIADA | 1 X 40 EN C/L REPARO TERMINACION EN RISER | C23040900048 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 223 | 2023-04-09 | 11150 | keep | 0 | Apr | 2023 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-09 08:39 | 2023-04-09 09:53 | 20 | 1:14 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23040900049 | New_Event | Animals | Include | Include | Wildlife | 74 | 2023-04-09 | 1480 | keep | 0 | Apr | 2023 | 0.001008 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-09 08:41 | 2023-04-10 16:00 | 12 | 31:19 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23040900050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1879 | 2023-04-09 | 22548 | keep | 0 | Apr | 2023 | 0.015357 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-04-09 08:43 | 2023-04-09 10:44 | 110 | 2:01 | P | ANIMAL | PAJARO CRUZO FASE 1 X 100 1 X 80 EN RISER | P23040900140 | New_Event | Animals | Include | Include | Wildlife | 121 | 2023-04-09 | 13310 | keep | 0 | Apr | 2023 | 0.0090654 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2023-04-09 08:47 | 2023-04-09 13:10 | 100 | 4:23 | P | ANIMAL | 2 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M23040900043 | New_Event | Animals | Include | Include | Wildlife | 263 | 2023-04-09 | 26300 | keep | 0 | Apr | 2023 | 0.017913 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-09 08:48 | 2023-04-09 10:45 | 18 | 1:57 | P | DESGANCHE | 1 X 30 EN C/L | C23040900052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-04-09 | 2106 | keep | 0 | Apr | 2023 | 0.0014344 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-04-09 09:14 | 2023-04-09 12:40 | 25 | 3:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | A23040900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2023-04-09 | 5150 | keep | 0 | Apr | 2023 | 0.0035076 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-04-09 09:33 | 2023-04-09 12:05 | 1 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO RISER PARA REPARAR CONECTORES QUEMADOS | M23040900052 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2023-04-09 | 152 | keep | 0 | Apr | 2023 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-09 09:38 | 2023-04-10 09:44 | 30 | 24:06 | P | DESGANCHE | 1 X 100 EN C/L SE RETIRO RAMA DE LAS LINEAS | B23040900024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1446 | 2023-04-09 | 43380 | keep | 0 | Apr | 2023 | 0.029546 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-09 09:55 | 2023-04-09 11:45 | 10 | 1:50 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA CRUZADA | M23040800276 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 110 | 2023-04-09 | 1100 | keep | 0 | Apr | 2023 | 0.0007492 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-09 10:02 | 2023-04-09 13:20 | 7 | 3:18 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23040900059 | New_Event | Animals | Include | Include | Wildlife | 198 | 2023-04-09 | 1386 | keep | 0 | Apr | 2023 | 0.000944 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-04-09 10:04 | 2023-04-09 10:55 | 4 | 0:51 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23040900055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-04-09 | 204 | keep | 0 | Apr | 2023 | 0.00013894 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-09 10:08 | 2023-04-10 12:04 | 40 | 25:56 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR 1 X 40 RISER 1 X 50 EN SU 16 | B23040900028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1556 | 2023-04-09 | 62240 | keep | 0 | Apr | 2023 | 0.042391 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-09 10:10 | 2023-04-09 16:24 | 51 | 6:14 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR IGUANA | B23040900034 | New_Event | Animals | Include | Include | Wildlife | 374 | 2023-04-09 | 19074 | keep | 0 | Apr | 2023 | 0.012991 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-04-09 10:12 | 2023-04-09 10:13 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL 1907-03 QUE LLEVA 1909-09 | S2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-09 10:12 | 2023-04-09 10:13 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1907-03 QUE LLEVA 1909-09 | S2304090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-09 | 4456 | keep | 0 | Apr | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2023-04-09 10:15 | 2023-04-09 14:28 | 6 | 4:13 | P | DESGANCHE | 1 X 15 EN C/L DESGANCHE | B23040900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2023-04-09 | 1518 | keep | 0 | Apr | 2023 | 0.0010339 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-04-09 10:17 | 2023-04-09 12:15 | 8 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | P23040900213 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2023-04-09 | 944 | keep | 0 | Apr | 2023 | 0.00064295 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-09 10:33 | 2023-04-09 10:55 | 10 | 0:22 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y DESGANCHE SECUNDARIO | S23040900017 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 22 | 2023-04-09 | 220 | keep | 0 | Apr | 2023 | 0.00014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-09 10:39 | 2023-04-09 13:00 | 6 | 2:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M23040900057 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 141 | 2023-04-09 | 846 | keep | 0 | Apr | 2023 | 0.00057621 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-09 10:40 | 2023-04-09 11:27 | 15 | 0:47 | P | TRANSFORMADOR AVERIADO | SE ABRIO TRANSFORMADOR PARA REPARAR BUSHING SECUNDARIO EN TRANSFORMADOR | M23040900056 | New_Event | Service Transformer Failure | Include | Include | Equipment | 47 | 2023-04-09 | 705 | keep | 0 | Apr | 2023 | 0.00048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-09 10:42 | 2023-04-09 13:06 | 1783 | 2:24 | P | CAUSAS EXTERNAS | MEDIANTE BY-230409-01 SE SECCIONALIZO ALIMENTADOR ABRIENDO AMARRE CON 1711-04 Y SE CERRO POR SCADA 1801-02. SE RETIRO GLOBO Y SE CERRO N/O | B23040900050 | New_Event | Damage From Public | Include | Include | Public | 144 | 2023-04-09 | 256752 | keep | 0 | Apr | 2023 | 0.17487 | 0.0012144 | Sustained | FALSE | FALSE | Not_TMED_Event | 1783
BAYAMON | 2023-04-09 10:42 | 2023-04-09 13:06 | 136 | 2:24 | P | ALIMENTADOR AMARRADO | MEDIANTE BY-230409-01 SE SECCIONALIZO ALIMENTADOR ABRIENDO AMARRE CON 1711-04 Y SE CERRO POR SCADA 1801-02. SE RETIRO GLOBO EN TRAMO 1711-04 Y SE CERRO N/O. 1801-02 LLEVA 10% DEL 1717-04 | B23040900050 | New_Event | Feeder Load Transferred | Include | Include | Other | 144 | 2023-04-09 | 19584 | keep | 0 | Apr | 2023 | 0.013339 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
BAYAMON | 2023-04-09 10:42 | 2023-04-09 11:59 | 186 | 1:17 | T | ALIMENTADOR AMARRADO | BY-230409-01 SE ABRIO AMARRE CONTRA 1711-04 LLEVA 90% 1711-04 LLEVA 10% 1717-01 POR GLOBO METALICO EN TRAMO 1711-04 | B23040900050 | New_Event | Feeder Load Transferred | Include | Include | Other | 77 | 2023-04-09 | 14322 | keep | 0 | Apr | 2023 | 0.0097546 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
YAUCO | 2023-04-09 10:48 | 2023-04-09 11:00 | 79 | 0:12 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA PAJARO CRUZO FASE | P23040900140 | New_Event | Animals | Include | Include | Wildlife | 12 | 2023-04-09 | 948 | keep | 0 | Apr | 2023 | 0.00064568 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2023-04-09 11:00 | 2023-04-09 12:48 | 10 | 1:48 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | B23040900014 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-04-09 | 1080 | keep | 0 | Apr | 2023 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-09 11:00 | 2023-04-09 11:01 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 652 | keep | 0 | Apr | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-04-09 11:01 | 2023-04-09 13:08 | 10 | 2:07 | P | DESGANCHE | 1 X 15 EN XMR Y DESGANCHE EVENTO DE VEGA BAJA | P23040900209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-04-09 | 1270 | keep | 0 | Apr | 2023 | 0.00086499 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-09 11:20 | 2023-04-09 11:30 | 1483 | 0:10 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR SE VERIFICO PERSONAL REALIZANDO PRUEBA EN SOTERRADO Y SE PROBO QUEDO EN SERVICIO 30% POR 1303-02 | S23040900065 | New_Event | Feeder Load Transferred | Include | Include | Other | 10 | 2023-04-09 | 14830 | keep | 0 | Apr | 2023 | 0.010101 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-04-09 11:20 | 2023-04-09 11:30 | 2435 | 0:10 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO INTERRUPTOR SE VERIFICO PERSONAL REALIZANDO PRUEBA EN SOTERRADO Y SE PROBO QUEDO EN SERVICIO LLEVA 30% DEL 1204-04 | S23040900065 | New_Event | Cutout Failure | Include | Include | Equipment | 10 | 2023-04-09 | 24350 | keep | 0 | Apr | 2023 | 0.016585 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-04-09 11:30 | 2023-04-09 15:14 | 150 | 3:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | S23040900123 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 224 | 2023-04-09 | 33600 | keep | 0 | Apr | 2023 | 0.022885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-09 11:30 | 2023-04-09 11:32 | 150 | 0:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER 2 X 50 EN SU-7 Y 1 X 80 EN OTRO RISER MAL TIEMPO LLUVIA | S23040800561 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-04-09 | 300 | keep | 0 | Apr | 2023 | 0.00020433 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-09 11:32 | 2023-04-09 11:35 | 220 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1303-05 SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 98% DE 1303-04 | S23040900113 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-09 | 660 | keep | 0 | Apr | 2023 | 0.00044952 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-04-09 11:32 | 2023-04-09 11:35 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 98% DEL 1303-04 | S23040900113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-09 | 2610 | keep | 0 | Apr | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-04-09 11:35 | 2023-04-09 13:04 | 80 | 1:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-2 NO CAUSA | S23040900050 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 89 | 2023-04-09 | 7120 | keep | 0 | Apr | 2023 | 0.0048494 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-04-09 11:46 | 2023-04-09 11:47 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 2722 | keep | 0 | Apr | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
UTUADO | 2023-04-09 11:47 | 2023-04-09 14:44 | 30 | 2:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA | P23040900218 | New_Event | Primary Wire Break | Include | Include | Equipment | 177 | 2023-04-09 | 5310 | keep | 0 | Apr | 2023 | 0.0036166 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-04-09 12:10 | 2023-04-09 12:11 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23040900223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 2379 | keep | 0 | Apr | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
VEGA BAJA | 2023-04-09 12:10 | 2023-04-09 14:33 | 40 | 2:23 | P | ANIMAL | 1 X 25 Y 1 X 40 EN CORTE DE LINEA POR AVE | A23040900021 | New_Event | Animals | Include | Include | Wildlife | 143 | 2023-04-09 | 5720 | keep | 0 | Apr | 2023 | 0.0038959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-09 12:15 | 2023-04-09 13:39 | 10 | 1:24 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23040900087 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-04-09 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-09 12:15 | 2023-04-09 20:48 | 40 | 8:33 | P | CABLE SOTERRADO AVERIADO | 1 X 30 SE CONTRUYO AEREO PROVISIONAL EXISTENTE A T-37 SE QUEDO UN XMR FUERA | B23040900010 | New_Event | UG Cable Fault | Include | Include | Equipment | 513 | 2023-04-09 | 20520 | keep | 0 | Apr | 2023 | 0.013976 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-09 12:32 | 2023-04-09 12:51 | 1 | 0:19 | P | DESGANCHE | 1 X 140 EN C/L | C23040900078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-04-09 | 19 | keep | 0 | Apr | 2023 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-09 12:42 | 2023-04-09 14:13 | 2092 | 1:31 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1619-02 (SPARE) LLEVA 42% DEL 1336-06 Y 50% 1619-03. SE REALIZARON OPERACIONES ENTRO 100% EN SERVICIO DEL 1336-06 Y 10% DEL 1619-03 | R23040900045 | New_Event | Feeder Load Transferred | Include | Include | Other | 91 | 2023-04-09 | 190372 | keep | 0 | Apr | 2023 | 0.12966 | 0.0014249 | Sustained | FALSE | FALSE | Not_TMED_Event | 2092
CANOVANAS | 2023-04-09 12:42 | 2023-04-09 14:13 | 2531 | 1:31 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 1619-02 (SPARE) LLEVA 42% DEL 1336-06 Y 50% 1619-03. SE REALIZARON OPERACIONES ENTRO 100% EN SERVICIO DEL 1336-06 Y 10% DEL 1619-03 | R23040900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2023-04-09 | 230321 | keep | 0 | Apr | 2023 | 0.15687 | 0.0017239 | Sustained | FALSE | FALSE | Not_TMED_Event | 2531
SAN JUAN | 2023-04-09 12:53 | 2023-04-09 15:22 | 40 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA Y 2 X 20 EN RISER MAL TIEMPO VIENTOS | S23040900141 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2023-04-09 | 5960 | keep | 0 | Apr | 2023 | 0.0040593 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-09 13:01 | 2023-04-10 11:20 | 12 | 22:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO BAJANTE | S23040900142 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1339 | 2023-04-09 | 16068 | keep | 0 | Apr | 2023 | 0.010944 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-09 13:02 | 2023-04-09 14:50 | 514 | 1:48 | T | ALIMENTADOR AMARRADO | DISPARO SE RETIRO ARBOL SOBRE LINEA RES. NEMESIO CANALES Y SE BORRO BANDERA SE PROBO BKR. 100% EN SEVICIO SU CARGA POR 1520-05 | S23040900146 | New_Event | Feeder Load Transferred | Include | Include | Other | 108 | 2023-04-09 | 55512 | keep | 0 | Apr | 2023 | 0.037809 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2023-04-09 13:02 | 2023-04-09 14:50 | 752 | 1:48 | T | ALIMENTADOR AMARRADO | DISPARO SE RETIRO ARBOL SOBRE LINEA RES. NEMSIO CANALES Y SE BORRO BANDERA SE PROBO BKR. 100% EN SEVICIO SU CARGA POR 1520-05 | S23040900146 | New_Event | Feeder Load Transferred | Include | Include | Other | 108 | 2023-04-09 | 81216 | keep | 0 | Apr | 2023 | 0.055316 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2023-04-09 13:02 | 2023-04-09 14:50 | 68 | 1:48 | T | ARBOL SOBRE LINEA | DISPARO SE RETIRO ARBOL SOBRE LINEA RES. NEMSIO CANALES Y SE BORRO BANDERA SE PROBO BKR. 100% EN SERVICIO LLEVA 1520-01 Y 4 | S23040900146 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 108 | 2023-04-09 | 7344 | keep | 0 | Apr | 2023 | 0.005002 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
MAYAGÃœEZ | 2023-04-09 13:34 | 2023-04-09 14:45 | 40 | 1:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE LINEA A RISER | M23040900070 | New_Event | Primary Wire Break | Include | Include | Equipment | 71 | 2023-04-09 | 2840 | keep | 0 | Apr | 2023 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-09 13:39 | 2023-04-10 14:02 | 42 | 24:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR QUEMADO 25KVA X 50KVA | C23040900083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1463 | 2023-04-09 | 61446 | keep | 0 | Apr | 2023 | 0.041851 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CAGUAS | 2023-04-09 13:58 | 2023-04-09 17:28 | 50 | 3:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23040900085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 210 | 2023-04-09 | 10500 | keep | 0 | Apr | 2023 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-09 14:10 | 2023-04-09 16:51 | 8 | 2:41 | P | ANIMAL | 1 X15 EN XMR POR CRUCE DE ANIMAL SE REPARO BUSHING | B23040900104 | New_Event | Animals | Include | Include | Wildlife | 161 | 2023-04-09 | 1288 | keep | 0 | Apr | 2023 | 0.00087725 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-04-09 14:11 | 2023-04-09 15:33 | 50 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C23040900086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-04-09 | 4100 | keep | 0 | Apr | 2023 | 0.0027925 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-09 14:13 | 2023-04-09 14:22 | 2278 | 0:09 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES PROBO BUENO EL TRAMO 70% EN SERVICIO DEL 1619-03 | R23040900045 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-04-09 | 20502 | keep | 0 | Apr | 2023 | 0.013964 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-09 14:22 | 2023-04-09 14:53 | 760 | 0:31 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES PROBO BUENO EL TRAMO 75% EN SERVICIO DEL 1619-03 | R23040900045 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 31 | 2023-04-09 | 23560 | keep | 0 | Apr | 2023 | 0.016047 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-09 14:30 | 2023-04-09 19:46 | 1 | 5:16 | P | DESGANCHE | 1 X 50 EN RISER Y 1 X 80 EN CORTE DE LINEA DESGANCHE | S23040900182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-04-09 | 316 | keep | 0 | Apr | 2023 | 0.00021523 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-09 14:31 | 2023-04-09 14:33 | 1825 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040900184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 3650 | keep | 0 | Apr | 2023 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-04-09 14:31 | 2023-04-09 14:33 | 47 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040900184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 94 | keep | 0 | Apr | 2023 | 6.4023e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-04-09 14:31 | 2023-04-09 14:33 | 315 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040900184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 630 | keep | 0 | Apr | 2023 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-04-09 14:31 | 2023-04-09 14:33 | 2 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040900184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 4 | keep | 0 | Apr | 2023 | 2.7244e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-09 14:31 | 2023-04-09 14:33 | 2391 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23040900184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 4782 | keep | 0 | Apr | 2023 | 0.003257 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2023-04-09 14:31 | 2023-04-09 14:33 | 2276 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040900091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 4552 | keep | 0 | Apr | 2023 | 0.0031003 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-04-09 14:31 | 2023-04-09 14:33 | 777 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040900091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 1554 | keep | 0 | Apr | 2023 | 0.0010584 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-04-09 14:31 | 2023-04-09 14:33 | 12 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040900091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 24 | keep | 0 | Apr | 2023 | 1.6346e-05 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-09 14:31 | 2023-04-09 14:33 | 1290 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | C23040900091 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-09 | 2580 | keep | 0 | Apr | 2023 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-04-09 14:33 | 2023-04-09 20:40 | 5 | 6:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SE REMPLAZO PUENTE DE LINEA A CAJA | S23040800601 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 367 | 2023-04-09 | 1835 | keep | 0 | Apr | 2023 | 0.0012498 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-09 14:42 | 2023-04-09 14:43 | 3597 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9405-05 LLEVA EL 1719-15 | B2304090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-09 | 3597 | keep | 0 | Apr | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-04-09 14:42 | 2023-04-09 14:43 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9405-05 LLEVA EL 1719-15 | B2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 3511 | keep | 0 | Apr | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-04-09 14:47 | 2023-04-09 14:48 | 2435 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-04-09 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-09 14:47 | 2023-04-09 14:48 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-09 | 2956 | keep | 0 | Apr | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-04-09 14:48 | 2023-04-09 14:52 | 244 | 0:04 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 4 | 2023-04-09 | 976 | keep | 0 | Apr | 2023 | 0.00066475 | 0.00016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 244
FAJARDO | 2023-04-09 14:49 | 2023-04-09 15:50 | 1 | 1:01 | P | NO SE REPORTO CAUSA | 1 NX X 10 EN XMR | R23040900114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-04-09 | 61 | keep | 0 | Apr | 2023 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-09 14:52 | 2023-04-09 14:54 | 2435 | 0:02 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-04-09 | 4870 | keep | 0 | Apr | 2023 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-09 14:52 | 2023-04-09 14:54 | 2956 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-09 | 5912 | keep | 0 | Apr | 2023 | 0.0040266 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CANOVANAS | 2023-04-09 14:53 | 2023-04-09 14:57 | 506 | 0:04 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES PROBO BUENO EL TRAMO 80% EN SERVICIO DEL 1619-03 | R23040900045 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-09 | 2024 | keep | 0 | Apr | 2023 | 0.0013785 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-09 14:54 | 2023-04-09 16:52 | 244 | 1:58 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 118 | 2023-04-09 | 28792 | keep | 0 | Apr | 2023 | 0.01961 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
CANOVANAS | 2023-04-09 14:57 | 2023-04-09 15:20 | 254 | 0:23 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES PROBO BUENO EL TRAMO 90% EN SERVICIO DEL 1619-03 | R23040900045 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 23 | 2023-04-09 | 5842 | keep | 0 | Apr | 2023 | 0.003979 | 0.000173 | Sustained | FALSE | FALSE | Not_TMED_Event | 254
ARECIBO | 2023-04-09 14:59 | 2023-04-09 17:35 | 246 | 2:36 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA POR LINEA PARTIDA POR CAMION | A23040900030 | New_Event | Damage From Public | Include | Include | Public | 156 | 2023-04-09 | 38376 | keep | 0 | Apr | 2023 | 0.026138 | 0.00016755 | Sustained | FALSE | FALSE | Not_TMED_Event | 246
SAN JUAN | 2023-04-09 15:02 | 2023-04-09 17:30 | 150 | 2:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-6 NO CAUSA | S23040900190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2023-04-09 | 22200 | keep | 0 | Apr | 2023 | 0.01512 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-09 15:03 | 2023-04-09 19:16 | 20 | 4:13 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN EL SU-C PARARRAYOS | B23040900110 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 253 | 2023-04-09 | 5060 | keep | 0 | Apr | 2023 | 0.0034463 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-04-09 15:11 | 2023-04-09 16:11 | 3 | 1:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO CAJA EN XMR | P23040900258 | New_Event | Cutout Failure | Include | Include | Equipment | 60 | 2023-04-09 | 180 | keep | 0 | Apr | 2023 | 0.0001226 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-09 15:18 | 2023-04-09 16:46 | 10 | 1:28 | P | ANIMAL | 1 X 10 EN XMR AVE CRUZO LINEAS | R23040900117 | New_Event | Animals | Include | Include | Wildlife | 88 | 2023-04-09 | 880 | keep | 0 | Apr | 2023 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-09 15:20 | 2023-04-09 15:34 | 127 | 0:14 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES PROBO BUENO EL TRAMO 100% EN SERVICIO DEL 1619-03 | R23040900045 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 14 | 2023-04-09 | 1778 | keep | 0 | Apr | 2023 | 0.001211 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-09 15:20 | 2023-04-09 15:21 | 539 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23040900118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 539 | keep | 0 | Apr | 2023 | 0.00036711 | 0.00036711 | Momentary | FALSE | FALSE | Not_TMED_Event | 539
CANOVANAS | 2023-04-09 15:23 | 2023-04-09 18:33 | 10 | 3:10 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23040900119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-04-09 | 1900 | keep | 0 | Apr | 2023 | 0.0012941 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-09 15:31 | 2023-04-09 19:28 | 50 | 3:57 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA ANIMAL CRUZO FASE | S23040900197 | New_Event | Animals | Include | Include | Wildlife | 237 | 2023-04-09 | 11850 | keep | 0 | Apr | 2023 | 0.008071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-09 15:45 | 2023-04-09 21:46 | 15 | 6:01 | P | DESGANCHE | 1 X 30 EN TRANSFORMADOR DESGANCHE | S23040900202 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2023-04-09 | 5415 | keep | 0 | Apr | 2023 | 0.0036881 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-04-09 15:50 | 2023-04-09 15:51 | 2092 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1619-02(SPARE) LLEVA 42% DEL 1336-06 Y 50% DEL 1619-03 | R2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 2092 | keep | 0 | Apr | 2023 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CANOVANAS | 2023-04-09 15:50 | 2023-04-09 15:51 | 2278 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1619-02(SPARE) LLEVA 42% DEL 1336-06 Y 50% DEL 1619-03 | R2304090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-09 | 2278 | keep | 0 | Apr | 2023 | 0.0015515 | 0.0015515 | Momentary | FALSE | FALSE | Not_TMED_Event | 2278
BARRANQUITAS | 2023-04-09 15:57 | 2023-04-09 17:19 | 1 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | C23040900095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-04-09 | 82 | keep | 0 | Apr | 2023 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-09 16:26 | 2023-04-10 09:41 | 12 | 17:15 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHE | S23040900206 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1035 | 2023-04-09 | 12420 | keep | 0 | Apr | 2023 | 0.0084592 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-09 16:39 | 2023-04-10 11:00 | 3 | 18:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SECUNDARIA | B23040900116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1101 | 2023-04-09 | 3303 | keep | 0 | Apr | 2023 | 0.0022497 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-09 16:52 | 2023-04-09 17:17 | 2435 | 0:25 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 25 | 2023-04-09 | 60875 | keep | 0 | Apr | 2023 | 0.041462 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-09 16:52 | 2023-04-09 17:17 | 2956 | 0:25 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 25 | 2023-04-09 | 73900 | keep | 0 | Apr | 2023 | 0.050333 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
AGUADILLA | 2023-04-09 16:58 | 2023-04-09 19:10 | 400 | 2:12 | P | TRANSFORMADOR AVERIADO | 3 X 140 EN CORTE DE LINEA CONVERTIDOR AVERIADO | M23040900092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 132 | 2023-04-09 | 52800 | keep | 0 | Apr | 2023 | 0.035962 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2023-04-09 17:00 | 2023-04-09 21:33 | 150 | 4:33 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE RETIRO PARARRAYO AVERIADO | S23040900220 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 273 | 2023-04-09 | 40950 | keep | 0 | Apr | 2023 | 0.027891 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-04-09 17:06 | 2023-04-09 17:50 | 35 | 0:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R23040900130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 44 | 2023-04-09 | 1540 | keep | 0 | Apr | 2023 | 0.0010489 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-04-09 17:13 | 2023-04-10 08:10 | 70 | 14:57 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | S23040900224 | New_Event | Animals | Include | Include | Wildlife | 897 | 2023-04-09 | 62790 | keep | 0 | Apr | 2023 | 0.042766 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-04-09 17:17 | 2023-04-09 18:40 | 244 | 1:23 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 83 | 2023-04-09 | 20252 | keep | 0 | Apr | 2023 | 0.013794 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-09 17:22 | 2023-04-09 19:35 | 75 | 2:13 | P | CRUCETA DEFECTUOSA O AVERIADA | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO CRUZETA PARTIDA | A23040900051 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 133 | 2023-04-09 | 9975 | keep | 0 | Apr | 2023 | 0.0067939 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-04-09 17:42 | 2023-04-09 19:28 | 9 | 1:46 | P | ANIMAL | 1 X 20 EN XMR CRUCE POR AVE | C23040900097 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-04-09 | 954 | keep | 0 | Apr | 2023 | 0.00064977 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-04-09 18:08 | 2023-04-09 18:10 | 362 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 90% POR 1620-01 | S2304090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-09 | 724 | keep | 0 | Apr | 2023 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-04-09 18:08 | 2023-04-09 18:10 | 36 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA 60% DEL 1620-02 Y 90% DEL 1336-10 | S23040900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-09 | 72 | keep | 0 | Apr | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-04-09 18:08 | 2023-04-09 18:10 | 2226 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 60% POR 1620-01 | S2304090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-09 | 4452 | keep | 0 | Apr | 2023 | 0.0030322 | 0.0015161 | Momentary | FALSE | FALSE | Not_TMED_Event | 2226
CANOVANAS | 2023-04-09 18:35 | 2023-04-09 19:34 | 1 | 0:59 | P | DESGANCHE | DESGANCHE Y 1 X 30 EN C/L | R23040900134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-04-09 | 59 | keep | 0 | Apr | 2023 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-09 18:40 | 2023-04-09 18:41 | 2435 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-04-09 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-09 18:40 | 2023-04-09 18:41 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-09 | 2956 | keep | 0 | Apr | 2023 | 0.0020133 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-09 18:41 | 2023-04-11 09:28 | 30 | 38:47 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE | S23040900297 | New_Event | Animals | Include | Include | Wildlife | 2327 | 2023-04-09 | 69810 | keep | 0 | Apr | 2023 | 0.047547 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-09 18:41 | 2023-04-09 18:53 | 244 | 0:12 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 12 | 2023-04-09 | 2928 | keep | 0 | Apr | 2023 | 0.0019942 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
VEGA BAJA | 2023-04-09 18:49 | 2023-04-09 20:05 | 400 | 1:16 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | A23040900057 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-04-09 | 30400 | keep | 0 | Apr | 2023 | 0.020705 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-04-09 18:53 | 2023-04-09 18:54 | 2435 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-04-09 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-09 18:53 | 2023-04-09 18:54 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-09 | 2956 | keep | 0 | Apr | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CANOVANAS | 2023-04-09 18:53 | 2023-04-09 20:27 | 33 | 1:34 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | R23040900137 | New_Event | Primary Wire Break | Include | Include | Equipment | 94 | 2023-04-09 | 3102 | keep | 0 | Apr | 2023 | 0.0021128 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-04-09 18:54 | 2023-04-09 18:56 | 244 | 0:02 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 2 | 2023-04-09 | 488 | keep | 0 | Apr | 2023 | 0.00033237 | 0.00016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 244
BAYAMON | 2023-04-09 18:56 | 2023-04-09 19:01 | 2435 | 0:05 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 5 | 2023-04-09 | 12175 | keep | 0 | Apr | 2023 | 0.0082923 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-09 18:56 | 2023-04-09 19:01 | 2956 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-09 | 14780 | keep | 0 | Apr | 2023 | 0.010067 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-04-09 19:01 | 2023-04-10 11:22 | 244 | 16:21 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE REEMPLAZO VS-05 AVERIADO BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 981 | 2023-04-09 | 239364 | keep | 0 | Apr | 2023 | 0.16303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-09 19:02 | 2023-04-09 19:03 | 3833 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | C23040900102 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-09 | 3833 | keep | 0 | Apr | 2023 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2023-04-09 19:03 | 2023-04-10 07:24 | 130 | 12:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA LLUVIAS | C23040900104 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 741 | 2023-04-09 | 96330 | keep | 0 | Apr | 2023 | 0.06561 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2023-04-09 19:06 | 2023-04-09 19:07 | 2234 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE BKR | B2304090000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-04-09 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-04-09 19:07 | 2023-04-10 11:40 | 8 | 16:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23040900137 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 993 | 2023-04-09 | 7944 | keep | 0 | Apr | 2023 | 0.0054106 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-04-09 19:10 | 2023-04-10 02:20 | 715 | 7:10 | P | TRANSFORMADOR AVERIADO | SE REPARO CONVERTIDOR SE CERRO MACHETES | M23040900092 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 430 | 2023-04-09 | 307450 | keep | 0 | Apr | 2023 | 0.2094 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-09 19:30 | 2023-04-10 10:42 | 15 | 15:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23040900108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 912 | 2023-04-09 | 13680 | keep | 0 | Apr | 2023 | 0.0093174 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-09 20:00 | 2023-04-10 07:01 | 46 | 11:01 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | S23040900340 | New_Event | Vegetation Contact | Include | Include | Vegetation | 661 | 2023-04-09 | 30406 | keep | 0 | Apr | 2023 | 0.020709 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
FAJARDO | 2023-04-09 20:14 | 2023-04-10 09:22 | 2 | 13:08 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R23040900141 | New_Event | Animals | Include | Include | Wildlife | 788 | 2023-04-09 | 1576 | keep | 0 | Apr | 2023 | 0.0010734 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-04-09 20:31 | 2023-04-10 08:10 | 83 | 11:39 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23040900297 | New_Event | Vegetation Contact | Include | Include | Vegetation | 699 | 2023-04-09 | 58017 | keep | 0 | Apr | 2023 | 0.039515 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
VEGA BAJA | 2023-04-09 20:35 | 2023-04-10 07:40 | 20 | 11:05 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | A23040900068 | New_Event | Primary Wire Break | Include | Include | Equipment | 665 | 2023-04-09 | 13300 | keep | 0 | Apr | 2023 | 0.0090586 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-09 20:48 | 2023-04-10 18:31 | 10 | 21:43 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PRVISIONAL AEREO 1 X 25 EN C/L | B23040900010 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1303 | 2023-04-09 | 13030 | keep | 0 | Apr | 2023 | 0.0088747 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-09 20:49 | 2023-04-09 20:50 | 1117 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 1117 | keep | 0 | Apr | 2023 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
HUMACAO | 2023-04-09 20:51 | 2023-04-09 20:52 | 1117 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304090000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 1117 | keep | 0 | Apr | 2023 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
CAGUAS | 2023-04-09 21:20 | 2023-04-09 22:59 | 445 | 1:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA | C23040900116 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 99 | 2023-04-09 | 44055 | keep | 0 | Apr | 2023 | 0.030006 | 0.00030309 | Sustained | FALSE | FALSE | Not_TMED_Event | 445
HUMACAO | 2023-04-09 22:10 | 2023-04-10 09:05 | 7 | 10:55 | P | PARARRAYOS DEFECTUOSO | SE FIJO CAJA Y PARARRAYOS ZAFADOS 1 X 10 EN XMR | C23040900120 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 655 | 2023-04-09 | 4585 | keep | 0 | Apr | 2023 | 0.0031228 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-04-09 22:15 | 2023-04-09 22:16 | 220 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1303-05 | S2304090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-09 | 220 | keep | 0 | Apr | 2023 | 0.00014984 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-04-09 22:15 | 2023-04-09 22:16 | 870 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE BKR 1303-05 LLEVA 98% 1303-04 | S2304090000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-09 | 870 | keep | 0 | Apr | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-04-09 22:16 | 2023-04-10 03:40 | 470 | 5:24 | P | CONDUCTOR ROTO O ABIERTO | SJ-230410-01 SE SECCIONALIZO ALIMENTADOR PARA CERRAR PUENTE ABIERTO | S23040900386 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 324 | 2023-04-09 | 152280 | keep | 0 | Apr | 2023 | 0.10372 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
BAYAMON | 2023-04-09 22:20 | 2023-04-10 15:01 | 33 | 16:41 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 Y SE REEMPLAZO POSTE PRIMARIO | B23040900380 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1001 | 2023-04-09 | 33033 | keep | 0 | Apr | 2023 | 0.022499 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
AGUADILLA | 2023-04-09 22:36 | 2023-04-09 22:37 | 2658 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23040900124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 2658 | keep | 0 | Apr | 2023 | 0.0018104 | 0.0018104 | Momentary | FALSE | FALSE | Not_TMED_Event | 2658
HUMACAO | 2023-04-09 22:39 | 2023-04-10 00:10 | 3420 | 1:31 | S | ANIMAL | LOCKOUT DE SUB 2906-00 SE TRANSFIRIO LA CARGA DEL 2906-02 AL 2604-02 SE HICIERON OPERACIONES CON CG-230409-01 LA CAUSA FUE CRUCE DE GATO EN EL AUX#7 | C23040900125 | New_Event | Animals | Include | Include | Wildlife | 91 | 2023-04-09 | 311220 | keep | 0 | Apr | 2023 | 0.21197 | 0.0023293 | Sustained | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2023-04-09 22:39 | 2023-04-10 19:50 | 4 | 21:11 | S | ANIMAL | LOCKOUT DE SUB 2906-00 SE HICIERON OPERACIONES CON CG-230409-01 LA CAUSA FUE CRUCE DE GATO EN EL AUX#7. SE DEJO FUERA POR ERROR SUBESTACION NO TIENE RTU. | C23040900125 | New_Event | Animals | Include | Include | Wildlife | 1271 | 2023-04-09 | 5084 | keep | 0 | Apr | 2023 | 0.0034627 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-04-09 22:39 | 2023-04-10 12:40 | 3 | 14:01 | S | ANIMAL | LOCKOUT DE SUB 2906-00 SE HICIERON OPERACIONES CON CG-230409-01. LA CAUSA FUE CRUCE DE GATO EN EL AUX#7. | C23040900125 | New_Event | Animals | Include | Include | Wildlife | 841 | 2023-04-09 | 2523 | keep | 0 | Apr | 2023 | 0.0017184 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-04-09 22:42 | 2023-04-10 10:30 | 10 | 11:48 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23040900075 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 708 | 2023-04-09 | 7080 | keep | 0 | Apr | 2023 | 0.0048222 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-09 22:59 | 2023-04-09 23:00 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23040900130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-04-09 23:00 | 2023-04-10 00:42 | 445 | 1:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA | C23040900116 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 102 | 2023-04-09 | 45390 | keep | 0 | Apr | 2023 | 0.030915 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-09 23:16 | 2023-04-09 23:22 | 222 | 0:06 | P | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA PARTE POR 1338-02 | S23040900419 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-09 | 1332 | keep | 0 | Apr | 2023 | 0.00090722 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
SAN JUAN | 2023-04-09 23:17 | 2023-04-09 23:18 | 849 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 7200 | S23040900422 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-09 | 849 | keep | 0 | Apr | 2023 | 0.00057825 | 0.00057825 | Momentary | FALSE | FALSE | Not_TMED_Event | 849
SAN JUAN | 2023-04-09 23:17 | 2023-04-09 23:18 | 893 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 7200 | S23040900422 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-09 | 893 | keep | 0 | Apr | 2023 | 0.00060822 | 0.00060822 | Momentary | FALSE | FALSE | Not_TMED_Event | 893
SAN JUAN | 2023-04-09 23:17 | 2023-04-09 23:18 | 602 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 7200 | S23040900422 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-09 | 602 | keep | 0 | Apr | 2023 | 0.00041002 | 0.00041002 | Momentary | FALSE | FALSE | Not_TMED_Event | 602
SAN JUAN | 2023-04-09 23:17 | 2023-04-09 23:18 | 43 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 7200 | S23040900422 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-09 | 43 | keep | 0 | Apr | 2023 | 2.9287e-05 | 2.9287e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-04-09 23:17 | 2023-04-09 23:18 | 1389 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 7200 | S23040900422 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-09 | 1389 | keep | 0 | Apr | 2023 | 0.00094604 | 0.00094604 | Momentary | FALSE | FALSE | Not_TMED_Event | 1389
SAN JUAN | 2023-04-09 23:17 | 2023-04-09 23:18 | 732 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | S2304090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-09 | 732 | keep | 0 | Apr | 2023 | 0.00049856 | 0.00049856 | Momentary | FALSE | FALSE | Not_TMED_Event | 732
GUAYAMA | 2023-04-10 01:09 | 2023-04-11 18:51 | 6 | 41:42 | P | CABLE SOTERRADO AVERIADO | SE REALIZO EXCAVACION PARA INSTALACION DE TUBERIA SOTERRADA Y CABLE SOTERRADO NUEVO | P23041000008 | New_Event | UG Cable Fault | Include | Include | Equipment | 2502 | 2023-04-10 | 15012 | keep | 0 | Apr | 2023 | 0.010225 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-04-10 01:15 | 2023-04-10 07:55 | 10 | 6:40 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C23041000003 | New_Event | Animals | Include | Include | Wildlife | 400 | 2023-04-10 | 4000 | keep | 0 | Apr | 2023 | 0.0027244 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-10 04:17 | 2023-04-10 04:18 | 1825 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 1825 | keep | 0 | Apr | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
CANOVANAS | 2023-04-10 04:57 | 2023-04-10 09:15 | 240 | 4:18 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR PALOMA | R23041000001 | New_Event | Animals | Include | Include | Wildlife | 258 | 2023-04-10 | 61920 | keep | 0 | Apr | 2023 | 0.042173 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
VEGA BAJA | 2023-04-10 05:44 | 2023-04-10 09:40 | 25 | 3:56 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23041000002 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 236 | 2023-04-10 | 5900 | keep | 0 | Apr | 2023 | 0.0040185 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-10 05:54 | 2023-04-10 10:17 | 276 | 4:23 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23041000002 | New_Event | Animals | Include | Include | Wildlife | 263 | 2023-04-10 | 72588 | keep | 0 | Apr | 2023 | 0.049439 | 0.00018798 | Sustained | FALSE | FALSE | Not_TMED_Event | 276
YAUCO | 2023-04-10 06:32 | 2023-04-10 07:18 | 21 | 0:46 | P | DESGANCHE | 1 X 65 EN COTE DE LINEA POR DESGANCHE | P23041000011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2023-04-10 | 966 | keep | 0 | Apr | 2023 | 0.00065794 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-04-10 06:34 | 2023-04-10 07:00 | 6 | 0:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23040900103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 26 | 2023-04-10 | 156 | keep | 0 | Apr | 2023 | 0.00010625 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-04-10 06:39 | 2023-04-10 09:25 | 6 | 2:46 | P | ANIMAL | 1 X 100 EN RISER CRUCE POR AVE | R23041000004 | New_Event | Animals | Include | Include | Wildlife | 166 | 2023-04-10 | 996 | keep | 0 | Apr | 2023 | 0.00067837 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-10 06:58 | 2023-04-10 13:18 | 7 | 6:20 | P | PARARRAYOS DEFECTUOSO | 1 X 15 XMR SE RETIRO PARARAYO | B23041000010 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 380 | 2023-04-10 | 2660 | keep | 0 | Apr | 2023 | 0.0018117 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-04-10 07:03 | 2023-04-10 11:20 | 105 | 4:17 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23041000028 | New_Event | Animals | Include | Include | Wildlife | 257 | 2023-04-10 | 26985 | keep | 0 | Apr | 2023 | 0.018379 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
PONCE | 2023-04-10 07:15 | 2023-04-10 12:15 | 15 | 5:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23041000032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-04-10 | 4500 | keep | 0 | Apr | 2023 | 0.0030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-04-10 07:16 | 2023-04-10 07:17 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 464 | keep | 0 | Apr | 2023 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
CANOVANAS | 2023-04-10 07:18 | 2023-04-10 17:27 | 1 | 10:09 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | R23041000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 609 | 2023-04-10 | 609 | keep | 0 | Apr | 2023 | 0.00041479 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-10 07:20 | 2023-04-10 11:15 | 21 | 3:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | P23041000039 | New_Event | Primary Wire Break | Include | Include | Equipment | 235 | 2023-04-10 | 4935 | keep | 0 | Apr | 2023 | 0.0033612 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2023-04-10 07:23 | 2023-04-10 09:15 | 1 | 1:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN RISER SE REMPLAZO CAJA PRIMARIA AVERIADA | M23041000009 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2023-04-10 | 112 | keep | 0 | Apr | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-10 07:26 | 2023-04-10 07:27 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | S23041000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 338 | keep | 0 | Apr | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
FAJARDO | 2023-04-10 07:34 | 2023-04-10 11:07 | 64 | 3:33 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | R23041000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-04-10 | 13632 | keep | 0 | Apr | 2023 | 0.0092847 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
VEGA BAJA | 2023-04-10 07:40 | 2023-04-10 08:10 | 40 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO SE CERRO CORTE DE LINEA | A23040900068 | New_Event | Primary Wire Break | Include | Include | Equipment | 30 | 2023-04-10 | 1200 | keep | 0 | Apr | 2023 | 0.00081731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-10 07:51 | 2023-04-11 11:04 | 1 | 27:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23041000037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1633 | 2023-04-10 | 1633 | keep | 0 | Apr | 2023 | 0.0011122 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-10 08:03 | 2023-04-10 14:02 | 58 | 5:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIA | B23041000013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 359 | 2023-04-10 | 20822 | keep | 0 | Apr | 2023 | 0.014182 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2023-04-10 08:10 | 2023-04-11 11:02 | 10 | 26:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | S23041000047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1612 | 2023-04-10 | 16120 | keep | 0 | Apr | 2023 | 0.010979 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-10 08:12 | 2023-04-10 23:14 | 20 | 15:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA CERRAR PUENTE SECUNDARIO | S23041000053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 902 | 2023-04-10 | 18040 | keep | 0 | Apr | 2023 | 0.012287 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-10 08:12 | 2023-04-10 13:00 | 1 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE RISER | A23041000014 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2023-04-10 | 288 | keep | 0 | Apr | 2023 | 0.00019616 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-04-10 08:16 | 2023-04-10 10:00 | 1 | 1:44 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23041000012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 104 | 2023-04-10 | 104 | keep | 0 | Apr | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-10 08:19 | 2023-04-10 19:24 | 300 | 11:05 | P | DESGANCHE | 1 X 100 EN RISER 1 X 80 EN RISER 1 X 65 EN RISER 2 X 50 EN RISER 1 X 20 EN TRANSFORMADOR SE REALIZO DESGANCHE | S23041000061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 665 | 2023-04-10 | 199500 | keep | 0 | Apr | 2023 | 0.13588 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2023-04-10 08:20 | 2023-04-10 16:24 | 562 | 8:04 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZO AISLADOR EN BARRA Y MACHETE EN EL # 5 | P23041000023 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 484 | 2023-04-10 | 272008 | keep | 0 | Apr | 2023 | 0.18526 | 0.00038278 | Sustained | FALSE | FALSE | Not_TMED_Event | 562
PONCE | 2023-04-10 08:20 | 2023-04-10 16:24 | 688 | 8:04 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZO AISLADOR EN BARRA Y MACHETE EN EL # 5 | P23041000023 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 484 | 2023-04-10 | 332992 | keep | 0 | Apr | 2023 | 0.2268 | 0.00046859 | Sustained | FALSE | FALSE | Not_TMED_Event | 688
PONCE | 2023-04-10 08:20 | 2023-04-10 16:24 | 658 | 8:04 | S | AVERIA EN BARRA DE DISTRIBUCION | SE REMPLAZO AISLADOR EN BARRA Y MACHETE EN EL # 5 | P23041000023 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 484 | 2023-04-10 | 318472 | keep | 0 | Apr | 2023 | 0.21691 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
SAN JUAN | 2023-04-10 08:24 | 2023-04-11 10:55 | 25 | 26:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 80 EN CORTE DE LINEA AISLADOR PARTIDO | S23041000071 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1591 | 2023-04-10 | 39775 | keep | 0 | Apr | 2023 | 0.027091 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-04-10 08:29 | 2023-04-10 10:25 | 1 | 1:56 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23041000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-04-10 | 116 | keep | 0 | Apr | 2023 | 7.9007e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-10 08:30 | 2023-04-10 09:15 | 6 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO TRAMO TRAS PATIO | S23040900139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-10 | 270 | keep | 0 | Apr | 2023 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-10 08:42 | 2023-04-10 10:50 | 100 | 2:08 | P | CAUSAS EXTERNAS | SE ELIMINO LA CORONA DE POSTE DE TELEFONICA QUE CAUSABA CRUCE 1 X 80 EN C/L | C23041000028 | New_Event | Damage From Public | Include | Include | Public | 128 | 2023-04-10 | 12800 | keep | 0 | Apr | 2023 | 0.008718 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-10 08:50 | 2023-04-10 11:35 | 250 | 2:45 | P | ANIMAL | DISPARO PORTATIL 8 FUNDIO 2 FUSIBLE DE ALTA GALLINA PALO CRUZO FASE LLEVA 20% DE SU CARGA SE PASO CARGA A LA 1401-08 | S23041000085 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-04-10 | 41250 | keep | 0 | Apr | 2023 | 0.028095 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-04-10 08:50 | 2023-04-10 11:35 | 1290 | 2:45 | S | ANIMAL | DISPARO PORTATIL 8 FUNDIO 2 FUSIBLE DE ALTA GALLINA PALO CRUZO FASE SE PASO CARGA AL 1401-8 | S23041000085 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-04-10 | 212850 | keep | 0 | Apr | 2023 | 0.14497 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
AGUADILLA | 2023-04-10 08:56 | 2023-04-10 11:00 | 60 | 2:04 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23041000024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-04-10 | 7440 | keep | 0 | Apr | 2023 | 0.0050674 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-04-10 08:58 | 2023-04-10 19:04 | 1 | 10:06 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23041000032 | New_Event | Animals | Include | Include | Wildlife | 606 | 2023-04-10 | 606 | keep | 0 | Apr | 2023 | 0.00041274 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-10 09:07 | 2023-04-10 09:08 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
CANOVANAS | 2023-04-10 09:17 | 2023-04-10 09:18 | 2561 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 50% DE SU CARGA POR EL 1619-02 | R2304100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 2561 | keep | 0 | Apr | 2023 | 0.0017443 | 0.0017443 | Momentary | FALSE | FALSE | Not_TMED_Event | 2561
MAYAGÃœEZ | 2023-04-10 09:30 | 2023-04-10 12:10 | 20 | 2:40 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23041000035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2023-04-10 | 3200 | keep | 0 | Apr | 2023 | 0.0021795 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-10 09:34 | 2023-04-10 17:55 | 23 | 8:21 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | R23041000034 | New_Event | Animals | Include | Include | Wildlife | 501 | 2023-04-10 | 11523 | keep | 0 | Apr | 2023 | 0.0078483 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
VEGA BAJA | 2023-04-10 09:37 | 2023-04-10 10:54 | 10 | 1:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50KV 1 X 15 | B23041000041 | New_Event | Service Transformer Failure | Include | Include | Equipment | 77 | 2023-04-10 | 770 | keep | 0 | Apr | 2023 | 0.00052444 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-10 09:40 | 2023-04-10 14:00 | 1 | 4:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23041000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2023-04-10 | 260 | keep | 0 | Apr | 2023 | 0.00017708 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-10 09:41 | 2023-04-10 10:51 | 1879 | 1:10 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO SE SECCIONALIZO | C23041000045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 70 | 2023-04-10 | 131530 | keep | 0 | Apr | 2023 | 0.089584 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
BAYAMON | 2023-04-10 10:00 | 2023-04-10 15:48 | 4 | 5:48 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIA | B23041000127 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 348 | 2023-04-10 | 1392 | keep | 0 | Apr | 2023 | 0.00094808 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-04-10 10:00 | 2023-04-10 12:15 | 1 | 2:15 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | C23041000073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2023-04-10 | 135 | keep | 0 | Apr | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-10 10:00 | 2023-04-10 14:55 | 10 | 4:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPAROO SECUNDARIA Y SE BAJO TAP DEL 5 AL 2 SE DEJO EN 124V POR FASE | B23040900027 | New_Event | Secondary Wire Break | Include | Include | Equipment | 295 | 2023-04-10 | 2950 | keep | 0 | Apr | 2023 | 0.0020092 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-10 10:32 | 2023-04-10 11:22 | 1 | 0:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO | C23041000108 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 50 | 2023-04-10 | 50 | keep | 0 | Apr | 2023 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-10 10:42 | 2023-04-10 13:28 | 1 | 2:46 | P | ANIMAL | 1 X 25 EN MONTURA DE TRANSFORMADOR AVE CRUZO FASE | P23041000127 | New_Event | Animals | Include | Include | Wildlife | 166 | 2023-04-10 | 166 | keep | 0 | Apr | 2023 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-10 10:51 | 2023-04-10 11:22 | 501 | 0:31 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS QUEMADOS EN TRONCAL | C23041000045 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 31 | 2023-04-10 | 15531 | keep | 0 | Apr | 2023 | 0.010578 | 0.00034123 | Sustained | FALSE | FALSE | Not_TMED_Event | 501
MAYAGÃœEZ | 2023-04-10 10:51 | 2023-04-10 10:52 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041000063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 312 | keep | 0 | Apr | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
GUAYAMA | 2023-04-10 11:00 | 2023-04-10 11:45 | 10 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REEMPLAZO DE BARRAS EN PEDESTAL | P23041000131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-10 | 450 | keep | 0 | Apr | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-10 11:13 | 2023-04-10 12:45 | 4 | 1:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23041000015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-04-10 | 368 | keep | 0 | Apr | 2023 | 0.00025064 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-04-10 11:22 | 2023-04-10 11:28 | 2999 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA | M23041000079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-10 | 17994 | keep | 0 | Apr | 2023 | 0.012256 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
HUMACAO | 2023-04-10 11:28 | 2023-04-10 15:00 | 1 | 3:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO | C23041000108 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 212 | 2023-04-10 | 212 | keep | 0 | Apr | 2023 | 0.00014439 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-10 11:31 | 2023-04-10 12:20 | 501 | 0:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS QUEMADOS EN TRONCAL | C23041000045 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 49 | 2023-04-10 | 24549 | keep | 0 | Apr | 2023 | 0.01672 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-10 11:32 | 2023-04-11 12:12 | 3 | 24:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. SJ-230410-50 | R23040800075 | New_Event | Primary Wire Break | Include | Include | Equipment | 1480 | 2023-04-10 | 4440 | keep | 0 | Apr | 2023 | 0.0030241 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-10 11:54 | 2023-04-10 13:30 | 1 | 1:36 | P | PROBLEMA DEL CLIENTE | 1 X 100 EN SU-24 Y 1 X 80 EN GABINETE CLIENTE (CONTAMINACION) | R23041000114 | New_Event | Customer-Related Interruption | Include | Include | Public | 96 | 2023-04-10 | 96 | keep | 0 | Apr | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-10 12:07 | 2023-04-10 12:08 | 1952 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | P23041000174 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-10 | 1952 | keep | 0 | Apr | 2023 | 0.0013295 | 0.0013295 | Momentary | FALSE | FALSE | Not_TMED_Event | 1952
PONCE | 2023-04-10 12:08 | 2023-04-10 15:22 | 150 | 3:14 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN C/L SE FIJO LINEA A AISLADOR | P23041000190 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 194 | 2023-04-10 | 29100 | keep | 0 | Apr | 2023 | 0.01982 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-10 12:17 | 2023-04-10 12:20 | 959 | 0:03 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE DISPARO BKR PARA ABRIR RISER HACIA VS-7 SE REALIZARON OPERACIONES BY-230408-02 50% EN SERVICIO CARGA POR 1904-07 | S23040800164 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 3 | 2023-04-10 | 2877 | keep | 0 | Apr | 2023 | 0.0019595 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-04-10 12:17 | 2023-04-10 12:20 | 959 | 0:03 | T | ALIMENTADOR AMARRADO | SE DISPARO BKR PARA ABRIR RISER HACIA VS-7 SE REALIZARON OPERACIONES BY-230408-02 100% EN SERVICIO CARGA POR 1904-07 | S23040800164 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-10 | 2877 | keep | 0 | Apr | 2023 | 0.0019595 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-04-10 12:20 | 2023-04-10 21:10 | 479 | 8:50 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZO OPERACION Y SE SECCIONALIZO TRAMO PARA TRABAJAR EN AVERIA DEL 1907-05 SE DEJO EN SERVICIO BY-230408-02 | S23040800164 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 530 | 2023-04-10 | 253870 | keep | 0 | Apr | 2023 | 0.17291 | 0.00032624 | Sustained | FALSE | FALSE | Not_TMED_Event | 479
CANOVANAS | 2023-04-10 12:29 | 2023-04-10 21:07 | 18 | 8:38 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REEMPLAZARON VARIOS TRAMOS DE SECUNDARIA TRASPATIO QUEMADA Y DESGANCHE | R23041000045 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 518 | 2023-04-10 | 9324 | keep | 0 | Apr | 2023 | 0.0063505 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-04-10 12:29 | 2023-04-10 12:30 | 2713 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041000102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-10 | 2713 | keep | 0 | Apr | 2023 | 0.0018478 | 0.0018478 | Momentary | FALSE | FALSE | Not_TMED_Event | 2713
MAYAGÃœEZ | 2023-04-10 12:42 | 2023-04-10 14:20 | 80 | 1:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23041000105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 98 | 2023-04-10 | 7840 | keep | 0 | Apr | 2023 | 0.0053398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-04-10 12:54 | 2023-04-10 14:16 | 10 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES EN LA SECUNDARIA Y BAJANTES SECUNDARIO | C23041000116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-04-10 | 820 | keep | 0 | Apr | 2023 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-10 13:04 | 2023-04-10 14:49 | 152 | 1:45 | P | DESGANCHE | DESGANCHE 1 X 40 EN C/L | S23041000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-04-10 | 15960 | keep | 0 | Apr | 2023 | 0.01087 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
HUMACAO | 2023-04-10 13:09 | 2023-04-10 13:11 | 327 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL CARGA X 2603-06 | C23041000260 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-10 | 654 | keep | 0 | Apr | 2023 | 0.00044544 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
AGUADILLA | 2023-04-10 13:15 | 2023-04-11 10:10 | 5 | 20:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR POR LLUVIA Y VIENTO RELACINADO AL EVENTO M23041000337 | M23041100050 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1255 | 2023-04-10 | 6275 | keep | 0 | Apr | 2023 | 0.0042739 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-10 13:25 | 2023-04-10 16:30 | 30 | 3:05 | P | DESGANCHE | 1 X 25 EN XMR Y 1 X 50 EN C/L DESGANCHE | B23041000123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-04-10 | 5550 | keep | 0 | Apr | 2023 | 0.0037801 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-10 13:25 | 2023-04-10 16:20 | 1 | 2:55 | P | ANIMAL | 1 X 50 EN SU-05 SE RETIRO RATA CARGA 1718-03 | B23041000117 | New_Event | Animals | Include | Include | Wildlife | 175 | 2023-04-10 | 175 | keep | 0 | Apr | 2023 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-10 13:25 | 2023-04-10 19:18 | 24 | 5:53 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23041000268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 353 | 2023-04-10 | 8472 | keep | 0 | Apr | 2023 | 0.0057702 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2023-04-10 13:25 | 2023-04-10 17:40 | 1 | 4:15 | P | DESGANCHE | 1 X 8 EN RISER SE RETIRO RAMAS SOBRE LAS LINEAS | M23041000114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2023-04-10 | 255 | keep | 0 | Apr | 2023 | 0.00017368 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-10 13:27 | 2023-04-10 14:10 | 7 | 0:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO | C23041000270 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 43 | 2023-04-10 | 301 | keep | 0 | Apr | 2023 | 0.00020501 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-04-10 13:33 | 2023-04-10 15:30 | 3 | 1:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041000118 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 117 | 2023-04-10 | 351 | keep | 0 | Apr | 2023 | 0.00023906 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-04-10 13:34 | 2023-04-10 13:37 | 718 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 90% DEL 1901-05 SE PROBO POR CONTROL QUEDO EN SERVICIO | S23041000329 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-10 | 2154 | keep | 0 | Apr | 2023 | 0.0014671 | 0.00048903 | Momentary | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2023-04-10 13:34 | 2023-04-10 13:37 | 558 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO 90% POR 1330-01 SE PROBO POR CONTROL QUEDO EN SERVICIO SE TRATA DE CAMBIAR DISTRITO A GUAYNABO Y DICE NO EXISTE | S23041000329 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-10 | 1674 | keep | 0 | Apr | 2023 | 0.0011402 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
SAN JUAN | 2023-04-10 13:36 | 2023-04-10 15:00 | 200 | 1:24 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA DESGANCHE | S23041000331 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-04-10 | 16800 | keep | 0 | Apr | 2023 | 0.011442 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-04-10 13:46 | 2023-04-11 14:10 | 1 | 24:24 | P | TERMINACION SOTERRADA AVERIADA | SE REEMPLAZO CAJAS SECAS EN MH-2 Y SE REEMPLAZO TERMINACION QUEMADA DE TIPO PISTOLA | C23041000275 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1464 | 2023-04-10 | 1464 | keep | 0 | Apr | 2023 | 0.00099712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-10 13:48 | 2023-04-10 16:16 | 139 | 2:28 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | R23041000141 | New_Event | Primary Wire Break | Include | Include | Equipment | 148 | 2023-04-10 | 20572 | keep | 0 | Apr | 2023 | 0.014011 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
CAGUAS | 2023-04-10 13:50 | 2023-04-10 15:55 | 1 | 2:05 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE EVENTO ES DE CAGUAS | C23041000276 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-04-10 | 125 | keep | 0 | Apr | 2023 | 8.5137e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-10 14:05 | 2023-04-10 14:14 | 4 | 0:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | B23041000126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 9 | 2023-04-10 | 36 | keep | 0 | Apr | 2023 | 2.4519e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-04-10 14:13 | 2023-04-10 16:35 | 80 | 2:22 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23041000283 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-04-10 | 11360 | keep | 0 | Apr | 2023 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-04-10 14:21 | 2023-04-10 16:00 | 17 | 1:39 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L SE REMPLAZO PARARAYO EN XMR | P23041000226 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 99 | 2023-04-10 | 1683 | keep | 0 | Apr | 2023 | 0.0011463 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2023-04-10 14:21 | 2023-04-10 15:54 | 9 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23041000286 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-04-10 | 837 | keep | 0 | Apr | 2023 | 0.00057008 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-04-10 14:31 | 2023-04-10 15:42 | 1 | 1:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO PORTAFUSIBLE Y 1 X 30 EN C/L | C23041000315 | New_Event | Cutout Failure | Include | Include | Equipment | 71 | 2023-04-10 | 71 | keep | 0 | Apr | 2023 | 4.8358e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-10 14:37 | 2023-04-10 14:39 | 1356 | 0:02 | T | OTRAS CAUSAS | SE ABRE INTERRUPTOR PARA ABRIR V.S.28 PARA INSPECIONAR MH YA QUE HABIA ESCAPE DE GAS | S23041000366 | New_Event | Other Causes | Include | Include | Other | 2 | 2023-04-10 | 2712 | keep | 0 | Apr | 2023 | 0.0018471 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
SAN JUAN | 2023-04-10 14:39 | 2023-04-10 18:39 | 20 | 4:00 | P | OTRAS CAUSAS | SE INSPECCIONO V.S.26 Y NO HUBO AVERIA Y SE VOLVIO A ENERGIZAR TRAMO V.S. 17 A V.S.26 | S23041000366 | 1st_after_momentary | Other Causes | Include | Include | Other | 240 | 2023-04-10 | 4800 | keep | 0 | Apr | 2023 | 0.0032693 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-10 14:43 | 2023-04-10 17:24 | 1 | 2:41 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR Y 1 X 65 3N C/L EVENTO TRANSFERIDO DE CAGUAS | C23041000293 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 161 | 2023-04-10 | 161 | keep | 0 | Apr | 2023 | 0.00010966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-10 14:50 | 2023-04-10 16:55 | 91 | 2:05 | P | ANIMAL | 1 X 30 Y 1 X 50 CRUCE POR AVE | R23041000155 | New_Event | Animals | Include | Include | Wildlife | 125 | 2023-04-10 | 11375 | keep | 0 | Apr | 2023 | 0.0077475 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
BARRANQUITAS | 2023-04-10 14:52 | 2023-04-10 22:05 | 50 | 7:13 | P | DESGANCHE | 1 X 40 EN C/L SE REQUIERE DESGANCHE MASIVO | C23041000298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 433 | 2023-04-10 | 21650 | keep | 0 | Apr | 2023 | 0.014746 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-10 14:52 | 2023-04-10 19:30 | 270 | 4:38 | P | CONDUCTOR ROTO O ABIERTO | SE DEJO SECCIONALIZO CON PUENTE ABIERTO ANTES Y DESPUES CONDUCTOR EN EL SUELO SE RETIRO PELIGRO. QUEDAN 200 CLIENTES FUERA. | C23041000297 | New_Event | Primary Wire Break | Include | Include | Equipment | 278 | 2023-04-10 | 75060 | keep | 0 | Apr | 2023 | 0.051123 | 0.0001839 | Sustained | FALSE | FALSE | Not_TMED_Event | 270
VEGA BAJA | 2023-04-10 15:01 | 2023-04-10 17:28 | 50 | 2:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23041000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-04-10 | 7350 | keep | 0 | Apr | 2023 | 0.0050061 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-10 15:14 | 2023-04-10 15:50 | 4 | 0:36 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE REPARO SECUNDARIA A CAUSA DE CAMION IMPACTO LINEAS | C23041000308 | New_Event | Damage From Public | Include | Include | Public | 36 | 2023-04-10 | 144 | keep | 0 | Apr | 2023 | 9.8078e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-10 15:15 | 2023-04-10 15:59 | 6 | 0:44 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR PARA RELAIZAR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | S23040900203 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 44 | 2023-04-10 | 264 | keep | 0 | Apr | 2023 | 0.00017981 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-10 15:33 | 2023-04-10 19:32 | 75 | 3:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | A23041000118 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2023-04-10 | 17925 | keep | 0 | Apr | 2023 | 0.012209 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-04-10 15:47 | 2023-04-11 15:49 | 28 | 24:02 | P | DESGANCHE | 1X100 EN C/L 1X15 EN XMR DESGANCHE PRIMARIO | S23041000410 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1442 | 2023-04-10 | 40376 | keep | 0 | Apr | 2023 | 0.0275 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2023-04-10 16:08 | 2023-04-10 19:50 | 382 | 3:42 | S | ANIMAL | DISPARO DE LA SUBESTACION IGUANA CAUSO EL DISPARO | M23041000141 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-04-10 | 84804 | keep | 0 | Apr | 2023 | 0.05776 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-04-10 16:08 | 2023-04-10 19:50 | 39 | 3:42 | S | ANIMAL | DISPARO DE LA SUBESTACION IGUANA CAUSO EL DISPARO | M23041000141 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-04-10 | 8658 | keep | 0 | Apr | 2023 | 0.0058969 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2023-04-10 16:14 | 2023-04-10 18:13 | 1879 | 1:59 | T | ANIMAL | DISPARO DE BKR SE SECCIONALIZO AVERIA Y SE CERRO POR CONTROL | C23041000331 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-04-10 | 223601 | keep | 0 | Apr | 2023 | 0.15229 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
MAYAGÃœEZ | 2023-04-10 16:16 | 2023-04-10 16:17 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041000148 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 2067 | keep | 0 | Apr | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
CAGUAS | 2023-04-10 16:18 | 2023-04-10 17:04 | 8 | 0:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23041000337 | New_Event | Secondary Wire Break | Include | Include | Equipment | 46 | 2023-04-10 | 368 | keep | 0 | Apr | 2023 | 0.00025064 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-04-10 16:21 | 2023-04-10 18:21 | 174 | 2:00 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | R23041000168 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-04-10 | 20880 | keep | 0 | Apr | 2023 | 0.014221 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
SAN JUAN | 2023-04-10 16:23 | 2023-04-11 15:03 | 1 | 22:40 | P | PARARRAYOS DEFECTUOSO | 2 X 30 EN C/L SE RETIRO PARARRAYO AVERIADO | S23041000421 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1360 | 2023-04-10 | 1360 | keep | 0 | Apr | 2023 | 0.00092629 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-10 16:29 | 2023-04-10 19:45 | 30 | 3:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | A23041000138 | New_Event | Primary Wire Break | Include | Include | Equipment | 196 | 2023-04-10 | 5880 | keep | 0 | Apr | 2023 | 0.0040048 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-10 17:05 | 2023-04-10 18:10 | 50 | 1:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23041000144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2023-04-10 | 3250 | keep | 0 | Apr | 2023 | 0.0022136 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-10 17:28 | 2023-04-10 18:36 | 15 | 1:08 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR POR RAYOS | A23041000101 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 68 | 2023-04-10 | 1020 | keep | 0 | Apr | 2023 | 0.00069472 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-10 17:38 | 2023-04-10 18:18 | 4 | 0:40 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B23041000164 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 40 | 2023-04-10 | 160 | keep | 0 | Apr | 2023 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-04-10 17:44 | 2023-04-10 18:37 | 990 | 0:53 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR SE PATRULLO Y NO SE ENCONTRO CAUSA SE HIZO PRUEBA Y QUEDO EN SERVICIO | M23041000199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2023-04-10 | 52470 | keep | 0 | Apr | 2023 | 0.035737 | 0.00067428 | Sustained | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2023-04-10 17:46 | 2023-04-10 21:45 | 8 | 3:59 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M23041000200 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 239 | 2023-04-10 | 1912 | keep | 0 | Apr | 2023 | 0.0013023 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-10 17:47 | 2023-04-10 18:22 | 25 | 0:35 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L POR PARARRAYOS | B23041000173 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 35 | 2023-04-10 | 875 | keep | 0 | Apr | 2023 | 0.00059596 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-10 17:50 | 2023-04-10 18:10 | 12 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S23040900325 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-04-10 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-10 18:13 | 2023-04-10 18:14 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 5252 | keep | 0 | Apr | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
CAGUAS | 2023-04-10 18:13 | 2023-04-10 20:15 | 500 | 2:02 | P | ANIMAL | SE REEMPLAZO MACHETE DEFECTUOSO POR CULEBRA CRUZADA EN MACHETE | C23041000331 | Partial_restoration | Animals | Include | Include | Wildlife | 122 | 2023-04-10 | 61000 | keep | 0 | Apr | 2023 | 0.041547 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-10 18:22 | 2023-04-10 18:25 | 3438 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CEERO POR SCADA | B2304100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-10 | 10314 | keep | 0 | Apr | 2023 | 0.0070248 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-04-10 18:25 | 2023-04-10 19:14 | 25 | 0:49 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L POR PARARRAYOS | B23041000173 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 49 | 2023-04-10 | 1225 | keep | 0 | Apr | 2023 | 0.00083434 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-10 18:32 | 2023-04-11 10:32 | 77 | 16:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23041000479 | New_Event | Vegetation Contact | Include | Include | Vegetation | 960 | 2023-04-10 | 73920 | keep | 0 | Apr | 2023 | 0.050347 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
VEGA BAJA | 2023-04-10 18:36 | 2023-04-11 12:10 | 6 | 17:34 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15KVA X 37KVA | A23041000101 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1054 | 2023-04-10 | 6324 | keep | 0 | Apr | 2023 | 0.0043072 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-10 18:43 | 2023-04-10 20:30 | 8 | 1:47 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23041000237 | New_Event | Primary Wire Break | Include | Include | Equipment | 107 | 2023-04-10 | 856 | keep | 0 | Apr | 2023 | 0.00058302 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-10 18:46 | 2023-04-10 21:04 | 60 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L SE REPORTA MAL TIEMPO LLUVIA | S23041000487 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2023-04-10 | 8280 | keep | 0 | Apr | 2023 | 0.0056395 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-04-10 18:51 | 2023-04-10 20:54 | 60 | 2:03 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23041000245 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-04-10 | 7380 | keep | 0 | Apr | 2023 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-10 19:03 | 2023-04-10 20:00 | 2435 | 0:57 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 57 | 2023-04-10 | 138795 | keep | 0 | Apr | 2023 | 0.094533 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-10 19:03 | 2023-04-10 20:00 | 2956 | 0:57 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE CERRO POR SCADA BY-230408-02 LLEVA LA CARGA DEL 1907-05 | S23040800164 | New_Event | Feeder Load Transferred | Include | Include | Other | 57 | 2023-04-10 | 168492 | keep | 0 | Apr | 2023 | 0.11476 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-04-10 19:07 | 2023-04-10 19:08 | 172 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2304100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 172 | keep | 0 | Apr | 2023 | 0.00011715 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
AGUADILLA | 2023-04-10 19:17 | 2023-04-11 13:37 | 8 | 18:20 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYO RELACIONADO AL EVENTO A23041000170 | A23041100090 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1100 | 2023-04-10 | 8800 | keep | 0 | Apr | 2023 | 0.0059936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-10 19:24 | 2023-04-11 05:27 | 50 | 10:03 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23041000193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 603 | 2023-04-10 | 30150 | keep | 0 | Apr | 2023 | 0.020535 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-10 19:26 | 2023-04-10 23:17 | 500 | 3:51 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23041000194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-04-10 | 115500 | keep | 0 | Apr | 2023 | 0.078667 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2023-04-10 19:28 | 2023-04-11 06:58 | 18 | 11:30 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REMOVIO ENREDADERA | P23041000279 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 690 | 2023-04-10 | 12420 | keep | 0 | Apr | 2023 | 0.0084592 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-04-10 19:30 | 2023-04-11 18:20 | 200 | 22:50 | P | CONDUCTOR ROTO O ABIERTO | SE RELOCALIZO LINEA PRIMARIA Y SE ENERGIZO | C23041000297 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1370 | 2023-04-10 | 274000 | keep | 0 | Apr | 2023 | 0.18662 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-10 19:32 | 2023-04-10 20:37 | 150 | 1:05 | P | MAL TIEMPO/RAYOS | 1 X 50 EN RISER POR RAYOS | A23041000173 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 65 | 2023-04-10 | 9750 | keep | 0 | Apr | 2023 | 0.0066407 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-04-10 19:38 | 2023-04-10 23:00 | 75 | 3:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | A23041000175 | New_Event | Primary Wire Break | Include | Include | Equipment | 202 | 2023-04-10 | 15150 | keep | 0 | Apr | 2023 | 0.010319 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-04-10 19:39 | 2023-04-11 07:26 | 50 | 11:47 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23041000437 | New_Event | Animals | Include | Include | Wildlife | 707 | 2023-04-10 | 35350 | keep | 0 | Apr | 2023 | 0.024077 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-10 19:42 | 2023-04-11 08:30 | 40 | 12:48 | P | DESGANCHE | 2 X 100 EN C/L Y 2 X 30 EN RISER SE DESGANCHO | S23041000621 | New_Event | Vegetation Contact | Include | Include | Vegetation | 768 | 2023-04-10 | 30720 | keep | 0 | Apr | 2023 | 0.020923 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-10 19:56 | 2023-04-11 00:16 | 102 | 4:20 | P | NO SE REPORTO CAUSA | 2 X 100 EN RISER NO CAUSA | B23041000201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2023-04-10 | 26520 | keep | 0 | Apr | 2023 | 0.018063 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
BARRANQUITAS | 2023-04-10 19:59 | 2023-04-10 21:29 | 30 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23041000440 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-04-10 | 2700 | keep | 0 | Apr | 2023 | 0.001839 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-10 20:00 | 2023-04-10 20:41 | 244 | 0:41 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA, SE REEMPLAZO VS-05 AVERIADO BY-230408-02 CARGA POR EL 1909-08 | S23040800164 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 41 | 2023-04-10 | 10004 | keep | 0 | Apr | 2023 | 0.0068137 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-10 20:02 | 2023-04-10 20:55 | 12 | 0:53 | P | ANIMAL | 1 X 30 EN C/L AVE CRUZO LINEAS | R23041000225 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-04-10 | 636 | keep | 0 | Apr | 2023 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-04-10 20:03 | 2023-04-10 22:19 | 25 | 2:16 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23041000226 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-04-10 | 3400 | keep | 0 | Apr | 2023 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-04-10 20:10 | 2023-04-10 21:43 | 50 | 1:33 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23041000297 | New_Event | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-04-10 | 4650 | keep | 0 | Apr | 2023 | 0.0031671 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-04-10 20:16 | 2023-04-11 11:40 | 20 | 15:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A23041000182 | New_Event | Cutout Failure | Include | Include | Equipment | 924 | 2023-04-10 | 18480 | keep | 0 | Apr | 2023 | 0.012587 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-10 20:19 | 2023-04-10 22:08 | 400 | 1:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041000286 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 109 | 2023-04-10 | 43600 | keep | 0 | Apr | 2023 | 0.029696 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
YAUCO | 2023-04-10 20:28 | 2023-04-10 20:29 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23041000297 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 179 | keep | 0 | Apr | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
CANOVANAS | 2023-04-10 20:35 | 2023-04-11 10:12 | 8 | 13:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | C23041000237 | New_Event | Cutout Failure | Include | Include | Equipment | 817 | 2023-04-10 | 6536 | keep | 0 | Apr | 2023 | 0.0044516 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-10 20:57 | 2023-04-11 11:30 | 2 | 14:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23041000715 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 873 | 2023-04-10 | 1746 | keep | 0 | Apr | 2023 | 0.0011892 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-10 21:03 | 2023-04-11 14:16 | 109 | 17:13 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO ROTO PEGADO A POSTE. QUEMO PARTE DE ARRIBA DE POSTE. POSTE A PUNTO DE PARTIRSE | S23041000716 | New_Event | Primary Wire Break | Include | Include | Equipment | 1033 | 2023-04-10 | 112597 | keep | 0 | Apr | 2023 | 0.076689 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
YAUCO | 2023-04-10 21:22 | 2023-04-11 08:30 | 91 | 11:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE BRISA | M23041000313 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 668 | 2023-04-10 | 60788 | keep | 0 | Apr | 2023 | 0.041402 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
BAYAMON | 2023-04-10 21:24 | 2023-04-11 04:18 | 76 | 6:54 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23041000719 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2023-04-10 | 31464 | keep | 0 | Apr | 2023 | 0.02143 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
HUMACAO | 2023-04-10 21:36 | 2023-04-11 09:19 | 100 | 11:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA CRUCE CON GLOBO | C23041000445 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 703 | 2023-04-10 | 70300 | keep | 0 | Apr | 2023 | 0.047881 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-10 21:39 | 2023-04-10 21:40 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 75% DE LA CARGA DEL 1718-03 | B2304100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-04-10 21:39 | 2023-04-10 21:40 | 1953 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 75% DE LA CARGA POR EL 1713-04 | B2304100000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-10 | 1953 | keep | 0 | Apr | 2023 | 0.0013302 | 0.0013302 | Momentary | FALSE | FALSE | Not_TMED_Event | 1953
VEGA BAJA | 2023-04-10 21:41 | 2023-04-11 07:30 | 32 | 9:49 | P | ANIMAL | 1 X 30 EN C/L SE RETIRO CULEBRA | B23041000205 | New_Event | Animals | Include | Include | Wildlife | 589 | 2023-04-10 | 18848 | keep | 0 | Apr | 2023 | 0.012837 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
ARECIBO | 2023-04-10 21:49 | 2023-04-11 09:10 | 7 | 11:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOPOR LLUVIAS | A23041000187 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 681 | 2023-04-10 | 4767 | keep | 0 | Apr | 2023 | 0.0032468 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-04-10 21:55 | 2023-04-11 09:00 | 5 | 11:05 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR IGUANA CRUZO FASE A TIERRA | M23041000324 | New_Event | Animals | Include | Include | Wildlife | 665 | 2023-04-10 | 3325 | keep | 0 | Apr | 2023 | 0.0022646 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-10 23:00 | 2023-04-11 07:32 | 70 | 8:32 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | S23041000730 | New_Event | Vegetation Contact | Include | Include | Vegetation | 512 | 2023-04-10 | 35840 | keep | 0 | Apr | 2023 | 0.02441 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-04-10 23:33 | 2023-04-10 23:42 | 250 | 0:09 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | AL TRATAR DE NORMALIZAR LA CARGA DE BKR SECUNDARIO DE LA PORTATIL#8 SE DISPARA INPIDIENDO NORMALIZAR SE CERRO N/O CON 1401-08 | S2304100000X | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 9 | 2023-04-10 | 2250 | keep | 0 | Apr | 2023 | 0.0015325 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-04-10 23:33 | 2023-04-10 23:42 | 1290 | 0:09 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | AL TRATAR DE NORMALIZAR LA CARGA DE BKR SECUNDARIO DE LA PORTATIL#8 SE DISPARA INPIDIENDO NORMALIZAR SE CERRO N/O CON 1401-08 | S2304100000X | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 9 | 2023-04-10 | 11610 | keep | 0 | Apr | 2023 | 0.0079075 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2023-04-10 23:51 | 2023-04-10 23:52 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-10 | 5252 | keep | 0 | Apr | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
BAYAMON | 2023-04-11 01:18 | 2023-04-11 02:41 | 50 | 1:23 | P | DESGANCHE | 1 X 50 EN C/L SE LEVANTO CONDUCTOR DESGANCHE | B23041100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-04-11 | 4150 | keep | 0 | Apr | 2023 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-11 03:59 | 2023-04-11 08:44 | 80 | 4:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | B23041100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 285 | 2023-04-11 | 22800 | keep | 0 | Apr | 2023 | 0.015529 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-11 04:30 | 2023-04-11 10:40 | 1 | 6:10 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN C/L SE ASEGURO BAJANTE DE LINEA A CAJA | B23041100015 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 370 | 2023-04-11 | 370 | keep | 0 | Apr | 2023 | 0.00025201 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-11 04:36 | 2023-04-11 04:37 | 3387 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | B2304110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-11 | 3387 | keep | 0 | Apr | 2023 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
ARECIBO | 2023-04-11 05:00 | 2023-04-11 10:00 | 60 | 5:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CORTE DE LINEA | A23041100004 | New_Event | Primary Wire Break | Include | Include | Equipment | 300 | 2023-04-11 | 18000 | keep | 0 | Apr | 2023 | 0.01226 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-04-11 05:46 | 2023-04-11 07:30 | 105 | 1:44 | P | ANIMAL | 2 X 80 EN SU-C PAJARO CRUZO FASE | P23041100053 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-04-11 | 10920 | keep | 0 | Apr | 2023 | 0.0074376 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2023-04-11 07:01 | 2023-04-11 07:02 | 73 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23041100020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-11 | 73 | keep | 0 | Apr | 2023 | 4.972e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2023-04-11 07:12 | 2023-04-11 11:15 | 10 | 4:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23041100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-04-11 | 2430 | keep | 0 | Apr | 2023 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-11 07:18 | 2023-04-11 12:25 | 35 | 5:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA Y 1 8 EN TRANSFORMADOR POR MAL TIEMPO | A23041100012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 307 | 2023-04-11 | 10745 | keep | 0 | Apr | 2023 | 0.0073184 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-04-11 07:20 | 2023-04-11 09:08 | 125 | 1:48 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R23041100005 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-04-11 | 13500 | keep | 0 | Apr | 2023 | 0.0091948 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-04-11 07:30 | 2023-04-11 08:04 | 1 | 0:34 | P | ANIMAL | 2 X 15 EN MONTURA SE RETIRO AVE | B23041100051 | New_Event | Animals | Include | Include | Wildlife | 34 | 2023-04-11 | 34 | keep | 0 | Apr | 2023 | 2.3157e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-11 07:31 | 2023-04-11 09:43 | 1 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR SE REPORTA MAL TIEMPO LLUVIA | B23041100046 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-04-11 | 132 | keep | 0 | Apr | 2023 | 8.9905e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-11 07:39 | 2023-04-11 11:44 | 23 | 4:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | C23041100011 | New_Event | Cutout Failure | Include | Include | Equipment | 245 | 2023-04-11 | 5635 | keep | 0 | Apr | 2023 | 0.003838 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BARRANQUITAS | 2023-04-11 07:47 | 2023-04-11 07:51 | 2725 | 0:04 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA ABRIR DESCONECTIVO SOLDADO PARA REALIZAR D2023-3258 REV. 2 YA QUE NO ABRIA CON LOAD BOOSTER Y VARETA. | C23041100016 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2023-04-11 | 10900 | keep | 0 | Apr | 2023 | 0.0074239 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
SAN JUAN | 2023-04-11 07:51 | 2023-04-12 20:53 | 25 | 37:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5 X 37.5KVA | S23041100026 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2222 | 2023-04-11 | 55550 | keep | 0 | Apr | 2023 | 0.037835 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-11 07:55 | 2023-04-11 10:05 | 60 | 2:10 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA POR AVE | A23041100017 | New_Event | Animals | Include | Include | Wildlife | 130 | 2023-04-11 | 7800 | keep | 0 | Apr | 2023 | 0.0053125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-04-11 07:56 | 2023-04-11 07:57 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-11 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2023-04-11 08:01 | 2023-04-11 09:23 | 11 | 1:22 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R23041100012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-04-11 | 902 | keep | 0 | Apr | 2023 | 0.00061435 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-04-11 08:08 | 2023-04-11 09:50 | 120 | 1:42 | P | ANIMAL | 1 X 65 Y 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C23041100026 | New_Event | Animals | Include | Include | Wildlife | 102 | 2023-04-11 | 12240 | keep | 0 | Apr | 2023 | 0.0083366 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2023-04-11 08:21 | 2023-04-11 13:13 | 100 | 4:52 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C23041100032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 292 | 2023-04-11 | 29200 | keep | 0 | Apr | 2023 | 0.019888 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-11 08:27 | 2023-04-11 14:58 | 1 | 6:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 EN RISER POR LLUVIA | S23041100029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 391 | 2023-04-11 | 391 | keep | 0 | Apr | 2023 | 0.00026631 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-11 08:31 | 2023-04-11 12:34 | 80 | 4:03 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23041100078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 243 | 2023-04-11 | 19440 | keep | 0 | Apr | 2023 | 0.01324 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-11 08:32 | 2023-04-11 08:34 | 2179 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | C2304110000X | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-04-11 | 4358 | keep | 0 | Apr | 2023 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2023-04-11 08:34 | 2023-04-11 09:08 | 500 | 0:34 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE PRIMARIO DE LINEA @ CAJA ENTRADA HACIA EL C/L MEDIANTE G.O.I. SJ-230411-50 | R23041100051 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 34 | 2023-04-11 | 17000 | keep | 0 | Apr | 2023 | 0.011579 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2023-04-11 08:48 | 2023-04-11 10:17 | 65 | 1:29 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P23041100078 | New_Event | Animals | Include | Include | Wildlife | 89 | 2023-04-11 | 5785 | keep | 0 | Apr | 2023 | 0.0039401 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2023-04-11 09:08 | 2023-04-11 09:11 | 2179 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO QUEDO EN SERVICIO | R23041100021 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-11 | 6537 | keep | 0 | Apr | 2023 | 0.0044523 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-11 09:11 | 2023-04-11 12:02 | 500 | 2:51 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE PRIMARIO DE LINEA @ CAJA ENTRADA HACIA EL C/L MEDIANTE G.O.I. SJ-230411-50 | R23041100051 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 171 | 2023-04-11 | 85500 | keep | 0 | Apr | 2023 | 0.058234 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2023-04-11 09:26 | 2023-04-11 12:18 | 1 | 2:52 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C23041100050 | New_Event | Animals | Include | Include | Wildlife | 172 | 2023-04-11 | 172 | keep | 0 | Apr | 2023 | 0.00011715 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-11 09:35 | 2023-04-11 09:55 | 1 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA | S23041000067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-04-11 | 20 | keep | 0 | Apr | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-11 09:35 | 2023-04-11 10:43 | 40 | 1:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 30 EN RISER POR MAL TIEMPO | A23041100045 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 68 | 2023-04-11 | 2720 | keep | 0 | Apr | 2023 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-11 09:43 | 2023-04-11 15:30 | 3 | 5:47 | P | DESGANCHE | 1 X 3O EN C/L SE DESGANCHO | B23041100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2023-04-11 | 1041 | keep | 0 | Apr | 2023 | 0.00070902 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-11 09:52 | 2023-04-11 13:17 | 130 | 3:25 | P | DESGANCHE | 1 X 50, 1 X 40 Y 1 X 30 EN CORTES DE LINEA | R23041100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-04-11 | 26650 | keep | 0 | Apr | 2023 | 0.018151 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BAYAMON | 2023-04-11 09:55 | 2023-04-11 15:45 | 1 | 5:50 | P | CAUSAS EXTERNAS | RELOCALIZO XMR POR POSTE IMPACTADO | B23041100111 | New_Event | Damage From Public | Include | Include | Public | 350 | 2023-04-11 | 350 | keep | 0 | Apr | 2023 | 0.00023838 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-11 09:56 | 2023-04-11 13:30 | 5 | 3:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO MONTURA DE TRANSFORMADOR Y SE REPARO CONEXIONES SECUNDARIAS | A23041100052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 214 | 2023-04-11 | 1070 | keep | 0 | Apr | 2023 | 0.00072877 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-04-11 10:00 | 2023-04-11 10:01 | 1047 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M23041100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-11 | 1047 | keep | 0 | Apr | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
SAN JUAN | 2023-04-11 10:03 | 2023-04-11 13:34 | 50 | 3:31 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23041100048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 211 | 2023-04-11 | 10550 | keep | 0 | Apr | 2023 | 0.0071856 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-04-11 10:06 | 2023-04-11 16:23 | 1 | 6:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN CAJA DE XMR | P23041100088 | New_Event | Primary Wire Break | Include | Include | Equipment | 377 | 2023-04-11 | 377 | keep | 0 | Apr | 2023 | 0.00025677 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-11 10:07 | 2023-04-11 15:52 | 150 | 5:45 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23041100052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2023-04-11 | 51750 | keep | 0 | Apr | 2023 | 0.035247 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-04-11 10:08 | 2023-04-11 10:09 | 1047 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | M23041100055 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-11 | 1047 | keep | 0 | Apr | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
SAN JUAN | 2023-04-11 10:15 | 2023-04-11 11:30 | 20 | 1:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR Y SE REPASO BAJANTE SECUNDARIO Y DESGANCHE SECUNDARIO | S23041000032 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 75 | 2023-04-11 | 1500 | keep | 0 | Apr | 2023 | 0.0010216 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-11 10:18 | 2023-04-11 10:19 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23041100060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-11 | 1307 | keep | 0 | Apr | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
AGUADILLA | 2023-04-11 10:21 | 2023-04-11 14:25 | 30 | 4:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23041100059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2023-04-11 | 7320 | keep | 0 | Apr | 2023 | 0.0049856 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-11 10:25 | 2023-04-11 15:05 | 6 | 4:40 | P | ANIMAL | 1 X 15 EN XMR SE RETIRO AVE | B23041100121 | New_Event | Animals | Include | Include | Wildlife | 280 | 2023-04-11 | 1680 | keep | 0 | Apr | 2023 | 0.0011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-04-11 10:25 | 2023-04-11 16:35 | 2 | 6:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23041100061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 370 | 2023-04-11 | 740 | keep | 0 | Apr | 2023 | 0.00050401 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-04-11 10:34 | 2023-04-11 12:06 | 50 | 1:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23041100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2023-04-11 | 4600 | keep | 0 | Apr | 2023 | 0.003133 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-11 10:38 | 2023-04-11 13:06 | 25 | 2:28 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M23041100067 | New_Event | Primary Wire Break | Include | Include | Equipment | 148 | 2023-04-11 | 3700 | keep | 0 | Apr | 2023 | 0.0025201 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-11 10:45 | 2023-04-11 11:07 | 1 | 0:22 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23041100123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-04-11 | 22 | keep | 0 | Apr | 2023 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-11 10:46 | 2023-04-11 14:04 | 85 | 3:18 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23041100067 | New_Event | Animals | Include | Include | Wildlife | 198 | 2023-04-11 | 16830 | keep | 0 | Apr | 2023 | 0.011463 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2023-04-11 10:49 | 2023-04-11 16:08 | 20 | 5:19 | P | ANIMAL | 2 X 65 EN RISER 1 X 10 EN SU-6 CULEBRA CRUZADA | B23041100124 | New_Event | Animals | Include | Include | Wildlife | 319 | 2023-04-11 | 6380 | keep | 0 | Apr | 2023 | 0.0043454 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-11 10:51 | 2023-04-11 13:23 | 45 | 2:32 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | B23041100127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-04-11 | 6840 | keep | 0 | Apr | 2023 | 0.0046587 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-04-11 10:57 | 2023-04-11 11:49 | 3 | 0:52 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | S23041100056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 52 | 2023-04-11 | 156 | keep | 0 | Apr | 2023 | 0.00010625 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-04-11 11:00 | 2023-04-11 12:34 | 1047 | 1:34 | T | DESGANCHE | SE RETIRO RAMA CAIDA SOBRE EL TRONCAL DEL ALIMENTADOR Y SE CERRO EL INTERRUPTOR | M23041100078 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-04-11 | 98418 | keep | 0 | Apr | 2023 | 0.067032 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
BAYAMON | 2023-04-11 11:10 | 2023-04-11 11:29 | 1 | 0:19 | P | ANIMAL | 1 X 15 EN XMR SE RETIRO AVE | B23041100137 | New_Event | Animals | Include | Include | Wildlife | 19 | 2023-04-11 | 19 | keep | 0 | Apr | 2023 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-11 11:12 | 2023-04-11 11:13 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041100103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-11 | 1746 | keep | 0 | Apr | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2023-04-11 11:25 | 2023-04-11 12:31 | 1 | 1:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN SU-3 SE REMPLAZO PORTAFUSIBLE | B23041100141 | New_Event | Cutout Failure | Include | Include | Equipment | 66 | 2023-04-11 | 66 | keep | 0 | Apr | 2023 | 4.4952e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-11 11:42 | 2023-04-11 13:15 | 12 | 1:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARRON CONECCIONES EN LINEA SECUNDARIA | P23041100113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 93 | 2023-04-11 | 1116 | keep | 0 | Apr | 2023 | 0.0007601 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-11 11:45 | 2023-04-11 12:15 | 8 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR Y SE REPARO PUENTE DE LINEA A CAJA TRANSFORMADOR CLIENTES ESTABAN EN FASE FUERA | S23041000462 | New_Event | Primary Wire Break | Include | Include | Equipment | 30 | 2023-04-11 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-11 11:50 | 2023-04-11 11:52 | 250 | 0:02 | P | ALIMENTADOR AMARRADO | SE ABRIO N/O CONTRA 1401-8 Y SE ENERGIZO A TRAVEZ 1348-00 LLEVA CARGA 1348-8 Y 1348-06 20% | S23041100000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-11 | 500 | keep | 0 | Apr | 2023 | 0.00034055 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-04-11 11:50 | 2023-04-11 11:52 | 1290 | 0:02 | S | DESCONECTIVO DEFECTUOSO | SE ABRIO N/O CONTRA 1401-8 Y SE ENERGIZO ATRAVEZ 1348-00 LLEVA CARGA 1348-8 Y 1348-06 20% | S23041100000 | New_Event | Switch Failure | Include | Include | Equipment | 2 | 2023-04-11 | 2580 | keep | 0 | Apr | 2023 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-04-11 11:50 | 2023-04-11 12:55 | 135 | 1:05 | T | ALIMENTADOR AMARRADO | DISPARO SE ENCONTRO GANG NO HIZO OPERACION COMPLETA EN SU-1 LAS VERDURAS ABRIO 2 FASES QUEDO 1 CERRADA, SE RETIRO CARGA PORTATIL 1348-00 PARA REALIZAR OPERACIONES 1401-08 | S23041100075 | New_Event | Feeder Load Transferred | Include | Include | Other | 65 | 2023-04-11 | 8775 | keep | 0 | Apr | 2023 | 0.0059766 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2023-04-11 11:52 | 2023-04-11 14:30 | 1 | 2:38 | P | TRANSFORMADOR AVERIADO | 1 X 8 EN XMR SE REEMPLAZO XMR DE 15KVA X 25 KVA EN MONTURA TRIFASICA | C23041100083 | New_Event | Service Transformer Failure | Include | Include | Equipment | 158 | 2023-04-11 | 158 | keep | 0 | Apr | 2023 | 0.00010761 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-11 11:54 | 2023-04-11 12:39 | 1 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARARON CONEXIONES EN RISER | P23041100098 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2023-04-11 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-11 12:02 | 2023-04-11 12:04 | 2179 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE CERRO POR CONTROL | R23041100050 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-04-11 | 4358 | keep | 0 | Apr | 2023 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2023-04-11 12:04 | 2023-04-11 12:07 | 500 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE PRIMARIO DE LINEA @ CAJA ENTRADA HACIA EL C/L MEDIANTE G.O.I. SJ-230411-50 | R23041100051 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-11 | 1500 | keep | 0 | Apr | 2023 | 0.0010216 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-04-11 12:07 | 2023-04-11 12:50 | 2179 | 0:43 | T | CONDUCTOR ROTO O ABIERTO | DISPARO BAJANTE SAFADO HACIA CORTE DE LINEA | R23041100050 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 43 | 2023-04-11 | 93697 | keep | 0 | Apr | 2023 | 0.063817 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
UTUADO | 2023-04-11 12:17 | 2023-04-11 15:10 | 1 | 2:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | A23041100079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 173 | 2023-04-11 | 173 | keep | 0 | Apr | 2023 | 0.00011783 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-11 12:23 | 2023-04-11 12:27 | 614 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S23041100085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-11 | 2456 | keep | 0 | Apr | 2023 | 0.0016728 | 0.00041819 | Momentary | FALSE | FALSE | Not_TMED_Event | 614
BAYAMON | 2023-04-11 12:27 | 2023-04-11 16:00 | 53 | 3:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 E C/L MAL TIEMPO | B23041100166 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 213 | 2023-04-11 | 11289 | keep | 0 | Apr | 2023 | 0.0076889 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2023-04-11 12:36 | 2023-04-11 12:45 | 250 | 0:09 | P | ALIMENTADOR AMARRADO | SE ABRE SECUNDARIO PORTATIL PARA PODER ABRIR MACHETE EN SU-1 LAS VERDURAS 1401-08 QUE NO HIZO OPERACION COMPLETA | S23041100000 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 9 | 2023-04-11 | 2250 | keep | 0 | Apr | 2023 | 0.0015325 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-04-11 12:36 | 2023-04-11 12:45 | 1290 | 0:09 | S | DESCONECTIVO DEFECTUOSO | SE ABRE SECUNDARIO PORTATIL PARA PODER ABRIR MACHETE EN SU-1 LAS VERDURAS 1401-08 QUE NO HIZO OPERACION COMPLETA | S23041100000 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 9 | 2023-04-11 | 11610 | keep | 0 | Apr | 2023 | 0.0079075 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2023-04-11 12:48 | 2023-04-12 13:56 | 1 | 25:08 | P | ANIMAL | 2 X 25 EN BANCO DE XMR AVE CRUZO LINEAS | B23041100081 | New_Event | Animals | Include | Include | Wildlife | 1508 | 2023-04-11 | 1508 | keep | 0 | Apr | 2023 | 0.0010271 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-11 12:50 | 2023-04-11 16:54 | 500 | 4:04 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE PRIMARIO DE LINEA @ CAJA ENTRADA HACIA EL C/L MEDIANTE G.O.I. SJ-230411-50 | R23041100051 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 244 | 2023-04-11 | 122000 | keep | 0 | Apr | 2023 | 0.083094 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-11 12:55 | 2023-04-11 16:10 | 25 | 3:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 Y 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | A23041100085 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2023-04-11 | 4875 | keep | 0 | Apr | 2023 | 0.0033203 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-11 13:06 | 2023-04-12 15:42 | 1 | 26:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO CAJA | B23041100086 | New_Event | Cutout Failure | Include | Include | Equipment | 1596 | 2023-04-11 | 1596 | keep | 0 | Apr | 2023 | 0.001087 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-11 13:15 | 2023-04-11 13:47 | 15 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE AJUSTARON BARRAS EN PEDESTAL | B23041100179 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-04-11 | 480 | keep | 0 | Apr | 2023 | 0.00032693 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-04-11 13:15 | 2023-04-11 18:13 | 50 | 4:58 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L SE REPORTAN DESCARGAS ELECTRICAS | B23041100180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 298 | 2023-04-11 | 14900 | keep | 0 | Apr | 2023 | 0.010148 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-11 13:16 | 2023-04-11 13:17 | 659 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE PARTE DE LA CARGA POR EL 2402-03 | R23041100077 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-11 | 659 | keep | 0 | Apr | 2023 | 0.00044884 | 0.00044884 | Momentary | FALSE | FALSE | Not_TMED_Event | 659
CANOVANAS | 2023-04-11 13:16 | 2023-04-11 13:17 | 4085 | 0:01 | T | DESGANCHE | RECIERRE LLEVANDO PARTE DE LA CARGA DEL 2302-03 | R23041100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-11 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-04-11 13:17 | 2023-04-11 15:09 | 30 | 1:52 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | R23041100083 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-04-11 | 3360 | keep | 0 | Apr | 2023 | 0.0022885 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-04-11 13:26 | 2023-04-11 16:23 | 3 | 2:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23041100092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2023-04-11 | 531 | keep | 0 | Apr | 2023 | 0.00036166 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-11 14:01 | 2023-04-11 14:02 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23041100088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-11 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-11 14:02 | 2023-04-11 15:24 | 1 | 1:22 | P | PARARRAYOS DEFECTUOSO | SE ABRIO EN BANCO DE XMRS DEL CLIENTE PARA ELIMINAR PARARRAYOS PRIVADO QUEMADO | R23041100089 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 82 | 2023-04-11 | 82 | keep | 0 | Apr | 2023 | 5.585e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-11 14:06 | 2023-04-11 14:07 | 154 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 15900 | M23041100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-11 | 154 | keep | 0 | Apr | 2023 | 0.00010489 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2023-04-11 14:06 | 2023-04-11 14:07 | 1261 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 15900 | M23041100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-11 | 1261 | keep | 0 | Apr | 2023 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2023-04-11 14:06 | 2023-04-11 14:07 | 3894 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 15900 | M23041100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-11 | 3894 | keep | 0 | Apr | 2023 | 0.0026522 | 0.0026522 | Momentary | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2023-04-11 14:06 | 2023-04-11 14:07 | 997 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 15900 | M23041100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-11 | 997 | keep | 0 | Apr | 2023 | 0.00067905 | 0.00067905 | Momentary | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-04-11 14:06 | 2023-04-11 14:07 | 1497 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 15900 | M23041100133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-11 | 1497 | keep | 0 | Apr | 2023 | 0.0010196 | 0.0010196 | Momentary | FALSE | FALSE | Not_TMED_Event | 1497
SAN JUAN | 2023-04-11 14:16 | 2023-04-11 14:20 | 8679 | 0:04 | P | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR 1206-03 PARA SECCIONALIZAR CONDUCTOR ROTO PEGADO A POSTE Y QUEMANDO. 1206-03 LLEVA 85% 1204-05 Y 16% DE SU CARGA TRANSFERIDA AL 1620-02 | S23041000716 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-04-11 | 34716 | keep | 0 | Apr | 2023 | 0.023645 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-04-11 14:16 | 2023-04-11 14:20 | 3472 | 0:04 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR 1206-03 PARA SECCIONALIZAR CONDUCTOR ROTO PEGADO A POSTE Y QUEMANDO. 1206-03 LLEVA 85% 1204-05 Y 16% DE SU CARGA TRANSFERIDA AL 1620-02 EN SERVICIO CARGA 1204-05 Y 10% 1206-03 | S23041000716 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 4 | 2023-04-11 | 13888 | keep | 0 | Apr | 2023 | 0.0094591 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-11 14:20 | 2023-04-11 16:50 | 2430 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR PARA REEMPLAZO DE POSTE QUEMADO POR CONDUCTOR PEGADO A POSTE. SE CERRO N/O CONTRA 1620-02. EN SERVICIO 80% DE LA CARGA 1206-03 | S23041000716 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 150 | 2023-04-11 | 364500 | keep | 0 | Apr | 2023 | 0.24826 | 0.0016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 2430
SAN JUAN | 2023-04-11 14:25 | 2023-04-11 15:12 | 11 | 0:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO Y CONECTOR EN NEUTRAL | S23041100011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 47 | 2023-04-11 | 517 | keep | 0 | Apr | 2023 | 0.00035213 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-04-11 14:28 | 2023-04-11 19:50 | 45 | 5:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23041100137 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 322 | 2023-04-11 | 14490 | keep | 0 | Apr | 2023 | 0.0098691 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-04-11 14:35 | 2023-04-11 17:14 | 1 | 2:39 | P | NO SE REPORTO CAUSA | 2 X 4O EN RISER Y 1 X 40 EN TRANSCLOSURE | B23041100208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2023-04-11 | 159 | keep | 0 | Apr | 2023 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-04-11 14:43 | 2023-04-11 19:55 | 400 | 5:12 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23041100106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-04-11 | 124800 | keep | 0 | Apr | 2023 | 0.085001 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-04-11 14:52 | 2023-04-11 18:00 | 25 | 3:08 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASES | M23041100147 | New_Event | Animals | Include | Include | Wildlife | 188 | 2023-04-11 | 4700 | keep | 0 | Apr | 2023 | 0.0032011 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-04-11 15:12 | 2023-04-11 19:47 | 5 | 4:35 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | P23041100152 | New_Event | Animals | Include | Include | Wildlife | 275 | 2023-04-11 | 1375 | keep | 0 | Apr | 2023 | 0.00093651 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-04-11 15:13 | 2023-04-12 13:45 | 15 | 22:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | POSTE PRIMARIO CON TENSOR PARTIDO Y VIRADO LA LINEA PRIMARIA ESTA CERCA DEL PISO SE VA HA ABRIR CORTE DE LINEA PRINCIPAL PARA PODER REPARAR LA AVERIA | A23041100117 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1352 | 2023-04-11 | 20280 | keep | 0 | Apr | 2023 | 0.013813 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-04-11 15:15 | 2023-04-11 15:54 | 20 | 0:39 | P | ANIMAL | 1X65 EN C/L CRUCE POR AVE | R23041100110 | New_Event | Animals | Include | Include | Wildlife | 39 | 2023-04-11 | 780 | keep | 0 | Apr | 2023 | 0.00053125 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-04-11 15:23 | 2023-04-11 16:50 | 12 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR NO SE REPORTO CAUSA | P23041100153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-04-11 | 1044 | keep | 0 | Apr | 2023 | 0.00071106 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-04-11 15:23 | 2023-04-11 20:09 | 250 | 4:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23041100123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2023-04-11 | 71500 | keep | 0 | Apr | 2023 | 0.048698 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
VEGA BAJA | 2023-04-11 15:28 | 2023-04-12 14:55 | 5 | 23:27 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5KVA | A23041100123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1407 | 2023-04-11 | 7035 | keep | 0 | Apr | 2023 | 0.0047915 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-04-11 15:37 | 2023-04-12 15:20 | 2 | 23:43 | P | ARBOL SOBRE LINEA | 2 X 25 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A23041100129 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1423 | 2023-04-11 | 2846 | keep | 0 | Apr | 2023 | 0.0019384 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-11 15:39 | 2023-04-11 15:48 | 820 | 0:09 | P | ERROR HUMANO | DISPARO INTERRUPTOR LLEVANDO CARGA 1119-04 Y 95% 1119-02 SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL PERSONAL DE SERVICE ELECTRIC TRABAJANDO PEGO CONDUCTOR A LA CRUCETA, TRABAJOS EN 1119-2 | S2304110000X | New_Event | Human Error | Include | Include | Other | 9 | 2023-04-11 | 7380 | keep | 0 | Apr | 2023 | 0.0050265 | 0.0005585 | Sustained | FALSE | FALSE | Not_TMED_Event | 820
SAN JUAN | 2023-04-11 15:39 | 2023-04-11 15:48 | 2720 | 0:09 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR LLEVANDO CARGA 1119-04 Y 95% 1119-02 SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL PERSONAL DE SERVICE ELECTRIC TRABAJANDO PEGO CONDUCTOR A LA CRUCETA | S2304110000X | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-04-11 | 24480 | keep | 0 | Apr | 2023 | 0.016673 | 0.0018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2023-04-11 15:45 | 2023-04-12 16:20 | 10 | 24:35 | P | CABLE SOTERRADO AVERIADO | 2X100 SU-2 @ PM (NO IDENTIFICADO) 1X80 SU-2 @ PM (NO IDENTIFICADO) Y SE REPARO TRAMO SOTERRADO AVERIADO EN PULLBOX ENTRE SU-2 @ PM (NO IDENTIFICADO) | S23041100218 | New_Event | UG Cable Fault | Include | Include | Equipment | 1475 | 2023-04-11 | 14750 | keep | 0 | Apr | 2023 | 0.010046 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-11 16:02 | 2023-04-11 16:03 | 1859 | 0:01 | T | ANIMAL | RECIERRE | B2304110000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-11 | 1859 | keep | 0 | Apr | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BARRANQUITAS | 2023-04-11 16:03 | 2023-04-11 18:49 | 15 | 2:46 | P | CAUSAS EXTERNAS | 1X40 EN C/L PERSONAL AJENO A LUMA REALIZANDO DESGANCHE | C23041100120 | New_Event | Damage From Public | Include | Include | Public | 166 | 2023-04-11 | 2490 | keep | 0 | Apr | 2023 | 0.0016959 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-11 16:03 | 2023-04-11 23:53 | 284 | 7:50 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | B23041100295 | 1st_after_momentary | Animals | Include | Include | Wildlife | 470 | 2023-04-11 | 133480 | keep | 0 | Apr | 2023 | 0.090913 | 0.00019343 | Sustained | FALSE | FALSE | Not_TMED_Event | 284
UTUADO | 2023-04-11 16:05 | 2023-04-11 21:30 | 40 | 5:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | A23041100141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2023-04-11 | 13000 | keep | 0 | Apr | 2023 | 0.0088542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-04-11 16:10 | 2023-04-11 17:10 | 10 | 1:00 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE | M23041100139 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 60 | 2023-04-11 | 600 | keep | 0 | Apr | 2023 | 0.00040866 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-11 16:13 | 2023-04-11 18:15 | 40 | 2:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23041100164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-04-11 | 4880 | keep | 0 | Apr | 2023 | 0.0033237 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-11 16:31 | 2023-04-11 18:57 | 10 | 2:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR CONEXONES EN SECUNDARIA | C23041100086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 146 | 2023-04-11 | 1460 | keep | 0 | Apr | 2023 | 0.0009944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-11 16:32 | 2023-04-11 19:38 | 19 | 3:06 | T | DESGANCHE | SE REALIZO DESGANCHE DE PALMA TRASPATIO CON VARETA Y SE CERRO POR CONTROL | S23041100301 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-04-11 | 3534 | keep | 0 | Apr | 2023 | 0.002407 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-04-11 16:33 | 2023-04-12 01:25 | 28 | 8:52 | P | DESGANCHE | 1 X 140 C/L DESGANCHE | B23041100232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2023-04-11 | 14896 | keep | 0 | Apr | 2023 | 0.010146 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
FAJARDO | 2023-04-11 16:41 | 2023-04-11 17:53 | 25 | 1:12 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | R23041100132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-04-11 | 1800 | keep | 0 | Apr | 2023 | 0.001226 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-11 16:50 | 2023-04-11 22:04 | 139 | 5:14 | P | CONDUCTOR ROTO O ABIERTO | SE RETIRO PARTE DE POSTE QUEMADA POR PUENTE PRIMARIO ABIERTO Y SE NORMALIZARON LAS CARGAS | S23041000716 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 314 | 2023-04-11 | 43646 | keep | 0 | Apr | 2023 | 0.029727 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-11 16:54 | 2023-04-11 21:15 | 35 | 4:21 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR RAYO | A23041100159 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 261 | 2023-04-11 | 9135 | keep | 0 | Apr | 2023 | 0.0062218 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-04-11 16:54 | 2023-04-12 09:03 | 2 | 16:09 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LAS LINEAS | A23041100159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 969 | 2023-04-11 | 1938 | keep | 0 | Apr | 2023 | 0.00132 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-11 17:08 | 2023-04-12 06:40 | 200 | 13:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA 1 X 65 EN C/L | B23041100321 | New_Event | Cutout Failure | Include | Include | Equipment | 812 | 2023-04-11 | 162400 | keep | 0 | Apr | 2023 | 0.11061 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-04-11 17:30 | 2023-04-11 19:11 | 30 | 1:41 | P | ANIMAL | 1X100 EN C/L CRUCE POR AVE | R23041100138 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-04-11 | 3030 | keep | 0 | Apr | 2023 | 0.0020637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-11 18:19 | 2023-04-11 20:02 | 50 | 1:43 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | A23041100175 | New_Event | Animals | Include | Include | Wildlife | 103 | 2023-04-11 | 5150 | keep | 0 | Apr | 2023 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-11 18:20 | 2023-04-11 19:09 | 1 | 0:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L SE REMPLAZO CAJA | B23041100284 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2023-04-11 | 49 | keep | 0 | Apr | 2023 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-11 18:30 | 2023-04-12 11:30 | 18 | 17:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 75KVA X 75KVA Y 1X10 EN EL NUEVO XMR | R23041100145 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1020 | 2023-04-11 | 18360 | keep | 0 | Apr | 2023 | 0.012505 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
HUMACAO | 2023-04-11 18:39 | 2023-04-11 20:12 | 40 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23041100146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-04-11 | 3720 | keep | 0 | Apr | 2023 | 0.0025337 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-04-11 18:52 | 2023-04-11 19:51 | 3 | 0:59 | P | ANIMAL | 1 X 30 EN C/L ANIMAL CRUZO LINEAS | P23041100180 | New_Event | Animals | Include | Include | Wildlife | 59 | 2023-04-11 | 177 | keep | 0 | Apr | 2023 | 0.00012055 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-04-11 18:59 | 2023-04-11 20:14 | 345 | 1:15 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L SE ELIMINO PARARRAYO | C23041100149 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 75 | 2023-04-11 | 25875 | keep | 0 | Apr | 2023 | 0.017623 | 0.00023498 | Sustained | FALSE | FALSE | Not_TMED_Event | 345
AGUADILLA | 2023-04-11 19:03 | 2023-04-11 21:50 | 50 | 2:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA DE CORTE DE LINEA | M23041100206 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2023-04-11 | 8350 | keep | 0 | Apr | 2023 | 0.0056871 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-11 19:04 | 2023-04-12 08:41 | 270 | 13:37 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23041100360 | New_Event | Vegetation Contact | Include | Include | Vegetation | 817 | 2023-04-11 | 220590 | keep | 0 | Apr | 2023 | 0.15024 | 0.0001839 | Sustained | FALSE | FALSE | Not_TMED_Event | 270
VEGA BAJA | 2023-04-11 19:25 | 2023-04-12 02:42 | 12 | 7:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDARIO | B23041100314 | New_Event | Secondary Wire Break | Include | Include | Equipment | 437 | 2023-04-11 | 5244 | keep | 0 | Apr | 2023 | 0.0035717 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-11 19:31 | 2023-04-12 04:45 | 867 | 9:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 80 EN C/L | B23041100320 | New_Event | Cutout Failure | Include | Include | Equipment | 554 | 2023-04-11 | 480318 | keep | 0 | Apr | 2023 | 0.32714 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
BAYAMON | 2023-04-11 19:33 | 2023-04-12 09:08 | 1 | 13:35 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23041100322 | New_Event | Vegetation Contact | Include | Include | Vegetation | 815 | 2023-04-11 | 815 | keep | 0 | Apr | 2023 | 0.00055509 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-11 19:56 | 2023-04-12 08:52 | 15 | 12:56 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | P23041100197 | New_Event | Primary Wire Break | Include | Include | Equipment | 776 | 2023-04-11 | 11640 | keep | 0 | Apr | 2023 | 0.007928 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-04-11 19:56 | 2023-04-12 12:25 | 5 | 16:29 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23041100185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 989 | 2023-04-11 | 4945 | keep | 0 | Apr | 2023 | 0.003368 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-04-11 20:08 | 2023-04-11 21:52 | 19 | 1:44 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR Y SE REEMPLAZO DE MACHETE QUEMADO SJ-230411-03 | S23041100301 | New_Event | Switch Failure | Include | Include | Equipment | 104 | 2023-04-11 | 1976 | keep | 0 | Apr | 2023 | 0.0013458 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
VEGA BAJA | 2023-04-11 20:15 | 2023-04-12 07:50 | 10 | 11:35 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A23041100187 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 695 | 2023-04-11 | 6950 | keep | 0 | Apr | 2023 | 0.0047336 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-11 20:21 | 2023-04-12 18:00 | 25 | 21:39 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ENREDADERA 1 X 18 AMP.NX EN AREAS COMUNES | S23041100397 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1299 | 2023-04-11 | 32475 | keep | 0 | Apr | 2023 | 0.022119 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-11 20:42 | 2023-04-12 08:33 | 20 | 11:51 | P | SOBRECARGA | 1 X 25 EN TRANSFORMADOR POR CARGA | M23041100218 | New_Event | Trip Due To Overload | Include | Include | Other | 711 | 2023-04-11 | 14220 | keep | 0 | Apr | 2023 | 0.0096852 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-11 21:09 | 2023-04-12 14:55 | 21 | 17:46 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | S23041100410 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1066 | 2023-04-11 | 22386 | keep | 0 | Apr | 2023 | 0.015247 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-04-11 21:25 | 2023-04-11 22:25 | 312 | 1:00 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE CERRO INTERRUPTOR EN SUBESTACION 1359-07 NO CARGA | S23041100425 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 60 | 2023-04-11 | 18720 | keep | 0 | Apr | 2023 | 0.01275 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
BAYAMON | 2023-04-11 22:50 | 2023-04-12 11:02 | 516 | 12:12 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE LINEA Y SE REPARO CONDUCTOR EN EL SUELO | B23041100370 | New_Event | Primary Wire Break | Include | Include | Equipment | 732 | 2023-04-11 | 377712 | keep | 0 | Apr | 2023 | 0.25726 | 0.00035145 | Sustained | FALSE | FALSE | Not_TMED_Event | 516
CAGUAS | 2023-04-11 22:55 | 2023-04-12 09:33 | 10 | 10:38 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE NO FUNDIO | C23041100167 | New_Event | Primary Wire Break | Include | Include | Equipment | 638 | 2023-04-11 | 6380 | keep | 0 | Apr | 2023 | 0.0043454 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-12 01:10 | 2023-04-12 09:44 | 70 | 8:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23041200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 514 | 2023-04-12 | 35980 | keep | 0 | Apr | 2023 | 0.024506 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-04-12 01:42 | 2023-04-12 01:43 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23041200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2023-04-12 05:11 | 2023-04-12 09:14 | 2 | 4:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO HACIA TRANSFORMADOR | R23041200002 | New_Event | Primary Wire Break | Include | Include | Equipment | 243 | 2023-04-12 | 486 | keep | 0 | Apr | 2023 | 0.00033101 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-04-12 05:39 | 2023-04-12 11:15 | 150 | 5:36 | P | PROBLEMA DEL CLIENTE | 3 X 40 EN RISER Y 3 X 50 EN CORTE DE LINEA AVERIA INTERNA | M23041200012 | New_Event | Customer-Related Interruption | Include | Include | Public | 336 | 2023-04-12 | 50400 | keep | 0 | Apr | 2023 | 0.034327 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-04-12 06:16 | 2023-04-12 11:51 | 19 | 5:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R23041200003 | New_Event | Cutout Failure | Include | Include | Equipment | 335 | 2023-04-12 | 6365 | keep | 0 | Apr | 2023 | 0.0043352 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2023-04-12 06:45 | 2023-04-12 09:40 | 20 | 2:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23041200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2023-04-12 | 3500 | keep | 0 | Apr | 2023 | 0.0023838 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-04-12 06:57 | 2023-04-12 11:57 | 1 | 5:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE CORTE DE LINEA 1 X 65 EN CORTE DE LINEA | P23041200007 | New_Event | Cutout Failure | Include | Include | Equipment | 300 | 2023-04-12 | 300 | keep | 0 | Apr | 2023 | 0.00020433 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-12 07:12 | 2023-04-12 07:44 | 1 | 0:32 | P | DESGANCHE | 2 X 65 EN RISER Y 2 SMU 20 DE 80A | C23041200011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 32 | 2023-04-12 | 32 | keep | 0 | Apr | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-12 07:19 | 2023-04-12 10:28 | 122 | 3:09 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | R23041200006 | New_Event | Animals | Include | Include | Wildlife | 189 | 2023-04-12 | 23058 | keep | 0 | Apr | 2023 | 0.015705 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
CAGUAS | 2023-04-12 07:20 | 2023-04-12 09:34 | 1 | 2:14 | P | ANIMAL | 2 X 10 EN BANCO DE XMRS CRUCE X AVE | C23041200012 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-04-12 | 134 | keep | 0 | Apr | 2023 | 9.1267e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-12 07:30 | 2023-04-12 15:44 | 15 | 8:14 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE ELIMINO PARARRAYO | S23041200023 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 494 | 2023-04-12 | 7410 | keep | 0 | Apr | 2023 | 0.0050469 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-04-12 07:38 | 2023-04-12 11:00 | 50 | 3:22 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23041200007 | New_Event | Animals | Include | Include | Wildlife | 202 | 2023-04-12 | 10100 | keep | 0 | Apr | 2023 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-12 07:44 | 2023-04-12 07:45 | 2354 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C2304120000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-04-12 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-04-12 07:45 | 2023-04-12 09:08 | 1 | 1:23 | P | DESGANCHE | 2 X 65 EN RISER Y 2 SMU 20 DE 80A | C23041200011 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-04-12 | 83 | keep | 0 | Apr | 2023 | 5.6531e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-12 07:53 | 2023-04-12 09:00 | 19 | 1:07 | T | DESCONECTIVO DEFECTUOSO | SJ-230412-01 SE ABRE INTERRUPTOR PARA REMPLAZO MACHETE TRONCAL ALIMENTADOR | S23041200032 | New_Event | Switch Failure | Include | Include | Equipment | 67 | 2023-04-12 | 1273 | keep | 0 | Apr | 2023 | 0.00086703 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2023-04-12 07:57 | 2023-04-12 10:47 | 13 | 2:50 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23041200015 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-04-12 | 2210 | keep | 0 | Apr | 2023 | 0.0015052 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-04-12 08:00 | 2023-04-12 16:25 | 50 | 8:25 | P | ERROR HUMANO | 1 X 50 EN CORTE DE LINEA PERSONAL COMPAÃ‘IA DESGANCHE CRUZO FASE | S23041200153 | New_Event | Human Error | Include | Include | Other | 505 | 2023-04-12 | 25250 | keep | 0 | Apr | 2023 | 0.017198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-12 08:05 | 2023-04-12 11:45 | 36 | 3:40 | P | PARARRAYOS DEFECTUOSO | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | R23041200018 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 220 | 2023-04-12 | 7920 | keep | 0 | Apr | 2023 | 0.0053943 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
UTUADO | 2023-04-12 08:12 | 2023-04-12 15:23 | 40 | 7:11 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO RAMA | A23041200014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 431 | 2023-04-12 | 17240 | keep | 0 | Apr | 2023 | 0.011742 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-04-12 08:12 | 2023-04-12 15:15 | 6 | 7:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50 KVA | A23041200067 | New_Event | Service Transformer Failure | Include | Include | Equipment | 423 | 2023-04-12 | 2538 | keep | 0 | Apr | 2023 | 0.0017286 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-04-12 08:53 | 2023-04-12 08:54 | 464 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041200019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 464 | keep | 0 | Apr | 2023 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
BARRANQUITAS | 2023-04-12 09:04 | 2023-04-12 10:37 | 5 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | C23041200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-04-12 | 465 | keep | 0 | Apr | 2023 | 0.00031671 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-04-12 09:20 | 2023-04-12 17:41 | 15 | 8:21 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR AVERIADO DE 37.5KVA X EL MISMO | M23041200029 | New_Event | Service Transformer Failure | Include | Include | Equipment | 501 | 2023-04-12 | 7515 | keep | 0 | Apr | 2023 | 0.0051184 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-04-12 09:20 | 2023-04-12 11:45 | 75 | 2:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA Y SE REPARO CONDICION DE LINEA PRIMARIA SAFADA SOBRE CRUCETA ELIMINANDO CRUCETA E INSTALANDO RIGIDOS | A23041200024 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 145 | 2023-04-12 | 10875 | keep | 0 | Apr | 2023 | 0.0074069 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-04-12 09:21 | 2023-04-12 13:23 | 1 | 4:02 | P | ANIMAL | 1 X 15 EN RISER CRUCE X CULEBRA | B23041200039 | New_Event | Animals | Include | Include | Wildlife | 242 | 2023-04-12 | 242 | keep | 0 | Apr | 2023 | 0.00016483 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-12 09:23 | 2023-04-12 09:24 | 1516 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | C23041200026 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-12 | 1516 | keep | 0 | Apr | 2023 | 0.0010325 | 0.0010325 | Momentary | FALSE | FALSE | Not_TMED_Event | 1516
BARRANQUITAS | 2023-04-12 09:24 | 2023-04-12 15:15 | 695 | 5:51 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO SAFADO EN TRONCAL | C23041200056 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 351 | 2023-04-12 | 243945 | keep | 0 | Apr | 2023 | 0.16615 | 0.00047336 | Sustained | FALSE | FALSE | Not_TMED_Event | 695
SAN JUAN | 2023-04-12 09:27 | 2023-04-12 15:00 | 8 | 5:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO CAUSA | S23041200062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2023-04-12 | 2664 | keep | 0 | Apr | 2023 | 0.0018144 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-12 09:27 | 2023-04-12 09:28 | 2234 | 0:01 | T | DESGANCHE | RECIERRE | B23041100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-12 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-04-12 09:28 | 2023-04-12 11:29 | 30 | 2:01 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | B23041200052 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-04-12 | 3630 | keep | 0 | Apr | 2023 | 0.0024724 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-12 09:36 | 2023-04-12 12:15 | 7 | 2:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON BARRAS EN PEDESTAL SECUNDARIO | R23041200032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 159 | 2023-04-12 | 1113 | keep | 0 | Apr | 2023 | 0.00075806 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-04-12 09:39 | 2023-04-12 10:49 | 30 | 1:10 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR AVE | P23041200025 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-04-12 | 2100 | keep | 0 | Apr | 2023 | 0.0014303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-04-12 09:43 | 2023-04-12 11:00 | 75 | 1:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTES DE LINEA SE REEMPLAZARON CAJAS QUEMADAS | R23041200035 | New_Event | Cutout Failure | Include | Include | Equipment | 77 | 2023-04-12 | 5775 | keep | 0 | Apr | 2023 | 0.0039333 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2023-04-12 09:50 | 2023-04-12 09:51 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041200028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 4132 | keep | 0 | Apr | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
HUMACAO | 2023-04-12 09:52 | 2023-04-12 09:53 | 2354 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C2304120000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-04-12 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-04-12 09:56 | 2023-04-12 09:57 | 2354 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C2304120000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-04-12 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
AGUADILLA | 2023-04-12 10:07 | 2023-04-12 15:30 | 13 | 5:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO | M23041200042 | New_Event | Primary Wire Break | Include | Include | Equipment | 323 | 2023-04-12 | 4199 | keep | 0 | Apr | 2023 | 0.0028599 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-04-12 10:12 | 2023-04-12 10:13 | 3387 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL | B23041200058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 3387 | keep | 0 | Apr | 2023 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
SAN JUAN | 2023-04-12 10:16 | 2023-04-12 15:06 | 20 | 4:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23041200079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2023-04-12 | 5800 | keep | 0 | Apr | 2023 | 0.0039504 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-12 10:20 | 2023-04-12 10:21 | 2354 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C2304120000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-04-12 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-04-12 10:25 | 2023-04-12 10:26 | 2354 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | C2304120000X | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 1 | 2023-04-12 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2023-04-12 10:29 | 2023-04-12 15:33 | 1 | 5:04 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR NO CAUSA | S23041200082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 304 | 2023-04-12 | 304 | keep | 0 | Apr | 2023 | 0.00020705 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-12 10:33 | 2023-04-12 12:20 | 2354 | 1:47 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO EL BKR POR MACHETES EN FUEGO Y SE SECCIONALIZO 2 MACHETES QUEMADOS Y 2 CAJAS QUEMADAS GOI CG-230412-01 | C23041200050 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 107 | 2023-04-12 | 251878 | keep | 0 | Apr | 2023 | 0.17155 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2023-04-12 10:44 | 2023-04-12 14:00 | 40 | 3:16 | P | DESGANCHE | 1 X 100 EN C/L | B23041200055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-04-12 | 7840 | keep | 0 | Apr | 2023 | 0.0053398 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-12 10:49 | 2023-04-12 14:35 | 5 | 3:46 | P | DESGANCHE | 1 X 20 EN C/L SE DESGANCHO | B23041200057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2023-04-12 | 1130 | keep | 0 | Apr | 2023 | 0.00076964 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-04-12 10:50 | 2023-04-12 11:48 | 22 | 0:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA TRANSFORMADOR | S23041200088 | New_Event | Cutout Failure | Include | Include | Equipment | 58 | 2023-04-12 | 1276 | keep | 0 | Apr | 2023 | 0.00086908 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2023-04-12 10:52 | 2023-04-12 13:44 | 40 | 2:52 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR | R23041200052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-04-12 | 6880 | keep | 0 | Apr | 2023 | 0.0046859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-12 10:55 | 2023-04-12 11:30 | 23 | 0:35 | P | CAUSAS EXTERNAS | SE ABRIO T-123 PARA ENDERSARLO YA QUE FUE IMPACTADO POR CAMION | S23041200366 | New_Event | Damage From Public | Include | Include | Public | 35 | 2023-04-12 | 805 | keep | 0 | Apr | 2023 | 0.00054828 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2023-04-12 11:00 | 2023-04-12 12:47 | 75 | 1:47 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23041200063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2023-04-12 | 8025 | keep | 0 | Apr | 2023 | 0.0054658 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
GUAYAMA | 2023-04-12 11:11 | 2023-04-12 12:39 | 10 | 1:28 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA POR LINEAS ARRIADAS | P23041200051 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 88 | 2023-04-12 | 880 | keep | 0 | Apr | 2023 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-12 11:12 | 2023-04-12 13:00 | 13 | 1:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | A23041200050 | New_Event | Cutout Failure | Include | Include | Equipment | 108 | 2023-04-12 | 1404 | keep | 0 | Apr | 2023 | 0.00095626 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-04-12 11:42 | 2023-04-12 13:00 | 2523 | 1:18 | P | DESGANCHE | RAMAS SOBRE LINEAS SE CIERRA POLE BREAKER 6014-02B P | M23041200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-04-12 | 196794 | keep | 0 | Apr | 2023 | 0.13404 | 0.0017184 | Sustained | FALSE | FALSE | Not_TMED_Event | 2523
BARRANQUITAS | 2023-04-12 12:01 | 2023-04-12 13:41 | 2 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | ABRIR XMR PARA LEVANTAR CONDUCTOR, REEMPLAZAR CAJA Y PARARRAYO | C23041200071 | New_Event | Primary Wire Break | Include | Include | Equipment | 100 | 2023-04-12 | 200 | keep | 0 | Apr | 2023 | 0.00013622 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-04-12 12:20 | 2023-04-12 12:36 | 118 | 0:16 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO 2 MACHETES QUEMADOS Y 2 CAJAS QUEMADAS Y SE CERRO N/O CONTRA EL 2604-03 GOI CG-230412-01 | C23041200050 | Partial_restoration | Switch Failure | Include | Include | Equipment | 16 | 2023-04-12 | 1888 | keep | 0 | Apr | 2023 | 0.0012859 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-04-12 12:45 | 2023-04-12 14:42 | 15 | 1:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA CONEXIONES SECUNDARIAS | M23041200035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 117 | 2023-04-12 | 1755 | keep | 0 | Apr | 2023 | 0.0011953 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-12 12:48 | 2023-04-12 18:00 | 10 | 5:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23041200117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 312 | 2023-04-12 | 3120 | keep | 0 | Apr | 2023 | 0.002125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-12 12:59 | 2023-04-12 14:02 | 1 | 1:03 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA DESGANCHAR Y REPARAR SECUNDARIA | C23041200119 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 63 | 2023-04-12 | 63 | keep | 0 | Apr | 2023 | 4.2909e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-12 13:04 | 2023-04-12 17:55 | 75 | 4:51 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | M23041200129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2023-04-12 | 21825 | keep | 0 | Apr | 2023 | 0.014865 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-04-12 13:14 | 2023-04-12 13:21 | 1017 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL SE VERIFICO PERSONAL FUERA | C23041200126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-04-12 | 7119 | keep | 0 | Apr | 2023 | 0.0048487 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
ARECIBO | 2023-04-12 13:14 | 2023-04-12 17:15 | 15 | 4:01 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE LINEA A CAJA DE TRANSFORMADOR | A23041200063 | New_Event | Primary Wire Break | Include | Include | Equipment | 241 | 2023-04-12 | 3615 | keep | 0 | Apr | 2023 | 0.0024622 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-12 13:20 | 2023-04-12 14:44 | 16 | 1:24 | P | ANIMAL | SE ABRIO 2 XMR PARA REEMPLAZO DE 2 AISLADORES Y SE RETIRARON 2 AVES CRUZADAS | C23041200123 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-04-12 | 1344 | keep | 0 | Apr | 2023 | 0.00091539 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-04-12 13:31 | 2023-04-12 15:30 | 3 | 1:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRAS EN PEDESTAL | C23041200130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 119 | 2023-04-12 | 357 | keep | 0 | Apr | 2023 | 0.00024315 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2023-04-12 13:45 | 2023-04-12 15:55 | 200 | 2:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA REMPLAZO DE POSTE | A23041100117 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 130 | 2023-04-12 | 26000 | keep | 0 | Apr | 2023 | 0.017708 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-04-12 13:58 | 2023-04-12 16:55 | 1 | 2:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23041200069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 177 | 2023-04-12 | 177 | keep | 0 | Apr | 2023 | 0.00012055 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-12 13:59 | 2023-04-12 16:48 | 13 | 2:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L SE LEVANTO CONDUCTOR DEL SUELO Y REPARO NEUTRAL PARTIDO | C23041200139 | New_Event | Primary Wire Break | Include | Include | Equipment | 169 | 2023-04-12 | 2197 | keep | 0 | Apr | 2023 | 0.0014964 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-04-12 14:05 | 2023-04-12 14:55 | 81 | 0:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23041200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-04-12 | 4050 | keep | 0 | Apr | 2023 | 0.0027584 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
SAN JUAN | 2023-04-12 14:07 | 2023-04-12 15:34 | 3 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA PARA LEVANTAR SECUNDARIA REF. S23041200116 | S23041200135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-04-12 | 261 | keep | 0 | Apr | 2023 | 0.00017777 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-12 14:13 | 2023-04-12 15:47 | 62 | 1:34 | P | ANIMAL | 1X80 EN C/L CRUCE POR AVE | R23041200067 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-04-12 | 5828 | keep | 0 | Apr | 2023 | 0.0039694 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-04-12 14:16 | 2023-04-12 16:21 | 30 | 2:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA | B23041200103 | New_Event | Cutout Failure | Include | Include | Equipment | 125 | 2023-04-12 | 3750 | keep | 0 | Apr | 2023 | 0.0025541 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-12 14:37 | 2023-04-12 14:38 | 27 | 0:01 | T | ANIMAL | RECERRO | B2304120000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-12 | 27 | keep | 0 | Apr | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-04-12 14:38 | 2023-04-12 17:02 | 20 | 2:24 | P | ANIMAL | 1 X 140 EN C/L CRUCE POR AVE | B23041200117 | 1st_after_momentary | Animals | Include | Include | Wildlife | 144 | 2023-04-12 | 2880 | keep | 0 | Apr | 2023 | 0.0019616 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-12 14:48 | 2023-04-12 14:49 | 67 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23041200077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 67 | keep | 0 | Apr | 2023 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2023-04-12 14:57 | 2023-04-12 20:50 | 40 | 5:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | A23041200078 | New_Event | Cutout Failure | Include | Include | Equipment | 353 | 2023-04-12 | 14120 | keep | 0 | Apr | 2023 | 0.0096171 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-12 15:00 | 2023-04-12 17:25 | 80 | 2:25 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23041200153 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-04-12 | 11600 | keep | 0 | Apr | 2023 | 0.0079007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-12 15:05 | 2023-04-12 15:06 | 3838 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 3838 | keep | 0 | Apr | 2023 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
FAJARDO | 2023-04-12 15:17 | 2023-04-12 16:01 | 16 | 0:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN XMR SE REMPLAZO CAJA PRIMARIA EN EL XMR | R23041200074 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2023-04-12 | 704 | keep | 0 | Apr | 2023 | 0.00047949 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-04-12 15:17 | 2023-04-12 18:00 | 8 | 2:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23041200119 | New_Event | Secondary Wire Break | Include | Include | Equipment | 163 | 2023-04-12 | 1304 | keep | 0 | Apr | 2023 | 0.00088815 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-04-12 15:32 | 2023-04-12 16:25 | 60 | 0:53 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23041200091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 53 | 2023-04-12 | 3180 | keep | 0 | Apr | 2023 | 0.0021659 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-04-12 15:40 | 2023-04-12 16:56 | 8 | 1:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 37.5KVA AVERIADO | A23041200092 | New_Event | Service Transformer Failure | Include | Include | Equipment | 76 | 2023-04-12 | 608 | keep | 0 | Apr | 2023 | 0.00041411 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-12 15:43 | 2023-04-12 16:40 | 20 | 0:57 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23041200155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 57 | 2023-04-12 | 1140 | keep | 0 | Apr | 2023 | 0.00077645 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-04-12 15:52 | 2023-04-12 17:50 | 50 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23041200098 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-04-12 | 5900 | keep | 0 | Apr | 2023 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-12 16:00 | 2023-04-12 16:02 | 837 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1401-07 LLEVANDO CARGA 1401-06. SE CERRO POR CONTROL | S23041200000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-12 | 1674 | keep | 0 | Apr | 2023 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-04-12 16:00 | 2023-04-12 16:02 | 908 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1401-06 | S23041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-12 | 1816 | keep | 0 | Apr | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
UTUADO | 2023-04-12 16:02 | 2023-04-12 18:45 | 60 | 2:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS | A23041200103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-04-12 | 9780 | keep | 0 | Apr | 2023 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-04-12 16:30 | 2023-04-12 17:15 | 11 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REEMPLAZO BAJANTES SECUNDARIOS | A23041200023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-12 | 495 | keep | 0 | Apr | 2023 | 0.00033714 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-04-12 16:37 | 2023-04-12 19:34 | 6 | 2:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | M23041200169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 177 | 2023-04-12 | 1062 | keep | 0 | Apr | 2023 | 0.00072332 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-04-12 16:45 | 2023-04-13 12:28 | 4 | 19:43 | P | TRANSFORMADOR AVERIADO | SE RELOCALIZO SECUNDARIA TRASPATIO A OTRO TRANSFORMADOR | R23041200080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1183 | 2023-04-12 | 4732 | keep | 0 | Apr | 2023 | 0.0032229 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-04-12 17:09 | 2023-04-13 09:30 | 6 | 16:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23041200173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 981 | 2023-04-12 | 5886 | keep | 0 | Apr | 2023 | 0.0040089 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-12 17:22 | 2023-04-12 18:46 | 150 | 1:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR RAMA CRUZO LINEA | M23041200178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-04-12 | 12600 | keep | 0 | Apr | 2023 | 0.0085818 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-04-12 17:38 | 2023-04-12 19:50 | 10 | 2:12 | P | NO SE REPORTO CAUSA | 1 SMU-25 X 25 EN SU-PB-5-B1 | C23041200180 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2023-04-12 | 1320 | keep | 0 | Apr | 2023 | 0.00089905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-12 17:44 | 2023-04-12 20:58 | 60 | 3:14 | P | DESGANCHE | 2 X 100 EN C/L | R23041200084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-04-12 | 11640 | keep | 0 | Apr | 2023 | 0.007928 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-04-12 17:51 | 2023-04-12 17:52 | 1516 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23041200181 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 1516 | keep | 0 | Apr | 2023 | 0.0010325 | 0.0010325 | Momentary | FALSE | FALSE | Not_TMED_Event | 1516
AGUADILLA | 2023-04-12 17:51 | 2023-04-13 08:51 | 1 | 15:00 | P | OTRAS CAUSAS | 3 X 20 EN TRANSFORMADO POR FUSIBLES SULFATADOS (TRIBUNAL) | A23041200116 | New_Event | Other Causes | Include | Include | Other | 900 | 2023-04-12 | 900 | keep | 0 | Apr | 2023 | 0.00061299 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-12 17:55 | 2023-04-12 17:56 | 1516 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23041200182 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 1516 | keep | 0 | Apr | 2023 | 0.0010325 | 0.0010325 | Momentary | FALSE | FALSE | Not_TMED_Event | 1516
BARRANQUITAS | 2023-04-12 17:57 | 2023-04-12 17:58 | 1516 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23041200183 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 1516 | keep | 0 | Apr | 2023 | 0.0010325 | 0.0010325 | Momentary | FALSE | FALSE | Not_TMED_Event | 1516
MAYAGÃœEZ | 2023-04-12 18:00 | 2023-04-12 19:50 | 15 | 1:50 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR CON ESCAPE DE ACEITE 50KVA X 50KVA | M23041200183 | New_Event | Service Transformer Failure | Include | Include | Equipment | 110 | 2023-04-12 | 1650 | keep | 0 | Apr | 2023 | 0.0011238 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-04-12 18:07 | 2023-04-12 20:50 | 30 | 2:43 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASES | A23041200119 | New_Event | Animals | Include | Include | Wildlife | 163 | 2023-04-12 | 4890 | keep | 0 | Apr | 2023 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-12 18:36 | 2023-04-12 21:00 | 150 | 2:24 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR IGUANA | M23041200193 | New_Event | Animals | Include | Include | Wildlife | 144 | 2023-04-12 | 21600 | keep | 0 | Apr | 2023 | 0.014712 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-04-12 18:38 | 2023-04-13 08:04 | 40 | 13:26 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | C23041200205 | New_Event | Animals | Include | Include | Wildlife | 806 | 2023-04-12 | 32240 | keep | 0 | Apr | 2023 | 0.021959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-12 18:41 | 2023-04-13 09:43 | 6 | 15:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN C/L Y SE REPARO CONDUCTOR EN EL SUELO | B23041200133 | New_Event | Primary Wire Break | Include | Include | Equipment | 902 | 2023-04-12 | 5412 | keep | 0 | Apr | 2023 | 0.0036861 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-04-12 18:51 | 2023-04-12 18:52 | 4085 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO | R23041200090 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-12 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-04-12 18:52 | 2023-04-12 21:24 | 61 | 2:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIAS | R23041200091 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 152 | 2023-04-12 | 9272 | keep | 0 | Apr | 2023 | 0.0063151 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-04-12 18:56 | 2023-04-12 18:59 | 1615 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23041200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-12 | 4845 | keep | 0 | Apr | 2023 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-04-12 19:01 | 2023-04-12 19:04 | 1494 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1619-02 LLEVA 30% DE LA CARGA DEL 1336-06 LLEVA 50% DEL 1619-03 SE CERRO POR CONTROL | R23041200102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-12 | 4482 | keep | 0 | Apr | 2023 | 0.0030527 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2023-04-12 19:01 | 2023-04-13 13:44 | 100 | 18:43 | P | DESGANCHE | 1 X 100 EN C/L Y 1X 65 EN C/L DESGANCHE | S23041200193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1123 | 2023-04-12 | 112300 | keep | 0 | Apr | 2023 | 0.076487 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-12 19:01 | 2023-04-12 19:04 | 2531 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1619-02 LLEVA 30% DE LA CARGA DEL 1336-06 LLEVA 50% DEL 1619-03 SE CERRO POR CONTROL | R23041200102 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-12 | 7593 | keep | 0 | Apr | 2023 | 0.0051716 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
BAYAMON | 2023-04-12 19:07 | 2023-04-12 19:08 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2304120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-12 | 325 | keep | 0 | Apr | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-04-12 19:11 | 2023-04-13 15:56 | 26 | 20:45 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO PRIMARIA Y SE REMPLAZO 2 CAJAS PRIMARIA SE CERRO C/L | S23041200197 | New_Event | Primary Wire Break | Include | Include | Equipment | 1245 | 2023-04-12 | 32370 | keep | 0 | Apr | 2023 | 0.022047 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BARRANQUITAS | 2023-04-12 19:13 | 2023-04-13 12:30 | 100 | 17:17 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO MEDIANTE G.O.I. CG-230413-01 | C23041200213 | New_Event | Switch Failure | Include | Include | Equipment | 1037 | 2023-04-12 | 103700 | keep | 0 | Apr | 2023 | 0.07063 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-12 19:51 | 2023-04-13 14:42 | 6 | 18:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REPARO SECUNDARIA CRUZADA | B23041200137 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1131 | 2023-04-12 | 6786 | keep | 0 | Apr | 2023 | 0.0046219 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-12 19:56 | 2023-04-13 15:00 | 11 | 19:04 | P | TRANSFORMADOR AVERIADO | 2 X 30 EN XMR REMPLAZO DE XMR | S23041200204 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1144 | 2023-04-12 | 12584 | keep | 0 | Apr | 2023 | 0.0085709 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-04-12 21:30 | 2023-04-12 22:55 | 918 | 1:25 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL DE LAS LINEAS | C23041200287 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 85 | 2023-04-12 | 78030 | keep | 0 | Apr | 2023 | 0.053146 | 0.00062525 | Sustained | FALSE | FALSE | Not_TMED_Event | 918
VEGA BAJA | 2023-04-12 21:45 | 2023-04-13 13:21 | 30 | 15:36 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR Y 1 X 30 EN CORTE DE LINEA POR AVE | A23041200132 | New_Event | Animals | Include | Include | Wildlife | 936 | 2023-04-12 | 28080 | keep | 0 | Apr | 2023 | 0.019125 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-04-12 22:39 | 2023-04-13 00:47 | 100 | 2:08 | P | DESGANCHE | 1 X 65 EN C/L | C23041200393 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-04-12 | 12800 | keep | 0 | Apr | 2023 | 0.008718 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-04-13 00:05 | 2023-04-13 06:16 | 80 | 6:11 | P | DESGANCHE | DESGANCHE 1 X 100 EN SALIDA DEL RISER | P23041300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 371 | 2023-04-13 | 29680 | keep | 0 | Apr | 2023 | 0.020215 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-13 03:19 | 2023-04-13 09:38 | 50 | 6:19 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23041300001 | New_Event | Animals | Include | Include | Wildlife | 379 | 2023-04-13 | 18950 | keep | 0 | Apr | 2023 | 0.012907 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-13 04:47 | 2023-04-13 04:48 | 5663 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1717-02 CERRADO POR SCADA LLEVA 95% 1713-05 | B23041300001 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-13 | 5663 | keep | 0 | Apr | 2023 | 0.003857 | 0.003857 | Momentary | FALSE | FALSE | Not_TMED_Event | 5663
BAYAMON | 2023-04-13 04:47 | 2023-04-13 04:48 | 911 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR 1717-02 CERRADO POR SCADA LLEVA 95% 1713-05 | B23041300001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 911 | keep | 0 | Apr | 2023 | 0.00062048 | 0.00062048 | Momentary | FALSE | FALSE | Not_TMED_Event | 911
CANOVANAS | 2023-04-13 05:13 | 2023-04-13 05:15 | 1494 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1619-02 LLEVA 30% DE LA CARGA DEL 1336-06 SE CERRO POR CONTROL | R2304130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-13 | 2988 | keep | 0 | Apr | 2023 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
CANOVANAS | 2023-04-13 05:13 | 2023-04-13 05:15 | 2531 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1619-02 LLEVA 30% DE LA CARGA DEL 1336-06 LLEVA 50% DEL 1619-03 SE CERRO POR CONTROL | R2304130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-13 | 5062 | keep | 0 | Apr | 2023 | 0.0034477 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
VEGA BAJA | 2023-04-13 06:20 | 2023-04-13 15:13 | 60 | 8:53 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23041300002 | New_Event | Primary Wire Break | Include | Include | Equipment | 533 | 2023-04-13 | 31980 | keep | 0 | Apr | 2023 | 0.021781 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-13 06:21 | 2023-04-13 09:21 | 6 | 3:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23041300003 | New_Event | Primary Wire Break | Include | Include | Equipment | 180 | 2023-04-13 | 1080 | keep | 0 | Apr | 2023 | 0.00073558 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-04-13 06:47 | 2023-04-13 09:54 | 10 | 3:07 | P | CAUSAS EXTERNAS | 1X10 EN XMR POR GENERADOR DE CLIENTE PRIVADO MAL CONECTADO | C23041300010 | New_Event | Damage From Public | Include | Include | Public | 187 | 2023-04-13 | 1870 | keep | 0 | Apr | 2023 | 0.0012736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-04-13 07:01 | 2023-04-13 10:36 | 14 | 3:35 | P | ANIMAL | 1 X 10 EN XMR AVE | R23041300004 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-04-13 | 3010 | keep | 0 | Apr | 2023 | 0.0020501 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2023-04-13 07:03 | 2023-04-13 09:54 | 50 | 2:51 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | P23041300016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-04-13 | 8550 | keep | 0 | Apr | 2023 | 0.0058234 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-13 07:14 | 2023-04-13 08:31 | 50 | 1:17 | P | ANIMAL | 1X80 EN C/L CRUCE POR AVE | C23041300016 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-04-13 | 3850 | keep | 0 | Apr | 2023 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-13 07:16 | 2023-04-13 07:19 | 922 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO 1401-08 QUE LLEVA 1346-05 SE VERIFICO PERSONAL FUERA DE ORDEN 6000 Y SE CERRO POR SCADA | S23041300016 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-13 | 2766 | keep | 0 | Apr | 2023 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-04-13 07:16 | 2023-04-13 07:19 | 135 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO 1401-08 QUE LLEVA 1346-05 SE VERIFICO PERSONAL FUERA DE ORDEN 6000 Y SE CERRO POR SCADA | S23041300016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-13 | 405 | keep | 0 | Apr | 2023 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CAGUAS | 2023-04-13 07:51 | 2023-04-13 07:54 | 2448 | 0:03 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO POR CONTROL | C23041300028 | New_Event | Cutout Failure | Include | Include | Equipment | 3 | 2023-04-13 | 7344 | keep | 0 | Apr | 2023 | 0.005002 | 0.0016673 | Momentary | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2023-04-13 07:54 | 2023-04-13 10:18 | 14 | 2:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO EN XMR PARA REMPLAZAR CAJA PRIMARIA | C23041300043 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 144 | 2023-04-13 | 2016 | keep | 0 | Apr | 2023 | 0.0013731 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-04-13 08:21 | 2023-04-13 10:00 | 1 | 1:39 | P | PROBLEMA DEL CLIENTE | 1 X 50 EN RISER POR FALTA DE MANTENIMIENTO | B23041300030 | New_Event | Customer-Related Interruption | Include | Include | Public | 99 | 2023-04-13 | 99 | keep | 0 | Apr | 2023 | 6.7428e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-13 08:21 | 2023-04-13 08:22 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041300026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 3718 | keep | 0 | Apr | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
GUAYAMA | 2023-04-13 08:22 | 2023-04-13 12:35 | 25 | 4:13 | P | CAUSAS EXTERNAS | 1 X 15 EN TRANSFORMADOR Y 1X 65 EN CORTE DE LINEA POR GLOBO HELIO | P23041300022 | New_Event | Damage From Public | Include | Include | Public | 253 | 2023-04-13 | 6325 | keep | 0 | Apr | 2023 | 0.0043079 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-13 08:22 | 2023-04-13 11:23 | 50 | 3:01 | P | ANIMAL | 1 X 25 Y 1 X 40 EN CORTE DE LINEA POR AVE | A23041300016 | New_Event | Animals | Include | Include | Wildlife | 181 | 2023-04-13 | 9050 | keep | 0 | Apr | 2023 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-13 08:28 | 2023-04-13 10:33 | 7 | 2:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA EN PEDESTAL | B23041300034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 125 | 2023-04-13 | 875 | keep | 0 | Apr | 2023 | 0.00059596 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2023-04-13 08:45 | 2023-04-13 08:46 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041300029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 4132 | keep | 0 | Apr | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
CAGUAS | 2023-04-13 08:49 | 2023-04-13 13:21 | 17 | 4:32 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN C/L PARA CERRAR PUENTE PRIMARIO DE LINEA @ CAJA | C23041300058 | New_Event | Primary Wire Break | Include | Include | Equipment | 272 | 2023-04-13 | 4624 | keep | 0 | Apr | 2023 | 0.0031494 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-04-13 08:53 | 2023-04-13 11:44 | 20 | 2:51 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23041300018 | New_Event | Animals | Include | Include | Wildlife | 171 | 2023-04-13 | 3420 | keep | 0 | Apr | 2023 | 0.0023293 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-13 09:02 | 2023-04-13 12:43 | 1 | 3:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN BANCO DE XMRS PARA REPARAR NEUTRAL PRIMARIO ABIERTO | C23041300065 | New_Event | Primary Wire Break | Include | Include | Equipment | 221 | 2023-04-13 | 221 | keep | 0 | Apr | 2023 | 0.00015052 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-13 09:06 | 2023-04-13 10:38 | 15 | 1:32 | P | ANIMAL | 1 X 25 EN C/L CRUCE POR AVE | R23041300013 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-04-13 | 1380 | keep | 0 | Apr | 2023 | 0.00093991 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-04-13 09:33 | 2023-04-13 12:10 | 1 | 2:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO LINEA SECUNDARIA AVERIADA CODIGO M POR QUE LAJAS PERTENECIA A DISTRITO DE SAN GERMAN REGION MAYAGÃœEZ | M23041300021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 157 | 2023-04-13 | 157 | keep | 0 | Apr | 2023 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-13 09:36 | 2023-04-13 16:51 | 8 | 7:15 | P | DESGANCHE | SE ABRIO C/L PARA REALIZAR DESGANCHE Y PARA REPARAR/LEVANTAR CONDUCTOR PRIMARIO DEL SUELO | C23041300076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2023-04-13 | 3480 | keep | 0 | Apr | 2023 | 0.0023702 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-13 09:37 | 2023-04-13 18:51 | 15 | 9:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 75KVA POR UNO DE IGUAL CAPACIDAD | S23041300047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 554 | 2023-04-13 | 8310 | keep | 0 | Apr | 2023 | 0.0056599 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-13 09:37 | 2023-04-13 12:15 | 79 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L Y SE LLEVO LINEA A AISLADOR | B23041300040 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-04-13 | 12482 | keep | 0 | Apr | 2023 | 0.0085014 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2023-04-13 09:37 | 2023-04-13 11:51 | 4 | 2:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23041300050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 134 | 2023-04-13 | 536 | keep | 0 | Apr | 2023 | 0.00036507 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-04-13 09:38 | 2023-04-13 12:38 | 1 | 3:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO PORTAFUSIBLES | R23041300017 | New_Event | Cutout Failure | Include | Include | Equipment | 180 | 2023-04-13 | 180 | keep | 0 | Apr | 2023 | 0.0001226 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-13 09:41 | 2023-04-13 13:17 | 1 | 3:36 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRIFASICA DESCARGA | P23041300051 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 216 | 2023-04-13 | 216 | keep | 0 | Apr | 2023 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-13 09:43 | 2023-04-13 09:47 | 2234 | 0:04 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | B23041300050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 4 | 2023-04-13 | 8936 | keep | 0 | Apr | 2023 | 0.0060863 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-04-13 09:47 | 2023-04-13 11:45 | 6 | 1:58 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN C/L Y SE REPARO CONDUCTOR EN EL SUELO | B23041200133 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 118 | 2023-04-13 | 708 | keep | 0 | Apr | 2023 | 0.00048222 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-13 09:47 | 2023-04-13 16:19 | 40 | 6:32 | P | DESGANCHE | 1 X 50 1 X 30 EN C/L SE REALIZO DESGANCHE | B23041300108 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 392 | 2023-04-13 | 15680 | keep | 0 | Apr | 2023 | 0.01068 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-04-13 09:50 | 2023-04-13 11:59 | 18 | 2:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50 KVA X 37.5 KVA | C23041300080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 129 | 2023-04-13 | 2322 | keep | 0 | Apr | 2023 | 0.0015815 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2023-04-13 09:50 | 2023-04-13 10:30 | 1 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR CONEXIONES EN LA SALIDA DEL TRANSFORMADOR A.A.A | A23041200134 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-04-13 | 40 | keep | 0 | Apr | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-13 10:24 | 2023-04-13 11:15 | 4 | 0:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | R23041300021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 51 | 2023-04-13 | 204 | keep | 0 | Apr | 2023 | 0.00013894 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-04-13 10:31 | 2023-04-13 10:32 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23041300093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 4634 | keep | 0 | Apr | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
MAYAGÃœEZ | 2023-04-13 10:40 | 2023-04-13 12:05 | 35 | 1:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LAS LINEAS | M23041300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-04-13 | 2975 | keep | 0 | Apr | 2023 | 0.0020263 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
UTUADO | 2023-04-13 10:58 | 2023-04-13 13:08 | 1 | 2:10 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR SE RETIRO ENREDADERA | A23041300045 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 130 | 2023-04-13 | 130 | keep | 0 | Apr | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-13 11:03 | 2023-04-13 11:04 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041300081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 2379 | keep | 0 | Apr | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BARRANQUITAS | 2023-04-13 11:06 | 2023-04-13 13:57 | 20 | 2:51 | P | PARARRAYOS DEFECTUOSO | 1X80 EN C/L SE REMOVIO PARARRAYOS VACANTE | C23041300105 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 171 | 2023-04-13 | 3420 | keep | 0 | Apr | 2023 | 0.0023293 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-13 11:18 | 2023-04-13 14:14 | 506 | 2:56 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | C23041300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 176 | 2023-04-13 | 89056 | keep | 0 | Apr | 2023 | 0.060656 | 0.00034463 | Sustained | FALSE | FALSE | Not_TMED_Event | 506
YAUCO | 2023-04-13 11:18 | 2023-04-13 15:12 | 10 | 3:54 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN XMR SE REPARO SECUNDARIA | P23041300082 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 234 | 2023-04-13 | 2340 | keep | 0 | Apr | 2023 | 0.0015938 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-13 11:31 | 2023-04-13 14:22 | 92 | 2:51 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23041300070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-04-13 | 15732 | keep | 0 | Apr | 2023 | 0.010715 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
BAYAMON | 2023-04-13 11:40 | 2023-04-13 11:57 | 178 | 0:17 | T | NO SE REPORTO CAUSA | DISPARO Y NO CERRO POR CONTROL, FAIL TO OPERATE. TAMPOCO ELECTRICAMENTE. SE CERRO MECANICAMENTE | S23041300087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-04-13 | 3026 | keep | 0 | Apr | 2023 | 0.002061 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
HUMACAO | 2023-04-13 11:49 | 2023-04-13 12:38 | 60 | 0:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO EN C/L RADIAL PARA REMPLAZAR CAJA PRIMARIA | C23041300112 | New_Event | Cutout Failure | Include | Include | Equipment | 49 | 2023-04-13 | 2940 | keep | 0 | Apr | 2023 | 0.0020024 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-04-13 11:52 | 2023-04-13 12:15 | 5069 | 0:23 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO SE LE DA PRUEBA HASTA VERIFICAR CON PERSONAL EN VIA LIBRE TRABAJANDO EN ALIMENTADOR SE CONFIRMO CON PERSONAL EN EL AREA Y SE LE DIO PRUEBA AL INTERRUPTOR QURDANDO EN SERVICIO | P23041300089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2023-04-13 | 116587 | keep | 0 | Apr | 2023 | 0.079407 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
BAYAMON | 2023-04-13 12:17 | 2023-04-13 14:58 | 10 | 2:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA AJUSTAR CONEXIONES EN PEDESTAL | B23041300075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 161 | 2023-04-13 | 1610 | keep | 0 | Apr | 2023 | 0.0010966 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-13 12:43 | 2023-04-13 17:24 | 109 | 4:41 | P | DESGANCHE | 1 X 40 EN RISER Y 1 X 50 EN C/L SE DESGANCHO | B23041300081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2023-04-13 | 30629 | keep | 0 | Apr | 2023 | 0.020861 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
GUAYAMA | 2023-04-13 12:54 | 2023-04-13 12:55 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041300109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 1945 | keep | 0 | Apr | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
FAJARDO | 2023-04-13 13:01 | 2023-04-13 14:00 | 7 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23041300036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2023-04-13 | 413 | keep | 0 | Apr | 2023 | 0.00028129 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-04-13 13:16 | 2023-04-13 17:00 | 20 | 3:44 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | R23041300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-04-13 | 4480 | keep | 0 | Apr | 2023 | 0.0030513 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-13 13:25 | 2023-04-13 15:33 | 10 | 2:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23041300180 | New_Event | Secondary Wire Break | Include | Include | Equipment | 128 | 2023-04-13 | 1280 | keep | 0 | Apr | 2023 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-13 13:27 | 2023-04-14 12:00 | 10 | 22:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARRO SECUNDARIA | S23041300101 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1353 | 2023-04-13 | 13530 | keep | 0 | Apr | 2023 | 0.0092152 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-13 13:27 | 2023-04-13 15:24 | 12 | 1:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR TRAMO SECUNDARIO APROX. 50' POSTE A POSTE | C23041300131 | New_Event | Secondary Wire Break | Include | Include | Equipment | 117 | 2023-04-13 | 1404 | keep | 0 | Apr | 2023 | 0.00095626 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-04-13 13:27 | 2023-04-13 15:50 | 3 | 2:23 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041300094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-04-13 | 429 | keep | 0 | Apr | 2023 | 0.00029219 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-04-13 13:40 | 2023-04-13 18:16 | 10 | 4:36 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO (EVENTO TRANSFERIDO DE REGION SJ) | S23041300103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2023-04-13 | 2760 | keep | 0 | Apr | 2023 | 0.0018798 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-13 13:41 | 2023-04-13 17:44 | 1 | 4:03 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L SE RETESO LINEAS | P23041300121 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 243 | 2023-04-13 | 243 | keep | 0 | Apr | 2023 | 0.00016551 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-13 13:45 | 2023-04-13 15:01 | 15 | 1:16 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | C23041300134 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-04-13 | 1140 | keep | 0 | Apr | 2023 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-13 13:56 | 2023-04-13 15:17 | 10 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C23041300135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2023-04-13 | 810 | keep | 0 | Apr | 2023 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-13 14:04 | 2023-04-13 16:37 | 16 | 2:33 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | R23041300040 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-04-13 | 2448 | keep | 0 | Apr | 2023 | 0.0016673 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-04-13 14:06 | 2023-04-13 15:18 | 1 | 1:12 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO DE XMRS | C23041300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2023-04-13 | 72 | keep | 0 | Apr | 2023 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-13 14:10 | 2023-04-13 18:40 | 60 | 4:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE SE REMPLAZO AISLADORES ROTOS | M23041300068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 270 | 2023-04-13 | 16200 | keep | 0 | Apr | 2023 | 0.011034 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-04-13 14:10 | 2023-04-13 14:30 | 1 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A23041300013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-04-13 | 20 | keep | 0 | Apr | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-13 14:12 | 2023-04-13 15:40 | 5 | 1:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23041300041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 88 | 2023-04-13 | 440 | keep | 0 | Apr | 2023 | 0.00029968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-04-13 14:20 | 2023-04-13 14:40 | 1 | 0:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B23041300110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2023-04-13 | 20 | keep | 0 | Apr | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-13 14:29 | 2023-04-13 17:58 | 13 | 3:29 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | S23041300111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-04-13 | 2717 | keep | 0 | Apr | 2023 | 0.0018505 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-04-13 14:35 | 2023-04-13 18:44 | 10 | 4:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZAR BAJANTE Y CONECTORES SECUNDARIOS | S23041300113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 249 | 2023-04-13 | 2490 | keep | 0 | Apr | 2023 | 0.0016959 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-13 14:47 | 2023-04-13 18:28 | 5 | 3:41 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | P23041300124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2023-04-13 | 1105 | keep | 0 | Apr | 2023 | 0.00075261 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-04-13 14:59 | 2023-04-13 17:09 | 1 | 2:10 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23041300151 | New_Event | Animals | Include | Include | Wildlife | 130 | 2023-04-13 | 130 | keep | 0 | Apr | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-13 15:09 | 2023-04-13 17:08 | 15 | 1:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO TRAMO PARA REEMPLAZAR 2 AISLADORES CON SJ-230413-50 | R23041300049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 119 | 2023-04-13 | 1785 | keep | 0 | Apr | 2023 | 0.0012158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-04-13 15:25 | 2023-04-13 18:40 | 80 | 3:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041300080 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2023-04-13 | 15600 | keep | 0 | Apr | 2023 | 0.010625 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-04-13 15:33 | 2023-04-13 15:34 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23041300088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 312 | keep | 0 | Apr | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-04-13 15:35 | 2023-04-13 15:52 | 10 | 0:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23041300128 | New_Event | Secondary Wire Break | Include | Include | Equipment | 17 | 2023-04-13 | 170 | keep | 0 | Apr | 2023 | 0.00011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-13 15:45 | 2023-04-14 14:30 | 4 | 22:45 | P | ANIMAL | 2 X 5 EN TRANSFORMADOR AVE CRUZO CAJAS | M23041300092 | New_Event | Animals | Include | Include | Wildlife | 1365 | 2023-04-13 | 5460 | keep | 0 | Apr | 2023 | 0.0037188 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2023-04-13 16:10 | 2023-04-13 16:58 | 1 | 0:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23041300151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-04-13 | 48 | keep | 0 | Apr | 2023 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-13 16:25 | 2023-04-13 19:42 | 25 | 3:17 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23041300101 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 197 | 2023-04-13 | 4925 | keep | 0 | Apr | 2023 | 0.0033544 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-13 16:43 | 2023-04-13 18:30 | 80 | 1:47 | P | CABLE SOTERRADO AVERIADO | 2 X 80 EN CORTE DE LINEA SE SECCIONALIZO RISER AVERIADO | M23041300107 | New_Event | UG Cable Fault | Include | Include | Equipment | 107 | 2023-04-13 | 8560 | keep | 0 | Apr | 2023 | 0.0058302 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-04-13 17:13 | 2023-04-13 18:11 | 70 | 0:58 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23041300171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-04-13 | 4060 | keep | 0 | Apr | 2023 | 0.0027652 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-04-13 17:17 | 2023-04-13 17:19 | 1494 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE BKR SPARE QUE LLEVA 30% DEL 1336-06 Y LLEVA 50% 1619-03 SE CERRO POR CONTROL | R2304130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-13 | 2988 | keep | 0 | Apr | 2023 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
CANOVANAS | 2023-04-13 17:17 | 2023-04-13 17:19 | 2531 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR SPARE QUE LLEVA 30% DEL 1336-06 Y LLEVA 50% 1619-03 SE CERRO POR CONTROL | R2304130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-13 | 5062 | keep | 0 | Apr | 2023 | 0.0034477 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
SAN JUAN | 2023-04-13 17:21 | 2023-04-13 21:35 | 1 | 4:14 | P | NO SE REPORTO CAUSA | 1 X 40 ENTRADA DE RISER 1 X 25 SALIDA DE RISER | S23041300141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 254 | 2023-04-13 | 254 | keep | 0 | Apr | 2023 | 0.000173 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-13 17:24 | 2023-04-14 11:55 | 1 | 18:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23041300126 | New_Event | Cutout Failure | Include | Include | Equipment | 1111 | 2023-04-13 | 1111 | keep | 0 | Apr | 2023 | 0.0007567 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-13 18:01 | 2023-04-13 22:15 | 181 | 4:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN AEREO PROVISIONAL SE REEMPLAZO CAJA PRIMARIA QUEMADA | B23041300130 | New_Event | Cutout Failure | Include | Include | Equipment | 254 | 2023-04-13 | 45974 | keep | 0 | Apr | 2023 | 0.031313 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
BAYAMON | 2023-04-13 18:09 | 2023-04-13 18:17 | 1588 | 0:08 | T | ALIMENTADOR AMARRADO | CARGA POR 1716-03 SE SECCIONALIZO CONDUCTOR SAFADO DE AISLADOR | B23041300144 | New_Event | Feeder Load Transferred | Include | Include | Other | 8 | 2023-04-13 | 12704 | keep | 0 | Apr | 2023 | 0.0086526 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-13 18:09 | 2023-04-13 18:17 | 13 | 0:08 | T | ALIMENTADOR AMARRADO | CARGA POR 1716-03 SE SECCIONALIZO CONDUCTOR SAFADO DE AISLADOR | B23041300144 | New_Event | Feeder Load Transferred | Include | Include | Other | 8 | 2023-04-13 | 104 | keep | 0 | Apr | 2023 | 7.0834e-05 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-13 18:09 | 2023-04-13 18:17 | 1812 | 0:08 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR SAFADO DE AISLADOR BY-230412-01 LLEVA LA CARGA DEL 1711-1 Y 1711-03 | B23041300144 | New_Event | Primary Wire Break | Include | Include | Equipment | 8 | 2023-04-13 | 14496 | keep | 0 | Apr | 2023 | 0.0098732 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2023-04-13 18:17 | 2023-04-13 21:10 | 15 | 2:53 | P | CONDUCTOR ROTO O ABIERTO | MEDIANTE GOI BY-230412-01 SE LLEVO LINEA SAFADA DE AISLADOR A SU LUGAR | B23041300144 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 173 | 2023-04-13 | 2595 | keep | 0 | Apr | 2023 | 0.0017674 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-13 18:26 | 2023-04-14 10:07 | 8 | 15:41 | P | DESGANCHE | 1 X 10 EN XMR Y DESGANCHE | B23041300162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 941 | 2023-04-13 | 7528 | keep | 0 | Apr | 2023 | 0.0051273 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-13 18:28 | 2023-04-14 14:29 | 6 | 20:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5KVA | B23041300170 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1201 | 2023-04-13 | 7206 | keep | 0 | Apr | 2023 | 0.004908 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-04-13 18:31 | 2023-04-13 18:58 | 3 | 0:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23041300065 | New_Event | Primary Wire Break | Include | Include | Equipment | 27 | 2023-04-13 | 81 | keep | 0 | Apr | 2023 | 5.5169e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-04-13 18:55 | 2023-04-13 18:56 | 45 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1303-05 CERRADO POR CONTROL LLEVA 98% DEL 1303-04 | S23041300152 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-13 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-04-13 18:55 | 2023-04-13 18:56 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 CERRADO POR CONTROL LLEVA 98% DEL 1303-04 | S23041300152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 870 | keep | 0 | Apr | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
PONCE | 2023-04-13 19:11 | 2023-04-14 06:28 | 10 | 11:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | CONEXIONES EN SECUNDARIA 1 X 10 EN TRANSFORMADOR | P23041300168 | New_Event | Secondary Wire Break | Include | Include | Equipment | 677 | 2023-04-13 | 6770 | keep | 0 | Apr | 2023 | 0.004611 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-13 19:13 | 2023-04-14 10:48 | 14 | 15:35 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO DE 25KVA SE ABRIRA CORTE DE LINEA PARA REMPLAZARLO YA QUE EL TRABAJO ES TRASPATIO Y ES A ESPUELAS | A23041300119 | New_Event | Service Transformer Failure | Include | Include | Equipment | 935 | 2023-04-13 | 13090 | keep | 0 | Apr | 2023 | 0.0089155 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-04-13 19:14 | 2023-04-13 19:49 | 7 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN XMR Y SE REPARO PUENTE PRIMARIO | C23041300190 | New_Event | Primary Wire Break | Include | Include | Equipment | 35 | 2023-04-13 | 245 | keep | 0 | Apr | 2023 | 0.00016687 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-04-13 20:05 | 2023-04-14 00:30 | 1825 | 4:25 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO INTERRUPTOR NO CERRO POR CONTROL NI MANUAL POSIBLE BOBINA DE CIERRE QUEMADA | M23041300164 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 265 | 2023-04-13 | 483625 | keep | 0 | Apr | 2023 | 0.32939 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
YAUCO | 2023-04-13 20:11 | 2023-04-13 22:16 | 50 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO VIENTOS | P23041300184 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-04-13 | 6250 | keep | 0 | Apr | 2023 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-13 20:29 | 2023-04-13 20:30 | 1474 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL BKR SE CERRO X CONTROL | R23041300069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 1474 | keep | 0 | Apr | 2023 | 0.0010039 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
CANOVANAS | 2023-04-13 20:35 | 2023-04-13 22:47 | 63 | 2:12 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN RISER CON EL SF SJ-230413-51 SE CORRIO N/O POR AISLADOR QUEMADO EN EL SU - 2 | R23041300070 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 132 | 2023-04-13 | 8316 | keep | 0 | Apr | 2023 | 0.005664 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2023-04-13 21:10 | 2023-04-14 14:09 | 25 | 16:59 | P | CABLE SOTERRADO AVERIADO | SJ-230414-01 SE SECCIONALIZO TRAMO AVERIA SOTERRADA DEL T-8 @ T-7 | S23041300188 | New_Event | UG Cable Fault | Include | Include | Equipment | 1019 | 2023-04-13 | 25475 | keep | 0 | Apr | 2023 | 0.017351 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-04-13 21:20 | 2023-04-13 23:18 | 53 | 1:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L FUERTES LLUVIAS | R23041300072 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 118 | 2023-04-13 | 6254 | keep | 0 | Apr | 2023 | 0.0042596 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
YAUCO | 2023-04-13 21:20 | 2023-04-14 09:09 | 20 | 11:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P23041300190 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 709 | 2023-04-13 | 14180 | keep | 0 | Apr | 2023 | 0.0096579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-04-13 21:21 | 2023-04-14 09:35 | 60 | 12:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA QUEMADA | C23041300198 | New_Event | Cutout Failure | Include | Include | Equipment | 734 | 2023-04-13 | 44040 | keep | 0 | Apr | 2023 | 0.029995 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-04-13 21:26 | 2023-04-13 21:27 | 2071 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23041300124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 2071 | keep | 0 | Apr | 2023 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2023-04-13 21:31 | 2023-04-13 21:32 | 2071 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23041300125 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-13 | 2071 | keep | 0 | Apr | 2023 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
UTUADO | 2023-04-13 21:45 | 2023-04-14 10:00 | 8 | 12:15 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23041300127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 735 | 2023-04-13 | 5880 | keep | 0 | Apr | 2023 | 0.0040048 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-04-13 22:01 | 2023-04-14 10:10 | 40 | 12:09 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA REQUIERE DESGANCHE | M23041300190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 729 | 2023-04-13 | 29160 | keep | 0 | Apr | 2023 | 0.019861 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-13 23:39 | 2023-04-14 09:59 | 90 | 10:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y 1 X 100 EN C/L | B23041300236 | New_Event | Cutout Failure | Include | Include | Equipment | 620 | 2023-04-13 | 55800 | keep | 0 | Apr | 2023 | 0.038005 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2023-04-14 01:03 | 2023-04-14 12:30 | 50 | 11:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041400001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 687 | 2023-04-14 | 34350 | keep | 0 | Apr | 2023 | 0.023396 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-14 01:55 | 2023-04-14 09:10 | 149 | 7:15 | P | DESGANCHE | 1 X 100 1 X 30 Y 1 X 50 EN C/L DESGANCHE | R23041400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 435 | 2023-04-14 | 64815 | keep | 0 | Apr | 2023 | 0.044145 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
MAYAGÃœEZ | 2023-04-14 03:00 | 2023-04-14 13:51 | 75 | 10:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M23041400003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 651 | 2023-04-14 | 48825 | keep | 0 | Apr | 2023 | 0.033254 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2023-04-14 03:29 | 2023-04-14 09:00 | 80 | 5:31 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23041400010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2023-04-14 | 26480 | keep | 0 | Apr | 2023 | 0.018035 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-04-14 04:00 | 2023-04-14 12:00 | 300 | 8:00 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 Y 3 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA AVERIADA | M23041400016 | New_Event | Primary Wire Break | Include | Include | Equipment | 480 | 2023-04-14 | 144000 | keep | 0 | Apr | 2023 | 0.098078 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-04-14 04:35 | 2023-04-14 10:00 | 40 | 5:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23041400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2023-04-14 | 13000 | keep | 0 | Apr | 2023 | 0.0088542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-04-14 04:35 | 2023-04-14 11:07 | 215 | 6:32 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR DESGANCHE | M23041400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 392 | 2023-04-14 | 84280 | keep | 0 | Apr | 2023 | 0.057403 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
PONCE | 2023-04-14 05:10 | 2023-04-14 07:48 | 150 | 2:38 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA DESGANCHE | P23041400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-04-14 | 23700 | keep | 0 | Apr | 2023 | 0.016142 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2023-04-14 06:23 | 2023-04-14 10:30 | 12 | 4:07 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR DE 37.5KVA A 7620 POR UNO MISMA CAPACIDAD | P23041400028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 247 | 2023-04-14 | 2964 | keep | 0 | Apr | 2023 | 0.0020188 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-14 06:36 | 2023-04-14 10:06 | 100 | 3:30 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | S23041400014 | New_Event | Animals | Include | Include | Wildlife | 210 | 2023-04-14 | 21000 | keep | 0 | Apr | 2023 | 0.014303 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-14 06:44 | 2023-04-14 09:36 | 10 | 2:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | B23041400011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 172 | 2023-04-14 | 1720 | keep | 0 | Apr | 2023 | 0.0011715 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-14 07:35 | 2023-04-15 09:07 | 24 | 25:32 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE INSTALO CORTE DE LINEA NUEVO Y SE LEVANTO NEUTRAL PRIMARIO Y SE CAMBIO AISLACION | P23041400034 | New_Event | Primary Wire Break | Include | Include | Equipment | 1532 | 2023-04-14 | 36768 | keep | 0 | Apr | 2023 | 0.025043 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-04-14 07:53 | 2023-04-14 13:18 | 181 | 5:25 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23041400014 | New_Event | Animals | Include | Include | Wildlife | 325 | 2023-04-14 | 58825 | keep | 0 | Apr | 2023 | 0.040065 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
CANOVANAS | 2023-04-14 07:55 | 2023-04-14 11:34 | 40 | 3:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | R23041400018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2023-04-14 | 8760 | keep | 0 | Apr | 2023 | 0.0059664 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-14 08:15 | 2023-04-14 15:25 | 14 | 7:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 15KVA AVERIADO X UNO 25 KVA | C23041400007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 430 | 2023-04-14 | 6020 | keep | 0 | Apr | 2023 | 0.0041002 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2023-04-14 08:16 | 2023-04-14 11:59 | 40 | 3:43 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | P23041400051 | New_Event | Primary Wire Break | Include | Include | Equipment | 223 | 2023-04-14 | 8920 | keep | 0 | Apr | 2023 | 0.0060754 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-04-14 08:25 | 2023-04-14 09:15 | 15 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23041300176 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-04-14 | 750 | keep | 0 | Apr | 2023 | 0.00051082 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-04-14 08:28 | 2023-04-14 13:13 | 100 | 4:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA POR LLUVIAS | M23041400049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 285 | 2023-04-14 | 28500 | keep | 0 | Apr | 2023 | 0.019411 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-04-14 08:28 | 2023-04-14 12:15 | 80 | 3:47 | P | DESGANCHE | 1 X 30 EN CONVERTIDOR SE RETIRO BAMBUS DE LAS LINEAS | A23041400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-04-14 | 18160 | keep | 0 | Apr | 2023 | 0.012369 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-04-14 08:45 | 2023-04-14 10:09 | 10 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE SECUNDARIA SULFATADA | C23041400012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-04-14 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-14 08:59 | 2023-04-14 09:28 | 6 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE Y LINEA SECUNDARIA | R23041400001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-04-14 | 174 | keep | 0 | Apr | 2023 | 0.00011851 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-14 09:01 | 2023-04-14 13:40 | 50 | 4:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A23041400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2023-04-14 | 13950 | keep | 0 | Apr | 2023 | 0.0095013 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-04-14 09:02 | 2023-04-14 09:21 | 55 | 0:19 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L MAQUINA EXCAVADORA SACUDIO LAS LINEAS | R23041400031 | New_Event | Damage From Public | Include | Include | Public | 19 | 2023-04-14 | 1045 | keep | 0 | Apr | 2023 | 0.00071174 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
SAN JUAN | 2023-04-14 09:09 | 2023-04-14 11:00 | 1 | 1:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO TOMAS QUEMADAS | S23041200179 | New_Event | Secondary Wire Break | Include | Include | Equipment | 111 | 2023-04-14 | 111 | keep | 0 | Apr | 2023 | 7.5602e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-14 09:22 | 2023-04-14 13:50 | 50 | 4:28 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M23041400078 | New_Event | Primary Wire Break | Include | Include | Equipment | 268 | 2023-04-14 | 13400 | keep | 0 | Apr | 2023 | 0.0091267 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-14 09:30 | 2023-04-14 14:57 | 10 | 5:27 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR Y SE REPARO SECUNDARIA Y SE DEJO CLIENTE FUERA POR TOMA AVERIADA | S23041400034 | New_Event | Customer-Related Interruption | Include | Include | Public | 327 | 2023-04-14 | 3270 | keep | 0 | Apr | 2023 | 0.0022272 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-04-14 09:40 | 2023-04-14 10:52 | 1475 | 1:12 | T | NO SE REPORTO CAUSA | SE ENCONTRO INTERRUPTOR ABIERTO YA QUE NO HAY RTU Y SE CERRO MANUALMENTE | P23041400091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2023-04-14 | 106200 | keep | 0 | Apr | 2023 | 0.072332 | 0.0010046 | Sustained | FALSE | FALSE | Not_TMED_Event | 1475
HUMACAO | 2023-04-14 09:44 | 2023-04-14 13:30 | 1074 | 3:46 | P | ANIMAL | SE CERRO PB-G ABIERTO SE RETIRO LAGARTO SOBRE LINEAS | C23041400025 | New_Event | Animals | Include | Include | Wildlife | 226 | 2023-04-14 | 242724 | keep | 0 | Apr | 2023 | 0.16532 | 0.0007315 | Sustained | FALSE | FALSE | Not_TMED_Event | 1074
SAN JUAN | 2023-04-14 09:54 | 2023-04-14 09:55 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2304140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-14 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-04-14 09:54 | 2023-04-14 18:00 | 50 | 8:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041400096 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 486 | 2023-04-14 | 24300 | keep | 0 | Apr | 2023 | 0.016551 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-14 10:00 | 2023-04-14 13:38 | 14 | 3:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REMPLAZO AISLADOR | R23041400040 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 218 | 2023-04-14 | 3052 | keep | 0 | Apr | 2023 | 0.0020787 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-04-14 10:03 | 2023-04-14 12:33 | 7 | 2:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZARON DISCOS PARTIDOS | C23041400043 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 150 | 2023-04-14 | 1050 | keep | 0 | Apr | 2023 | 0.00071515 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2023-04-14 10:06 | 2023-04-14 10:07 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-14 | 4132 | keep | 0 | Apr | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2023-04-14 10:18 | 2023-04-14 12:19 | 1 | 2:01 | P | PROBLEMA DEL CLIENTE | SE DEJA ABIERTO Y TAGEADO EN FID 1001322953 BOMBAS AES | P23041400086 | New_Event | Customer-Related Interruption | Include | Include | Public | 121 | 2023-04-14 | 121 | keep | 0 | Apr | 2023 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-14 10:48 | 2023-04-14 15:17 | 250 | 4:29 | P | TRANSFORMADOR AVERIADO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR TRANSFORMADOR DE 37.5 KVA POR 37.5 KVA YA QUE EL TRABAJO ES TRASPATIO Y A ESPUELAS | A23041400042 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 269 | 2023-04-14 | 67250 | keep | 0 | Apr | 2023 | 0.045804 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-04-14 10:57 | 2023-04-14 12:28 | 1 | 1:31 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23041400061 | New_Event | Animals | Include | Include | Wildlife | 91 | 2023-04-14 | 91 | keep | 0 | Apr | 2023 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-14 10:57 | 2023-04-14 16:30 | 40 | 5:33 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE RETIRO PARARRAYO | A23041400043 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 333 | 2023-04-14 | 13320 | keep | 0 | Apr | 2023 | 0.0090722 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-14 11:01 | 2023-04-14 12:30 | 6 | 1:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE BAJO TAP DEL 4 AL 2 123V POR FASE | S23041400053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 89 | 2023-04-14 | 534 | keep | 0 | Apr | 2023 | 0.0003637 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-14 11:08 | 2023-04-14 14:52 | 6 | 3:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X 10 EN XMR Y SE REEMPLAZO CAJA | C23041400068 | New_Event | Cutout Failure | Include | Include | Equipment | 224 | 2023-04-14 | 1344 | keep | 0 | Apr | 2023 | 0.00091539 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-04-14 11:24 | 2023-04-14 12:15 | 1 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO NEUTRAL DE TRANSFORMADOR Y FUSIBLE NO CERRADO CORRECTAMENTE | P23041400106 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2023-04-14 | 51 | keep | 0 | Apr | 2023 | 3.4736e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-14 12:04 | 2023-04-14 14:35 | 15 | 2:31 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | M23041400156 | New_Event | Animals | Include | Include | Wildlife | 151 | 2023-04-14 | 2265 | keep | 0 | Apr | 2023 | 0.0015427 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-14 12:20 | 2023-04-14 14:53 | 4 | 2:33 | P | ANIMAL | 1 X 8 EN XMR CRUCE X AVE | C23041400089 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-04-14 | 612 | keep | 0 | Apr | 2023 | 0.00041683 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-04-14 12:31 | 2023-04-14 17:37 | 6 | 5:06 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR Y DESGANCHE SECUNDARIO | C23041400097 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 306 | 2023-04-14 | 1836 | keep | 0 | Apr | 2023 | 0.0012505 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-04-14 12:43 | 2023-04-14 13:20 | 8 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23041400055 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-04-14 | 296 | keep | 0 | Apr | 2023 | 0.0002016 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-04-14 12:53 | 2023-04-14 15:31 | 80 | 2:38 | P | ANIMAL | 1 X 65 C/L CRUCE POR AVE | R23041400067 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-04-14 | 12640 | keep | 0 | Apr | 2023 | 0.008609 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-14 13:01 | 2023-04-14 15:06 | 25 | 2:05 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L SE REPORTA FUERTES LLUVIA | B23041400061 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 125 | 2023-04-14 | 3125 | keep | 0 | Apr | 2023 | 0.0021284 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-04-14 13:01 | 2023-04-14 14:40 | 100 | 1:39 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23041400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-04-14 | 9900 | keep | 0 | Apr | 2023 | 0.0067428 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-04-14 13:02 | 2023-04-14 16:50 | 5 | 3:48 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-04-14 | 1140 | keep | 0 | Apr | 2023 | 0.00077645 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-04-14 13:06 | 2023-04-14 15:00 | 10 | 1:54 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 30 EN TRANSFORMADOR CUCE DE BARRA EN PEDESTAL | P23041400127 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 114 | 2023-04-14 | 1140 | keep | 0 | Apr | 2023 | 0.00077645 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-14 13:09 | 2023-04-14 13:37 | 9 | 0:28 | P | CAUSAS EXTERNAS | CAMION IMPACTO PM SE ABRIO T-19 PARA ACOMODAR EL MISMO | S23041400080 | New_Event | Damage From Public | Include | Include | Public | 28 | 2023-04-14 | 252 | keep | 0 | Apr | 2023 | 0.00017164 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-04-14 13:16 | 2023-04-14 14:51 | 32 | 1:35 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | R23041400071 | New_Event | Animals | Include | Include | Wildlife | 95 | 2023-04-14 | 3040 | keep | 0 | Apr | 2023 | 0.0020705 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
VEGA BAJA | 2023-04-14 13:27 | 2023-04-15 15:57 | 10 | 26:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 15 KVA POR UNO DE 25 KVA | A23041400064 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1590 | 2023-04-14 | 15900 | keep | 0 | Apr | 2023 | 0.010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-14 13:38 | 2023-04-14 14:46 | 1 | 1:08 | P | NO SE REPORTO CAUSA | 1X10 DE RISER @ T-2 | R23041400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2023-04-14 | 68 | keep | 0 | Apr | 2023 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-14 13:51 | 2023-04-14 16:00 | 60 | 2:09 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO | A23041400071 | New_Event | Primary Wire Break | Include | Include | Equipment | 129 | 2023-04-14 | 7740 | keep | 0 | Apr | 2023 | 0.0052717 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-14 14:09 | 2023-04-14 14:10 | 138 | 0:01 | P | ALIMENTADOR AMARRADO | 10% POR 1206-04 HACIENDO PRUEBA EN RISER PROBO MALO Y RECERRO EL ALIMENTADOR 1206-04 | S2304140000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-14 | 138 | keep | 0 | Apr | 2023 | 9.3991e-05 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-04-14 14:09 | 2023-04-14 14:10 | 1977 | 0:01 | P | ALIMENTADOR AMARRADO | 40% POR 1206-04 HACIENDO PRUEBA EN RISER PROBO MALO Y RECERRO EL ALIMENTADOR 1206-04 | S2304140000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-14 | 1977 | keep | 0 | Apr | 2023 | 0.0013465 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-04-14 14:09 | 2023-04-14 14:10 | 1799 | 0:01 | T | CABLE SOTERRADO AVERIADO | LLEVA 10% 1204-03 LLEVA 40% 1204-04 HACIENDO PRUEBA EN RISER PROBO MALO Y RECERRO EL ALIMENTADOR 1206-04 | S2304140000X | Additional_clients | UG Cable Fault | Include | Include | Equipment | 1 | 2023-04-14 | 1799 | keep | 0 | Apr | 2023 | 0.0012253 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-14 14:10 | 2023-04-14 17:59 | 25 | 3:49 | P | CABLE SOTERRADO AVERIADO | SJ-230414-01 SE SECCIONALIZO TRAMO AVERIA SOTERRADA DEL T-8 @ T-7 | S23041300188 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 229 | 2023-04-14 | 5725 | keep | 0 | Apr | 2023 | 0.0038993 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-04-14 14:24 | 2023-04-14 16:53 | 1 | 2:29 | P | ANIMAL | 2 X 25 EN CORTE DE LINEA Y 2 X 20 EN RISER CRUCE POR AVE. | C23041400145 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-04-14 | 149 | keep | 0 | Apr | 2023 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-14 14:26 | 2023-04-14 15:51 | 10 | 1:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 50 KVA X 50 KVA | R23041400077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 85 | 2023-04-14 | 850 | keep | 0 | Apr | 2023 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-14 14:28 | 2023-04-14 15:52 | 4 | 1:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON BAJANTES SECUNDARIOS | C23041400146 | New_Event | Secondary Wire Break | Include | Include | Equipment | 84 | 2023-04-14 | 336 | keep | 0 | Apr | 2023 | 0.00022885 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-04-14 14:32 | 2023-04-14 15:15 | 10 | 0:43 | P | DESGANCHE | SE FIJO BAJANTE PRIMARIO EN TRANSFORMADOR | P23041400139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2023-04-14 | 430 | keep | 0 | Apr | 2023 | 0.00029287 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-14 14:37 | 2023-04-14 16:40 | 60 | 2:03 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23041400190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-04-14 | 7380 | keep | 0 | Apr | 2023 | 0.0050265 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-04-14 14:37 | 2023-04-14 18:10 | 50 | 3:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041400085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-04-14 | 10650 | keep | 0 | Apr | 2023 | 0.0072537 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-14 14:50 | 2023-04-14 21:30 | 350 | 6:40 | P | DESGANCHE | 1 X100 EN C/L Y 2 X 80 EN C/L, SE RETIRO ARBOL Y SE LEVANTARON 3 CONDUCTORES PRIMARIOS | C23041400152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2023-04-14 | 140000 | keep | 0 | Apr | 2023 | 0.095353 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
AGUADILLA | 2023-04-14 14:52 | 2023-04-14 17:45 | 60 | 2:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTE | M23041400195 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 173 | 2023-04-14 | 10380 | keep | 0 | Apr | 2023 | 0.0070698 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-04-14 14:54 | 2023-04-14 14:56 | 2483 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR UN SOLO RECIERRE SE CERRO POR SCADA NO SE REPORTO CAUSA | M23041400197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-14 | 4966 | keep | 0 | Apr | 2023 | 0.0033823 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
GUAYAMA | 2023-04-14 15:16 | 2023-04-14 16:40 | 34 | 1:24 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA FASES CRUZADAS | P23041400144 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 84 | 2023-04-14 | 2856 | keep | 0 | Apr | 2023 | 0.0019452 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
GUAYAMA | 2023-04-14 15:16 | 2023-04-14 18:52 | 10 | 3:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO CAJA PRIMARIA | P23041400153 | New_Event | Cutout Failure | Include | Include | Equipment | 216 | 2023-04-14 | 2160 | keep | 0 | Apr | 2023 | 0.0014712 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-14 15:24 | 2023-04-14 16:31 | 30 | 1:07 | P | ANIMAL | 1 X 25 EN C/L SE RETIRO AVE | B23041400089 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-04-14 | 2010 | keep | 0 | Apr | 2023 | 0.001369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-14 15:30 | 2023-04-14 15:31 | 2302 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23041400164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-14 | 2302 | keep | 0 | Apr | 2023 | 0.0015679 | 0.0015679 | Momentary | FALSE | FALSE | Not_TMED_Event | 2302
CAGUAS | 2023-04-14 15:38 | 2023-04-14 16:10 | 1 | 0:32 | P | NO SE REPORTO CAUSA | 1 X 20 EN BANCO XMR | C23041400165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 32 | 2023-04-14 | 32 | keep | 0 | Apr | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-14 15:46 | 2023-04-14 16:19 | 80 | 0:33 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR PRIMARIO MEDIANTE G.O.I. SJ-230413-51 | R23041400082 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 33 | 2023-04-14 | 2640 | keep | 0 | Apr | 2023 | 0.0017981 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-14 16:12 | 2023-04-14 17:11 | 2 | 0:59 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR SE REMPLAZO XMR 37.5KVA X 37.5KVA | R23041400086 | New_Event | Service Transformer Failure | Include | Include | Equipment | 59 | 2023-04-14 | 118 | keep | 0 | Apr | 2023 | 8.0369e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-04-14 17:23 | 2023-04-14 19:00 | 150 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041400213 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2023-04-14 | 14550 | keep | 0 | Apr | 2023 | 0.0099099 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-14 17:24 | 2023-04-15 16:23 | 6 | 22:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABIRO XMR PARA REMPLAZAR SECUNDARIA | S23041400105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1379 | 2023-04-14 | 8274 | keep | 0 | Apr | 2023 | 0.0056354 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-14 17:43 | 2023-04-14 19:27 | 10 | 1:44 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR PARA REMPLAZO BUSHIN SECUNDARIO 127/254 | S23041400107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 104 | 2023-04-14 | 1040 | keep | 0 | Apr | 2023 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-14 17:47 | 2023-04-14 18:45 | 80 | 0:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23041400226 | New_Event | Cutout Failure | Include | Include | Equipment | 58 | 2023-04-14 | 4640 | keep | 0 | Apr | 2023 | 0.0031603 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-14 17:50 | 2023-04-14 19:41 | 30 | 1:51 | P | SOBRECARGA | 1 X 40 EN C/L POR CARGA | B23041400099 | New_Event | Trip Due To Overload | Include | Include | Other | 111 | 2023-04-14 | 3330 | keep | 0 | Apr | 2023 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-04-14 17:54 | 2023-04-14 21:39 | 6 | 3:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR TRAMO SECUNDARIO EN VARIOS PUNTOS | R23041400091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 225 | 2023-04-14 | 1350 | keep | 0 | Apr | 2023 | 0.00091948 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-14 17:56 | 2023-04-15 09:23 | 25 | 15:27 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN RISER Y 1 X 25 EN CORTE DE LINEA SE RETIRO PARARRAYOS CRUZADO | M23041400228 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 927 | 2023-04-14 | 23175 | keep | 0 | Apr | 2023 | 0.015784 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-14 18:04 | 2023-04-14 19:40 | 60 | 1:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23041400232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-04-14 | 5760 | keep | 0 | Apr | 2023 | 0.0039231 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-14 18:52 | 2023-04-15 08:52 | 51 | 14:00 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | S23041400111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 840 | 2023-04-14 | 42840 | keep | 0 | Apr | 2023 | 0.029178 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
VEGA BAJA | 2023-04-14 19:08 | 2023-04-15 09:10 | 9 | 14:02 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23041400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2023-04-14 | 7578 | keep | 0 | Apr | 2023 | 0.0051613 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2023-04-14 19:20 | 2023-04-15 09:03 | 20 | 13:43 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | P23041400164 | New_Event | Animals | Include | Include | Wildlife | 823 | 2023-04-14 | 16460 | keep | 0 | Apr | 2023 | 0.011211 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-14 19:54 | 2023-04-14 23:25 | 100 | 3:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041400241 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 211 | 2023-04-14 | 21100 | keep | 0 | Apr | 2023 | 0.014371 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-04-14 20:07 | 2023-04-15 16:10 | 7 | 20:03 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | A23041400117 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 1203 | 2023-04-14 | 8421 | keep | 0 | Apr | 2023 | 0.0057355 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-04-14 22:32 | 2023-04-15 11:01 | 150 | 12:29 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23041400254 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 749 | 2023-04-14 | 112350 | keep | 0 | Apr | 2023 | 0.076521 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-04-14 22:57 | 2023-04-15 16:15 | 10 | 17:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23041400266 | New_Event | Primary Wire Break | Include | Include | Equipment | 1038 | 2023-04-14 | 10380 | keep | 0 | Apr | 2023 | 0.0070698 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-15 00:28 | 2023-04-15 11:23 | 24 | 10:55 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23041500001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 655 | 2023-04-15 | 15720 | keep | 0 | Apr | 2023 | 0.010707 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-04-15 01:06 | 2023-04-15 01:08 | 271 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | S23041500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-15 | 542 | keep | 0 | Apr | 2023 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2023-04-15 02:03 | 2023-04-15 02:04 | 2106 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R23041500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 2106 | keep | 0 | Apr | 2023 | 0.0014344 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
VEGA BAJA | 2023-04-15 02:06 | 2023-04-15 02:08 | 2468 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL LLEVA EL 9101-04 | B23041500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-15 | 4936 | keep | 0 | Apr | 2023 | 0.0033619 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-04-15 02:06 | 2023-04-15 02:08 | 1494 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL 9101-03 | B23041500001 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-15 | 2988 | keep | 0 | Apr | 2023 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
BAYAMON | 2023-04-15 02:33 | 2023-04-15 02:34 | 2926 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23041500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 2926 | keep | 0 | Apr | 2023 | 0.0019929 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
YAUCO | 2023-04-15 02:36 | 2023-04-15 08:37 | 179 | 6:01 | T | NO SE REPORTO CAUSA | JOSE COLLADO PATRULLO EL ALIMENTADOR E INSPECCIONO TODO EN LA SUBESTACION Y NO ENCONTRO CAUSA PARA EL DISPARO SE LE HIZO UNA PRUEBA Y QUEDO EN SERVICIO | M23041500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 361 | 2023-04-15 | 64619 | keep | 0 | Apr | 2023 | 0.044012 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
GUAYAMA | 2023-04-15 02:52 | 2023-04-15 02:53 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 449 | keep | 0 | Apr | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
CANOVANAS | 2023-04-15 02:53 | 2023-04-15 02:54 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23041500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-04-15 02:54 | 2023-04-15 05:34 | 150 | 2:40 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | R23041500003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 160 | 2023-04-15 | 24000 | keep | 0 | Apr | 2023 | 0.016346 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-04-15 03:42 | 2023-04-15 05:14 | 1494 | 1:32 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR SE ABRIO MACHETES PARA SECCIONALIZAR ALIMENTADOR, EN SERVICIO 90% DE 1494 CLIENTES DEL 1336-06 FALTA 50% DEL 1619-03 Y 10% DEL 1336-06 | R23041500032 | New_Event | Feeder Load Transferred | Include | Include | Other | 92 | 2023-04-15 | 137448 | keep | 0 | Apr | 2023 | 0.093615 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
CANOVANAS | 2023-04-15 03:46 | 2023-04-15 08:11 | 2179 | 4:25 | T | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR | R23041500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-04-15 | 577435 | keep | 0 | Apr | 2023 | 0.39329 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2023-04-15 04:13 | 2023-04-15 05:21 | 681 | 1:08 | T | DESGANCHE | SJ-230415-01 SE SECCIONALIZO PARA QUE COMPAÃ‘IA PRIVADA REALIZARA DESGANCHE 85% EN SERVICIO | S23041500003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-04-15 | 46308 | keep | 0 | Apr | 2023 | 0.03154 | 0.00046383 | Sustained | FALSE | FALSE | Not_TMED_Event | 681
CANOVANAS | 2023-04-15 04:52 | 2023-04-15 04:53 | 3838 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23041500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 3838 | keep | 0 | Apr | 2023 | 0.002614 | 0.002614 | Momentary | FALSE | FALSE | Not_TMED_Event | 3838
CANOVANAS | 2023-04-15 05:14 | 2023-04-15 05:50 | 149 | 0:36 | P | ALIMENTADOR AMARRADO | EN SERVICIO TOTAL EL 1336-06 FALTA 50% DEL 1619-03 CONTINUAN PATRULLANDO | R23041500032 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 36 | 2023-04-15 | 5364 | keep | 0 | Apr | 2023 | 0.0036534 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-15 05:14 | 2023-04-15 06:39 | 1076 | 1:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR | R23041500032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 85 | 2023-04-15 | 91460 | keep | 0 | Apr | 2023 | 0.062293 | 0.00073286 | Sustained | FALSE | FALSE | Not_TMED_Event | 1076
BAYAMON | 2023-04-15 05:14 | 2023-04-15 09:10 | 10 | 3:56 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23041500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2023-04-15 | 2360 | keep | 0 | Apr | 2023 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-15 05:21 | 2023-04-15 19:17 | 102 | 13:56 | P | DESGANCHE | SJ-230415-01 SE SECCIONALIZO PARA QUE COMPAÃ‘IA PRIVADA REALIZARA DESGANCHE 100% EN SERVICIO | S23041500003 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 836 | 2023-04-15 | 85272 | keep | 0 | Apr | 2023 | 0.058078 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-15 05:22 | 2023-04-15 11:45 | 50 | 6:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23041500012 | New_Event | Cutout Failure | Include | Include | Equipment | 383 | 2023-04-15 | 19150 | keep | 0 | Apr | 2023 | 0.013043 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-15 05:34 | 2023-04-15 05:35 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23041500122 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-15 05:35 | 2023-04-15 13:20 | 150 | 7:45 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | R23041500003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 465 | 2023-04-15 | 69750 | keep | 0 | Apr | 2023 | 0.047506 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-15 05:46 | 2023-04-15 05:47 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 5809 | keep | 0 | Apr | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
VEGA BAJA | 2023-04-15 05:59 | 2023-04-15 17:50 | 22 | 11:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 Y 1 X 15 EN CORTE DE LINEA MAL TIEMPO LLUVIA | B23041500010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 711 | 2023-04-15 | 15642 | keep | 0 | Apr | 2023 | 0.010654 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
PONCE | 2023-04-15 06:20 | 2023-04-15 07:57 | 1746 | 1:37 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO ENTRADA SOTERRADO CASCO URBANO SE LE DIO PRUEBA A INTERRUPTOR QUEDANDO EN SERVICIO | P23041500012 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 97 | 2023-04-15 | 169362 | keep | 0 | Apr | 2023 | 0.11535 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
VEGA BAJA | 2023-04-15 06:28 | 2023-04-15 16:45 | 50 | 10:17 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23041500004 | New_Event | Animals | Include | Include | Wildlife | 617 | 2023-04-15 | 30850 | keep | 0 | Apr | 2023 | 0.021012 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-15 06:39 | 2023-04-15 07:08 | 968 | 0:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR | R23041500032 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 29 | 2023-04-15 | 28072 | keep | 0 | Apr | 2023 | 0.01912 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 14:12 | 72 | 7:24 | P | ALIMENTADOR AMARRADO | SJ-230415-02 SE SECCIONALIZO PARA SUBIR CABLE PRIMARIO EN EL SUELO 5% POR 1404-07 | S23041500030 | New_Event | Feeder Load Transferred | Include | Include | Other | 444 | 2023-04-15 | 31968 | keep | 0 | Apr | 2023 | 0.021773 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 08:57 | 143 | 2:09 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230415-03. EN AVERIA DE CONDUCTOR EN EL SUELO BKR 1404-07 NO ABRIO Y OPERO EL 0020, SE DEJO EL 1404-07 FUERA Y SE ENERGIZO SUBESTACION Y NORMALIZARON LOS DEMAS ALIMENTADORES. 1404-06 LLEVA 80% DEL 1404-07 | S23041500024 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 129 | 2023-04-15 | 18447 | keep | 0 | Apr | 2023 | 0.012564 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 08:58 | 1085 | 2:10 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230415-03. EN AVERIA DE CONDUCTOR EN EL SUELO BKR 1404-07 NO ABRIO Y OPERO EL 0020, SE DEJO EL 1404-07 FUERA Y SE ENERGIZO SUBESTACION Y NORMALIZARON LOS DEMAS ALIMENTADORES. 80% DEL 1404-07 POR 1404-06 | S23041500024 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 130 | 2023-04-15 | 141050 | keep | 0 | Apr | 2023 | 0.096069 | 0.00073899 | Sustained | FALSE | FALSE | Not_TMED_Event | 1085
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 08:58 | 328 | 2:10 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230415-03. EN AVERIA DE CONDUCTOR EN EL SUELO BKR 1404-07 NO ABRIO Y OPERO EL 0020, SE DEJO EL 1404-07 FUERA Y SE ENERGIZO SUBESTACION Y NORMALIZARON LOS DEMAS ALIMENTADORES | S23041500024 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 130 | 2023-04-15 | 42640 | keep | 0 | Apr | 2023 | 0.029042 | 0.0002234 | Sustained | FALSE | FALSE | Not_TMED_Event | 328
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 08:58 | 242 | 2:10 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230415-03. EN AVERIA DE CONDUCTOR EN EL SUELO BKR 1404-07 NO ABRIO Y OPERO EL 0020, SE DEJO EL 1404-07 FUERA Y SE ENERGIZO SUBESTACION Y NORMALIZARON LOS DEMAS ALIMENTADORES. 1404-09 LLEVA 1420-05 Y 20% DE SU CARGA POR 1401-07 Y 30% POR EL 1420-04 | S23041500024 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 130 | 2023-04-15 | 31460 | keep | 0 | Apr | 2023 | 0.021427 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 06:52 | 262 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 ALIMENTADOR 1404-7 NO ABRIÃ“ EN AVERÃA Y OPERO EL OO2O HATO REY GIS Y EL 5730 TRES MONJITAS APAGÃNDOSE LA BARRA 38KV HATO REY GIS. | S23041500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-15 | 1048 | keep | 0 | Apr | 2023 | 0.00071379 | 0.00017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 262
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 06:52 | 296 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 ALIMENTADOR 1404-7 NO ABRIÃ“ EN AVERÃA Y OPERO EL OO2O HATO REY GIS Y EL 5730 TRES MONJITAS APAGÃNDOSE LA BARRA 38KV HATO REY GIS. | S23041500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-15 | 1184 | keep | 0 | Apr | 2023 | 0.00080642 | 0.0002016 | Momentary | FALSE | FALSE | Not_TMED_Event | 296
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 06:52 | 79 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 ALIMENTADOR 1404-7 NO ABRIÃ“ EN AVERÃA Y OPERO EL OO2O HATO REY GIS Y EL 5730 TRES MONJITAS APAGÃNDOSE LA BARRA 38KV HATO REY GIS. | S23041500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-15 | 316 | keep | 0 | Apr | 2023 | 0.00021523 | 5.3807e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 06:52 | 1129 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 ALIMENTADOR 1404-7 NO ABRIÃ“ EN AVERÃA Y OPERO EL OO2O HATO REY GIS Y EL 5730 TRES MONJITAS APAGÃNDOSE LA BARRA 38KV HATO REY GIS. | S23041500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-15 | 4516 | keep | 0 | Apr | 2023 | 0.0030758 | 0.00076896 | Momentary | FALSE | FALSE | Not_TMED_Event | 1129
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 06:52 | 1573 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5700 ALIMENTADOR 1404-7 NO ABRIÃ“ EN AVERÃA Y OPERO EL OO2O HATO REY GIS Y EL 5730 TRES MONJITAS APAGÃNDOSE LA BARRA 38KV HATO REY GIS. | S23041500015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-04-15 | 6292 | keep | 0 | Apr | 2023 | 0.0042855 | 0.0010714 | Momentary | FALSE | FALSE | Not_TMED_Event | 1573
SAN JUAN | 2023-04-15 06:48 | 2023-04-15 08:58 | 4 | 2:10 | T | ALIMENTADOR AMARRADO | SJ-230415-03. EN AVERIA DE CONDUCTOR EN EL SUELO BKR 1404-07 NO ABRIO Y OPERO EL 0020, SE DEJO EL 1404-07 FUERA Y SE ENERGIZO SUBESTACION Y NORMALIZARON LOS DEMAS ALIMENTADORES. 1404-09 LLEVA 1420-05 Y 20% DE SU CARGA POR 1401-07 Y 30% POR EL 1420-04 | S23041500024 | New_Event | Feeder Load Transferred | Include | Include | Other | 130 | 2023-04-15 | 520 | keep | 0 | Apr | 2023 | 0.00035417 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-15 06:51 | 2023-04-15 06:52 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 1362 | keep | 0 | Apr | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2023-04-15 06:52 | 2023-04-15 09:05 | 107 | 2:13 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | B23041500018 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-04-15 | 14231 | keep | 0 | Apr | 2023 | 0.0096927 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
CANOVANAS | 2023-04-15 07:08 | 2023-04-15 07:48 | 919 | 0:40 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR | R23041500032 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 40 | 2023-04-15 | 36760 | keep | 0 | Apr | 2023 | 0.025037 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-15 07:46 | 2023-04-15 11:35 | 2584 | 3:49 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRE INTERRUPTOR POR ORDEN DE CCE MONACILLOS (HERMINIO) PARA BAJAR TRANSFERENCIA DE LINEA 8500 DE SANTA ISABEL TC POR PERDIDA BANCO 115/38 | P23041500027 | New_Event |  |  |  |  | 229 | 2023-04-15 | 591736 | keep | 0 | Apr | 2023 | 0.40303 | 0.00176 | Sustained | FALSE | FALSE | Not_TMED_Event | 2584
GUAYAMA | 2023-04-15 07:55 | 2023-04-15 07:56 | 4035 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 4035 | keep | 0 | Apr | 2023 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
VEGA BAJA | 2023-04-15 07:55 | 2023-04-15 15:45 | 15 | 7:50 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA COQUI CRUZO LINEA | A23041500006 | New_Event | Animals | Include | Include | Wildlife | 470 | 2023-04-15 | 7050 | keep | 0 | Apr | 2023 | 0.0048017 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-04-15 07:57 | 2023-04-15 08:25 | 200 | 0:28 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE CIERRA RISER ENTRADA SOTERRADO CASCO URBANO Y DISPARA INTERRUPTOR | P23041500012 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 28 | 2023-04-15 | 5600 | keep | 0 | Apr | 2023 | 0.0038141 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-15 08:00 | 2023-04-15 08:02 | 837 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO 1401-07 QUE LLEVA 1401-06 Y SE CERRO POR SCADA | S23041500040 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-15 | 1674 | keep | 0 | Apr | 2023 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-04-15 08:00 | 2023-04-15 08:02 | 908 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 1401-07 QUE LLEVA 1401-06 Y SE CERRO POR SCADA | S23041500040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-15 | 1816 | keep | 0 | Apr | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
MAYAGÃœEZ | 2023-04-15 08:06 | 2023-04-15 18:07 | 15 | 10:01 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | M23041500046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 601 | 2023-04-15 | 9015 | keep | 0 | Apr | 2023 | 0.0061401 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-04-15 08:06 | 2023-04-15 12:40 | 40 | 4:34 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23041500045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 274 | 2023-04-15 | 10960 | keep | 0 | Apr | 2023 | 0.0074648 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-15 08:08 | 2023-04-15 14:04 | 292 | 5:56 | P | ANIMAL | 1 X 100 Y 1 X 80 EN CORTES DE LINEA CRUCE POR AVE | R23041500206 | New_Event | Animals | Include | Include | Wildlife | 356 | 2023-04-15 | 103952 | keep | 0 | Apr | 2023 | 0.070801 | 0.00019888 | Sustained | FALSE | FALSE | Not_TMED_Event | 292
CANOVANAS | 2023-04-15 08:11 | 2023-04-15 08:47 | 654 | 0:36 | P | DESGANCHE | PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | R23041500007 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-04-15 | 23544 | keep | 0 | Apr | 2023 | 0.016036 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-04-15 08:12 | 2023-04-15 10:06 | 37 | 1:54 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO LINEA Y 1 X 40 EN C/L | C23041500012 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 114 | 2023-04-15 | 4218 | keep | 0 | Apr | 2023 | 0.0028729 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CANOVANAS | 2023-04-15 08:14 | 2023-04-15 12:12 | 68 | 3:58 | P | DESGANCHE | 1 X 80 EN C/L | R23041500211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-04-15 | 16184 | keep | 0 | Apr | 2023 | 0.011023 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BARRANQUITAS | 2023-04-15 08:21 | 2023-04-15 12:46 | 10 | 4:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23041500013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 265 | 2023-04-15 | 2650 | keep | 0 | Apr | 2023 | 0.0018049 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-15 08:25 | 2023-04-15 08:26 | 2725 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 2725 | keep | 0 | Apr | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
PONCE | 2023-04-15 08:25 | 2023-04-15 08:29 | 1746 | 0:04 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRE RISER ENTRADA SOTERRADO CASCO URBANO Y SE DA PRUEBA A INTERRUPTOR QUEDANDO EN SERVICIO | P23041500038 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 4 | 2023-04-15 | 6984 | keep | 0 | Apr | 2023 | 0.0047568 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-15 08:29 | 2023-04-15 09:33 | 180 | 1:04 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REALIZARON OPERACIONES PARA BUSCAR AVERIA | P23041500012 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 64 | 2023-04-15 | 11520 | keep | 0 | Apr | 2023 | 0.0078462 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
ARECIBO | 2023-04-15 08:33 | 2023-04-15 09:40 | 20 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23041500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2023-04-15 | 1340 | keep | 0 | Apr | 2023 | 0.00091267 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-15 08:47 | 2023-04-15 08:49 | 2179 | 0:02 | T | DESGANCHE | DISPARO PERSONAL REALIZANDO OPERACIONES PARA LOCALIZAR AVERIA | R23041500213 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-15 | 4358 | keep | 0 | Apr | 2023 | 0.0029682 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-15 08:49 | 2023-04-15 10:10 | 109 | 1:21 | P | DESGANCHE | SE SECCIONALIZO EL ALIMENTADOR Y CERRO N/O CONTRA EL 1646-03 | R23041500213 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-04-15 | 8829 | keep | 0 | Apr | 2023 | 0.0060134 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
SAN JUAN | 2023-04-15 08:58 | 2023-04-15 14:12 | 271 | 5:14 | P | CONDUCTOR ROTO O ABIERTO | SJ-230415-02 SE ABRIO BKR 1404-07 PARA SECCIONALIZAR CABLE PRIMARIO EN EL SUELO 80% POR 1404-06 LLEVA 5% DEL 1112-04 | S23041500030 | New_Event | Primary Wire Break | Include | Include | Equipment | 314 | 2023-04-15 | 85094 | keep | 0 | Apr | 2023 | 0.057957 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
PONCE | 2023-04-15 09:33 | 2023-04-15 09:34 | 1746 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | HACIENDO MANIOBRAS SE ENCONTRO VACUMM QUEMADO EN MH 83 | P23041500061 | Additional_clients | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-04-15 | 1746 | keep | 0 | Apr | 2023 | 0.0011892 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-15 09:34 | 2023-04-15 10:44 | 180 | 1:10 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO DEL MH81 AL MH 83 Y ESTA RADIAL POR VACUUM SWITCH AVERIADO CALLE GUADALUPE FINAL | P23041500012 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 70 | 2023-04-15 | 12600 | keep | 0 | Apr | 2023 | 0.0085818 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
BAYAMON | 2023-04-15 09:46 | 2023-04-15 09:47 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1713-04 LLEVA 75% DEL 1718-03 | B23041500035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-04-15 09:46 | 2023-04-15 09:47 | 1953 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1713-04 LLEVA 75% DEL 1718-03 | B23041500035 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-15 | 1953 | keep | 0 | Apr | 2023 | 0.0013302 | 0.0013302 | Momentary | FALSE | FALSE | Not_TMED_Event | 1953
BAYAMON | 2023-04-15 10:07 | 2023-04-15 14:03 | 174 | 3:56 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A LINEA | B23041500040 | New_Event | Primary Wire Break | Include | Include | Equipment | 236 | 2023-04-15 | 41064 | keep | 0 | Apr | 2023 | 0.027969 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
HUMACAO | 2023-04-15 10:08 | 2023-04-15 10:09 | 1117 | 0:01 | T | AVERIA EN BARRA DE DISTRIBUCION | RECIERRE DE INTERRUPTOR MAS TARDE SE ENCONTRO AISLADOR EN BARRA AUX AVERIADO INTERRUPTOR 2602-02 TENIA LA BARRA EN CALENTAMINETO | C2304150000X | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 1 | 2023-04-15 | 1117 | keep | 0 | Apr | 2023 | 0.00076078 | 0.00076078 | Momentary | FALSE | FALSE | Not_TMED_Event | 1117
CANOVANAS | 2023-04-15 10:10 | 2023-04-15 10:12 | 2179 | 0:02 | T | OTRAS CAUSAS | DISPARO PERSONAL REALIZANDO OPERACIONES | R23041500213 | New_Event | Other Causes | Include | Include | Other | 2 | 2023-04-15 | 4358 | keep | 0 | Apr | 2023 | 0.0029682 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
CANOVANAS | 2023-04-15 10:12 | 2023-04-15 11:29 | 109 | 1:17 | P | DESGANCHE | SE DESGANCHO REMPLAZO CAJA PARTIDA Y CONECTOR DE PLANCHA | R23041500213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-04-15 | 8393 | keep | 0 | Apr | 2023 | 0.0057164 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
CANOVANAS | 2023-04-15 10:12 | 2023-04-15 10:13 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23041500270 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 1271 | keep | 0 | Apr | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
BARRANQUITAS | 2023-04-15 10:19 | 2023-04-15 10:21 | 1604 | 0:02 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR TRAMO CON POSTE EN EL SUELO | C23041500070 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2 | 2023-04-15 | 3208 | keep | 0 | Apr | 2023 | 0.002185 | 0.0010925 | Momentary | FALSE | FALSE | Not_TMED_Event | 1604
SAN JUAN | 2023-04-15 10:20 | 2023-04-15 11:50 | 10 | 1:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR SE REMPLAZO POSTE CON TRANSFORMADOR 22-003-HC-FIONA EMERGENCIA | S23041500074 | New_Event | Primary Pole Failure | Include | Include | Equipment | 90 | 2023-04-15 | 900 | keep | 0 | Apr | 2023 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-15 10:21 | 2023-04-15 18:25 | 334 | 8:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO TRAMO Y SE REEMPLAZO POSTE PRIMARIO PARTIDO | C23041500070 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 484 | 2023-04-15 | 161656 | keep | 0 | Apr | 2023 | 0.1101 | 0.00022749 | Sustained | FALSE | FALSE | Not_TMED_Event | 334
BARRANQUITAS | 2023-04-15 10:24 | 2023-04-15 10:25 | 2486 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 2486 | keep | 0 | Apr | 2023 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
VEGA BAJA | 2023-04-15 10:26 | 2023-04-15 14:30 | 300 | 4:04 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23041500032 | New_Event | Primary Wire Break | Include | Include | Equipment | 244 | 2023-04-15 | 73200 | keep | 0 | Apr | 2023 | 0.049856 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2023-04-15 10:44 | 2023-04-15 14:49 | 20 | 4:05 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ELIMINO VACUUM SWITCH SE ABRIO RISER Y SE CERRO DEL MH-84-MH83 | P23041500081 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 245 | 2023-04-15 | 4900 | keep | 0 | Apr | 2023 | 0.0033374 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-15 10:48 | 2023-04-15 10:49 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
CANOVANAS | 2023-04-15 10:55 | 2023-04-15 14:56 | 1 | 4:01 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR EN MONTURA ESTRELLA ABIERTA DELTA | R23041500276 | New_Event | Service Transformer Failure | Include | Include | Equipment | 241 | 2023-04-15 | 241 | keep | 0 | Apr | 2023 | 0.00016414 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-15 10:59 | 2023-04-15 18:30 | 25 | 7:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA | B23041500065 | New_Event | Cutout Failure | Include | Include | Equipment | 451 | 2023-04-15 | 11275 | keep | 0 | Apr | 2023 | 0.0076794 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-04-15 11:01 | 2023-04-15 14:30 | 15 | 3:29 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | R23041500280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-04-15 | 3135 | keep | 0 | Apr | 2023 | 0.0021352 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-15 11:10 | 2023-04-15 14:35 | 519 | 3:25 | S | AVERIA EN BARRA DE DISTRIBUCION | AISLADOR AVERIADO EN BARRA DE INSPECCION CG-230415-02 | C23041500135 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 205 | 2023-04-15 | 106395 | keep | 0 | Apr | 2023 | 0.072465 | 0.00035349 | Sustained | FALSE | FALSE | Not_TMED_Event | 519
HUMACAO | 2023-04-15 11:10 | 2023-04-15 14:35 | 1117 | 3:25 | S | AVERIA EN BARRA DE DISTRIBUCION | AISLADOR AVERIADO EN BARRA DE INSPECCION CG-230415-02 | C23041500135 | 1st_after_momentary | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 205 | 2023-04-15 | 228985 | keep | 0 | Apr | 2023 | 0.15596 | 0.00076078 | Sustained | FALSE | FALSE | Not_TMED_Event | 1117
HUMACAO | 2023-04-15 11:10 | 2023-04-15 14:35 | 4161 | 3:25 | S | AVERIA EN BARRA DE DISTRIBUCION | AISLADOR AVERIADO EN BARRA DE INSPECCION CG-230415-02 | C23041500135 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 205 | 2023-04-15 | 853005 | keep | 0 | Apr | 2023 | 0.58098 | 0.002834 | Sustained | FALSE | FALSE | Not_TMED_Event | 4161
BARRANQUITAS | 2023-04-15 11:16 | 2023-04-15 11:19 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-15 | 2610 | keep | 0 | Apr | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2023-04-15 11:40 | 2023-04-15 13:02 | 64 | 1:22 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR 1 X 140 EN C/L | C23041500163 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 82 | 2023-04-15 | 5248 | keep | 0 | Apr | 2023 | 0.0035744 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2023-04-15 11:53 | 2023-04-15 16:14 | 5 | 4:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO SECUANDARIA | S23041500084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 261 | 2023-04-15 | 1305 | keep | 0 | Apr | 2023 | 0.00088883 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-04-15 12:08 | 2023-04-15 12:09 | 5063 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA QUEDO EN SERVICIO | P23041500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 5063 | keep | 0 | Apr | 2023 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
BAYAMON | 2023-04-15 12:12 | 2023-04-15 15:07 | 1 | 2:55 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN RISER Y 1 X 40 EN SU-1, SE REEMPLAZO PARARRAYO | B23041500083 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 175 | 2023-04-15 | 175 | keep | 0 | Apr | 2023 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-15 12:26 | 2023-04-15 14:00 | 6 | 1:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23041500088 | New_Event | Secondary Wire Break | Include | Include | Equipment | 94 | 2023-04-15 | 564 | keep | 0 | Apr | 2023 | 0.00038414 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-04-15 12:42 | 2023-04-15 16:00 | 1 | 3:18 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 10 EN MONTURA DE TRANSFORMADOR LUNEA ARRIADA | P23041500101 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 198 | 2023-04-15 | 198 | keep | 0 | Apr | 2023 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-15 13:19 | 2023-04-15 16:51 | 10 | 3:32 | P | NO SE REPORTO CAUSA | 1 X 20 C/L | S23041500095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2023-04-15 | 2120 | keep | 0 | Apr | 2023 | 0.0014439 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-15 13:45 | 2023-04-15 15:55 | 18 | 2:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 2 X 100 EN C/L | C23041500212 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2023-04-15 | 2340 | keep | 0 | Apr | 2023 | 0.0015938 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2023-04-15 14:05 | 2023-04-15 15:56 | 307 | 1:51 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | R23041500291 | New_Event | Primary Wire Break | Include | Include | Equipment | 111 | 2023-04-15 | 34077 | keep | 0 | Apr | 2023 | 0.02321 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
GUAYAMA | 2023-04-15 14:11 | 2023-04-15 14:21 | 4035 | 0:10 | T | LINEA DE TRANSMISION 38KV | SE TRANSFIERE CARGA POR DISPARO BANCO 115/38KV SANTA ISABEL TC LINEA 8500 CAYEY TC EN SOBRECARGA | P23041500128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-04-15 | 40350 | keep | 0 | Apr | 2023 | 0.027482 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
SAN JUAN | 2023-04-15 14:16 | 2023-04-15 14:17 | 1964 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1106-04 QUE LLEVA 60% DEL 1110-03 | S2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 1964 | keep | 0 | Apr | 2023 | 0.0013377 | 0.0013377 | Momentary | FALSE | FALSE | Not_TMED_Event | 1964
SAN JUAN | 2023-04-15 14:16 | 2023-04-15 14:17 | 915 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1106-04 60% DE SU CARGA POR EL 1106-04 | S2304150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-15 | 915 | keep | 0 | Apr | 2023 | 0.0006232 | 0.0006232 | Momentary | FALSE | FALSE | Not_TMED_Event | 915
PONCE | 2023-04-15 14:16 | 2023-04-15 17:41 | 45 | 3:25 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRMARIA 1 X 50 EN CORTA DE LINEA | P23041500130 | New_Event | Primary Wire Break | Include | Include | Equipment | 205 | 2023-04-15 | 9225 | keep | 0 | Apr | 2023 | 0.0062831 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-04-15 14:18 | 2023-04-15 15:35 | 70 | 1:17 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C23041500223 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-04-15 | 5390 | keep | 0 | Apr | 2023 | 0.0036711 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-04-15 14:23 | 2023-04-15 15:30 | 4 | 1:07 | P | PROBLEMA DEL CLIENTE | PROBLEMA INTERNO DE CLIENTE | S23041500105 | New_Event | Customer-Related Interruption | Include | Include | Public | 67 | 2023-04-15 | 268 | keep | 0 | Apr | 2023 | 0.00018253 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2023-04-15 14:23 | 2023-04-15 14:26 | 3718 | 0:03 | T | LINEA DE TRANSMISION 38KV | SE TRANSFIERE CARGA POR DISPARO BANCO SANTA ISABEL TC LINEA 8500 CAYEY TC EN SOBRECARGA | P23041500137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-15 | 11154 | keep | 0 | Apr | 2023 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BARRANQUITAS | 2023-04-15 14:35 | 2023-04-15 16:51 | 547 | 2:16 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE CERRO PUENTE ABIERTO CG-230415-03 | C23041500180 | New_Event | Primary Wire Break | Include | Include | Equipment | 136 | 2023-04-15 | 74392 | keep | 0 | Apr | 2023 | 0.050668 | 0.00037256 | Sustained | FALSE | FALSE | Not_TMED_Event | 547
BAYAMON | 2023-04-15 14:53 | 2023-04-15 16:05 | 39 | 1:12 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR CHANGO | B23041500117 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-04-15 | 2808 | keep | 0 | Apr | 2023 | 0.0019125 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
GUAYAMA | 2023-04-15 15:24 | 2023-04-15 15:52 | 10 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON BAJANTES SECUNDARIOS | P23041500115 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-04-15 | 280 | keep | 0 | Apr | 2023 | 0.00019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-15 15:34 | 2023-04-15 15:39 | 138 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1206-04 10% POR 1206-04 | S2304150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-15 | 690 | keep | 0 | Apr | 2023 | 0.00046996 | 9.3991e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-04-15 15:34 | 2023-04-15 15:39 | 1977 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1206-04 40% POR 1206-04 | S2304150000X | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-15 | 9885 | keep | 0 | Apr | 2023 | 0.0067326 | 0.0013465 | Momentary | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-04-15 15:34 | 2023-04-15 15:39 | 1799 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 10% 1204-03 LLEVA 40% 1204-04 | S2304150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-15 | 8995 | keep | 0 | Apr | 2023 | 0.0061265 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
BAYAMON | 2023-04-15 15:34 | 2023-04-15 15:41 | 1588 | 0:07 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA DEL 1711-01 POR EL 1716-03 SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | B23041500121 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-04-15 | 11116 | keep | 0 | Apr | 2023 | 0.0075711 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-15 15:34 | 2023-04-15 15:41 | 13 | 0:07 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR CARGA DEL 1711-03 POR EL 1716-03 SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | B23041500121 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-04-15 | 91 | keep | 0 | Apr | 2023 | 6.198e-05 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-15 15:34 | 2023-04-15 15:41 | 1812 | 0:07 | T | DESGANCHE | DISPARO INTERRUPTOR LLEVA LA CARGA DEL 1711-01 Y 1711-03 SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL | B23041500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 7 | 2023-04-15 | 12684 | keep | 0 | Apr | 2023 | 0.008639 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
CANOVANAS | 2023-04-15 15:41 | 2023-04-15 19:27 | 44 | 3:46 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | R23041500315 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 226 | 2023-04-15 | 9944 | keep | 0 | Apr | 2023 | 0.0067728 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2023-04-15 15:41 | 2023-04-15 17:49 | 1 | 2:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | B23041500142 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-04-15 | 128 | keep | 0 | Apr | 2023 | 8.718e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-15 16:26 | 2023-04-15 16:27 | 315 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | S23041500131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 315 | keep | 0 | Apr | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
GUAYAMA | 2023-04-15 16:39 | 2023-04-15 16:40 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041500158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 449 | keep | 0 | Apr | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
GUAYAMA | 2023-04-15 16:39 | 2023-04-15 16:40 | 4035 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE SU CARGA X 4402-02 | P23041500158 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-15 | 4035 | keep | 0 | Apr | 2023 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
GUAYAMA | 2023-04-15 16:39 | 2023-04-15 16:40 | 3718 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE SU CARGA X 4402-0 | P23041500158 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-15 | 3718 | keep | 0 | Apr | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
GUAYAMA | 2023-04-15 16:46 | 2023-04-15 17:05 | 29 | 0:19 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRE INTERRUPTOR POR SOBRECARGA EN LINEA 8500 | P23041500159 | New_Event |  |  |  |  | 19 | 2023-04-15 | 551 | keep | 0 | Apr | 2023 | 0.00037528 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
HUMACAO | 2023-04-15 17:09 | 2023-04-15 17:52 | 11 | 0:43 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C23041500253 | New_Event | Secondary Wire Break | Include | Include | Equipment | 43 | 2023-04-15 | 473 | keep | 0 | Apr | 2023 | 0.00032216 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-04-15 17:24 | 2023-04-15 17:25 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23041500313 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-04-15 17:26 | 2023-04-15 17:29 | 171 | 0:03 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 CARGA POR 1110-5 | S23041500137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-15 | 513 | keep | 0 | Apr | 2023 | 0.0003494 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
SAN JUAN | 2023-04-15 17:26 | 2023-04-15 17:29 | 1837 | 0:03 | T | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 CARGA POR 1110-5 | S23041500137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-15 | 5511 | keep | 0 | Apr | 2023 | 0.0037535 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
SAN JUAN | 2023-04-15 17:26 | 2023-04-15 17:29 | 218 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S23041500137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-15 | 654 | keep | 0 | Apr | 2023 | 0.00044544 | 0.00014848 | Momentary | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2023-04-15 17:26 | 2023-04-15 17:29 | 455 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S23041500137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-15 | 1365 | keep | 0 | Apr | 2023 | 0.0009297 | 0.0003099 | Momentary | FALSE | FALSE | Not_TMED_Event | 455
SAN JUAN | 2023-04-15 17:26 | 2023-04-15 17:29 | 611 | 0:03 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 | S23041500137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-15 | 1833 | keep | 0 | Apr | 2023 | 0.0012484 | 0.00041615 | Momentary | FALSE | FALSE | Not_TMED_Event | 611
SAN JUAN | 2023-04-15 17:26 | 2023-04-15 17:29 | 283 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6700 LLEVA 1102-02 LLEVA 1102-03 | S23041500137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-15 | 849 | keep | 0 | Apr | 2023 | 0.00057825 | 0.00019275 | Momentary | FALSE | FALSE | Not_TMED_Event | 283
CAGUAS | 2023-04-15 17:29 | 2023-04-16 08:33 | 10 | 15:04 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23041500257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 904 | 2023-04-15 | 9040 | keep | 0 | Apr | 2023 | 0.0061571 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-04-15 18:02 | 2023-04-15 19:00 | 12 | 0:58 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO HOT CLAMP QUEMADO EN TRANSFORMADOR | P23041500170 | New_Event | Primary Wire Break | Include | Include | Equipment | 58 | 2023-04-15 | 696 | keep | 0 | Apr | 2023 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-04-15 18:12 | 2023-04-15 22:30 | 300 | 4:18 | P | MAL TIEMPO/LLUVIA O VIENTO | SE CERRO "POLE BREAKER" 6012-02A LLUVIA Y FUERTES VIENTOS | M23041500133 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 258 | 2023-04-15 | 77400 | keep | 0 | Apr | 2023 | 0.052717 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2023-04-15 18:30 | 2023-04-15 18:51 | 4035 | 0:21 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRE AMARRE PARA NORMALIZAR CARGA DE 4603-00 YA QUE SU CARGA FUE TRANSFERIDA A 4402-02 POR SOBRECARGA EN LINEA 8500 4603-00 Y 4402-00 NO FASEAN | P23041500219 | New_Event |  |  |  |  | 21 | 2023-04-15 | 84735 | keep | 0 | Apr | 2023 | 0.057713 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
GUAYAMA | 2023-04-15 18:30 | 2023-04-15 18:48 | 3718 | 0:18 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRE AMARRE PARA NORMALIZAR CARGA DE 4603-00 YA QUE SU CARGA FUE TRANSFERIDA A 4402-02 POR SOBRECARGA EN LINEA 8500 4603-00 Y 4402-00 NO FASEAN | P23041500220 | New_Event |  |  |  |  | 18 | 2023-04-15 | 66924 | keep | 0 | Apr | 2023 | 0.045582 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2023-04-15 18:32 | 2023-04-16 13:00 | 2 | 18:28 | P | PROBLEMA DEL CLIENTE | 1 X 30 EN CORTE DE LINEA SE DEJO RISER ABIERTO POR TRANSFORMADOR PRIVADO AVERIADO | A23041500058 | New_Event | Customer-Related Interruption | Include | Include | Public | 1108 | 2023-04-15 | 2216 | keep | 0 | Apr | 2023 | 0.0015093 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-04-15 18:47 | 2023-04-15 18:48 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23041500144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 2999 | keep | 0 | Apr | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2023-04-15 18:57 | 2023-04-16 09:39 | 60 | 14:42 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23041500145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 882 | 2023-04-15 | 52920 | keep | 0 | Apr | 2023 | 0.036044 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-15 19:05 | 2023-04-15 19:06 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23041500155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-15 | 1859 | keep | 0 | Apr | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-04-15 19:12 | 2023-04-15 21:09 | 23 | 1:57 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESPEGO CABLE DEL CORNED BRAKET CON VARETA | B23041500156 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 117 | 2023-04-15 | 2691 | keep | 0 | Apr | 2023 | 0.0018328 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-04-15 19:17 | 2023-04-16 09:22 | 16 | 14:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO PORTAFUSIBLES | S23041500148 | New_Event | Cutout Failure | Include | Include | Equipment | 845 | 2023-04-15 | 13520 | keep | 0 | Apr | 2023 | 0.0092084 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-04-15 19:34 | 2023-04-16 06:08 | 14 | 10:34 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23041500158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 634 | 2023-04-15 | 8876 | keep | 0 | Apr | 2023 | 0.0060454 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-04-15 19:53 | 2023-04-16 10:08 | 15 | 14:15 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23041500167 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 855 | 2023-04-15 | 12825 | keep | 0 | Apr | 2023 | 0.008735 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-04-15 19:56 | 2023-04-16 09:47 | 30 | 13:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23041500235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 831 | 2023-04-15 | 24930 | keep | 0 | Apr | 2023 | 0.01698 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-04-15 21:06 | 2023-04-16 08:47 | 60 | 11:41 | P | CAUSAS EXTERNAS | 1 X 100 EN RISER POR CONTAMINACION AMBIENTE DEL PORTA FUSIBLE | P23041500246 | New_Event | Damage From Public | Include | Include | Public | 701 | 2023-04-15 | 42060 | keep | 0 | Apr | 2023 | 0.028647 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-15 22:05 | 2023-04-16 11:15 | 5 | 13:10 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23041500318 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 790 | 2023-04-15 | 3950 | keep | 0 | Apr | 2023 | 0.0026903 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-15 22:35 | 2023-04-16 03:18 | 165 | 4:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | B23041500164 | New_Event | Cutout Failure | Include | Include | Equipment | 283 | 2023-04-15 | 46695 | keep | 0 | Apr | 2023 | 0.031804 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
AGUADILLA | 2023-04-15 23:10 | 2023-04-16 08:16 | 30 | 9:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23041500208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 546 | 2023-04-15 | 16380 | keep | 0 | Apr | 2023 | 0.011156 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-15 23:12 | 2023-04-16 14:56 | 76 | 15:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP Y AISLADOR | C23041500276 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 944 | 2023-04-15 | 71744 | keep | 0 | Apr | 2023 | 0.048865 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
MAYAGÃœEZ | 2023-04-15 23:36 | 2023-04-16 09:30 | 60 | 9:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUVIA Y VIENTO | M23041500210 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 594 | 2023-04-15 | 35640 | keep | 0 | Apr | 2023 | 0.024274 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-04-15 23:38 | 2023-04-16 00:19 | 100 | 0:41 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEAS | M23041500209 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 41 | 2023-04-15 | 4100 | keep | 0 | Apr | 2023 | 0.0027925 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-16 00:45 | 2023-04-16 11:45 | 50 | 11:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | S23041600003 | New_Event | Cutout Failure | Include | Include | Equipment | 660 | 2023-04-16 | 33000 | keep | 0 | Apr | 2023 | 0.022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-04-16 01:06 | 2023-04-16 01:15 | 75 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR | P23041600022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-04-16 | 675 | keep | 0 | Apr | 2023 | 0.00045974 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-04-16 01:46 | 2023-04-16 11:30 | 15 | 9:44 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 50KVA | A23041600002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 584 | 2023-04-16 | 8760 | keep | 0 | Apr | 2023 | 0.0059664 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-16 03:03 | 2023-04-16 11:59 | 20 | 8:56 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23041600003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2023-04-16 | 10720 | keep | 0 | Apr | 2023 | 0.0073013 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-16 03:07 | 2023-04-16 07:38 | 76 | 4:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 25 EN MONTURA 1 X 50 EN C/L MAL TIEMPO | B23041600004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 271 | 2023-04-16 | 20596 | keep | 0 | Apr | 2023 | 0.014028 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
MAYAGÃœEZ | 2023-04-16 03:41 | 2023-04-16 03:42 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M23041600015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 4381 | keep | 0 | Apr | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2023-04-16 06:28 | 2023-04-16 11:25 | 21 | 4:57 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO PARA CERRAR PUENTE ABIERTO MEDIANTE SJ-230416-01 | S23041600006 | New_Event | Primary Wire Break | Include | Include | Equipment | 297 | 2023-04-16 | 6237 | keep | 0 | Apr | 2023 | 0.004248 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
YAUCO | 2023-04-16 06:33 | 2023-04-16 06:34 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041600027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 1352 | keep | 0 | Apr | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
VEGA BAJA | 2023-04-16 06:36 | 2023-04-16 09:51 | 29 | 3:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE LLEVO LINEAS A AISLADOR | B23041600028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 195 | 2023-04-16 | 5655 | keep | 0 | Apr | 2023 | 0.0038516 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CANOVANAS | 2023-04-16 06:43 | 2023-04-16 06:44 | 1615 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S2304160000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-16 | 1615 | keep | 0 | Apr | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-04-16 06:44 | 2023-04-16 09:37 | 70 | 2:53 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23041600001 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-04-16 | 12110 | keep | 0 | Apr | 2023 | 0.0082481 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-04-16 06:52 | 2023-04-16 08:22 | 7 | 1:30 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23041600030 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-04-16 | 630 | keep | 0 | Apr | 2023 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-16 07:00 | 2023-04-16 07:01 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE 1908-01 Y LLEVA 1908-04 Y 1908-05 | S2304160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 3 | keep | 0 | Apr | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-16 07:00 | 2023-04-16 07:01 | 58 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE 1908-01 Y LLEVA 1908-04 Y 1908-05 | S2304160000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-16 | 58 | keep | 0 | Apr | 2023 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2023-04-16 07:00 | 2023-04-16 07:01 | 386 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE 1908-01 Y LLEVA 1908-04 Y 1908-05 | S2304160000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-16 | 386 | keep | 0 | Apr | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
BAYAMON | 2023-04-16 07:28 | 2023-04-16 07:30 | 652 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23041600038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-16 | 1304 | keep | 0 | Apr | 2023 | 0.00088815 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-04-16 07:28 | 2023-04-16 07:30 | 2704 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23041600038 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-16 | 5408 | keep | 0 | Apr | 2023 | 0.0036834 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
BAYAMON | 2023-04-16 07:28 | 2023-04-16 07:30 | 1526 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23041600039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-16 | 3052 | keep | 0 | Apr | 2023 | 0.0020787 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
BAYAMON | 2023-04-16 07:28 | 2023-04-16 07:30 | 308 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23041600039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-16 | 616 | keep | 0 | Apr | 2023 | 0.00041955 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-04-16 07:28 | 2023-04-16 07:30 | 1397 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23041600039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-16 | 2794 | keep | 0 | Apr | 2023 | 0.001903 | 0.00095149 | Momentary | FALSE | FALSE | Not_TMED_Event | 1397
BAYAMON | 2023-04-16 07:28 | 2023-04-16 07:30 | 2926 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7800 | B23041600039 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-16 | 5852 | keep | 0 | Apr | 2023 | 0.0039858 | 0.0019929 | Momentary | FALSE | FALSE | Not_TMED_Event | 2926
HUMACAO | 2023-04-16 08:03 | 2023-04-16 09:09 | 2 | 1:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23041600002 | New_Event | Cutout Failure | Include | Include | Equipment | 66 | 2023-04-16 | 132 | keep | 0 | Apr | 2023 | 8.9905e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2023-04-16 08:05 | 2023-04-16 08:58 | 30 | 0:53 | P | ANIMAL | 1 X 50 Y 1 X 40 EN CORTES DE LINEA CRUCE POR AVE | R23041600005 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-04-16 | 1590 | keep | 0 | Apr | 2023 | 0.0010829 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-16 08:28 | 2023-04-16 11:25 | 2 | 2:57 | P | DESGANCHE | 1 X 20 EN C/L Y 1 X 15 EN XMR | S23041600012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2023-04-16 | 354 | keep | 0 | Apr | 2023 | 0.00024111 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-16 08:29 | 2023-04-16 09:20 | 10 | 0:51 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23041600067 | New_Event | Animals | Include | Include | Wildlife | 51 | 2023-04-16 | 510 | keep | 0 | Apr | 2023 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-16 08:39 | 2023-04-16 13:14 | 180 | 4:35 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C23041600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-04-16 | 49500 | keep | 0 | Apr | 2023 | 0.033714 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
SAN JUAN | 2023-04-16 08:42 | 2023-04-16 13:11 | 1 | 4:29 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | S23041600013 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 269 | 2023-04-16 | 269 | keep | 0 | Apr | 2023 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-16 08:42 | 2023-04-16 10:41 | 15 | 1:59 | P | NO SE REPORTO CAUSA | 1 X 25 EN BANCO DE XMR | R23041600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2023-04-16 | 1785 | keep | 0 | Apr | 2023 | 0.0012158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-16 08:44 | 2023-04-16 10:14 | 191 | 1:30 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23041600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-04-16 | 17190 | keep | 0 | Apr | 2023 | 0.011708 | 0.00013009 | Sustained | FALSE | FALSE | Not_TMED_Event | 191
CAGUAS | 2023-04-16 08:58 | 2023-04-16 10:09 | 40 | 1:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN RISER MAL TIEMPO LLUVIA | C23041600011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 71 | 2023-04-16 | 2840 | keep | 0 | Apr | 2023 | 0.0019343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-16 09:00 | 2023-04-16 11:26 | 15 | 2:26 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | R23041600011 | New_Event | Animals | Include | Include | Wildlife | 146 | 2023-04-16 | 2190 | keep | 0 | Apr | 2023 | 0.0014916 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-04-16 09:12 | 2023-04-16 12:07 | 50 | 2:55 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23041600013 | New_Event | Animals | Include | Include | Wildlife | 175 | 2023-04-16 | 8750 | keep | 0 | Apr | 2023 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-04-16 09:40 | 2023-04-16 09:41 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041600041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 1945 | keep | 0 | Apr | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
BAYAMON | 2023-04-16 09:47 | 2023-04-16 14:25 | 11 | 4:38 | P | DESGANCHE | 1 X 20 EN C/ Y DESGANCHE | B23041600077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2023-04-16 | 3058 | keep | 0 | Apr | 2023 | 0.0020828 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-04-16 09:51 | 2023-04-16 12:59 | 100 | 3:08 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE TRASPATIO | C23041600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-04-16 | 18800 | keep | 0 | Apr | 2023 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-16 10:09 | 2023-04-16 10:10 | 3495 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR 20% DE SU CARGA POR EL 3604-06 EN SERVICIO | C2304160000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-16 | 3495 | keep | 0 | Apr | 2023 | 0.0023804 | 0.0023804 | Momentary | FALSE | FALSE | Not_TMED_Event | 3495
CAGUAS | 2023-04-16 10:10 | 2023-04-16 11:56 | 40 | 1:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN RISER MAL TIEMPO LLUVIA | C23041600011 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 106 | 2023-04-16 | 4240 | keep | 0 | Apr | 2023 | 0.0028878 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-16 10:20 | 2023-04-16 10:21 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 75% DEL 1718-03 | B2304160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-04-16 10:20 | 2023-04-16 10:21 | 1954 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1713-04 LLEVA 1718-03 75% | B2304160000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-16 | 1954 | keep | 0 | Apr | 2023 | 0.0013309 | 0.0013309 | Momentary | FALSE | FALSE | Not_TMED_Event | 1954
GUAYAMA | 2023-04-16 10:23 | 2023-04-16 11:40 | 1 | 1:17 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23041600042 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-04-16 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-16 10:30 | 2023-04-16 10:31 | 3833 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR EN SERVICIO | C23041600035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 3833 | keep | 0 | Apr | 2023 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
FAJARDO | 2023-04-16 10:33 | 2023-04-16 12:58 | 8 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA Y BAJANTE SECUNDARIO | R23041600015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-04-16 | 1160 | keep | 0 | Apr | 2023 | 0.00079007 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-04-16 10:49 | 2023-04-16 11:54 | 333 | 1:05 | P | CAUSAS EXTERNAS | ABRIR C/L PARA SECCIONALIZAR POSTE Y CONDUCTORES VIVOS EN EL PISO POR IMPACTO DE VEHICULO. SE ABRIO PUENTES Y SE CERRO C/L ENTRARON 200 EN SERVICIO | C23041600023 | New_Event | Damage From Public | Include | Include | Public | 65 | 2023-04-16 | 21645 | keep | 0 | Apr | 2023 | 0.014742 | 0.0002268 | Sustained | FALSE | FALSE | Not_TMED_Event | 333
CAGUAS | 2023-04-16 10:53 | 2023-04-16 13:47 | 12 | 2:54 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23041600045 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-04-16 | 2088 | keep | 0 | Apr | 2023 | 0.0014221 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-16 10:54 | 2023-04-16 10:57 | 2178 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR CERRADO POR CONTROL | C2304160000X | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-16 | 6534 | keep | 0 | Apr | 2023 | 0.0044503 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
YAUCO | 2023-04-16 10:55 | 2023-04-16 16:08 | 4 | 5:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA CAMBIAR SECUNDARIA | P23041600043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 313 | 2023-04-16 | 1252 | keep | 0 | Apr | 2023 | 0.00085273 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-04-16 11:05 | 2023-04-16 15:46 | 20 | 4:41 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | P23041600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2023-04-16 | 5620 | keep | 0 | Apr | 2023 | 0.0038278 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-16 11:15 | 2023-04-16 16:05 | 4 | 4:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA | C23041600057 | New_Event | Service Transformer Failure | Include | Include | Equipment | 290 | 2023-04-16 | 1160 | keep | 0 | Apr | 2023 | 0.00079007 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-16 11:25 | 2023-04-16 12:10 | 99 | 0:45 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO Y SE NORMALIZO CARGA MEDIANTE SJ-230416-01 | S23041600006 | New_Event | Primary Wire Break | Include | Include | Equipment | 45 | 2023-04-16 | 4455 | keep | 0 | Apr | 2023 | 0.0030343 | 6.7428e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 99
SAN JUAN | 2023-04-16 11:28 | 2023-04-16 12:52 | 25 | 1:24 | P | DESGANCHE | 1 X 50 EN C/L DEGANCHE | S23041600028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-04-16 | 2100 | keep | 0 | Apr | 2023 | 0.0014303 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-16 11:53 | 2023-04-16 12:58 | 5 | 1:05 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE SEPARO LINEAS SECUNDARIAS CRUZADAS | M23041600056 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 65 | 2023-04-16 | 325 | keep | 0 | Apr | 2023 | 0.00022136 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-04-16 11:54 | 2023-04-16 17:35 | 133 | 5:41 | P | CAUSAS EXTERNAS | 3 X 65 EN CORTE DE LINEA NUEVO SE REEMPLAZO POSTE PRIMARIO IMPACTADO POR VEHICULO | C23041600023 | Partial_restoration | Damage From Public | Include | Include | Public | 341 | 2023-04-16 | 45353 | keep | 0 | Apr | 2023 | 0.03089 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-04-16 12:02 | 2023-04-16 12:03 | 650 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON, CERRADO POR SCADA | A23041600012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 650 | keep | 0 | Apr | 2023 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
SAN JUAN | 2023-04-16 12:22 | 2023-04-16 12:23 | 362 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1620-01 QUE LLEVA 90% 1336-10 Y LLEVA 60% DEL 1620-02 Y SE CERRO POR SCADA | S2304160000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-16 | 362 | keep | 0 | Apr | 2023 | 0.00024656 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-04-16 12:22 | 2023-04-16 12:23 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-01 QUE LLEVA 90% 1336-10 Y LLEVA 60% DEL 1620-02 Y SE CERRO POR SCADA | S2304160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 36 | keep | 0 | Apr | 2023 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-04-16 12:22 | 2023-04-16 12:23 | 2230 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1620-01 QUE LLEVA 90% 1336-10 Y LLEVA 60% DEL 1620-02 Y SE CERRO POR SCADA | S2304160000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-16 | 2230 | keep | 0 | Apr | 2023 | 0.0015188 | 0.0015188 | Momentary | FALSE | FALSE | Not_TMED_Event | 2230
BARRANQUITAS | 2023-04-16 12:50 | 2023-04-16 15:10 | 9 | 2:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C23041600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2023-04-16 | 1260 | keep | 0 | Apr | 2023 | 0.00085818 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-04-16 13:10 | 2023-04-16 13:32 | 2 | 0:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO TRANSFORMADOR PARA REPARAR NEUTRAL PRIMARIO | M23041600061 | New_Event | Primary Wire Break | Include | Include | Equipment | 22 | 2023-04-16 | 44 | keep | 0 | Apr | 2023 | 2.9968e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-04-16 13:42 | 2023-04-16 19:17 | 80 | 5:35 | P | TRANSFORMADOR AVERIADO | SE DEJO PUENTE ABIERTO EN UNA FASE TRANSFORMADOR AVERIADO SE INSTALO TAG DE 25KVA A 7620 FID 5061591 Y 2 X 80 EN DIFERENTES CORTES DE LINEA 8 CLIENTES FUERA | P23041600054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 335 | 2023-04-16 | 26800 | keep | 0 | Apr | 2023 | 0.018253 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-16 14:11 | 2023-04-16 15:46 | 4291 | 1:35 | T | PROBLEMA DEL CLIENTE | SE SECCIONALIZO ALIMENTADOR 95% EN SERVICIO SE ENCONTRO PARARRAYO AVERIADO | S23041600047 | New_Event | Customer-Related Interruption | Include | Include | Public | 95 | 2023-04-16 | 407645 | keep | 0 | Apr | 2023 | 0.27765 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2023-04-16 14:19 | 2023-04-16 16:47 | 81 | 2:28 | P | ANIMAL | 2 X 80 EN C/L POR AVE | B23041600096 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-04-16 | 11988 | keep | 0 | Apr | 2023 | 0.008165 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
ARECIBO | 2023-04-16 14:22 | 2023-04-16 16:50 | 20 | 2:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | A23041600019 | New_Event | Primary Wire Break | Include | Include | Equipment | 148 | 2023-04-16 | 2960 | keep | 0 | Apr | 2023 | 0.002016 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-16 14:25 | 2023-04-16 14:26 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 5809 | keep | 0 | Apr | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
ARECIBO | 2023-04-16 14:43 | 2023-04-16 18:30 | 4 | 3:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A23041600020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-04-16 | 908 | keep | 0 | Apr | 2023 | 0.00061843 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-16 14:50 | 2023-04-16 21:33 | 98 | 6:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | S23041600075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 403 | 2023-04-16 | 39494 | keep | 0 | Apr | 2023 | 0.026899 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
SAN JUAN | 2023-04-16 15:14 | 2023-04-16 16:38 | 64 | 1:24 | P | DESGANCHE | 2 X 50 EN RISER Y 1 X 80 EN CORTE DE LINEA DESPEJE DE LINEA | S23041600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-04-16 | 5376 | keep | 0 | Apr | 2023 | 0.0036616 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2023-04-16 15:35 | 2023-04-16 20:10 | 10 | 4:35 | P | TRANSFORMADOR AVERIADO | SE ABRE TRANSFORMADOR CON LIQUEO DE ACEITE Y SE REMPLAZO 37.5 X 37.5 KVA | S23041600068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 275 | 2023-04-16 | 2750 | keep | 0 | Apr | 2023 | 0.001873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-16 15:37 | 2023-04-16 15:38 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | S23041600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-04-16 15:43 | 2023-04-16 15:44 | 4664 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR AISLADOR ROTO | M23041600080 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-04-16 | 4664 | keep | 0 | Apr | 2023 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
SAN JUAN | 2023-04-16 15:46 | 2023-04-16 16:41 | 214 | 0:55 | P | PROBLEMA DEL CLIENTE | SE ELIMINO PUENTE HACIA PARARRAYO DE CLIENTE Y AL CERRAR MACHETE DISPARO ALIMENTADOR | S23041600047 | Partial_restoration | Customer-Related Interruption | Include | Include | Public | 55 | 2023-04-16 | 11770 | keep | 0 | Apr | 2023 | 0.0080165 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-16 15:49 | 2023-04-16 15:50 | 4664 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR AISLADOR ROTO | M23041600085 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-04-16 | 4664 | keep | 0 | Apr | 2023 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2023-04-16 15:53 | 2023-04-16 15:54 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041600089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
GUAYAMA | 2023-04-16 15:58 | 2023-04-16 17:06 | 3718 | 1:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR QUEMADO | P23041600079 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 68 | 2023-04-16 | 252824 | keep | 0 | Apr | 2023 | 0.1722 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
FAJARDO | 2023-04-16 15:59 | 2023-04-16 16:19 | 1 | 0:20 | P | ANIMAL | 1 X 25 EN C/L CRUCE POR AVE | R23041600024 | New_Event | Animals | Include | Include | Wildlife | 20 | 2023-04-16 | 20 | keep | 0 | Apr | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-16 15:59 | 2023-04-16 16:00 | 4664 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR AISLADOR ROTO | M23041600093 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-04-16 | 4664 | keep | 0 | Apr | 2023 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
BAYAMON | 2023-04-16 16:02 | 2023-04-16 17:57 | 15 | 1:55 | P | DESGANCHE | 1 X 30 EN C/L 1 X 50 ENC/L DESGANCHE | B23041600107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-04-16 | 1725 | keep | 0 | Apr | 2023 | 0.0011749 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-04-16 16:04 | 2023-04-16 16:05 | 4664 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR AISLADOR ROTO | M23041600094 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-04-16 | 4664 | keep | 0 | Apr | 2023 | 0.0031766 | 0.0031766 | Momentary | FALSE | FALSE | Not_TMED_Event | 4664
CAGUAS | 2023-04-16 16:10 | 2023-04-16 18:04 | 5 | 1:54 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23041600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-04-16 | 570 | keep | 0 | Apr | 2023 | 0.00038822 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-04-16 16:18 | 2023-04-16 16:39 | 78 | 0:21 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C23041600096 | New_Event | Animals | Include | Include | Wildlife | 21 | 2023-04-16 | 1638 | keep | 0 | Apr | 2023 | 0.0011156 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
CAGUAS | 2023-04-16 16:19 | 2023-04-16 22:31 | 151 | 6:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23041600097 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 372 | 2023-04-16 | 56172 | keep | 0 | Apr | 2023 | 0.038258 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
MAYAGÃœEZ | 2023-04-16 16:30 | 2023-04-16 17:05 | 750 | 0:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR AISLADOR ROTO | M23041600092 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 35 | 2023-04-16 | 26250 | keep | 0 | Apr | 2023 | 0.017879 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
MAYAGÃœEZ | 2023-04-16 16:30 | 2023-04-16 19:00 | 60 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M23041600109 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2023-04-16 | 9000 | keep | 0 | Apr | 2023 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-04-16 16:35 | 2023-04-16 17:47 | 190 | 1:12 | P | ANIMAL | 1 X 140 EN CORTE DE LINEA CRUCE POR AVE | C23041600100 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-04-16 | 13680 | keep | 0 | Apr | 2023 | 0.0093174 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
SAN JUAN | 2023-04-16 16:41 | 2023-04-16 16:47 | 4291 | 0:06 | T | PROBLEMA DEL CLIENTE | SE ELIMINO PUENTE HACIA PARARRAYO DE CLIENTE Y AL CERRAR MACHETE DISPARO ALIMENTADOR SE CERRARON LOS MACHETE MUY ALTO Y SE CERRO ALIMENTADOR 100% EN SERVICIO | S23041600047 | Additional_clients | Customer-Related Interruption | Include | Include | Public | 6 | 2023-04-16 | 25746 | keep | 0 | Apr | 2023 | 0.017535 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-16 16:41 | 2023-04-16 16:42 | 4641 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041600113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-16 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2023-04-16 16:42 | 2023-04-16 18:41 | 150 | 1:59 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23041600120 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 119 | 2023-04-16 | 17850 | keep | 0 | Apr | 2023 | 0.012158 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-04-16 17:05 | 2023-04-16 17:06 | 4664 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DEL INTERRUPTOR AISLADOR ROTO | M23041600121 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-04-16 | 4664 | keep | 0 | Apr | 2023 | 0.0031766 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-16 17:06 | 2023-04-16 17:15 | 750 | 0:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA REMPLAZAR AISLADOR ROTO | M23041600092 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 9 | 2023-04-16 | 6750 | keep | 0 | Apr | 2023 | 0.0045974 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
PONCE | 2023-04-16 17:07 | 2023-04-16 20:32 | 75 | 3:25 | P | CAUSAS EXTERNAS | 1 X 50 EN SALIDA RISER 1 X 65 EN CORTE DE LINEA TENNIS CRUZANDO FASE | P23041600102 | New_Event | Damage From Public | Include | Include | Public | 205 | 2023-04-16 | 15375 | keep | 0 | Apr | 2023 | 0.010472 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-04-16 17:08 | 2023-04-16 19:26 | 42 | 2:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE DE PALMA | C23041600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-04-16 | 5796 | keep | 0 | Apr | 2023 | 0.0039476 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
HUMACAO | 2023-04-16 17:16 | 2023-04-16 17:44 | 12 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C23041600105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-04-16 | 336 | keep | 0 | Apr | 2023 | 0.00022885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-16 17:29 | 2023-04-16 21:00 | 380 | 3:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA QUEMADA | C23041600109 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2023-04-16 | 80180 | keep | 0 | Apr | 2023 | 0.05461 | 0.00025882 | Sustained | FALSE | FALSE | Not_TMED_Event | 380
MAYAGÃœEZ | 2023-04-16 17:31 | 2023-04-16 19:50 | 20 | 2:19 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23041600133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 139 | 2023-04-16 | 2780 | keep | 0 | Apr | 2023 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-16 17:40 | 2023-04-17 17:25 | 12 | 23:45 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | S23041600139 | New_Event | Primary Wire Break | Include | Include | Equipment | 1425 | 2023-04-16 | 17100 | keep | 0 | Apr | 2023 | 0.011647 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-04-16 17:51 | 2023-04-16 17:52 | 2132 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | A23041600029 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 2132 | keep | 0 | Apr | 2023 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2023-04-16 17:51 | 2023-04-16 17:52 | 2366 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | A23041600029 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 2366 | keep | 0 | Apr | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2023-04-16 17:51 | 2023-04-16 17:52 | 1976 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | A23041600029 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 1976 | keep | 0 | Apr | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2023-04-16 17:51 | 2023-04-16 17:52 | 3688 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE LINEA 36100 SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | A23041600029 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 3688 | keep | 0 | Apr | 2023 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600109 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600109 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 2735 | keep | 0 | Apr | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600109 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 1070 | keep | 0 | Apr | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600110 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 1647 | keep | 0 | Apr | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600110 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 3295 | keep | 0 | Apr | 2023 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600110 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 1180 | keep | 0 | Apr | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600111 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 320 | keep | 0 | Apr | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-04-16 17:51 | 2023-04-16 17:52 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 36100 DE PIÃ‘AS A CIALES SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600111 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-16 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
CAGUAS | 2023-04-16 18:04 | 2023-04-16 18:05 | 3495 | 0:01 | P | DESGANCHE | RECERRO INTERRUPTOR 20% DE SU CARGA POR EL 3604-06 EN SERVICIO | C23041600114 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-16 | 3495 | keep | 0 | Apr | 2023 | 0.0023804 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-16 18:05 | 2023-04-16 18:16 | 5 | 0:11 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23041600095 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 11 | 2023-04-16 | 55 | keep | 0 | Apr | 2023 | 3.746e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-04-16 18:08 | 2023-04-17 11:35 | 27 | 17:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23041600113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1047 | 2023-04-16 | 28269 | keep | 0 | Apr | 2023 | 0.019254 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
AGUADILLA | 2023-04-16 18:13 | 2023-04-16 19:50 | 50 | 1:37 | P | ARBOL SOBRE LINEA | 1 X 65 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23041600142 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 97 | 2023-04-16 | 4850 | keep | 0 | Apr | 2023 | 0.0033033 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-16 18:14 | 2023-04-16 22:51 | 40 | 4:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y 1 X 25 RISER SE REMPLAZO CAJA QUEMADA | S23041600141 | New_Event | Cutout Failure | Include | Include | Equipment | 277 | 2023-04-16 | 11080 | keep | 0 | Apr | 2023 | 0.0075465 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-16 18:16 | 2023-04-16 18:17 | 3495 | 0:01 | P | DESGANCHE | RECERRO INTERRUPTOR 20% DE SU CARGA POR EL 3604-06 EN SERVICIO | C23041600118 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-16 | 3495 | keep | 0 | Apr | 2023 | 0.0023804 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-16 18:17 | 2023-04-16 18:19 | 946 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR SU CARGA POR 1525-05 SE PROBO QUEDO EN SERVICIO | S23041600142 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-16 | 1892 | keep | 0 | Apr | 2023 | 0.0012886 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2023-04-16 18:17 | 2023-04-16 18:19 | 937 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA 1525-02 SE PROBO QUEDO EN SERVICIO | S23041600142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-16 | 1874 | keep | 0 | Apr | 2023 | 0.0012764 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
CAGUAS | 2023-04-16 18:17 | 2023-04-17 10:09 | 5 | 15:52 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23041600095 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 952 | 2023-04-16 | 4760 | keep | 0 | Apr | 2023 | 0.003242 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-04-16 18:18 | 2023-04-16 18:55 | 10 | 0:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA | R23041600028 | New_Event | Cutout Failure | Include | Include | Equipment | 37 | 2023-04-16 | 370 | keep | 0 | Apr | 2023 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-16 18:51 | 2023-04-16 18:53 | 3957 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO | S23041600151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-16 | 7914 | keep | 0 | Apr | 2023 | 0.0053902 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
PONCE | 2023-04-16 19:01 | 2023-04-16 21:17 | 24 | 2:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23041600145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-04-16 | 3264 | keep | 0 | Apr | 2023 | 0.0022231 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2023-04-16 19:06 | 2023-04-17 14:34 | 120 | 19:28 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | A23041600035 | New_Event | Primary Wire Break | Include | Include | Equipment | 1168 | 2023-04-16 | 140160 | keep | 0 | Apr | 2023 | 0.095462 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-04-16 19:11 | 2023-04-16 23:11 | 1647 | 4:00 | T | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO EL BKR Y SE TRANSFIRIO LA CARGA AL 9501-01 SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600257 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 240 | 2023-04-16 | 395280 | keep | 0 | Apr | 2023 | 0.26922 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-04-16 19:11 | 2023-04-16 23:45 | 3295 | 4:34 | T | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO EL BKR Y SE TRANSFIRIO 40% DE LA CARGA AL 9501-02 SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600257 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 274 | 2023-04-16 | 902830 | keep | 0 | Apr | 2023 | 0.61491 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-04-16 19:11 | 2023-04-17 02:43 | 1180 | 7:32 | T | LINEA DE TRANSMISION 115KV | SE SECCIONALIZO EL BKR Y SE TRANSFIRIO 70% DE LA CARGA AL 9801-03 SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600257 | 1st_after_momentary | 115 kV Transmission Line Source | Include | Include | Power supply | 452 | 2023-04-16 | 533360 | keep | 0 | Apr | 2023 | 0.36327 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
VEGA BAJA | 2023-04-16 19:16 | 2023-04-16 19:17 | 2132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041600040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 2132 | keep | 0 | Apr | 2023 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
PONCE | 2023-04-16 19:17 | 2023-04-17 07:01 | 8 | 11:44 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 25KVA A 7620VOLTS AVERIADO | P23041600151 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 704 | 2023-04-16 | 5632 | keep | 0 | Apr | 2023 | 0.0038359 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-16 19:20 | 2023-04-16 19:21 | 2340 | 0:01 | T | CRUCETA DEFECTUOSA O AVERIADA | RECIERRE | P23041600152 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1 | 2023-04-16 | 2340 | keep | 0 | Apr | 2023 | 0.0015938 | 0.0015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 2340
YAUCO | 2023-04-16 19:21 | 2023-04-17 19:04 | 150 | 23:43 | P | CRUCETA DEFECTUOSA O AVERIADA | 3 X 50 EN CORTE DE LINEA SE REMPLAZARON 4 CRUCETAS PARTIDAS | M23041600169 | 1st_after_momentary | Primary Crossarm Failure | Include | Include | Equipment | 1423 | 2023-04-16 | 213450 | keep | 0 | Apr | 2023 | 0.14538 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-16 19:45 | 2023-04-16 19:46 | 3957 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO | S23041600164 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 3957 | keep | 0 | Apr | 2023 | 0.0026951 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
GUAYAMA | 2023-04-16 19:50 | 2023-04-17 09:52 | 30 | 14:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 40 EN CORTE DE LINEA | P23041600156 | New_Event | Cutout Failure | Include | Include | Equipment | 842 | 2023-04-16 | 25260 | keep | 0 | Apr | 2023 | 0.017204 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-04-16 19:59 | 2023-04-16 22:30 | 200 | 2:31 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | A23041600044 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-04-16 | 30200 | keep | 0 | Apr | 2023 | 0.020569 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-04-16 20:21 | 2023-04-16 20:22 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041600168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-16 | 3041 | keep | 0 | Apr | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2023-04-16 20:46 | 2023-04-17 20:28 | 54 | 23:42 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L SE REPARO CONDUCTOR PRIMARIO | S23041600177 | New_Event | Primary Wire Break | Include | Include | Equipment | 1422 | 2023-04-16 | 76788 | keep | 0 | Apr | 2023 | 0.0523 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
ARECIBO | 2023-04-16 20:50 | 2023-04-17 09:30 | 5 | 12:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A23041600050 | New_Event | Cutout Failure | Include | Include | Equipment | 760 | 2023-04-16 | 3800 | keep | 0 | Apr | 2023 | 0.0025882 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-04-16 20:51 | 2023-04-17 00:12 | 150 | 3:21 | P | DESCONECTIVO DEFECTUOSO | SE REPARO MACHETE AVERIADO | A23041600053 | New_Event | Switch Failure | Include | Include | Equipment | 201 | 2023-04-16 | 30150 | keep | 0 | Apr | 2023 | 0.020535 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-04-16 23:22 | 2023-04-17 02:23 | 230 | 3:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO POSTAFUSIBLE | C23041600137 | New_Event | Cutout Failure | Include | Include | Equipment | 181 | 2023-04-16 | 41630 | keep | 0 | Apr | 2023 | 0.028354 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
CAGUAS | 2023-04-16 23:35 | 2023-04-17 01:30 | 79 | 1:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | C23041600142 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2023-04-16 | 9085 | keep | 0 | Apr | 2023 | 0.0061878 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
VEGA BAJA | 2023-04-16 23:35 | 2023-04-17 08:40 | 80 | 9:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041600162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 545 | 2023-04-16 | 43600 | keep | 0 | Apr | 2023 | 0.029696 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-16 23:45 | 2023-04-17 09:00 | 1318 | 9:15 | P | LINEA DE TRANSMISION 115KV | SE REPARO BASE DE FUSIBLE DE LA ALTA DEL XMR Y SE CERRO BKR SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600257 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 555 | 2023-04-16 | 731490 | keep | 0 | Apr | 2023 | 0.49821 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-17 | 2023-04-17 11:02 | 1483 | 11:02 | P | ALIMENTADOR AMARRADO | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 30% DE SU CARGA POR EL 1336-08 | S23041700001 | New_Event | Feeder Load Transferred | Include | Include | Other | 662 | 2023-04-17 | 981746 | keep | 0 | Apr | 2023 | 0.66866 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-04-17 | 2023-04-17 18:25 | 1531 | 18:25 | P | ALIMENTADOR AMARRADO | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 15% DE SU CARGA POR EL 1336-08 | S23041700001 | New_Event | Feeder Load Transferred | Include | Include | Other | 1105 | 2023-04-17 | 1691755 | keep | 0 | Apr | 2023 | 1.1522 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-04-17 | 2023-04-17 03:12 | 1061 | 3:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION BKR 0040 NO ABRIO EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. | S23041700122 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 192 | 2023-04-17 | 203712 | keep | 0 | Apr | 2023 | 0.13875 | 0.00072264 | Sustained | FALSE | FALSE | Not_TMED_Event | 1061
SAN JUAN | 2023-04-17 | 2023-04-17 03:12 | 742 | 3:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION BKR 0040 NO ABRIÃ“ EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. | S23041700122 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 192 | 2023-04-17 | 142464 | keep | 0 | Apr | 2023 | 0.097032 | 0.00050537 | Sustained | FALSE | FALSE | Not_TMED_Event | 742
SAN JUAN | 2023-04-17 | 2023-04-17 03:12 | 998 | 3:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION BKR 0040 NO ABRIÃ“ EN AVERÃA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. | S23041700122 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 192 | 2023-04-17 | 191616 | keep | 0 | Apr | 2023 | 0.13051 | 0.00067973 | Sustained | FALSE | FALSE | Not_TMED_Event | 998
SAN JUAN | 2023-04-17 | 2023-04-17 03:12 | 1397 | 3:12 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE TRANSMISION BKR 0040 NO ABRIÃ“ EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. | S23041700122 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 192 | 2023-04-17 | 268224 | keep | 0 | Apr | 2023 | 0.18269 | 0.00095149 | Sustained | FALSE | FALSE | Not_TMED_Event | 1397
CANOVANAS | 2023-04-17 | 2023-04-17 04:23 | 1743 | 4:23 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 40% DE SU CARGA POR EL 1619-02, 25% POR EL 1620-04 LLEVA LA CARGA DEL 1657-02 | S23041700001 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 263 | 2023-04-17 | 458409 | keep | 0 | Apr | 2023 | 0.31222 | 0.0011871 | Sustained | FALSE | FALSE | Not_TMED_Event | 1743
SAN JUAN | 2023-04-17 | 2023-04-17 08:30 | 6244 | 8:30 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 | S23041700001 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 510 | 2023-04-17 | 3184440 | keep | 0 | Apr | 2023 | 2.1689 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
SAN JUAN | 2023-04-17 | 2023-04-17 18:25 | 5290 | 18:25 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 LLEVA 15% DEL 1204-05 | S23041700001 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 1105 | 2023-04-17 | 5845450 | keep | 0 | Apr | 2023 | 3.9813 | 0.003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 5290
SAN JUAN | 2023-04-17 | 2023-04-17 12:55 | 207 | 12:55 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 | S23041700001 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 775 | 2023-04-17 | 160425 | keep | 0 | Apr | 2023 | 0.10926 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-04-17 | 2023-04-17 06:57 | 40 | 6:57 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 90% DE SU CARGA POR EL 1620-01 | S23041700001 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 417 | 2023-04-17 | 16680 | keep | 0 | Apr | 2023 | 0.011361 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-17 | 2023-04-17 00:03 | 601 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV BERWIND TC BKR 0040 NO ABRIO EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. SE APAGA LINEA 17400 LLEVANDO LA CARGA DE SUB. 1437 SAN JOSE . | S23041700015 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-04-17 | 1803 | keep | 0 | Apr | 2023 | 0.001228 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2023-04-17 | 2023-04-17 00:03 | 640 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV BERWIND TC BKR 0040 NO ABRIO EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. SE APAGA LINEA 17400 LLEVANDO LA CARGA DE SUB. 1437 SAN JOSE . | S23041700015 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-04-17 | 1920 | keep | 0 | Apr | 2023 | 0.0013077 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2023-04-17 | 2023-04-17 00:03 | 1699 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV BERWIND TC BKR 0040 NO ABRIO EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. SE APAGA LINEA 17400 LLEVANDO LA CARGA DE SUB. 1437 SAN JOSE . | S23041700015 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-04-17 | 5097 | keep | 0 | Apr | 2023 | 0.0034715 | 0.0011572 | Momentary | FALSE | FALSE | Not_TMED_Event | 1699
SAN JUAN | 2023-04-17 | 2023-04-17 00:03 | 892 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV BERWIND TC BKR 0040 NO ABRIO EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. SE APAGA LINEA 17400 LLEVANDO LA CARGA DE SUB. 1437 SAN JOSE . | S23041700015 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-04-17 | 2676 | keep | 0 | Apr | 2023 | 0.0018226 | 0.00060754 | Momentary | FALSE | FALSE | Not_TMED_Event | 892
SAN JUAN | 2023-04-17 | 2023-04-17 00:03 | 1066 | 0:03 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA 38KV BERWIND TC BKR 0040 NO ABRIO EN AVERIA ALIMENTADOR 1336-8 DEBIDO A BOBINA DE TRIP QUEMADA. DISPARA LA BARRA DE 38KV BERWIND TC Y BANCO 115/38KV. SE APAGA LINEA 17400 LLEVANDO LA CARGA DE SUB. 1437 SAN JOSE . | S23041700015 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 3 | 2023-04-17 | 3198 | keep | 0 | Apr | 2023 | 0.0021781 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
CANOVANAS | 2023-04-17 | 2023-04-17 04:23 | 1937 | 4:23 | T | ALIMENTADOR AMARRADO | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 CARGA POR EL 1336-06 | S23041700001 | New_Event | Feeder Load Transferred | Include | Include | Other | 263 | 2023-04-17 | 509431 | keep | 0 | Apr | 2023 | 0.34697 | 0.0013193 | Sustained | FALSE | FALSE | Not_TMED_Event | 1937
AGUADILLA | 2023-04-17 00:05 | 2023-04-17 00:06 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23041700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 1192 | keep | 0 | Apr | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
HUMACAO | 2023-04-17 00:41 | 2023-04-17 00:42 | 2873 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23041700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 2873 | keep | 0 | Apr | 2023 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
SAN JUAN | 2023-04-17 01:45 | 2023-04-17 06:56 | 5 | 5:11 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECIONALIZO TRAMO PARA REPARA VS AVERIADO SJ-230417-02 LLEVA LA CARGA DEL 1117-08 | S23041700431 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 311 | 2023-04-17 | 1555 | keep | 0 | Apr | 2023 | 0.0010591 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-04-17 01:45 | 2023-04-17 09:54 | 466 | 8:09 | T | ALIMENTADOR AMARRADO | SE SECIONALIZO TRAMO Y SE REPARO AVERIA EN SU POLICIA MUNICIPAL SJ-230417-02 CARGA POR EL 1116-05 | S23041700431 | New_Event | Feeder Load Transferred | Include | Include | Other | 489 | 2023-04-17 | 227874 | keep | 0 | Apr | 2023 | 0.1552 | 0.00031739 | Sustained | FALSE | FALSE | Not_TMED_Event | 466
CAGUAS | 2023-04-17 02:05 | 2023-04-17 02:06 | 1228 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C23041700003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-17 | 1228 | keep | 0 | Apr | 2023 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2023-04-17 02:06 | 2023-04-17 12:43 | 30 | 10:37 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23041700004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 637 | 2023-04-17 | 19110 | keep | 0 | Apr | 2023 | 0.013016 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-17 02:43 | 2023-04-17 09:00 | 354 | 6:17 | P | LINEA DE TRANSMISION 115KV | SE REPARO BASE DE SOPORTE DE FUSIBLE DE ALTA DE XMR Y SE CERRO BKR SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600257 | Partial_restoration | 115 kV Transmission Line Source | Include | Include | Power supply | 377 | 2023-04-17 | 133458 | keep | 0 | Apr | 2023 | 0.090898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-17 04:23 | 2023-04-17 06:57 | 286 | 2:34 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA TRANSFERIR LAS CARGAS Y SECCIONALIZAR AVERIA SJ-230417-01 | S23041700001 | Partial_restoration | Feeder Breaker Failure | Include | Include | Equipment | 154 | 2023-04-17 | 44044 | keep | 0 | Apr | 2023 | 0.029998 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-04-17 05:29 | 2023-04-17 09:36 | 78 | 4:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMEPLAZO PORTAFUSIBLE QUEMADO | C23041700006 | New_Event | Cutout Failure | Include | Include | Equipment | 247 | 2023-04-17 | 19266 | keep | 0 | Apr | 2023 | 0.013122 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
PONCE | 2023-04-17 05:48 | 2023-04-17 06:51 | 40 | 1:03 | P | DESGANCHE | 1 X 40 EN SALIDA RISER DESGANCHE | P23041700032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-04-17 | 2520 | keep | 0 | Apr | 2023 | 0.0017164 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-04-17 06:06 | 2023-04-17 12:37 | 20 | 6:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P23041700033 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 391 | 2023-04-17 | 7820 | keep | 0 | Apr | 2023 | 0.0053262 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-17 06:07 | 2023-04-17 14:50 | 271 | 8:43 | S | ANIMAL | LOCKOUT CRUCE POR AVE EN BARRA DE DISTRIBUCION SJ-230417-03 | S23041700588 | New_Event | Animals | Include | Include | Wildlife | 523 | 2023-04-17 | 141733 | keep | 0 | Apr | 2023 | 0.096534 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-04-17 06:07 | 2023-04-17 11:07 | 74 | 5:00 | S | ANIMAL | LOCKOUT CRUCE POR AVE EN BARRA DE DISTRIBUCION SJ-230417-03 | S23041700588 | New_Event | Animals | Include | Include | Wildlife | 300 | 2023-04-17 | 22200 | keep | 0 | Apr | 2023 | 0.01512 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
YAUCO | 2023-04-17 06:09 | 2023-04-17 07:50 | 150 | 1:41 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | P23041700035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-04-17 | 15150 | keep | 0 | Apr | 2023 | 0.010319 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-04-17 06:10 | 2023-04-17 10:11 | 300 | 4:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23041700004 | New_Event | Cutout Failure | Include | Include | Equipment | 241 | 2023-04-17 | 72300 | keep | 0 | Apr | 2023 | 0.049243 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2023-04-17 06:33 | 2023-04-17 12:47 | 8 | 6:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTES SECUNDARIO | B23041700011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 374 | 2023-04-17 | 2992 | keep | 0 | Apr | 2023 | 0.0020378 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-17 06:39 | 2023-04-17 13:26 | 200 | 6:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | C23041700008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 407 | 2023-04-17 | 81400 | keep | 0 | Apr | 2023 | 0.055441 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-04-17 06:41 | 2023-04-17 19:05 | 35 | 12:24 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REEMPLAZO CRUCETA PARTIDA 3 X 80 1 X 65 EN CORTE DE LINEA | P23041700042 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 744 | 2023-04-17 | 26040 | keep | 0 | Apr | 2023 | 0.017736 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-04-17 06:52 | 2023-04-17 08:45 | 20 | 1:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23041700006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-04-17 | 2260 | keep | 0 | Apr | 2023 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-17 06:56 | 2023-04-17 09:04 | 343 | 2:08 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0020 POR AVERIA EN SU DEL ALIMENTADOR 1116-05 BOBINA DE TRIP DEL BKR AVERIADA LLEVA 30% DEL 1115-04 | S23041700431 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 128 | 2023-04-17 | 43904 | keep | 0 | Apr | 2023 | 0.029903 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
SAN JUAN | 2023-04-17 06:56 | 2023-04-17 09:04 | 996 | 2:08 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0020 POR AVERIA EN SU DEL ALIMENTADOR 1116-05 BOBINA DE TRIP DEL BKR AVERIADA | S23041700431 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 128 | 2023-04-17 | 127488 | keep | 0 | Apr | 2023 | 0.086831 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
SAN JUAN | 2023-04-17 06:56 | 2023-04-17 09:04 | 169 | 2:08 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0020 POR AVERIA EN SU DEL ALIMENTADOR 1116-05 BOBINA DE TRIP DEL BKR AVERIADA | S23041700431 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 128 | 2023-04-17 | 21632 | keep | 0 | Apr | 2023 | 0.014733 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
SAN JUAN | 2023-04-17 06:56 | 2023-04-17 09:04 | 5 | 2:08 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DEL 0020 POR AVERIA EN SU DEL ALIMENTADOR 1116-05 BOBINA DE TRIP DEL BKR AVERIADA | S23041700431 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 128 | 2023-04-17 | 640 | keep | 0 | Apr | 2023 | 0.0004359 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-04-17 07:01 | 2023-04-17 07:02 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23041700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 2379 | keep | 0 | Apr | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2023-04-17 07:02 | 2023-04-17 14:14 | 8 | 7:12 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 25 KVA A 7620VOLTS AVERIADO | P23041600151 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 432 | 2023-04-17 | 3456 | keep | 0 | Apr | 2023 | 0.0023539 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-17 07:24 | 2023-04-17 07:25 | 4089 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2304170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 4089 | keep | 0 | Apr | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BARRANQUITAS | 2023-04-17 07:41 | 2023-04-17 13:17 | 47 | 5:36 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | C23041700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 336 | 2023-04-17 | 15792 | keep | 0 | Apr | 2023 | 0.010756 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2023-04-17 08:04 | 2023-04-17 13:20 | 160 | 5:16 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | C23041700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-04-17 | 50560 | keep | 0 | Apr | 2023 | 0.034436 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
HUMACAO | 2023-04-17 08:06 | 2023-04-17 08:44 | 1 | 0:38 | P | ANIMAL | 1 X 65 EN RISER CRUCE X AVE | C23041700017 | New_Event | Animals | Include | Include | Wildlife | 38 | 2023-04-17 | 38 | keep | 0 | Apr | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-17 08:15 | 2023-04-17 09:45 | 20 | 1:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23041700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-04-17 | 1800 | keep | 0 | Apr | 2023 | 0.001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-17 08:21 | 2023-04-17 16:15 | 5 | 7:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041700012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 474 | 2023-04-17 | 2370 | keep | 0 | Apr | 2023 | 0.0016142 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-04-17 08:22 | 2023-04-17 10:25 | 1 | 2:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23041700015 | New_Event | Cutout Failure | Include | Include | Equipment | 123 | 2023-04-17 | 123 | keep | 0 | Apr | 2023 | 8.3775e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-17 08:26 | 2023-04-17 08:46 | 1 | 0:20 | P | NO SE REPORTO CAUSA | 1 X 10 EN BANCO DE XMR | R23041700123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2023-04-17 | 20 | keep | 0 | Apr | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-17 08:35 | 2023-04-17 14:00 | 10 | 5:25 | P | MAL TIEMPO/RAYOS | 1 X 30 EN C/L LLUVIA | R23041700125 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 325 | 2023-04-17 | 3250 | keep | 0 | Apr | 2023 | 0.0022136 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-17 08:39 | 2023-04-17 14:00 | 2 | 5:21 | P | PARARRAYOS DEFECTUOSO | 3 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO DEFECTUOSO | M23041700017 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 321 | 2023-04-17 | 642 | keep | 0 | Apr | 2023 | 0.00043726 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-04-17 08:40 | 2023-04-17 11:04 | 4 | 2:24 | P | PROBLEMA DEL CLIENTE | ABRIR RISER PARA DESENERGIZAR T-51 PARA QUE PERITO PUEDA HACER TRABAJOS FID 12471053 WR6311314 | P23041700085 | New_Event | Customer-Related Interruption | Include | Include | Public | 144 | 2023-04-17 | 576 | keep | 0 | Apr | 2023 | 0.00039231 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-04-17 08:45 | 2023-04-17 10:17 | 1 | 1:32 | P | ANIMAL | 1 X 80 EN RISER CRUCE X AVE | C23041700022 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-04-17 | 92 | keep | 0 | Apr | 2023 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-04-17 08:47 | 2023-04-17 09:23 | 1 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 XMR Y SE REPARO BAJANTE SECUNDARIO | R23041700126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2023-04-17 | 36 | keep | 0 | Apr | 2023 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-17 08:50 | 2023-04-17 13:07 | 1 | 4:17 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR Y 1 X 50 EN CORTE DE LINEA DESGANCHE | P23041700087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2023-04-17 | 257 | keep | 0 | Apr | 2023 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-17 08:56 | 2023-04-17 08:57 | 3597 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9405-05 | B2304170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-17 | 3597 | keep | 0 | Apr | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
UTUADO | 2023-04-17 08:56 | 2023-04-17 09:50 | 25 | 0:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041700021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-04-17 | 1350 | keep | 0 | Apr | 2023 | 0.00091948 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-17 08:56 | 2023-04-17 08:57 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 3511 | keep | 0 | Apr | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
SAN JUAN | 2023-04-17 09:04 | 2023-04-17 09:54 | 3 | 0:50 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECIONALIZO TRAMO PARA REPARA VS AVERIADO SJ-230417-02 | S23041700431 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 50 | 2023-04-17 | 150 | keep | 0 | Apr | 2023 | 0.00010216 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-17 09:21 | 2023-04-17 11:17 | 37 | 1:56 | P | ANIMAL | 1 X 20 EN RISER 1 X 100 EN C/L CRUCE POR AVE | B23041700031 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-04-17 | 4292 | keep | 0 | Apr | 2023 | 0.0029233 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
MAYAGÃœEZ | 2023-04-17 09:21 | 2023-04-17 09:31 | 4664 | 0:10 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 6012-02 SE VERIFICO PERSONAL FUERA DE LAS LINEAS SE CERRO INTERRUPTOR | M23041700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-04-17 | 46640 | keep | 0 | Apr | 2023 | 0.031766 | 0.0031766 | Sustained | FALSE | FALSE | Not_TMED_Event | 4664
MAYAGÃœEZ | 2023-04-17 09:21 | 2023-04-17 09:23 | 810 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE PARTIÃ“ TENSOR POR ACCIDENTE DE AUTOMÃ“VIL. | M23041700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-17 | 1620 | keep | 0 | Apr | 2023 | 0.0011034 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2023-04-17 09:21 | 2023-04-17 09:23 | 1235 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE PARTIÃ“ TENSOR POR ACCIDENTE DE AUTOMÃ“VIL. | M23041700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-17 | 2470 | keep | 0 | Apr | 2023 | 0.0016823 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2023-04-17 09:21 | 2023-04-17 09:23 | 93 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE PARTIÃ“ TENSOR POR ACCIDENTE DE AUTOMÃ“VIL. | M23041700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-17 | 186 | keep | 0 | Apr | 2023 | 0.00012668 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2023-04-17 09:21 | 2023-04-17 09:23 | 1825 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE PARTIÃ“ TENSOR POR ACCIDENTE DE AUTOMÃ“VIL. | M23041700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-17 | 3650 | keep | 0 | Apr | 2023 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2023-04-17 09:21 | 2023-04-17 09:23 | 3230 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5600 SE PARTIÃ“ TENSOR POR ACCIDENTE DE AUTOMÃ“VIL. | M23041700036 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-17 | 6460 | keep | 0 | Apr | 2023 | 0.0043999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
CANOVANAS | 2023-04-17 09:29 | 2023-04-17 11:24 | 25 | 1:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23041700130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-04-17 | 2875 | keep | 0 | Apr | 2023 | 0.0019581 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-17 09:31 | 2023-04-17 14:00 | 8 | 4:29 | P | NO SE REPORTO CAUSA | 1 X 15 XMR | B23041700032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 269 | 2023-04-17 | 2152 | keep | 0 | Apr | 2023 | 0.0014657 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-17 09:36 | 2023-04-17 19:33 | 186 | 9:57 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | S23041701261 | New_Event | Animals | Include | Include | Wildlife | 597 | 2023-04-17 | 111042 | keep | 0 | Apr | 2023 | 0.07563 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
YAUCO | 2023-04-17 09:51 | 2023-04-17 14:28 | 1 | 4:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23041700049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2023-04-17 | 277 | keep | 0 | Apr | 2023 | 0.00018866 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-17 09:54 | 2023-04-17 15:16 | 1 | 5:22 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECIONALIZO TRAMO Y SE REPARO AVERIA EN SU POLICIA MUNICIPAL SJ-230417-02 | S23041700431 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 322 | 2023-04-17 | 322 | keep | 0 | Apr | 2023 | 0.00021931 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-17 09:54 | 2023-04-17 10:07 | 826 | 0:13 | P | LINEA DE TRANSMISION 115KV | SE ABRIO N/O CONTRA 9801-03 Y SE CERRO MACHETES PARA NORMALIZAR CARGA ESTO SE HIZO PORQUE NO HAY FASEO ENTRE AMBOS. SUB. 9502 FUNDIÃ“ UN FUSIBLE Y SE QUEMO PORTAFUSIBLE | B23041600257 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 13 | 2023-04-17 | 10738 | keep | 0 | Apr | 2023 | 0.0073136 | 0.00056258 | Sustained | FALSE | FALSE | Not_TMED_Event | 826
BAYAMON | 2023-04-17 10:10 | 2023-04-17 12:57 | 8 | 2:47 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23041700041 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-04-17 | 1336 | keep | 0 | Apr | 2023 | 0.00090994 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-04-17 10:20 | 2023-04-17 15:00 | 10 | 4:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23041700037 | New_Event | Cutout Failure | Include | Include | Equipment | 280 | 2023-04-17 | 2800 | keep | 0 | Apr | 2023 | 0.0019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-17 10:37 | 2023-04-17 12:40 | 50 | 2:03 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | R23041700134 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-04-17 | 6150 | keep | 0 | Apr | 2023 | 0.0041887 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-17 10:44 | 2023-04-17 17:10 | 31 | 6:26 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR Y SE PARO POSTE DE 40' Y SE TRANSFIRIEON LINEAS SECUNDARIAS A POSTE NUEVO | B23041700044 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 386 | 2023-04-17 | 11966 | keep | 0 | Apr | 2023 | 0.00815 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
MAYAGÃœEZ | 2023-04-17 10:52 | 2023-04-17 10:53 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23041700069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 312 | keep | 0 | Apr | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
CANOVANAS | 2023-04-17 10:56 | 2023-04-17 10:57 | 188 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE 1602-05 | R23041700138 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-04-17 | 188 | keep | 0 | Apr | 2023 | 0.00012805 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
ARECIBO | 2023-04-17 11:10 | 2023-04-17 12:05 | 8 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A23041700045 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-04-17 | 440 | keep | 0 | Apr | 2023 | 0.00029968 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-17 11:20 | 2023-04-17 14:47 | 5 | 3:27 | P | FUEGO | 1 X 10 EN XMR CASAS SE QUEMARON POR CORTO CIRCUITO | C23041700043 | New_Event | Fire | Include | Include | Public | 207 | 2023-04-17 | 1035 | keep | 0 | Apr | 2023 | 0.00070493 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-04-17 11:21 | 2023-04-17 16:54 | 50 | 5:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO PORTAFUSIBLE | C23041700045 | New_Event | Cutout Failure | Include | Include | Equipment | 333 | 2023-04-17 | 16650 | keep | 0 | Apr | 2023 | 0.01134 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-17 11:40 | 2023-04-17 12:14 | 60 | 0:34 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M23041700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2023-04-17 | 2040 | keep | 0 | Apr | 2023 | 0.0013894 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-04-17 11:48 | 2023-04-17 15:30 | 1 | 3:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE MONTURA DE TRANSFORMADORES | A23041700054 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-04-17 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-17 12:47 | 2023-04-17 12:48 | 188 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE 1602-05 | R23041700149 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-04-17 | 188 | keep | 0 | Apr | 2023 | 0.00012805 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
CANOVANAS | 2023-04-17 12:54 | 2023-04-17 14:31 | 188 | 1:37 | T | TERMINACION SOTERRADA AVERIADA | TERMINACION QUEMADA EN RISER DE SALIDA HACIA BKR | R23041700151 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 97 | 2023-04-17 | 18236 | keep | 0 | Apr | 2023 | 0.01242 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
PONCE | 2023-04-17 12:56 | 2023-04-17 13:28 | 1 | 0:32 | P | ANIMAL | 1 X 100 SMU EN BOVEDA POR GATO | P23041700017 | New_Event | Animals | Include | Include | Wildlife | 32 | 2023-04-17 | 32 | keep | 0 | Apr | 2023 | 2.1795e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-17 12:57 | 2023-04-17 12:58 | 4369 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE | C2304170000X | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-04-17 | 4369 | keep | 0 | Apr | 2023 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2023-04-17 12:58 | 2023-04-17 17:11 | 120 | 4:13 | P | TERMINACION SOTERRADA AVERIADA | 1 X 80 EN C/L SE REEMPLAZO TERMINACION EN PROVISIONAL AEREO @ T-20 | C23041700068 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 253 | 2023-04-17 | 30360 | keep | 0 | Apr | 2023 | 0.020678 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-04-17 13:09 | 2023-04-17 15:10 | 12 | 2:01 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23041700066 | New_Event | Animals | Include | Include | Wildlife | 121 | 2023-04-17 | 1452 | keep | 0 | Apr | 2023 | 0.00098895 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-04-17 13:16 | 2023-04-17 14:15 | 1 | 0:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23041700097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 59 | 2023-04-17 | 59 | keep | 0 | Apr | 2023 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-17 13:17 | 2023-04-17 13:35 | 15 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | A23041700035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-04-17 | 270 | keep | 0 | Apr | 2023 | 0.0001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-17 13:52 | 2023-04-17 14:36 | 167 | 0:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CAJA PRIMARIA ARQUEANDO PARA REEMPLAZARLA Y SE REPARO BAJANTE PRIMARIO DE LINEA CAJA | C23041700088 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2023-04-17 | 7348 | keep | 0 | Apr | 2023 | 0.0050047 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
GUAYAMA | 2023-04-17 14:07 | 2023-04-17 17:10 | 7 | 3:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P23041700196 | New_Event | Cutout Failure | Include | Include | Equipment | 183 | 2023-04-17 | 1281 | keep | 0 | Apr | 2023 | 0.00087248 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-04-17 14:10 | 2023-04-17 15:25 | 12 | 1:15 | P | PROBLEMA DEL CLIENTE | SE ABRE TRANSFORMADOR PARA CONECTAR TOMA | P23041700198 | New_Event | Customer-Related Interruption | Include | Include | Public | 75 | 2023-04-17 | 900 | keep | 0 | Apr | 2023 | 0.00061299 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-04-17 14:43 | 2023-04-17 17:40 | 11 | 2:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO DE SECUNDARIAS | R23041700159 | New_Event | Secondary Wire Break | Include | Include | Equipment | 177 | 2023-04-17 | 1947 | keep | 0 | Apr | 2023 | 0.0013261 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-04-17 14:51 | 2023-04-17 14:52 | 5663 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1717-02 LLEVA EL 95% 1713-05 SE CERRO X CONTROL | B23041700079 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-17 | 5663 | keep | 0 | Apr | 2023 | 0.003857 | 0.003857 | Momentary | FALSE | FALSE | Not_TMED_Event | 5663
BAYAMON | 2023-04-17 14:51 | 2023-04-17 14:52 | 911 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR LLEVA EL 95% 1713-05 SE CERRO X CONTROL | B23041700079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 911 | keep | 0 | Apr | 2023 | 0.00062048 | 0.00062048 | Momentary | FALSE | FALSE | Not_TMED_Event | 911
BAYAMON | 2023-04-17 14:51 | 2023-04-17 19:10 | 15 | 4:19 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | B23041700078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-04-17 | 3885 | keep | 0 | Apr | 2023 | 0.0026461 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-17 15:05 | 2023-04-18 14:10 | 70 | 23:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA | S23041701739 | New_Event | Cutout Failure | Include | Include | Equipment | 1385 | 2023-04-17 | 96950 | keep | 0 | Apr | 2023 | 0.066032 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-04-17 15:08 | 2023-04-17 20:25 | 35 | 5:17 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041700097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 317 | 2023-04-17 | 11095 | keep | 0 | Apr | 2023 | 0.0075568 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-04-17 15:23 | 2023-04-17 16:20 | 50 | 0:57 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23041700126 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 57 | 2023-04-17 | 2850 | keep | 0 | Apr | 2023 | 0.0019411 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-17 15:31 | 2023-04-17 18:33 | 11 | 3:02 | P | DESGANCHE | 2 X 100 DESGANCHE | R23041700162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-04-17 | 2002 | keep | 0 | Apr | 2023 | 0.0013636 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-04-17 15:36 | 2023-04-18 08:07 | 60 | 16:31 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041700099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 991 | 2023-04-17 | 59460 | keep | 0 | Apr | 2023 | 0.040498 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-17 15:50 | 2023-04-18 07:25 | 35 | 15:35 | P | ANIMAL | 2 X 30 EN MONTURA 3 X 100 EN C/L CRUCE POR AVE | B23041700083 | New_Event | Animals | Include | Include | Wildlife | 935 | 2023-04-17 | 32725 | keep | 0 | Apr | 2023 | 0.022289 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-04-17 16:16 | 2023-04-17 17:13 | 5 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REEMPLAZO PEDESTAL Y AJUSTE EN LAS BARRAS 123V. EVENTO TRANSFERIDO DE ARECIBO | A23041300101 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-04-17 | 285 | keep | 0 | Apr | 2023 | 0.00019411 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-04-17 16:27 | 2023-04-17 19:42 | 150 | 3:15 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23041700113 | New_Event | Animals | Include | Include | Wildlife | 195 | 2023-04-17 | 29250 | keep | 0 | Apr | 2023 | 0.019922 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2023-04-17 16:40 | 2023-04-17 18:00 | 25 | 1:20 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23041700227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 80 | 2023-04-17 | 2000 | keep | 0 | Apr | 2023 | 0.0013622 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-04-17 16:42 | 2023-04-17 19:38 | 291 | 2:56 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA SE ELIMINO PARARRAYO ROTO DESGANCHE | P23041700228 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 176 | 2023-04-17 | 51216 | keep | 0 | Apr | 2023 | 0.034883 | 0.0001982 | Sustained | FALSE | FALSE | Not_TMED_Event | 291
BARRANQUITAS | 2023-04-17 16:44 | 2023-04-17 19:20 | 8 | 2:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO DE TRANSFORMADOR DE 25KVA X 25KVA Y SE DIVIDIERON CARGAS | C23041700117 | New_Event | Service Transformer Failure | Include | Include | Equipment | 156 | 2023-04-17 | 1248 | keep | 0 | Apr | 2023 | 0.00085001 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-04-17 16:46 | 2023-04-17 16:47 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23041700106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 3431 | keep | 0 | Apr | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
VEGA BAJA | 2023-04-17 16:47 | 2023-04-17 18:10 | 50 | 1:23 | P | ANIMAL | 1 X 50 EN RISER AVE CRUZO LINEAS | A23041700105 | New_Event | Animals | Include | Include | Wildlife | 83 | 2023-04-17 | 4150 | keep | 0 | Apr | 2023 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-04-17 16:50 | 2023-04-17 18:15 | 2 | 1:25 | P | OTRAS CAUSAS | SE ABRE TRANSFORMADOR PARA FIJARLO A POSTE | P23041700229 | New_Event | Other Causes | Include | Include | Other | 85 | 2023-04-17 | 170 | keep | 0 | Apr | 2023 | 0.00011579 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-04-17 17:06 | 2023-04-17 20:30 | 50 | 3:24 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23041700120 | New_Event | Animals | Include | Include | Wildlife | 204 | 2023-04-17 | 10200 | keep | 0 | Apr | 2023 | 0.0069472 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-17 17:08 | 2023-04-17 23:57 | 109 | 6:49 | P | INTERRUPTOR DEFECTUOSO O NO OPERA | CG-230417-01 INTERRUPTOR TENIA UNA CAMARA ABRIERTA, NO CERRO CUANDO LO NORMALIZARON. SE TRANSFIRIO CARGA AL 2603-06 | C23041700121 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 409 | 2023-04-17 | 44581 | keep | 0 | Apr | 2023 | 0.030364 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
HUMACAO | 2023-04-17 17:21 | 2023-04-18 16:00 | 5 | 22:39 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO BANCO DE XMR TRIFASICO RELACIONADO A EVENTO C23041700124 | C23041800009 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1359 | 2023-04-17 | 6795 | keep | 0 | Apr | 2023 | 0.004628 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-04-17 17:23 | 2023-04-17 18:50 | 14 | 1:27 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | R23041700170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-04-17 | 1218 | keep | 0 | Apr | 2023 | 0.00082957 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-04-17 17:38 | 2023-04-17 19:45 | 75 | 2:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | A23041700107 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 127 | 2023-04-17 | 9525 | keep | 0 | Apr | 2023 | 0.0064874 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-04-17 17:45 | 2023-04-17 18:11 | 9 | 0:26 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | B23041700101 | New_Event | Animals | Include | Include | Wildlife | 26 | 2023-04-17 | 234 | keep | 0 | Apr | 2023 | 0.00015938 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2023-04-17 17:58 | 2023-04-18 06:43 | 1 | 12:45 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE | P23041700250 | New_Event | Animals | Include | Include | Wildlife | 765 | 2023-04-17 | 765 | keep | 0 | Apr | 2023 | 0.00052104 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-17 18:01 | 2023-04-18 15:10 | 10 | 21:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR 50KVA X 50KVA | A23041700111 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1269 | 2023-04-17 | 12690 | keep | 0 | Apr | 2023 | 0.0086431 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-17 18:02 | 2023-04-17 18:13 | 1 | 0:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO Y SE LEVANTO SECUNDARIA EN EL SUELO | B23041700103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 11 | 2023-04-17 | 11 | keep | 0 | Apr | 2023 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-17 18:25 | 2023-04-17 21:21 | 529 | 2:56 | P | CONDUCTOR ROTO O ABIERTO | LOCKOUT TRIP POR AVERIA DEL INTERRUPTOR 1336-08 SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO PARA REPARAR PUENTE ABIERTO POR OPERACIONES DE TRANSFERENCIA SJ-230417-01 | S23041700001 | New_Event | Primary Wire Break | Include | Include | Equipment | 176 | 2023-04-17 | 93104 | keep | 0 | Apr | 2023 | 0.063413 | 0.0003603 | Sustained | FALSE | FALSE | Not_TMED_Event | 529
MAYAGÃœEZ | 2023-04-17 18:25 | 2023-04-18 01:15 | 1825 | 6:50 | T | CAUSAS EXTERNAS | SE ABRIO INTERRUPTOR PARA REMPLAZO DE POSTE SOCAVADO POR EXPLOSION DE TUBERIA DE AAA | M23041700153 | New_Event | Damage From Public | Include | Include | Public | 410 | 2023-04-17 | 748250 | keep | 0 | Apr | 2023 | 0.50963 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
AGUADILLA | 2023-04-17 18:37 | 2023-04-17 18:38 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23041700158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 3041 | keep | 0 | Apr | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2023-04-17 18:49 | 2023-04-17 18:50 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23041701932 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 338 | keep | 0 | Apr | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
BAYAMON | 2023-04-17 18:57 | 2023-04-17 18:58 | 1784 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1801-02 LLEVA 90% DEL 1711-04 Y LLEVA EL 10% 1717-01 SE CERRO POR CONTROL | B2304170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-17 | 1784 | keep | 0 | Apr | 2023 | 0.0012151 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-04-17 18:57 | 2023-04-17 18:58 | 453 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1801-02 LLEVA 90% DEL 1711-04 Y LLEVA EL 10% 1717-01 SE CERRO POR CONTROL | B2304170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-17 | 453 | keep | 0 | Apr | 2023 | 0.00030854 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-04-17 18:57 | 2023-04-17 18:58 | 186 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR LLEVA 90% DEL 1711-04 Y LLEVA EL 10% 1717-01 SE CERRO POR CONTROL | B2304170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 186 | keep | 0 | Apr | 2023 | 0.00012668 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2023-04-17 19:00 | 2023-04-17 19:01 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23041700108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 1362 | keep | 0 | Apr | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
YAUCO | 2023-04-17 19:07 | 2023-04-17 22:36 | 661 | 3:29 | T | CONDUCTOR ARRIADO O CRUZADO | SE DESENRREDO FACES | P23041700262 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 209 | 2023-04-17 | 138149 | keep | 0 | Apr | 2023 | 0.094093 | 0.0004502 | Sustained | FALSE | FALSE | Not_TMED_Event | 661
PONCE | 2023-04-17 19:25 | 2023-04-17 19:30 | 1979 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | P23041700267 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-17 | 9895 | keep | 0 | Apr | 2023 | 0.0067394 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
BAYAMON | 2023-04-17 19:27 | 2023-04-18 09:45 | 30 | 14:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO C/L TOTAL PARA REEMPLAZAR AISLADOR 1 X 50 EN C/L | B23041700118 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 858 | 2023-04-17 | 25740 | keep | 0 | Apr | 2023 | 0.017531 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-17 19:33 | 2023-04-17 19:34 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23041700169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 990 | keep | 0 | Apr | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
ARECIBO | 2023-04-17 19:36 | 2023-04-17 19:37 | 1883 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23041700126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-17 | 1883 | keep | 0 | Apr | 2023 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | Not_TMED_Event | 1883
HUMACAO | 2023-04-17 20:30 | 2023-04-17 21:14 | 5 | 0:44 | P | ANIMAL | 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA QUEMADA A CAUSA DE CRUCE X AVE | C23041700120 | Partial_restoration | Animals | Include | Include | Wildlife | 44 | 2023-04-17 | 220 | keep | 0 | Apr | 2023 | 0.00014984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-17 20:37 | 2023-04-18 10:45 | 25 | 14:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041700178 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 848 | 2023-04-17 | 21200 | keep | 0 | Apr | 2023 | 0.014439 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-17 21:21 | 2023-04-17 23:26 | 105 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZARON OPERACIONES PARA SECCIONALIZAR TRAMO Y SE REPARO PUENTE ABIERTO POR OPERACIONES DE TRANSFERENCIA SJ-230417-01 | S23041700001 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 125 | 2023-04-17 | 13125 | keep | 0 | Apr | 2023 | 0.0089394 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-17 21:42 | 2023-04-18 11:40 | 62 | 13:58 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE Y SE REEMPLAZO AISLADOR | R23041700180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 838 | 2023-04-17 | 51956 | keep | 0 | Apr | 2023 | 0.035387 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
CAGUAS | 2023-04-17 22:14 | 2023-04-18 19:10 | 10 | 20:56 | P | ARBOL SOBRE LINEA | 2 X 40 EN C/L SE RETIRO PALMA SOBRE LA LINEA | C23041700171 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1256 | 2023-04-17 | 12560 | keep | 0 | Apr | 2023 | 0.0085546 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-18 00:03 | 2023-04-18 12:43 | 20 | 12:40 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23041800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 760 | 2023-04-18 | 15200 | keep | 0 | Apr | 2023 | 0.010353 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-18 00:03 | 2023-04-18 00:04 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CANOVANAS | 2023-04-18 00:06 | 2023-04-18 09:46 | 67 | 9:40 | P | ANIMAL | 1 X 40 EN PROVICIONAL AEREO CRUCE POR AVE | R23041800001 | New_Event | Animals | Include | Include | Wildlife | 580 | 2023-04-18 | 38860 | keep | 0 | Apr | 2023 | 0.026467 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-04-18 00:48 | 2023-04-18 11:13 | 10 | 10:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO PORTA FUSIBLE | S23041800004 | New_Event | Cutout Failure | Include | Include | Equipment | 625 | 2023-04-18 | 6250 | keep | 0 | Apr | 2023 | 0.0042568 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-18 00:49 | 2023-04-18 00:51 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C23041800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-18 | 4252 | keep | 0 | Apr | 2023 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2023-04-18 00:51 | 2023-04-18 10:01 | 38 | 9:10 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23041800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 550 | 2023-04-18 | 20900 | keep | 0 | Apr | 2023 | 0.014235 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
HUMACAO | 2023-04-18 01:20 | 2023-04-18 01:23 | 2126 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C23041800003 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-18 | 6378 | keep | 0 | Apr | 2023 | 0.004344 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2023-04-18 01:47 | 2023-04-18 01:48 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | B23041800006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
HUMACAO | 2023-04-18 03:31 | 2023-04-18 07:25 | 29 | 3:54 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23041800007 | New_Event | Animals | Include | Include | Wildlife | 234 | 2023-04-18 | 6786 | keep | 0 | Apr | 2023 | 0.0046219 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
MAYAGÃœEZ | 2023-04-18 03:50 | 2023-04-18 03:51 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23041800001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 4304 | keep | 0 | Apr | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
ARECIBO | 2023-04-18 03:50 | 2023-04-18 08:55 | 150 | 5:05 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23041800007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-04-18 | 45750 | keep | 0 | Apr | 2023 | 0.03116 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-04-18 03:51 | 2023-04-18 14:16 | 100 | 10:25 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23041800005 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 625 | 2023-04-18 | 62500 | keep | 0 | Apr | 2023 | 0.042568 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-18 05:07 | 2023-04-18 08:49 | 12 | 3:42 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | R23041800004 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-04-18 | 2664 | keep | 0 | Apr | 2023 | 0.0018144 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-18 07:15 | 2023-04-18 13:12 | 10 | 5:57 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23041800012 | New_Event | Animals | Include | Include | Wildlife | 357 | 2023-04-18 | 3570 | keep | 0 | Apr | 2023 | 0.0024315 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-18 07:22 | 2023-04-18 11:16 | 17 | 3:54 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23041800025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-04-18 | 3978 | keep | 0 | Apr | 2023 | 0.0027094 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-04-18 07:30 | 2023-04-18 14:11 | 30 | 6:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL PARA REPARAR PUENTE ABIERTO TRASPATIO | B23041800029 | New_Event | Primary Wire Break | Include | Include | Equipment | 401 | 2023-04-18 | 12030 | keep | 0 | Apr | 2023 | 0.0081936 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-18 07:48 | 2023-04-18 07:49 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 1907-03 LLEVA 1909-09 | S2304180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-18 07:48 | 2023-04-18 07:49 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1907-03 LLEVA 1909-09 | S2304180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-18 | 4456 | keep | 0 | Apr | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
CAGUAS | 2023-04-18 07:55 | 2023-04-18 13:09 | 7 | 5:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REEMPLAZO CAJA PRIMARIA Y CRUCE X AVE | C23041800014 | New_Event | Cutout Failure | Include | Include | Equipment | 314 | 2023-04-18 | 2198 | keep | 0 | Apr | 2023 | 0.001497 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-04-18 07:58 | 2023-04-18 12:56 | 5 | 4:58 | P | PROBLEMA DEL CLIENTE | 1 SMU-20 X 20 EN GABINETE Y 1 X 50 EN RISER GABINETE EN CONTAMINACION DEL CLIENTE | C23041800017 | New_Event | Customer-Related Interruption | Include | Include | Public | 298 | 2023-04-18 | 1490 | keep | 0 | Apr | 2023 | 0.0010148 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-18 08:04 | 2023-04-18 10:36 | 150 | 2:32 | P | NO SE REPORTO CAUSA | 1 X 40 1 X 80 EN C/L | B23041800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2023-04-18 | 22800 | keep | 0 | Apr | 2023 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-04-18 08:20 | 2023-04-18 10:19 | 8 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN XMR SE REEMPLAZO HOT CLAMP | C23041800008 | New_Event | Primary Wire Break | Include | Include | Equipment | 119 | 2023-04-18 | 952 | keep | 0 | Apr | 2023 | 0.0006484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-18 08:21 | 2023-04-18 16:10 | 260 | 7:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE CORTE DE LINEA PARA FIJAR LINEA Y REMPLAZAR AISLADOR TIENE 2 FUSIBLES FUNDIDO | S23041800014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 469 | 2023-04-18 | 121940 | keep | 0 | Apr | 2023 | 0.083053 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
SAN JUAN | 2023-04-18 08:26 | 2023-04-18 11:16 | 10 | 2:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIAS | S23041800019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 170 | 2023-04-18 | 1700 | keep | 0 | Apr | 2023 | 0.0011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-18 08:27 | 2023-04-18 10:02 | 2 | 1:35 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | P23041800020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-04-18 | 190 | keep | 0 | Apr | 2023 | 0.00012941 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-04-18 08:27 | 2023-04-18 11:39 | 1 | 3:12 | P | DESGANCHE | DESGANCHE 1 X 40 EN MONTURA | P23041800021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2023-04-18 | 192 | keep | 0 | Apr | 2023 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-18 08:29 | 2023-04-18 12:47 | 1 | 4:18 | P | PROBLEMA DEL CLIENTE | 1 X 20 EN RISER SE ELIMINO PARARRAYO DE CLIENTE | S23041800022 | New_Event | Customer-Related Interruption | Include | Include | Public | 258 | 2023-04-18 | 258 | keep | 0 | Apr | 2023 | 0.00017572 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-18 08:40 | 2023-04-18 15:10 | 6 | 6:30 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23041800022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 390 | 2023-04-18 | 2340 | keep | 0 | Apr | 2023 | 0.0015938 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-04-18 08:53 | 2023-04-18 10:26 | 10 | 1:33 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR A CASUA IMPACTO POR DIGGERS | R23041800023 | New_Event | Damage From Public | Include | Include | Public | 93 | 2023-04-18 | 930 | keep | 0 | Apr | 2023 | 0.00063342 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-18 08:55 | 2023-04-18 11:53 | 18 | 2:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | R23041800025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 178 | 2023-04-18 | 3204 | keep | 0 | Apr | 2023 | 0.0021822 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
YAUCO | 2023-04-18 09:07 | 2023-04-18 11:11 | 1 | 2:04 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA IGUANA | M23041800023 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-04-18 | 124 | keep | 0 | Apr | 2023 | 8.4456e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-18 09:13 | 2023-04-18 14:18 | 60 | 5:05 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23041800086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-04-18 | 18300 | keep | 0 | Apr | 2023 | 0.012464 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-18 09:14 | 2023-04-18 12:49 | 50 | 3:35 | P | ANIMAL | 1 X 15 RISER 1 X 50 SU-5 1 X 25 SU-7 CRUCE POR IGUANA | B23041800067 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-04-18 | 10750 | keep | 0 | Apr | 2023 | 0.0073218 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-04-18 09:14 | 2023-04-18 12:52 | 8 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR MAL TIEMPO | P23041800029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2023-04-18 | 1744 | keep | 0 | Apr | 2023 | 0.0011878 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-04-18 09:17 | 2023-04-18 09:22 | 796 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO QUEDO EN SERVICIO 16% POR 1620-04 | S23041800092 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-18 | 3980 | keep | 0 | Apr | 2023 | 0.0027108 | 0.00054215 | Momentary | FALSE | FALSE | Not_TMED_Event | 796
CANOVANAS | 2023-04-18 09:17 | 2023-04-18 09:22 | 172 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 16% DEL 1336-06 | S23041800092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-18 | 860 | keep | 0 | Apr | 2023 | 0.00058574 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
YAUCO | 2023-04-18 09:18 | 2023-04-18 10:11 | 10 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA Y DESGANCHE | M23041800020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-04-18 | 530 | keep | 0 | Apr | 2023 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-04-18 09:30 | 2023-04-18 12:15 | 4 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE DE TRANSFORMADOR | A23041800047 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2023-04-18 | 660 | keep | 0 | Apr | 2023 | 0.00044952 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-18 09:32 | 2023-04-18 14:19 | 120 | 4:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN CORTE DE LINEA SE REPARO CAJA | S23041800100 | New_Event | Cutout Failure | Include | Include | Equipment | 287 | 2023-04-18 | 34440 | keep | 0 | Apr | 2023 | 0.023457 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-04-18 09:35 | 2023-04-18 14:33 | 18 | 4:58 | P | ANIMAL | SE REEMPLAZARON 2 CAJAS PRIMARIAS 2 X 25 EN C/L Y SE RETIRO IGUANA | B23041800073 | New_Event | Animals | Include | Include | Wildlife | 298 | 2023-04-18 | 5364 | keep | 0 | Apr | 2023 | 0.0036534 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2023-04-18 10:01 | 2023-04-18 13:26 | 2 | 3:25 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | P23041800040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-04-18 | 410 | keep | 0 | Apr | 2023 | 0.00027925 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-04-18 10:07 | 2023-04-18 10:08 | 2580 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R23041800035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-18 | 2580 | keep | 0 | Apr | 2023 | 0.0017572 | 0.0017572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2580
CANOVANAS | 2023-04-18 10:07 | 2023-04-18 10:08 | 500 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11100 | R23041800035 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-18 | 500 | keep | 0 | Apr | 2023 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-04-18 10:09 | 2023-04-18 13:31 | 7 | 3:22 | P | CAUSAS EXTERNAS | 1 X 30 EN C/L CAMION IMPACTA POSTE | R23041800033 | New_Event | Damage From Public | Include | Include | Public | 202 | 2023-04-18 | 1414 | keep | 0 | Apr | 2023 | 0.00096307 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-18 10:12 | 2023-04-18 20:31 | 1 | 10:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA EN RISER | S23041800112 | New_Event | Primary Wire Break | Include | Include | Equipment | 619 | 2023-04-18 | 619 | keep | 0 | Apr | 2023 | 0.0004216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-18 10:20 | 2023-04-18 12:29 | 10 | 2:09 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR | A23041800055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2023-04-18 | 1290 | keep | 0 | Apr | 2023 | 0.00087861 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-18 10:29 | 2023-04-18 13:08 | 25 | 2:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X25 EN TRANSFORMADOR SE REPARO PUENTE DE CAJA A TRANSFORMADOR | S23041800119 | New_Event | Primary Wire Break | Include | Include | Equipment | 159 | 2023-04-18 | 3975 | keep | 0 | Apr | 2023 | 0.0027074 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-04-18 10:31 | 2023-04-18 12:30 | 1 | 1:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23041800046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-04-18 | 119 | keep | 0 | Apr | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-18 10:33 | 2023-04-18 11:52 | 1243 | 1:19 | T | DESGANCHE | SE RETIRO RAMA DE LA LINEA CON VARETA Y SE CERRO BKR | B23041800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-04-18 | 98197 | keep | 0 | Apr | 2023 | 0.066882 | 0.0008466 | Sustained | FALSE | FALSE | Not_TMED_Event | 1243
SAN JUAN | 2023-04-18 10:36 | 2023-04-18 21:25 | 25 | 10:49 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER AVERIA NUEVA SU-2 A T-9 AVERIA VIEJA DE T-7 A T-8 SE CERRO N/O DE RISER A SU-2 QUEDARON 2 TRANSFORMADORES FUERA | S23041800124 | New_Event | UG Cable Fault | Include | Include | Equipment | 649 | 2023-04-18 | 16225 | keep | 0 | Apr | 2023 | 0.011051 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-18 10:47 | 2023-04-18 11:49 | 7 | 1:02 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REPARO SECUNDARIA DESGANCHE | B23041800126 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 62 | 2023-04-18 | 434 | keep | 0 | Apr | 2023 | 0.0002956 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-04-18 11:08 | 2023-04-18 13:31 | 32 | 2:23 | P | CONDUCTOR ROTO O ABIERTO | 3 X 40 EN C/L SE DEZCRUZO CONDUCTOR PRIMARIO | C23041800044 | New_Event | Primary Wire Break | Include | Include | Equipment | 143 | 2023-04-18 | 4576 | keep | 0 | Apr | 2023 | 0.0031167 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2023-04-18 11:09 | 2023-04-18 15:46 | 1 | 4:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 20 EN TRANSFORMADOR NO CAUSA | S23041800136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2023-04-18 | 277 | keep | 0 | Apr | 2023 | 0.00018866 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-18 11:10 | 2023-04-18 13:46 | 1 | 2:36 | P | PROBLEMA DEL CLIENTE | 1 X 50 EN C/L PROBLEMA EN MONTURA DE CLIENTE (PROA) | B23041800094 | New_Event | Customer-Related Interruption | Include | Include | Public | 156 | 2023-04-18 | 156 | keep | 0 | Apr | 2023 | 0.00010625 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-18 11:13 | 2023-04-18 12:05 | 12 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRAS SECUNDARIAS EN PEDESTAL | B23041800095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-04-18 | 624 | keep | 0 | Apr | 2023 | 0.000425 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-18 11:15 | 2023-04-18 16:39 | 7 | 5:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO CAJA PRIMARIA | B23041700054 | New_Event | Cutout Failure | Include | Include | Equipment | 324 | 2023-04-18 | 2268 | keep | 0 | Apr | 2023 | 0.0015447 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-04-18 11:16 | 2023-04-18 15:15 | 60 | 3:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M23041800051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-04-18 | 14340 | keep | 0 | Apr | 2023 | 0.0097669 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-18 11:21 | 2023-04-18 13:50 | 1 | 2:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO CAJA | S23041800138 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2023-04-18 | 149 | keep | 0 | Apr | 2023 | 0.00010148 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-18 11:32 | 2023-04-18 11:35 | 1891 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C23041800053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-18 | 5673 | keep | 0 | Apr | 2023 | 0.0038639 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2023-04-18 11:32 | 2023-04-18 11:35 | 1250 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C23041800053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-18 | 3750 | keep | 0 | Apr | 2023 | 0.0025541 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2023-04-18 11:32 | 2023-04-18 11:35 | 2141 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C23041800053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-18 | 6423 | keep | 0 | Apr | 2023 | 0.0043747 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2023-04-18 11:32 | 2023-04-18 11:35 | 1827 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3700 | C23041800053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-04-18 | 5481 | keep | 0 | Apr | 2023 | 0.0037331 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
VEGA BAJA | 2023-04-18 11:38 | 2023-04-18 13:55 | 1 | 2:17 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23041800064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2023-04-18 | 137 | keep | 0 | Apr | 2023 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-18 11:41 | 2023-04-18 14:38 | 12 | 2:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | BUSHING SECUNDARIO EN XMR Y SE REPARO SECUNDARIA | P23041700062 | New_Event | Secondary Wire Break | Include | Include | Equipment | 177 | 2023-04-18 | 2124 | keep | 0 | Apr | 2023 | 0.0014466 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-04-18 11:50 | 2023-04-18 15:38 | 17 | 3:48 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA ENDEREZAR PM YA QUE TERRENO SEDIO | R23041800050 | New_Event | Damage From Public | Include | Include | Public | 228 | 2023-04-18 | 3876 | keep | 0 | Apr | 2023 | 0.0026399 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2023-04-18 11:53 | 2023-04-18 11:54 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2304180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 3699 | keep | 0 | Apr | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
CANOVANAS | 2023-04-18 11:54 | 2023-04-18 13:12 | 18 | 1:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | R23041800025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 78 | 2023-04-18 | 1404 | keep | 0 | Apr | 2023 | 0.00095626 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2023-04-18 12:13 | 2023-04-18 13:54 | 17 | 1:41 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | R23041800058 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-04-18 | 1717 | keep | 0 | Apr | 2023 | 0.0011694 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-04-18 12:24 | 2023-04-18 14:49 | 12 | 2:25 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR AVERIADO DE 25KVA X 25KVA | A23041800070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 145 | 2023-04-18 | 1740 | keep | 0 | Apr | 2023 | 0.0011851 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-04-18 12:27 | 2023-04-18 13:40 | 52 | 1:13 | T | ALIMENTADOR AMARRADO | SE VERIFICO INTERRUPTOR 7004-06 ABIERTO EN LA SUBESTACION YA QUE LA MISMA NO TIENE RTU SE PATRULLO NO SE ENCONTRO CAUSA PARA EL DISPARO SE CERRO Y QUEDO EN SERVICIO ESTE LLEVA LA CARGA DEL 7004-02 | M23041800071 | New_Event | Feeder Load Transferred | Include | Include | Other | 73 | 2023-04-18 | 3796 | keep | 0 | Apr | 2023 | 0.0025854 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
AGUADILLA | 2023-04-18 12:27 | 2023-04-18 13:40 | 32 | 1:13 | T | ALIMENTADOR AMARRADO | SE VERIFICO INTERRUPTOR 7004-06 ABIERTO EN LA SUBESTACION YA QUE LA MISMA NO TIENE RTU SE PATRULLO NO SE ENCONTRO CAUSA PARA EL DISPARO SE CERRO Y QUEDO EN SERVICIO ESTE LLEVA LA CARGA DEL 7004-03 | M23041800071 | New_Event | Feeder Load Transferred | Include | Include | Other | 73 | 2023-04-18 | 2336 | keep | 0 | Apr | 2023 | 0.001591 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
AGUADILLA | 2023-04-18 12:27 | 2023-04-18 13:40 | 146 | 1:13 | T | ALIMENTADOR AMARRADO | SE VERIFICO INTERRUPTOR 7004-06 ABIERTO EN LA SUBESTACION YA QUE LA MISMA NO TIENE RTU SE PATRULLO NO SE ENCONTRO CAUSA PARA EL DISPARO SE CERRO Y QUEDO EN SERVICIO ESTE LLEVA LA CARGA DEL 7004-05 | M23041800071 | New_Event | Feeder Load Transferred | Include | Include | Other | 73 | 2023-04-18 | 10658 | keep | 0 | Apr | 2023 | 0.0072591 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
AGUADILLA | 2023-04-18 12:27 | 2023-04-18 13:40 | 69 | 1:13 | T | NO SE REPORTO CAUSA | SE VERIFICO INTERRUPTOR ABIERTO EN LA SUBESTACION YA QUE LA MISMA NO TIENE RTU SE PATRULLO NO SE ENCONTRO CAUSA PARA EL DISPARO SE CERRO Y QUEDO EN SERVICIO | M23041800071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-04-18 | 5037 | keep | 0 | Apr | 2023 | 0.0034307 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BARRANQUITAS | 2023-04-18 12:57 | 2023-04-18 14:44 | 2280 | 1:47 | T | DESGANCHE | DISPARO DE BKR SE SECCIONALIZO AVERIA Y SE CERRO POR CONTROL 15% EN SERVICIO CG-230418-02 | C23041800069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-04-18 | 243960 | keep | 0 | Apr | 2023 | 0.16616 | 0.0015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 2280
SAN JUAN | 2023-04-18 13:04 | 2023-04-18 21:28 | 3 | 8:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE ENDEREZO CAJA PRIMARIA | S23041800172 | New_Event | Cutout Failure | Include | Include | Equipment | 504 | 2023-04-18 | 1512 | keep | 0 | Apr | 2023 | 0.0010298 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-18 13:20 | 2023-04-18 14:37 | 12 | 1:17 | P | NO SE REPORTO CAUSA | 1 X 12 EN XMR | R23041800062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2023-04-18 | 924 | keep | 0 | Apr | 2023 | 0.00062933 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-04-18 13:26 | 2023-04-18 15:49 | 40 | 2:23 | P | DESGANCHE | 1 X 50 EN C/L Y 1 X 10 EN XMR DESGANCHE | R23041800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-04-18 | 5720 | keep | 0 | Apr | 2023 | 0.0038959 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-04-18 13:33 | 2023-04-18 16:51 | 1 | 3:18 | P | ANIMAL | 2 X 10 EN XMR AVE CRUZO LINEAS | P23041800083 | New_Event | Animals | Include | Include | Wildlife | 198 | 2023-04-18 | 198 | keep | 0 | Apr | 2023 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-18 13:35 | 2023-04-18 16:05 | 31 | 2:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA LEVANTAR LINEA SECUNDARIA REF.S23041800162 | S23041800179 | New_Event | Secondary Wire Break | Include | Include | Equipment | 150 | 2023-04-18 | 4650 | keep | 0 | Apr | 2023 | 0.0031671 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-04-18 13:36 | 2023-04-18 16:35 | 1408 | 2:59 | T | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO AMARRE CONTRA 1714-03. EN SERVICIO 70% 1714-02 | B23041800113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-04-18 | 252032 | keep | 0 | Apr | 2023 | 0.17166 | 0.00095898 | Sustained | FALSE | FALSE | Not_TMED_Event | 1408
BAYAMON | 2023-04-18 13:36 | 2023-04-18 14:28 | 455 | 0:52 | T | ALIMENTADOR AMARRADO | SE ABRIO AMARRE CONTRA 1714-02 Y SE CERRO POR SCADA | B23041800113 | New_Event | Feeder Load Transferred | Include | Include | Other | 52 | 2023-04-18 | 23660 | keep | 0 | Apr | 2023 | 0.016115 | 0.0003099 | Sustained | FALSE | FALSE | Not_TMED_Event | 455
CANOVANAS | 2023-04-18 13:37 | 2023-04-18 17:27 | 80 | 3:50 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REMPLAZO AISLADOR | R23041800068 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 230 | 2023-04-18 | 18400 | keep | 0 | Apr | 2023 | 0.012532 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-04-18 13:43 | 2023-04-18 15:35 | 1 | 1:52 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE ENCONTRO CAUSA | M23041800089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2023-04-18 | 112 | keep | 0 | Apr | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-18 13:53 | 2023-04-18 15:51 | 3157 | 1:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23041800215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2023-04-18 | 372526 | keep | 0 | Apr | 2023 | 0.25373 | 0.0021502 | Sustained | FALSE | FALSE | Not_TMED_Event | 3157
VEGA BAJA | 2023-04-18 13:53 | 2023-04-18 15:51 | 35 | 1:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23041800215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2023-04-18 | 4130 | keep | 0 | Apr | 2023 | 0.0028129 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-04-18 13:53 | 2023-04-18 15:51 | 2916 | 1:58 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23041800215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2023-04-18 | 344088 | keep | 0 | Apr | 2023 | 0.23436 | 0.0019861 | Sustained | FALSE | FALSE | Not_TMED_Event | 2916
SAN JUAN | 2023-04-18 14:00 | 2023-04-18 15:10 | 12 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA EN VARIOS PUNTOS | S23041800154 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-04-18 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-04-18 14:01 | 2023-04-20 13:27 | 1 | 47:26 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23041800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2846 | 2023-04-18 | 2846 | keep | 0 | Apr | 2023 | 0.0019384 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-18 14:06 | 2023-04-18 17:12 | 100 | 3:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REMPLAZO AISLADOR | R23041800074 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 186 | 2023-04-18 | 18600 | keep | 0 | Apr | 2023 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-18 14:11 | 2023-04-18 15:40 | 120 | 1:29 | P | NO SE REPORTO CAUSA | 1 X 80 SMU 20 EN SU 8 | B23041800152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2023-04-18 | 10680 | keep | 0 | Apr | 2023 | 0.0072741 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-04-18 14:11 | 2023-04-18 15:36 | 90 | 1:25 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE | B23041800144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-04-18 | 7650 | keep | 0 | Apr | 2023 | 0.0052104 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-04-18 14:28 | 2023-04-18 18:40 | 1 | 4:12 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE TRANSFORMADOR PARA CERRAR PUENTE DE LINEA A CAJA TRANSFORMADOR | S23041800184 | New_Event | Primary Wire Break | Include | Include | Equipment | 252 | 2023-04-18 | 252 | keep | 0 | Apr | 2023 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-18 14:30 | 2023-04-18 15:15 | 10 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S23041800076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-18 | 450 | keep | 0 | Apr | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-18 14:33 | 2023-04-18 14:36 | 1362 | 0:03 | T | ANIMAL | IGUANA QUE CRUZO CAJA PRIMARIA AL RETIRARLA CRUZO LINEAS | B23041800161 | New_Event | Animals | Include | Include | Wildlife | 3 | 2023-04-18 | 4086 | keep | 0 | Apr | 2023 | 0.002783 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2023-04-18 14:36 | 2023-04-18 16:28 | 18 | 1:52 | P | ANIMAL | SE REEMPLAZARON 2 CAJAS PRIMARIAS 2 X 25 EN C/L Y SE RETIRO IGUANA | B23041800073 | 1st_after_momentary | Animals | Include | Include | Wildlife | 112 | 2023-04-18 | 2016 | keep | 0 | Apr | 2023 | 0.0013731 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-04-18 14:41 | 2023-04-18 16:41 | 1 | 2:00 | P | ANIMAL | 1 X 30 EN RISER AVE CRUZO FASE A TIERRA | M23041800098 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-04-18 | 120 | keep | 0 | Apr | 2023 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-18 14:44 | 2023-04-18 15:30 | 1938 | 0:46 | P | DESGANCHE | SE REALIZO DESGANCHE DE BAMBUAS Y SE REEMPLAZO PIN DE AISLADOR AVERRIADO SE CERRO MACHETES. 50% EN SERVICIO | C23041800069 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 46 | 2023-04-18 | 89148 | keep | 0 | Apr | 2023 | 0.060718 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-18 14:46 | 2023-04-18 14:47 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2023-04-18 15:00 | 2023-04-19 10:54 | 2 | 19:54 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO CAUSA | S23041800191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1194 | 2023-04-18 | 2388 | keep | 0 | Apr | 2023 | 0.0016265 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-04-18 15:03 | 2023-04-18 17:48 | 125 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR LLUVIAS | A23041800181 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-04-18 | 20625 | keep | 0 | Apr | 2023 | 0.014048 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-04-18 15:05 | 2023-04-18 16:21 | 25 | 1:16 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23041800085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-04-18 | 1900 | keep | 0 | Apr | 2023 | 0.0012941 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-04-18 15:10 | 2023-04-18 16:50 | 3 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | M23041800100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2023-04-18 | 300 | keep | 0 | Apr | 2023 | 0.00020433 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-18 15:14 | 2023-04-18 16:46 | 11 | 1:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REEMPLAZO CAJA PRIMARIA | B23041800187 | New_Event | Cutout Failure | Include | Include | Equipment | 92 | 2023-04-18 | 1012 | keep | 0 | Apr | 2023 | 0.00068927 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-04-18 15:30 | 2023-04-18 15:47 | 1140 | 0:17 | P | DESGANCHE | SE CERRO MACHETES FALTANTES 100% EN SERVICIO | C23041800069 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 17 | 2023-04-18 | 19380 | keep | 0 | Apr | 2023 | 0.0132 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-18 15:36 | 2023-04-18 17:38 | 25 | 2:02 | P | CAUSAS EXTERNAS | 1 X 25 EN C/L GLOBO CRUZO LINEAS | P23041800103 | New_Event | Damage From Public | Include | Include | Public | 122 | 2023-04-18 | 3050 | keep | 0 | Apr | 2023 | 0.0020773 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-18 15:40 | 2023-04-18 15:41 | 3597 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9405-05 LLEVANDO CARGA 1719-15 | B2304180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-18 | 3597 | keep | 0 | Apr | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-04-18 15:40 | 2023-04-18 15:41 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9405-05 LLEVANDO CARGA 1719-15 | B2304180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 3511 | keep | 0 | Apr | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-04-18 15:41 | 2023-04-18 15:47 | 120 | 0:06 | P | NO SE REPORTO CAUSA | 1 X 80 SMU 20 EN SU 8 | B23041800152 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-18 | 720 | keep | 0 | Apr | 2023 | 0.00049039 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-18 15:45 | 2023-04-18 16:25 | 17 | 0:40 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZA TRANSFORMADOR AVERIADO DE 50 KVA X 50KVA | A23041800204 | New_Event | Service Transformer Failure | Include | Include | Equipment | 40 | 2023-04-18 | 680 | keep | 0 | Apr | 2023 | 0.00046314 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-04-18 15:48 | 2023-04-18 15:53 | 455 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR AL CERRAR N/O CONTRA 1714-02 | B23041800113 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-18 | 2275 | keep | 0 | Apr | 2023 | 0.0015495 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-18 15:53 | 2023-04-18 18:30 | 72 | 2:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | A23041800210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-04-18 | 11304 | keep | 0 | Apr | 2023 | 0.0076991 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-04-18 15:55 | 2023-04-18 17:56 | 641 | 2:01 | P | NO SE REPORTO CAUSA | SE ENCONTRO PB CON HLT ACTIVADO SE PATRULLO Y SE CERRO PB QUEDO EN SERVICIO | S23041800216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2023-04-18 | 77561 | keep | 0 | Apr | 2023 | 0.052826 | 0.00043658 | Sustained | FALSE | FALSE | Not_TMED_Event | 641
SAN JUAN | 2023-04-18 16:10 | 2023-04-18 17:40 | 389 | 1:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN CORTE DE LINEA SE REMPLAZO AISLADOR Y SE FIJO LINEA A AISLADOR | S23041800014 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 90 | 2023-04-18 | 35010 | keep | 0 | Apr | 2023 | 0.023845 | 0.00026495 | Sustained | FALSE | FALSE | Not_TMED_Event | 389
BAYAMON | 2023-04-18 16:10 | 2023-04-18 16:11 | 723 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR 1912-08 LLEVANDO CARGA 1711-02 Y 1711-05 | B2304180000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-18 | 723 | keep | 0 | Apr | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-04-18 16:10 | 2023-04-18 16:11 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1912-08 LLEVANDO CARGA 1711-02 Y 1711-05 | B2304180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-18 | 1976 | keep | 0 | Apr | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-04-18 16:10 | 2023-04-18 16:11 | 577 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1912-08 LLEVANDO CARGA 1711-02 Y 1711-05 | B2304180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-18 | 577 | keep | 0 | Apr | 2023 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-04-18 16:11 | 2023-04-18 17:24 | 109 | 1:13 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE CARGA DE 1711-02 POR 1912-08 | B23041800227 | 1st_after_momentary | Animals | Include | Include | Wildlife | 73 | 2023-04-18 | 7957 | keep | 0 | Apr | 2023 | 0.0054195 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
CANOVANAS | 2023-04-18 16:14 | 2023-04-18 20:06 | 20 | 3:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | R23041800100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 232 | 2023-04-18 | 4640 | keep | 0 | Apr | 2023 | 0.0031603 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-18 16:20 | 2023-04-18 16:55 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23041800105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-04-18 | 350 | keep | 0 | Apr | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-18 16:35 | 2023-04-18 17:08 | 422 | 0:33 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR Y SE CERRO MACHETES PARA DESPEJAR LINEAS DE RAMA CRUZANDOLAS. 80% EN SERVICIO | B23041800113 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-04-18 | 13926 | keep | 0 | Apr | 2023 | 0.0094849 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-18 16:52 | 2023-04-18 18:52 | 6 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN XMR NO FUNDIO | B23041800240 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2023-04-18 | 720 | keep | 0 | Apr | 2023 | 0.00049039 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-18 17:08 | 2023-04-18 17:58 | 282 | 0:50 | P | DESGANCHE | SE RETIRO RAMA CRUZANDO LINEAS Y SE CERRO MACHETES | B23041800113 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-04-18 | 14100 | keep | 0 | Apr | 2023 | 0.0096034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-18 17:30 | 2023-04-18 17:31 | 2368 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 2368 | keep | 0 | Apr | 2023 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
BAYAMON | 2023-04-18 17:31 | 2023-04-18 17:41 | 33 | 0:10 | P | ANIMAL | 1 X 30 EN C/L AVE CRUZO LINEAS | B23041800255 | New_Event | Animals | Include | Include | Wildlife | 10 | 2023-04-18 | 330 | keep | 0 | Apr | 2023 | 0.00022476 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-04-18 17:40 | 2023-04-19 09:18 | 10 | 15:38 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | B23041800260 | New_Event | Animals | Include | Include | Wildlife | 938 | 2023-04-18 | 9380 | keep | 0 | Apr | 2023 | 0.0063887 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-18 17:43 | 2023-04-18 19:08 | 40 | 1:25 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23041800115 | New_Event | Animals | Include | Include | Wildlife | 85 | 2023-04-18 | 3400 | keep | 0 | Apr | 2023 | 0.0023157 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-18 17:51 | 2023-04-18 19:51 | 120 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIA | A23041800234 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2023-04-18 | 14400 | keep | 0 | Apr | 2023 | 0.0098078 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-04-18 18:14 | 2023-04-18 21:50 | 1827 | 3:36 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6000 ESTE INTERRUPTOR ABRIO EN LA AVERIA POR OVERHEAD CAIDO DE LA LINEA 6000 SOBRE ESTE ALIMENTADOR PERO NO SE SABIA NADA PORQUE LA SUBESTACION TIENE EL RTU FUERA DE SERVICIO SE CORRIGIO CONDICION Y SE CERRO EL INTERRUPTOR | M23041800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 216 | 2023-04-18 | 394632 | keep | 0 | Apr | 2023 | 0.26878 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-04-18 18:14 | 2023-04-18 21:23 | 1047 | 3:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6000 OHGW SOBRE LA LINEA. | M23041800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2023-04-18 | 197883 | keep | 0 | Apr | 2023 | 0.13478 | 0.00071311 | Sustained | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2023-04-18 18:14 | 2023-04-18 21:23 | 4882 | 3:09 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6000 OHGW SOBRE LA LINEA. | M23041800139 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 189 | 2023-04-18 | 922698 | keep | 0 | Apr | 2023 | 0.62845 | 0.0033251 | Sustained | FALSE | FALSE | Not_TMED_Event | 4882
BAYAMON | 2023-04-18 18:25 | 2023-04-18 19:36 | 11 | 1:11 | P | CAUSAS EXTERNAS | E ABRIO XMR Y SE REPARO/LEVANTO SECUNDARIA QUE CAMION SE ENREDO | B23041800247 | New_Event | Damage From Public | Include | Include | Public | 71 | 2023-04-18 | 781 | keep | 0 | Apr | 2023 | 0.00053194 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-04-18 18:55 | 2023-04-20 18:43 | 4 | 47:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO LINEA SECUNDARIA SOTERRADA AVERIADA Y SE ENERGIZO TRANSFORMADOR | M23041800171 | New_Event | Secondary Wire Break | Include | Include | Equipment | 2868 | 2023-04-18 | 11472 | keep | 0 | Apr | 2023 | 0.0078135 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-04-18 19:06 | 2023-04-18 20:57 | 1057 | 1:51 | T | LINEA DE TRANSMISION 38KV | SE ABRIO EL INTERRUPTOR POR SEGURIDAD A PETICION DE JOSE UGARTE PARA RETIRAR OVERHEAD ROTO DE LA LINEA 6000 CAIDO SOBRE EL TRONCAL DEL ALIMENTADOR 7003-05 | M23041800178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2023-04-18 | 117327 | keep | 0 | Apr | 2023 | 0.079911 | 0.00071992 | Sustained | FALSE | FALSE | Not_TMED_Event | 1057
MAYAGÃœEZ | 2023-04-18 19:18 | 2023-04-19 10:35 | 10 | 15:17 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE EN CONTRO CAUSA | M23041800184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 917 | 2023-04-18 | 9170 | keep | 0 | Apr | 2023 | 0.0062456 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-18 19:22 | 2023-04-18 21:49 | 45 | 2:27 | P | DESGANCHE | 1 X 65 EN C/L Y 1 X 50 EN C/L REQUIERE DESGANCHE | C23041800120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-04-18 | 6615 | keep | 0 | Apr | 2023 | 0.0045054 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-04-18 19:35 | 2023-04-18 22:35 | 150 | 3:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A23041800248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-04-18 | 27000 | keep | 0 | Apr | 2023 | 0.01839 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-18 20:18 | 2023-04-19 11:47 | 30 | 15:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN C/L Y SE REEMPLAZO PORTA FUSIBLE | B23041800301 | New_Event | Cutout Failure | Include | Include | Equipment | 929 | 2023-04-18 | 27870 | keep | 0 | Apr | 2023 | 0.018982 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-18 20:22 | 2023-04-18 20:25 | 922 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S23041800310 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-18 | 2766 | keep | 0 | Apr | 2023 | 0.0018839 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-04-18 20:22 | 2023-04-18 20:25 | 135 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1346-05 | S23041800310 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-18 | 405 | keep | 0 | Apr | 2023 | 0.00027584 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-04-18 20:29 | 2023-04-18 20:31 | 922 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1401-08 | S23041800315 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-18 | 1844 | keep | 0 | Apr | 2023 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-04-18 20:29 | 2023-04-18 20:31 | 135 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA CARGA 1346-05 | S23041800315 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-18 | 270 | keep | 0 | Apr | 2023 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
HUMACAO | 2023-04-18 20:37 | 2023-04-18 20:38 | 3833 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | C2304180000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-18 | 3833 | keep | 0 | Apr | 2023 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2023-04-18 20:38 | 2023-04-19 01:47 | 100 | 5:09 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTARON CONDUCTORES DEL SUELO | C23041800128 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 309 | 2023-04-18 | 30900 | keep | 0 | Apr | 2023 | 0.021046 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-18 21:09 | 2023-04-18 22:05 | 118 | 0:56 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 25 EN CORTES DE LINEA SE PATRULLO | R23041800115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 56 | 2023-04-18 | 6608 | keep | 0 | Apr | 2023 | 0.0045007 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
SAN JUAN | 2023-04-18 21:23 | 2023-04-19 10:30 | 30 | 13:07 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | S23041800325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 787 | 2023-04-18 | 23610 | keep | 0 | Apr | 2023 | 0.016081 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-18 21:35 | 2023-04-19 10:39 | 17 | 13:04 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA VIEJA T-7 A T-8 SE REPARO PISTOLA EN T-7 Y SE ENERGIZO TRAMO A TRAVEZ T-7 | S23041800124 | New_Event | UG Cable Fault | Include | Include | Equipment | 784 | 2023-04-18 | 13328 | keep | 0 | Apr | 2023 | 0.0090776 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-04-18 21:38 | 2023-04-18 21:39 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23041800306 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 4702 | keep | 0 | Apr | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-04-18 21:47 | 2023-04-19 08:12 | 8 | 10:25 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | A23041800264 | New_Event | Animals | Include | Include | Wildlife | 625 | 2023-04-18 | 5000 | keep | 0 | Apr | 2023 | 0.0034055 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-18 21:50 | 2023-04-19 08:18 | 45 | 10:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | C23041800207 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 628 | 2023-04-18 | 28260 | keep | 0 | Apr | 2023 | 0.019248 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-04-18 22:47 | 2023-04-18 22:48 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23041800240 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-18 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
GUAYAMA | 2023-04-18 23:00 | 2023-04-19 14:00 | 6 | 15:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50 KVA A 7.62 KV AVERIADO | P23041800167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 900 | 2023-04-18 | 5400 | keep | 0 | Apr | 2023 | 0.0036779 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-19 00:12 | 2023-04-19 08:17 | 9 | 8:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE | B23041900001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 485 | 2023-04-19 | 4365 | keep | 0 | Apr | 2023 | 0.002973 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-04-19 00:12 | 2023-04-19 08:15 | 7 | 8:03 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | B23041900002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2023-04-19 | 3381 | keep | 0 | Apr | 2023 | 0.0023028 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-04-19 02:30 | 2023-04-19 06:22 | 200 | 3:52 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 80 EN C/L CRUCE X AVE | C23041900007 | New_Event | Animals | Include | Include | Wildlife | 232 | 2023-04-19 | 46400 | keep | 0 | Apr | 2023 | 0.031603 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-04-19 02:42 | 2023-04-19 11:22 | 30 | 8:40 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23041900008 | New_Event | Animals | Include | Include | Wildlife | 520 | 2023-04-19 | 15600 | keep | 0 | Apr | 2023 | 0.010625 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-19 03:05 | 2023-04-19 03:06 | 2735 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2204190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 2735 | keep | 0 | Apr | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
VEGA BAJA | 2023-04-19 03:26 | 2023-04-19 05:26 | 776 | 2:00 | S | DISPARO DE BARRA DE TRANSMISION | SE REMPLAZO BOBINA QUEMADA DEL GCB 0030 POR PARTE DEL PERSONAL DE CDS AL DISPARAR LA LINEA 2200 RADIAL SE INICIA ERRONEAMENTE EL BREAKER FAILURE Y SE DISPARA LA BARRA DE 38KV | B23041900016 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2023-04-19 | 93120 | keep | 0 | Apr | 2023 | 0.063424 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
VEGA BAJA | 2023-04-19 03:26 | 2023-04-19 05:26 | 2216 | 2:00 | S | DISPARO DE BARRA DE TRANSMISION | SE REMPLAZO BOBINA QUEMADA DEL GCB 0030 POR PARTE DEL PERSONAL DE CDS AL DISPARAR LA LINEA 2200 RADIAL SE INICIA ERRONEAMENTE EL BREAKER FAILURE Y SE DISPARA LA BARRA DE 38KV | B23041900016 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 120 | 2023-04-19 | 265920 | keep | 0 | Apr | 2023 | 0.18112 | 0.0015093 | Sustained | FALSE | FALSE | Not_TMED_Event | 2216
VEGA BAJA | 2023-04-19 03:26 | 2023-04-19 03:27 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23041900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 4702 | keep | 0 | Apr | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CAGUAS | 2023-04-19 05:10 | 2023-04-19 12:16 | 70 | 7:06 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23041900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 426 | 2023-04-19 | 29820 | keep | 0 | Apr | 2023 | 0.02031 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-04-19 05:42 | 2023-04-19 05:43 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2304190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 1362 | keep | 0 | Apr | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
HUMACAO | 2023-04-19 06:22 | 2023-04-19 06:24 | 1089 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C2304190000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-19 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2023-04-19 06:22 | 2023-04-19 06:24 | 3896 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C2304190000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-19 | 7792 | keep | 0 | Apr | 2023 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2023-04-19 06:22 | 2023-04-19 06:24 | 1467 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C2304190000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-04-19 | 2934 | keep | 0 | Apr | 2023 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2023-04-19 06:24 | 2023-04-19 09:59 | 200 | 3:35 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 80 EN C/L CRUCE X AVE | C23041900007 | Partial_restoration | Animals | Include | Include | Wildlife | 215 | 2023-04-19 | 43000 | keep | 0 | Apr | 2023 | 0.029287 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-19 06:25 | 2023-04-19 11:00 | 80 | 4:35 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CL SE REMPLAZO AISLADOR | P23041900017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 275 | 2023-04-19 | 22000 | keep | 0 | Apr | 2023 | 0.014984 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-04-19 06:26 | 2023-04-19 09:03 | 2530 | 2:37 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M23041900004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2023-04-19 | 397210 | keep | 0 | Apr | 2023 | 0.27054 | 0.0017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2023-04-19 06:26 | 2023-04-19 09:03 | 199 | 2:37 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 6008-04 QUE SE ENCUENTRA LLEVANDO LA CARGA DEL 6008-05 | M23041900004 | New_Event | Feeder Load Transferred | Include | Include | Other | 157 | 2023-04-19 | 31243 | keep | 0 | Apr | 2023 | 0.021279 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-04-19 06:34 | 2023-04-19 08:53 | 15 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA POR LLUVIAS | A23041900002 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-04-19 | 2085 | keep | 0 | Apr | 2023 | 0.0014201 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-19 06:40 | 2023-04-19 10:37 | 1 | 3:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA EN RISER | B23041900057 | New_Event | Cutout Failure | Include | Include | Equipment | 237 | 2023-04-19 | 237 | keep | 0 | Apr | 2023 | 0.00016142 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-19 06:49 | 2023-04-19 08:41 | 3 | 1:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA | P23041900019 | New_Event | Cutout Failure | Include | Include | Equipment | 112 | 2023-04-19 | 336 | keep | 0 | Apr | 2023 | 0.00022885 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-04-19 06:49 | 2023-04-19 09:25 | 4 | 2:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS EN BAJANTES DE TRANSFORMADOR | M23041900010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 156 | 2023-04-19 | 624 | keep | 0 | Apr | 2023 | 0.000425 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-04-19 07:12 | 2023-04-19 13:18 | 50 | 6:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L SE REMPLAZO CAJA PRIMARIA Y PORTAFUSIBLE | R23041900004 | New_Event | Cutout Failure | Include | Include | Equipment | 366 | 2023-04-19 | 18300 | keep | 0 | Apr | 2023 | 0.012464 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-19 07:15 | 2023-04-19 10:50 | 3 | 3:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23041900064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 215 | 2023-04-19 | 645 | keep | 0 | Apr | 2023 | 0.00043931 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-04-19 07:38 | 2023-04-19 09:30 | 2354 | 1:52 | S | OTRAS CAUSAS | LOCKOUT TRIP A CAUSA DE AVERIA EN EL BUS SUPPORT DEL 115KV. SE TRANSFIRIO CARGA AL 2603-07. | C23041900071 | New_Event | Other Causes | Include | Include | Other | 112 | 2023-04-19 | 263648 | keep | 0 | Apr | 2023 | 0.17957 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
HUMACAO | 2023-04-19 07:38 | 2023-04-19 09:55 | 3025 | 2:17 | S | OTRAS CAUSAS | LOCKOUT TRIP A CAUSA DE AVERIA EN EL BUS SUPPORT DEL 115KV. SE TRANSFIRIO CARGA AL 2906-02. | C23041900071 | New_Event | Other Causes | Include | Include | Other | 137 | 2023-04-19 | 414425 | keep | 0 | Apr | 2023 | 0.28226 | 0.0020603 | Sustained | FALSE | FALSE | Not_TMED_Event | 3025
HUMACAO | 2023-04-19 07:38 | 2023-04-19 10:10 | 1593 | 2:32 | S | OTRAS CAUSAS | LOCKOUT TRIP A CAUSA DE AVERIA EN EL BUS SUPPORT DEL 115KV. SE TRANSFIRIO CARGA AL 2906-02. | C23041900071 | New_Event | Other Causes | Include | Include | Other | 152 | 2023-04-19 | 242136 | keep | 0 | Apr | 2023 | 0.16492 | 0.001085 | Sustained | FALSE | FALSE | Not_TMED_Event | 1593
BARRANQUITAS | 2023-04-19 07:43 | 2023-04-19 10:18 | 60 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23041900046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-04-19 | 9300 | keep | 0 | Apr | 2023 | 0.0063342 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-19 07:54 | 2023-04-19 09:24 | 7 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REPARO SECUNDARIA | B23041900068 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-04-19 | 630 | keep | 0 | Apr | 2023 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
GUAYAMA | 2023-04-19 07:56 | 2023-04-19 09:19 | 1 | 1:23 | P | ANIMAL | 2 X 10 EN MONTURA AVE | P23041900025 | New_Event | Animals | Include | Include | Wildlife | 83 | 2023-04-19 | 83 | keep | 0 | Apr | 2023 | 5.6531e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-19 07:59 | 2023-04-19 12:12 | 56 | 4:13 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | S23041900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2023-04-19 | 14168 | keep | 0 | Apr | 2023 | 0.0096498 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2023-04-19 08:02 | 2023-04-19 15:01 | 10 | 6:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA OMS ESTABA FUERA DE SERVICIO | S2304190000X | New_Event | Secondary Wire Break | Include | Include | Equipment | 419 | 2023-04-19 | 4190 | keep | 0 | Apr | 2023 | 0.0028538 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-19 08:03 | 2023-04-19 08:04 | 1835 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2304190000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-19 | 1835 | keep | 0 | Apr | 2023 | 0.0012498 | 0.0012498 | Momentary | FALSE | FALSE | Not_TMED_Event | 1835
HUMACAO | 2023-04-19 08:04 | 2023-04-19 11:28 | 30 | 3:24 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23041900120 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-04-19 | 6120 | keep | 0 | Apr | 2023 | 0.0041683 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-04-19 08:05 | 2023-04-19 13:32 | 60 | 5:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA DEFECTUOSA Y SE CERRO PUENTE | A23041900011 | New_Event | Cutout Failure | Include | Include | Equipment | 327 | 2023-04-19 | 19620 | keep | 0 | Apr | 2023 | 0.013363 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-04-19 08:19 | 2023-04-19 13:28 | 1 | 5:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CL FUERTES VIENTOS | P23041900026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 309 | 2023-04-19 | 309 | keep | 0 | Apr | 2023 | 0.00021046 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-19 08:23 | 2023-04-19 10:35 | 7 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | A23041900016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-04-19 | 924 | keep | 0 | Apr | 2023 | 0.00062933 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-04-19 08:26 | 2023-04-19 13:11 | 10 | 4:45 | P | CAUSAS EXTERNAS | 1 X 25 EN C/L SE LEVANTO CONDUCTOR PRIMARIO A CAUSA DE IMPACTO POR CAMION | C23041900042 | New_Event | Damage From Public | Include | Include | Public | 285 | 2023-04-19 | 2850 | keep | 0 | Apr | 2023 | 0.0019411 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-19 08:26 | 2023-04-19 11:04 | 50 | 2:38 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23041900092 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-04-19 | 7900 | keep | 0 | Apr | 2023 | 0.0053807 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-19 08:31 | 2023-04-19 13:30 | 2 | 4:59 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | A23041900019 | New_Event | Animals | Include | Include | Wildlife | 299 | 2023-04-19 | 598 | keep | 0 | Apr | 2023 | 0.0004073 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-04-19 09:06 | 2023-04-19 14:37 | 70 | 5:31 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE MASIVO | B23041900085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2023-04-19 | 23170 | keep | 0 | Apr | 2023 | 0.015781 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-04-19 09:07 | 2023-04-19 09:10 | 651 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B2304190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-19 | 1953 | keep | 0 | Apr | 2023 | 0.0013302 | 0.00044339 | Momentary | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2023-04-19 09:07 | 2023-04-19 09:08 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2304190000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 1362 | keep | 0 | Apr | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
YAUCO | 2023-04-19 09:09 | 2023-04-19 10:35 | 1 | 1:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJAS PRIMARIAS EN RISER | M23041800004 | New_Event | Cutout Failure | Include | Include | Equipment | 86 | 2023-04-19 | 86 | keep | 0 | Apr | 2023 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-19 09:11 | 2023-04-19 09:12 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2304190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-04-19 09:12 | 2023-04-19 12:00 | 20 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 140 EN RISER NO CAUSA | B23041900101 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-04-19 | 3360 | keep | 0 | Apr | 2023 | 0.0022885 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-19 09:34 | 2023-04-19 11:58 | 80 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR NO CAUSA | S23041900032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2023-04-19 | 11520 | keep | 0 | Apr | 2023 | 0.0078462 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-19 09:51 | 2023-04-19 13:31 | 8 | 3:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL Y SE RETEZO LINEAS PRIMARIA | B23041600103 | New_Event | Primary Wire Break | Include | Include | Equipment | 220 | 2023-04-19 | 1760 | keep | 0 | Apr | 2023 | 0.0011987 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-19 09:53 | 2023-04-19 13:01 | 40 | 3:08 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23041900095 | New_Event | Animals | Include | Include | Wildlife | 188 | 2023-04-19 | 7520 | keep | 0 | Apr | 2023 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-19 10:07 | 2023-04-19 12:30 | 14 | 2:23 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR PALOMA CRUZO FASE | S23041900037 | New_Event | Animals | Include | Include | Wildlife | 143 | 2023-04-19 | 2002 | keep | 0 | Apr | 2023 | 0.0013636 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-04-19 10:30 | 2023-04-19 15:51 | 7 | 5:21 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA TARABAJOS CON TOMA DEL CLIENTE. OMS FUERA DE SERVICIO | B2304190000X | New_Event | Customer-Related Interruption | Include | Include | Public | 321 | 2023-04-19 | 2247 | keep | 0 | Apr | 2023 | 0.0015304 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-04-19 10:39 | 2023-04-19 10:46 | 138 | 0:07 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE VERIFICO PERSONAL FUERA ESTABAN REALIZANDO PRUEBA DE CABLE PERSONAL SOTERRADO 10% POR 1206-04 | S23041900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-04-19 | 966 | keep | 0 | Apr | 2023 | 0.00065794 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-04-19 10:39 | 2023-04-19 10:46 | 719 | 0:07 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE VERIFICO PERSONAL FUERA ESTABAN REALIZANDO PRUEBA DE CABLE PERSONAL SOTERRADO 40% POR 1206-04 | S23041900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 7 | 2023-04-19 | 5033 | keep | 0 | Apr | 2023 | 0.003428 | 0.00048971 | Sustained | FALSE | FALSE | Not_TMED_Event | 719
SAN JUAN | 2023-04-19 10:39 | 2023-04-19 10:46 | 1799 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE VERIFICO PERSONAL FUERA ESTABAN REALIZANDO PRUEBA DE CABLE PERSONAL SOTERRADO LLEVA 10% DEL 1204-03 Y 40% DEL 1204-04 | S23041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-04-19 | 12593 | keep | 0 | Apr | 2023 | 0.008577 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
ARECIBO | 2023-04-19 10:41 | 2023-04-19 12:01 | 1 | 1:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR POR CAJA DEFECTUOSA | A23041900042 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2023-04-19 | 80 | keep | 0 | Apr | 2023 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-19 10:46 | 2023-04-19 15:45 | 17 | 4:59 | P | CABLE SOTERRADO AVERIADO | SE REPARO AVERIA VIEJA T-7 A T-8 SE REPARO PISTOLA EN T-7 Y SE ENERGIZO TRAMO A TRAVEZ T-7 | S23041800124 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 299 | 2023-04-19 | 5083 | keep | 0 | Apr | 2023 | 0.003462 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-19 10:54 | 2023-04-19 13:50 | 8 | 2:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE CAJAS EN TRANSFORMADOR PARA REMPLAZAR CONECTORES SECUNDARIOS | P23041900069 | New_Event | Secondary Wire Break | Include | Include | Equipment | 176 | 2023-04-19 | 1408 | keep | 0 | Apr | 2023 | 0.00095898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-19 11:15 | 2023-04-19 15:36 | 50 | 4:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN RISER SE REEMPLAZO CAJA PRIMARIA | C23041900172 | New_Event | Cutout Failure | Include | Include | Equipment | 261 | 2023-04-19 | 13050 | keep | 0 | Apr | 2023 | 0.0088883 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-19 11:20 | 2023-04-19 11:21 | 1843 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2304190000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-19 | 1843 | keep | 0 | Apr | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-04-19 11:21 | 2023-04-19 16:48 | 15 | 5:27 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23041900188 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 327 | 2023-04-19 | 4905 | keep | 0 | Apr | 2023 | 0.0033408 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-19 11:29 | 2023-04-19 14:35 | 4 | 3:06 | P | DESGANCHE | 1 X 8 EN XMR DESGANCHE PRIMARIO | C23041900176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-04-19 | 744 | keep | 0 | Apr | 2023 | 0.00050674 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-19 11:34 | 2023-04-19 13:21 | 30 | 1:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA Y PARARRAYO EN RISER 22-003HCFIONA | S23041900000 | New_Event | Cutout Failure | Include | Include | Equipment | 107 | 2023-04-19 | 3210 | keep | 0 | Apr | 2023 | 0.0021863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-19 11:46 | 2023-04-19 15:36 | 80 | 3:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 50 EN C/L Y SE REPARO SECUNDARIA | B23041900117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 230 | 2023-04-19 | 18400 | keep | 0 | Apr | 2023 | 0.012532 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-04-19 11:53 | 2023-04-19 15:17 | 40 | 3:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO PORTAFUSIBLE | C23041900181 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2023-04-19 | 8160 | keep | 0 | Apr | 2023 | 0.0055577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-04-19 12:03 | 2023-04-19 15:07 | 25 | 3:04 | P | CAUSAS EXTERNAS | 1 X 100 CLIENTE TIRA BAMBU SOBRE LINEA PRIMARIA Y ABRE PUENTE PRIMARIO | P23041900079 | New_Event | Damage From Public | Include | Include | Public | 184 | 2023-04-19 | 4600 | keep | 0 | Apr | 2023 | 0.003133 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-19 12:10 | 2023-04-19 15:33 | 200 | 3:23 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN CORTE DE LINEA SE RETEZO LINEAS PRIMARIAS | M23041900207 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 203 | 2023-04-19 | 40600 | keep | 0 | Apr | 2023 | 0.027652 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-19 12:11 | 2023-04-19 15:00 | 50 | 2:49 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23041900072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-04-19 | 8450 | keep | 0 | Apr | 2023 | 0.0057553 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-19 12:24 | 2023-04-19 14:28 | 138 | 2:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23041900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-04-19 | 17112 | keep | 0 | Apr | 2023 | 0.011655 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
BAYAMON | 2023-04-19 12:24 | 2023-04-19 14:31 | 60 | 2:07 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23041900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-04-19 | 7620 | keep | 0 | Apr | 2023 | 0.0051899 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-19 12:30 | 2023-04-19 14:00 | 16 | 1:30 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR DESGANCHE SECUNDARIO Y REPARAR SECUNDARIA | S23041900106 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 90 | 2023-04-19 | 1440 | keep | 0 | Apr | 2023 | 0.00098078 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-04-19 12:40 | 2023-04-19 14:40 | 7 | 2:00 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR ESCAPE DE 50 KVA X 50KVA | A23032400014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 120 | 2023-04-19 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-04-19 12:49 | 2023-04-19 17:31 | 50 | 4:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-A | C23041900201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 282 | 2023-04-19 | 14100 | keep | 0 | Apr | 2023 | 0.0096034 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-19 12:57 | 2023-04-19 20:19 | 7 | 7:22 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE LEVANTO LINEA | B23041800106 | New_Event | Primary Pole Failure | Include | Include | Equipment | 442 | 2023-04-19 | 3094 | keep | 0 | Apr | 2023 | 0.0021073 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-04-19 13:04 | 2023-04-19 13:09 | 5668 | 0:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CERRO POR CONTROL | R2304190000X | New_Event | Cutout Failure | Include | Include | Equipment | 5 | 2023-04-19 | 28340 | keep | 0 | Apr | 2023 | 0.019302 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
CANOVANAS | 2023-04-19 13:09 | 2023-04-19 17:56 | 30 | 4:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L SE REMPLAZO CAJA PRIMARIA | R23041900080 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 287 | 2023-04-19 | 8610 | keep | 0 | Apr | 2023 | 0.0058642 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-19 13:10 | 2023-04-19 15:25 | 200 | 2:15 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE PRIMARIO QUEMADO EN EL TRONCAL (RADIAL) NO FUNDIO | R23041900033 | New_Event | Switch Failure | Include | Include | Equipment | 135 | 2023-04-19 | 27000 | keep | 0 | Apr | 2023 | 0.01839 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-04-19 13:11 | 2023-04-19 16:28 | 25 | 3:17 | P | DESGANCHE | 1X65 EN C/L Y 1X50 EN OTRO C/L DESGANCHE | R23041900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-04-19 | 4925 | keep | 0 | Apr | 2023 | 0.0033544 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-19 13:26 | 2023-04-19 13:27 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO ALIMENTADOR | S23041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 181 | keep | 0 | Apr | 2023 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
CANOVANAS | 2023-04-19 13:35 | 2023-04-19 15:12 | 20 | 1:37 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PM AVERIADO (T-6) MEDIANTE G.O.I. SJ-230419-50 (WR-6311589) (NO HABIA OMS AL MOMENTO, NO SE PUDO GENERAR EVENTO) | R2304190000X | New_Event | Service Transformer Failure | Include | Include | Equipment | 97 | 2023-04-19 | 1940 | keep | 0 | Apr | 2023 | 0.0013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-19 13:36 | 2023-04-19 13:45 | 922 | 0:09 | T | ALIMENTADOR AMARRADO | DISPARO SU CARGA POR 1401-08 SE PROBO QUEDO EN SERVICIO | S23041900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-04-19 | 8298 | keep | 0 | Apr | 2023 | 0.0056517 | 0.00062797 | Sustained | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-04-19 13:36 | 2023-04-19 13:45 | 135 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO LLEVA CARGA 1346-05 SE PROBO QUEDO EN SERVICIO | S23041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-04-19 | 1215 | keep | 0 | Apr | 2023 | 0.00082753 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2023-04-19 13:36 | 2023-04-19 14:44 | 1 | 1:08 | P | DESGANCHE | 1X50 EN C/L 1X10 EN MONTURA DE XMRS DEL CLIENTE POR DESGANCHE PRIMARIO | R23041900040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-04-19 | 68 | keep | 0 | Apr | 2023 | 4.6314e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-19 13:36 | 2023-04-19 16:50 | 20 | 3:14 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRARON BAMBUS DE LAS LINEAS | M23041900242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-04-19 | 3880 | keep | 0 | Apr | 2023 | 0.0026427 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-19 13:42 | 2023-04-19 13:47 | 220 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR 98% POR 1303-05 | S23041900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-19 | 1100 | keep | 0 | Apr | 2023 | 0.0007492 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-04-19 13:42 | 2023-04-19 13:47 | 870 | 0:05 | T | CONDUCTOR ROTO O ABIERTO | DISPARO ALIMENTADOR LLEVA 98% DEL 1303-04 | S23041900000 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2023-04-19 | 4350 | keep | 0 | Apr | 2023 | 0.0029628 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BAYAMON | 2023-04-19 13:55 | 2023-04-19 13:56 | 1715 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | B2304190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 1715 | keep | 0 | Apr | 2023 | 0.0011681 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-04-19 14:20 | 2023-04-19 15:29 | 10 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA OMS FUERA DE SERVICIO | B23041900143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-04-19 | 690 | keep | 0 | Apr | 2023 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-19 14:22 | 2023-04-19 14:50 | 2 | 0:28 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIR RISER Y SE REPARO PUENTE DE CAJA A LINEA | S23041900069 | New_Event | Primary Wire Break | Include | Include | Equipment | 28 | 2023-04-19 | 56 | keep | 0 | Apr | 2023 | 3.8141e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-19 14:24 | 2023-04-19 14:27 | 220 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 98% POR 1303-05 | S23041900000 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-19 | 660 | keep | 0 | Apr | 2023 | 0.00044952 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-19 14:24 | 2023-04-19 14:27 | 870 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 98% DEL 1303-04 | S23041900000 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-19 | 2610 | keep | 0 | Apr | 2023 | 0.0017777 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-19 14:27 | 2023-04-19 17:15 | 116 | 2:48 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO ENREDADO ENTRE ARBOLES | S23041900088 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 168 | 2023-04-19 | 19488 | keep | 0 | Apr | 2023 | 0.013273 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
ARECIBO | 2023-04-19 14:51 | 2023-04-19 17:20 | 50 | 2:29 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23041900056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 149 | 2023-04-19 | 7450 | keep | 0 | Apr | 2023 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-04-19 15:10 | 2023-04-19 18:16 | 25 | 3:06 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA PUENTE | A23041900060 | New_Event | Primary Wire Break | Include | Include | Equipment | 186 | 2023-04-19 | 4650 | keep | 0 | Apr | 2023 | 0.0031671 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-19 15:22 | 2023-04-19 17:57 | 8 | 2:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE Y SE REPARO SECUNDARIA | B23041900161 | New_Event | Secondary Wire Break | Include | Include | Equipment | 155 | 2023-04-19 | 1240 | keep | 0 | Apr | 2023 | 0.00084456 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-19 15:22 | 2023-04-19 16:44 | 180 | 1:22 | P | DESGANCHE | 1 X 100 EN C/L ESGANCHE | B23041900165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-04-19 | 14760 | keep | 0 | Apr | 2023 | 0.010053 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
PONCE | 2023-04-19 15:22 | 2023-04-19 17:18 | 340 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CL FUERTES VIENTOS | P23041900123 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-04-19 | 39440 | keep | 0 | Apr | 2023 | 0.026862 | 0.00023157 | Sustained | FALSE | FALSE | Not_TMED_Event | 340
GUAYAMA | 2023-04-19 15:32 | 2023-04-19 17:41 | 10 | 2:09 | P | ANIMAL | 1 X 50 EN CL CRUCE DE FASE PRIMARIA POR AVE | P23041800145 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-04-19 | 1290 | keep | 0 | Apr | 2023 | 0.00087861 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-19 15:44 | 2023-04-19 19:10 | 80 | 3:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA QUEMADA | A23041900085 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2023-04-19 | 16480 | keep | 0 | Apr | 2023 | 0.011224 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-19 15:45 | 2023-04-19 16:00 | 4 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR Y REPARAR PUENTE SECUNDARIO | S23041900044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-04-19 | 60 | keep | 0 | Apr | 2023 | 4.0866e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-04-19 16:14 | 2023-04-19 18:52 | 10 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23041900326 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-04-19 | 1580 | keep | 0 | Apr | 2023 | 0.0010761 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-19 16:15 | 2023-04-19 16:16 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | S23041900000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 181 | keep | 0 | Apr | 2023 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2023-04-19 16:15 | 2023-04-19 16:19 | 2052 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% DE SU CARGA POR 1118-10 LLEVA 1115-03 | S23041900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-19 | 8208 | keep | 0 | Apr | 2023 | 0.0055904 | 0.0013976 | Momentary | FALSE | FALSE | Not_TMED_Event | 2052
SAN JUAN | 2023-04-19 16:15 | 2023-04-19 16:19 | 134 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% DE SU CARGA POR 1118-10 SU CARGA POR 1111-01 | S23041900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-04-19 | 536 | keep | 0 | Apr | 2023 | 0.00036507 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
ARECIBO | 2023-04-19 16:17 | 2023-04-19 17:25 | 40 | 1:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23041900092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 68 | 2023-04-19 | 2720 | keep | 0 | Apr | 2023 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-04-19 16:27 | 2023-04-19 21:20 | 360 | 4:53 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 50 EN CORTE DE LINEA SE SEPARARON LINEAS CRUZADAS | M23041900329 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 293 | 2023-04-19 | 105480 | keep | 0 | Apr | 2023 | 0.071842 | 0.00024519 | Sustained | FALSE | FALSE | Not_TMED_Event | 360
CANOVANAS | 2023-04-19 16:31 | 2023-04-19 16:56 | 10 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN XMR PARA REPARAR/CERRAR NEUTRAL DEL SISTEMA (NO HABIA OMS DISPONIBLE AL MOMENTO) | R2304190000X | New_Event | Primary Wire Break | Include | Include | Equipment | 25 | 2023-04-19 | 250 | keep | 0 | Apr | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-19 16:31 | 2023-04-19 18:18 | 60 | 1:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M23041900331 | New_Event | Cutout Failure | Include | Include | Equipment | 107 | 2023-04-19 | 6420 | keep | 0 | Apr | 2023 | 0.0043726 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-04-19 16:36 | 2023-04-19 18:23 | 25 | 1:47 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO SE ENCONTRO CAUSA | M23041900334 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 107 | 2023-04-19 | 2675 | keep | 0 | Apr | 2023 | 0.0018219 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-19 17:07 | 2023-04-19 17:45 | 1 | 0:38 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO EN TRANSFORMADOR | M23041600147 | New_Event | Primary Wire Break | Include | Include | Equipment | 38 | 2023-04-19 | 38 | keep | 0 | Apr | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-19 17:15 | 2023-04-19 20:17 | 348 | 3:02 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE Y SE CERRO PUENTE PRIMARIO ENREDADO ENTRE ARBOLES | S23041900088 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 182 | 2023-04-19 | 63336 | keep | 0 | Apr | 2023 | 0.043138 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-19 17:18 | 2023-04-19 18:25 | 7 | 1:07 | P | SECUNDARIA/DESGANCHE | 1 X20 EN TRANSFORMADOR DESGANCHE SECUNDARIO | S23041900184 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 67 | 2023-04-19 | 469 | keep | 0 | Apr | 2023 | 0.00031943 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-19 17:43 | 2023-04-19 20:16 | 60 | 2:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/ Y SE REMPLAZO CAJA PRIMARIA | B23041900187 | New_Event | Cutout Failure | Include | Include | Equipment | 153 | 2023-04-19 | 9180 | keep | 0 | Apr | 2023 | 0.0062525 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-04-19 18:04 | 2023-04-19 19:10 | 3 | 1:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA EN TRANSFORMADOR | P23041900164 | New_Event | Cutout Failure | Include | Include | Equipment | 66 | 2023-04-19 | 198 | keep | 0 | Apr | 2023 | 0.00013486 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-04-19 18:16 | 2023-04-19 18:23 | 232 | 0:07 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR Y SE CIERRA PUENTE PRIMARIO | A23041900060 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 7 | 2023-04-19 | 1624 | keep | 0 | Apr | 2023 | 0.0011061 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-19 18:21 | 2023-04-19 18:22 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23041900093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-19 | 2039 | keep | 0 | Apr | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
GUAYAMA | 2023-04-19 18:28 | 2023-04-19 21:36 | 22 | 3:08 | P | CAUSAS EXTERNAS | 1 X 65 EN CL CARPA CRUZA LINEA | P23041900168 | New_Event | Damage From Public | Include | Include | Public | 188 | 2023-04-19 | 4136 | keep | 0 | Apr | 2023 | 0.002817 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
YAUCO | 2023-04-19 18:46 | 2023-04-20 13:04 | 1 | 18:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M23041900373 | New_Event | Primary Wire Break | Include | Include | Equipment | 1098 | 2023-04-19 | 1098 | keep | 0 | Apr | 2023 | 0.00074784 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-19 18:47 | 2023-04-20 07:34 | 24 | 12:47 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23041900260 | New_Event | Animals | Include | Include | Wildlife | 767 | 2023-04-19 | 18408 | keep | 0 | Apr | 2023 | 0.012538 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BARRANQUITAS | 2023-04-19 19:03 | 2023-04-19 21:51 | 70 | 2:48 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | C23041900265 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-04-19 | 11760 | keep | 0 | Apr | 2023 | 0.0080097 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-04-19 19:13 | 2023-04-20 12:50 | 8 | 17:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C23041900271 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1057 | 2023-04-19 | 8456 | keep | 0 | Apr | 2023 | 0.0057593 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-19 19:14 | 2023-04-19 23:17 | 16 | 4:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR SE REPARO SECUNDARIA | S23041900207 | New_Event | Secondary Wire Break | Include | Include | Equipment | 243 | 2023-04-19 | 3888 | keep | 0 | Apr | 2023 | 0.0026481 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-04-19 19:15 | 2023-04-19 22:00 | 100 | 2:45 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASES | M23041900378 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-04-19 | 16500 | keep | 0 | Apr | 2023 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-19 19:20 | 2023-04-20 08:32 | 40 | 13:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041900381 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 792 | 2023-04-19 | 31680 | keep | 0 | Apr | 2023 | 0.021577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-04-19 19:33 | 2023-04-20 15:05 | 1 | 19:32 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE PRIMARIO Y CAJA PRIMARIA RELACIONADO EVENTO A23041900121 | A23042000080 | New_Event | Primary Wire Break | Include | Include | Equipment | 1172 | 2023-04-19 | 1172 | keep | 0 | Apr | 2023 | 0.00079824 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-19 19:43 | 2023-04-20 10:00 | 300 | 14:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041900384 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 857 | 2023-04-19 | 257100 | keep | 0 | Apr | 2023 | 0.17511 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2023-04-19 19:46 | 2023-04-20 14:00 | 6 | 18:14 | P | CONDUCTOR ROTO O ABIERTO | PERSONAL INDICO QUE LOS CLIENTES ESTABAN SIN SERVICIO DEBIDO A NEUTRAL PRIMARIO SE ABRIO TRANSFORMADOR REPARAR NEUTRAL PRIMARIO | A23041900127 | New_Event | Primary Wire Break | Include | Include | Equipment | 1094 | 2023-04-19 | 6564 | keep | 0 | Apr | 2023 | 0.0044707 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-04-19 19:55 | 2023-04-20 07:00 | 5 | 11:05 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO A CAJA EN TRANSFORMADOR | P23041900180 | New_Event | Primary Wire Break | Include | Include | Equipment | 665 | 2023-04-19 | 3325 | keep | 0 | Apr | 2023 | 0.0022646 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-04-19 20:14 | 2023-04-20 08:15 | 2 | 12:01 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE | A23041900131 | New_Event | Animals | Include | Include | Wildlife | 721 | 2023-04-19 | 1442 | keep | 0 | Apr | 2023 | 0.00098214 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-04-19 20:26 | 2023-04-20 12:16 | 30 | 15:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23041900389 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 950 | 2023-04-19 | 28500 | keep | 0 | Apr | 2023 | 0.019411 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-19 20:35 | 2023-04-20 10:29 | 15 | 13:54 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | B23041900199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 834 | 2023-04-19 | 12510 | keep | 0 | Apr | 2023 | 0.0085205 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-19 22:52 | 2023-04-20 01:39 | 253 | 2:47 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | S23041900237 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-04-19 | 42251 | keep | 0 | Apr | 2023 | 0.028777 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
CAGUAS | 2023-04-19 23:03 | 2023-04-20 08:18 | 35 | 9:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C23041900284 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 555 | 2023-04-19 | 19425 | keep | 0 | Apr | 2023 | 0.01323 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-04-19 23:29 | 2023-04-20 15:19 | 15 | 15:50 | P | SECUNDARIA/DESGANCHE | SE ABRE MONTURA PARA REPARAR SECUNDARIA Y DESGANCHE SECUNDARIO | S23041900239 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 950 | 2023-04-19 | 14250 | keep | 0 | Apr | 2023 | 0.0097056 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-20 01:14 | 2023-04-20 09:14 | 12 | 8:00 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DE RISER @ T-117 EN SERVICIO | B23042000001 | New_Event | UG Cable Fault | Include | Include | Equipment | 480 | 2023-04-20 | 5760 | keep | 0 | Apr | 2023 | 0.0039231 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-04-20 02:01 | 2023-04-20 20:30 | 6 | 18:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN RISER SE DESCONECTO TOMA SECUNDARIA SOTERRADA AVERIADA | M23042000001 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1109 | 2023-04-20 | 6654 | keep | 0 | Apr | 2023 | 0.004532 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-04-20 02:39 | 2023-04-20 02:53 | 1615 | 0:14 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23042000003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2023-04-20 | 22610 | keep | 0 | Apr | 2023 | 0.0154 | 0.0011 | Sustained | FALSE | FALSE | Not_TMED_Event | 1615
BAYAMON | 2023-04-20 05:31 | 2023-04-20 08:16 | 18 | 2:45 | P | CAUSAS EXTERNAS | 1 X 10 EN XMR POR CAMION QUE IMPACTO GUY EN POSTE | B23042000004 | New_Event | Damage From Public | Include | Include | Public | 165 | 2023-04-20 | 2970 | keep | 0 | Apr | 2023 | 0.0020229 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2023-04-20 06:00 | 2023-04-20 06:01 | 396 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23042000001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 396 | keep | 0 | Apr | 2023 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
HUMACAO | 2023-04-20 06:42 | 2023-04-20 06:43 | 551 | 0:01 | T | ANIMAL | RECIERRE | C23042000010 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-20 | 551 | keep | 0 | Apr | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-04-20 06:43 | 2023-04-20 08:38 | 1 | 1:55 | P | ANIMAL | 2 X 30 EN RISER Y 2 X 80 EN C/L CRUCE X AVE | C23042000011 | 1st_after_momentary | Animals | Include | Include | Wildlife | 115 | 2023-04-20 | 115 | keep | 0 | Apr | 2023 | 7.8326e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-20 06:48 | 2023-04-20 09:55 | 225 | 3:07 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B23042000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2023-04-20 | 42075 | keep | 0 | Apr | 2023 | 0.028657 | 0.00015325 | Sustained | FALSE | FALSE | Not_TMED_Event | 225
CANOVANAS | 2023-04-20 07:08 | 2023-04-20 10:34 | 62 | 3:26 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | R23042000023 | New_Event | Animals | Include | Include | Wildlife | 206 | 2023-04-20 | 12772 | keep | 0 | Apr | 2023 | 0.008699 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
CANOVANAS | 2023-04-20 07:18 | 2023-04-20 11:18 | 38 | 4:00 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | R23042000024 | New_Event | Animals | Include | Include | Wildlife | 240 | 2023-04-20 | 9120 | keep | 0 | Apr | 2023 | 0.0062116 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BAYAMON | 2023-04-20 07:48 | 2023-04-20 07:49 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR SOLO LLEVA EL 50% DE SU CARAGA | B23042000009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 766 | keep | 0 | Apr | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
MAYAGÃœEZ | 2023-04-20 07:56 | 2023-04-20 09:53 | 20 | 1:57 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23042000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-04-20 | 2340 | keep | 0 | Apr | 2023 | 0.0015938 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-04-20 08:00 | 2023-04-20 10:45 | 1 | 2:45 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23042000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2023-04-20 | 165 | keep | 0 | Apr | 2023 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-20 08:20 | 2023-04-20 11:53 | 7 | 3:33 | P | SOBRECARGA | 1 X 100 EN SU-B POR CARGA | B23042000011 | New_Event | Trip Due To Overload | Include | Include | Other | 213 | 2023-04-20 | 1491 | keep | 0 | Apr | 2023 | 0.0010155 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-04-20 08:21 | 2023-04-20 17:58 | 1 | 9:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR | A23042000022 | New_Event | Cutout Failure | Include | Include | Equipment | 577 | 2023-04-20 | 577 | keep | 0 | Apr | 2023 | 0.00039299 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-20 08:36 | 2023-04-20 13:55 | 20 | 5:19 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA NO CAUSA | A23042000027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 319 | 2023-04-20 | 6380 | keep | 0 | Apr | 2023 | 0.0043454 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-04-20 08:43 | 2023-04-20 10:57 | 8 | 2:14 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REMOVIO PARARRAYO | P23042000013 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 134 | 2023-04-20 | 1072 | keep | 0 | Apr | 2023 | 0.00073013 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-04-20 08:49 | 2023-04-20 10:45 | 7 | 1:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR LINEA SECUNDARIA AVERIADA | A23042000030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 116 | 2023-04-20 | 812 | keep | 0 | Apr | 2023 | 0.00055305 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-20 08:50 | 2023-04-20 17:37 | 10 | 8:47 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE SECUNDARIO OMS FUERA DE SERVICIO | S2304200000X | New_Event | Secondary Vegetation | Include | Include | Vegetation | 527 | 2023-04-20 | 5270 | keep | 0 | Apr | 2023 | 0.0035894 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-20 09:02 | 2023-04-20 10:19 | 7 | 1:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE DESGANCHO Y SE REPARO SECUNDARIA | S23041900224 | New_Event | Secondary Wire Break | Include | Include | Equipment | 77 | 2023-04-20 | 539 | keep | 0 | Apr | 2023 | 0.00036711 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-04-20 09:06 | 2023-04-20 15:02 | 40 | 5:56 | P | CONDUCTOR ROTO O ABIERTO | FIJO BAJANTE DE CAJA A LINEA NO FUNDIO | C23042000060 | New_Event | Primary Wire Break | Include | Include | Equipment | 356 | 2023-04-20 | 14240 | keep | 0 | Apr | 2023 | 0.0096988 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-04-20 09:10 | 2023-04-20 11:53 | 40 | 2:43 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23042000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-04-20 | 6520 | keep | 0 | Apr | 2023 | 0.0044407 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-20 09:13 | 2023-04-20 12:40 | 70 | 3:27 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA AVE | A23042000034 | New_Event | Animals | Include | Include | Wildlife | 207 | 2023-04-20 | 14490 | keep | 0 | Apr | 2023 | 0.0098691 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-04-20 09:20 | 2023-04-20 12:22 | 40 | 3:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23042000026 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2023-04-20 | 7280 | keep | 0 | Apr | 2023 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-04-20 09:24 | 2023-04-20 11:33 | 11 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON 2 BARRAS EN PEDESTAL | R23042000044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2023-04-20 | 1419 | keep | 0 | Apr | 2023 | 0.00096647 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-04-20 09:29 | 2023-04-20 23:00 | 60 | 13:31 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO 1 POSTE Y SE ABRIO PUENTES A OTRO POSTE PARTIDO EN EL AREA Y SE CERRO CORTE DE LINEA | M23042000034 | New_Event | Primary Pole Failure | Include | Include | Equipment | 811 | 2023-04-20 | 48660 | keep | 0 | Apr | 2023 | 0.033142 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-20 09:38 | 2023-04-20 13:00 | 712 | 3:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L DE EMERGENCIA POR CORNER BRAKET DEFECTUOSO Y SE ANCLARON LINEAS AL POSTE | R23042000042 | New_Event | Primary Wire Break | Include | Include | Equipment | 202 | 2023-04-20 | 143824 | keep | 0 | Apr | 2023 | 0.097958 | 0.00048494 | Sustained | FALSE | FALSE | Not_TMED_Event | 712
PONCE | 2023-04-20 09:45 | 2023-04-20 09:46 | 485 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QIUEDA EN SERVICIO | P23042000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 485 | keep | 0 | Apr | 2023 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
UTUADO | 2023-04-20 09:52 | 2023-04-20 16:50 | 30 | 6:58 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 418 | 2023-04-20 | 12540 | keep | 0 | Apr | 2023 | 0.0085409 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-20 10:08 | 2023-04-20 15:02 | 6 | 4:54 | P | CONDUCTOR ARRIADO O CRUZADO | INSTALO POSTE PARA PODER RETEZAR LINEAS | C23042000080 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 294 | 2023-04-20 | 1764 | keep | 0 | Apr | 2023 | 0.0012015 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-04-20 10:08 | 2023-04-20 12:00 | 100 | 1:52 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-04-20 | 11200 | keep | 0 | Apr | 2023 | 0.0076283 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-20 10:10 | 2023-04-20 11:04 | 80 | 0:54 | P | ANIMAL | 1 X 65 Y 1 X 40 EN C/L CRUCE POR AVE | B23042000034 | New_Event | Animals | Include | Include | Wildlife | 54 | 2023-04-20 | 4320 | keep | 0 | Apr | 2023 | 0.0029423 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-20 10:14 | 2023-04-20 14:00 | 6 | 3:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REMPLAZO SECUNDARIA SOTERRADA OMS DOWN | S23041300053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 226 | 2023-04-20 | 1356 | keep | 0 | Apr | 2023 | 0.00092357 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-20 10:19 | 2023-04-20 15:12 | 65 | 4:53 | P | ARBOL SOBRE LINEA | 1 X 40 Y 1 X 50 EN C/LS RETIRO ARBOL DE LAS LINEAS | C23042000085 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 293 | 2023-04-20 | 19045 | keep | 0 | Apr | 2023 | 0.012971 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-04-20 10:46 | 2023-04-20 13:07 | 138 | 2:21 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | S23042000106 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-04-20 | 19458 | keep | 0 | Apr | 2023 | 0.013253 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
BAYAMON | 2023-04-20 10:50 | 2023-04-20 10:51 | 723 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO 1912-08 LLEVA 1711-02 & 1711-05 | S2304200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-20 | 723 | keep | 0 | Apr | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-04-20 10:50 | 2023-04-20 10:51 | 1976 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO 1912-08 Y LLEVA 1711-02 & 1711-05 | S2304200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 1976 | keep | 0 | Apr | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-04-20 10:50 | 2023-04-20 10:51 | 577 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO LLEVA LA CARGA DEL 1711-02 & 1711-05 | S2304200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-20 | 577 | keep | 0 | Apr | 2023 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-04-20 10:51 | 2023-04-20 12:41 | 140 | 1:50 | P | ANIMAL | 1 X 80 EN C/L SE RETIRO IGUANA | B23042000042 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-04-20 | 15400 | keep | 0 | Apr | 2023 | 0.010489 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2023-04-20 11:00 | 2023-04-20 11:50 | 1 | 0:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN MONTURA POR MAL TIEMPO | B23042000048 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 50 | 2023-04-20 | 50 | keep | 0 | Apr | 2023 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-04-20 11:33 | 2023-04-20 15:04 | 48 | 3:31 | P | CAUSAS EXTERNAS | 1 X 20 EN CORTE DE LINEA CRUCE POR HILO DE CHIRINGA | R23042000078 | New_Event | Damage From Public | Include | Include | Public | 211 | 2023-04-20 | 10128 | keep | 0 | Apr | 2023 | 0.0068981 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2023-04-20 11:47 | 2023-04-20 11:48 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 1907-05 | S2304200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 2956 | keep | 0 | Apr | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-04-20 11:48 | 2023-04-20 11:49 | 2435 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO 1909-08 | S2304200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-20 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
CANOVANAS | 2023-04-20 11:54 | 2023-04-20 12:32 | 1 | 0:38 | P | DESGANCHE | 1X 40 RISER Y DESGANCHE | R23042000058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2023-04-20 | 38 | keep | 0 | Apr | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-20 12:17 | 2023-04-20 12:53 | 7 | 0:36 | P | TRANSFORMADOR AVERIADO | SJ-230420-50 SE REEMPLAZO PM T-13 CON DERRAME DE ACEITE | R23042000059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 36 | 2023-04-20 | 252 | keep | 0 | Apr | 2023 | 0.00017164 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-04-20 12:29 | 2023-04-20 13:22 | 12 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | C23042000122 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-04-20 | 636 | keep | 0 | Apr | 2023 | 0.00043318 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-20 12:30 | 2023-04-20 13:20 | 2 | 0:50 | P | SECUNDARIA/DESGANCHE | SE ABRE TRANSFORMADOR Y SE REPAOR BAJANTE SECUNDARIO Y DESGANCHE SECUNDARIO | S23042000121 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 50 | 2023-04-20 | 100 | keep | 0 | Apr | 2023 | 6.811e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-20 12:35 | 2023-04-20 12:36 | 661 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-02 SE CERRO POR SCADA | S23042000128 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-20 | 661 | keep | 0 | Apr | 2023 | 0.0004502 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-04-20 12:35 | 2023-04-20 12:36 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 16% 1206-03 SE CERRO POR SCADA | S23042000128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 3718 | keep | 0 | Apr | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2023-04-20 12:38 | 2023-04-20 14:24 | 10 | 1:46 | P | CONDUCTOR ROTO O ABIERTO | FIJO BAJANTE DE LINEA CAJA | C23042000126 | New_Event | Primary Wire Break | Include | Include | Equipment | 106 | 2023-04-20 | 1060 | keep | 0 | Apr | 2023 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-20 12:49 | 2023-04-20 12:52 | 3296 | 0:03 | T | DESGANCHE | DISPARO CERRADO X CONTROL LUEGO EN PATRULLAJE SE ENCONTRO DESGANCHE | C23042000128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-04-20 | 9888 | keep | 0 | Apr | 2023 | 0.0067347 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
FAJARDO | 2023-04-20 12:55 | 2023-04-20 13:16 | 2 | 0:21 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23042000065 | New_Event | Animals | Include | Include | Wildlife | 21 | 2023-04-20 | 42 | keep | 0 | Apr | 2023 | 2.8606e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-20 12:59 | 2023-04-20 14:32 | 35 | 1:33 | P | ANIMAL | 1 X 65 EN C/L PRINCIPAL Y 1 X 25 EN C/L PROVISIONAL CRUCE X IGUANA | B23042000067 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-04-20 | 3255 | keep | 0 | Apr | 2023 | 0.002217 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-04-20 13:04 | 2023-04-20 13:05 | 207 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | S2304200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 207 | keep | 0 | Apr | 2023 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-04-20 13:16 | 2023-04-20 18:09 | 30 | 4:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23042000136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-04-20 | 8790 | keep | 0 | Apr | 2023 | 0.0059868 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-20 13:19 | 2023-04-20 16:35 | 1 | 3:16 | P | NO SE REPORTO CAUSA | 2 X 40 EN SU-5 NO CUASA | S23042000137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2023-04-20 | 196 | keep | 0 | Apr | 2023 | 0.00013349 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-20 13:20 | 2023-04-20 17:08 | 100 | 3:48 | P | DESGANCHE | 1 X 40 EN C/L Y 1 X 50 EN C/L DESGANCHE | B23042000072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-04-20 | 22800 | keep | 0 | Apr | 2023 | 0.015529 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-20 13:25 | 2023-04-20 20:57 | 50 | 7:32 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L LEVANTO NEUTRAL PRIMARIO | C23042000133 | New_Event | Primary Wire Break | Include | Include | Equipment | 452 | 2023-04-20 | 22600 | keep | 0 | Apr | 2023 | 0.015393 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-04-20 13:27 | 2023-04-20 17:15 | 10 | 3:48 | P | SECUNDARIA/OTROS | SE ABRE MONTURA DE TRANSFORMADOR PARA REPARACIONES EN PEDESTAL SECUNDARIO | M23042000078 | New_Event |  |  |  |  | 228 | 2023-04-20 | 2280 | keep | 0 | Apr | 2023 | 0.0015529 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-20 13:28 | 2023-04-20 17:10 | 7 | 3:42 | P | DESGANCHE | SE ABRIO CORTE DE LINEA POR EMERGENCIA PARA QUE CONTRATISTA REALIZARA DESGANCHE MASIVO | R23042000067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-04-20 | 1554 | keep | 0 | Apr | 2023 | 0.0010584 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-04-20 13:32 | 2023-04-20 19:17 | 10 | 5:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO 3 TRANSFORMADOR DE 50KVA 3 CAJA Y 3 PARARRAYO | S23042000138 | New_Event | Service Transformer Failure | Include | Include | Equipment | 345 | 2023-04-20 | 3450 | keep | 0 | Apr | 2023 | 0.0023498 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-20 13:34 | 2023-04-20 13:36 | 661 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1620-02 SE CERRO POR SCADA | S23042000128 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-20 | 1322 | keep | 0 | Apr | 2023 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-04-20 13:34 | 2023-04-20 13:37 | 3718 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 16% 1206-03 SE CERRO POR SCADA | S23042000128 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-20 | 11154 | keep | 0 | Apr | 2023 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
MAYAGÃœEZ | 2023-04-20 13:48 | 2023-04-20 15:20 | 40 | 1:32 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA ESCAVADORA IMPACTO POSTE Y CAUSO CRUCE DE LINEAS | M23042000083 | New_Event | Damage From Public | Include | Include | Public | 92 | 2023-04-20 | 3680 | keep | 0 | Apr | 2023 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-20 13:57 | 2023-04-20 18:06 | 40 | 4:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23042000085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-04-20 | 9960 | keep | 0 | Apr | 2023 | 0.0067837 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-20 14:17 | 2023-04-20 15:16 | 5 | 0:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | R23042000074 | New_Event | Service Transformer Failure | Include | Include | Equipment | 59 | 2023-04-20 | 295 | keep | 0 | Apr | 2023 | 0.00020092 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-04-20 14:25 | 2023-04-20 17:56 | 138 | 3:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23042000149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2023-04-20 | 29118 | keep | 0 | Apr | 2023 | 0.019832 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
MAYAGÃœEZ | 2023-04-20 14:25 | 2023-04-20 15:52 | 2 | 1:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO LINEA SECUNDARIA | M23042000091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 87 | 2023-04-20 | 174 | keep | 0 | Apr | 2023 | 0.00011851 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-04-20 14:25 | 2023-04-20 16:22 | 7 | 1:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042000089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 117 | 2023-04-20 | 819 | keep | 0 | Apr | 2023 | 0.00055782 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-04-20 14:38 | 2023-04-20 16:47 | 8 | 2:09 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M23042000095 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-04-20 | 1032 | keep | 0 | Apr | 2023 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-04-20 15:20 | 2023-04-20 18:58 | 100 | 3:38 | P | ANIMAL | 1 X 40 1 X 50 Y 1 X 65 EN C/LS CRUCE X AVE | C23042000163 | New_Event | Animals | Include | Include | Wildlife | 218 | 2023-04-20 | 21800 | keep | 0 | Apr | 2023 | 0.014848 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-20 15:25 | 2023-04-20 17:05 | 25 | 1:40 | P | TRANSFORMADOR AVERIADO | SJ-230420-51 SE REEMPLAZO TRANSFORMADOR PM T-17 DE 75 KVA X 75 KVA CON DERRAME DE ACEITE | R23042000082 | New_Event | Service Transformer Failure | Include | Include | Equipment | 100 | 2023-04-20 | 2500 | keep | 0 | Apr | 2023 | 0.0017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-20 15:25 | 2023-04-20 15:27 | 3296 | 0:02 | T | DESGANCHE | DISPARO CERRADO X CONTROL LUEGO EN PATRULLAJE SE ENCONTRO DESGANCHE | C23042000166 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-20 | 6592 | keep | 0 | Apr | 2023 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
AGUADILLA | 2023-04-20 15:30 | 2023-04-20 16:00 | 8 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR PAR REPARAR BAJANTES SECUNDARIOS | M23042000015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-04-20 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-20 15:47 | 2023-04-20 18:41 | 7 | 2:54 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23042000172 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-04-20 | 1218 | keep | 0 | Apr | 2023 | 0.00082957 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-04-20 16:16 | 2023-04-20 17:34 | 40 | 1:18 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23042000182 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-04-20 | 3120 | keep | 0 | Apr | 2023 | 0.002125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-20 16:50 | 2023-04-20 17:10 | 4291 | 0:20 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONAL EN EL AREA CERTIFICARON PERSONAL FUERA SE PROBO QUEDO EN SERVICIO | S23042000196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2023-04-20 | 85820 | keep | 0 | Apr | 2023 | 0.058452 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2023-04-20 17:27 | 2023-04-20 19:01 | 4431 | 1:34 | T | CAUSAS EXTERNAS | DISPARO DE INTERRUPTOR CAMION SE LLEVO TENSOR QUE SE ENREDO EN EL ALIMENTADOR SE RETIRO TENSOR CON VARETA Y SE CERRO POR CONTROL SWF BY-230420-02 | B23042000130 | New_Event | Damage From Public | Include | Include | Public | 94 | 2023-04-20 | 416514 | keep | 0 | Apr | 2023 | 0.28369 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
CAGUAS | 2023-04-20 17:55 | 2023-04-20 21:16 | 80 | 3:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23042000191 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2023-04-20 | 16080 | keep | 0 | Apr | 2023 | 0.010952 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-04-20 18:01 | 2023-04-20 18:02 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042000194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 551 | keep | 0 | Apr | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
HUMACAO | 2023-04-20 18:06 | 2023-04-20 20:58 | 6 | 2:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C23042000195 | New_Event | Cutout Failure | Include | Include | Equipment | 172 | 2023-04-20 | 1032 | keep | 0 | Apr | 2023 | 0.00070289 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-20 18:40 | 2023-04-21 11:15 | 31 | 16:35 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHE SEC | S23042000244 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 995 | 2023-04-20 | 30845 | keep | 0 | Apr | 2023 | 0.021008 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-04-20 18:47 | 2023-04-20 20:37 | 1483 | 1:50 | P | ALIMENTADOR AMARRADO | DISPARO PB-A MACHETE QUEMADO 1336-08 SE REPARO Y SE CERRO MACHETE 30% POR 1336-08 | S23042000251 | New_Event | Feeder Load Transferred | Include | Include | Other | 110 | 2023-04-20 | 163130 | keep | 0 | Apr | 2023 | 0.11111 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-04-20 18:47 | 2023-04-20 20:37 | 1531 | 1:50 | P | ALIMENTADOR AMARRADO | DISPARO PB-A MACHETE QUEMADO 1336-08 SE REPARO Y SE CERRO MACHETE SU 15% POR 1336-08 | S23042000251 | New_Event | Feeder Load Transferred | Include | Include | Other | 110 | 2023-04-20 | 168410 | keep | 0 | Apr | 2023 | 0.1147 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-04-20 18:47 | 2023-04-20 19:24 | 2646 | 0:37 | P | DESCONECTIVO DEFECTUOSO | DISPARO PB-A MACHETE QUEMADO Y SE SECCIONALIZO TRAMO | S23042000251 | New_Event | Switch Failure | Include | Include | Equipment | 37 | 2023-04-20 | 97902 | keep | 0 | Apr | 2023 | 0.066681 | 0.0018022 | Sustained | FALSE | FALSE | Not_TMED_Event | 2646
MAYAGÃœEZ | 2023-04-20 19:22 | 2023-04-20 21:45 | 80 | 2:23 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | M23042000124 | New_Event | Animals | Include | Include | Wildlife | 143 | 2023-04-20 | 11440 | keep | 0 | Apr | 2023 | 0.0077917 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-20 19:24 | 2023-04-20 20:37 | 577 | 1:13 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE Y SE ENERGIZO TRAMO | S23042000025 | Partial_restoration | Switch Failure | Include | Include | Equipment | 73 | 2023-04-20 | 42121 | keep | 0 | Apr | 2023 | 0.028688 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-20 19:24 | 2023-04-20 20:49 | 2 | 1:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042000273 | New_Event | Secondary Wire Break | Include | Include | Equipment | 85 | 2023-04-20 | 170 | keep | 0 | Apr | 2023 | 0.00011579 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-20 19:48 | 2023-04-21 11:15 | 7 | 15:27 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | B23042000276 | New_Event | Vegetation Contact | Include | Include | Vegetation | 927 | 2023-04-20 | 6489 | keep | 0 | Apr | 2023 | 0.0044196 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-04-20 19:48 | 2023-04-21 10:25 | 300 | 14:37 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE AVERIADO | P23042000114 | New_Event | Switch Failure | Include | Include | Equipment | 877 | 2023-04-20 | 263100 | keep | 0 | Apr | 2023 | 0.1792 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2023-04-20 19:51 | 2023-04-20 22:02 | 80 | 2:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | EVENTO TRANSFERIDO POR LA REGION DE ARECIBO 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | A23042000119 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2023-04-20 | 10480 | keep | 0 | Apr | 2023 | 0.0071379 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-20 20:09 | 2023-04-21 09:48 | 39 | 13:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SEC | B23042000279 | New_Event | Secondary Wire Break | Include | Include | Equipment | 819 | 2023-04-20 | 31941 | keep | 0 | Apr | 2023 | 0.021755 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2023-04-20 20:20 | 2023-04-21 10:36 | 5 | 14:16 | P | CONDUCTOR ROTO O ABIERTO | REPARAR BAJANTE PRIMARIO DE TRANSFORMADOR | M23042000139 | New_Event | Primary Wire Break | Include | Include | Equipment | 856 | 2023-04-20 | 4280 | keep | 0 | Apr | 2023 | 0.0029151 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-04-20 20:53 | 2023-04-20 20:54 | 1862 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC | R23042000096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-20 | 1862 | keep | 0 | Apr | 2023 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-04-20 20:53 | 2023-04-20 20:54 | 1613 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC | R23042000096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-20 | 1613 | keep | 0 | Apr | 2023 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-04-20 20:53 | 2023-04-20 20:54 | 1448 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC | R23042000096 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-20 | 1448 | keep | 0 | Apr | 2023 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
BAYAMON | 2023-04-20 20:54 | 2023-04-20 21:06 | 1 | 0:12 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | B23042000245 | New_Event | Animals | Include | Include | Wildlife | 12 | 2023-04-20 | 12 | keep | 0 | Apr | 2023 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-20 21:45 | 2023-04-20 21:46 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SOLO LLEVA EL 50% DE SU CARGA | B23042000286 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 766 | keep | 0 | Apr | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-04-20 22:08 | 2023-04-21 07:37 | 193 | 9:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA Y 1 X 100 Y 2N 65 EN OTROS CORTES DE LINEA | S23042000638 | New_Event | Cutout Failure | Include | Include | Equipment | 569 | 2023-04-20 | 109817 | keep | 0 | Apr | 2023 | 0.074796 | 0.00013145 | Sustained | FALSE | FALSE | Not_TMED_Event | 193
SAN JUAN | 2023-04-20 23:55 | 2023-04-20 23:56 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2304200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-20 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-04-21 00:38 | 2023-04-21 15:30 | 24 | 14:52 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S23042100004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 892 | 2023-04-21 | 21408 | keep | 0 | Apr | 2023 | 0.014581 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2023-04-21 01:11 | 2023-04-21 04:07 | 130 | 2:56 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23042100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-04-21 | 22880 | keep | 0 | Apr | 2023 | 0.015583 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2023-04-21 01:12 | 2023-04-21 02:28 | 173 | 1:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 Y 2 X 50 EN CORTES DE LINEAS SE REEMPLAZARON CAJAS QUEMADAS | R23042100093 | New_Event | Cutout Failure | Include | Include | Equipment | 76 | 2023-04-21 | 13148 | keep | 0 | Apr | 2023 | 0.008955 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
PONCE | 2023-04-21 03:12 | 2023-04-21 06:29 | 12 | 3:17 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR AVE | P23042100008 | New_Event | Animals | Include | Include | Wildlife | 197 | 2023-04-21 | 2364 | keep | 0 | Apr | 2023 | 0.0016101 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-04-21 04:51 | 2023-04-21 09:16 | 50 | 4:25 | P | ANIMAL | 1 X 50 EN C/L Y 1 X 10 EN XMR CRUCE X AVE | R23042100002 | New_Event | Animals | Include | Include | Wildlife | 265 | 2023-04-21 | 13250 | keep | 0 | Apr | 2023 | 0.0090245 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-21 05:01 | 2023-04-22 13:26 | 7 | 32:25 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA AVERIADO POR UNO DE IGUAL CAPACIDAD | S23042100007 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1945 | 2023-04-21 | 13615 | keep | 0 | Apr | 2023 | 0.0092731 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-21 05:11 | 2023-04-21 09:11 | 629 | 4:00 | P | DESGANCHE | 1 X 30 EN RISER Y 1 X 65 EN C/L DESGANCHE | B23042100013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2023-04-21 | 150960 | keep | 0 | Apr | 2023 | 0.10282 | 0.00042841 | Sustained | FALSE | FALSE | Not_TMED_Event | 629
BAYAMON | 2023-04-21 05:20 | 2023-04-21 17:57 | 14 | 12:37 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO Y SE ENERGIZO T-83 Y T-82 | B23042100014 | New_Event | UG Cable Fault | Include | Include | Equipment | 757 | 2023-04-21 | 10598 | keep | 0 | Apr | 2023 | 0.0072182 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-04-21 05:28 | 2023-04-21 11:55 | 90 | 6:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | M23042100005 | New_Event | Primary Wire Break | Include | Include | Equipment | 387 | 2023-04-21 | 34830 | keep | 0 | Apr | 2023 | 0.023723 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2023-04-21 05:38 | 2023-04-21 08:15 | 122 | 2:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23042100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-04-21 | 19154 | keep | 0 | Apr | 2023 | 0.013046 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
CANOVANAS | 2023-04-21 06:04 | 2023-04-21 10:20 | 70 | 4:16 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R23042100003 | New_Event | Animals | Include | Include | Wildlife | 256 | 2023-04-21 | 17920 | keep | 0 | Apr | 2023 | 0.012205 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-04-21 06:05 | 2023-04-21 07:50 | 10 | 1:45 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PARARRAYO AVERIADO | A23042100002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 105 | 2023-04-21 | 1050 | keep | 0 | Apr | 2023 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-04-21 06:19 | 2023-04-21 10:59 | 50 | 4:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA PARTIDA | R23042100006 | New_Event | Cutout Failure | Include | Include | Equipment | 280 | 2023-04-21 | 14000 | keep | 0 | Apr | 2023 | 0.0095353 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-21 06:26 | 2023-04-21 09:20 | 2985 | 2:54 | P | CONDUCTOR ARRIADO O CRUZADO | CG-230421-01 DISPARO DE INTELIRRUPTER 2603-08D SE SECCIONALIZO SE CONTINUA PATRULLANDO | C23042100007 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 174 | 2023-04-21 | 519390 | keep | 0 | Apr | 2023 | 0.35375 | 0.0020331 | Sustained | FALSE | FALSE | Not_TMED_Event | 2985
GUAYAMA | 2023-04-21 06:39 | 2023-04-21 09:20 | 6 | 2:41 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE | P23042100009 | New_Event | Animals | Include | Include | Wildlife | 161 | 2023-04-21 | 966 | keep | 0 | Apr | 2023 | 0.00065794 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-21 06:41 | 2023-04-21 06:42 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23042100022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-21 | 2126 | keep | 0 | Apr | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-04-21 07:01 | 2023-04-21 07:37 | 1 | 0:36 | P | ANIMAL | 1 X 6 EN BANCO DE TRANSFORMADORES CRUCE POR AVE | C23042100039 | New_Event | Animals | Include | Include | Wildlife | 36 | 2023-04-21 | 36 | keep | 0 | Apr | 2023 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-21 07:02 | 2023-04-21 11:19 | 293 | 4:17 | S | CONDUCTOR ROTO O ABIERTO | 100% EN SERVICIO SE REPARO NEUTRAL PARTIDO DE 1903-02 MEDIANTE SF BY-230421-01. SE REMPLAZO 2 FUSIBLES EN LA ALTA 125SLOW SPEED SE LIMPIO BASE DE ESTOS. SE NORMALIZO CARGAS | S23042100014 | New_Event | Primary Wire Break | Include | Include | Equipment | 257 | 2023-04-21 | 75301 | keep | 0 | Apr | 2023 | 0.051287 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2023-04-21 07:02 | 2023-04-21 12:39 | 315 | 5:37 | S | CONDUCTOR ROTO O ABIERTO | 100% EN SERVICIO SE REPARO NEUTRAL PARTIDO DE 1903-02 MEDIANTE SF BY-230421-01. SE REMPLAZO 2 FUSIBLES EN LA ALTA 125SLOW SPEED SE LIMPIO BASE DE ESTOS. SE NORMALIZO CARGAS | S23042100014 | New_Event | Primary Wire Break | Include | Include | Equipment | 337 | 2023-04-21 | 106155 | keep | 0 | Apr | 2023 | 0.072302 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BAYAMON | 2023-04-21 07:02 | 2023-04-21 12:39 | 216 | 5:37 | S | CONDUCTOR ROTO O ABIERTO | 100% EN SERVICIO SE REPARO NEUTRAL PARTIDO DE 1903-02 MEDIANTE SF BY-230421-01. SE REMPLAZO 2 FUSIBLES EN LA ALTA 125SLOW SPEED SE LIMPIO BASE DE ESTOS. SE NORMALIZO CARGAS. 1903-03 LLEVA 70% DEL 1924-04 | S23042100014 | New_Event | Primary Wire Break | Include | Include | Equipment | 337 | 2023-04-21 | 72792 | keep | 0 | Apr | 2023 | 0.049578 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BAYAMON | 2023-04-21 07:02 | 2023-04-21 11:19 | 1310 | 4:17 | S | CONDUCTOR ROTO O ABIERTO | 100% EN SERVICIO SE REPARO NEUTRAL PARTIDO DE 1903-02 MEDIANTE SF BY-230421-01. SE REMPLAZO 2 FUSIBLES EN LA ALTA 125SLOW SPEED SE LIMPIO BASE DE ESTOS. SE NORMALIZO CARGAS | S23042100014 | New_Event | Primary Wire Break | Include | Include | Equipment | 257 | 2023-04-21 | 336670 | keep | 0 | Apr | 2023 | 0.2293 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2023-04-21 07:02 | 2023-04-21 12:39 | 31 | 5:37 | P | ALIMENTADOR AMARRADO | 100% EN SERVICIO SE REPARO NEUTRAL PARTIDO DE 1903-02 MEDIANTE SF BY-230421-01. SE REMPLAZO 2 FUSIBLES EN LA ALTA 125SLOW SPEED SE LIMPIO BASE DE ESTOS. SE NORMALIZO CARGAS. 1903-03 LLEVA 70% DEL 1924-04 | S23042100014 | New_Event | Feeder Load Transferred | Include | Include | Other | 337 | 2023-04-21 | 10447 | keep | 0 | Apr | 2023 | 0.0071154 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-04-21 07:16 | 2023-04-21 14:02 | 1 | 6:46 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23042100018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 406 | 2023-04-21 | 406 | keep | 0 | Apr | 2023 | 0.00027652 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-21 07:40 | 2023-04-21 14:00 | 28 | 6:20 | P | DESGANCHE | DESGANCHE 1 X 40 EN C/L | S23042100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2023-04-21 | 10640 | keep | 0 | Apr | 2023 | 0.0072469 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2023-04-21 07:44 | 2023-04-21 09:00 | 12 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23042100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2023-04-21 | 912 | keep | 0 | Apr | 2023 | 0.00062116 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-04-21 07:48 | 2023-04-21 12:45 | 6 | 4:57 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA PARTIDA | M23042100022 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 297 | 2023-04-21 | 1782 | keep | 0 | Apr | 2023 | 0.0012137 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-21 07:52 | 2023-04-21 10:25 | 12 | 2:33 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO CAJA | A23042100010 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-04-21 | 1836 | keep | 0 | Apr | 2023 | 0.0012505 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-04-21 08:03 | 2023-04-21 13:36 | 5 | 5:33 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE INSTALO AISLADOR POSTE PARTIDO EN LA PERILLA | C23042100079 | New_Event | Primary Pole Failure | Include | Include | Equipment | 333 | 2023-04-21 | 1665 | keep | 0 | Apr | 2023 | 0.001134 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-21 08:05 | 2023-04-21 10:22 | 19 | 2:17 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23042100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-04-21 | 2603 | keep | 0 | Apr | 2023 | 0.0017729 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
MAYAGÃœEZ | 2023-04-21 08:13 | 2023-04-21 13:25 | 4 | 5:12 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23042100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-04-21 | 1248 | keep | 0 | Apr | 2023 | 0.00085001 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-04-21 08:20 | 2023-04-21 13:50 | 60 | 5:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M23042100036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 330 | 2023-04-21 | 19800 | keep | 0 | Apr | 2023 | 0.013486 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-21 08:21 | 2023-04-21 09:30 | 1 | 1:09 | P | DESGANCHE | SE CERRO PUENTE DE LINEA A CAJA Y DESGANCHE | S23042100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2023-04-21 | 69 | keep | 0 | Apr | 2023 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-21 08:25 | 2023-04-21 10:15 | 100 | 1:50 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C23042100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-04-21 | 11000 | keep | 0 | Apr | 2023 | 0.007492 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-04-21 08:40 | 2023-04-21 15:10 | 40 | 6:30 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE DESCONECTO PARARRAYOS CRUZADO | M23042100043 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 390 | 2023-04-21 | 15600 | keep | 0 | Apr | 2023 | 0.010625 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-21 08:42 | 2023-04-21 10:32 | 29 | 1:50 | P | ANIMAL | 1 X 50 EN C/L AVE | B23042100026 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-04-21 | 3190 | keep | 0 | Apr | 2023 | 0.0021727 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-04-21 09:01 | 2023-04-21 19:36 | 30 | 10:35 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23042100041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 635 | 2023-04-21 | 19050 | keep | 0 | Apr | 2023 | 0.012975 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-21 09:01 | 2023-04-21 18:10 | 12 | 9:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR QUEMADO DE 50KVA X 50KVA | B23042100028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 549 | 2023-04-21 | 6588 | keep | 0 | Apr | 2023 | 0.0044871 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-21 09:01 | 2023-04-21 18:12 | 6 | 9:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA X 50KVA | B23042100028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 551 | 2023-04-21 | 3306 | keep | 0 | Apr | 2023 | 0.0022517 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-21 09:02 | 2023-04-21 12:32 | 6 | 3:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042100030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 210 | 2023-04-21 | 1260 | keep | 0 | Apr | 2023 | 0.00085818 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-04-21 09:08 | 2023-04-21 10:56 | 100 | 1:48 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA CAMION IMPACTO LINEA DE TELEFONO Y MOVIO POSTE PRIMARIO | C23042100115 | New_Event | Damage From Public | Include | Include | Public | 108 | 2023-04-21 | 10800 | keep | 0 | Apr | 2023 | 0.0073558 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-04-21 09:10 | 2023-04-21 09:11 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23042100053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-21 | 312 | keep | 0 | Apr | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
HUMACAO | 2023-04-21 09:20 | 2023-04-21 10:09 | 2827 | 0:49 | P | CONDUCTOR ARRIADO O CRUZADO | CG-230421-01 DISPARO DE INTELIRRUPTER 2603-08D SE SECCIONALIZO SE CONTINUA PATRULLANDO | C23042100007 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 49 | 2023-04-21 | 138523 | keep | 0 | Apr | 2023 | 0.094347 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-21 09:20 | 2023-04-21 09:56 | 1352 | 0:36 | T | DESGANCHE | SE RETIRO ENREDADERA EN LINEA PRIMARIA | M23042100055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-04-21 | 48672 | keep | 0 | Apr | 2023 | 0.03315 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-04-21 09:20 | 2023-04-21 09:56 | 871 | 0:36 | T | ALIMENTADOR AMARRADO | SU CARGA POR 6012-05 | M23042100055 | New_Event | Feeder Load Transferred | Include | Include | Other | 36 | 2023-04-21 | 31356 | keep | 0 | Apr | 2023 | 0.021356 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
AGUADILLA | 2023-04-21 09:25 | 2023-04-21 15:10 | 10 | 5:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | M23042100056 | New_Event | Primary Wire Break | Include | Include | Equipment | 345 | 2023-04-21 | 3450 | keep | 0 | Apr | 2023 | 0.0023498 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-21 09:29 | 2023-04-21 13:20 | 293 | 3:51 | P | ANIMAL | 2 X 65, 2X 50 Y 2 X 30 EN CORTES DE LINEA CRUCE POR CHANGO | C23042100129 | New_Event | Animals | Include | Include | Wildlife | 231 | 2023-04-21 | 67683 | keep | 0 | Apr | 2023 | 0.046099 | 0.00019956 | Sustained | FALSE | FALSE | Not_TMED_Event | 293
BAYAMON | 2023-04-21 09:46 | 2023-04-21 12:26 | 1 | 2:40 | P | ANIMAL | 1 X 25 EN RISER AVE | B23042100036 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-04-21 | 160 | keep | 0 | Apr | 2023 | 0.00010898 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-21 09:50 | 2023-04-21 14:50 | 1 | 5:00 | P | ANIMAL | 1 X 10 EN MONTURA DE XMR CRUCE X AVE | C23042100137 | New_Event | Animals | Include | Include | Wildlife | 300 | 2023-04-21 | 300 | keep | 0 | Apr | 2023 | 0.00020433 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-21 09:57 | 2023-04-21 16:00 | 40 | 6:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23042100024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 363 | 2023-04-21 | 14520 | keep | 0 | Apr | 2023 | 0.0098895 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-04-21 10:09 | 2023-04-21 10:20 | 2985 | 0:11 | P | CONDUCTOR ARRIADO O CRUZADO | CG-230421-01 DISPARO DE INTELIRRUPTER 2603-08D SE SECCIONALIZO ENTRO UN 50% EN SERVICIO | C23042100007 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 11 | 2023-04-21 | 32835 | keep | 0 | Apr | 2023 | 0.022364 | 0.0020331 | Sustained | FALSE | FALSE | Not_TMED_Event | 2985
VEGA BAJA | 2023-04-21 10:16 | 2023-04-21 12:20 | 2 | 2:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA CORROSION EL FUSIBLE | A23042100026 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2023-04-21 | 248 | keep | 0 | Apr | 2023 | 0.00016891 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-21 10:19 | 2023-04-21 16:38 | 1 | 6:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA | S23042100064 | New_Event | Primary Wire Break | Include | Include | Equipment | 379 | 2023-04-21 | 379 | keep | 0 | Apr | 2023 | 0.00025814 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-21 10:20 | 2023-04-21 10:30 | 1492 | 0:10 | P | CONDUCTOR ARRIADO O CRUZADO | CG-230421-01 DISPARO DE INTELIRRUPTER 2603-08D SE SECCIONALIZO ENTRO UN 25% | C23042100007 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 10 | 2023-04-21 | 14920 | keep | 0 | Apr | 2023 | 0.010162 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-21 10:25 | 2023-04-21 12:40 | 10 | 2:15 | P | OTRAS CAUSAS | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA INSTALAR MAQUINA DE FRECUENCIA Y RASTREAR LINEA SOTERRADA. SE MARCO LINEA SOTERRADA PARA EXCAVACION DE CONTRATISTA | C23042100145 | New_Event | Other Causes | Include | Include | Other | 135 | 2023-04-21 | 1350 | keep | 0 | Apr | 2023 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-21 10:25 | 2023-04-21 12:23 | 50 | 1:58 | P | ANIMAL | 1 X 50 EN PROVISIONAL AVE | B23042100039 | New_Event | Animals | Include | Include | Wildlife | 118 | 2023-04-21 | 5900 | keep | 0 | Apr | 2023 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-21 10:27 | 2023-04-21 13:50 | 200 | 3:23 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA GRUPO PRIVADO DESGANCHE CRUZO LINEAS PRIMARIAS | M23042100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-04-21 | 40600 | keep | 0 | Apr | 2023 | 0.027652 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-04-21 10:29 | 2023-04-21 12:08 | 15 | 1:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA | A23042100016 | New_Event | Primary Wire Break | Include | Include | Equipment | 99 | 2023-04-21 | 1485 | keep | 0 | Apr | 2023 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-21 10:30 | 2023-04-21 10:57 | 746 | 0:27 | P | CONDUCTOR ARRIADO O CRUZADO | CG-230421-01 DISPARO DE INTELIRRUPTER 2603-08D SE ENCONTRO LINEA ARRIADA A LA CUAL SE LE COLOCO TIGUERO 100% EN SERVICIO | C23042100007 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 27 | 2023-04-21 | 20142 | keep | 0 | Apr | 2023 | 0.013719 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-21 10:40 | 2023-04-21 16:50 | 2 | 6:10 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M23042100090 | New_Event | Animals | Include | Include | Wildlife | 370 | 2023-04-21 | 740 | keep | 0 | Apr | 2023 | 0.00050401 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-04-21 10:50 | 2023-04-21 11:35 | 12 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REPARAR SECUNDARIA | R23042100040 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-21 | 540 | keep | 0 | Apr | 2023 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-04-21 10:51 | 2023-04-21 13:46 | 60 | 2:55 | P | ANIMAL | 1 X 80 SMU-20 EN SU-6 AVE | P23042100058 | New_Event | Animals | Include | Include | Wildlife | 175 | 2023-04-21 | 10500 | keep | 0 | Apr | 2023 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-21 10:55 | 2023-04-21 11:43 | 227 | 0:48 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRALLO | S23042100061 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 48 | 2023-04-21 | 10896 | keep | 0 | Apr | 2023 | 0.0074212 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
SAN JUAN | 2023-04-21 11:01 | 2023-04-22 12:59 | 1 | 25:58 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 50 EN RISER Y 1 X 40 EN BOVEDA CONTAMINACION EN TRANSCLOSURE | S23042100071 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1558 | 2023-04-21 | 1558 | keep | 0 | Apr | 2023 | 0.0010611 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-21 11:07 | 2023-04-21 13:30 | 25 | 2:23 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C23042100158 | New_Event | Animals | Include | Include | Wildlife | 143 | 2023-04-21 | 3575 | keep | 0 | Apr | 2023 | 0.0024349 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-21 12:03 | 2023-04-21 12:04 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23042100165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-21 | 2203 | keep | 0 | Apr | 2023 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
SAN JUAN | 2023-04-21 12:18 | 2023-04-21 12:21 | 1058 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 20% POR EL 1424-08 | S23042100082 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-21 | 3174 | keep | 0 | Apr | 2023 | 0.0021618 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-04-21 12:18 | 2023-04-21 12:21 | 2 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 80% DE SU CARGA POR EL 1424-08 | S23042100082 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-21 | 6 | keep | 0 | Apr | 2023 | 4.0866e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-21 12:18 | 2023-04-21 12:21 | 1295 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1424-08 | S23042100082 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-21 | 3885 | keep | 0 | Apr | 2023 | 0.0026461 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-04-21 12:18 | 2023-04-21 12:21 | 9 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 80% DEL 1348-06 20% DEL 1336-08 100% EL 1401-10 | S23042100082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-21 | 27 | keep | 0 | Apr | 2023 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-04-21 12:23 | 2023-04-21 16:20 | 20 | 3:57 | P | DESGANCHE | 1 X 50 EN C/L | R23042100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2023-04-21 | 4740 | keep | 0 | Apr | 2023 | 0.0032284 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-21 12:35 | 2023-04-21 14:23 | 6 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA BAJANTE SECUNDARIO | A23042100004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2023-04-21 | 648 | keep | 0 | Apr | 2023 | 0.00044135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-21 12:36 | 2023-04-21 14:36 | 8679 | 2:00 | P | ANIMAL | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES, SE RETIRO IGUANA Y SE CERRO N/O 85% DE SU CARGA POR EL 1206-03 SJ-230421-01 | S23042100084 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-04-21 | 1041480 | keep | 0 | Apr | 2023 | 0.70935 | 0.0059112 | Sustained | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-04-21 12:36 | 2023-04-21 13:48 | 3471 | 1:12 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR LLEVA 85% DE LA CARGA DEL 1204-05 SE ABRIO N/O Y SE CERRO POR SCADA SJ-230421-01 16% DE SU CARGA POR EL 1620-02 | S23042100084 | New_Event | Feeder Load Transferred | Include | Include | Other | 72 | 2023-04-21 | 249912 | keep | 0 | Apr | 2023 | 0.17021 | 0.0023641 | Sustained | FALSE | FALSE | Not_TMED_Event | 3471
BARRANQUITAS | 2023-04-21 12:36 | 2023-04-21 13:56 | 183 | 1:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO CORTE DE LINEA PARA RETEZAR LINEA PRIMARIA INSTALANDO RIGIDO | C23042100171 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 80 | 2023-04-21 | 14640 | keep | 0 | Apr | 2023 | 0.0099712 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
SAN JUAN | 2023-04-21 12:52 | 2023-04-22 11:05 | 33 | 22:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE ELIMINO SEC. VACANTE | S23042100127 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1333 | 2023-04-21 | 43989 | keep | 0 | Apr | 2023 | 0.029961 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BARRANQUITAS | 2023-04-21 12:55 | 2023-04-21 18:00 | 2 | 5:05 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO XMR PARA LEVANTAR NEUTRAL PRIMARIO SIN CARGA | C23042100179 | New_Event | Primary Wire Break | Include | Include | Equipment | 305 | 2023-04-21 | 610 | keep | 0 | Apr | 2023 | 0.00041547 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-04-21 13:00 | 2023-04-21 13:01 | 6285 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23042100131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-21 | 6285 | keep | 0 | Apr | 2023 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
SAN JUAN | 2023-04-21 13:05 | 2023-04-21 13:07 | 660 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2304210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-21 | 1320 | keep | 0 | Apr | 2023 | 0.00089905 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
AGUADILLA | 2023-04-21 13:08 | 2023-04-21 14:35 | 1617 | 1:27 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE ABRIO CORTE DE LINEAS PARA SECCIONALIZAR LINEAS PRIMARIAS ROTAS Y SE CERRO EL INTERRUPTOR | M23042100132 | New_Event | Primary Wire Break | Include | Include | Equipment | 87 | 2023-04-21 | 140679 | keep | 0 | Apr | 2023 | 0.095816 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
BAYAMON | 2023-04-21 13:11 | 2023-04-21 15:24 | 300 | 2:13 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23042100175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-04-21 | 39900 | keep | 0 | Apr | 2023 | 0.027176 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2023-04-21 13:21 | 2023-04-21 14:30 | 1 | 1:09 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA ARRIADA TIENE TIGUERO INSTALADO | C23042100186 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 69 | 2023-04-21 | 69 | keep | 0 | Apr | 2023 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-21 13:49 | 2023-04-21 19:56 | 150 | 6:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | A23042100051 | New_Event | Primary Wire Break | Include | Include | Equipment | 367 | 2023-04-21 | 55050 | keep | 0 | Apr | 2023 | 0.037494 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2023-04-21 13:57 | 2023-04-21 14:22 | 5 | 0:25 | P | CAUSAS EXTERNAS | 1 X 15 EN XMR PERSONA ROBANDO CABLES CRUZO LINEAS | P23042100087 | New_Event | Damage From Public | Include | Include | Public | 25 | 2023-04-21 | 125 | keep | 0 | Apr | 2023 | 8.5137e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-04-21 14:00 | 2023-04-21 20:39 | 200 | 6:39 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE PUENTE PARA SECIONALIZAR AVERIA DE POSTE PARTIDO 3 X 140 EN CONVERTIDOR | A23042100055 | New_Event | Primary Pole Failure | Include | Include | Equipment | 399 | 2023-04-21 | 79800 | keep | 0 | Apr | 2023 | 0.054351 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-04-21 14:10 | 2023-04-21 17:08 | 125 | 2:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR RAMA SOBRE LINEA | A23042100060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-04-21 | 22250 | keep | 0 | Apr | 2023 | 0.015154 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-04-21 14:25 | 2023-04-21 16:09 | 10 | 1:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042100064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 104 | 2023-04-21 | 1040 | keep | 0 | Apr | 2023 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-21 14:31 | 2023-04-21 17:41 | 45 | 3:10 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23042100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-04-21 | 8550 | keep | 0 | Apr | 2023 | 0.0058234 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-04-21 14:35 | 2023-04-21 16:20 | 275 | 1:45 | P | CONDUCTOR ROTO O ABIERTO | 3 X 65 Y 1 X 100 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR LINEAS PRIMARIAS ROTAS | M23042100162 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 105 | 2023-04-21 | 28875 | keep | 0 | Apr | 2023 | 0.019667 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-21 14:45 | 2023-04-21 16:38 | 1105 | 1:53 | T | DESGANCHE | SE ABRE CORTE DE LINEA FID-33775518 EN CARR 146 KM 5.3 BO LIMON UTUADO PARA SECCIONALIZAR Y SE CIERRA INTERRUPTOR | A23042100082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-04-21 | 124865 | keep | 0 | Apr | 2023 | 0.085045 | 0.00075261 | Sustained | FALSE | FALSE | Not_TMED_Event | 1105
CANOVANAS | 2023-04-21 14:59 | 2023-04-21 16:51 | 1 | 1:52 | P | NO SE REPORTO CAUSA | 2 X 20 EN RISER | R23042100062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2023-04-21 | 112 | keep | 0 | Apr | 2023 | 7.6283e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-21 15:00 | 2023-04-21 22:05 | 1 | 7:05 | P | NO SE REPORTO CAUSA | 1X25 EN BANCO DE XMRS | S23042100284 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 425 | 2023-04-21 | 425 | keep | 0 | Apr | 2023 | 0.00028947 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-21 15:00 | 2023-04-22 09:08 | 2 | 18:08 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | R23042100064 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1088 | 2023-04-21 | 2176 | keep | 0 | Apr | 2023 | 0.0014821 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-04-21 15:00 | 2023-04-21 15:55 | 100 | 0:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | M23042100166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-04-21 | 5500 | keep | 0 | Apr | 2023 | 0.003746 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-21 15:28 | 2023-04-21 16:42 | 40 | 1:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23042100093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-04-21 | 2960 | keep | 0 | Apr | 2023 | 0.002016 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-04-21 15:31 | 2023-04-21 17:15 | 4 | 1:44 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23042100196 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-04-21 | 416 | keep | 0 | Apr | 2023 | 0.00028334 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-04-21 15:39 | 2023-04-21 18:39 | 20 | 3:00 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR NO CAUSA | P23042100111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 180 | 2023-04-21 | 3600 | keep | 0 | Apr | 2023 | 0.0024519 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-21 16:00 | 2023-04-21 18:04 | 173 | 2:04 | P | ANIMAL | 1 X 50 EN C/L Y 1 X 30 EN C/L CRUCE POR AVE | C23042100203 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-04-21 | 21452 | keep | 0 | Apr | 2023 | 0.014611 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
AGUADILLA | 2023-04-21 16:06 | 2023-04-21 16:07 | 390 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | M23042100177 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-21 | 390 | keep | 0 | Apr | 2023 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2023-04-21 16:07 | 2023-04-21 17:35 | 80 | 1:28 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23042100179 | 1st_after_momentary | Animals | Include | Include | Wildlife | 88 | 2023-04-21 | 7040 | keep | 0 | Apr | 2023 | 0.0047949 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-04-21 16:20 | 2023-04-22 12:28 | 2 | 20:08 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REMPLAZO CRUCETA | M23042100180 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 1208 | 2023-04-21 | 2416 | keep | 0 | Apr | 2023 | 0.0016455 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-04-21 16:35 | 2023-04-21 17:38 | 5668 | 1:03 | T | DESGANCHE | SE REALIZO DESGANCHE DE PISO | R23042100069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-04-21 | 357084 | keep | 0 | Apr | 2023 | 0.24321 | 0.0038604 | Sustained | FALSE | FALSE | Not_TMED_Event | 5668
HUMACAO | 2023-04-21 16:37 | 2023-04-21 18:50 | 9 | 2:13 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23042100208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2023-04-21 | 1197 | keep | 0 | Apr | 2023 | 0.00081527 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2023-04-21 16:38 | 2023-04-21 19:18 | 276 | 2:40 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | A23042100149 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-04-21 | 44160 | keep | 0 | Apr | 2023 | 0.030077 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-21 16:55 | 2023-04-21 18:25 | 100 | 1:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA POR LLUVIAS | A23042100132 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 90 | 2023-04-21 | 9000 | keep | 0 | Apr | 2023 | 0.0061299 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-21 16:56 | 2023-04-21 18:42 | 15 | 1:46 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA POR RAMA SOBRE LINEA | A23042100134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-04-21 | 1590 | keep | 0 | Apr | 2023 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-04-21 17:05 | 2023-04-22 09:30 | 10 | 16:25 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR BAJANTE PRIMARIO DE CAJA CRUZADO | A23042100144 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 985 | 2023-04-21 | 9850 | keep | 0 | Apr | 2023 | 0.0067088 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-21 17:08 | 2023-04-21 21:00 | 100 | 3:52 | P | ANIMAL | 1 X 40 Y 1 X 25 EN CORTE DE LINEA POR AVE | A23042100145 | New_Event | Animals | Include | Include | Wildlife | 232 | 2023-04-21 | 23200 | keep | 0 | Apr | 2023 | 0.015801 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-04-21 17:18 | 2023-04-21 17:19 | 2041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042100079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-21 | 2041 | keep | 0 | Apr | 2023 | 0.0013901 | 0.0013901 | Momentary | FALSE | FALSE | Not_TMED_Event | 2041
CANOVANAS | 2023-04-21 17:36 | 2023-04-22 08:17 | 2 | 14:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R23042100080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 881 | 2023-04-21 | 1762 | keep | 0 | Apr | 2023 | 0.0012001 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-04-21 17:38 | 2023-04-21 19:40 | 1 | 2:02 | P | NO SE REPORTO CAUSA | 2 SMU 20 EN VS | S23042100310 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2023-04-21 | 122 | keep | 0 | Apr | 2023 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-21 17:53 | 2023-04-22 10:45 | 10 | 16:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | A23042100167 | New_Event | Cutout Failure | Include | Include | Equipment | 1012 | 2023-04-21 | 10120 | keep | 0 | Apr | 2023 | 0.0068927 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-21 19:18 | 2023-04-22 10:13 | 8 | 14:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23042100323 | New_Event | Secondary Wire Break | Include | Include | Equipment | 895 | 2023-04-21 | 7160 | keep | 0 | Apr | 2023 | 0.0048766 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-21 19:43 | 2023-04-21 19:44 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042100218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-21 | 918 | keep | 0 | Apr | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-04-21 19:44 | 2023-04-21 21:08 | 136 | 1:24 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN C/L Y SE DESPEGO TENSOR ARRIADO | C23042100212 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 84 | 2023-04-21 | 11424 | keep | 0 | Apr | 2023 | 0.0077808 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
YAUCO | 2023-04-21 19:57 | 2023-04-21 22:32 | 3973 | 2:35 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR NO RECERRO Y NO OPERO POR CONTROL SE SECCIONALIZO Y SE REMPLAZO CORTE DE LINEA | P23042100146 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2023-04-21 | 615815 | keep | 0 | Apr | 2023 | 0.41943 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
CANOVANAS | 2023-04-21 20:09 | 2023-04-21 22:39 | 70 | 2:30 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | R23042100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-04-21 | 10500 | keep | 0 | Apr | 2023 | 0.0071515 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2023-04-21 20:39 | 2023-04-22 19:00 | 30 | 22:21 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO Y SE REPARO LINEAS PRIMARIAS ROTAS | A23042100055 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1341 | 2023-04-21 | 40230 | keep | 0 | Apr | 2023 | 0.0274 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-21 20:43 | 2023-04-21 22:45 | 203 | 2:02 | P | DESGANCHE | 1X100 EN C/L | B23042100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-04-21 | 24766 | keep | 0 | Apr | 2023 | 0.016868 | 0.00013826 | Sustained | FALSE | FALSE | Not_TMED_Event | 203
VEGA BAJA | 2023-04-21 21:20 | 2023-04-22 07:22 | 40 | 10:02 | P | DESGANCHE | 1 X 40 EN C/L Y DEGSNACHE | B23042100105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 602 | 2023-04-21 | 24080 | keep | 0 | Apr | 2023 | 0.016401 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-21 21:41 | 2023-04-22 08:30 | 4 | 10:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO POSTAFUSIBLE Y 1 X 15 EN C/L | B23042100108 | New_Event | Cutout Failure | Include | Include | Equipment | 649 | 2023-04-21 | 2596 | keep | 0 | Apr | 2023 | 0.0017681 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-21 22:22 | 2023-04-22 12:59 | 1 | 14:37 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN C/L Y 1 X 80 EN OTRO C/L SE REMPLAZO PARRARAYO | S23042100333 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 877 | 2023-04-21 | 877 | keep | 0 | Apr | 2023 | 0.00059732 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-04-21 22:30 | 2023-04-22 09:40 | 80 | 11:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DE CAJA PRIMARIA EN CORTE DE LINEA | P23042100181 | New_Event | Cutout Failure | Include | Include | Equipment | 670 | 2023-04-21 | 53600 | keep | 0 | Apr | 2023 | 0.036507 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2023-04-21 22:32 | 2023-04-22 01:15 | 103 | 2:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO Y SE REMPLAZO CORTE DE LINEA | P23042100146 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 163 | 2023-04-21 | 16789 | keep | 0 | Apr | 2023 | 0.011435 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-21 23:55 | 2023-04-22 14:47 | 6 | 14:52 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE REQUIERE DESGANCHE | A23042100199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 892 | 2023-04-21 | 5352 | keep | 0 | Apr | 2023 | 0.0036452 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-22 00:13 | 2023-04-22 00:14 | 2107 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14700 | A23042200001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 2107 | keep | 0 | Apr | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-04-22 00:13 | 2023-04-22 00:14 | 308 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14700 | A23042200001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 308 | keep | 0 | Apr | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
VEGA BAJA | 2023-04-22 00:13 | 2023-04-22 00:14 | 2697 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14700 | A23042200001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 2697 | keep | 0 | Apr | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-04-22 00:13 | 2023-04-22 00:14 | 67 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14700 | A23042200001 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 67 | keep | 0 | Apr | 2023 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2023-04-22 00:15 | 2023-04-22 14:35 | 11 | 14:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA AVERIADO | B23042200003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 860 | 2023-04-22 | 9460 | keep | 0 | Apr | 2023 | 0.0064432 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2023-04-22 01:15 | 2023-04-22 10:23 | 1 | 9:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | EN EVENTO DE DISPARO DE INTERRUPTOR SE HABIA DEJADO MACHETES ABIERTOS PARA PATRULLAR TRAMO DE DIA SE ENCONTRO TODO NORMAL Y SE CERRO MACHETES | P23042200001 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 548 | 2023-04-22 | 548 | keep | 0 | Apr | 2023 | 0.00037324 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-22 02:27 | 2023-04-22 08:31 | 16 | 6:04 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23042200001 | New_Event | Animals | Include | Include | Wildlife | 364 | 2023-04-22 | 5824 | keep | 0 | Apr | 2023 | 0.0039667 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-04-22 03:45 | 2023-04-22 10:15 | 75 | 6:30 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23042200004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 390 | 2023-04-22 | 29250 | keep | 0 | Apr | 2023 | 0.019922 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-04-22 04:14 | 2023-04-22 08:57 | 60 | 4:43 | P | ANIMAL | 1 X 30 Y 1 X 40 EN C/LS CRUCE X AVE | C23042200003 | New_Event | Animals | Include | Include | Wildlife | 283 | 2023-04-22 | 16980 | keep | 0 | Apr | 2023 | 0.011565 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-22 04:37 | 2023-04-22 07:17 | 180 | 2:40 | P | DESGANCHE | 1 X 80 EN CONVERTIDOR Y DESGANCHE | B23042200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-04-22 | 28800 | keep | 0 | Apr | 2023 | 0.019616 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
ARECIBO | 2023-04-22 05:14 | 2023-04-22 05:15 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23042200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 199 | keep | 0 | Apr | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
CANOVANAS | 2023-04-22 05:59 | 2023-04-22 06:00 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 931 CLIENTES DEL 2402-02 | R23042200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-22 05:59 | 2023-04-22 06:00 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 931 CLIENTES POR EL 2302-03 | R23042200004 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-22 | 931 | keep | 0 | Apr | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
CANOVANAS | 2023-04-22 06:03 | 2023-04-22 06:04 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23042200006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
AGUADILLA | 2023-04-22 06:16 | 2023-04-22 08:45 | 25 | 2:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042200015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 149 | 2023-04-22 | 3725 | keep | 0 | Apr | 2023 | 0.0025371 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-22 06:26 | 2023-04-22 14:42 | 35 | 8:16 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | B23042200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 496 | 2023-04-22 | 17360 | keep | 0 | Apr | 2023 | 0.011824 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-04-22 06:36 | 2023-04-22 10:25 | 43 | 3:49 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE DE PENCA | R23042200008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-04-22 | 9847 | keep | 0 | Apr | 2023 | 0.0067067 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2023-04-22 06:39 | 2023-04-22 16:13 | 40 | 9:34 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | R23042200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 574 | 2023-04-22 | 22960 | keep | 0 | Apr | 2023 | 0.015638 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-22 06:45 | 2023-04-22 12:19 | 10 | 5:34 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23042200005 | New_Event | Animals | Include | Include | Wildlife | 334 | 2023-04-22 | 3340 | keep | 0 | Apr | 2023 | 0.0022749 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-22 07:23 | 2023-04-22 09:13 | 114 | 1:50 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23042200010 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-04-22 | 12540 | keep | 0 | Apr | 2023 | 0.0085409 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
MAYAGÃœEZ | 2023-04-22 07:23 | 2023-04-22 09:45 | 60 | 2:22 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23042200020 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-04-22 | 8520 | keep | 0 | Apr | 2023 | 0.0058029 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-04-22 07:28 | 2023-04-22 17:15 | 90 | 9:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | P23042200007 | New_Event | Cutout Failure | Include | Include | Equipment | 587 | 2023-04-22 | 52830 | keep | 0 | Apr | 2023 | 0.035982 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2023-04-22 07:28 | 2023-04-22 12:22 | 50 | 4:54 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23042200022 | New_Event | Animals | Include | Include | Wildlife | 294 | 2023-04-22 | 14700 | keep | 0 | Apr | 2023 | 0.010012 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-22 07:30 | 2023-04-22 07:31 | 3076 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | B23042200041 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-04-22 | 3076 | keep | 0 | Apr | 2023 | 0.002095 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
VEGA BAJA | 2023-04-22 07:31 | 2023-04-22 11:32 | 600 | 4:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 Y 1 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA QUEMADA | B23042200042 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 241 | 2023-04-22 | 144600 | keep | 0 | Apr | 2023 | 0.098486 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
VEGA BAJA | 2023-04-22 07:40 | 2023-04-22 12:20 | 85 | 4:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042200015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 280 | 2023-04-22 | 23800 | keep | 0 | Apr | 2023 | 0.01621 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2023-04-22 07:42 | 2023-04-22 09:21 | 70 | 1:39 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23042200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-04-22 | 6930 | keep | 0 | Apr | 2023 | 0.00472 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-04-22 07:48 | 2023-04-22 09:14 | 80 | 1:26 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | M23042200024 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-04-22 | 6880 | keep | 0 | Apr | 2023 | 0.0046859 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-04-22 07:50 | 2023-04-22 11:50 | 1 | 4:00 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA CRUCE POR AVE | R23042200011 | New_Event | Animals | Include | Include | Wildlife | 240 | 2023-04-22 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-22 07:57 | 2023-04-22 07:58 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 931 CLIENTES DEL 2402-02 | R23042200013 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-22 07:57 | 2023-04-22 07:58 | 931 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 931 CLIENTES POR EL 2302-03 | R23042200013 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-22 | 931 | keep | 0 | Apr | 2023 | 0.0006341 | 0.0006341 | Momentary | FALSE | FALSE | Not_TMED_Event | 931
SAN JUAN | 2023-04-22 08:32 | 2023-04-22 10:53 | 500 | 2:21 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S23042200006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-04-22 | 70500 | keep | 0 | Apr | 2023 | 0.048017 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-04-22 08:47 | 2023-04-22 14:38 | 12 | 5:51 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN C/L Y 1X 50 EN C/L. SE REEMPLAZO AISLADOR QUEMADO | R23042200015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 351 | 2023-04-22 | 4212 | keep | 0 | Apr | 2023 | 0.0028688 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-04-22 08:54 | 2023-04-22 12:00 | 11 | 3:06 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | R23042200016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 186 | 2023-04-22 | 2046 | keep | 0 | Apr | 2023 | 0.0013935 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-04-22 09:02 | 2023-04-22 17:28 | 4 | 8:26 | P | TRANSFORMADOR AVERIADO | SE PASAN CLIENTES A OTRO TRANSFORMADOR POR TRANSFORMADOR AVERIADO | M23042200038 | New_Event | Service Transformer Failure | Include | Include | Equipment | 506 | 2023-04-22 | 2024 | keep | 0 | Apr | 2023 | 0.0013785 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-04-22 09:10 | 2023-04-22 10:29 | 95 | 1:19 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23042200015 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-04-22 | 7505 | keep | 0 | Apr | 2023 | 0.0051116 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
CANOVANAS | 2023-04-22 09:41 | 2023-04-22 09:42 | 1615 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO Y SE CERRO POR SCADA | S2304220000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-04-22 | 1615 | keep | 0 | Apr | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-04-22 09:42 | 2023-04-22 14:56 | 574 | 5:14 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | R23042200037 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 314 | 2023-04-22 | 180236 | keep | 0 | Apr | 2023 | 0.12276 | 0.00039095 | Sustained | FALSE | FALSE | Not_TMED_Event | 574
SAN JUAN | 2023-04-22 09:44 | 2023-04-22 14:53 | 3709 | 5:09 | S | LINEA DE TRANSMISION 38KV | EN DISPARO DE LINEA 7100 CON PUENTE ABIERTO SUB. SE FUE A LOCKOUT. NO SE REPORTO CONDICION ADICIONAL Y SE NORMALIZO SUB. MEDIANTE SJ-230422-01 | S23042200040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 309 | 2023-04-22 | 1146081 | keep | 0 | Apr | 2023 | 0.78059 | 0.0025262 | Sustained | FALSE | FALSE | Not_TMED_Event | 3709
SAN JUAN | 2023-04-22 09:44 | 2023-04-22 14:53 | 24 | 5:09 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 7100 CON PUENTE ABIERTO SUB. SE FUE A LOCKOUT. NO SE REPORTO CONDICION. PUENTE ABIERTO ENTRE VIADUCTO Y ACB 7131A Y OTRO EN EL ACB 7131B, PARARRAYOS AVERIADO EN TOMA SOTERRADA HACIA WALMART. | S23042200040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 309 | 2023-04-22 | 7416 | keep | 0 | Apr | 2023 | 0.005051 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-04-22 09:44 | 2023-04-22 14:50 | 1 | 5:06 | S | LINEA DE TRANSMISION 38KV | EN DISPARO DE LINEA 7100 CON PUENTE ABIERTO SUB. SE FUE A LOCKOUT. NO SE REPORTO CONDICION ADICIONAL Y SE NORMALIZO SUB. MEDIANTE SJ-230422-01 | S23042200040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 306 | 2023-04-22 | 306 | keep | 0 | Apr | 2023 | 0.00020842 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-22 09:44 | 2023-04-22 14:53 | 79 | 5:09 | P | LINEA DE TRANSMISION 38KV | EN DISPARO DE LINEA 7100 CON PUENTE ABIERTO SUB. SE FUE A LOCKOUT. NO SE REPORTO CONDICION ADICIONAL Y SE NORMALIZO SUB. MEDIANTE SJ-230422-01. BKR 1114-02 SPARE LLEVA 70% DEL 1115-04 | S23042200040 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 309 | 2023-04-22 | 24411 | keep | 0 | Apr | 2023 | 0.016626 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
SAN JUAN | 2023-04-22 09:44 | 2023-04-22 09:45 | 620 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION PUENTE ABIERTO ENTRE VIADUCTO Y ACB 7131A Y OTRO EN EL ACB 7131B, PARARRAYOS AVERIADO EN TOMA SOTERRADA HACIA WALMART. | S23042200044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 620 | keep | 0 | Apr | 2023 | 0.00042228 | 0.00042228 | Momentary | FALSE | FALSE | Not_TMED_Event | 620
SAN JUAN | 2023-04-22 09:44 | 2023-04-22 09:45 | 451 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA DE TRANSMISION | S23042200044 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 451 | keep | 0 | Apr | 2023 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2023-04-22 09:45 | 2023-04-22 11:26 | 1 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRAS EN PEDESTAL | B23042200057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2023-04-22 | 101 | keep | 0 | Apr | 2023 | 6.8791e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-22 09:46 | 2023-04-22 17:41 | 17 | 7:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO LINEA SECUNDARIA CRUZADA CON CASCO DEL XMR | S23042200036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 475 | 2023-04-22 | 8075 | keep | 0 | Apr | 2023 | 0.0054998 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-04-22 09:48 | 2023-04-22 11:18 | 150 | 1:30 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23042200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-04-22 | 13500 | keep | 0 | Apr | 2023 | 0.0091948 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-04-22 10:13 | 2023-04-22 13:15 | 60 | 3:02 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA CRUZADA | M23042200050 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 182 | 2023-04-22 | 10920 | keep | 0 | Apr | 2023 | 0.0074376 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-04-22 10:15 | 2023-04-22 10:40 | 272 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE C/L PARA CERRAR PUENTE PRIMARIO ABIERTO | P23042200015 | New_Event | Primary Wire Break | Include | Include | Equipment | 25 | 2023-04-22 | 6800 | keep | 0 | Apr | 2023 | 0.0046314 | 0.00018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 272
SAN JUAN | 2023-04-22 10:17 | 2023-04-22 12:41 | 161 | 2:24 | P | DESGANCHE | 1 X 100 EN C/L RAMA | S23042200062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-04-22 | 23184 | keep | 0 | Apr | 2023 | 0.015791 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
VEGA BAJA | 2023-04-22 10:18 | 2023-04-22 15:00 | 8 | 4:42 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR SE REMOVIO RAMAS DE SOBRE EL TRANSFORMADOR | A23042200041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-04-22 | 2256 | keep | 0 | Apr | 2023 | 0.0015366 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-04-22 10:22 | 2023-04-22 14:50 | 1 | 4:28 | P | OTRAS CAUSAS | 1 X 30 EN CORTE DE LINEA SE DESCONECTO EQUIPO DE MEDICION CON PROBLEMAS | A23042200043 | New_Event | Other Causes | Include | Include | Other | 268 | 2023-04-22 | 268 | keep | 0 | Apr | 2023 | 0.00018253 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-22 10:36 | 2023-04-22 13:40 | 8 | 3:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR REPARO SECUNDARIA | C23042200025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 184 | 2023-04-22 | 1472 | keep | 0 | Apr | 2023 | 0.0010026 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-22 10:37 | 2023-04-22 14:44 | 12 | 4:07 | P | DESGANCHE | 1 X 50 Y 1 X 30 EN CORTES DE LINEA SE REALIZO DESGANCHE PRIMARIO | S23042200084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-04-22 | 2964 | keep | 0 | Apr | 2023 | 0.0020188 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-04-22 10:43 | 2023-04-22 12:40 | 75 | 1:57 | P | DESGANCHE | 3 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS REQUIERE DESGANCHE | A23042200045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-04-22 | 8775 | keep | 0 | Apr | 2023 | 0.0059766 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-04-22 10:47 | 2023-04-22 10:48 | 4702 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL | B2304220000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-22 | 4702 | keep | 0 | Apr | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-04-22 10:48 | 2023-04-22 18:27 | 215 | 7:39 | P | MAL TIEMPO/RAYOS | 3 X 100 EN C/L SE REPORTA MAL TIEMPO | B23042200086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 459 | 2023-04-22 | 98685 | keep | 0 | Apr | 2023 | 0.067214 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-04-22 10:50 | 2023-04-22 10:51 | 4398 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23042200090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 4398 | keep | 0 | Apr | 2023 | 0.0029955 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
SAN JUAN | 2023-04-22 11:00 | 2023-04-22 15:43 | 209 | 4:43 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23042200095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-04-22 | 59147 | keep | 0 | Apr | 2023 | 0.040285 | 0.00014235 | Sustained | FALSE | FALSE | Not_TMED_Event | 209
BARRANQUITAS | 2023-04-22 11:00 | 2023-04-22 14:33 | 8 | 3:33 | P | DESGANCHE | ABRIO C/L PARA DESGANCHAR Y RETEZAR CONDUCTORES | C23042200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 213 | 2023-04-22 | 1704 | keep | 0 | Apr | 2023 | 0.0011606 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-04-22 11:15 | 2023-04-22 12:35 | 1 | 1:20 | P | NO SE REPORTO CAUSA | SE REMPLAZO 1 X 20 EN BANCO DE TRANSFORMADOR | B23042200071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-04-22 | 80 | keep | 0 | Apr | 2023 | 5.4488e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-22 11:51 | 2023-04-22 11:52 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y CERRO POR SCADA | B2304220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 4431 | keep | 0 | Apr | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
ARECIBO | 2023-04-22 12:02 | 2023-04-22 15:05 | 30 | 3:03 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE SEPARO LINEAS CRUZADAS | A23042200057 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 183 | 2023-04-22 | 5490 | keep | 0 | Apr | 2023 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-22 12:14 | 2023-04-22 14:20 | 136 | 2:06 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | R23042200062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-04-22 | 17136 | keep | 0 | Apr | 2023 | 0.011671 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
BAYAMON | 2023-04-22 12:19 | 2023-04-23 10:40 | 172 | 22:21 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23042200073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1341 | 2023-04-22 | 230652 | keep | 0 | Apr | 2023 | 0.1571 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
BARRANQUITAS | 2023-04-22 12:20 | 2023-04-22 12:23 | 3296 | 0:03 | T | DESGANCHE | DISPARO NO RECIERRA CERRADO X CONTROL | C23042200034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-04-22 | 9888 | keep | 0 | Apr | 2023 | 0.0067347 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-04-22 12:23 | 2023-04-22 14:21 | 7 | 1:58 | P | DESGANCHE | DESGANCHO Y REMPLAZO CAJA QUEMADA NO FUNDIO | C23042200041 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-04-22 | 826 | keep | 0 | Apr | 2023 | 0.00056258 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-04-22 12:28 | 2023-04-22 13:36 | 1617 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 DISCO PARTIDO Y OHGW ARRIADO ENTRE LAS MARIAS Y MARICAO. | M23042200122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-04-22 | 109956 | keep | 0 | Apr | 2023 | 0.074891 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
AGUADILLA | 2023-04-22 12:28 | 2023-04-22 13:36 | 1017 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 DISCO PARTIDO Y OHGW ARRIADO ENTRE LAS MARIAS Y MARICAO. | M23042200122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-04-22 | 69156 | keep | 0 | Apr | 2023 | 0.047102 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2023-04-22 12:28 | 2023-04-22 13:36 | 828 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 DISCO PARTIDO Y OHGW ARRIADO ENTRE LAS MARIAS Y MARICAO. | M23042200122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-04-22 | 56304 | keep | 0 | Apr | 2023 | 0.038348 | 0.00056395 | Sustained | FALSE | FALSE | Not_TMED_Event | 828
MAYAGÃœEZ | 2023-04-22 12:28 | 2023-04-22 14:34 | 863 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 EN SERVICIO DISCO PARTIDO Y OHGW ARRIADO ENTRE LAS MARIAS Y MARICAO. | M23042200124 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-04-22 | 108738 | keep | 0 | Apr | 2023 | 0.074061 | 0.00058779 | Sustained | FALSE | FALSE | Not_TMED_Event | 863
MAYAGÃœEZ | 2023-04-22 12:28 | 2023-04-22 14:34 | 309 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 EN SERVICIO DISCO PARTIDO Y OHGW ARRIADO ENTRE LAS MARIAS Y MARICAO. | M23042200124 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-04-22 | 38934 | keep | 0 | Apr | 2023 | 0.026518 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
MAYAGÃœEZ | 2023-04-22 12:28 | 2023-04-22 14:34 | 176 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 EN SERVICIO DISCO PARTIDO Y OHGW ARRIADO ENTRE LAS MARIAS Y MARICAO. | M23042200124 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-04-22 | 22176 | keep | 0 | Apr | 2023 | 0.015104 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
MAYAGÃœEZ | 2023-04-22 12:28 | 2023-04-22 14:34 | 974 | 2:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2000 EN SERVICIO DISCO PARTIDO Y OHGW ARRIADO ENTRE LAS MARIAS Y MARICAO. | M23042200125 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 126 | 2023-04-22 | 122724 | keep | 0 | Apr | 2023 | 0.083587 | 0.00066339 | Sustained | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2023-04-22 12:31 | 2023-04-22 13:45 | 12 | 1:14 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE SECUNDARIO | P23042200040 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 74 | 2023-04-22 | 888 | keep | 0 | Apr | 2023 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-04-22 12:47 | 2023-04-22 12:48 | 3941 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 3941 | keep | 0 | Apr | 2023 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
CANOVANAS | 2023-04-22 12:47 | 2023-04-22 14:04 | 75 | 1:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23042200067 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 77 | 2023-04-22 | 5775 | keep | 0 | Apr | 2023 | 0.0039333 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-04-22 13:00 | 2023-04-22 14:14 | 5 | 1:14 | P | ANIMAL | 1 X 8 EN XMR CRUCE X AVE | C23042200037 | New_Event | Animals | Include | Include | Wildlife | 74 | 2023-04-22 | 370 | keep | 0 | Apr | 2023 | 0.00025201 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-04-22 13:00 | 2023-04-22 15:04 | 7 | 2:04 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | ABRIO XMR PARA REPARAR SECUNDARIA EN PEDESTAL | C23042200038 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 124 | 2023-04-22 | 868 | keep | 0 | Apr | 2023 | 0.00059119 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-04-22 13:08 | 2023-04-22 16:00 | 80 | 2:52 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE VERIFICADO EN BITACORA Y OMS APARECE 9901-01 | C23042200042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-04-22 | 13760 | keep | 0 | Apr | 2023 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-04-22 13:19 | 2023-04-22 13:20 | 1394 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 16500 DE FAJARDO TC A DOS MARINA LLEVA LA CARGA DEL 2005-07 Y 2005-08 | R23042200069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 1394 | keep | 0 | Apr | 2023 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2023-04-22 13:19 | 2023-04-22 13:20 | 412 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 16500 DE FAJARDO TC A DOS MARINA | R23042200069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 412 | keep | 0 | Apr | 2023 | 0.00028061 | 0.00028061 | Momentary | FALSE | FALSE | Not_TMED_Event | 412
FAJARDO | 2023-04-22 13:19 | 2023-04-22 13:20 | 424 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 16500 DE FAJARDO TC A DOS MARINA CARGA POR EL 2003-01 | R23042200069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 424 | keep | 0 | Apr | 2023 | 0.00028878 | 0.00028878 | Momentary | FALSE | FALSE | Not_TMED_Event | 424
FAJARDO | 2023-04-22 13:19 | 2023-04-22 13:20 | 240 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 16500 DE FAJARDO TC A DOS MARINA CARGA POR EL 2003-01 | R23042200069 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-22 | 240 | keep | 0 | Apr | 2023 | 0.00016346 | 0.00016346 | Momentary | FALSE | FALSE | Not_TMED_Event | 240
AGUADILLA | 2023-04-22 13:36 | 2023-04-22 14:15 | 10 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO MONTURA DE TRANSFORMADOR Y SE REEMPLAZO TRAMO DE LINEA SECUNDARIA EN MALAS CONDICIONES | M23042200117 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-04-22 | 390 | keep | 0 | Apr | 2023 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-22 13:37 | 2023-04-22 15:42 | 100 | 2:05 | P | MAL TIEMPO/RAYOS | 3 X 50 EN C/L RAYOS | C23042200046 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 125 | 2023-04-22 | 12500 | keep | 0 | Apr | 2023 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-22 13:39 | 2023-04-22 14:38 | 8 | 0:59 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23042200048 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 59 | 2023-04-22 | 472 | keep | 0 | Apr | 2023 | 0.00032148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-04-22 13:47 | 2023-04-22 21:29 | 40 | 7:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 25 EN CONVERTIDOR SE RETIRO BAMBUS DE LAS LINEAS | A23042200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 462 | 2023-04-22 | 18480 | keep | 0 | Apr | 2023 | 0.012587 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-04-22 13:50 | 2023-04-22 16:09 | 20 | 2:19 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CL LINEA PRIMARIA ARRIADA | P23042200065 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 139 | 2023-04-22 | 2780 | keep | 0 | Apr | 2023 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-22 14:08 | 2023-04-23 14:55 | 80 | 24:47 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE Y SE SUBIO CONDUCTOR | B23042200093 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1487 | 2023-04-22 | 118960 | keep | 0 | Apr | 2023 | 0.081023 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-04-22 14:11 | 2023-04-22 19:10 | 80 | 4:59 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE SEPARO LINEA CRIZADA | A23042200066 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 299 | 2023-04-22 | 23920 | keep | 0 | Apr | 2023 | 0.016292 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-22 14:25 | 2023-04-23 08:29 | 20 | 18:04 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23042200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1084 | 2023-04-22 | 21680 | keep | 0 | Apr | 2023 | 0.014766 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-22 14:37 | 2023-04-22 17:08 | 44 | 2:31 | P | TRANSFORMADOR AVERIADO | 2 X 40 EN RISER SE REMPLAZO PISTOLA EN T-181 Y BUSHING | S23042200152 | New_Event | Service Transformer Failure | Include | Include | Equipment | 151 | 2023-04-22 | 6644 | keep | 0 | Apr | 2023 | 0.0045252 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2023-04-22 14:40 | 2023-04-22 16:00 | 40 | 1:20 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN C/L SE REMPLAZO PARARAYO | B23042200100 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 80 | 2023-04-22 | 3200 | keep | 0 | Apr | 2023 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-04-22 14:47 | 2023-04-22 14:48 | 4607 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23042200077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 4607 | keep | 0 | Apr | 2023 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
BAYAMON | 2023-04-22 14:49 | 2023-04-22 16:53 | 50 | 2:04 | P | MAL TIEMPO/RAYOS | 1 X 25 EN C/L 1 X 15 EN XMR MAL TIEMPO | B23042200103 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 124 | 2023-04-22 | 6200 | keep | 0 | Apr | 2023 | 0.0042228 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-22 14:49 | 2023-04-22 16:19 | 76 | 1:30 | P | MAL TIEMPO/RAYOS | 1 X 80 EN C/L MAL TIEMPO | B23042200105 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 90 | 2023-04-22 | 6840 | keep | 0 | Apr | 2023 | 0.0046587 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
VEGA BAJA | 2023-04-22 14:52 | 2023-04-23 12:35 | 184 | 21:43 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE Y CERRARON CORTE DE LINEA MONOFASICO | B23042200107 | New_Event | Primary Wire Break | Include | Include | Equipment | 1303 | 2023-04-22 | 239752 | keep | 0 | Apr | 2023 | 0.16329 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
BARRANQUITAS | 2023-04-22 15:02 | 2023-04-22 16:57 | 30 | 1:55 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23042200058 | New_Event | Animals | Include | Include | Wildlife | 115 | 2023-04-22 | 3450 | keep | 0 | Apr | 2023 | 0.0023498 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-22 15:11 | 2023-04-22 17:00 | 6 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | A23042200081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-04-22 | 654 | keep | 0 | Apr | 2023 | 0.00044544 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-04-22 15:14 | 2023-04-22 15:15 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23042200114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BARRANQUITAS | 2023-04-22 15:25 | 2023-04-22 15:27 | 3296 | 0:02 | T | DESGANCHE | DISPARO NO RECIERRA CERRADO X CONTROL | C23042200063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-22 | 6592 | keep | 0 | Apr | 2023 | 0.0044898 | 0.0022449 | Momentary | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-04-22 15:27 | 2023-04-22 18:53 | 62 | 3:26 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHO Y REMPLAZO CAJA QUEMADA | C23042200064 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-04-22 | 12772 | keep | 0 | Apr | 2023 | 0.008699 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
PONCE | 2023-04-22 15:34 | 2023-04-22 15:35 | 752 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23042200074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 752 | keep | 0 | Apr | 2023 | 0.00051218 | 0.00051218 | Momentary | FALSE | FALSE | Not_TMED_Event | 752
BAYAMON | 2023-04-22 15:35 | 2023-04-22 15:36 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 75% 1718-03 | B2304220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-04-22 15:35 | 2023-04-22 15:36 | 1950 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 1713-04 Y LLEVA 75% 1718-03 | B2304220000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-22 | 1950 | keep | 0 | Apr | 2023 | 0.0013281 | 0.0013281 | Momentary | FALSE | FALSE | Not_TMED_Event | 1950
BAYAMON | 2023-04-22 15:57 | 2023-04-22 15:58 | 1514 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR CONTROL | B23042200132 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-22 | 1514 | keep | 0 | Apr | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
HUMACAO | 2023-04-22 15:57 | 2023-04-22 15:58 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2023-04-22 15:58 | 2023-04-22 19:56 | 300 | 3:58 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | B23042200127 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 238 | 2023-04-22 | 71400 | keep | 0 | Apr | 2023 | 0.04863 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2023-04-22 15:58 | 2023-04-22 21:58 | 100 | 6:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA POR AISLADOR | M23042200185 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 360 | 2023-04-22 | 36000 | keep | 0 | Apr | 2023 | 0.024519 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-22 16:03 | 2023-04-22 20:07 | 80 | 4:04 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23042200187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 244 | 2023-04-22 | 19520 | keep | 0 | Apr | 2023 | 0.013295 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-22 16:04 | 2023-04-22 16:05 | 3798 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23042200132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 3798 | keep | 0 | Apr | 2023 | 0.0025868 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
SAN JUAN | 2023-04-22 16:13 | 2023-04-22 16:15 | 661 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DEL BKR 1620-02 LLEVA 16% 1206-03 SE CERRO POR CONTROL | S23042200168 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-22 | 1322 | keep | 0 | Apr | 2023 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-04-22 16:13 | 2023-04-22 16:15 | 3718 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL BKR LLEVA 16% 1206-03 SE CERRO POR CONTROL | S23042200168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-22 | 7436 | keep | 0 | Apr | 2023 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2023-04-22 16:16 | 2023-04-22 16:17 | 2107 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR AVE | A23042200085 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-22 | 2107 | keep | 0 | Apr | 2023 | 0.0014351 | 0.0014351 | Momentary | FALSE | FALSE | Not_TMED_Event | 2107
VEGA BAJA | 2023-04-22 16:17 | 2023-04-22 19:47 | 40 | 3:30 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23042200088 | 1st_after_momentary | Animals | Include | Include | Wildlife | 210 | 2023-04-22 | 8400 | keep | 0 | Apr | 2023 | 0.0057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-04-22 16:22 | 2023-04-22 20:36 | 15 | 4:14 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5KVA POR LA MISMA CAPACIDAD | A23042200086 | New_Event | Service Transformer Failure | Include | Include | Equipment | 254 | 2023-04-22 | 3810 | keep | 0 | Apr | 2023 | 0.002595 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-22 16:29 | 2023-04-22 16:30 | 551 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042200076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 551 | keep | 0 | Apr | 2023 | 0.00037528 | 0.00037528 | Momentary | FALSE | FALSE | Not_TMED_Event | 551
VEGA BAJA | 2023-04-22 16:31 | 2023-04-22 17:52 | 24 | 1:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO PORTAFUSIBLE | B23042200136 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2023-04-22 | 1944 | keep | 0 | Apr | 2023 | 0.001324 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
MAYAGÃœEZ | 2023-04-22 16:42 | 2023-04-22 17:13 | 30 | 0:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR RAMA SOBRE LINEA | M23042200192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-04-22 | 930 | keep | 0 | Apr | 2023 | 0.00063342 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-04-22 16:46 | 2023-04-22 16:50 | 1 | 0:04 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CAJA EN TRANSFORMADOR PARA RETIRAR CARGA Y FIJAR BAJANTE DE LINEA PRIMARIA A CAJA EN MONTURA | P23042200130 | New_Event | Primary Wire Break | Include | Include | Equipment | 4 | 2023-04-22 | 4 | keep | 0 | Apr | 2023 | 2.7244e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-22 16:49 | 2023-04-22 21:28 | 50 | 4:39 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CL SE REPARO LINEA PRIMARIA | P23042200086 | New_Event | Primary Wire Break | Include | Include | Equipment | 279 | 2023-04-22 | 13950 | keep | 0 | Apr | 2023 | 0.0095013 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-04-22 17:00 | 2023-04-22 18:31 | 20 | 1:31 | P | DESGANCHE | 2 X 50 EN CL DESGANCHE BAMBU | P23042200093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-04-22 | 1820 | keep | 0 | Apr | 2023 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-22 17:03 | 2023-04-22 18:00 | 1 | 0:57 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | C23042200082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2023-04-22 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-22 17:11 | 2023-04-22 17:12 | 1356 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1117-11 Y SE CERRO POR SCADA | S23042200174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 1356 | keep | 0 | Apr | 2023 | 0.00092357 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
ARECIBO | 2023-04-22 17:24 | 2023-04-23 15:40 | 25 | 22:16 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA LINEA PRIMARIA ROTA SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR | A23042200097 | New_Event | Primary Wire Break | Include | Include | Equipment | 1336 | 2023-04-22 | 33400 | keep | 0 | Apr | 2023 | 0.022749 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-22 17:29 | 2023-04-22 22:10 | 150 | 4:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA Y SE REMPLAZO CAJA EN MALAS CONDICIONES | M23042200212 | New_Event | Primary Wire Break | Include | Include | Equipment | 281 | 2023-04-22 | 42150 | keep | 0 | Apr | 2023 | 0.028708 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-04-22 18:22 | 2023-04-22 19:34 | 1 | 1:12 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23042200096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-04-22 | 72 | keep | 0 | Apr | 2023 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-22 18:34 | 2023-04-22 18:38 | 308 | 0:04 | T | DESCONECTIVO DEFECTUOSO | SJ-230422-03 SE ABRIO BKR 1105-02 QUE LLEVA 1133-04 POR MACHETE N/O EN FUEGO CALLE LOIZA SANTURCE SE SECCIONALIZO SE REMPLAZO MACHETE QUEMADO DE N/O Y LUEGO SE NORMALIZO | S23042200184 | New_Event | Switch Failure | Include | Include | Equipment | 4 | 2023-04-22 | 1232 | keep | 0 | Apr | 2023 | 0.00083911 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
SAN JUAN | 2023-04-22 18:34 | 2023-04-22 19:22 | 333 | 0:48 | T | ALIMENTADOR AMARRADO | SJ-230422-03 SE ABRIO BKR 1105-02 QUE LLEVA 1133-04 POR MACHETE N/O EN FUEGO CALLE LOIZA SANTURCE SE SECCIONALIZO SE REMPLAZO MACHETE QUEMADO DE N/O Y LUEGO SE NORMALIZO | S23042200184 | New_Event | Feeder Load Transferred | Include | Include | Other | 48 | 2023-04-22 | 15984 | keep | 0 | Apr | 2023 | 0.010887 | 0.0002268 | Sustained | FALSE | FALSE | Not_TMED_Event | 333
BARRANQUITAS | 2023-04-22 18:38 | 2023-04-23 09:08 | 32 | 14:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS | C23042200100 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 870 | 2023-04-22 | 27840 | keep | 0 | Apr | 2023 | 0.018962 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CANOVANAS | 2023-04-22 18:45 | 2023-04-22 20:15 | 148 | 1:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN RISER | R23042200094 | New_Event | Cutout Failure | Include | Include | Equipment | 90 | 2023-04-22 | 13320 | keep | 0 | Apr | 2023 | 0.0090722 | 0.0001008 | Sustained | FALSE | FALSE | Not_TMED_Event | 148
BAYAMON | 2023-04-22 18:56 | 2023-04-23 13:00 | 40 | 18:04 | P | MAL TIEMPO/LLUVIA O VIENTO | SE REPUSO 1 X 65 EN C/L MAL TIEMPO | B23042200187 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1084 | 2023-04-22 | 43360 | keep | 0 | Apr | 2023 | 0.029532 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-22 19:09 | 2023-04-23 00:42 | 1588 | 5:33 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 LLEVA LA CARGA DEL 1711-01 Y 1711-03 SE SECCIONALIZO PARA CERRAR PUENTE PRIMARIO ABIERTO EN TRONCAL 1716-03 80% EN SERVICIO 1711-01 Y 1711-03 100% EN SERVICIO | B23042200199 | New_Event | Feeder Load Transferred | Include | Include | Other | 333 | 2023-04-22 | 528804 | keep | 0 | Apr | 2023 | 0.36017 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-22 19:09 | 2023-04-23 00:42 | 13 | 5:33 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1716-03 LLEVA LA CARGA DEL 1711-01 Y 1711-03 SE SECCIONALIZO PARA CERRAR PUENTE PRIMARIO ABIERTO EN TRONCAL 1716-03 80% EN SERVICIO 1711-01 Y 1711-03 100% EN SERVICIO | B23042200199 | New_Event | Feeder Load Transferred | Include | Include | Other | 333 | 2023-04-22 | 4329 | keep | 0 | Apr | 2023 | 0.0029485 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-22 19:09 | 2023-04-23 00:42 | 1812 | 5:33 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1716-03 LLEVA LA CARGA DEL 1711-01 Y 1711-03 BY-230422-01 SE SECCIONALIZO PARA CERRAR PUENTE PRIMARIO ABIERTO EN TRONCAL 1716-03 80% EN SERVICIO 1711-01 Y 1711-03 100% EN SERVICIO | B23042200199 | New_Event | Switch Failure | Include | Include | Equipment | 333 | 2023-04-22 | 603396 | keep | 0 | Apr | 2023 | 0.41097 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
PONCE | 2023-04-22 19:09 | 2023-04-23 09:36 | 10 | 14:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P23042200111 | New_Event | Cutout Failure | Include | Include | Equipment | 867 | 2023-04-22 | 8670 | keep | 0 | Apr | 2023 | 0.0059051 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-04-22 19:10 | 2023-04-22 19:13 | 3420 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C2304220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-22 | 10260 | keep | 0 | Apr | 2023 | 0.006988 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
PONCE | 2023-04-22 19:12 | 2023-04-23 11:37 | 40 | 16:25 | P | CABLE SOTERRADO AVERIADO | SE REALIZO EN SU-4 TRANSPOSICION DE FASES AVERIA SOTERRADA DEL RISER AL SU-4 | P23042200115 | New_Event | UG Cable Fault | Include | Include | Equipment | 985 | 2023-04-22 | 39400 | keep | 0 | Apr | 2023 | 0.026835 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-22 19:14 | 2023-04-22 19:15 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23042200202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 5252 | keep | 0 | Apr | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
PONCE | 2023-04-22 19:14 | 2023-04-22 23:30 | 64 | 4:16 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23042200116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-04-22 | 16384 | keep | 0 | Apr | 2023 | 0.011159 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
VEGA BAJA | 2023-04-22 19:30 | 2023-04-22 19:32 | 215 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23042200229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-22 | 430 | keep | 0 | Apr | 2023 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-04-22 19:31 | 2023-04-22 19:37 | 837 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO 1401-07 QUE LLEVA 1401-06 Y SE CERRO POR SCADA | S23042200195 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-04-22 | 5022 | keep | 0 | Apr | 2023 | 0.0034205 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-04-22 19:31 | 2023-04-22 19:37 | 908 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO 1401-07 QUE LLEVA 1401-06 Y SE CERRO POR SCADA | S23042200195 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-22 | 5448 | keep | 0 | Apr | 2023 | 0.0037106 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-04-22 19:32 | 2023-04-22 19:33 | 60 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1420-02 QUE LLEVA 10% DEL 1420-03 CERRADO POR SCADA | S23042200197 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 60 | keep | 0 | Apr | 2023 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-22 19:32 | 2023-04-22 19:33 | 54 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE 1420-02 QUE LLEVA 10% DEL 1420-03 CERRADO POR SCADA | S23042200197 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-22 | 54 | keep | 0 | Apr | 2023 | 3.6779e-05 | 3.6779e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 54
VEGA BAJA | 2023-04-22 19:32 | 2023-04-22 20:48 | 153 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23042200239 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 76 | 2023-04-22 | 11628 | keep | 0 | Apr | 2023 | 0.0079198 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
BAYAMON | 2023-04-22 19:35 | 2023-04-22 19:36 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2304220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-04-22 19:41 | 2023-04-23 12:00 | 73 | 16:19 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO MACHETES MEDIANTE SF SJ-230423-03 | S23042200206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 979 | 2023-04-22 | 71467 | keep | 0 | Apr | 2023 | 0.048676 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
CAGUAS | 2023-04-22 19:54 | 2023-04-23 09:12 | 10 | 13:18 | P | ERROR HUMANO | SE CERRO FUSIBLE QUE SE DEJO ABIERTO POR ERROR POR EL PERSONAL DE CAMPO MIENTRAS SE TRABAJABA CON CONDICION DE DESGANCHE. | C23042200104 | New_Event | Human Error | Include | Include | Other | 798 | 2023-04-22 | 7980 | keep | 0 | Apr | 2023 | 0.0054351 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-22 20:23 | 2023-04-22 20:24 | 1320 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042200110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 1320 | keep | 0 | Apr | 2023 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
MAYAGÃœEZ | 2023-04-22 20:41 | 2023-04-23 11:33 | 40 | 14:52 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M23042200248 | New_Event | Vegetation Contact | Include | Include | Vegetation | 892 | 2023-04-22 | 35680 | keep | 0 | Apr | 2023 | 0.024301 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-22 20:46 | 2023-04-23 00:14 | 150 | 3:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L Y 1 X 65 EN C/L MAL TIEMPO LLUVIAS | C23042200125 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 208 | 2023-04-22 | 31200 | keep | 0 | Apr | 2023 | 0.02125 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-04-22 20:48 | 2023-04-22 22:52 | 12 | 2:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L Y 1 X 8 EN XMR SE ENDEREZO CAJA PRIMARIA | R23042200110 | New_Event | Cutout Failure | Include | Include | Equipment | 124 | 2023-04-22 | 1488 | keep | 0 | Apr | 2023 | 0.0010135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-04-22 20:53 | 2023-04-23 08:03 | 30 | 11:10 | P | ANIMAL | 2 X 100 EN C/L CRCUE X AVE | C23042200128 | New_Event | Animals | Include | Include | Wildlife | 670 | 2023-04-22 | 20100 | keep | 0 | Apr | 2023 | 0.01369 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-22 20:56 | 2023-04-22 22:24 | 2178 | 1:28 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE BKR SE REALIZARON OPERACIONES Y SE CERRO POR CONTROL 40% EN SERVICIO | C23042200132 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 88 | 2023-04-22 | 191664 | keep | 0 | Apr | 2023 | 0.13054 | 0.0014834 | Sustained | FALSE | FALSE | Not_TMED_Event | 2178
BARRANQUITAS | 2023-04-22 20:56 | 2023-04-23 11:03 | 25 | 14:07 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23042200129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 847 | 2023-04-22 | 21175 | keep | 0 | Apr | 2023 | 0.014422 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-04-22 20:58 | 2023-04-22 22:55 | 250 | 1:57 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA REQUIERE DESGANCHE | M23042200255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-04-22 | 29250 | keep | 0 | Apr | 2023 | 0.019922 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2023-04-22 21:23 | 2023-04-23 12:17 | 1 | 14:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23042200113 | New_Event | Cutout Failure | Include | Include | Equipment | 894 | 2023-04-22 | 894 | keep | 0 | Apr | 2023 | 0.0006089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-22 21:26 | 2023-04-22 21:27 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042200143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 1307 | keep | 0 | Apr | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
CAGUAS | 2023-04-22 21:29 | 2023-04-23 01:21 | 65 | 3:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | C23042200145 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 232 | 2023-04-22 | 15080 | keep | 0 | Apr | 2023 | 0.010271 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-04-22 21:44 | 2023-04-23 14:51 | 40 | 17:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO | B23042200333 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1027 | 2023-04-22 | 41080 | keep | 0 | Apr | 2023 | 0.027979 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-04-22 22:06 | 2023-04-23 08:30 | 300 | 10:24 | P | ANIMAL | 1 X 140 EN CL CRUCE DE FASE PRIMARIA POR AVE | P23042200141 | New_Event | Animals | Include | Include | Wildlife | 624 | 2023-04-22 | 187200 | keep | 0 | Apr | 2023 | 0.1275 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-04-22 22:20 | 2023-04-22 22:21 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2304220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-22 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
CAGUAS | 2023-04-22 22:24 | 2023-04-22 23:13 | 1307 | 0:49 | P | CONDUCTOR ARRIADO O CRUZADO | NO SE ENCONTRO AVERIA. SE TRANSFIRIO LA CARGA RESTANTE AL 3015-07. 100% EN SERVICIO | C23042200132 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 49 | 2023-04-22 | 64043 | keep | 0 | Apr | 2023 | 0.043619 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-23 00:14 | 2023-04-23 00:20 | 5063 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | P23042300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-23 | 30378 | keep | 0 | Apr | 2023 | 0.02069 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
BAYAMON | 2023-04-23 00:42 | 2023-04-23 11:49 | 362 | 11:07 | P | DESCONECTIVO DEFECTUOSO | SE HICIERON OPERACIONES CON BY-230422-01 SE REEMPLAZO MACHETE QUEMADO 100% EN SERVICIO ENTRO EL 20% QUE FALTABA | B23042200199 | Partial_restoration | Switch Failure | Include | Include | Equipment | 667 | 2023-04-23 | 241454 | keep | 0 | Apr | 2023 | 0.16445 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 00:44 | 2023-04-23 17:00 | 27 | 16:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23042300005 | New_Event | Cutout Failure | Include | Include | Equipment | 976 | 2023-04-23 | 26352 | keep | 0 | Apr | 2023 | 0.017948 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-04-23 01:07 | 2023-04-23 11:55 | 116 | 10:48 | P | DESGANCHE | 1 X 65 EN C/L | B23042300036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 648 | 2023-04-23 | 75168 | keep | 0 | Apr | 2023 | 0.051197 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
BARRANQUITAS | 2023-04-23 02:19 | 2023-04-23 12:05 | 20 | 9:46 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | C23042300016 | New_Event | Primary Wire Break | Include | Include | Equipment | 586 | 2023-04-23 | 11720 | keep | 0 | Apr | 2023 | 0.0079824 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-23 02:33 | 2023-04-23 07:34 | 1307 | 5:01 | P | CONDUCTOR ARRIADO O CRUZADO | DISPARO DE BKR 3015-07 LLEVA 60% DEL 3103-05 SE SECCIONALIZO SE CERRO POR CONTROL ENTRO 10% ADICIONAL | C23042300028 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 301 | 2023-04-23 | 393407 | keep | 0 | Apr | 2023 | 0.26795 | 0.00089019 | Sustained | FALSE | FALSE | Not_TMED_Event | 1307
MAYAGÃœEZ | 2023-04-23 02:33 | 2023-04-23 09:55 | 20 | 7:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23042300001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 442 | 2023-04-23 | 8840 | keep | 0 | Apr | 2023 | 0.0060209 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-23 02:50 | 2023-04-23 11:25 | 30 | 8:35 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CULEBRA CRUZO LINEAS | A23042300002 | New_Event | Animals | Include | Include | Wildlife | 515 | 2023-04-23 | 15450 | keep | 0 | Apr | 2023 | 0.010523 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-23 03:09 | 2023-04-23 03:11 | 60 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1420-02 LLEVA 10% DEL 1420-03 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23042300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-23 | 120 | keep | 0 | Apr | 2023 | 8.1731e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-23 03:09 | 2023-04-23 03:11 | 54 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1420-02 LLEVA 10% DEL 1420-03 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23042300008 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-23 | 108 | keep | 0 | Apr | 2023 | 7.3558e-05 | 3.6779e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 54
SAN JUAN | 2023-04-23 03:41 | 2023-04-23 05:43 | 83 | 2:02 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23042300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-04-23 | 10126 | keep | 0 | Apr | 2023 | 0.0068968 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
AGUADILLA | 2023-04-23 04:05 | 2023-04-23 11:05 | 20 | 7:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23042300004 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 420 | 2023-04-23 | 8400 | keep | 0 | Apr | 2023 | 0.0057212 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-23 04:12 | 2023-04-23 09:16 | 84 | 5:04 | P | DESGANCHE | 1 X 140 EN C/L | R23042300002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2023-04-23 | 25536 | keep | 0 | Apr | 2023 | 0.017392 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
CAGUAS | 2023-04-23 04:15 | 2023-04-23 04:16 | 845 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23042300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 845 | keep | 0 | Apr | 2023 | 0.00057553 | 0.00057553 | Momentary | FALSE | FALSE | Not_TMED_Event | 845
BAYAMON | 2023-04-23 05:05 | 2023-04-24 06:50 | 105 | 25:45 | P | ANIMAL | 1 X 65 EN CL CRUCE POR AVE | B23042300144 | New_Event | Animals | Include | Include | Wildlife | 1545 | 2023-04-23 | 162225 | keep | 0 | Apr | 2023 | 0.11049 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
BAYAMON | 2023-04-23 05:42 | 2023-04-23 05:43 | 1570 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23042300153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1570 | keep | 0 | Apr | 2023 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
HUMACAO | 2023-04-23 06:03 | 2023-04-23 08:35 | 20 | 2:32 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE | C23042300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-04-23 | 3040 | keep | 0 | Apr | 2023 | 0.0020705 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-23 06:28 | 2023-04-23 09:58 | 130 | 3:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | B23042300163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-04-23 | 27300 | keep | 0 | Apr | 2023 | 0.018594 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2023-04-23 06:37 | 2023-04-23 19:00 | 124 | 12:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | C23042300023 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 743 | 2023-04-23 | 92132 | keep | 0 | Apr | 2023 | 0.062751 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
CAGUAS | 2023-04-23 06:40 | 2023-04-23 16:42 | 150 | 10:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO | C23042300025 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 602 | 2023-04-23 | 90300 | keep | 0 | Apr | 2023 | 0.061503 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-23 06:42 | 2023-04-23 06:43 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1908-01 LLEVA 1908-04 Y 1908-05 | S2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 3 | keep | 0 | Apr | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-23 06:42 | 2023-04-23 06:43 | 58 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1908-01 LLEVA 1908-04 Y 1908-05 | S2304230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 58 | keep | 0 | Apr | 2023 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2023-04-23 06:42 | 2023-04-23 06:43 | 386 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1908-01 LLEVA 1908-04 Y 1908-05 | S2304230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 386 | keep | 0 | Apr | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
CANOVANAS | 2023-04-23 07:05 | 2023-04-23 07:06 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
CANOVANAS | 2023-04-23 07:05 | 2023-04-23 07:06 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
VEGA BAJA | 2023-04-23 07:14 | 2023-04-23 07:15 | 1494 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO SE CERRO POR SCADA | A23042300008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1494 | keep | 0 | Apr | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
SAN JUAN | 2023-04-23 07:15 | 2023-04-23 13:55 | 84 | 6:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S23042300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 400 | 2023-04-23 | 33600 | keep | 0 | Apr | 2023 | 0.022885 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
SAN JUAN | 2023-04-23 07:18 | 2023-04-23 21:41 | 30 | 14:23 | P | CABLE SOTERRADO AVERIADO | SE ABRIO RISER @ T-5 , TRAMO AVERIADO, SE CERRO LAZO EN T-13 TODO EN SERVICIO | S23042300012 | New_Event | UG Cable Fault | Include | Include | Equipment | 863 | 2023-04-23 | 25890 | keep | 0 | Apr | 2023 | 0.017634 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-23 07:21 | 2023-04-23 07:22 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23042300015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 4634 | keep | 0 | Apr | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
HUMACAO | 2023-04-23 07:24 | 2023-04-23 07:25 | 3701 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23042300037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 3701 | keep | 0 | Apr | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
CAGUAS | 2023-04-23 07:34 | 2023-04-23 08:03 | 1089 | 0:29 | P | CONDUCTOR ARRIADO O CRUZADO | SE REALIZO OPERACIONES 90% EN SERVICIO | C23042300028 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 29 | 2023-04-23 | 31581 | keep | 0 | Apr | 2023 | 0.02151 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 07:43 | 2023-04-23 07:44 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR LLEVA 75% 1718-03 | B2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-04-23 07:43 | 2023-04-23 07:44 | 1953 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1713-04 LLEVA 75% 1718-03 | B2304230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 1953 | keep | 0 | Apr | 2023 | 0.0013302 | 0.0013302 | Momentary | FALSE | FALSE | Not_TMED_Event | 1953
HUMACAO | 2023-04-23 07:45 | 2023-04-23 07:46 | 3896 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 3896 | keep | 0 | Apr | 2023 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2023-04-23 07:57 | 2023-04-23 09:46 | 159 | 1:49 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REEMPLAZO AISLADOR | C23042300044 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 109 | 2023-04-23 | 17331 | keep | 0 | Apr | 2023 | 0.011804 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
CAGUAS | 2023-04-23 08:03 | 2023-04-23 09:29 | 218 | 1:26 | P | CONDUCTOR ARRIADO O CRUZADO | SE REALIZO OPERACIONES Y AL PROBAR TRAMO DISPARO EL BKR | C23042300028 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 86 | 2023-04-23 | 18748 | keep | 0 | Apr | 2023 | 0.012769 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-23 08:09 | 2023-04-23 17:31 | 10 | 9:22 | P | DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE | C23042300049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 562 | 2023-04-23 | 5620 | keep | 0 | Apr | 2023 | 0.0038278 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-23 08:21 | 2023-04-23 08:22 | 2907 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23042300054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 2907 | keep | 0 | Apr | 2023 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | Not_TMED_Event | 2907
ARECIBO | 2023-04-23 08:27 | 2023-04-23 08:28 | 3431 | 0:01 | T | ANIMAL | RECIERRE DEL INTERRUPTOR AVE CRUZO LINEAS | A23042300015 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-23 | 3431 | keep | 0 | Apr | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
VEGA BAJA | 2023-04-23 08:27 | 2023-04-23 08:29 | 4702 | 0:02 | T | DESGANCHE | DISPARO DE BKR SE CERRO POR CONTROL | B23042300207 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-23 | 9404 | keep | 0 | Apr | 2023 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
SAN JUAN | 2023-04-23 08:28 | 2023-04-23 08:29 | 220 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1303-05 QUE LLEVA 98% 1303-04 CERRADO POR SCADA | S23042300044 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 220 | keep | 0 | Apr | 2023 | 0.00014984 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-04-23 08:28 | 2023-04-23 08:29 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1303-05 QUE LLEVA 98% 1303-04 CERRADO POR SCADA | S23042300044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 870 | keep | 0 | Apr | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
ARECIBO | 2023-04-23 08:28 | 2023-04-23 11:00 | 25 | 2:32 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23042300017 | 1st_after_momentary | Animals | Include | Include | Wildlife | 152 | 2023-04-23 | 3800 | keep | 0 | Apr | 2023 | 0.0025882 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-23 08:29 | 2023-04-23 15:53 | 142 | 7:24 | P | DESGANCHE | 1 X 100 EN C/L Y SE REEMPLAZARON AISLADORES | B23042300214 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 444 | 2023-04-23 | 63048 | keep | 0 | Apr | 2023 | 0.042942 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
BARRANQUITAS | 2023-04-23 08:31 | 2023-04-23 12:05 | 124 | 3:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | C23042300059 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 214 | 2023-04-23 | 26536 | keep | 0 | Apr | 2023 | 0.018074 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
PONCE | 2023-04-23 08:38 | 2023-04-23 08:39 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23042300067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 3744 | keep | 0 | Apr | 2023 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
MAYAGÃœEZ | 2023-04-23 08:40 | 2023-04-23 10:45 | 100 | 2:05 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23042300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-04-23 | 12500 | keep | 0 | Apr | 2023 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-23 08:45 | 2023-04-23 10:15 | 10 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23042300007 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-04-23 | 900 | keep | 0 | Apr | 2023 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-23 08:47 | 2023-04-23 10:49 | 20 | 2:02 | P | DESGANCHE | 1 X 25 EN C/L | R23042300012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-04-23 | 2440 | keep | 0 | Apr | 2023 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-23 08:50 | 2023-04-23 08:51 | 234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042300014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 234 | keep | 0 | Apr | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
CANOVANAS | 2023-04-23 09:00 | 2023-04-23 13:16 | 24 | 4:16 | P | DESGANCHE | 1 X 30 Y 1 X 10 EN XMR DESGANCHE Y REMPLAZO CAJA QUEMADA PARARRAYO Y DISCO | R23042300015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-04-23 | 6144 | keep | 0 | Apr | 2023 | 0.0041847 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2023-04-23 09:07 | 2023-04-23 12:30 | 8 | 3:23 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23042300019 | New_Event | Animals | Include | Include | Wildlife | 203 | 2023-04-23 | 1624 | keep | 0 | Apr | 2023 | 0.0011061 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-23 09:12 | 2023-04-23 09:13 | 6197 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C2304230000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-23 | 6197 | keep | 0 | Apr | 2023 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
CAGUAS | 2023-04-23 09:13 | 2023-04-23 10:00 | 10 | 0:47 | P | ERROR HUMANO | SE CERRO FUSIBLE QUE SE DEJO ABIERTO POR ERROR POR EL PERSONAL DE CAMPO MIENTRAS SE TRABAJABA CON CONDICION DE DESGANCHE. | C23042200104 | New_Event | Human Error | Include | Include | Other | 47 | 2023-04-23 | 470 | keep | 0 | Apr | 2023 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-23 09:17 | 2023-04-23 13:54 | 97 | 4:37 | P | NO SE REPORTO CAUSA | 2 X 80 EN C/L | S23042300178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2023-04-23 | 26869 | keep | 0 | Apr | 2023 | 0.0183 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
CAGUAS | 2023-04-23 09:29 | 2023-04-23 09:32 | 1307 | 0:03 | P | CONDUCTOR ARRIADO O CRUZADO | DISPARO BKR 3015-07 LLEVA 60% DEL 3103-05 SE ABRIO MACHETE Y SE CERRO BKR POR CONTROL 90% EN SERVICIO | C23042300028 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 3 | 2023-04-23 | 3921 | keep | 0 | Apr | 2023 | 0.0026706 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-23 09:32 | 2023-04-23 10:39 | 218 | 1:07 | P | CONDUCTOR ARRIADO O CRUZADO | SE DESPEGO LINEA DE CRUCETA 98% EN SERVICIO | C23042300028 | 1st_after_momentary | Primary To Primary Contact | Include | Include | Equipment | 67 | 2023-04-23 | 14606 | keep | 0 | Apr | 2023 | 0.0099481 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
CAGUAS | 2023-04-23 10:00 | 2023-04-23 11:21 | 6197 | 1:21 | T | DESGANCHE | SE ABRIO BKR A PETICION DE RAUL SUAREZ POR CONDUCTOR EN EL SUELO ENERGIZADO DEBIDO A BAMBUA. ENTRO 30% EN SERVICIO | C23042300121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-04-23 | 501957 | keep | 0 | Apr | 2023 | 0.34188 | 0.0042207 | Sustained | FALSE | FALSE | Not_TMED_Event | 6197
MAYAGÃœEZ | 2023-04-23 10:33 | 2023-04-23 10:34 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON RECIERRE EN ON, NO RECERRO, CERRADO POR SCADA | M23042300014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 4304 | keep | 0 | Apr | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CAGUAS | 2023-04-23 10:39 | 2023-04-23 10:45 | 44 | 0:06 | P | CONDUCTOR ARRIADO O CRUZADO | SE REALIZARON OPERACIONES 100% EN SERVICIO | C23042300028 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 6 | 2023-04-23 | 264 | keep | 0 | Apr | 2023 | 0.00017981 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
VEGA BAJA | 2023-04-23 11:00 | 2023-04-23 13:15 | 6 | 2:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23042300034 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 135 | 2023-04-23 | 810 | keep | 0 | Apr | 2023 | 0.00055169 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-04-23 11:06 | 2023-04-23 15:39 | 10 | 4:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR FUERTES LLUVIAS | R23042300020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 273 | 2023-04-23 | 2730 | keep | 0 | Apr | 2023 | 0.0018594 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-23 11:15 | 2023-04-23 14:45 | 12 | 3:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO NEUTRAL SECUNDARIO PARTIDO | M23042300020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 210 | 2023-04-23 | 2520 | keep | 0 | Apr | 2023 | 0.0017164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-23 11:21 | 2023-04-23 11:58 | 4338 | 0:37 | P | DESGANCHE | SE SECCIONALIZO CONDUCTOR ROTO POR BAMBUAS EN EL SUELO 98% EN SERVICIO | C23042300121 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-04-23 | 160506 | keep | 0 | Apr | 2023 | 0.10932 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-23 11:21 | 2023-04-23 13:00 | 10 | 1:39 | P | ERROR HUMANO | SE CERRO FUSIBLE QUE SE DEJO ABIERTO POR ERROR POR EL PERSONAL DE CAMPO MIENTRAS SE TRABAJABA CON CONDICION DE DESGANCHE. | C23042200104 | Partial_restoration | Human Error | Include | Include | Other | 99 | 2023-04-23 | 990 | keep | 0 | Apr | 2023 | 0.00067428 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-23 11:35 | 2023-04-23 11:36 | 4641 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | M23042300022 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-23 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
MAYAGÃœEZ | 2023-04-23 11:36 | 2023-04-23 13:30 | 40 | 1:54 | P | ANIMAL | 2 X 40 EN CORTE DE LINEA AVE CRUZO FASES A TIERRA | M23042300025 | 1st_after_momentary | Animals | Include | Include | Wildlife | 114 | 2023-04-23 | 4560 | keep | 0 | Apr | 2023 | 0.0031058 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-04-23 11:38 | 2023-04-23 13:57 | 20 | 2:19 | P | SECUNDARIA/DESGANCHE | SE REMPLAZA LINEA SECUNDARIA AVERIADA POR ARBOL | P23042300088 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 139 | 2023-04-23 | 2780 | keep | 0 | Apr | 2023 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-04-23 11:45 | 2023-04-23 14:05 | 12 | 2:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | P23042300090 | New_Event | Secondary Wire Break | Include | Include | Equipment | 140 | 2023-04-23 | 1680 | keep | 0 | Apr | 2023 | 0.0011442 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-23 11:51 | 2023-04-23 14:00 | 312 | 2:09 | P | ALIMENTADOR AMARRADO | SJ-230423-04 SE SECCIONALIZO ALIMENTADOR NO SE VIO CONDICION Y SE CERRO MACHETES. 1345-02 LLEVA 80% DEL 1342-04 | S23042300386 | New_Event | Feeder Load Transferred | Include | Include | Other | 129 | 2023-04-23 | 40248 | keep | 0 | Apr | 2023 | 0.027413 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-04-23 11:51 | 2023-04-23 13:19 | 435 | 1:28 | T | NO SE REPORTO CAUSA | SJ-230423-04 SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA. 1345-02 LLEVA 80% DEL 1342-04 | S23042300386 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2023-04-23 | 38280 | keep | 0 | Apr | 2023 | 0.026072 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
MAYAGÃœEZ | 2023-04-23 11:52 | 2023-04-23 13:22 | 29 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE LINEA SECUNDARIA | M23042300024 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-04-23 | 2610 | keep | 0 | Apr | 2023 | 0.0017777 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2023-04-23 11:54 | 2023-04-23 12:55 | 1588 | 1:01 | T | ALIMENTADOR AMARRADO | BY-230423-01 DISPARO DE BKR 1716-03 LLEVA EL 1711-01 Y 1711-03 | B23042200199 | New_Event | Feeder Load Transferred | Include | Include | Other | 61 | 2023-04-23 | 96868 | keep | 0 | Apr | 2023 | 0.065976 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-04-23 11:54 | 2023-04-23 12:55 | 13 | 1:01 | T | ALIMENTADOR AMARRADO | BY-230423-01 DISPARO DE BKR 1716-03 LLEVA EL 1711-01 Y 1711-03 | B23042200199 | New_Event | Feeder Load Transferred | Include | Include | Other | 61 | 2023-04-23 | 793 | keep | 0 | Apr | 2023 | 0.00054011 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-23 11:54 | 2023-04-23 12:55 | 1812 | 1:01 | T | NO SE REPORTO CAUSA | BY-230423-01 DISPARO DE BKR 1716-03 LLEVA EL 1711-01 Y 1711-03 | B23042200199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-04-23 | 110532 | keep | 0 | Apr | 2023 | 0.075283 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
CAGUAS | 2023-04-23 11:58 | 2023-04-23 13:30 | 124 | 1:32 | P | DESGANCHE | SE LEVANTO CONDUCTOR PRIMARIO 100% EN SERVICIO | C23042300121 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-04-23 | 11408 | keep | 0 | Apr | 2023 | 0.0077699 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 12:08 | 2023-04-23 13:34 | 22 | 1:26 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23042300396 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-04-23 | 1892 | keep | 0 | Apr | 2023 | 0.0012886 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-04-23 12:11 | 2023-04-23 13:50 | 160 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23042300398 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-04-23 | 15840 | keep | 0 | Apr | 2023 | 0.010789 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
HUMACAO | 2023-04-23 12:11 | 2023-04-23 15:57 | 1 | 3:46 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE TRANSFORMADOR PARA REPARAR BAJANTE DE CAJA A TRANSFORMADOR | C23042300269 | New_Event | Primary Wire Break | Include | Include | Equipment | 226 | 2023-04-23 | 226 | keep | 0 | Apr | 2023 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-23 12:11 | 2023-04-23 13:42 | 4 | 1:31 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M23042300028 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 91 | 2023-04-23 | 364 | keep | 0 | Apr | 2023 | 0.00024792 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-23 12:29 | 2023-04-23 12:55 | 40 | 0:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | BY-230423-01 SE CORRIO N/O POR CAJA QUEMADA | B23042300288 | New_Event | Cutout Failure | Include | Include | Equipment | 26 | 2023-04-23 | 1040 | keep | 0 | Apr | 2023 | 0.00070834 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-23 12:38 | 2023-04-23 16:59 | 40 | 4:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIA | B23042300290 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 261 | 2023-04-23 | 10440 | keep | 0 | Apr | 2023 | 0.0071106 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-04-23 12:41 | 2023-04-23 14:22 | 200 | 1:41 | P | DESGANCHE | 2 X 80 Y 2 X 100 EN C/LS | R23042300026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-04-23 | 20200 | keep | 0 | Apr | 2023 | 0.013758 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-04-23 12:41 | 2023-04-23 12:42 | 2859 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | C2304230000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-23 | 2859 | keep | 0 | Apr | 2023 | 0.0019473 | 0.0019473 | Momentary | FALSE | FALSE | Not_TMED_Event | 2859
BARRANQUITAS | 2023-04-23 12:42 | 2023-04-23 18:30 | 556 | 5:48 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA | C23042300319 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 348 | 2023-04-23 | 193488 | keep | 0 | Apr | 2023 | 0.13178 | 0.00037869 | Sustained | FALSE | FALSE | Not_TMED_Event | 556
CAGUAS | 2023-04-23 12:45 | 2023-04-23 17:52 | 58 | 5:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | C23042300287 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 307 | 2023-04-23 | 17806 | keep | 0 | Apr | 2023 | 0.012128 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
VEGA BAJA | 2023-04-23 12:47 | 2023-04-23 18:28 | 10 | 5:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR MAL TIEMPO LLUVIAS Y FUERTES VIENTOS | B23042300297 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 341 | 2023-04-23 | 3410 | keep | 0 | Apr | 2023 | 0.0023225 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-23 12:50 | 2023-04-23 14:32 | 40 | 1:42 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CL SE RETEZO LINEA PRIMARIA CRUZADA CON LINEAS SECUNDARIAS | P23042300095 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 102 | 2023-04-23 | 4080 | keep | 0 | Apr | 2023 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-23 13:00 | 2023-04-23 18:55 | 282 | 5:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIA | S23042300432 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 355 | 2023-04-23 | 100110 | keep | 0 | Apr | 2023 | 0.068184 | 0.00019207 | Sustained | FALSE | FALSE | Not_TMED_Event | 282
BAYAMON | 2023-04-23 13:01 | 2023-04-23 13:02 | 3597 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 9405-05 LLEVA 1719-15 | B2304230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 3597 | keep | 0 | Apr | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-04-23 13:01 | 2023-04-23 13:02 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BK R9405-05 LLEVA 1719-15 | B2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 3511 | keep | 0 | Apr | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-04-23 13:04 | 2023-04-24 05:48 | 50 | 16:44 | P | ARBOL SOBRE LINEA | 2 X 65 EN C/L ARBOL SOBRE LINEA | B23042300304 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1004 | 2023-04-23 | 50200 | keep | 0 | Apr | 2023 | 0.034191 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-04-23 13:08 | 2023-04-23 15:56 | 30 | 2:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23042300039 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 168 | 2023-04-23 | 5040 | keep | 0 | Apr | 2023 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-04-23 13:11 | 2023-04-23 15:46 | 30 | 2:35 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | P23042300096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-04-23 | 4650 | keep | 0 | Apr | 2023 | 0.0031671 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-23 13:19 | 2023-04-23 14:00 | 217 | 0:41 | P | NO SE REPORTO CAUSA | SJ-230423-04 SE SECCIONALIZO ALIMENTADOR NO SE VIO CONDICION Y SE CERRO MACHETES. 1345-02 LLEVA 80% DEL 1342-04 | S23042300386 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 41 | 2023-04-23 | 8897 | keep | 0 | Apr | 2023 | 0.0060597 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 13:19 | 2023-04-23 13:20 | 1533 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23042300313 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1533 | keep | 0 | Apr | 2023 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
SAN JUAN | 2023-04-23 13:20 | 2023-04-23 14:00 | 138 | 0:40 | P | ALIMENTADOR AMARRADO | DISPARO 10% POR 1206-04 SE VERIFICO CON PERSONAL Y SE PROBO QUEDO EN SERVICIO | S23042300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 40 | 2023-04-23 | 5520 | keep | 0 | Apr | 2023 | 0.0037596 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
SAN JUAN | 2023-04-23 13:20 | 2023-04-23 14:00 | 1977 | 0:40 | P | ALIMENTADOR AMARRADO | DISPARO 40% POR 1206-04 SE VERIFICO CON PERSONAL Y SE PROBO QUEDO EN SERVICIO | S23042300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 40 | 2023-04-23 | 79080 | keep | 0 | Apr | 2023 | 0.053861 | 0.0013465 | Sustained | FALSE | FALSE | Not_TMED_Event | 1977
SAN JUAN | 2023-04-23 13:20 | 2023-04-23 14:00 | 1799 | 0:40 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 40% DEL 1204-04 Y 10% DEL 1204-03 SE VERIFICO CON PERSONAL Y SE PROBO QUEDO EN SERVICIO | S23042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2023-04-23 | 71960 | keep | 0 | Apr | 2023 | 0.049012 | 0.0012253 | Sustained | FALSE | FALSE | Not_TMED_Event | 1799
HUMACAO | 2023-04-23 13:28 | 2023-04-23 16:13 | 1 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO | C23042300317 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-04-23 | 165 | keep | 0 | Apr | 2023 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-23 13:31 | 2023-04-23 13:32 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2023-04-23 13:33 | 2023-04-23 16:56 | 1588 | 3:23 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR ENTRO UN 20% | B23042200199 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 203 | 2023-04-23 | 322364 | keep | 0 | Apr | 2023 | 0.21956 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 13:33 | 2023-04-23 18:55 | 13 | 5:22 | T | ALIMENTADOR AMARRADO | SE REALIZARON OPERACIONES SE CERRARON MACHETES 100% EN SERVICIO | B23042200199 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 322 | 2023-04-23 | 4186 | keep | 0 | Apr | 2023 | 0.0028511 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 13:33 | 2023-04-23 15:09 | 1812 | 1:36 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR 1716-03 LLEVA 1711-01 Y 1711-03 SE SECCIONALIZO ENTRO UN 5% 1716-03 AUN LAS CARGAS DEL 1711-1 Y 1711-03 ESTAN FUERA | B23042200199 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 96 | 2023-04-23 | 173952 | keep | 0 | Apr | 2023 | 0.11848 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 13:34 | 2023-04-23 13:36 | 3957 | 0:02 | T | ARBOL SOBRE LINEA | DISPARO Y SE CERRO POR SCADA | S2304230000X | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 2 | 2023-04-23 | 7914 | keep | 0 | Apr | 2023 | 0.0053902 | 0.0026951 | Momentary | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2023-04-23 13:36 | 2023-04-23 14:14 | 1483 | 0:38 | P | ALIMENTADOR AMARRADO | DISPARO 30% POR 1303-02 Y SE PROBO QUEDO EN SERVICIO | S23042300498 | New_Event | Feeder Load Transferred | Include | Include | Other | 38 | 2023-04-23 | 56354 | keep | 0 | Apr | 2023 | 0.038382 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-04-23 13:36 | 2023-04-23 14:14 | 2435 | 0:38 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 30% DEL 1204-04 Y SE PROBO QUEDO EN SERVICIO | S23042300498 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2023-04-23 | 92530 | keep | 0 | Apr | 2023 | 0.063022 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-04-23 13:36 | 2023-04-23 16:10 | 2387 | 2:34 | P | ARBOL SOBRE LINEA | CERRADO PB | S23042300590 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 154 | 2023-04-23 | 367598 | keep | 0 | Apr | 2023 | 0.25037 | 0.0016258 | Sustained | FALSE | FALSE | Not_TMED_Event | 2387
BAYAMON | 2023-04-23 13:36 | 2023-04-23 16:30 | 22 | 2:54 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23042300396 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 174 | 2023-04-23 | 3828 | keep | 0 | Apr | 2023 | 0.0026072 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-23 13:42 | 2023-04-23 15:24 | 32 | 1:42 | P | DESGANCHE | 1 X 40 EN C/L | R23042300039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-04-23 | 3264 | keep | 0 | Apr | 2023 | 0.0022231 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
AGUADILLA | 2023-04-23 13:47 | 2023-04-23 14:32 | 50 | 0:45 | P | DESGANCHE | 1 X 5O EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23042300034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2023-04-23 | 2250 | keep | 0 | Apr | 2023 | 0.0015325 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-23 14:00 | 2023-04-23 15:39 | 250 | 1:39 | P | DESGANCHE | SJ-230423-05 CON DISPARO DE PORTATIL SE SECCIONALIZO Y SE TRANSFIRIO CARGA AL 1336-08 INCLUYENDO HOSPITAL SAN FRANCISCO | S23042300631 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-04-23 | 24750 | keep | 0 | Apr | 2023 | 0.016857 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-04-23 14:00 | 2023-04-23 16:17 | 1032 | 2:17 | P | DESGANCHE | SJ-230423-05 CON DISPARO DE PORTATIL SE SECCIONALIZO Y ENERGIZO BKR SECUNDARIO DE LA PORTATIL 20% EN SERVICIO | S23042300631 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-04-23 | 141384 | keep | 0 | Apr | 2023 | 0.096296 | 0.00070289 | Sustained | FALSE | FALSE | Not_TMED_Event | 1032
CANOVANAS | 2023-04-23 14:06 | 2023-04-23 14:07 | 4154 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | R23042300044 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-23 | 4154 | keep | 0 | Apr | 2023 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2023-04-23 14:07 | 2023-04-23 19:57 | 40 | 5:50 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE NO FUNDIO | R23042300047 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 350 | 2023-04-23 | 14000 | keep | 0 | Apr | 2023 | 0.0095353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-23 14:13 | 2023-04-23 14:16 | 1681 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO MAL TIEMPO LLEVA 1346-06 SE PROBO QUEDO ENB SERVICIO | S23042300689 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2023-04-23 | 5043 | keep | 0 | Apr | 2023 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-04-23 14:13 | 2023-04-23 14:16 | 1598 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO MAL TIEMPO LLEVA 1346-06 SE PROBO QUEDO ENB SERVICIO | S23042300689 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-23 | 4794 | keep | 0 | Apr | 2023 | 0.0032652 | 0.0010884 | Momentary | FALSE | FALSE | Not_TMED_Event | 1598
SAN JUAN | 2023-04-23 14:16 | 2023-04-23 19:00 | 304 | 4:44 | P | NO SE REPORTO CAUSA | SE CERR PB EN EL CAMPO | S23042300797 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 284 | 2023-04-23 | 86336 | keep | 0 | Apr | 2023 | 0.058803 | 0.00020705 | Sustained | FALSE | FALSE | Not_TMED_Event | 304
AGUADILLA | 2023-04-23 14:16 | 2023-04-23 14:17 | 390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23042300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 390 | keep | 0 | Apr | 2023 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BAYAMON | 2023-04-23 14:19 | 2023-04-23 14:20 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 4431 | keep | 0 | Apr | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
ARECIBO | 2023-04-23 14:20 | 2023-04-23 19:46 | 7 | 5:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO CONEXIONES SECUNDARIAS | A23042300041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 326 | 2023-04-23 | 2282 | keep | 0 | Apr | 2023 | 0.0015543 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-04-23 14:20 | 2023-04-23 14:21 | 3431 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DEL INTERRUPTOR MAL TIEMPO VIENTOS FUERTES | A23042300042 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-23 | 3431 | keep | 0 | Apr | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-04-23 14:21 | 2023-04-23 17:15 | 200 | 2:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 Y 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23042300046 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 174 | 2023-04-23 | 34800 | keep | 0 | Apr | 2023 | 0.023702 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-04-23 14:25 | 2023-04-23 14:30 | 2178 | 0:05 | T | PARARRAYOS DEFECTUOSO | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO | C23042300000 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 5 | 2023-04-23 | 10890 | keep | 0 | Apr | 2023 | 0.0074171 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2023-04-23 14:32 | 2023-04-23 14:33 | 1382 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR ESCADA | B23042300357 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1382 | keep | 0 | Apr | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
CAGUAS | 2023-04-23 14:32 | 2023-04-23 14:33 | 2178 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECERRO | C23042300000 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-04-23 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-23 14:34 | 2023-04-23 17:00 | 30 | 2:26 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | P23042300114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-04-23 | 4380 | keep | 0 | Apr | 2023 | 0.0029832 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-23 14:36 | 2023-04-23 14:38 | 922 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1401-08 | S23042300762 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-23 | 1844 | keep | 0 | Apr | 2023 | 0.0012559 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-04-23 14:36 | 2023-04-23 14:38 | 135 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1346-05 Y SE CERRO POR SCADA | S23042300762 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-23 | 270 | keep | 0 | Apr | 2023 | 0.0001839 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2023-04-23 14:37 | 2023-04-23 14:38 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042300053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 3046 | keep | 0 | Apr | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
VEGA BAJA | 2023-04-23 14:37 | 2023-04-23 17:21 | 60 | 2:44 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | B23042300361 | New_Event | Animals | Include | Include | Wildlife | 164 | 2023-04-23 | 9840 | keep | 0 | Apr | 2023 | 0.006702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-04-23 14:38 | 2023-04-23 16:15 | 2178 | 1:37 | T | PARARRAYOS DEFECTUOSO | DISPARO ALIMENTADOR SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO 50% EN SERVICIO | C23042300352 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 97 | 2023-04-23 | 211266 | keep | 0 | Apr | 2023 | 0.14389 | 0.0014834 | Sustained | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2023-04-23 14:39 | 2023-04-23 18:27 | 198 | 3:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN C/L MAL TIEMPO LLUVIA | B23042300363 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 228 | 2023-04-23 | 45144 | keep | 0 | Apr | 2023 | 0.030747 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BAYAMON | 2023-04-23 14:40 | 2023-04-24 08:05 | 95 | 17:25 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23042300365 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1045 | 2023-04-23 | 99275 | keep | 0 | Apr | 2023 | 0.067616 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
CANOVANAS | 2023-04-23 14:48 | 2023-04-23 14:49 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042300056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
BAYAMON | 2023-04-23 14:48 | 2023-04-23 16:19 | 134 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 C/L LLUVIAS FUERTES MAL TIEMPO | B23042300374 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2023-04-23 | 12194 | keep | 0 | Apr | 2023 | 0.0083053 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2023-04-23 14:50 | 2023-04-23 15:50 | 40 | 1:00 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23042300375 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2023-04-23 | 2400 | keep | 0 | Apr | 2023 | 0.0016346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-23 15:01 | 2023-04-23 15:02 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042300061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
PONCE | 2023-04-23 15:01 | 2023-04-23 16:22 | 10 | 1:21 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | P23042300117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-04-23 | 810 | keep | 0 | Apr | 2023 | 0.00055169 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-23 15:06 | 2023-04-24 17:12 | 79 | 26:06 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23042300846 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1566 | 2023-04-23 | 123714 | keep | 0 | Apr | 2023 | 0.084261 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2023-04-23 15:09 | 2023-04-23 15:42 | 1721 | 0:33 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ENTRO EN SERVICIO UN 50% DEL 1716-03 CONTINUAL FUERA 1711-03 Y 1711-01 | B23042200199 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 33 | 2023-04-23 | 56793 | keep | 0 | Apr | 2023 | 0.038681 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-23 15:20 | 2023-04-23 16:25 | 40 | 1:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M23042300043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2023-04-23 | 2600 | keep | 0 | Apr | 2023 | 0.0017708 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-23 15:30 | 2023-04-23 18:05 | 127 | 2:35 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23042300898 | New_Event | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-04-23 | 19685 | keep | 0 | Apr | 2023 | 0.013407 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
ARECIBO | 2023-04-23 15:40 | 2023-04-24 17:25 | 4 | 25:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | A23042200097 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1545 | 2023-04-23 | 6180 | keep | 0 | Apr | 2023 | 0.0042092 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 15:41 | 2023-04-23 15:42 | 946 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1525-05 CERRADO POR SCADA | S23042300929 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 946 | keep | 0 | Apr | 2023 | 0.00064432 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2023-04-23 15:41 | 2023-04-23 15:42 | 937 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1525-02 CERRADO POR SCADA | S23042300929 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 937 | keep | 0 | Apr | 2023 | 0.00063819 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
BAYAMON | 2023-04-23 15:42 | 2023-04-23 16:49 | 906 | 1:07 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ENTRO EN SERVICIO UN 70 DEL 1716-03 CONTINUAL FUERA 1711-03 Y 1711-01 | B23042200199 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 67 | 2023-04-23 | 60702 | keep | 0 | Apr | 2023 | 0.041344 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 15:46 | 2023-04-23 15:47 | 621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S23042300938 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 621 | keep | 0 | Apr | 2023 | 0.00042296 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
CAGUAS | 2023-04-23 15:53 | 2023-04-23 18:48 | 1378 | 2:55 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO MACHETE Y SE CERRO INTERRUPTOR ASILADOR PARTIDO SE SECCIONALIZO 80% EN SERVICIO | C23042300368 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 175 | 2023-04-23 | 241150 | keep | 0 | Apr | 2023 | 0.16425 | 0.00093855 | Sustained | FALSE | FALSE | Not_TMED_Event | 1378
BAYAMON | 2023-04-23 15:57 | 2023-04-24 00:54 | 71 | 8:57 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | B23042300423 | New_Event | Primary Wire Break | Include | Include | Equipment | 537 | 2023-04-23 | 38127 | keep | 0 | Apr | 2023 | 0.025968 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
FAJARDO | 2023-04-23 16:09 | 2023-04-23 19:10 | 10 | 3:01 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R23042300087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-04-23 | 1810 | keep | 0 | Apr | 2023 | 0.0012328 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-23 16:15 | 2023-04-23 16:19 | 1089 | 0:04 | P | PARARRAYOS DEFECTUOSO | SE PATRULLO SE ENCONTRO PARARRAYO AVERIADO FTE. CDT CAGUAS Y SE ELIMINO Y SE DEJO MACHETE ABIERTO N/C FID-1001721707 SE DEJO COMO N/O Y SE CERRO 3015-07 LLEVANDO 50% DE SU CARGA | C23042300352 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2023-04-23 | 4356 | keep | 0 | Apr | 2023 | 0.0029669 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 16:17 | 2023-04-23 17:59 | 258 | 1:42 | P | DESGANCHE | SJ-230423-05 CON DISPARO DE PORTATIL SE SECCIONALIZO Y ENERGIZO BKR SECUNDARIO DE LA PORTATIL 20% EN SERVICIO, SE REALIZO DESGANCHE EN CDT Y SE CEERO MACHETES | S23042300631 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-04-23 | 26316 | keep | 0 | Apr | 2023 | 0.017924 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-23 16:20 | 2023-04-23 16:45 | 40 | 0:25 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042300057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2023-04-23 | 1000 | keep | 0 | Apr | 2023 | 0.0006811 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-04-23 16:21 | 2023-04-23 18:28 | 40 | 2:07 | P | DESGANCHE | 1 X 40 EN C/L | R23042300088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-04-23 | 5080 | keep | 0 | Apr | 2023 | 0.00346 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-23 16:30 | 2023-04-23 16:32 | 3957 | 0:02 | T | DESGANCHE | DISPARO Y SE CERRO POR SCADA | S23042300938 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-23 | 7914 | keep | 0 | Apr | 2023 | 0.0053902 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 16:32 | 2023-04-23 18:40 | 3877 | 2:08 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO TRAMO MEDIANTE SJ-230423-06, SE CERRP PB ENTRANDO UN 98% DEL 1908-03 | S23042300938 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 128 | 2023-04-23 | 496256 | keep | 0 | Apr | 2023 | 0.338 | 0.0026406 | Sustained | FALSE | FALSE | Not_TMED_Event | 3877
BAYAMON | 2023-04-23 16:32 | 2023-04-23 18:47 | 22 | 2:15 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23042300396 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-04-23 | 2970 | keep | 0 | Apr | 2023 | 0.0020229 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-04-23 16:49 | 2023-04-23 16:56 | 543 | 0:07 | P | NO SE REPORTO CAUSA | SE SECCIONALIZO ENTRO EN SERVICIO UN 80% DEL 1716-03 CONTINUAL FUERA 1711-03, Y ENTRO 20% 1711-01 | B23042200199 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-04-23 | 3801 | keep | 0 | Apr | 2023 | 0.0025888 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 16:56 | 2023-04-23 17:10 | 317 | 0:14 | P | ALIMENTADOR AMARRADO | SE DISPARO EL ALIMENTADOR TRATANDO DE NORMALIZARLO | B23042200199 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 14 | 2023-04-23 | 4438 | keep | 0 | Apr | 2023 | 0.0030227 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 16:56 | 2023-04-23 17:10 | 1450 | 0:14 | P | NO SE REPORTO CAUSA | SE DISPARO EL ALIMENTADOR TRATANDO DE NORMALIZARLO | B23042200199 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 14 | 2023-04-23 | 20300 | keep | 0 | Apr | 2023 | 0.013826 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 17:10 | 2023-04-23 17:21 | 1588 | 0:11 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO ALIMENTADOR 90% DEL 1716-03 EN SERVICIO Y UN 40% 1711-01 | B23042200199 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 11 | 2023-04-23 | 17468 | keep | 0 | Apr | 2023 | 0.011897 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 17:10 | 2023-04-23 17:21 | 1450 | 0:11 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR 90% DEL 1716-03 EN SERVICIO Y UN 40% 1711-01 | B23042200199 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 11 | 2023-04-23 | 15950 | keep | 0 | Apr | 2023 | 0.010863 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-23 17:15 | 2023-04-23 22:55 | 15 | 5:40 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | R23042300101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2023-04-23 | 5100 | keep | 0 | Apr | 2023 | 0.0034736 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-04-23 17:19 | 2023-04-23 18:17 | 30 | 0:58 | P | ANIMAL | 1 X 40 EN CL CRUCE DE FASE POR AVE | P23042300130 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-04-23 | 1740 | keep | 0 | Apr | 2023 | 0.0011851 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-23 17:21 | 2023-04-23 21:56 | 128 | 4:35 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO PUENTE DE LINEA A CAJA NO FUNDIO | R23042300102 | New_Event | Primary Wire Break | Include | Include | Equipment | 275 | 2023-04-23 | 35200 | keep | 0 | Apr | 2023 | 0.023975 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
BAYAMON | 2023-04-23 17:21 | 2023-04-23 18:55 | 953 | 1:34 | P | ALIMENTADOR AMARRADO | SE REALIZARON OPERACIONES SE CERRARON MACHETES 100% EN SERVICIO | B23042200199 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 94 | 2023-04-23 | 89582 | keep | 0 | Apr | 2023 | 0.061014 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 17:21 | 2023-04-23 18:55 | 181 | 1:34 | P | NO SE REPORTO CAUSA | SE REALIZARON OPERACIONES SE CERRARON MACHETES 100% EN SERVICIO | B23042200199 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-04-23 | 17014 | keep | 0 | Apr | 2023 | 0.011588 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-23 17:28 | 2023-04-23 18:37 | 10 | 1:09 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO FASE | C23042300391 | New_Event | Animals | Include | Include | Wildlife | 69 | 2023-04-23 | 690 | keep | 0 | Apr | 2023 | 0.00046996 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-23 17:29 | 2023-04-23 17:30 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1620-05 Y SE CERRO POR SCADA | S2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1615 | keep | 0 | Apr | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-04-23 17:36 | 2023-04-23 17:37 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042300109 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-23 17:37 | 2023-04-23 21:00 | 120 | 3:23 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23042300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-04-23 | 24360 | keep | 0 | Apr | 2023 | 0.016591 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-04-23 17:43 | 2023-04-24 08:45 | 41 | 15:02 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23042300494 | New_Event | Vegetation Contact | Include | Include | Vegetation | 902 | 2023-04-23 | 36982 | keep | 0 | Apr | 2023 | 0.025188 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BARRANQUITAS | 2023-04-23 17:43 | 2023-04-23 17:44 | 2362 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO | C23042300397 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-23 | 2362 | keep | 0 | Apr | 2023 | 0.0016087 | 0.0016087 | Momentary | FALSE | FALSE | Not_TMED_Event | 2362
BARRANQUITAS | 2023-04-23 17:44 | 2023-04-23 20:23 | 862 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23042300411 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2023-04-23 | 137058 | keep | 0 | Apr | 2023 | 0.09335 | 0.0005871 | Sustained | FALSE | FALSE | Not_TMED_Event | 862
SAN JUAN | 2023-04-23 17:48 | 2023-04-23 20:29 | 120 | 2:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 50 EN C/L MAL TIEMPO LLUVIAS | S23042301168 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 161 | 2023-04-23 | 19320 | keep | 0 | Apr | 2023 | 0.013159 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2023-04-23 17:53 | 2023-04-23 17:55 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | B23042300497 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-23 | 6774 | keep | 0 | Apr | 2023 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
CANOVANAS | 2023-04-23 18:09 | 2023-04-24 12:50 | 8 | 18:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA | R23042300120 | New_Event | Cutout Failure | Include | Include | Equipment | 1121 | 2023-04-23 | 8968 | keep | 0 | Apr | 2023 | 0.0061081 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-04-23 18:12 | 2023-04-23 22:35 | 10 | 4:23 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO CAUSA | R23042300122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 263 | 2023-04-23 | 2630 | keep | 0 | Apr | 2023 | 0.0017913 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-04-23 18:14 | 2023-04-23 21:13 | 100 | 2:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23042300416 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 179 | 2023-04-23 | 17900 | keep | 0 | Apr | 2023 | 0.012192 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-23 18:16 | 2023-04-23 20:40 | 70 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23042300062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2023-04-23 | 10080 | keep | 0 | Apr | 2023 | 0.0068654 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-04-23 18:18 | 2023-04-24 09:46 | 60 | 15:28 | P | NO SE REPORTO CAUSA | 1 X 50 RBA | S23042301212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 928 | 2023-04-23 | 55680 | keep | 0 | Apr | 2023 | 0.037923 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-04-23 18:39 | 2023-04-23 20:59 | 1879 | 2:20 | T | DESGANCHE | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 80% EN SERVICIO | C23042300420 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-04-23 | 263060 | keep | 0 | Apr | 2023 | 0.17917 | 0.0012798 | Sustained | FALSE | FALSE | Not_TMED_Event | 1879
SAN JUAN | 2023-04-23 18:40 | 2023-04-23 18:49 | 80 | 0:09 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO TRAMO MEDIANTE SJ-230423-06, SE CERRO PB ENTRANDO UN 98% DEL 1908-03 Y DISPARO SIN HABER HECHO OPERACIONES EL BKR 1908-03 | S23042300938 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 9 | 2023-04-23 | 720 | keep | 0 | Apr | 2023 | 0.00049039 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-23 18:46 | 2023-04-23 18:47 | 1212 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23042300137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1212 | keep | 0 | Apr | 2023 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
CAGUAS | 2023-04-23 18:48 | 2023-04-23 19:07 | 257 | 0:19 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR Y SE ABRE INTERRUPTOR PARA CERRAR MACHETE | C23042300368 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 19 | 2023-04-23 | 4883 | keep | 0 | Apr | 2023 | 0.0033258 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 18:49 | 2023-04-23 18:56 | 3957 | 0:07 | T | ARBOL SOBRE LINEA | DISPARO SE SECCIONALIZO CON SJ-230423-06 | S23042301027 | Additional_clients | Vegetation Uprooted Tree | Include | Include | Vegetation | 7 | 2023-04-23 | 27699 | keep | 0 | Apr | 2023 | 0.018866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-23 18:49 | 2023-04-23 19:50 | 50 | 1:01 | P | ARBOL SOBRE LINEA | 1 X 50 Y 1 X 65 EN CORTE DE LINEA ARBOL SOBRE LINEA | C23042300380 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 61 | 2023-04-23 | 3050 | keep | 0 | Apr | 2023 | 0.0020773 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-23 18:51 | 2023-04-24 11:45 | 30 | 16:54 | P | ARBOL SOBRE LINEA | 1 X 40 Y 1 X 30 EN DIFERENTES CORTES DE LINEA SE RETIRO ARBOL SOBRE LINEAS | A23042300066 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1014 | 2023-04-23 | 30420 | keep | 0 | Apr | 2023 | 0.020719 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-23 18:55 | 2023-04-24 09:38 | 31 | 14:43 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23042300516 | New_Event | Vegetation Contact | Include | Include | Vegetation | 883 | 2023-04-23 | 27373 | keep | 0 | Apr | 2023 | 0.018644 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-04-23 18:56 | 2023-04-23 19:24 | 2387 | 0:28 | P | ARBOL SOBRE LINEA | SJ-230423-06 SE SECCIONALIZO TRAMO Y SE VOLVIO A CERRAR PB 98% EN SERVICIO | S23042301027 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 28 | 2023-04-23 | 66836 | keep | 0 | Apr | 2023 | 0.045522 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 19:01 | 2023-04-23 19:03 | 320 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | B2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-23 | 640 | keep | 0 | Apr | 2023 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-04-23 19:02 | 2023-04-23 19:03 | 723 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1912-08 LLEVA 1711-02 Y 1711-05 | B2304230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 723 | keep | 0 | Apr | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-04-23 19:02 | 2023-04-23 19:03 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1912-08 LLEVA 1711-02 Y 1711-05 | B2304230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 1976 | keep | 0 | Apr | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-04-23 19:02 | 2023-04-23 19:03 | 577 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR LLEVA 1711-02 Y 1711-05 | B2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 577 | keep | 0 | Apr | 2023 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BARRANQUITAS | 2023-04-23 19:06 | 2023-04-23 20:54 | 35 | 1:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L CERRO PUENTE | C23042300432 | New_Event | Primary Wire Break | Include | Include | Equipment | 108 | 2023-04-23 | 3780 | keep | 0 | Apr | 2023 | 0.0025745 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-04-23 19:07 | 2023-04-23 19:11 | 1378 | 0:04 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE INTERRUPTOR PARA CERRAR MACHETE Y SE CERRO 100% EN SERVICIO | C23042300368 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 4 | 2023-04-23 | 5512 | keep | 0 | Apr | 2023 | 0.0037542 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 19:12 | 2023-04-24 13:57 | 12 | 18:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN XMR NO CAUSA | S23042301293 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1125 | 2023-04-23 | 13500 | keep | 0 | Apr | 2023 | 0.0091948 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-23 19:14 | 2023-04-23 19:16 | 686 | 0:02 | T | ARBOL SOBRE LINEA | DISPARO Y SE CERRO POR SCADA | S23042301298 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 2 | 2023-04-23 | 1372 | keep | 0 | Apr | 2023 | 0.00093446 | 0.00046723 | Momentary | FALSE | FALSE | Not_TMED_Event | 686
FAJARDO | 2023-04-23 19:14 | 2023-04-24 08:11 | 10 | 12:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REEMPLAZO PORTAFUSIBLE | R23042300143 | New_Event | Cutout Failure | Include | Include | Equipment | 777 | 2023-04-23 | 7770 | keep | 0 | Apr | 2023 | 0.0052921 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-23 19:17 | 2023-04-23 19:30 | 686 | 0:13 | T | ARBOL SOBRE LINEA | SE SECCIONALIZO CONDUCTOR EN EL SUELO MEDIANTE SJ-230423-06 Y SE CERRO POR SCADA CORRE CON 1908-03 EN CARR. 842 98% EN SERVICIO | S23042301298 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 13 | 2023-04-23 | 8918 | keep | 0 | Apr | 2023 | 0.006074 | 0.00046723 | Sustained | FALSE | FALSE | Not_TMED_Event | 686
SAN JUAN | 2023-04-23 19:24 | 2023-04-23 22:40 | 80 | 3:16 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA CRUZANDO AMBOS ALIMENTADORES CORRE CON EL 1345-04 100% EN SERVICIO | S23042301027 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 196 | 2023-04-23 | 15680 | keep | 0 | Apr | 2023 | 0.01068 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-23 19:26 | 2023-04-23 20:03 | 86 | 0:37 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23042300521 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 37 | 2023-04-23 | 3182 | keep | 0 | Apr | 2023 | 0.0021672 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
SAN JUAN | 2023-04-23 19:30 | 2023-04-23 22:37 | 14 | 3:07 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA CRUZANDO AMBOS ALIMENTADORES CORRE CON EL 1908-03, SE LEVANTO CONDUCTOR PRIMARIO Y SE REEMPLAZO 4 AISLADORES. 100% EN SERVICIO | S23042301298 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 187 | 2023-04-23 | 2618 | keep | 0 | Apr | 2023 | 0.0017831 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-23 19:38 | 2023-04-24 01:10 | 229 | 5:32 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO EN TRONCAL | S23042301348 | New_Event | Primary Wire Break | Include | Include | Equipment | 332 | 2023-04-23 | 76028 | keep | 0 | Apr | 2023 | 0.051782 | 0.00015597 | Sustained | FALSE | FALSE | Not_TMED_Event | 229
CAGUAS | 2023-04-23 19:44 | 2023-04-23 19:45 | 3005 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO AL MOMENTO QUE SE CERRO 3006-02 SE LE INFORMO A PERSONAL EN EL CAMPO Y SE CERRO ALIMENTADOR 3006-05 CONTINUAN PATRULLANDO 3006-02 | C23042300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 3005 | keep | 0 | Apr | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
BAYAMON | 2023-04-23 19:53 | 2023-04-23 23:27 | 26 | 3:34 | P | SOBRECARGA | 1 NX X 12 EN XMR POR CARGA | B23042300527 | New_Event | Trip Due To Overload | Include | Include | Other | 214 | 2023-04-23 | 5564 | keep | 0 | Apr | 2023 | 0.0037896 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
VEGA BAJA | 2023-04-23 19:54 | 2023-04-23 21:26 | 200 | 1:32 | P | ANIMAL | 1 X 80 EN C/L 1 X 65 EN RISER CRUCE POR AVE | B23042300529 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-04-23 | 18400 | keep | 0 | Apr | 2023 | 0.012532 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-04-23 20:15 | 2023-04-23 20:16 | 621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1423-05 | S2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 621 | keep | 0 | Apr | 2023 | 0.00042296 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
SAN JUAN | 2023-04-23 20:23 | 2023-04-23 20:24 | 621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1423-05 | S2304230000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 621 | keep | 0 | Apr | 2023 | 0.00042296 | 0.00042296 | Momentary | FALSE | FALSE | Not_TMED_Event | 621
PONCE | 2023-04-23 20:29 | 2023-04-23 22:52 | 948 | 2:23 | T | DESGANCHE | SE RALIZO DESGANCHE Y SE PUSO ALIMENTADOR EN SERVICIO | P23042300140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-04-23 | 135564 | keep | 0 | Apr | 2023 | 0.092332 | 0.00064568 | Sustained | FALSE | FALSE | Not_TMED_Event | 948
BAYAMON | 2023-04-23 20:29 | 2023-04-24 10:12 | 6 | 13:43 | P | DESGANCHE | DESGANCHE 2 X 65 Y 1 X 50 EN CORTES DE LINEA | B23042300551 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2023-04-23 | 4938 | keep | 0 | Apr | 2023 | 0.0033632 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-23 20:45 | 2023-04-24 13:16 | 164 | 16:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23042300479 | New_Event | Vegetation Contact | Include | Include | Vegetation | 991 | 2023-04-23 | 162524 | keep | 0 | Apr | 2023 | 0.11069 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
BAYAMON | 2023-04-23 20:48 | 2023-04-23 21:21 | 2 | 0:33 | P | DESGANCHE | 1 X 50 EN CL DESGANCHE | B23042301485 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-04-23 | 66 | keep | 0 | Apr | 2023 | 4.4952e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-04-23 20:59 | 2023-04-24 08:35 | 376 | 11:36 | P | DESGANCHE | SE REALIZO DESGANCHE EN VARIOS PUNTOS | C23042300420 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 696 | 2023-04-23 | 261696 | keep | 0 | Apr | 2023 | 0.17824 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-23 21:01 | 2023-04-24 11:55 | 12 | 14:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23042300072 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 894 | 2023-04-23 | 10728 | keep | 0 | Apr | 2023 | 0.0073068 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-04-23 21:11 | 2023-04-23 22:40 | 250 | 1:29 | P | ANIMAL | 1 X 140 EN CORTE DE LINEA AVE CRUZO LINEA | A23042300077 | New_Event | Animals | Include | Include | Wildlife | 89 | 2023-04-23 | 22250 | keep | 0 | Apr | 2023 | 0.015154 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-04-23 21:13 | 2023-04-24 01:21 | 1647 | 4:08 | T | ARBOL SOBRE LINEA | DISPARO DE BKR SE SECCIONALIZO Y SE CERRO POR CONTROL 50% EN SERVIICIO | B23042300575 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 248 | 2023-04-23 | 408456 | keep | 0 | Apr | 2023 | 0.2782 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
VEGA BAJA | 2023-04-23 21:18 | 2023-04-24 10:20 | 17 | 13:02 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMA | A23042300080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 782 | 2023-04-23 | 13294 | keep | 0 | Apr | 2023 | 0.0090545 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
FAJARDO | 2023-04-23 21:36 | 2023-04-24 08:52 | 106 | 11:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIA | R23042300169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 676 | 2023-04-23 | 71656 | keep | 0 | Apr | 2023 | 0.048805 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
PONCE | 2023-04-23 21:41 | 2023-04-23 21:42 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23042300155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 1746 | keep | 0 | Apr | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
VEGA BAJA | 2023-04-23 21:52 | 2023-04-24 01:00 | 100 | 3:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LINEAS | A23042300086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-04-23 | 18800 | keep | 0 | Apr | 2023 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-04-23 22:41 | 2023-04-24 08:35 | 15 | 9:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 25 EN TRANSFORMADOR SE REPARO BAJANTE DEL TRANSFORMADOR | A23042300091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 594 | 2023-04-23 | 8910 | keep | 0 | Apr | 2023 | 0.0060686 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-04-23 23:20 | 2023-04-24 00:40 | 97 | 1:20 | P | FUEGO | SE ABRE CORTE DE LINEA POR FUEGO EN POSTE SE RETIRO PARTE DE POSTE QUEMADO FUEGO FORRESTAL | P23042300172 | New_Event | Fire | Include | Include | Public | 80 | 2023-04-23 | 7760 | keep | 0 | Apr | 2023 | 0.0052853 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
BAYAMON | 2023-04-23 23:27 | 2023-04-23 23:28 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1713-04 LLEVA EL 75% DEL 1718-03 | B2304230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-23 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
BAYAMON | 2023-04-23 23:27 | 2023-04-23 23:28 | 1954 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1713-04 LLEVA EL 75% DEL 1718-03 | B2304230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-23 | 1954 | keep | 0 | Apr | 2023 | 0.0013309 | 0.0013309 | Momentary | FALSE | FALSE | Not_TMED_Event | 1954
MAYAGÃœEZ | 2023-04-23 23:35 | 2023-04-24 09:20 | 30 | 9:45 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23042300062 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 585 | 2023-04-23 | 17550 | keep | 0 | Apr | 2023 | 0.011953 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-24 00:39 | 2023-04-24 00:40 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23042400002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-04-24 01:10 | 2023-04-24 02:14 | 686 | 1:04 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR A PETICION DE JOSE CARRASQUILLO PARA SECCIONALIZAR Y TRABAJAR CONDICION DE PUENTE ABIERTO EN LOS MACHETES QUE SE ENCUENTRAN DESPUES DEL RISER DE SALIDA. | S23042400022 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 64 | 2023-04-24 | 43904 | keep | 0 | Apr | 2023 | 0.029903 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-24 01:21 | 2023-04-24 02:06 | 824 | 0:45 | P | ARBOL SOBRE LINEA | SE RETIRO RAMA Y ARBOL SOBRE LA LINEA 100% EN SERVICIO | B23042300575 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 45 | 2023-04-24 | 37080 | keep | 0 | Apr | 2023 | 0.025255 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-24 01:43 | 2023-04-24 03:01 | 20 | 1:18 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO TRAMO PARA REEMPLAZAR POSTE PRIMARIO BY-230424-01 | B23042400007 | New_Event | Primary Pole Failure | Include | Include | Equipment | 78 | 2023-04-24 | 1560 | keep | 0 | Apr | 2023 | 0.0010625 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-24 02:37 | 2023-04-24 02:38 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23042400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 4291 | keep | 0 | Apr | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-04-24 02:59 | 2023-04-24 04:59 | 1681 | 2:00 | T | DESGANCHE | SJ-230424-02 SE SECCIONALIZO ALIMENTADOR 1303-01 QUE LLEVA 1346-06 Y SE CERRO POR SCADA 5% EN SERVICIO | S23042400027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-04-24 | 201720 | keep | 0 | Apr | 2023 | 0.13739 | 0.0011449 | Sustained | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-04-24 02:59 | 2023-04-24 10:09 | 1598 | 7:10 | T | ALIMENTADOR AMARRADO | SJ-230424-02 LUEGO DE ABIERTO AMARRE SE REALIZO DESGANCHE EN ORIENTAL DE LA CARR. 177 Y SE CERRO AMARRE | S23042400027 | New_Event | Feeder Load Transferred | Include | Include | Other | 430 | 2023-04-24 | 687140 | keep | 0 | Apr | 2023 | 0.46801 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2023-04-24 03:01 | 2023-04-24 03:02 | 3941 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO BKR A PETICION DE HECTOR GIERBOLINI PARA RETIRAR PELIGRO, SE RETIRO EL CABLE DE ENCIMA DEL AUTO POR POSTE PARTIDO Y SE CERRO BKR NUEVAMENTE | B2304240000X | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-04-24 | 3941 | keep | 0 | Apr | 2023 | 0.0026842 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-24 03:02 | 2023-04-24 17:45 | 20 | 14:43 | P | ALIMENTADOR AMARRADO | SE SECCIONALIZO TRAMO PARA REEMPLAZAR POSTE PRIMARIO BY-230424-01 | B23042400007 | New_Event | Feeder Load Transferred | Include | Include | Other | 883 | 2023-04-24 | 17660 | keep | 0 | Apr | 2023 | 0.012028 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-24 03:22 | 2023-04-24 03:25 | 3387 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-24 | 10161 | keep | 0 | Apr | 2023 | 0.0069206 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2023-04-24 03:40 | 2023-04-24 03:43 | 215 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | B23042400013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-24 | 645 | keep | 0 | Apr | 2023 | 0.00043931 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-04-24 03:43 | 2023-04-24 14:00 | 48 | 10:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L | B23042400015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 617 | 2023-04-24 | 29616 | keep | 0 | Apr | 2023 | 0.020171 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
AGUADILLA | 2023-04-24 04:02 | 2023-04-24 06:55 | 400 | 2:53 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23042400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2023-04-24 | 69200 | keep | 0 | Apr | 2023 | 0.047132 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CAGUAS | 2023-04-24 04:16 | 2023-04-24 16:38 | 30 | 12:22 | P | DESGANCHE | 1 X 30 EN C/L | C23042400007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 742 | 2023-04-24 | 22260 | keep | 0 | Apr | 2023 | 0.015161 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-24 04:59 | 2023-04-24 05:35 | 1596 | 0:36 | P | DESGANCHE | SJ-230424-02 SE ABRE INTERRUPTOR POR SEGURIDAD A PETICION DE JOSE CARRASQUILLO(MACHETES INCOMODOS PARA CERRAR) | S23042400027 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-04-24 | 57456 | keep | 0 | Apr | 2023 | 0.039133 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-24 05:19 | 2023-04-24 05:20 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
SAN JUAN | 2023-04-24 05:35 | 2023-04-24 05:45 | 1681 | 0:10 | T | DESGANCHE | SJ-230424-02 SE ABRE INTERRUPTOR POR SEGURIDAD A PETICION DE JOSE CARRASQUILLO(MACHETES INCOMODOS PARA CERRAR), PROBO MALO SE VOLVIERON A ABRIR MACHETES Y SE CERRO POR SCADA 5% EN SERVICIO | S23042400027 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 10 | 2023-04-24 | 16810 | keep | 0 | Apr | 2023 | 0.011449 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-24 05:45 | 2023-04-24 08:16 | 1596 | 2:31 | P | DESGANCHE | SJ-230424-02 SE ABRE AMARRE CONTRA 1346-06 Y SE CIERRAN MACHETES ANTES ABIERTOS | S23042400027 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-04-24 | 240996 | keep | 0 | Apr | 2023 | 0.16414 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-24 05:50 | 2023-04-24 12:10 | 17 | 6:20 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYO Y 1 X 25 EN C/L | R23042400005 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 380 | 2023-04-24 | 6460 | keep | 0 | Apr | 2023 | 0.0043999 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2023-04-24 06:04 | 2023-04-24 06:05 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042400011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 676 | keep | 0 | Apr | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
VEGA BAJA | 2023-04-24 06:16 | 2023-04-24 16:00 | 75 | 9:44 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A23042400020 | New_Event | Primary Wire Break | Include | Include | Equipment | 584 | 2023-04-24 | 43800 | keep | 0 | Apr | 2023 | 0.029832 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-04-24 06:17 | 2023-04-24 06:18 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
PONCE | 2023-04-24 06:19 | 2023-04-24 07:45 | 15 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO VIENTOS | P23042400041 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2023-04-24 | 1290 | keep | 0 | Apr | 2023 | 0.00087861 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-24 06:37 | 2023-04-24 06:39 | 327 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-24 | 654 | keep | 0 | Apr | 2023 | 0.00044544 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BAYAMON | 2023-04-24 06:44 | 2023-04-24 06:45 | 1180 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 1180 | keep | 0 | Apr | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
GUAYAMA | 2023-04-24 06:49 | 2023-04-24 09:02 | 1 | 2:13 | P | ANIMAL | 2 X 15 EN XMR AVE CRUZO LINEAS | P23042400045 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-04-24 | 133 | keep | 0 | Apr | 2023 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-24 06:51 | 2023-04-24 11:04 | 3 | 4:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE REPARO ALAMBRE PRIMARIO | P23042400047 | New_Event | Primary Wire Break | Include | Include | Equipment | 253 | 2023-04-24 | 759 | keep | 0 | Apr | 2023 | 0.00051695 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-24 06:52 | 2023-04-24 18:15 | 11 | 11:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 50KVA X 50KVA | B23042400024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 683 | 2023-04-24 | 7513 | keep | 0 | Apr | 2023 | 0.0051171 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-04-24 06:55 | 2023-04-24 09:18 | 237 | 2:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN RISER Y 1 X 80 EN C/L MAL TIEMPO LLUVIA | R23042400010 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 143 | 2023-04-24 | 33891 | keep | 0 | Apr | 2023 | 0.023083 | 0.00016142 | Sustained | FALSE | FALSE | Not_TMED_Event | 237
FAJARDO | 2023-04-24 07:02 | 2023-04-24 09:57 | 51 | 2:55 | P | ANIMAL | 1 X 20 EN XMR Y 1 X 25 EN C/L CRUCE X AVE | R23042400012 | New_Event | Animals | Include | Include | Wildlife | 175 | 2023-04-24 | 8925 | keep | 0 | Apr | 2023 | 0.0060788 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
HUMACAO | 2023-04-24 07:12 | 2023-04-24 10:51 | 1 | 3:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L Y 2 SMU 20 DE 80A EN SU 11.4 LLUVIAS | C23042400016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 219 | 2023-04-24 | 219 | keep | 0 | Apr | 2023 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-24 07:15 | 2023-04-24 07:16 | 922 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO BKR 1401-08 QUE LLEVA 1346-05 | S2304240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-24 | 922 | keep | 0 | Apr | 2023 | 0.00062797 | 0.00062797 | Momentary | FALSE | FALSE | Not_TMED_Event | 922
SAN JUAN | 2023-04-24 07:15 | 2023-04-24 07:16 | 135 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO BKR 1401-08 QUE LLEVA 1346-05 | S2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 135 | keep | 0 | Apr | 2023 | 9.1948e-05 | 9.1948e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 135
SAN JUAN | 2023-04-24 07:16 | 2023-04-24 14:13 | 1 | 6:57 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | S23042400183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 417 | 2023-04-24 | 417 | keep | 0 | Apr | 2023 | 0.00028402 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-24 07:22 | 2023-04-24 07:23 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
VEGA BAJA | 2023-04-24 07:24 | 2023-04-25 11:30 | 50 | 28:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 50 EN CORTE DE LINEA SE REMPLAZARON AISLADORES ROTOS | A23042400028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1686 | 2023-04-24 | 84300 | keep | 0 | Apr | 2023 | 0.057416 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-24 07:32 | 2023-04-24 10:09 | 5 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA A LINEA | R23042400018 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2023-04-24 | 785 | keep | 0 | Apr | 2023 | 0.00053466 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-04-24 07:32 | 2023-04-24 07:33 | 4607 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23042400032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 4607 | keep | 0 | Apr | 2023 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
CANOVANAS | 2023-04-24 07:46 | 2023-04-24 10:47 | 135 | 3:01 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23042400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-04-24 | 24435 | keep | 0 | Apr | 2023 | 0.016643 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
BARRANQUITAS | 2023-04-24 07:51 | 2023-04-24 15:26 | 12 | 7:35 | P | DESGANCHE | 1 X 30 EN C/L | C23042400025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2023-04-24 | 5460 | keep | 0 | Apr | 2023 | 0.0037188 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-04-24 08:09 | 2023-04-24 11:20 | 6 | 3:11 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN XMR REMPLAZO PARARRAYO Y BAJANTE | C23042400027 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 191 | 2023-04-24 | 1146 | keep | 0 | Apr | 2023 | 0.00078054 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-04-24 08:09 | 2023-04-24 11:20 | 11 | 3:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIAS | C23042400028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 191 | 2023-04-24 | 2101 | keep | 0 | Apr | 2023 | 0.001431 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-04-24 08:10 | 2023-04-24 12:49 | 40 | 4:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO LLUVIAS | S23042400026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 279 | 2023-04-24 | 11160 | keep | 0 | Apr | 2023 | 0.007601 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-24 08:10 | 2023-04-25 11:35 | 6 | 27:25 | P | SOBRECARGA | 1 X 15 EN XMR POR CARGA | B23042400041 | New_Event | Trip Due To Overload | Include | Include | Other | 1645 | 2023-04-24 | 9870 | keep | 0 | Apr | 2023 | 0.0067224 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-04-24 08:14 | 2023-04-24 10:32 | 30 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO VIENTOS | P23042400063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2023-04-24 | 4140 | keep | 0 | Apr | 2023 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-04-24 08:17 | 2023-04-24 11:21 | 100 | 3:04 | P | ANIMAL | 1 X100 EN C/L AVE CRUZO LINEAS | P23042400064 | New_Event | Animals | Include | Include | Wildlife | 184 | 2023-04-24 | 18400 | keep | 0 | Apr | 2023 | 0.012532 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-24 08:20 | 2023-04-24 10:37 | 400 | 2:17 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | B23042400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-04-24 | 54800 | keep | 0 | Apr | 2023 | 0.037324 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-04-24 08:20 | 2023-04-24 12:15 | 1 | 3:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | B23042400047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 235 | 2023-04-24 | 235 | keep | 0 | Apr | 2023 | 0.00016006 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-24 08:28 | 2023-04-24 09:27 | 2435 | 0:59 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE BKR SE SECCIONALIZO EL ALIMENTADOR | C23042400038 | New_Event | Cutout Failure | Include | Include | Equipment | 59 | 2023-04-24 | 143665 | keep | 0 | Apr | 2023 | 0.09785 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
MAYAGÃœEZ | 2023-04-24 08:32 | 2023-04-24 08:33 | 1352 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR RAMA SOBRE LINEAS LLEVA LA CARGA DEL 6014-03 | M23042400032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-24 | 1352 | keep | 0 | Apr | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-04-24 08:32 | 2023-04-24 08:33 | 871 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL INTERRUPTOR 6012-05 EL CUAL LLEVA LA CARGA DEL 6014-03 | M23042400032 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-24 | 871 | keep | 0 | Apr | 2023 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
MAYAGÃœEZ | 2023-04-24 08:33 | 2023-04-24 12:15 | 80 | 3:42 | P | DESGANCHE | 1 X 100 Y 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23042400012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-04-24 | 17760 | keep | 0 | Apr | 2023 | 0.012096 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-24 08:35 | 2023-04-24 13:01 | 15 | 4:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN C/L MAL TIEMPO LLUVIA | R23042400032 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 266 | 2023-04-24 | 3990 | keep | 0 | Apr | 2023 | 0.0027176 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-24 08:39 | 2023-04-24 08:40 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304240000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
GUAYAMA | 2023-04-24 08:44 | 2023-04-24 09:14 | 4132 | 0:30 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO CARGA A BKR 4003-02 BKR DEFECTUOSO | P23042400071 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 30 | 2023-04-24 | 123960 | keep | 0 | Apr | 2023 | 0.084429 | 0.0028143 | Sustained | FALSE | FALSE | Not_TMED_Event | 4132
BAYAMON | 2023-04-24 08:53 | 2023-04-24 13:19 | 16 | 4:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042400053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 266 | 2023-04-24 | 4256 | keep | 0 | Apr | 2023 | 0.0028987 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-04-24 08:58 | 2023-04-24 09:30 | 5 | 0:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23042300165 | New_Event | Secondary Wire Break | Include | Include | Equipment | 32 | 2023-04-24 | 160 | keep | 0 | Apr | 2023 | 0.00010898 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-04-24 09:04 | 2023-04-24 21:10 | 50 | 12:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN CORTE DE LINEA | A23042400050 | New_Event | Cutout Failure | Include | Include | Equipment | 726 | 2023-04-24 | 36300 | keep | 0 | Apr | 2023 | 0.024724 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-24 09:07 | 2023-04-26 18:15 | 1 | 57:08 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR SE RETIRO NIDO DE AVE RELACIONADO AVENTO A23042600143 | A23042400052 | New_Event | Animals | Include | Include | Wildlife | 3428 | 2023-04-24 | 3428 | keep | 0 | Apr | 2023 | 0.0023348 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-24 09:08 | 2023-04-24 12:18 | 63 | 3:10 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23042400063 | New_Event | Animals | Include | Include | Wildlife | 190 | 2023-04-24 | 11970 | keep | 0 | Apr | 2023 | 0.0081527 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CAGUAS | 2023-04-24 09:16 | 2023-04-24 19:25 | 20 | 10:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C23042400066 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 609 | 2023-04-24 | 12180 | keep | 0 | Apr | 2023 | 0.0082957 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-24 09:25 | 2023-04-24 14:45 | 103 | 5:20 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23042400069 | New_Event | Animals | Include | Include | Wildlife | 320 | 2023-04-24 | 32960 | keep | 0 | Apr | 2023 | 0.022449 | 7.0153e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 103
BARRANQUITAS | 2023-04-24 09:27 | 2023-04-24 16:00 | 487 | 6:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA Y CRUCETA PARTIDA Y AISLADORES | C23042400038 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 393 | 2023-04-24 | 191391 | keep | 0 | Apr | 2023 | 0.13036 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-24 09:27 | 2023-04-24 11:53 | 6 | 2:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRAS EN PEDESTAL Y SE REPARO SECUNDARIA | P23042400084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 146 | 2023-04-24 | 876 | keep | 0 | Apr | 2023 | 0.00059664 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-04-24 09:34 | 2023-04-24 14:03 | 1 | 4:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 100 EN C/L SE REMPLAZO CAJA QUEMADA | C23042400079 | New_Event | Cutout Failure | Include | Include | Equipment | 269 | 2023-04-24 | 269 | keep | 0 | Apr | 2023 | 0.00018321 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-24 09:35 | 2023-04-24 12:19 | 40 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23042400087 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2023-04-24 | 6560 | keep | 0 | Apr | 2023 | 0.004468 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-04-24 09:37 | 2023-04-24 09:47 | 6 | 0:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | R23042400049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 10 | 2023-04-24 | 60 | keep | 0 | Apr | 2023 | 4.0866e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-24 09:46 | 2023-04-24 13:29 | 253 | 3:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SJ-230424-05 SE SECCIONALIZO CAJAS QUEMADAS EN PUEBLO DE RIO PIEDRAS Y SE ENERGIZO BAJA DE PORTATIL, LUEGO SE REMPLAZARON CAJAS Y SE CERRO MACHETES | S23042400365 | New_Event | Cutout Failure | Include | Include | Equipment | 223 | 2023-04-24 | 56419 | keep | 0 | Apr | 2023 | 0.038427 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
SAN JUAN | 2023-04-24 09:46 | 2023-04-24 12:05 | 1290 | 2:19 | S | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SJ-230424-05 SE SECCIONALIZO CAJAS QUEMADAS EN PUEBLO DE RIO PIEDRAS Y SE ENERGIZO BAJA DE PORTATIL | S23042400365 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2023-04-24 | 179310 | keep | 0 | Apr | 2023 | 0.12213 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
CANOVANAS | 2023-04-24 09:49 | 2023-04-24 10:37 | 3699 | 0:48 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE BKR HIZO LAS TRES OPERACIONES SE DEJO FUERA SE SECCIONALIZO CON SJ-230424-50 AISLADOR ROTO Y CAJA PRIMARIA QUEMADA EN RISER ENTRO UN 85% EN SERVICIO | R23042400053 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2023-04-24 | 177552 | keep | 0 | Apr | 2023 | 0.12093 | 0.0025194 | Sustained | FALSE | FALSE | Not_TMED_Event | 3699
CAGUAS | 2023-04-24 09:53 | 2023-04-24 17:41 | 30 | 7:48 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23042400090 | New_Event | Animals | Include | Include | Wildlife | 468 | 2023-04-24 | 14040 | keep | 0 | Apr | 2023 | 0.0095626 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-24 10:01 | 2023-04-24 17:03 | 50 | 7:02 | P | DESGANCHE | 1 X 50 EN C/L Y 1 X 10 EN XMR | C23042400093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 422 | 2023-04-24 | 21100 | keep | 0 | Apr | 2023 | 0.014371 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-24 10:14 | 2023-04-24 10:15 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042400101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 906 | keep | 0 | Apr | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
BAYAMON | 2023-04-24 10:23 | 2023-04-24 11:37 | 3070 | 1:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 25 EN BANCO DE XMR | B23042400081 | New_Event | Cutout Failure | Include | Include | Equipment | 74 | 2023-04-24 | 227180 | keep | 0 | Apr | 2023 | 0.15473 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
SAN JUAN | 2023-04-24 10:24 | 2023-04-24 17:31 | 106 | 7:07 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO CONDUCTOR EN EL SUELO | S23042400395 | New_Event | Primary Wire Break | Include | Include | Equipment | 427 | 2023-04-24 | 45262 | keep | 0 | Apr | 2023 | 0.030828 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
BAYAMON | 2023-04-24 10:34 | 2023-04-24 10:36 | 3798 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23042400085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-24 | 7596 | keep | 0 | Apr | 2023 | 0.0051736 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
PONCE | 2023-04-24 10:35 | 2023-04-24 12:18 | 80 | 1:43 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23042400118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 103 | 2023-04-24 | 8240 | keep | 0 | Apr | 2023 | 0.0056122 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-24 10:37 | 2023-04-24 13:08 | 554 | 2:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO AISLADOR ROTO CON SJ-230424-50 ENTRO UN 15% EN SERVICIO QUE FALTABA. 3 X 65 EN RISER Y SE REEMPLAZO CAJA PRIMARIA EN RISER | R23042400053 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2023-04-24 | 83654 | keep | 0 | Apr | 2023 | 0.056976 | 0.00037733 | Sustained | FALSE | FALSE | Not_TMED_Event | 554
AGUADILLA | 2023-04-24 10:38 | 2023-04-24 12:25 | 12 | 1:47 | P | ANIMAL | 1 X 5 EN TRANSFORMADOR AVE CRUZO LINEAS | M23042400049 | New_Event | Animals | Include | Include | Wildlife | 107 | 2023-04-24 | 1284 | keep | 0 | Apr | 2023 | 0.00087453 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-04-24 10:41 | 2023-04-24 19:55 | 5 | 9:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA SE CERRO CORTE DE LINEA | A23042400091 | New_Event | Primary Wire Break | Include | Include | Equipment | 554 | 2023-04-24 | 2770 | keep | 0 | Apr | 2023 | 0.0018866 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-24 10:44 | 2023-04-24 11:30 | 1 | 0:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | B23042400088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 46 | 2023-04-24 | 46 | keep | 0 | Apr | 2023 | 3.133e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-04-24 10:52 | 2023-04-24 10:53 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23042400056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 179 | keep | 0 | Apr | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2023-04-24 10:59 | 2023-04-24 13:44 | 7 | 2:45 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y DESGANCHE SECUNDARIO | B23042400090 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 165 | 2023-04-24 | 1155 | keep | 0 | Apr | 2023 | 0.00078667 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-04-24 11:03 | 2023-04-24 11:09 | 327 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO CERRADO X CONTROL | C2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-24 | 1962 | keep | 0 | Apr | 2023 | 0.0013363 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
FAJARDO | 2023-04-24 11:08 | 2023-04-24 14:00 | 120 | 2:52 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23042400081 | New_Event | Animals | Include | Include | Wildlife | 172 | 2023-04-24 | 20640 | keep | 0 | Apr | 2023 | 0.014058 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2023-04-24 11:09 | 2023-04-24 17:30 | 18 | 6:21 | P | DESGANCHE | 1 X 100 , 1 X 65 EN CORTES DE LINEA DESGANCHE | B23042400095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2023-04-24 | 6858 | keep | 0 | Apr | 2023 | 0.004671 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
UTUADO | 2023-04-24 11:22 | 2023-04-25 11:15 | 2 | 23:53 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042400104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1433 | 2023-04-24 | 2866 | keep | 0 | Apr | 2023 | 0.001952 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-04-24 11:23 | 2023-04-24 12:50 | 18 | 1:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN C/L QUEMADA | P23042400136 | New_Event | Cutout Failure | Include | Include | Equipment | 87 | 2023-04-24 | 1566 | keep | 0 | Apr | 2023 | 0.0010666 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2023-04-24 11:27 | 2023-04-24 17:00 | 9 | 5:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23042400140 | New_Event | Secondary Wire Break | Include | Include | Equipment | 333 | 2023-04-24 | 2997 | keep | 0 | Apr | 2023 | 0.0020412 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-04-24 11:31 | 2023-04-24 12:08 | 1 | 0:37 | P | ANIMAL | 1 X 50 EN RISER CRUCE POR RATA | B23042400104 | New_Event | Animals | Include | Include | Wildlife | 37 | 2023-04-24 | 37 | keep | 0 | Apr | 2023 | 2.5201e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-24 11:39 | 2023-04-25 07:08 | 1 | 19:29 | P | ANIMAL | 1 X 15 EN BANCO XMR AVE CRUZO LINEAS | C23042400134 | New_Event | Animals | Include | Include | Wildlife | 1169 | 2023-04-24 | 1169 | keep | 0 | Apr | 2023 | 0.0007962 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-24 11:43 | 2023-04-24 12:35 | 1 | 0:52 | P | ANIMAL | 2 X 15 EN XMR AVE CRUZO LINEAS | P23042400150 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-04-24 | 52 | keep | 0 | Apr | 2023 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-24 11:47 | 2023-04-24 16:23 | 8 | 4:36 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR SECUNDARIA Y TOMAS AVERIADAS X CAMION | C23042400135 | New_Event | Damage From Public | Include | Include | Public | 276 | 2023-04-24 | 2208 | keep | 0 | Apr | 2023 | 0.0015039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-24 12:05 | 2023-04-24 15:19 | 60 | 3:14 | P | NO SE REPORTO CAUSA | 1 X 50 RBA | S23042301212 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 194 | 2023-04-24 | 11640 | keep | 0 | Apr | 2023 | 0.007928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-24 12:07 | 2023-04-24 13:00 | 100 | 0:53 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | P23042400161 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-04-24 | 5300 | keep | 0 | Apr | 2023 | 0.0036098 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-24 12:30 | 2023-04-24 15:35 | 100 | 3:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 1 X 80 1 X 65 Y 1 X 40 EN C/L SE REEMPLAZO AISLADOR Y DESGANCHE | R23042400092 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 185 | 2023-04-24 | 18500 | keep | 0 | Apr | 2023 | 0.0126 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-04-24 12:33 | 2023-04-24 13:00 | 50 | 0:27 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | P23042400165 | New_Event | Animals | Include | Include | Wildlife | 27 | 2023-04-24 | 1350 | keep | 0 | Apr | 2023 | 0.00091948 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-24 12:38 | 2023-04-25 12:16 | 1 | 23:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA EN PEDESTAL | S23042400466 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1418 | 2023-04-24 | 1418 | keep | 0 | Apr | 2023 | 0.00096579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-24 12:38 | 2023-04-25 09:36 | 10 | 20:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23042400141 | New_Event | Primary Wire Break | Include | Include | Equipment | 1258 | 2023-04-24 | 12580 | keep | 0 | Apr | 2023 | 0.0085682 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-24 12:47 | 2023-04-25 14:19 | 30 | 25:32 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23042400471 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1532 | 2023-04-24 | 45960 | keep | 0 | Apr | 2023 | 0.031303 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-24 12:52 | 2023-04-25 09:28 | 25 | 20:36 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23042400153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1236 | 2023-04-24 | 30900 | keep | 0 | Apr | 2023 | 0.021046 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-04-24 12:59 | 2023-04-24 15:00 | 1 | 2:01 | P | NO SE REPORTO CAUSA | 2 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23042400147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 121 | 2023-04-24 | 121 | keep | 0 | Apr | 2023 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-24 13:07 | 2023-04-24 19:54 | 63 | 6:47 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23042400126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 407 | 2023-04-24 | 25641 | keep | 0 | Apr | 2023 | 0.017464 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
SAN JUAN | 2023-04-24 13:08 | 2023-04-24 15:03 | 4 | 1:55 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | S23042400480 | New_Event | Vegetation Contact | Include | Include | Vegetation | 115 | 2023-04-24 | 460 | keep | 0 | Apr | 2023 | 0.0003133 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-04-24 13:12 | 2023-04-24 15:24 | 40 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042400088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-04-24 | 5280 | keep | 0 | Apr | 2023 | 0.0035962 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-24 13:13 | 2023-04-24 14:02 | 25 | 0:49 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE LEVANTO CUNDUCTOR | B23042400097 | New_Event | Primary Wire Break | Include | Include | Equipment | 49 | 2023-04-24 | 1225 | keep | 0 | Apr | 2023 | 0.00083434 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-04-24 13:15 | 2023-04-24 15:33 | 2708 | 2:18 | S | ANIMAL | DISPARO DEL BKR DE ALTA 0010, LA CAUSA FUE AVE CRUZO BARRA DE DISTRIBUCION EN LA CAJA DE MEDICION REMOTA | R23042400106 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-04-24 | 373704 | keep | 0 | Apr | 2023 | 0.25453 | 0.0018444 | Sustained | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-04-24 13:15 | 2023-04-24 15:33 | 2524 | 2:18 | S | ANIMAL | DISPARO DEL BKR DE ALTA, LA CAUSA FUE AVE CRUZO BARRA DE DISTRIBUCION EN LA CAJA DE MEDICION REMOTA | R23042400106 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-04-24 | 348312 | keep | 0 | Apr | 2023 | 0.23723 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2023-04-24 13:15 | 2023-04-24 15:33 | 1648 | 2:18 | S | ANIMAL | DISPARO DEL BKR DE ALTA, LA CAUSA FUE AVE CRUZO BARRA DE DISTRIBUCION EN LA CAJA DE MEDICION REMOTA | R23042400106 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-04-24 | 227424 | keep | 0 | Apr | 2023 | 0.1549 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
SAN JUAN | 2023-04-24 13:19 | 2023-04-25 17:20 | 95 | 28:01 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN EL SU-6 Y SE ENERGIZO 100% EN SERVICIO | S23042400483 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1681 | 2023-04-24 | 159695 | keep | 0 | Apr | 2023 | 0.10877 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
SAN JUAN | 2023-04-24 13:28 | 2023-04-25 12:57 | 100 | 23:29 | P | CONDUCTOR ROTO O ABIERTO | SJ-230425-01 SE CERRO PUENTE ABIERTO Y SE NORMALIZO CARGA | S23042400487 | New_Event | Primary Wire Break | Include | Include | Equipment | 1409 | 2023-04-24 | 140900 | keep | 0 | Apr | 2023 | 0.095966 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-24 13:31 | 2023-04-24 17:19 | 21 | 3:48 | P | DESGANCHE | 1 X 100 EN C/L 1 X 20 EN XMR DESGANCHE | S23042400934 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-04-24 | 4788 | keep | 0 | Apr | 2023 | 0.0032611 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
PONCE | 2023-04-24 13:32 | 2023-04-24 15:00 | 40 | 1:28 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23042400183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-04-24 | 3520 | keep | 0 | Apr | 2023 | 0.0023975 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-24 13:49 | 2023-04-24 17:55 | 150 | 4:06 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN RISER SE REEMPLAZO PIN POLE TOP | R23042400122 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 246 | 2023-04-24 | 36900 | keep | 0 | Apr | 2023 | 0.025132 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-24 14:10 | 2023-04-25 10:29 | 15 | 20:19 | P | ANIMAL | 1 X 20 EN XMR CRUCE POR AVE | S23042400503 | New_Event | Animals | Include | Include | Wildlife | 1219 | 2023-04-24 | 18285 | keep | 0 | Apr | 2023 | 0.012454 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-04-24 14:12 | 2023-04-24 14:41 | 45 | 0:29 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23042400169 | New_Event | Animals | Include | Include | Wildlife | 29 | 2023-04-24 | 1305 | keep | 0 | Apr | 2023 | 0.00088883 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-04-24 14:17 | 2023-04-24 16:52 | 300 | 2:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 200 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042400107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 155 | 2023-04-24 | 46500 | keep | 0 | Apr | 2023 | 0.031671 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-04-24 14:30 | 2023-04-25 18:27 | 8 | 27:57 | P | DESGANCHE | SE ABRIO TRANSFORMADOR SE HIZO DESGANCHE TRASPATIO, SE REPARARON CONECTORES EN BAJANTE SECUNDARIOS DE XMR | S23042400510 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1677 | 2023-04-24 | 13416 | keep | 0 | Apr | 2023 | 0.0091376 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-24 14:30 | 2023-04-24 14:32 | 271 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | S2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-24 | 542 | keep | 0 | Apr | 2023 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BARRANQUITAS | 2023-04-24 14:35 | 2023-04-24 16:47 | 1017 | 2:12 | T | CAUSAS EXTERNAS | SE SECCIONALIZO EL ALIMENTADOR | C23042400178 | New_Event | Damage From Public | Include | Include | Public | 132 | 2023-04-24 | 134244 | keep | 0 | Apr | 2023 | 0.091433 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
AGUADILLA | 2023-04-24 14:40 | 2023-04-24 16:30 | 12 | 1:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23042400099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 110 | 2023-04-24 | 1320 | keep | 0 | Apr | 2023 | 0.00089905 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-04-24 14:45 | 2023-04-24 16:03 | 100 | 1:18 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | R23042400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-04-24 | 7800 | keep | 0 | Apr | 2023 | 0.0053125 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-24 15:13 | 2023-04-24 20:06 | 108 | 4:53 | P | DESGANCHE | 1 X 65 EN C/L | C23042400194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-04-24 | 31644 | keep | 0 | Apr | 2023 | 0.021553 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
VEGA BAJA | 2023-04-24 15:37 | 2023-04-24 17:00 | 50 | 1:23 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A23042400193 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 83 | 2023-04-24 | 4150 | keep | 0 | Apr | 2023 | 0.0028265 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-04-24 15:50 | 2023-04-25 12:15 | 1 | 20:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23042540139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1225 | 2023-04-24 | 1225 | keep | 0 | Apr | 2023 | 0.00083434 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-24 15:59 | 2023-04-25 13:00 | 22 | 21:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIO | S23042400563 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1261 | 2023-04-24 | 27742 | keep | 0 | Apr | 2023 | 0.018895 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2023-04-24 16:05 | 2023-04-24 17:41 | 8 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRA DE PEDESTAL | C23042400212 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-04-24 | 768 | keep | 0 | Apr | 2023 | 0.00052308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-04-24 16:08 | 2023-04-24 19:32 | 1 | 3:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23042400216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2023-04-24 | 204 | keep | 0 | Apr | 2023 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-24 16:22 | 2023-04-24 18:38 | 134 | 2:16 | P | DESGANCHE | 1 X 65 Y 1 X 80 EN C/LS | C23042400221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-04-24 | 18224 | keep | 0 | Apr | 2023 | 0.012412 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BAYAMON | 2023-04-24 16:27 | 2023-04-24 17:59 | 1 | 1:32 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23042400165 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-04-24 | 92 | keep | 0 | Apr | 2023 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-24 16:32 | 2023-04-24 17:15 | 1 | 0:43 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23042400235 | New_Event | Primary Wire Break | Include | Include | Equipment | 43 | 2023-04-24 | 43 | keep | 0 | Apr | 2023 | 2.9287e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-24 16:45 | 2023-04-24 17:45 | 30 | 1:00 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA REALIZAR DESGANCHE | M23042400146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2023-04-24 | 1800 | keep | 0 | Apr | 2023 | 0.001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-24 16:47 | 2023-04-24 17:26 | 203 | 0:39 | P | CAUSAS EXTERNAS | SE DESPEGO POSTE DE COMUNICACIONES DE LINEA PRIMARIA | C23042400178 | Partial_restoration | Damage From Public | Include | Include | Public | 39 | 2023-04-24 | 7917 | keep | 0 | Apr | 2023 | 0.0053922 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-04-24 16:50 | 2023-04-25 16:39 | 50 | 23:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIAS | C23042500234 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1429 | 2023-04-24 | 71450 | keep | 0 | Apr | 2023 | 0.048664 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-24 17:06 | 2023-04-24 18:34 | 1 | 1:28 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23042400188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-04-24 | 88 | keep | 0 | Apr | 2023 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-24 17:19 | 2023-04-24 18:39 | 75 | 1:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO LLUVIAS | P23042400248 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 80 | 2023-04-24 | 6000 | keep | 0 | Apr | 2023 | 0.0040866 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-04-24 17:25 | 2023-04-24 18:56 | 25 | 1:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042400172 | New_Event | Secondary Wire Break | Include | Include | Equipment | 91 | 2023-04-24 | 2275 | keep | 0 | Apr | 2023 | 0.0015495 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-24 17:29 | 2023-04-25 10:36 | 9 | 17:07 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23042400173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1027 | 2023-04-24 | 9243 | keep | 0 | Apr | 2023 | 0.0062954 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-04-24 17:31 | 2023-04-24 18:19 | 321 | 0:48 | P | CONDUCTOR ROTO O ABIERTO | SJ230424-07 SE SECCIONALIZO PARA ABRIR PUENTES PRIMARIO Y SECCIONALIZAR CONDUCTOR PRIMARIO EN EL SUELO TRASPATIO Y SE CERRO N/O CONTRA 1345-05 | S23042400395 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 48 | 2023-04-24 | 15408 | keep | 0 | Apr | 2023 | 0.010494 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-24 17:36 | 2023-04-25 10:44 | 10 | 17:08 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO LINEAS | A23042400207 | New_Event | Animals | Include | Include | Wildlife | 1028 | 2023-04-24 | 10280 | keep | 0 | Apr | 2023 | 0.0070017 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-24 17:50 | 2023-04-24 22:45 | 60 | 4:55 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23042400157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2023-04-24 | 17700 | keep | 0 | Apr | 2023 | 0.012055 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-04-24 17:55 | 2023-04-24 18:00 | 30 | 0:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE REPARO ALAMBRE PRIMARIO | P23042400262 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2023-04-24 | 150 | keep | 0 | Apr | 2023 | 0.00010216 | 2.0433e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-24 18:03 | 2023-04-24 18:08 | 2842 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C23042400250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-24 | 14210 | keep | 0 | Apr | 2023 | 0.0096784 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CANOVANAS | 2023-04-24 18:04 | 2023-04-24 20:10 | 30 | 2:06 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23042400206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-04-24 | 3780 | keep | 0 | Apr | 2023 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-24 18:06 | 2023-04-24 19:19 | 45 | 1:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23042400161 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2023-04-24 | 3285 | keep | 0 | Apr | 2023 | 0.0022374 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-04-24 18:07 | 2023-04-24 20:52 | 42 | 2:45 | P | DESGANCHE | 1 X 40 EN C/L | C23042400253 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-04-24 | 6930 | keep | 0 | Apr | 2023 | 0.00472 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2023-04-24 18:19 | 2023-04-25 17:44 | 9 | 23:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR PRIMARIO, PUENTE ABIERTO Y DESGANCHE MASIVO | S23042400395 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1405 | 2023-04-24 | 12645 | keep | 0 | Apr | 2023 | 0.0086125 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-04-24 18:38 | 2023-04-24 20:27 | 94 | 1:49 | P | DESGANCHE | 1 X 50 EN C/L | C23042400264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-04-24 | 10246 | keep | 0 | Apr | 2023 | 0.0069785 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
CANOVANAS | 2023-04-24 18:57 | 2023-04-24 20:46 | 50 | 1:49 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23042400216 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-04-24 | 5450 | keep | 0 | Apr | 2023 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-24 19:08 | 2023-04-24 21:04 | 10 | 1:56 | P | DESGANCHE | 2 X 20 EN C/L DESGANCHE | R23042400219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-04-24 | 1160 | keep | 0 | Apr | 2023 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-24 19:14 | 2023-04-24 19:15 | 1243 | 0:01 | P | NO SE REPORTO CAUSA | LLEVA 90% 1204-03 RECIERRE DE BKR | S2304240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-24 | 1243 | keep | 0 | Apr | 2023 | 0.0008466 | 0.0008466 | Momentary | FALSE | FALSE | Not_TMED_Event | 1243
YAUCO | 2023-04-24 19:17 | 2023-04-24 20:50 | 20 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO VIENTOS | P23042400271 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-04-24 | 1860 | keep | 0 | Apr | 2023 | 0.0012668 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-24 19:19 | 2023-04-24 20:23 | 2 | 1:04 | P | DESGANCHE | 1 X 30 EN C/L | C23042400266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-04-24 | 128 | keep | 0 | Apr | 2023 | 8.718e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-04-24 19:29 | 2023-04-25 11:58 | 6 | 16:29 | P | ANIMAL | 1 X 15 EN XMR CULEBRA CRUZO LINEAS | B23042400188 | New_Event | Animals | Include | Include | Wildlife | 989 | 2023-04-24 | 5934 | keep | 0 | Apr | 2023 | 0.0040416 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-04-24 19:30 | 2023-04-25 12:13 | 67 | 16:43 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23042400268 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1003 | 2023-04-24 | 67201 | keep | 0 | Apr | 2023 | 0.04577 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
GUAYAMA | 2023-04-24 19:33 | 2023-04-24 21:36 | 20 | 2:03 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYOS | P23042400275 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 123 | 2023-04-24 | 2460 | keep | 0 | Apr | 2023 | 0.0016755 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-24 19:36 | 2023-04-25 10:42 | 1 | 15:06 | P | ANIMAL | 2 X 50 EN RISER SE REEMPLAZARON DOS CAJAS PRIMARIAS CRUCE POR AVE | R23042400225 | New_Event | Animals | Include | Include | Wildlife | 906 | 2023-04-24 | 906 | keep | 0 | Apr | 2023 | 0.00061707 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-24 19:40 | 2023-04-25 14:31 | 8 | 18:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 37.5 KVA POR 50 KVA | S23042400654 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1131 | 2023-04-24 | 9048 | keep | 0 | Apr | 2023 | 0.0061626 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-24 19:43 | 2023-04-25 09:58 | 10 | 14:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE DESGANCHO Y SE REPARO SECUNDARIA. | S23042400662 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 855 | 2023-04-24 | 8550 | keep | 0 | Apr | 2023 | 0.0058234 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-24 20:09 | 2023-04-24 22:34 | 376 | 2:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | S23042400667 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2023-04-24 | 54520 | keep | 0 | Apr | 2023 | 0.037133 | 0.00025609 | Sustained | FALSE | FALSE | Not_TMED_Event | 376
HUMACAO | 2023-04-24 20:40 | 2023-04-24 22:58 | 120 | 2:18 | P | ANIMAL | 1 X 100 EN C/L CRUCE X LAGARTO | C23042400282 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-04-24 | 16560 | keep | 0 | Apr | 2023 | 0.011279 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-04-24 20:40 | 2023-04-25 09:50 | 80 | 13:10 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO | M23042400178 | New_Event | Primary Wire Break | Include | Include | Equipment | 790 | 2023-04-24 | 63200 | keep | 0 | Apr | 2023 | 0.043045 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-24 21:19 | 2023-04-24 21:42 | 90 | 0:23 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23042400296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-04-24 | 2070 | keep | 0 | Apr | 2023 | 0.0014099 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-04-24 22:20 | 2023-04-24 23:52 | 603 | 1:32 | T | ALIMENTADOR AMARRADO | RECERRO 3 VECES QUEDO ABIERTO SE ABRIO N/O 9206-08 Y 9 Y SE CERRO INTERRUPTOR 9206-08 QUEDO EN SERVICIO CONTINUA FUERA 9206-09 | B23042400202 | New_Event | Feeder Load Transferred | Include | Include | Other | 92 | 2023-04-24 | 55476 | keep | 0 | Apr | 2023 | 0.037784 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-04-24 22:20 | 2023-04-25 19:09 | 6 | 20:49 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO TRAMO Y SE REPARO AVERIA EN VS-07 BY-230424-03 | B23042400202 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1249 | 2023-04-24 | 7494 | keep | 0 | Apr | 2023 | 0.0051041 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-04-24 22:21 | 2023-04-25 09:20 | 100 | 10:59 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042400232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 659 | 2023-04-24 | 65900 | keep | 0 | Apr | 2023 | 0.044884 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-04-24 22:24 | 2023-04-25 08:10 | 15 | 9:46 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA | A23042400233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 586 | 2023-04-24 | 8790 | keep | 0 | Apr | 2023 | 0.0059868 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-24 22:40 | 2023-04-25 09:04 | 66 | 10:24 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23042400205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 624 | 2023-04-24 | 41184 | keep | 0 | Apr | 2023 | 0.02805 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
SAN JUAN | 2023-04-24 23:02 | 2023-04-25 09:03 | 30 | 10:01 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23042400695 | New_Event | Vegetation Contact | Include | Include | Vegetation | 601 | 2023-04-24 | 18030 | keep | 0 | Apr | 2023 | 0.01228 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-25 00:17 | 2023-04-25 00:19 | 1565 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23042500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-25 | 3130 | keep | 0 | Apr | 2023 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
CANOVANAS | 2023-04-25 00:18 | 2023-04-25 09:07 | 5 | 8:49 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | R23042500001 | New_Event | Animals | Include | Include | Wildlife | 529 | 2023-04-25 | 2645 | keep | 0 | Apr | 2023 | 0.0018015 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-04-25 01:12 | 2023-04-25 01:13 | 603 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR REALIZANDO OPERACIONES CONTRA 9206-09 TRAMO AVERIADO SU-1 A SU-1A | B23042500001 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-25 | 603 | keep | 0 | Apr | 2023 | 0.0004107 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-25 01:32 | 2023-04-25 03:25 | 26 | 1:53 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L PARA ABRIR PUENTE Y SECCIONALIZAR POSTE PRIMARIO PARTIDO Y SE CERRO C/L | R23042500003 | New_Event | Primary Pole Failure | Include | Include | Equipment | 113 | 2023-04-25 | 2938 | keep | 0 | Apr | 2023 | 0.0020011 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BAYAMON | 2023-04-25 02:02 | 2023-04-25 02:03 | 603 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR REALIZANDO MANIOBRAS ABRIENDO DE V.S.MH-7 A SU-1 Y CERRANDO N/O 9206-8 Y 9 SE ABRIO Y SE DEJO FUERA PARA PERSONAL VERIFIQUE SOTERRADO | B23042500004 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-25 | 603 | keep | 0 | Apr | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
SAN JUAN | 2023-04-25 02:47 | 2023-04-25 02:48 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | S23042500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
PONCE | 2023-04-25 03:13 | 2023-04-25 03:14 | 396 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23042500003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 396 | keep | 0 | Apr | 2023 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
CANOVANAS | 2023-04-25 03:25 | 2023-04-25 15:58 | 10 | 12:33 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO, SE LEVANTO CONDUCTORES PRIMARIOS Y SECUNDARIA | R23042500005 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 753 | 2023-04-25 | 7530 | keep | 0 | Apr | 2023 | 0.0051286 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-04-25 04:30 | 2023-04-25 09:20 | 150 | 4:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042500001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 290 | 2023-04-25 | 43500 | keep | 0 | Apr | 2023 | 0.029628 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-04-25 04:51 | 2023-04-25 04:52 | 1026 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23042500006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
SAN JUAN | 2023-04-25 05:20 | 2023-04-25 05:22 | 255 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO | S23042500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-25 | 510 | keep | 0 | Apr | 2023 | 0.00034736 | 0.00017368 | Momentary | FALSE | FALSE | Not_TMED_Event | 255
UTUADO | 2023-04-25 05:21 | 2023-04-25 19:00 | 25 | 13:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23042500003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 819 | 2023-04-25 | 20475 | keep | 0 | Apr | 2023 | 0.013945 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-25 06:06 | 2023-04-25 14:22 | 120 | 8:16 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | C23042500007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 496 | 2023-04-25 | 59520 | keep | 0 | Apr | 2023 | 0.040539 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-04-25 06:16 | 2023-04-25 09:19 | 1 | 3:03 | P | ANIMAL | 1 X 25 EN RISER AVE CRUZO LINEAS | R23042500010 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-04-25 | 183 | keep | 0 | Apr | 2023 | 0.00012464 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-25 06:20 | 2023-04-25 06:47 | 1 | 0:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23042500005 | New_Event | Primary Wire Break | Include | Include | Equipment | 27 | 2023-04-25 | 27 | keep | 0 | Apr | 2023 | 1.839e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-04-25 06:24 | 2023-04-25 09:41 | 15 | 3:17 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESGANCHE | R23042500011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-04-25 | 2955 | keep | 0 | Apr | 2023 | 0.0020126 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-04-25 06:27 | 2023-04-25 10:14 | 1 | 3:47 | P | NO SE REPORTO CAUSA | 1 X 40 SMU 20 DE SU-2B A TRANSCLOSURE | R23042500037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 227 | 2023-04-25 | 227 | keep | 0 | Apr | 2023 | 0.00015461 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-25 06:52 | 2023-04-25 11:00 | 6 | 4:08 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | A23042500010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 248 | 2023-04-25 | 1488 | keep | 0 | Apr | 2023 | 0.0010135 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-04-25 06:57 | 2023-04-25 06:58 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 906 | keep | 0 | Apr | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CANOVANAS | 2023-04-25 07:06 | 2023-04-25 07:07 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 4981 | keep | 0 | Apr | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
BAYAMON | 2023-04-25 07:21 | 2023-04-25 09:53 | 2435 | 2:32 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR 1909-08 LLEVA LA CARGA DEL 1907-05 SE REEMPLAZO CAJA PRIMARIA BY-230425-02 | S23042500047 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2023-04-25 | 370120 | keep | 0 | Apr | 2023 | 0.25209 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-25 07:21 | 2023-04-25 09:53 | 2956 | 2:32 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 1907-05 SE REEMPLAZO CAJA PRIMARIA BY-230425-02 | S23042500047 | New_Event | Cutout Failure | Include | Include | Equipment | 152 | 2023-04-25 | 449312 | keep | 0 | Apr | 2023 | 0.30602 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
CAGUAS | 2023-04-25 07:29 | 2023-04-25 14:21 | 161 | 6:52 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C23042500018 | New_Event | Animals | Include | Include | Wildlife | 412 | 2023-04-25 | 66332 | keep | 0 | Apr | 2023 | 0.045178 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
MAYAGÃœEZ | 2023-04-25 07:29 | 2023-04-25 09:54 | 1 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER NO SE REPORTO CAUSA | M23042500015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-04-25 | 145 | keep | 0 | Apr | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-25 07:39 | 2023-04-25 07:40 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
VEGA BAJA | 2023-04-25 07:48 | 2023-04-25 21:23 | 57 | 13:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L Y 1 X 65 SE CERRO PUENTE ABIERTO | B23042500018 | New_Event | Primary Wire Break | Include | Include | Equipment | 815 | 2023-04-25 | 46455 | keep | 0 | Apr | 2023 | 0.03164 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-04-25 08:09 | 2023-04-25 10:39 | 30 | 2:30 | P | ANIMAL | CRUCE POR AVE 1 X 40 EN C/L | B23042500024 | New_Event | Animals | Include | Include | Wildlife | 150 | 2023-04-25 | 4500 | keep | 0 | Apr | 2023 | 0.0030649 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-25 08:12 | 2023-04-25 08:13 | 637 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR | M23042500021 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-04-25 | 637 | keep | 0 | Apr | 2023 | 0.00043386 | 0.00043386 | Momentary | FALSE | FALSE | Not_TMED_Event | 637
MAYAGÃœEZ | 2023-04-25 08:13 | 2023-04-25 12:40 | 80 | 4:27 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | M23042500023 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 267 | 2023-04-25 | 21360 | keep | 0 | Apr | 2023 | 0.014548 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-25 08:21 | 2023-04-25 11:16 | 96 | 2:55 | P | ANIMAL | 1 X 10 EN XMR Y 1 X 100 EN C/L CRUCE POR AVE | B23042500029 | New_Event | Animals | Include | Include | Wildlife | 175 | 2023-04-25 | 16800 | keep | 0 | Apr | 2023 | 0.011442 | 6.5385e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 96
BARRANQUITAS | 2023-04-25 08:34 | 2023-04-25 11:14 | 12 | 2:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA AVERIADA | C23042500035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 160 | 2023-04-25 | 1920 | keep | 0 | Apr | 2023 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-25 08:56 | 2023-04-25 09:10 | 3709 | 0:14 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO LINEA 7100 1114-02 LLEVA 70% DEL 1115-04 EN VIA LIBRE DE EMERGENCIA PARA REPARAR PROBLEMA EN INTERRUPTOR 7110 VIADUCTO SE ABRIÃ“ EL MISMO SIN ANTES CERRAR EL MOD 7115 CONDADO. | S23042500269 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-04-25 | 51926 | keep | 0 | Apr | 2023 | 0.035367 | 0.0025262 | Sustained | FALSE | FALSE | Not_TMED_Event | 3709
SAN JUAN | 2023-04-25 08:56 | 2023-04-25 09:10 | 24 | 0:14 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO LINEA 7100 1114-02 LLEVA 70% DEL 1115-04 EN VIA LIBRE DE EMERGENCIA PARA REPARAR PROBLEMA EN INTERRUPTOR 7110 VIADUCTO SE ABRIÃ“ EL MISMO SIN ANTES CERRAR EL MOD 7115 CONDADO. | S23042500269 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-04-25 | 336 | keep | 0 | Apr | 2023 | 0.00022885 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-04-25 08:56 | 2023-04-25 09:10 | 1 | 0:14 | S | LINEA DE TRANSMISION 38KV | CCE ABRIO LINEA 7100 1114-02 LLEVA 70% DEL 1115-04 EN VIA LIBRE DE EMERGENCIA PARA REPARAR PROBLEMA EN INTERRUPTOR 7110 VIADUCTO SE ABRIÃ“ EL MISMO SIN ANTES CERRAR EL MOD 7115 CONDADO. | S23042500269 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-04-25 | 14 | keep | 0 | Apr | 2023 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-25 08:56 | 2023-04-25 09:10 | 80 | 0:14 | P | LINEA DE TRANSMISION 38KV | CCE ABRIO LINEA 7100 1114-02 LLEVA 70% DEL 1115-04 EN VIA LIBRE DE EMERGENCIA PARA REPARAR PROBLEMA EN INTERRUPTOR 7110 VIADUCTO SE ABRIÃ“ EL MISMO SIN ANTES CERRAR EL MOD 7115 CONDADO. | S23042500269 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 14 | 2023-04-25 | 1120 | keep | 0 | Apr | 2023 | 0.00076283 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-04-25 09:01 | 2023-04-25 14:19 | 300 | 5:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO | C23042500044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 318 | 2023-04-25 | 95400 | keep | 0 | Apr | 2023 | 0.064977 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2023-04-25 09:03 | 2023-04-25 11:14 | 49 | 2:11 | P | DESGANCHE | 1 X 30 EN C/L SE REALIZO DESPEJE DE LINEA | R23042500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-04-25 | 6419 | keep | 0 | Apr | 2023 | 0.004372 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
FAJARDO | 2023-04-25 09:10 | 2023-04-25 11:12 | 10 | 2:02 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | R23042500027 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-04-25 | 1220 | keep | 0 | Apr | 2023 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-25 09:11 | 2023-04-25 09:12 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO CARGA 1647-10 Y 15% 1647-09 | R23042500028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 3046 | keep | 0 | Apr | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-04-25 09:11 | 2023-04-25 09:12 | 308 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO CARGA 1647-10 Y 15% 1647-09 | R23042500028 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-25 | 308 | keep | 0 | Apr | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-04-25 09:11 | 2023-04-25 09:12 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1646-03 LLEVANDO CARGA 1647-10 Y 15% 1647-09 | R23042500028 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-25 | 61 | keep | 0 | Apr | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-04-25 09:20 | 2023-04-25 11:31 | 1 | 2:11 | P | ANIMAL | 1 X 20 EN RISER CRUCE POR AVE | S23042500292 | New_Event | Animals | Include | Include | Wildlife | 131 | 2023-04-25 | 131 | keep | 0 | Apr | 2023 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-25 09:22 | 2023-04-26 10:32 | 1 | 25:10 | P | ANIMAL | 1X25 EN RISER CRUCE POR AVE | S23042500294 | New_Event | Animals | Include | Include | Wildlife | 1510 | 2023-04-25 | 1510 | keep | 0 | Apr | 2023 | 0.0010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-25 09:25 | 2023-04-25 12:05 | 100 | 2:40 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | S23042500296 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 160 | 2023-04-25 | 16000 | keep | 0 | Apr | 2023 | 0.010898 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-25 09:26 | 2023-04-25 15:12 | 160 | 5:46 | P | ANIMAL | 2 X 40 Y 1 X 50 EN CORTES DE LINEA Y RISER CRUCE POR AVE | C23042500053 | New_Event | Animals | Include | Include | Wildlife | 346 | 2023-04-25 | 55360 | keep | 0 | Apr | 2023 | 0.037705 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
BARRANQUITAS | 2023-04-25 09:28 | 2023-04-25 13:07 | 8 | 3:39 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA RETEZAR SECUNDARIA ARRIADA | C23042400073 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 219 | 2023-04-25 | 1752 | keep | 0 | Apr | 2023 | 0.0011933 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-25 09:31 | 2023-04-25 09:32 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | B23042500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 320 | keep | 0 | Apr | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2023-04-25 09:35 | 2023-04-25 10:36 | 15 | 1:01 | P | DESGANCHE | 1 X 30 EN C/L DESGACHE | S23042500309 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2023-04-25 | 915 | keep | 0 | Apr | 2023 | 0.0006232 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-25 09:50 | 2023-04-25 09:51 | 271 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR SCADA | S2304250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 271 | keep | 0 | Apr | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
AGUADILLA | 2023-04-25 09:50 | 2023-04-25 10:25 | 150 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE ABIERTO | M23042500178 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 35 | 2023-04-25 | 5250 | keep | 0 | Apr | 2023 | 0.0035758 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-25 09:54 | 2023-04-25 11:54 | 40 | 2:00 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23042500044 | New_Event | Animals | Include | Include | Wildlife | 120 | 2023-04-25 | 4800 | keep | 0 | Apr | 2023 | 0.0032693 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-04-25 10:02 | 2023-04-25 10:03 | 1256 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | CARGA POR 7002-04 POSTE PARTIDO | M23042500059 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-04-25 | 1256 | keep | 0 | Apr | 2023 | 0.00085546 | 0.00085546 | Momentary | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2023-04-25 10:02 | 2023-04-25 10:03 | 558 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECIERRE DE INTERRUPTOR | M23042500059 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-04-25 | 558 | keep | 0 | Apr | 2023 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
CANOVANAS | 2023-04-25 10:14 | 2023-04-25 10:58 | 10 | 0:44 | P | ANIMAL | 1 X 25 EN C/L CRUCE POR AVE | R23042500038 | New_Event | Animals | Include | Include | Wildlife | 44 | 2023-04-25 | 440 | keep | 0 | Apr | 2023 | 0.00029968 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-25 10:23 | 2023-04-25 14:30 | 15 | 4:07 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042500050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-04-25 | 3705 | keep | 0 | Apr | 2023 | 0.0025235 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-04-25 10:26 | 2023-04-25 14:22 | 11 | 3:56 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | C23042500077 | New_Event | Animals | Include | Include | Wildlife | 236 | 2023-04-25 | 2596 | keep | 0 | Apr | 2023 | 0.0017681 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
PONCE | 2023-04-25 10:28 | 2023-04-25 12:56 | 50 | 2:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN SU MAL TIEMPO LLUVIAS | P23042500061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 148 | 2023-04-25 | 7400 | keep | 0 | Apr | 2023 | 0.0050401 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-25 10:36 | 2023-04-25 10:38 | 220 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 1303-05 SE VERIFICO PERSONAL Y SE CERRO POR SCADA LLEVA 98% 1303-04 | S23042500350 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-25 | 440 | keep | 0 | Apr | 2023 | 0.00029968 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-04-25 10:36 | 2023-04-25 10:38 | 870 | 0:02 | T | DESGANCHE | DISPARO SE VERIFICO PERSONAL Y SE CERRO POR SCADA LLEVA 98% 1303-04 | S23042500350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-04-25 | 1740 | keep | 0 | Apr | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-04-25 10:38 | 2023-04-25 15:47 | 15 | 5:09 | P | DESGANCHE | 1 X 30 EN C/L DESGACHE | S23042500309 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 309 | 2023-04-25 | 4635 | keep | 0 | Apr | 2023 | 0.0031569 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-25 10:40 | 2023-04-25 13:08 | 34 | 2:28 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | B23042500087 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-04-25 | 5032 | keep | 0 | Apr | 2023 | 0.0034273 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
PONCE | 2023-04-25 10:41 | 2023-04-25 16:43 | 150 | 6:02 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | P23042500280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 362 | 2023-04-25 | 54300 | keep | 0 | Apr | 2023 | 0.036983 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-04-25 10:46 | 2023-04-25 10:59 | 1256 | 0:13 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR POSTE PARTIDO CARGA POR 7002-04 SE ABRIO MACHETES | M23042500078 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 13 | 2023-04-25 | 16328 | keep | 0 | Apr | 2023 | 0.011121 | 0.00085546 | Sustained | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2023-04-25 10:46 | 2023-04-25 10:59 | 558 | 0:13 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR POSTE PARTIDO DEL 7002-03, LLEVA LA CARGA DEL 7002-03 | M23042500078 | New_Event | Feeder Load Transferred | Include | Include | Other | 13 | 2023-04-25 | 7254 | keep | 0 | Apr | 2023 | 0.0049407 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
PONCE | 2023-04-25 10:47 | 2023-04-25 16:25 | 10 | 5:38 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE SECUNDARIO | P23042500082 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 338 | 2023-04-25 | 3380 | keep | 0 | Apr | 2023 | 0.0023021 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-04-25 10:59 | 2023-04-25 12:10 | 567 | 1:11 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES Y SE CERRO MACHETES POSTE PRIMARIO PARTIDO | M23042500081 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 71 | 2023-04-25 | 40257 | keep | 0 | Apr | 2023 | 0.027419 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-25 11:02 | 2023-04-25 13:13 | 1 | 2:11 | P | PROBLEMA DEL CLIENTE | 1 X 40 EN C/L TRANSFORMADOR AVERIADO | B23042400091 | New_Event | Customer-Related Interruption | Include | Include | Public | 131 | 2023-04-25 | 131 | keep | 0 | Apr | 2023 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-04-25 11:09 | 2023-04-25 12:16 | 40 | 1:07 | P | ANIMAL | 1 X 25 EN C/L AVE CRUZO LINEAS | P23042500104 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-04-25 | 2680 | keep | 0 | Apr | 2023 | 0.0018253 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-25 11:16 | 2023-04-25 12:31 | 78 | 1:15 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | R23042500040 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-04-25 | 5850 | keep | 0 | Apr | 2023 | 0.0039844 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
HUMACAO | 2023-04-25 11:27 | 2023-04-25 11:28 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2304250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2023-04-25 11:51 | 2023-04-25 17:17 | 1 | 5:26 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23042500370 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2023-04-25 | 326 | keep | 0 | Apr | 2023 | 0.00022204 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-25 12:04 | 2023-04-25 14:34 | 32 | 2:30 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23042500047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-04-25 | 4800 | keep | 0 | Apr | 2023 | 0.0032693 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
AGUADILLA | 2023-04-25 12:10 | 2023-04-25 21:20 | 12 | 9:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE REPARO PUENTES PRIMARIOS | M23042500081 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 550 | 2023-04-25 | 6600 | keep | 0 | Apr | 2023 | 0.0044952 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-25 12:12 | 2023-04-25 12:29 | 1 | 0:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN RISER SE REPORTA MAL TIEMPO LLUVIA | B23042500073 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 17 | 2023-04-25 | 17 | keep | 0 | Apr | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-04-25 12:50 | 2023-04-25 13:13 | 4 | 0:23 | P | DESGANCHE | 1 X 15 EN XMR SE REALIZO DESPEJE DE LINEA | R23042500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-04-25 | 92 | keep | 0 | Apr | 2023 | 6.2661e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2023-04-25 13:01 | 2023-04-25 20:30 | 8 | 7:29 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO LINEA SECUNDARIA | P23042500180 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 449 | 2023-04-25 | 3592 | keep | 0 | Apr | 2023 | 0.0024465 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-25 13:13 | 2023-04-25 17:56 | 268 | 4:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y 1 X 100 EN C/L | S23042500400 | New_Event | Cutout Failure | Include | Include | Equipment | 283 | 2023-04-25 | 75844 | keep | 0 | Apr | 2023 | 0.051657 | 0.00018253 | Sustained | FALSE | FALSE | Not_TMED_Event | 268
SAN JUAN | 2023-04-25 13:16 | 2023-04-25 21:29 | 2 | 8:13 | P | NO SE REPORTO CAUSA | 2 X 30 EN C/L | S23042500402 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 493 | 2023-04-25 | 986 | keep | 0 | Apr | 2023 | 0.00067156 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-25 13:16 | 2023-04-25 14:24 | 4 | 1:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23042500401 | New_Event | Secondary Wire Break | Include | Include | Equipment | 68 | 2023-04-25 | 272 | keep | 0 | Apr | 2023 | 0.00018526 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-04-25 13:37 | 2023-04-25 15:02 | 30 | 1:25 | P | NO SE REPORTO CAUSA | 2 X 25 EN CORTE DE LINEA | A23042500089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-04-25 | 2550 | keep | 0 | Apr | 2023 | 0.0017368 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-04-25 13:42 | 2023-04-25 18:30 | 10 | 4:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23042500092 | New_Event | Cutout Failure | Include | Include | Equipment | 288 | 2023-04-25 | 2880 | keep | 0 | Apr | 2023 | 0.0019616 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-25 13:44 | 2023-04-25 14:14 | 25 | 0:30 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23042500097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 30 | 2023-04-25 | 750 | keep | 0 | Apr | 2023 | 0.00051082 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-04-25 13:55 | 2023-04-25 13:56 | 6285 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23042500110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 6285 | keep | 0 | Apr | 2023 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
AGUADILLA | 2023-04-25 14:13 | 2023-04-25 16:40 | 80 | 2:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23042500104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 147 | 2023-04-25 | 11760 | keep | 0 | Apr | 2023 | 0.0080097 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-04-25 14:16 | 2023-04-25 15:29 | 80 | 1:13 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE. | C23042500163 | New_Event | Animals | Include | Include | Wildlife | 73 | 2023-04-25 | 5840 | keep | 0 | Apr | 2023 | 0.0039776 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-25 14:24 | 2023-04-25 17:30 | 144 | 3:06 | P | SOBRECARGA | 1 X 100 EN C/L POR CARGA | B23042500112 | New_Event | Trip Due To Overload | Include | Include | Other | 186 | 2023-04-25 | 26784 | keep | 0 | Apr | 2023 | 0.018242 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
AGUADILLA | 2023-04-25 14:39 | 2023-04-25 16:10 | 400 | 1:31 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23042500118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 91 | 2023-04-25 | 36400 | keep | 0 | Apr | 2023 | 0.024792 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-04-25 14:43 | 2023-04-25 16:41 | 1 | 1:58 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23042500121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-04-25 | 118 | keep | 0 | Apr | 2023 | 8.0369e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-25 14:58 | 2023-04-25 17:18 | 10 | 2:20 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 2 X 8 EN TRANSFORMADOR SE REPARO LINEA CRUZADA SECUNDARIA | C23042500175 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 140 | 2023-04-25 | 1400 | keep | 0 | Apr | 2023 | 0.00095353 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-04-25 15:01 | 2023-04-25 17:29 | 80 | 2:28 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23042500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-04-25 | 11840 | keep | 0 | Apr | 2023 | 0.0080642 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-25 15:13 | 2023-04-25 16:57 | 10 | 1:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S23042500423 | New_Event | Secondary Wire Break | Include | Include | Equipment | 104 | 2023-04-25 | 1040 | keep | 0 | Apr | 2023 | 0.00070834 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-25 15:16 | 2023-04-25 17:15 | 15 | 1:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23042500249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-04-25 | 1785 | keep | 0 | Apr | 2023 | 0.0012158 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-25 15:17 | 2023-04-25 18:18 | 30 | 3:01 | P | CONDUCTOR ROTO O ABIERTO | 1X 80 EN C/L SE CERRO PUENTE DE LINEA A CAJA | S23042500425 | New_Event | Primary Wire Break | Include | Include | Equipment | 181 | 2023-04-25 | 5430 | keep | 0 | Apr | 2023 | 0.0036983 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-25 15:18 | 2023-04-26 03:44 | 14 | 12:26 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | S23042500427 | New_Event | Animals | Include | Include | Wildlife | 746 | 2023-04-25 | 10444 | keep | 0 | Apr | 2023 | 0.0071134 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-04-25 15:24 | 2023-04-25 18:12 | 30 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23042500129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-04-25 | 5040 | keep | 0 | Apr | 2023 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-25 15:58 | 2023-04-25 19:03 | 12 | 3:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE RETEZO LINEA SECUNDARIA | S23042500432 | New_Event | Secondary Wire Break | Include | Include | Equipment | 185 | 2023-04-25 | 2220 | keep | 0 | Apr | 2023 | 0.001512 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-25 16:00 | 2023-04-25 17:30 | 15 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO MONTURA DE XMR PARA REPARAR CONECTORES SECUNDARIOS Y DESGANCHE SECUNDARIO | S23042400676 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-04-25 | 1350 | keep | 0 | Apr | 2023 | 0.00091948 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-25 16:00 | 2023-04-26 06:15 | 1 | 14:15 | P | ANIMAL | 2 X 10 EN BANCO XMR CRUCE X AVE | B23042500149 | New_Event | Animals | Include | Include | Wildlife | 855 | 2023-04-25 | 855 | keep | 0 | Apr | 2023 | 0.00058234 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-25 16:00 | 2023-04-25 16:20 | 145 | 0:20 | P | ARBOL SOBRE LINEA | SE ABRE CORTE DE LINEA PARA RETIRAR ARBOL DE LINEA PRIMARIA | P23042500268 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 20 | 2023-04-25 | 2900 | keep | 0 | Apr | 2023 | 0.0019752 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
CANOVANAS | 2023-04-25 16:05 | 2023-04-25 16:56 | 30 | 0:51 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23042500063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-04-25 | 1530 | keep | 0 | Apr | 2023 | 0.0010421 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-04-25 16:10 | 2023-04-25 17:54 | 50 | 1:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23042500271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-04-25 | 5200 | keep | 0 | Apr | 2023 | 0.0035417 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-25 16:17 | 2023-04-25 16:21 | 3597 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 9405-05 QUE LLEVA 1719-15 SE CERRO POR SCADA | B23042500152 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-04-25 | 14388 | keep | 0 | Apr | 2023 | 0.0097996 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-04-25 16:17 | 2023-04-25 16:21 | 3511 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 9405-05 QUE LLEVA 1719-15 SE CERRO POR SCADA | B23042500152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-25 | 14044 | keep | 0 | Apr | 2023 | 0.0095653 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
HUMACAO | 2023-04-25 16:31 | 2023-04-25 16:32 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2304250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
MAYAGÃœEZ | 2023-04-25 16:40 | 2023-04-25 19:00 | 90 | 2:20 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23042500156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-04-25 | 12600 | keep | 0 | Apr | 2023 | 0.0085818 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
MAYAGÃœEZ | 2023-04-25 16:41 | 2023-04-26 10:15 | 15 | 17:34 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23042500157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1054 | 2023-04-25 | 15810 | keep | 0 | Apr | 2023 | 0.010768 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-04-25 16:42 | 2023-04-25 17:26 | 25 | 0:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REEMPLAZO PORTAFUSIBLE QUEMADO | R23042500069 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2023-04-25 | 1100 | keep | 0 | Apr | 2023 | 0.0007492 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-25 16:42 | 2023-04-25 18:38 | 40 | 1:56 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA | C23042500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-04-25 | 4640 | keep | 0 | Apr | 2023 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-04-25 16:54 | 2023-04-25 20:19 | 349 | 3:25 | T | LINEA DE TRANSMISION 38KV | FASE DE LINEA 500 EN EL PISO CONDUCTOR EN EL PISO Y CRUCETA PARTIDA | P23042500303 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2023-04-25 | 71545 | keep | 0 | Apr | 2023 | 0.048729 | 0.0002377 | Sustained | FALSE | FALSE | Not_TMED_Event | 349
PONCE | 2023-04-25 16:54 | 2023-04-25 20:19 | 653 | 3:25 | T | LINEA DE TRANSMISION 38KV | FASE DE LINEA 500 EN EL PISO CONDUCTOR EN EL PISO Y CRUCETA PARTIDA | P23042500303 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2023-04-25 | 133865 | keep | 0 | Apr | 2023 | 0.091175 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
PONCE | 2023-04-25 16:54 | 2023-04-25 20:19 | 860 | 3:25 | T | LINEA DE TRANSMISION 38KV | FASE DE LINEA 500 EN EL PISO CONDUCTOR EN EL PISO Y CRUCETA PARTIDA | P23042500303 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 205 | 2023-04-25 | 176300 | keep | 0 | Apr | 2023 | 0.12008 | 0.00058574 | Sustained | FALSE | FALSE | Not_TMED_Event | 860
PONCE | 2023-04-25 16:54 | 2023-04-25 20:26 | 114 | 3:32 | T | LINEA DE TRANSMISION 38KV | FASE DE LINEA 500 SOBRE ALIMENTADOR | P23042500305 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2023-04-25 | 24168 | keep | 0 | Apr | 2023 | 0.016461 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
SAN JUAN | 2023-04-25 17:02 | 2023-04-25 17:03 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2304250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-25 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
HUMACAO | 2023-04-25 17:13 | 2023-04-25 18:41 | 16 | 1:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA SULFATADA | C23042500198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 88 | 2023-04-25 | 1408 | keep | 0 | Apr | 2023 | 0.00095898 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-04-25 17:19 | 2023-04-25 20:55 | 100 | 3:36 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C23042500199 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-04-25 | 21600 | keep | 0 | Apr | 2023 | 0.014712 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-25 17:22 | 2023-04-25 20:55 | 20 | 3:33 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23042500462 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2023-04-25 | 4260 | keep | 0 | Apr | 2023 | 0.0029015 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-25 17:31 | 2023-04-25 18:48 | 1 | 1:17 | P | DESGANCHE | 2 X 25 EN C/L DESGANCHE | R23042500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-04-25 | 77 | keep | 0 | Apr | 2023 | 5.2444e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-25 17:33 | 2023-04-25 20:05 | 60 | 2:32 | P | ARBOL SOBRE LINEA | 1 X 40 Y 2 X 50 EN C/L SE RETIRO ARBOL SOBRE LINEA | S23042500464 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 152 | 2023-04-25 | 9120 | keep | 0 | Apr | 2023 | 0.0062116 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-25 17:36 | 2023-04-25 18:52 | 1 | 1:16 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | R23042500073 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-04-25 | 76 | keep | 0 | Apr | 2023 | 5.1763e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-25 17:38 | 2023-04-25 19:41 | 100 | 2:03 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | S23042500466 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-04-25 | 12300 | keep | 0 | Apr | 2023 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-25 17:44 | 2023-04-25 19:15 | 321 | 1:31 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA CERRAR LOS PUENTES ABIERTOS Y ENERGIZAR 100% EN SERVICIO | S23042400395 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 91 | 2023-04-25 | 29211 | keep | 0 | Apr | 2023 | 0.019895 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-25 18:10 | 2023-04-25 19:52 | 40 | 1:42 | P | DESGANCHE | SE DESGANCHO ENRREDADERA DENTRO DEL SU-D 1 X 80 EN SU1 Y 2 X100 EN RISER | R23042500076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-04-25 | 4080 | keep | 0 | Apr | 2023 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-25 18:15 | 2023-04-26 07:15 | 70 | 13:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L PORTA FUSIBLE QUEMADO | B23042500211 | New_Event | Cutout Failure | Include | Include | Equipment | 780 | 2023-04-25 | 54600 | keep | 0 | Apr | 2023 | 0.037188 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-04-25 18:20 | 2023-04-25 20:00 | 25 | 1:40 | P | DESGANCHE | 1 X 8 EN CORTE DE LINEA SE RETIRO ENREDADERA | P23042500317 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-04-25 | 2500 | keep | 0 | Apr | 2023 | 0.0017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-25 18:27 | 2023-04-26 06:42 | 40 | 12:15 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | S23042500492 | New_Event | Animals | Include | Include | Wildlife | 735 | 2023-04-25 | 29400 | keep | 0 | Apr | 2023 | 0.020024 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-25 18:28 | 2023-04-25 18:44 | 1 | 0:16 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | B23042500214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-04-25 | 16 | keep | 0 | Apr | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-25 18:34 | 2023-04-25 19:37 | 20 | 1:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE LINEA A CAJA EN C/L | R23042500079 | New_Event | Primary Wire Break | Include | Include | Equipment | 63 | 2023-04-25 | 1260 | keep | 0 | Apr | 2023 | 0.00085818 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-25 18:48 | 2023-04-26 09:08 | 8 | 14:20 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE RETIRO RANA DE LAS LINEAS | M23042500169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 860 | 2023-04-25 | 6880 | keep | 0 | Apr | 2023 | 0.0046859 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-04-25 18:57 | 2023-04-26 11:12 | 6 | 16:15 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23042500171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 975 | 2023-04-25 | 5850 | keep | 0 | Apr | 2023 | 0.0039844 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-04-25 19:01 | 2023-04-25 20:40 | 15 | 1:39 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23042500224 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-04-25 | 1485 | keep | 0 | Apr | 2023 | 0.0010114 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-25 19:05 | 2023-04-25 19:18 | 17 | 0:13 | P | DESGANCHE | 1 X 15 EN XMR Y DESGANCHE | B23042500225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 13 | 2023-04-25 | 221 | keep | 0 | Apr | 2023 | 0.00015052 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
ARECIBO | 2023-04-25 19:16 | 2023-04-26 12:40 | 40 | 17:24 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A23042500148 | New_Event | Primary Wire Break | Include | Include | Equipment | 1044 | 2023-04-25 | 41760 | keep | 0 | Apr | 2023 | 0.028443 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-25 19:21 | 2023-04-25 20:13 | 7 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS | R23042500070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-04-25 | 364 | keep | 0 | Apr | 2023 | 0.00024792 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-04-25 19:29 | 2023-04-25 20:25 | 26 | 0:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN C/L LLUVIA FUERTE | R23042500085 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 56 | 2023-04-25 | 1456 | keep | 0 | Apr | 2023 | 0.00099167 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2023-04-25 19:50 | 2023-04-26 08:25 | 43 | 12:35 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23042500223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 755 | 2023-04-25 | 32465 | keep | 0 | Apr | 2023 | 0.022112 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
SAN JUAN | 2023-04-25 20:01 | 2023-04-26 12:32 | 127 | 16:31 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | S23042500515 | New_Event | Animals | Include | Include | Wildlife | 991 | 2023-04-25 | 125857 | keep | 0 | Apr | 2023 | 0.085721 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
CAGUAS | 2023-04-25 20:23 | 2023-04-26 13:20 | 10 | 16:57 | P | TRANSFORMADOR AVERIADO | SE ABRIO Y SE REEMPLAZO EL MISMO | C23042500225 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1017 | 2023-04-25 | 10170 | keep | 0 | Apr | 2023 | 0.0069267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-04-25 20:56 | 2023-04-26 09:50 | 6 | 12:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR POR LLUVIA | A23042500154 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 774 | 2023-04-25 | 4644 | keep | 0 | Apr | 2023 | 0.003163 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-04-25 21:16 | 2023-04-26 10:37 | 21 | 13:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23042500228 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 801 | 2023-04-25 | 16821 | keep | 0 | Apr | 2023 | 0.011457 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
PONCE | 2023-04-25 21:23 | 2023-04-26 07:00 | 50 | 9:37 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE REMPLAZO AISLADOR | P23042500350 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 577 | 2023-04-25 | 28850 | keep | 0 | Apr | 2023 | 0.01965 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-25 21:33 | 2023-04-26 09:28 | 104 | 11:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN SU-1 RH | R23042500099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 715 | 2023-04-25 | 74360 | keep | 0 | Apr | 2023 | 0.050646 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
SAN JUAN | 2023-04-25 21:39 | 2023-04-26 10:31 | 10 | 12:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR SE REPARO SECUNDARIA | S23042500521 | New_Event | Secondary Wire Break | Include | Include | Equipment | 772 | 2023-04-25 | 7720 | keep | 0 | Apr | 2023 | 0.0052581 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-04-25 22:37 | 2023-04-25 22:40 | 1058 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 1348-07, LLEVA 80% DEL 1348-06, 20% DEL 1336-08 Y 100% DEL 1401-10 | S23042500526 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-25 | 3174 | keep | 0 | Apr | 2023 | 0.0021618 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-04-25 22:37 | 2023-04-25 22:40 | 1000 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 1348-07, LLEVA 80% DEL 1348-06, 20% DEL 1336-08 Y 100% DEL 1401-10 | S23042500526 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-25 | 3000 | keep | 0 | Apr | 2023 | 0.0020433 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-04-25 22:37 | 2023-04-25 22:40 | 278 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 1348-07, LLEVA 80% DEL 1348-06, 20% DEL 1336-08 Y 1401-10 | S23042500526 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-25 | 834 | keep | 0 | Apr | 2023 | 0.00056803 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-04-25 22:37 | 2023-04-25 22:40 | 1295 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 1348-07, LLEVA 80% DEL 1348-06, 20% DEL 1336-08 Y 100% DEL 1401-10 | S23042500526 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-25 | 3885 | keep | 0 | Apr | 2023 | 0.0026461 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-04-25 22:37 | 2023-04-25 22:40 | 9 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 1348-07, LLEVA 80% DEL 1348-06, 20% DEL 1336-08 Y 1401-10 | S23042500526 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-25 | 27 | keep | 0 | Apr | 2023 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-04-25 23:07 | 2023-04-25 23:51 | 6 | 0:44 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ABRIO TIE DEL 9206-08/9206-09 PARA SECCIONALIZAR MH-7 POR PROBLEMAS DE ROTACION INVERSA Y SE CERRO EN SU#2 ENTRO 50% EN SERVICIO. | B23042500238 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 44 | 2023-04-25 | 264 | keep | 0 | Apr | 2023 | 0.00017981 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-25 23:11 | 2023-04-26 15:20 | 70 | 16:09 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO, SE REMPLAZO CAJA PRIMARIA, Y SE REALIZO PODA EN SERVICIO. INFORMO OTNIEL QUINONES. EN SERVICIO | S23042500531 | New_Event | Primary Wire Break | Include | Include | Equipment | 969 | 2023-04-25 | 67830 | keep | 0 | Apr | 2023 | 0.046199 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-04-25 23:41 | 2023-04-27 19:25 | 100 | 43:44 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO | A23042500157 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2624 | 2023-04-25 | 262400 | keep | 0 | Apr | 2023 | 0.17872 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-25 23:51 | 2023-04-26 13:00 | 3 | 13:09 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE ELIMINO VS-MH-7 AVERIADO SE CORRIGIO FASEO Y SE ENERGIZARON NUEVAMENTE LOS CLIENTES. CON GOI BY-230424-03 | B23042500238 | Partial_restoration | UG Switching Unit Failure | Include | Include | Equipment | 789 | 2023-04-25 | 2367 | keep | 0 | Apr | 2023 | 0.0016122 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-04-26 02:16 | 2023-04-26 16:39 | 4 | 14:23 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 37.5 X 25KVA | C23042600001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 863 | 2023-04-26 | 3452 | keep | 0 | Apr | 2023 | 0.0023511 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-04-26 02:26 | 2023-04-26 10:47 | 129 | 8:21 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTES PRIMARIOS | C23042600002 | New_Event | Primary Wire Break | Include | Include | Equipment | 501 | 2023-04-26 | 64629 | keep | 0 | Apr | 2023 | 0.044019 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
SAN JUAN | 2023-04-26 03:44 | 2023-04-26 03:47 | 1483 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 | B2304260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-26 | 4449 | keep | 0 | Apr | 2023 | 0.0030302 | 0.0010101 | Momentary | FALSE | FALSE | Not_TMED_Event | 1483
SAN JUAN | 2023-04-26 03:44 | 2023-04-26 03:47 | 1532 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 | B2304260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-26 | 4596 | keep | 0 | Apr | 2023 | 0.0031303 | 0.0010434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1532
SAN JUAN | 2023-04-26 03:44 | 2023-04-26 03:47 | 4232 | 0:03 | P | ANIMAL | DISPARO DE INTERRUPTOR 1336-08 LLEVA 80% DE SU CARGA, LLEVA 30% DEL 1204-04 Y 15% DEL 1204-05 | B2304260000X | Additional_clients | Animals | Include | Include | Wildlife | 3 | 2023-04-26 | 12696 | keep | 0 | Apr | 2023 | 0.0086472 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-26 03:47 | 2023-04-26 09:34 | 14 | 5:47 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | S23042500427 | 1st_after_momentary | Animals | Include | Include | Wildlife | 347 | 2023-04-26 | 4858 | keep | 0 | Apr | 2023 | 0.0033088 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-04-26 04:16 | 2023-04-26 10:29 | 60 | 6:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X80 EN C/L SE REMPLAZO CAJA PRIMARIA QUEMADA | S23042600012 | New_Event | Cutout Failure | Include | Include | Equipment | 373 | 2023-04-26 | 22380 | keep | 0 | Apr | 2023 | 0.015243 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-04-26 04:33 | 2023-04-26 09:12 | 15 | 4:39 | P | DESGANCHE | 1 X 20 EN C/L Y DESGANCHE | B23042600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 279 | 2023-04-26 | 4185 | keep | 0 | Apr | 2023 | 0.0028504 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-04-26 04:50 | 2023-04-26 09:40 | 50 | 4:50 | P | NO SE REPORTO CAUSA | 1 X 65 Y 1 X 40 EN DIFERENTES CORTES DE LINEA NO SE REPORTO | M23042600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 290 | 2023-04-26 | 14500 | keep | 0 | Apr | 2023 | 0.0098759 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-26 05:00 | 2023-04-26 10:42 | 40 | 5:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIA | A23042600009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 342 | 2023-04-26 | 13680 | keep | 0 | Apr | 2023 | 0.0093174 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-26 05:33 | 2023-04-26 05:34 | 3 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1908-01 LLEVA EL 1908-04 Y 1908-05 | S2304260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 3 | keep | 0 | Apr | 2023 | 2.0433e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-26 05:33 | 2023-04-26 05:34 | 58 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1908-01 LLEVA EL 1908-04 Y 1908-05 | S2304260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-26 | 58 | keep | 0 | Apr | 2023 | 3.9504e-05 | 3.9504e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2023-04-26 05:33 | 2023-04-26 05:34 | 386 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1908-01 LLEVA EL 1908-04 Y 1908-05 | S2304260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-26 | 386 | keep | 0 | Apr | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
FAJARDO | 2023-04-26 06:27 | 2023-04-26 09:34 | 80 | 3:07 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO LINEA A CAJA EN RISER | R23042600008 | New_Event | Primary Wire Break | Include | Include | Equipment | 187 | 2023-04-26 | 14960 | keep | 0 | Apr | 2023 | 0.010189 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-26 06:53 | 2023-04-26 11:38 | 40 | 4:45 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23042600029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2023-04-26 | 11400 | keep | 0 | Apr | 2023 | 0.0077645 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-26 07:11 | 2023-04-26 07:12 | 723 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1912-08 LLEVA 1711-02 Y LLEVA 1711-05 | B2304260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-26 | 723 | keep | 0 | Apr | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-04-26 07:11 | 2023-04-26 07:12 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1912-08 LLEVA 1711-02 Y LLEVA 1711-05 | B2304260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-26 | 1976 | keep | 0 | Apr | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-04-26 07:11 | 2023-04-26 07:12 | 577 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1912-08 LLEVA 1711-02 Y LLEVA 1711-05 | B2304260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 577 | keep | 0 | Apr | 2023 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
HUMACAO | 2023-04-26 07:24 | 2023-04-26 08:50 | 6 | 1:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTES SECUNDARIOS | C23042600011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 86 | 2023-04-26 | 516 | keep | 0 | Apr | 2023 | 0.00035145 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-26 07:29 | 2023-04-26 07:30 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1206-03 16% DE SU CARGA TRANSFERIDA AL 1620-02 LLEVA 85% DE LA CARGA DEL 1204-05 SE CERRO POR CONTROL | S23042600033 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-26 | 8679 | keep | 0 | Apr | 2023 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-04-26 07:29 | 2023-04-26 07:30 | 3471 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1206-03 16% DE SU CARGA TRANSFERIDA AL 1620-02 LLEVA 85% DE LA CARGA DEL 1204-05 SE CERRO POR CONTROL | S23042600033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 3471 | keep | 0 | Apr | 2023 | 0.0023641 | 0.0023641 | Momentary | FALSE | FALSE | Not_TMED_Event | 3471
BARRANQUITAS | 2023-04-26 07:39 | 2023-04-26 13:24 | 20 | 5:45 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23042600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 345 | 2023-04-26 | 6900 | keep | 0 | Apr | 2023 | 0.0046996 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-04-26 07:53 | 2023-04-26 17:13 | 50 | 9:20 | P | NO SE REPORTO CAUSA | 2 X 30, 2 X 65 Y 1 X 100 EN CORTES DE LINEA Y RISER SE PATRULLO | S23042600044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 560 | 2023-04-26 | 28000 | keep | 0 | Apr | 2023 | 0.019071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-26 07:54 | 2023-04-26 12:16 | 60 | 4:22 | P | ANIMAL | 1 X 25 EN C/L SE INSTALO AISLADOR PARA MEJORAR DESPEJE CRUCE POR AVE | R23042600012 | New_Event | Animals | Include | Include | Wildlife | 262 | 2023-04-26 | 15720 | keep | 0 | Apr | 2023 | 0.010707 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-04-26 08:13 | 2023-04-26 08:50 | 12 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA AJUSTAR VOLTAJE SECUNDARIO Y SE REPARO BAJANTES SECUNDARIOS | M23042600016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-04-26 | 444 | keep | 0 | Apr | 2023 | 0.00030241 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-04-26 08:21 | 2023-04-26 10:46 | 1 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER HACIA MONTURA PRIVADA | R23042600017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-04-26 | 145 | keep | 0 | Apr | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-26 08:26 | 2023-04-26 13:40 | 30 | 5:14 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA Y SE REALIZO DESGANCHE | A23042600037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2023-04-26 | 9420 | keep | 0 | Apr | 2023 | 0.0064159 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-26 08:38 | 2023-04-26 09:14 | 1825 | 0:36 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR - DIO FAIL TO OPERATE - SE CERRO LOCALMENTE EN LA SUBESTACION | S23042600059 | New_Event | Primary Wire Break | Include | Include | Equipment | 36 | 2023-04-26 | 65700 | keep | 0 | Apr | 2023 | 0.044748 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
CAGUAS | 2023-04-26 08:57 | 2023-04-26 16:10 | 1 | 7:13 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU SE INSPECCIONO | C23042600031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 433 | 2023-04-26 | 433 | keep | 0 | Apr | 2023 | 0.00029491 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-26 09:08 | 2023-04-26 11:56 | 25 | 2:48 | P | ANIMAL | 1 X 15 EN XMR Y 1 X 30 EN C/L CRUCE X LAGARTIJO | B23042600015 | New_Event | Animals | Include | Include | Wildlife | 168 | 2023-04-26 | 4200 | keep | 0 | Apr | 2023 | 0.0028606 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-26 09:14 | 2023-04-26 11:48 | 140 | 2:34 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN EL TRONCAL | S23042600080 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 154 | 2023-04-26 | 21560 | keep | 0 | Apr | 2023 | 0.014684 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-04-26 09:15 | 2023-04-26 12:26 | 20 | 3:11 | P | ANIMAL | 1 X 80 EN C/L 1 X 10 XMR CRUCE POR LAGARTIJO | C23042600035 | New_Event | Animals | Include | Include | Wildlife | 191 | 2023-04-26 | 3820 | keep | 0 | Apr | 2023 | 0.0026018 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-26 09:15 | 2023-04-26 12:30 | 15 | 3:15 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEAS CRUZADAS | M23042600041 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 195 | 2023-04-26 | 2925 | keep | 0 | Apr | 2023 | 0.0019922 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-04-26 09:34 | 2023-04-26 11:49 | 1 | 2:15 | P | ANIMAL | 1 X 10 DE RISER A SUB PRIVADA CRUCE X SAPO | B23042600025 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-04-26 | 135 | keep | 0 | Apr | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-26 09:45 | 2023-04-26 10:17 | 65 | 0:32 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE PUENTE PARA SECCIONALIZAR AVERIA DE POSTE PARTIDO Y SE CIERRA CORTE DE LINEA | A23042600046 | New_Event | Primary Pole Failure | Include | Include | Equipment | 32 | 2023-04-26 | 2080 | keep | 0 | Apr | 2023 | 0.0014167 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
FAJARDO | 2023-04-26 09:49 | 2023-04-26 10:42 | 144 | 0:53 | P | ANIMAL | 1 X 40 EN C/L 2 X 30 EN C/L SE REEMPLAZO PORTAFUSIBLE CRUCE POR AVE | R23042600029 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-04-26 | 7632 | keep | 0 | Apr | 2023 | 0.0051981 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
BAYAMON | 2023-04-26 10:06 | 2023-04-26 12:30 | 260 | 2:24 | P | ANIMAL | 1 X 80 EN C/L SE RETIRO AVE | B23042600035 | New_Event | Animals | Include | Include | Wildlife | 144 | 2023-04-26 | 37440 | keep | 0 | Apr | 2023 | 0.0255 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
SAN JUAN | 2023-04-26 10:07 | 2023-04-26 14:36 | 150 | 4:29 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L Y SE LEVANTO CONDUCTOR PRIMARIO | S23042600096 | New_Event | Primary Wire Break | Include | Include | Equipment | 269 | 2023-04-26 | 40350 | keep | 0 | Apr | 2023 | 0.027482 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-26 10:08 | 2023-04-26 10:09 | 6136 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23042600038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 6136 | keep | 0 | Apr | 2023 | 0.0041792 | 0.0041792 | Momentary | FALSE | FALSE | Not_TMED_Event | 6136
SAN JUAN | 2023-04-26 10:17 | 2023-04-26 10:18 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23042600101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
ARECIBO | 2023-04-26 10:17 | 2023-04-26 18:16 | 22 | 7:59 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE Y SE CERRO PUENTE PRIMARIO | A23042600074 | New_Event | Primary Pole Failure | Include | Include | Equipment | 479 | 2023-04-26 | 10538 | keep | 0 | Apr | 2023 | 0.0071774 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-04-26 10:51 | 2023-04-26 10:52 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2304260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 5809 | keep | 0 | Apr | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BARRANQUITAS | 2023-04-26 11:02 | 2023-04-26 17:09 | 6 | 6:07 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE SECUNDARIO DERRIBADO POR CAMION | C23042600068 | New_Event | Damage From Public | Include | Include | Public | 367 | 2023-04-26 | 2202 | keep | 0 | Apr | 2023 | 0.0014998 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-04-26 11:04 | 2023-04-26 14:13 | 1 | 3:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN XMR SE REEMPLAZO PORTAFUSIBLE | R23042600034 | New_Event | Cutout Failure | Include | Include | Equipment | 189 | 2023-04-26 | 189 | keep | 0 | Apr | 2023 | 0.00012873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-26 11:05 | 2023-04-26 13:36 | 43 | 2:31 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23042600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-04-26 | 6493 | keep | 0 | Apr | 2023 | 0.0044224 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2023-04-26 11:21 | 2023-04-26 14:31 | 25 | 3:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | C23042600071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 190 | 2023-04-26 | 4750 | keep | 0 | Apr | 2023 | 0.0032352 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-26 11:28 | 2023-04-26 11:30 | 4702 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23042600078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-26 | 9404 | keep | 0 | Apr | 2023 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
VEGA BAJA | 2023-04-26 11:31 | 2023-04-26 15:25 | 80 | 3:54 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-04-26 | 18720 | keep | 0 | Apr | 2023 | 0.01275 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-26 11:48 | 2023-04-26 14:35 | 411 | 2:47 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PARA REPARAR PUENTE ABIERTO EN TRONCAL Y SE ENERGIZO 100% SERVICIO | S23042600080 | New_Event | Primary Wire Break | Include | Include | Equipment | 167 | 2023-04-26 | 68637 | keep | 0 | Apr | 2023 | 0.046748 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
BAYAMON | 2023-04-26 11:53 | 2023-04-26 14:30 | 1 | 2:37 | P | DESGANCHE | 1 X 10 EN C/L SE DESGANCHO | B23042600087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-04-26 | 157 | keep | 0 | Apr | 2023 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-26 11:57 | 2023-04-26 13:21 | 4 | 1:24 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE REPARO SECUNDARIA AVERIADA IMPACTADA POR CAMION | C23042600082 | New_Event | Damage From Public | Include | Include | Public | 84 | 2023-04-26 | 336 | keep | 0 | Apr | 2023 | 0.00022885 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-04-26 12:30 | 2023-04-26 12:50 | 14 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA AJUSTAR VOLTAJE SECUNDARIO Y SE REPARO BAJANTES SECUNDARIOS | M23042600093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-04-26 | 280 | keep | 0 | Apr | 2023 | 0.00019071 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2023-04-26 12:31 | 2023-04-26 14:30 | 50 | 1:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN CORTE DE LINEA SE FIJO LINEA ZAFADA DE AISLADOR | A23042600078 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 119 | 2023-04-26 | 5950 | keep | 0 | Apr | 2023 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-26 12:42 | 2023-04-26 14:20 | 5 | 1:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BARRA EN PEDESTAL | B23042300094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 98 | 2023-04-26 | 490 | keep | 0 | Apr | 2023 | 0.00033374 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-04-26 12:48 | 2023-04-26 14:20 | 100 | 1:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23042600098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-04-26 | 9200 | keep | 0 | Apr | 2023 | 0.0062661 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-26 12:49 | 2023-04-26 13:50 | 3 | 1:01 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | S23042600163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-04-26 | 183 | keep | 0 | Apr | 2023 | 0.00012464 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-04-26 12:50 | 2023-04-26 15:00 | 3 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | A23042600083 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-04-26 | 390 | keep | 0 | Apr | 2023 | 0.00026563 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-04-26 13:03 | 2023-04-26 18:07 | 1 | 5:04 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 50KVA AVERIADO | S23042600167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 304 | 2023-04-26 | 304 | keep | 0 | Apr | 2023 | 0.00020705 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-26 13:05 | 2023-04-26 14:24 | 40 | 1:19 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESPEJE DE LINEA | R23042600042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-04-26 | 3160 | keep | 0 | Apr | 2023 | 0.0021523 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-26 13:09 | 2023-04-26 13:28 | 1352 | 0:19 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23042600102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-04-26 | 25688 | keep | 0 | Apr | 2023 | 0.017496 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-04-26 13:09 | 2023-04-26 13:28 | 871 | 0:19 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 6012-05 CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR ESTE ESTA LLEVANDO LA CARGA DEL 6014-03 | M23042600102 | New_Event | Feeder Load Transferred | Include | Include | Other | 19 | 2023-04-26 | 16549 | keep | 0 | Apr | 2023 | 0.011271 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
GUAYAMA | 2023-04-26 13:24 | 2023-04-26 13:36 | 1 | 0:12 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR NO SE REPORTO CAUSA | P23042600079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2023-04-26 | 12 | keep | 0 | Apr | 2023 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-26 13:58 | 2023-04-26 14:58 | 1 | 1:00 | P | NO SE REPORTO CAUSA | 1 X 8 EN BANCO XMR | S23042600177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 60 | 2023-04-26 | 60 | keep | 0 | Apr | 2023 | 4.0866e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-26 14:05 | 2023-04-26 15:21 | 40 | 1:16 | P | ANIMAL | 1 X 25 EN PROVISIONAL SE RETIRO AVE | B23042600115 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-04-26 | 3040 | keep | 0 | Apr | 2023 | 0.0020705 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-04-26 14:07 | 2023-04-26 17:45 | 30 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042600132 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2023-04-26 | 6540 | keep | 0 | Apr | 2023 | 0.0044544 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-04-26 14:11 | 2023-04-26 16:51 | 1548 | 2:40 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE REMPLAZO AISLADORES | A23042600101 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 160 | 2023-04-26 | 247680 | keep | 0 | Apr | 2023 | 0.16869 | 0.0010543 | Sustained | FALSE | FALSE | Not_TMED_Event | 1548
ARECIBO | 2023-04-26 14:11 | 2023-04-26 16:51 | 3431 | 2:40 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR SE REMPLAZO AISLADORES | A23042600100 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 160 | 2023-04-26 | 548960 | keep | 0 | Apr | 2023 | 0.37389 | 0.0023368 | Sustained | FALSE | FALSE | Not_TMED_Event | 3431
SAN JUAN | 2023-04-26 14:35 | 2023-04-26 16:39 | 300 | 2:04 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANCO CONDUCTORES DEL SUELO | S23042600080 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 124 | 2023-04-26 | 37200 | keep | 0 | Apr | 2023 | 0.025337 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-04-26 14:50 | 2023-04-26 15:30 | 4 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23042600143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-04-26 | 160 | keep | 0 | Apr | 2023 | 0.00010898 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-04-26 14:51 | 2023-04-26 19:45 | 70 | 4:54 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | C23042600119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-04-26 | 20580 | keep | 0 | Apr | 2023 | 0.014017 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-04-26 14:54 | 2023-04-26 16:41 | 30 | 1:47 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO | S23042600182 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 107 | 2023-04-26 | 3210 | keep | 0 | Apr | 2023 | 0.0021863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-26 15:01 | 2023-04-27 06:48 | 20 | 15:47 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | B23042600132 | New_Event | Animals | Include | Include | Wildlife | 947 | 2023-04-26 | 18940 | keep | 0 | Apr | 2023 | 0.0129 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-04-26 15:03 | 2023-04-26 17:04 | 100 | 2:01 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23042600121 | New_Event | Animals | Include | Include | Wildlife | 121 | 2023-04-26 | 12100 | keep | 0 | Apr | 2023 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-04-26 15:06 | 2023-04-26 17:02 | 45 | 1:56 | P | DESGANCHE | 1 X 80 EN C/L SE REALIZO DESPEJE | R23042600052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-04-26 | 5220 | keep | 0 | Apr | 2023 | 0.0035553 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-04-26 15:14 | 2023-04-26 17:34 | 135 | 2:20 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN C/L SE DESGANCHO | B23042600134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-04-26 | 18900 | keep | 0 | Apr | 2023 | 0.012873 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
MAYAGÃœEZ | 2023-04-26 15:17 | 2023-04-26 18:14 | 25 | 2:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REEMPLAZAR BAJANTES SECUNDARIOS | M23042600153 | New_Event | Secondary Wire Break | Include | Include | Equipment | 177 | 2023-04-26 | 4425 | keep | 0 | Apr | 2023 | 0.0030138 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-26 15:19 | 2023-04-26 19:58 | 25 | 4:39 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER SE SECCIONALIZO CABLE SOTERRADO AVERIADO | B23042600135 | New_Event | UG Cable Fault | Include | Include | Equipment | 279 | 2023-04-26 | 6975 | keep | 0 | Apr | 2023 | 0.0047506 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-26 15:30 | 2023-04-26 18:47 | 34 | 3:17 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE ELIMINO PARARAYO | B23042600137 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 197 | 2023-04-26 | 6698 | keep | 0 | Apr | 2023 | 0.004562 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2023-04-26 15:51 | 2023-04-26 15:52 | 3941 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2304260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 3941 | keep | 0 | Apr | 2023 | 0.0026842 | 0.0026842 | Momentary | FALSE | FALSE | Not_TMED_Event | 3941
BAYAMON | 2023-04-26 15:52 | 2023-04-27 10:35 | 294 | 18:43 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE Y SE REPARO PUENTE ABIERTO | B23042600150 | New_Event | Primary Wire Break | Include | Include | Equipment | 1123 | 2023-04-26 | 330162 | keep | 0 | Apr | 2023 | 0.22487 | 0.00020024 | Sustained | FALSE | FALSE | Not_TMED_Event | 294
BARRANQUITAS | 2023-04-26 16:04 | 2023-04-26 18:57 | 30 | 2:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 20 EN CORTE DE LINEA SE REEMPLAZARON PIN POLE TOPS PARTIDOS | C23042600132 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 173 | 2023-04-26 | 5190 | keep | 0 | Apr | 2023 | 0.0035349 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-26 16:46 | 2023-04-26 20:01 | 13 | 3:15 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23042600196 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-04-26 | 2535 | keep | 0 | Apr | 2023 | 0.0017266 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-04-26 16:48 | 2023-04-26 16:50 | 2354 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2304260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-26 | 4708 | keep | 0 | Apr | 2023 | 0.0032066 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2023-04-26 16:51 | 2023-04-26 18:58 | 12 | 2:07 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN XMR SE REPARO BAJANTE PRIMARIO | B23042600162 | New_Event | Primary Wire Break | Include | Include | Equipment | 127 | 2023-04-26 | 1524 | keep | 0 | Apr | 2023 | 0.001038 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-26 16:57 | 2023-04-26 19:21 | 16 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S23042600199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2023-04-26 | 2304 | keep | 0 | Apr | 2023 | 0.0015692 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-04-26 17:01 | 2023-04-26 22:46 | 30 | 5:45 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA DESPEGAR CONDUCTOR CRUZADO CON POSTE Y SE CERRO C/L | B23042600167 | New_Event | Primary Wire Break | Include | Include | Equipment | 345 | 2023-04-26 | 10350 | keep | 0 | Apr | 2023 | 0.0070493 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-26 17:04 | 2023-04-26 18:26 | 10 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ABIERTA | S23042600201 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-04-26 | 820 | keep | 0 | Apr | 2023 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-26 17:09 | 2023-04-27 13:37 | 7 | 20:28 | P | ERROR HUMANO | SE CONECTO XMR CORRECTAMENTE | C23042600149 | New_Event | Human Error | Include | Include | Other | 1228 | 2023-04-26 | 8596 | keep | 0 | Apr | 2023 | 0.0058547 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-04-26 17:18 | 2023-04-26 17:35 | 1 | 0:17 | P | ANIMAL | 1 X 5 EN MONTURA CRUCE POR AVE | P23042600117 | New_Event | Animals | Include | Include | Wildlife | 17 | 2023-04-26 | 17 | keep | 0 | Apr | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-26 17:57 | 2023-04-26 17:58 | 1648 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR 2302-03 LLEVANDO 40% 2402-02 | R23042600065 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-04-26 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-26 17:57 | 2023-04-26 17:58 | 1675 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 2302-03 LLEVANDO 40% 2402-02 | R23042600065 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-26 | 1675 | keep | 0 | Apr | 2023 | 0.0011408 | 0.0011408 | Momentary | FALSE | FALSE | Not_TMED_Event | 1675
CANOVANAS | 2023-04-26 17:58 | 2023-04-26 20:11 | 183 | 2:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN XMR 2 X 65 , 2 X 80 , Y 2 X 100 EN CORTES DE LINEA | R23042600066 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 133 | 2023-04-26 | 24339 | keep | 0 | Apr | 2023 | 0.016577 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
BAYAMON | 2023-04-26 18:10 | 2023-04-27 12:38 | 30 | 18:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRAS EN PEDESTAL | B23042600196 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1108 | 2023-04-26 | 33240 | keep | 0 | Apr | 2023 | 0.02264 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-26 18:19 | 2023-04-27 14:00 | 10 | 19:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA POR LA MISMA CAPACIDAD | M23042600182 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1181 | 2023-04-26 | 11810 | keep | 0 | Apr | 2023 | 0.0080437 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-04-26 18:40 | 2023-04-26 19:20 | 50 | 0:40 | P | ANIMAL | 1 X 65 EN CL CRUCE DE FASE POR AVE | P23042600136 | New_Event | Animals | Include | Include | Wildlife | 40 | 2023-04-26 | 2000 | keep | 0 | Apr | 2023 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-26 19:07 | 2023-04-27 10:26 | 40 | 15:19 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23042600215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 919 | 2023-04-26 | 36760 | keep | 0 | Apr | 2023 | 0.025037 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-26 19:17 | 2023-04-27 11:09 | 10 | 15:52 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE TRANFORMADOR | S23042600217 | New_Event | Primary Wire Break | Include | Include | Equipment | 952 | 2023-04-26 | 9520 | keep | 0 | Apr | 2023 | 0.006484 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-04-26 19:47 | 2023-04-27 00:52 | 40 | 5:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23042600213 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 305 | 2023-04-26 | 12200 | keep | 0 | Apr | 2023 | 0.0083094 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-26 19:58 | 2023-04-28 17:12 | 25 | 45:14 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL PARA DAR SERVICIO DESDE T-9 @ T-12 BY-230428-01 | B23042600135 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 2714 | 2023-04-26 | 67850 | keep | 0 | Apr | 2023 | 0.046212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-26 20:11 | 2023-04-26 23:01 | 350 | 2:50 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | A23042600162 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-04-26 | 59500 | keep | 0 | Apr | 2023 | 0.040525 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
MAYAGÃœEZ | 2023-04-26 20:15 | 2023-04-27 02:24 | 30 | 6:09 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR IGUANA | M23042600022 | New_Event | Animals | Include | Include | Wildlife | 369 | 2023-04-26 | 11070 | keep | 0 | Apr | 2023 | 0.0075397 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-04-26 20:19 | 2023-04-26 20:20 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23042600227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-26 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
CANOVANAS | 2023-04-26 20:24 | 2023-04-27 09:46 | 3 | 13:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN XMR Y SE REEMPLAZO PORTAFUSIBLE | R23042600089 | New_Event | Cutout Failure | Include | Include | Equipment | 802 | 2023-04-26 | 2406 | keep | 0 | Apr | 2023 | 0.0016387 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2023-04-26 20:27 | 2023-04-27 06:20 | 60 | 9:53 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23042600178 | New_Event | Animals | Include | Include | Wildlife | 593 | 2023-04-26 | 35580 | keep | 0 | Apr | 2023 | 0.024233 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-04-26 21:05 | 2023-04-27 09:16 | 12 | 12:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA | B23042600228 | New_Event | Cutout Failure | Include | Include | Equipment | 731 | 2023-04-26 | 8772 | keep | 0 | Apr | 2023 | 0.0059746 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-04-26 21:09 | 2023-04-27 10:03 | 25 | 12:54 | P | CONDUCTOR ROTO O ABIERTO | 3 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A23042600167 | New_Event | Primary Wire Break | Include | Include | Equipment | 774 | 2023-04-26 | 19350 | keep | 0 | Apr | 2023 | 0.013179 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-04-26 21:30 | 2023-04-27 10:30 | 15 | 13:00 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN C/L | P23042600194 | New_Event | Primary Wire Break | Include | Include | Equipment | 780 | 2023-04-26 | 11700 | keep | 0 | Apr | 2023 | 0.0079688 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-04-26 21:41 | 2023-04-27 13:29 | 14 | 15:48 | P | TRANSFORMADOR AVERIADO | 1X15 EN XMR SE REMPLAZO XMR 75KVA X 75KVA - FASE @ TIERRA | S23042600227 | New_Event | Service Transformer Failure | Include | Include | Equipment | 948 | 2023-04-26 | 13272 | keep | 0 | Apr | 2023 | 0.0090395 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-04-26 21:42 | 2023-04-27 09:44 | 6 | 12:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | A23042600169 | New_Event | Cutout Failure | Include | Include | Equipment | 722 | 2023-04-26 | 4332 | keep | 0 | Apr | 2023 | 0.0029505 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-04-26 21:45 | 2023-04-27 02:57 | 80 | 5:12 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | C23042600174 | New_Event | Animals | Include | Include | Wildlife | 312 | 2023-04-26 | 24960 | keep | 0 | Apr | 2023 | 0.017 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-04-26 21:48 | 2023-04-27 15:55 | 343 | 18:07 | P | CAUSAS EXTERNAS | 3 X 100 Y 3 X 40 EN C/LS SE REMPLAZO POSTE PRIMARIO PARTIDO POR ACCIDENTE DE VEHICULO | C23042600175 | New_Event | Damage From Public | Include | Include | Public | 1087 | 2023-04-26 | 372841 | keep | 0 | Apr | 2023 | 0.25394 | 0.00023362 | Sustained | FALSE | FALSE | Not_TMED_Event | 343
ARECIBO | 2023-04-26 22:14 | 2023-04-27 09:22 | 50 | 11:08 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A23042600170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 668 | 2023-04-26 | 33400 | keep | 0 | Apr | 2023 | 0.022749 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-26 22:33 | 2023-04-27 07:26 | 56 | 8:53 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23042600240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 533 | 2023-04-26 | 29848 | keep | 0 | Apr | 2023 | 0.020329 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
CAGUAS | 2023-04-27 | 2023-04-27 20:15 | 8 | 20:15 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN XMR SE REMPLAZO XMR AVERIADO DE 50 KVA X 37.5 KVA | C23042700001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1215 | 2023-04-27 | 9720 | keep | 0 | Apr | 2023 | 0.0066202 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-27 00:05 | 2023-04-27 10:13 | 155 | 10:08 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23042700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 608 | 2023-04-27 | 94240 | keep | 0 | Apr | 2023 | 0.064186 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
BAYAMON | 2023-04-27 01:38 | 2023-04-27 10:10 | 1834 | 8:32 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE REMPLAZARON 3 FUSIBLES FUNDIDOS EN LA ALTA DEL TRANSFORMADOR SE TRANFIRIO CARGA AL BREAKER 9203-01 25% EN SERVICIO SE REEMPLAZO CAPACITOR TRIP | B23042700011 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 512 | 2023-04-27 | 939008 | keep | 0 | Apr | 2023 | 0.63955 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2023-04-27 01:38 | 2023-04-27 07:52 | 2324 | 6:14 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE REMPLAZARON 3 FUSIBLES FUNDIDOS EN LA ALTA DEL TRANSFORMADOR | B23042700011 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 374 | 2023-04-27 | 869176 | keep | 0 | Apr | 2023 | 0.59199 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
BAYAMON | 2023-04-27 01:38 | 2023-04-27 07:53 | 1570 | 6:15 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE REMPLAZARON 3 FUSIBLES FUNDIDOS EN LA ALTA DEL TRANSFORMADOR | B23042700011 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 375 | 2023-04-27 | 588750 | keep | 0 | Apr | 2023 | 0.40099 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
FAJARDO | 2023-04-27 02:04 | 2023-04-27 04:37 | 300 | 2:33 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO CAUSA | R23042700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2023-04-27 | 45900 | keep | 0 | Apr | 2023 | 0.031262 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2023-04-27 03:49 | 2023-04-27 06:50 | 28 | 3:01 | P | DESGANCHE | 1 X 30 EN C/L | C23042700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-04-27 | 5068 | keep | 0 | Apr | 2023 | 0.0034518 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2023-04-27 04:22 | 2023-04-27 04:23 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUTOR | M23042700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 4381 | keep | 0 | Apr | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
VEGA BAJA | 2023-04-27 04:25 | 2023-04-27 10:54 | 150 | 6:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | A23042700005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 389 | 2023-04-27 | 58350 | keep | 0 | Apr | 2023 | 0.039742 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-27 04:46 | 2023-04-27 04:48 | 34 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1116-02 LLEVA 30% 1115-04 | S2304270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-27 | 68 | keep | 0 | Apr | 2023 | 4.6314e-05 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
AGUADILLA | 2023-04-27 05:25 | 2023-04-27 07:47 | 721 | 2:22 | T | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR Y SE CERRO EL INTERRUPTOR | M23042700007 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 142 | 2023-04-27 | 102382 | keep | 0 | Apr | 2023 | 0.069732 | 0.00049107 | Sustained | FALSE | FALSE | Not_TMED_Event | 721
SAN JUAN | 2023-04-27 05:42 | 2023-04-27 05:43 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | S23042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
VEGA BAJA | 2023-04-27 05:45 | 2023-04-27 08:17 | 109 | 2:32 | P | ANIMAL | 1 X 15 EN XMR 1 X 30 C/L Y 1 X 65 EN C/L CRUCE POR LAGARTIJO | B23042700065 | New_Event | Animals | Include | Include | Wildlife | 152 | 2023-04-27 | 16568 | keep | 0 | Apr | 2023 | 0.011284 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
BAYAMON | 2023-04-27 05:52 | 2023-04-27 11:02 | 1 | 5:10 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE LINEA A TRANSFORMADOR | B23042700066 | New_Event | Primary Wire Break | Include | Include | Equipment | 310 | 2023-04-27 | 310 | keep | 0 | Apr | 2023 | 0.00021114 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-04-27 05:54 | 2023-04-27 05:55 | 215 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23042700001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 215 | keep | 0 | Apr | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
CAGUAS | 2023-04-27 06:08 | 2023-04-27 07:35 | 69 | 1:27 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23042700014 | New_Event | Animals | Include | Include | Wildlife | 87 | 2023-04-27 | 6003 | keep | 0 | Apr | 2023 | 0.0040886 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
MAYAGÃœEZ | 2023-04-27 06:18 | 2023-04-27 08:35 | 140 | 2:17 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | M23042700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-04-27 | 19180 | keep | 0 | Apr | 2023 | 0.013063 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2023-04-27 06:22 | 2023-04-27 10:37 | 30 | 4:15 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA SE RETIRO GATO QUE CRUZO FASE A TIERRA | M23042700012 | New_Event | Animals | Include | Include | Wildlife | 255 | 2023-04-27 | 7650 | keep | 0 | Apr | 2023 | 0.0052104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-04-27 06:47 | 2023-04-27 09:38 | 40 | 2:51 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23042700015 | New_Event | Animals | Include | Include | Wildlife | 171 | 2023-04-27 | 6840 | keep | 0 | Apr | 2023 | 0.0046587 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-04-27 07:13 | 2023-04-27 07:14 | 990 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | M23042700016 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-27 | 990 | keep | 0 | Apr | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
MAYAGÃœEZ | 2023-04-27 07:14 | 2023-04-27 10:05 | 15 | 2:51 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASES | M23042700018 | 1st_after_momentary | Animals | Include | Include | Wildlife | 171 | 2023-04-27 | 2565 | keep | 0 | Apr | 2023 | 0.001747 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-04-27 07:21 | 2023-04-27 10:05 | 40 | 2:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23042700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-04-27 | 6560 | keep | 0 | Apr | 2023 | 0.004468 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-04-27 07:24 | 2023-04-27 12:01 | 150 | 4:37 | P | ANIMAL | 2 X 65 EN C/L CRUCE X AVE | C23042700019 | New_Event | Animals | Include | Include | Wildlife | 277 | 2023-04-27 | 41550 | keep | 0 | Apr | 2023 | 0.0283 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-27 07:44 | 2023-04-27 10:29 | 35 | 2:45 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23042700106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-04-27 | 5775 | keep | 0 | Apr | 2023 | 0.0039333 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-04-27 07:47 | 2023-04-27 09:25 | 450 | 1:38 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE ABRIO PUENTES PARA SECCIONALIZAR LINEA PRIMARIA ZAFADA DE AISLADOR Y SE CERRO LAS OTRAS DOS CAJAS QUE SE HABIAN ABIERTO | M23042700023 | Partial_restoration | Primary To Primary Contact | Include | Include | Equipment | 98 | 2023-04-27 | 44100 | keep | 0 | Apr | 2023 | 0.030036 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-04-27 07:53 | 2023-04-27 07:55 | 1403 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECIERRA CERRADO X CONTROL | C23042700025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-27 | 2806 | keep | 0 | Apr | 2023 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
BAYAMON | 2023-04-27 07:53 | 2023-04-27 10:55 | 458 | 3:02 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZARON 3 FUSIBLES FUNDIDOS EN LA ALTA DEL TRANSFORMADOR SE ABRIO MACHETE Y SE CERRO PUENTE ABIERTO EN EL TRONCAL BY-230427-01 | B23042700011 | New_Event | Primary Wire Break | Include | Include | Equipment | 182 | 2023-04-27 | 83356 | keep | 0 | Apr | 2023 | 0.056773 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
SAN JUAN | 2023-04-27 07:58 | 2023-04-27 16:14 | 30 | 8:16 | P | CONDUCTOR ROTO O ABIERTO | 2X20 EN XMR SE REPARO PUENTE PRIMARIO ABIERTO DE LINEA @ CAJA DE XMR | S23042700012 | New_Event | Primary Wire Break | Include | Include | Equipment | 496 | 2023-04-27 | 14880 | keep | 0 | Apr | 2023 | 0.010135 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-27 08:04 | 2023-04-27 09:49 | 8 | 1:45 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | B23042700120 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-04-27 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-04-27 08:11 | 2023-04-27 22:01 | 40 | 13:50 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION EN V.S.MH-8 | S23042700016 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 830 | 2023-04-27 | 33200 | keep | 0 | Apr | 2023 | 0.022612 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-04-27 08:12 | 2023-04-27 08:13 | 1648 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | R23042700007 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-27 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-27 08:12 | 2023-04-27 08:13 | 1675 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR | R23042700007 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-27 | 1675 | keep | 0 | Apr | 2023 | 0.0011408 | 0.0011408 | Momentary | FALSE | FALSE | Not_TMED_Event | 1675
CANOVANAS | 2023-04-27 08:12 | 2023-04-27 10:58 | 48 | 2:46 | P | ANIMAL | 1 X 65 Y 1 X 40 EN C/L AVE | R23042700006 | New_Event | Animals | Include | Include | Wildlife | 166 | 2023-04-27 | 7968 | keep | 0 | Apr | 2023 | 0.005427 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CANOVANAS | 2023-04-27 08:13 | 2023-04-27 10:23 | 176 | 2:10 | P | ANIMAL | 1 X 80 Y 1 X 65 EN C/L AVE CRUZO LINEAS | R23042700010 | 1st_after_momentary | Animals | Include | Include | Wildlife | 130 | 2023-04-27 | 22880 | keep | 0 | Apr | 2023 | 0.015583 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
FAJARDO | 2023-04-27 08:15 | 2023-04-27 08:33 | 20 | 0:18 | P | CAUSAS EXTERNAS | 1 X 40 Y 1 X 50 EN C/L PERSONAL AJENO A LUMA DESGANCHANDO CRUZO LINEAS | R23042700008 | New_Event | Damage From Public | Include | Include | Public | 18 | 2023-04-27 | 360 | keep | 0 | Apr | 2023 | 0.00024519 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-27 08:18 | 2023-04-27 11:01 | 1 | 2:43 | P | MAL TIEMPO/RAYOS | 1 X 20 EN RISER DEL CLIENTE ALEGA QUE CAYO RAYO POR LAS LLUVIAS | S23042700019 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 163 | 2023-04-27 | 163 | keep | 0 | Apr | 2023 | 0.00011102 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-04-27 08:29 | 2023-04-27 12:41 | 150 | 4:12 | P | ANIMAL | 1X50 EN C/L, 1X40 EN OTRO C/L CRUCE POR AVE | C23042700034 | New_Event | Animals | Include | Include | Wildlife | 252 | 2023-04-27 | 37800 | keep | 0 | Apr | 2023 | 0.025745 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-04-27 08:31 | 2023-04-27 11:30 | 300 | 2:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | B23042700129 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2023-04-27 | 53700 | keep | 0 | Apr | 2023 | 0.036575 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
YAUCO | 2023-04-27 08:40 | 2023-04-27 15:00 | 25 | 6:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO PRIMARIO | P23042700042 | New_Event | Primary Wire Break | Include | Include | Equipment | 380 | 2023-04-27 | 9500 | keep | 0 | Apr | 2023 | 0.0064704 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-27 08:45 | 2023-04-27 10:48 | 150 | 2:03 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | A23042700028 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-04-27 | 18450 | keep | 0 | Apr | 2023 | 0.012566 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-04-27 08:46 | 2023-04-27 15:51 | 3 | 7:05 | P | NO SE REPORTO CAUSA | 1X25 DEL SU-23 @ MH-4 | S23042700030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 425 | 2023-04-27 | 1275 | keep | 0 | Apr | 2023 | 0.0008684 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-04-27 08:56 | 2023-04-27 08:57 | 770 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23042700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 770 | keep | 0 | Apr | 2023 | 0.00052444 | 0.00052444 | Momentary | FALSE | FALSE | Not_TMED_Event | 770
SAN JUAN | 2023-04-27 09:09 | 2023-04-27 09:14 | 220 | 0:05 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S23042700039 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-04-27 | 1100 | keep | 0 | Apr | 2023 | 0.0007492 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-04-27 09:09 | 2023-04-27 09:14 | 870 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S23042700039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-04-27 | 4350 | keep | 0 | Apr | 2023 | 0.0029628 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2023-04-27 09:17 | 2023-04-27 12:08 | 6 | 2:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C23042700046 | New_Event | Cutout Failure | Include | Include | Equipment | 171 | 2023-04-27 | 1026 | keep | 0 | Apr | 2023 | 0.0006988 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-27 09:22 | 2023-04-27 13:06 | 20 | 3:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR/LEVANTAR TRAMO SECUNDARIO DEL SUELO | S23042700042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 224 | 2023-04-27 | 4480 | keep | 0 | Apr | 2023 | 0.0030513 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-04-27 09:23 | 2023-04-27 13:56 | 382 | 4:33 | S | ANIMAL | DISPARO DE SUBESTACION POR IGUANA QUE CRUZO FASE A TIERRA EN UN PARARRAYOS | M23042700053 | New_Event | Animals | Include | Include | Wildlife | 273 | 2023-04-27 | 104286 | keep | 0 | Apr | 2023 | 0.071029 | 0.00026018 | Sustained | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-04-27 09:23 | 2023-04-27 13:56 | 39 | 4:33 | S | ANIMAL | DISPARO DE SUBESTACION POR IGUANA QUE CRUZO FASE A TIERRA EN UN PARARRAYOS | M23042700053 | New_Event | Animals | Include | Include | Wildlife | 273 | 2023-04-27 | 10647 | keep | 0 | Apr | 2023 | 0.0072516 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2023-04-27 09:25 | 2023-04-27 13:00 | 10 | 3:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA ZAFADA DE AISLADOR Y SE CERRO PUENTES | M23042700023 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2023-04-27 | 2150 | keep | 0 | Apr | 2023 | 0.0014644 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-27 09:27 | 2023-04-27 09:30 | 2179 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | R23042700029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-27 | 6537 | keep | 0 | Apr | 2023 | 0.0044523 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
FAJARDO | 2023-04-27 09:39 | 2023-04-27 12:56 | 18 | 3:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE Y CONEXIONES SECUNDARIAS | R23042700032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 197 | 2023-04-27 | 3546 | keep | 0 | Apr | 2023 | 0.0024152 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2023-04-27 09:52 | 2023-04-27 14:03 | 90 | 4:11 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCO ROTO | R23042700053 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 251 | 2023-04-27 | 22590 | keep | 0 | Apr | 2023 | 0.015386 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-04-27 09:53 | 2023-04-27 12:19 | 1 | 2:26 | P | DESGANCHE | 1 X 20 EN RISER DESGANCHE | B23042700153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-04-27 | 146 | keep | 0 | Apr | 2023 | 9.944e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-04-27 10:03 | 2023-04-27 10:26 | 1527 | 0:23 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR VERIFICAR PERSONAL TRABAJANDO EN EL AREA | A23042700049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2023-04-27 | 35121 | keep | 0 | Apr | 2023 | 0.023921 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
CAGUAS | 2023-04-27 10:15 | 2023-04-27 11:50 | 5 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23042700057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-04-27 | 475 | keep | 0 | Apr | 2023 | 0.00032352 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-04-27 10:26 | 2023-04-27 15:50 | 25 | 5:24 | P | CONDUCTOR ROTO O ABIERTO | 3 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A23042600167 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 324 | 2023-04-27 | 8100 | keep | 0 | Apr | 2023 | 0.0055169 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-04-27 10:26 | 2023-04-27 11:55 | 30 | 1:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23042700053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-04-27 | 2670 | keep | 0 | Apr | 2023 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-27 10:35 | 2023-04-27 10:36 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23042700069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 45 | keep | 0 | Apr | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-04-27 10:38 | 2023-04-27 10:46 | 1531 | 0:08 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 20% DE SU CARGA TRANSFERIDA AL 1424-08 LLEVA 15% DEL 1204-05 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23042700070 | New_Event | Feeder Load Transferred | Include | Include | Other | 8 | 2023-04-27 | 12248 | keep | 0 | Apr | 2023 | 0.0083421 | 0.0010428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1531
SAN JUAN | 2023-04-27 10:38 | 2023-04-27 10:46 | 4232 | 0:08 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 20% DE SU CARGA TRANSFERIDA AL 1424-08 LLEVA 15% DEL 1204-05 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23042700070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 8 | 2023-04-27 | 33856 | keep | 0 | Apr | 2023 | 0.023059 | 0.0028824 | Sustained | FALSE | FALSE | Not_TMED_Event | 4232
SAN JUAN | 2023-04-27 10:46 | 2023-04-27 12:30 | 500 | 1:44 | P | NO SE REPORTO CAUSA | SE CERRO PB 1336-08A | S23042700062 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-04-27 | 52000 | keep | 0 | Apr | 2023 | 0.035417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-04-27 10:48 | 2023-04-27 10:49 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23042700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
BAYAMON | 2023-04-27 10:55 | 2023-04-27 12:42 | 917 | 1:47 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZARON 3 FUSIBLES FUNDIDOS EN LA ALTA DEL TRANSFORMADOR SE CERRO PUENTE ABIERTO EN EL TRONCAL BY-230427-01 | B23042700011 | New_Event | Primary Wire Break | Include | Include | Equipment | 107 | 2023-04-27 | 98119 | keep | 0 | Apr | 2023 | 0.066828 | 0.00062456 | Sustained | FALSE | FALSE | Not_TMED_Event | 917
BAYAMON | 2023-04-27 11:08 | 2023-04-27 11:42 | 5 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE DE XMR | B23042700173 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-04-27 | 170 | keep | 0 | Apr | 2023 | 0.00011579 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-04-27 11:08 | 2023-04-27 11:41 | 1 | 0:33 | P | DESGANCHE | 1 X 50 EN C/L | C23042700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-04-27 | 33 | keep | 0 | Apr | 2023 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-27 11:12 | 2023-04-27 11:13 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042700068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 1017 | keep | 0 | Apr | 2023 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
CANOVANAS | 2023-04-27 11:26 | 2023-04-27 18:26 | 130 | 7:00 | P | DESGANCHE | 1 X 20, 1 X 50 Y 1 X 65 EN CORTES DE LINEA | R23042700073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 420 | 2023-04-27 | 54600 | keep | 0 | Apr | 2023 | 0.037188 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2023-04-27 11:32 | 2023-04-27 12:08 | 10 | 0:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SERCUNDARIO | R23042700049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 36 | 2023-04-27 | 360 | keep | 0 | Apr | 2023 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-27 11:35 | 2023-04-27 16:20 | 13 | 4:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042700185 | New_Event | Secondary Wire Break | Include | Include | Equipment | 285 | 2023-04-27 | 3705 | keep | 0 | Apr | 2023 | 0.0025235 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-04-27 11:44 | 2023-04-27 14:10 | 10 | 2:26 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE REALIZO DESGANCHE | M23042700084 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 146 | 2023-04-27 | 1460 | keep | 0 | Apr | 2023 | 0.0009944 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-27 11:50 | 2023-04-27 13:49 | 30 | 1:59 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | S23042700219 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-04-27 | 3570 | keep | 0 | Apr | 2023 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-27 12:03 | 2023-04-27 14:50 | 1 | 2:47 | P | ANIMAL | 2 X 50 EN RISER CRUCE X REPTIL | C23042700081 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-04-27 | 167 | keep | 0 | Apr | 2023 | 0.00011374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-27 12:37 | 2023-04-28 12:26 | 100 | 23:49 | P | ANIMAL | 1X50 EN CONVERTIDOR SE RETIRO UNA CULEBRA (SERPIENTE) | B23042700309 | New_Event | Animals | Include | Include | Wildlife | 1429 | 2023-04-27 | 142900 | keep | 0 | Apr | 2023 | 0.097329 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-27 12:42 | 2023-04-28 14:10 | 11 | 25:28 | P | TRANSFORMADOR AVERIADO | 1 X 15 EN TRANSFORMADOR SE REMPLAZO TRANSFORMADOR DE 37.5 KVA POR 50 KVA | A23042700076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1528 | 2023-04-27 | 16808 | keep | 0 | Apr | 2023 | 0.011448 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
VEGA BAJA | 2023-04-27 12:42 | 2023-04-27 21:03 | 1 | 8:21 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA DESGANCHE | B23042700252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 501 | 2023-04-27 | 501 | keep | 0 | Apr | 2023 | 0.00034123 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-27 12:44 | 2023-04-27 14:37 | 8 | 1:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR DESGANCHE | B23042700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-04-27 | 904 | keep | 0 | Apr | 2023 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-04-27 12:50 | 2023-04-27 13:15 | 1 | 0:25 | P | ARBOL SOBRE LINEA | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARAN CONEXIONES SE RETIRO ARBOL | A23042700034 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 25 | 2023-04-27 | 25 | keep | 0 | Apr | 2023 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-27 12:56 | 2023-04-27 13:15 | 13 | 0:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR BARRA DE PEDESTAL | C23042700095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 19 | 2023-04-27 | 247 | keep | 0 | Apr | 2023 | 0.00016823 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-04-27 13:11 | 2023-04-27 15:19 | 20 | 2:08 | P | NO SE REPORTO CAUSA | 1 X 40 EN CL NO SE REPORTO CAUSA | A23042700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2023-04-27 | 2560 | keep | 0 | Apr | 2023 | 0.0017436 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-04-27 13:23 | 2023-04-27 13:24 | 1057 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23042700104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 1057 | keep | 0 | Apr | 2023 | 0.00071992 | 0.00071992 | Momentary | FALSE | FALSE | Not_TMED_Event | 1057
SAN JUAN | 2023-04-27 13:29 | 2023-04-27 13:30 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23042700304 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 4291 | keep | 0 | Apr | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-04-27 13:30 | 2023-04-27 16:12 | 14 | 2:42 | P | TRANSFORMADOR AVERIADO | 1X15 EN XMR SE REMPLAZO XMR 75KVA X 75KVA - FASE @ TIERRA | S23042600227 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 162 | 2023-04-27 | 2268 | keep | 0 | Apr | 2023 | 0.0015447 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-27 13:32 | 2023-04-27 17:23 | 12 | 3:51 | P | DESGANCHE | 2X80 EN C/L DESGANCHE | S23042700306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 231 | 2023-04-27 | 2772 | keep | 0 | Apr | 2023 | 0.001888 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-04-27 13:32 | 2023-04-27 19:48 | 40 | 6:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L REMPLAZO CAJA QUEMADA | C23042700106 | New_Event | Cutout Failure | Include | Include | Equipment | 376 | 2023-04-27 | 15040 | keep | 0 | Apr | 2023 | 0.010244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-04-27 13:36 | 2023-04-27 14:30 | 1 | 0:54 | P | ANIMAL | 2 X 65 EN C/L AVE CRUZO LINEAS | P23042700097 | New_Event | Animals | Include | Include | Wildlife | 54 | 2023-04-27 | 54 | keep | 0 | Apr | 2023 | 3.6779e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-27 13:41 | 2023-04-27 17:54 | 75 | 4:13 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23042700221 | New_Event | Vegetation Contact | Include | Include | Vegetation | 253 | 2023-04-27 | 18975 | keep | 0 | Apr | 2023 | 0.012924 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-04-27 14:01 | 2023-04-27 14:02 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042700108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 1709 | keep | 0 | Apr | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
FAJARDO | 2023-04-27 14:02 | 2023-04-27 17:50 | 1 | 3:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 EN CAJA PRIMARIA SE REPARO BAJATE SAFADO HACIA CAJA PRIMARIA | R23042700068 | New_Event | Primary Wire Break | Include | Include | Equipment | 228 | 2023-04-27 | 228 | keep | 0 | Apr | 2023 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-27 14:10 | 2023-04-27 15:36 | 1510 | 1:26 | T | DESGANCHE | CG-230427-01 DISPARO DE BKR, SE SECCIONALIZO EL ALIMENTADOR POR DESGANCHE | C23042700110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-04-27 | 129860 | keep | 0 | Apr | 2023 | 0.088447 | 0.0010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1510
CAGUAS | 2023-04-27 14:25 | 2023-04-27 16:12 | 25 | 1:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | C23042700116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-04-27 | 2675 | keep | 0 | Apr | 2023 | 0.0018219 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-04-27 14:27 | 2023-04-27 14:28 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042700118 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 1709 | keep | 0 | Apr | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
BAYAMON | 2023-04-27 14:37 | 2023-04-27 19:34 | 14 | 4:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO CAJA PRIMARIA QUEMADA | B23042700235 | New_Event | Cutout Failure | Include | Include | Equipment | 297 | 2023-04-27 | 4158 | keep | 0 | Apr | 2023 | 0.002832 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-04-27 14:46 | 2023-04-27 14:50 | 220 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S23042700361 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-04-27 | 880 | keep | 0 | Apr | 2023 | 0.00059936 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-04-27 14:46 | 2023-04-27 14:50 | 870 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S23042700361 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-27 | 3480 | keep | 0 | Apr | 2023 | 0.0023702 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
HUMACAO | 2023-04-27 14:50 | 2023-04-27 15:30 | 1 | 0:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L Y 1 X 10 EN BANCO DE XMR REMPLAZO PORTAFUSIBLE QUEMADO | C23042700122 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2023-04-27 | 40 | keep | 0 | Apr | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-27 14:53 | 2023-04-27 16:47 | 14 | 1:54 | P | TRANSFORMADOR AVERIADO | SE RELOCALIZO SECUNDARIA PARA TRANSFERIR CARGA A XMR ALEDAÃ‘O Y SE REFIRIO PARA CAMBIO DE XMR AVERIADO | S23042700370 | New_Event | Service Transformer Failure | Include | Include | Equipment | 114 | 2023-04-27 | 1596 | keep | 0 | Apr | 2023 | 0.001087 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-04-27 15:03 | 2023-04-27 21:05 | 6 | 6:02 | P | CONDUCTOR ROTO O ABIERTO | SE CONECTO BAJANTE DE CAJA A XMR NO FUNDIO | C23042700128 | New_Event | Primary Wire Break | Include | Include | Equipment | 362 | 2023-04-27 | 2172 | keep | 0 | Apr | 2023 | 0.0014793 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-04-27 15:07 | 2023-04-27 16:59 | 7 | 1:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23042700129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 112 | 2023-04-27 | 784 | keep | 0 | Apr | 2023 | 0.00053398 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-04-27 15:19 | 2023-04-27 18:32 | 80 | 3:13 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE CERRO PUENTE PRIMARIO DE LINEA @ CAJA | S23042700409 | New_Event | Primary Wire Break | Include | Include | Equipment | 193 | 2023-04-27 | 15440 | keep | 0 | Apr | 2023 | 0.010516 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-04-27 15:36 | 2023-04-27 17:15 | 8 | 1:39 | P | PARARRAYOS DEFECTUOSO | 1 X 25 EN CORTE DE LINEA SE REEMPLAZO PARARRAYO EXPLOTADO. | R23042700073 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 99 | 2023-04-27 | 792 | keep | 0 | Apr | 2023 | 0.00053943 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-27 15:36 | 2023-04-27 18:23 | 302 | 2:47 | P | DESGANCHE | CG-230427-01 SE REALIZO DESGANCHE DE PISO Y CERRO MACHETES | C23042700110 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-04-27 | 50434 | keep | 0 | Apr | 2023 | 0.03435 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-04-27 15:45 | 2023-04-27 19:38 | 100 | 3:53 | P | DESGANCHE | 1 X 20, 1 X 50 Y 1 X 65 EN CORTES DE LINEA | R23042700075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-04-27 | 23300 | keep | 0 | Apr | 2023 | 0.01587 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-27 15:46 | 2023-04-28 12:09 | 1 | 20:23 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO HACIA CLIENTE | S23042700431 | New_Event | Primary Wire Break | Include | Include | Equipment | 1223 | 2023-04-27 | 1223 | keep | 0 | Apr | 2023 | 0.00083298 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-27 15:54 | 2023-04-27 18:52 | 238 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L FUERTES LLUVIAS | C23042700146 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-04-27 | 42364 | keep | 0 | Apr | 2023 | 0.028854 | 0.0001621 | Sustained | FALSE | FALSE | Not_TMED_Event | 238
AGUADILLA | 2023-04-27 16:08 | 2023-04-27 17:34 | 100 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23042700130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-04-27 | 8600 | keep | 0 | Apr | 2023 | 0.0058574 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-27 16:12 | 2023-04-27 17:39 | 817 | 1:27 | T | DESGANCHE | SE REALIZO DESGANCHE DE PISO | C23042700153 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-04-27 | 71079 | keep | 0 | Apr | 2023 | 0.048412 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-27 16:23 | 2023-04-27 18:45 | 2796 | 2:22 | P | NO SE REPORTO CAUSA | SE CERRO PB 1336-07A | S23042700438 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2023-04-27 | 397032 | keep | 0 | Apr | 2023 | 0.27042 | 0.0019043 | Sustained | FALSE | FALSE | Not_TMED_Event | 2796
HUMACAO | 2023-04-27 16:27 | 2023-04-28 10:52 | 18 | 18:25 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 37.5 X 37.5 | C23042700158 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1105 | 2023-04-27 | 19890 | keep | 0 | Apr | 2023 | 0.013547 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-04-27 16:30 | 2023-04-28 09:20 | 20 | 16:50 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23042700138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1010 | 2023-04-27 | 20200 | keep | 0 | Apr | 2023 | 0.013758 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-27 16:35 | 2023-04-27 17:00 | 6 | 0:25 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA RETEZAR LINEA SECUNDARIA ARRIADA | R23042700085 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 25 | 2023-04-27 | 150 | keep | 0 | Apr | 2023 | 0.00010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-04-27 16:35 | 2023-04-27 19:00 | 50 | 2:25 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R23042700084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2023-04-27 | 7250 | keep | 0 | Apr | 2023 | 0.0049379 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-27 16:47 | 2023-04-27 19:26 | 1381 | 2:39 | T | ALIMENTADOR AMARRADO | CARGA TRANSFERIDA AL 1204-01 SE REALIZARON OPERACIONES DE CAMPO PARA SECCIONALIZAR DESCONECTIVO DEFECTUOSO Y SE DEJO 100% EN SERVICIO | S23042700481 | New_Event | Feeder Load Transferred | Include | Include | Other | 159 | 2023-04-27 | 219579 | keep | 0 | Apr | 2023 | 0.14955 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2023-04-27 16:47 | 2023-04-27 19:26 | 4944 | 2:39 | T | DESCONECTIVO DEFECTUOSO | CARGA TRANSFERIDA AL 1204-01 SE REALIZARON OPERACIONES DE CAMPO PARA SECCIONALIZAR DESCONECTIVO DEFECTUOSO Y SE DEJO 100% EN SERVICIO | S23042700481 | New_Event | Switch Failure | Include | Include | Equipment | 159 | 2023-04-27 | 786096 | keep | 0 | Apr | 2023 | 0.53541 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
SAN JUAN | 2023-04-27 16:59 | 2023-04-27 17:20 | 137 | 0:21 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 SE ENCONTRÃ“ PUENTE ABIERTO EN LINEA 3100 AL ABRIR BKR 3110 PARA VÃA LIBRE | S23042700716 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-04-27 | 2877 | keep | 0 | Apr | 2023 | 0.0019595 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-04-27 16:59 | 2023-04-27 17:20 | 760 | 0:21 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 SE ENCONTRÃ“ PUENTE ABIERTO EN LINEA 3100 AL ABRIR BKR 3110 PARA VÃA LIBRE | S23042700716 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-04-27 | 15960 | keep | 0 | Apr | 2023 | 0.01087 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-04-27 16:59 | 2023-04-27 17:20 | 1225 | 0:21 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 SE ENCONTRÃ“ PUENTE ABIERTO EN LINEA 3100 AL ABRIR BKR 3110 PARA VÃA LIBRE | S23042700726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-04-27 | 25725 | keep | 0 | Apr | 2023 | 0.017521 | 0.00083434 | Sustained | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-04-27 16:59 | 2023-04-27 17:20 | 1452 | 0:21 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 SE ENCONTRÃ“ PUENTE ABIERTO EN LINEA 3100 AL ABRIR BKR 3110 PARA VÃA LIBRE | S23042700726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-04-27 | 30492 | keep | 0 | Apr | 2023 | 0.020768 | 0.00098895 | Sustained | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-04-27 16:59 | 2023-04-27 17:20 | 616 | 0:21 | S | LINEA DE TRANSMISION 38KV | OPERACION LINEA 3100 SE ENCONTRÃ“ PUENTE ABIERTO EN LINEA 3100 AL ABRIR BKR 3110 PARA VÃA LIBRE | S23042700726 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 21 | 2023-04-27 | 12936 | keep | 0 | Apr | 2023 | 0.0088107 | 0.00041955 | Sustained | FALSE | FALSE | Not_TMED_Event | 616
FAJARDO | 2023-04-27 17:11 | 2023-04-27 21:42 | 130 | 4:31 | P | DESGANCHE | 1 X 30 Y 1 X 50 EN CORTE DE LINEA | R23042700089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2023-04-27 | 35230 | keep | 0 | Apr | 2023 | 0.023995 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CAGUAS | 2023-04-27 17:39 | 2023-04-27 18:02 | 25 | 0:23 | P | DESGANCHE | 1 X 50 EN C/L | C23042700116 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-04-27 | 575 | keep | 0 | Apr | 2023 | 0.00039163 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-27 17:59 | 2023-04-27 18:00 | 1702 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | C23042700188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-27 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-04-27 18:00 | 2023-04-27 19:34 | 185 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 Y 1 X 30 EN C/LS FUERTES LLUVIAS | C23042700189 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-04-27 | 17390 | keep | 0 | Apr | 2023 | 0.011844 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
CANOVANAS | 2023-04-27 18:28 | 2023-04-27 19:53 | 50 | 1:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R23042700110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-04-27 | 4250 | keep | 0 | Apr | 2023 | 0.0028947 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-27 18:41 | 2023-04-27 20:23 | 75 | 1:42 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23042700197 | New_Event | Animals | Include | Include | Wildlife | 102 | 2023-04-27 | 7650 | keep | 0 | Apr | 2023 | 0.0052104 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2023-04-27 19:02 | 2023-04-28 10:00 | 10 | 14:58 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A23042700129 | New_Event | Primary Wire Break | Include | Include | Equipment | 898 | 2023-04-27 | 8980 | keep | 0 | Apr | 2023 | 0.0061162 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-27 19:21 | 2023-04-27 19:56 | 100 | 0:35 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | R23042700126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 35 | 2023-04-27 | 3500 | keep | 0 | Apr | 2023 | 0.0023838 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-27 19:25 | 2023-04-28 06:56 | 33 | 11:31 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23042700266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 691 | 2023-04-27 | 22803 | keep | 0 | Apr | 2023 | 0.015531 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
SAN JUAN | 2023-04-27 19:26 | 2023-04-27 21:09 | 14 | 1:43 | P | TRANSFORMADOR AVERIADO | SE RELOCALIZO SECUNDARIA PARA TRANSFERIR CARGA A XMR ALEDAÃ‘O Y SE REFIRIO PARA CAMBIO DE XMR AVERIADO | S23042700370 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 103 | 2023-04-27 | 1442 | keep | 0 | Apr | 2023 | 0.00098214 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-04-27 19:31 | 2023-04-28 06:51 | 50 | 11:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA EN C/L | P23042700146 | New_Event | Cutout Failure | Include | Include | Equipment | 680 | 2023-04-27 | 34000 | keep | 0 | Apr | 2023 | 0.023157 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-27 19:41 | 2023-04-27 19:42 | 1834 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 1834 | keep | 0 | Apr | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
VEGA BAJA | 2023-04-27 19:45 | 2023-04-28 15:03 | 40 | 19:18 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042700131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1158 | 2023-04-27 | 46320 | keep | 0 | Apr | 2023 | 0.031548 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-27 19:56 | 2023-04-28 14:16 | 24 | 18:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23042701147 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1100 | 2023-04-27 | 26400 | keep | 0 | Apr | 2023 | 0.017981 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
FAJARDO | 2023-04-27 20:12 | 2023-04-27 23:05 | 94 | 2:53 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | R23042700142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-04-27 | 16262 | keep | 0 | Apr | 2023 | 0.011076 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
CAGUAS | 2023-04-27 20:16 | 2023-04-28 10:04 | 50 | 13:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23042700214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 828 | 2023-04-27 | 41400 | keep | 0 | Apr | 2023 | 0.028197 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-27 20:31 | 2023-04-28 11:12 | 55 | 14:41 | P | ANIMAL | 2X80 EN C/L CRUCE POR AVE | B23042700275 | New_Event | Animals | Include | Include | Wildlife | 881 | 2023-04-27 | 48455 | keep | 0 | Apr | 2023 | 0.033002 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BAYAMON | 2023-04-27 20:32 | 2023-04-28 10:34 | 23 | 14:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X15 EN XMR SE REMPLAZO CONECTOR SECUNDARIO QUEMADO | B23042700277 | New_Event | Secondary Wire Break | Include | Include | Equipment | 842 | 2023-04-27 | 19366 | keep | 0 | Apr | 2023 | 0.01319 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-04-27 20:45 | 2023-04-28 15:53 | 21 | 19:08 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER AVERIA VIEJA DE T512 A T513 Y AVERIA NUEVA DE T514 A T513 | B23042700283 | New_Event | UG Cable Fault | Include | Include | Equipment | 1148 | 2023-04-27 | 24108 | keep | 0 | Apr | 2023 | 0.01642 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-04-27 20:54 | 2023-04-27 23:42 | 150 | 2:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A23042700140 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 168 | 2023-04-27 | 25200 | keep | 0 | Apr | 2023 | 0.017164 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-04-27 21:00 | 2023-04-28 10:00 | 8 | 13:00 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23042700159 | New_Event | Animals | Include | Include | Wildlife | 780 | 2023-04-27 | 6240 | keep | 0 | Apr | 2023 | 0.00425 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-04-27 21:18 | 2023-04-27 23:36 | 50 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO | P23042700166 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2023-04-27 | 6900 | keep | 0 | Apr | 2023 | 0.0046996 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-27 21:35 | 2023-04-27 21:36 | 2900 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042700216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 2900 | keep | 0 | Apr | 2023 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BAYAMON | 2023-04-27 21:43 | 2023-04-28 09:55 | 92 | 12:12 | P | DESGANCHE | 1X140 EN C/L DESGANCHE | B27042700311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 732 | 2023-04-27 | 67344 | keep | 0 | Apr | 2023 | 0.045868 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
CANOVANAS | 2023-04-27 22:03 | 2023-04-28 12:32 | 70 | 14:29 | P | NO SE REPORTO CAUSA | 1 X 40 EN SU-70 | R23042700172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 869 | 2023-04-27 | 60830 | keep | 0 | Apr | 2023 | 0.041431 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-04-27 22:05 | 2023-04-28 22:13 | 7 | 24:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 15 EN XMR | S23042701165 | New_Event | Cutout Failure | Include | Include | Equipment | 1448 | 2023-04-27 | 10136 | keep | 0 | Apr | 2023 | 0.0069036 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-27 22:19 | 2023-04-28 14:10 | 16 | 15:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042700329 | New_Event | Secondary Wire Break | Include | Include | Equipment | 951 | 2023-04-27 | 15216 | keep | 0 | Apr | 2023 | 0.010364 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-04-27 22:29 | 2023-04-28 17:15 | 18 | 18:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23042700330 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1126 | 2023-04-27 | 20268 | keep | 0 | Apr | 2023 | 0.013804 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-04-27 22:41 | 2023-04-28 09:38 | 70 | 10:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23042700144 | New_Event | Cutout Failure | Include | Include | Equipment | 657 | 2023-04-27 | 45990 | keep | 0 | Apr | 2023 | 0.031324 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-04-27 23:41 | 2023-04-27 23:42 | 2512 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SOLO LLEVA EL 60% DE SU CARGA | R23042700179 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-27 | 2512 | keep | 0 | Apr | 2023 | 0.0017109 | 0.0017109 | Momentary | FALSE | FALSE | Not_TMED_Event | 2512
CANOVANAS | 2023-04-27 23:42 | 2023-04-28 09:23 | 50 | 9:41 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R23042700180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 581 | 2023-04-27 | 29050 | keep | 0 | Apr | 2023 | 0.019786 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-28 00:12 | 2023-04-28 02:56 | 151 | 2:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23042800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-04-28 | 24764 | keep | 0 | Apr | 2023 | 0.016867 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
SAN JUAN | 2023-04-28 00:17 | 2023-04-28 17:42 | 50 | 17:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZARON 2 CAJAS PRIMARIAS | S23042800001 | New_Event | Cutout Failure | Include | Include | Equipment | 1045 | 2023-04-28 | 52250 | keep | 0 | Apr | 2023 | 0.035587 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-04-28 00:24 | 2023-04-28 10:03 | 150 | 9:39 | P | DESGANCHE | 3 X 65 EN C/L Y DESGANCHE | R23042800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 579 | 2023-04-28 | 86850 | keep | 0 | Apr | 2023 | 0.059153 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2023-04-28 00:30 | 2023-04-28 10:28 | 12 | 9:58 | P | PARARRAYOS DEFECTUOSO | 1 X 10 EN XMR SE ELIMINO PARARRAYO | P23042800001 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 598 | 2023-04-28 | 7176 | keep | 0 | Apr | 2023 | 0.0048875 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-28 00:43 | 2023-04-28 06:07 | 4291 | 5:24 | T | CONDUCTOR ROTO O ABIERTO | SJ-230428-01 SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO N/O CONTRA 1204-03 | S23042800064 | New_Event | Primary Wire Break | Include | Include | Equipment | 324 | 2023-04-28 | 1390284 | keep | 0 | Apr | 2023 | 0.94692 | 0.0029226 | Sustained | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-04-28 00:43 | 2023-04-28 00:48 | 1381 | 0:05 | T | LINEA DE TRANSMISION 115KV | RECERRO 1204-02 Y ABRIO 37930 Y 37940 SE RETIRO CARGA 1204-01 Y 1204-02 Y SE CCE CERRO 37930 Y 37940 SE CERRO 1204-01 QUE LLEVA 1204-03 Y 4, SE DEJA FUERA 1204-02 PARA QUE PATRULLEN Y VERIFIQUEN SETTINGS | S23042800064 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-04-28 | 6905 | keep | 0 | Apr | 2023 | 0.004703 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2023-04-28 00:43 | 2023-04-28 00:48 | 1381 | 0:05 | T | LINEA DE TRANSMISION 115KV | RECERRO 1204-02 Y ABRIO 37930 Y 37940 SE RETIRO CARGA 1204-01 Y 1204-02 Y SE CCE CERRO 37930 Y 37940 SE CERRO 1204-01 QUE LLEVA 1204-03 Y 4, SE DEJA FUERA 1204-02 PARA QUE PATRULLEN Y VERIFIQUEN SETTING | S23042800064 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-04-28 | 6905 | keep | 0 | Apr | 2023 | 0.004703 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2023-04-28 00:43 | 2023-04-28 00:48 | 10211 | 0:05 | T | LINEA DE TRANSMISION 115KV | RECERRO 1204-02 Y DISPARO 37930 Y 37940 SE RETIRO CARGA Y SE CERRO 37930 Y 37940 SE ENERGIZO CARGA Y SE DEJO FUERA 1204-02 PARA QUE PATRULLEN | S23042800064 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-04-28 | 51055 | keep | 0 | Apr | 2023 | 0.034773 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
CAGUAS | 2023-04-28 00:52 | 2023-04-28 00:53 | 1089 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 50% DE SU CARGA | C2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 1089 | keep | 0 | Apr | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
CAGUAS | 2023-04-28 00:55 | 2023-04-28 09:00 | 100 | 8:05 | P | DESGANCHE | 1 X 100 EN RISER SE DESGANCHO BAMBUA | C23042800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2023-04-28 | 48500 | keep | 0 | Apr | 2023 | 0.033033 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-04-28 01:14 | 2023-04-28 01:15 | 2192 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 2192 | keep | 0 | Apr | 2023 | 0.001493 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
CANOVANAS | 2023-04-28 01:27 | 2023-04-28 09:04 | 90 | 7:37 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23042800011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2023-04-28 | 41130 | keep | 0 | Apr | 2023 | 0.028013 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CANOVANAS | 2023-04-28 03:11 | 2023-04-28 03:12 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23042800034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 3464 | keep | 0 | Apr | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
SAN JUAN | 2023-04-28 03:20 | 2023-04-28 13:15 | 54 | 9:55 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR | S23042800151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 595 | 2023-04-28 | 32130 | keep | 0 | Apr | 2023 | 0.021884 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
BARRANQUITAS | 2023-04-28 03:31 | 2023-04-28 14:35 | 22 | 11:04 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | C23042800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 664 | 2023-04-28 | 14608 | keep | 0 | Apr | 2023 | 0.0099494 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-04-28 03:35 | 2023-04-28 17:07 | 15 | 13:32 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23042800153 | New_Event | Primary Wire Break | Include | Include | Equipment | 812 | 2023-04-28 | 12180 | keep | 0 | Apr | 2023 | 0.0082957 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-04-28 04:13 | 2023-04-28 14:08 | 16 | 9:55 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23042800041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 595 | 2023-04-28 | 9520 | keep | 0 | Apr | 2023 | 0.006484 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
YAUCO | 2023-04-28 04:23 | 2023-04-28 10:25 | 20 | 6:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DF LINEA POR LLUVIA Y VIENTO | M23042800003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 362 | 2023-04-28 | 7240 | keep | 0 | Apr | 2023 | 0.0049311 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-28 05:51 | 2023-04-28 09:19 | 21 | 3:28 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23042800006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2023-04-28 | 4368 | keep | 0 | Apr | 2023 | 0.002975 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
FAJARDO | 2023-04-28 05:57 | 2023-04-28 09:41 | 200 | 3:44 | P | ANIMAL | 2 X 50 Y 1 X 40 EN CORTES DE LINEA Y 1 X 10 EN XMR CRUCE X AVE | R23042800056 | New_Event | Animals | Include | Include | Wildlife | 224 | 2023-04-28 | 44800 | keep | 0 | Apr | 2023 | 0.030513 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-04-28 06:05 | 2023-04-28 08:48 | 60 | 2:43 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER | R23042800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2023-04-28 | 9780 | keep | 0 | Apr | 2023 | 0.0066611 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-04-28 06:07 | 2023-04-28 06:08 | 643 | 0:01 | P | CONDUCTOR ROTO O ABIERTO | SJ-230428-01 SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO BKR 1204-02 PARA ESTABLECER GOI | S23042800064 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-28 | 643 | keep | 0 | Apr | 2023 | 0.00043794 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-28 06:07 | 2023-04-28 11:50 | 75 | 5:43 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R23042800062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2023-04-28 | 25725 | keep | 0 | Apr | 2023 | 0.017521 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-04-28 06:08 | 2023-04-28 07:40 | 214 | 1:32 | P | CONDUCTOR ROTO O ABIERTO | SJ-230428-01 SE LEVANTO CONDUCTOR Y SE NORMALIZO LA CARGA DEL 1204-02, SE TRANSFIRIO PARA HACERLE PRUEBAS LUEGO DE DISPARO DE MADUGADA | S23042800064 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 92 | 2023-04-28 | 19688 | keep | 0 | Apr | 2023 | 0.013409 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
YAUCO | 2023-04-28 06:11 | 2023-04-28 08:14 | 3973 | 2:03 | T | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO NADA ANORMAL LE DIO PRUEBA QUEDO EN SERVICIO | P23042800033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-04-28 | 488679 | keep | 0 | Apr | 2023 | 0.33284 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
HUMACAO | 2023-04-28 06:43 | 2023-04-28 08:50 | 94 | 2:07 | P | ANIMAL | CRUCE POR AVE 1 X 65 1 X 50 EN C/L | C23042800010 | New_Event | Animals | Include | Include | Wildlife | 127 | 2023-04-28 | 11938 | keep | 0 | Apr | 2023 | 0.0081309 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
BARRANQUITAS | 2023-04-28 06:50 | 2023-04-28 11:42 | 396 | 4:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L REEMPLAZO CAJA QUEMADA | C23042800014 | New_Event | Cutout Failure | Include | Include | Equipment | 292 | 2023-04-28 | 115632 | keep | 0 | Apr | 2023 | 0.078756 | 0.00026971 | Sustained | FALSE | FALSE | Not_TMED_Event | 396
PONCE | 2023-04-28 06:59 | 2023-04-28 08:30 | 20 | 1:31 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | P23042800049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-04-28 | 1820 | keep | 0 | Apr | 2023 | 0.0012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-04-28 07:16 | 2023-04-28 10:40 | 60 | 3:24 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN CORTE DE LINEA 1 X 30 EN CORTE DE LINEA 1 X 25 EN CORTE DE LINEA SE SECCIONALIZO ABRIENDO PUENTES | A23042800003 | New_Event | Primary Pole Failure | Include | Include | Equipment | 204 | 2023-04-28 | 12240 | keep | 0 | Apr | 2023 | 0.0083366 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-04-28 07:19 | 2023-04-28 09:18 | 75 | 1:59 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P23042800055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-04-28 | 8925 | keep | 0 | Apr | 2023 | 0.0060788 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-04-28 07:24 | 2023-04-28 12:33 | 50 | 5:09 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B23042800018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 309 | 2023-04-28 | 15450 | keep | 0 | Apr | 2023 | 0.010523 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-28 07:27 | 2023-04-28 11:37 | 2 | 4:10 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHO | C23042800026 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 250 | 2023-04-28 | 500 | keep | 0 | Apr | 2023 | 0.00034055 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-04-28 07:38 | 2023-04-28 10:43 | 50 | 3:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L REEMPLAZO AISLADOR | C23042800032 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 185 | 2023-04-28 | 9250 | keep | 0 | Apr | 2023 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-04-28 07:40 | 2023-04-28 12:43 | 1 | 5:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REEMPLAZO CAJA QUEMADA | C23042800033 | New_Event | Cutout Failure | Include | Include | Equipment | 303 | 2023-04-28 | 303 | keep | 0 | Apr | 2023 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-28 07:56 | 2023-04-28 11:10 | 1 | 3:14 | P | PROBLEMA DEL CLIENTE | 1 X 25 EN RISER CONTAMINACION EN LA SUB. DEL CLIENTE | R23042800108 | New_Event | Customer-Related Interruption | Include | Include | Public | 194 | 2023-04-28 | 194 | keep | 0 | Apr | 2023 | 0.00013213 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-28 07:57 | 2023-04-28 12:24 | 8 | 4:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR/LEVANTAR SECUNDARIA DEL SUELO | B23042800032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 267 | 2023-04-28 | 2136 | keep | 0 | Apr | 2023 | 0.0014548 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-04-28 07:58 | 2023-04-28 12:20 | 1 | 4:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23042800007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 262 | 2023-04-28 | 262 | keep | 0 | Apr | 2023 | 0.00017845 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-28 07:59 | 2023-04-28 09:35 | 1 | 1:36 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 2 X 40 EN SU-2B CONTAMINACION | R23042800109 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 96 | 2023-04-28 | 96 | keep | 0 | Apr | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-28 08:03 | 2023-04-28 13:45 | 180 | 5:42 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE REPARO NEUTRAL PRIMARIO PARTIDO | M23042800020 | New_Event | Primary Wire Break | Include | Include | Equipment | 342 | 2023-04-28 | 61560 | keep | 0 | Apr | 2023 | 0.041928 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
AGUADILLA | 2023-04-28 08:05 | 2023-04-28 08:06 | 6285 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23042800021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 6285 | keep | 0 | Apr | 2023 | 0.0042807 | 0.0042807 | Momentary | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2023-04-28 08:09 | 2023-04-28 11:00 | 90 | 2:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA Y PARARRAYOS EN TRANSFORMADOR | M23042800022 | New_Event | Cutout Failure | Include | Include | Equipment | 171 | 2023-04-28 | 15390 | keep | 0 | Apr | 2023 | 0.010482 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2023-04-28 08:10 | 2023-04-28 12:40 | 9 | 4:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REPARO SECUNDARIA | C23042800042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 270 | 2023-04-28 | 2430 | keep | 0 | Apr | 2023 | 0.0016551 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-04-28 08:58 | 2023-04-28 08:59 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C23042800051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 2126 | keep | 0 | Apr | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
ARECIBO | 2023-04-28 09:01 | 2023-04-28 15:30 | 3 | 6:29 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA REPARO PUENTE PRIMARIO | A23042800013 | New_Event | Primary Wire Break | Include | Include | Equipment | 389 | 2023-04-28 | 1167 | keep | 0 | Apr | 2023 | 0.00079484 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-04-28 09:16 | 2023-04-28 09:18 | 2891 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL | R23042800142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-28 | 5782 | keep | 0 | Apr | 2023 | 0.0039381 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
PONCE | 2023-04-28 09:34 | 2023-04-28 15:37 | 1979 | 6:03 | T | LINEA DE TRANSMISION 38KV | OHGW SOBRE CONDUCTOR SE CERRO PUENTE PRIMARIO Y SE CERRO INTERRUPTOR POR SCADA | P23042800254 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 363 | 2023-04-28 | 718377 | keep | 0 | Apr | 2023 | 0.48928 | 0.0013479 | Sustained | FALSE | FALSE | Not_TMED_Event | 1979
PONCE | 2023-04-28 09:34 | 2023-04-28 12:00 | 3114 | 2:26 | S | LINEA DE TRANSMISION 38KV | OVERHEAD DE LINEA 38 KV LINEA 500 CAYO SOBRE FEEDER 1 OVERHEAD GROUND WIRE AVERIADO | P23042800157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 146 | 2023-04-28 | 454644 | keep | 0 | Apr | 2023 | 0.30966 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
PONCE | 2023-04-28 09:34 | 2023-04-28 12:00 | 5069 | 2:26 | S | LINEA DE TRANSMISION 38KV | OVERHEAD DE LINEA 38 KV LINEA 500 CAYO SOBRE FEEDER 1 OVERHEAD GROUND WIRE AVERIADO | P23042800157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 146 | 2023-04-28 | 740074 | keep | 0 | Apr | 2023 | 0.50406 | 0.0034525 | Sustained | FALSE | FALSE | Not_TMED_Event | 5069
PONCE | 2023-04-28 09:34 | 2023-04-28 12:00 | 2696 | 2:26 | S | LINEA DE TRANSMISION 38KV | OVERHEAD DE LINEA 38 KV LINEA 500 CAYO SOBRE FEEDER 1 OVERHEAD GROUND WIRE AVERIADO | P23042800157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 146 | 2023-04-28 | 393616 | keep | 0 | Apr | 2023 | 0.26809 | 0.0018362 | Sustained | FALSE | FALSE | Not_TMED_Event | 2696
PONCE | 2023-04-28 09:34 | 2023-04-28 12:00 | 5063 | 2:26 | S | LINEA DE TRANSMISION 38KV | OVERHEAD DE LINEA 38 KV LINEA 500 CAYO SOBRE FEEDER 1 OVERHEAD GROUND WIRE AVERIADO | P23042800157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 146 | 2023-04-28 | 739198 | keep | 0 | Apr | 2023 | 0.50346 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
PONCE | 2023-04-28 09:34 | 2023-04-28 12:48 | 1863 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 361422 | keep | 0 | Apr | 2023 | 0.24616 | 0.0012689 | Sustained | FALSE | FALSE | Not_TMED_Event | 1863
PONCE | 2023-04-28 09:34 | 2023-04-28 12:48 | 708 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800161 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 137352 | keep | 0 | Apr | 2023 | 0.09355 | 0.00048222 | Sustained | FALSE | FALSE | Not_TMED_Event | 708
YAUCO | 2023-04-28 09:34 | 2023-04-28 12:48 | 502 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 97388 | keep | 0 | Apr | 2023 | 0.066331 | 0.00034191 | Sustained | FALSE | FALSE | Not_TMED_Event | 502
YAUCO | 2023-04-28 09:34 | 2023-04-28 12:48 | 2747 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 532918 | keep | 0 | Apr | 2023 | 0.36297 | 0.001871 | Sustained | FALSE | FALSE | Not_TMED_Event | 2747
YAUCO | 2023-04-28 09:34 | 2023-04-28 12:48 | 1587 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 307878 | keep | 0 | Apr | 2023 | 0.20969 | 0.0010809 | Sustained | FALSE | FALSE | Not_TMED_Event | 1587
YAUCO | 2023-04-28 09:34 | 2023-04-28 12:48 | 2671 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 518174 | keep | 0 | Apr | 2023 | 0.35293 | 0.0018192 | Sustained | FALSE | FALSE | Not_TMED_Event | 2671
YAUCO | 2023-04-28 09:34 | 2023-04-28 12:48 | 508 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 98552 | keep | 0 | Apr | 2023 | 0.067123 | 0.000346 | Sustained | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-04-28 09:34 | 2023-04-28 12:48 | 64 | 3:14 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 500 OVERHEAD GROUND WIRE AVERIADO | P23042800168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 194 | 2023-04-28 | 12416 | keep | 0 | Apr | 2023 | 0.0084565 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
BAYAMON | 2023-04-28 09:35 | 2023-04-28 17:01 | 30 | 7:26 | P | ANIMAL | 1 X 50 EN RISER CRUCE POR AVE | B23042800065 | New_Event | Animals | Include | Include | Wildlife | 446 | 2023-04-28 | 13380 | keep | 0 | Apr | 2023 | 0.0091131 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-04-28 09:56 | 2023-04-28 10:24 | 5 | 0:28 | P | ANIMAL | 1 X 15 EN XMR CRUCE X CULEBRA | R23042800152 | New_Event | Animals | Include | Include | Wildlife | 28 | 2023-04-28 | 140 | keep | 0 | Apr | 2023 | 9.5353e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-04-28 10:00 | 2023-04-28 13:33 | 1 | 3:33 | P | NO SE REPORTO CAUSA | 1X50 C/L Y 1X40 EN RISER | B23042800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 213 | 2023-04-28 | 213 | keep | 0 | Apr | 2023 | 0.00014507 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-04-28 10:11 | 2023-04-28 12:00 | 35 | 1:49 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA AVE | A23042800023 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-04-28 | 3815 | keep | 0 | Apr | 2023 | 0.0025984 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-04-28 10:18 | 2023-04-28 11:51 | 262 | 1:33 | T | NO SE REPORTO CAUSA | SE ENCONTRO FUSIBLE FUNDIDO HACIA BOMBAS DE AAA, SE DEJO FUERA Y SE CERRO POR SCADA 1 X 140 EN RISER A BOMBAS LUEGO NO CAUSA | S23042800224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-04-28 | 24366 | keep | 0 | Apr | 2023 | 0.016596 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
PONCE | 2023-04-28 10:22 | 2023-04-28 14:10 | 1109 | 3:48 | T | LINEA DE TRANSMISION 38KV | SE RETIRO OVERHEAD Y SE CAMBIO CONECTOR Y SE CERRO INTERRUPTOR POR SCADA OVERHEAD GROUND WIRE AVERIADO | P23042800190 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 228 | 2023-04-28 | 252852 | keep | 0 | Apr | 2023 | 0.17222 | 0.00075533 | Sustained | FALSE | FALSE | Not_TMED_Event | 1109
VEGA BAJA | 2023-04-28 10:40 | 2023-04-28 19:10 | 20 | 8:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO Y SE CERRO PUENTES PRIMARIOS | A23042800002 | New_Event | Primary Pole Failure | Include | Include | Equipment | 510 | 2023-04-28 | 10200 | keep | 0 | Apr | 2023 | 0.0069472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-28 10:43 | 2023-04-28 13:52 | 18 | 3:09 | P | CAUSAS EXTERNAS | MAQUINARIA EXCAVADORA PRIVADA DE CONTRATISTA AVERIO TRAMO DE T46 A T47 SE EMPALMO TRAMO SOTERRADO Y SE REEMPLAZARON TERMINACIONES SOTERRADAS | R23042800159 | New_Event | Damage From Public | Include | Include | Public | 189 | 2023-04-28 | 3402 | keep | 0 | Apr | 2023 | 0.0023171 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-04-28 10:52 | 2023-04-29 10:50 | 1 | 23:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO DE XMR 15KVA X 25KVA | C23042800068 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1438 | 2023-04-28 | 1438 | keep | 0 | Apr | 2023 | 0.00097942 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-04-28 11:29 | 2023-04-28 12:42 | 1 | 1:13 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23042800238 | New_Event | Animals | Include | Include | Wildlife | 73 | 2023-04-28 | 73 | keep | 0 | Apr | 2023 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-28 11:35 | 2023-04-28 13:29 | 70 | 1:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN RISER SE REEMPLAZO AISLADOR ROTO | R23042800167 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 114 | 2023-04-28 | 7980 | keep | 0 | Apr | 2023 | 0.0054351 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-04-28 11:38 | 2023-04-28 15:43 | 40 | 4:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23042800076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-04-28 | 9800 | keep | 0 | Apr | 2023 | 0.0066747 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-28 11:51 | 2023-04-28 13:18 | 1 | 1:27 | P | NO SE REPORTO CAUSA | SE ENCONTRO FUSIBLE FUNDIDO HACIA BOMBAS DE AAA, SE DEJO FUERA Y SE CERRO POR SCADA 1 X 140 EN RISER A BOMBAS LUEGO NO CAUSA | S23042800224 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-04-28 | 87 | keep | 0 | Apr | 2023 | 5.9255e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-04-28 11:54 | 2023-04-28 13:39 | 132 | 1:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L LLUVIAS | C23042800078 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 105 | 2023-04-28 | 13860 | keep | 0 | Apr | 2023 | 0.00944 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
CANOVANAS | 2023-04-28 12:11 | 2023-04-28 13:01 | 13 | 0:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE XMR 75KVA X 75KVA POR PROBLEMAS DE VOLTAJE | R23042800173 | New_Event | Service Transformer Failure | Include | Include | Equipment | 50 | 2023-04-28 | 650 | keep | 0 | Apr | 2023 | 0.00044271 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-04-28 12:17 | 2023-04-28 13:51 | 4 | 1:34 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | C23042800086 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-04-28 | 376 | keep | 0 | Apr | 2023 | 0.00025609 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-04-28 12:18 | 2023-04-28 17:20 | 1 | 5:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA POR 25 KVA | A23042800035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 302 | 2023-04-28 | 302 | keep | 0 | Apr | 2023 | 0.00020569 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-04-28 12:22 | 2023-04-28 13:26 | 1 | 1:04 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE TRANSFORMADOR | C23042800091 | New_Event | Primary Wire Break | Include | Include | Equipment | 64 | 2023-04-28 | 64 | keep | 0 | Apr | 2023 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-28 12:23 | 2023-04-28 12:27 | 4291 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO 1204-01 QUE LLEVA 1204-02 Y 1204-03 CERRADO POR SCADA | S23042800250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-04-28 | 17164 | keep | 0 | Apr | 2023 | 0.01169 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-04-28 12:23 | 2023-04-28 12:27 | 1381 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO 1204-01 QUE LLEVA 1204-02 Y 1204-03 CERRADO POR SCADA | S23042800250 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-04-28 | 5524 | keep | 0 | Apr | 2023 | 0.0037624 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
CANOVANAS | 2023-04-28 12:26 | 2023-04-28 15:16 | 70 | 2:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R23042800176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-04-28 | 11900 | keep | 0 | Apr | 2023 | 0.008105 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-04-28 12:29 | 2023-04-28 21:45 | 12 | 9:16 | P | CABLE SOTERRADO AVERIADO | SE INSTALO POSTE PROVISIONAL Y 3 RISERS SECUNDARIOS | P23042800087 | New_Event | UG Cable Fault | Include | Include | Equipment | 556 | 2023-04-28 | 6672 | keep | 0 | Apr | 2023 | 0.0045443 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-28 12:33 | 2023-04-28 12:34 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE 1204-01 QUE LLEVA 1204-02 Y 1204-03 | S2304280000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 4291 | keep | 0 | Apr | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
SAN JUAN | 2023-04-28 12:33 | 2023-04-28 12:34 | 1381 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1204-01 QUE LLEVA 1204-02 Y 1204-03 | S2304280000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-28 | 1381 | keep | 0 | Apr | 2023 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
ARECIBO | 2023-04-28 12:37 | 2023-04-28 13:55 | 5 | 1:18 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CULEBRA | A23042800038 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-04-28 | 390 | keep | 0 | Apr | 2023 | 0.00026563 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-04-28 12:39 | 2023-04-28 14:18 | 12 | 1:39 | P | ANIMAL | 1 X 25 EN C/L CRUCE POR IGUANA | C23042800096 | New_Event | Animals | Include | Include | Wildlife | 99 | 2023-04-28 | 1188 | keep | 0 | Apr | 2023 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-28 13:03 | 2023-04-28 13:04 | 4232 | 0:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SJ-230428-02 SE ABRE INTERRUPTOR POR CAJA EN FUEGO PARA SECCIONALIZARLA, SE CERRO POR SCADA UNA VEZ SECCIONALIZADO. SOLO LLEVANDO 80% DE SU CARGA | S23042800204 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-04-28 | 4232 | keep | 0 | Apr | 2023 | 0.0028824 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
SAN JUAN | 2023-04-28 13:04 | 2023-04-28 15:41 | 77 | 2:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SJ-230428-02 SE ABRE INTERRUPTOR POR CAJA EN FUEGO PARA SECCIONALIZARLA, SE CERRO POR SCADA UNA VEZ SECCIONALIZADO. SE REMPLAZO CAJA PRIMARIA Y 1 X 50 EN C/L | S23042800204 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 157 | 2023-04-28 | 12089 | keep | 0 | Apr | 2023 | 0.0082338 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
AGUADILLA | 2023-04-28 13:25 | 2023-04-28 14:20 | 19 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23042800094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-04-28 | 1045 | keep | 0 | Apr | 2023 | 0.00071174 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
VEGA BAJA | 2023-04-28 14:08 | 2023-04-28 18:30 | 300 | 4:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23042800054 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2023-04-28 | 78600 | keep | 0 | Apr | 2023 | 0.053534 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2023-04-28 14:11 | 2023-04-28 15:23 | 10 | 1:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO CAJA DE TRANSFORMADOR Y SE CERRO TRANSFORMADOR | P23042800273 | New_Event | Primary Wire Break | Include | Include | Equipment | 72 | 2023-04-28 | 720 | keep | 0 | Apr | 2023 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-28 14:23 | 2023-04-28 17:00 | 9 | 2:37 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR | R23042800193 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 157 | 2023-04-28 | 1413 | keep | 0 | Apr | 2023 | 0.00096239 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-04-28 14:25 | 2023-04-29 13:14 | 39 | 22:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN C/L SE REMPLAZO CAJA PRIMARIA | S23042800284 | New_Event | Cutout Failure | Include | Include | Equipment | 1369 | 2023-04-28 | 53391 | keep | 0 | Apr | 2023 | 0.036364 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2023-04-28 14:27 | 2023-04-28 17:47 | 83 | 3:20 | P | DESGANCHE | 1 X 65 EN C/L | C23042800114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-04-28 | 16600 | keep | 0 | Apr | 2023 | 0.011306 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
BAYAMON | 2023-04-28 14:28 | 2023-04-28 14:29 | 4089 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 4089 | keep | 0 | Apr | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
VEGA BAJA | 2023-04-28 14:28 | 2023-04-28 16:57 | 11 | 2:29 | P | DESGANCHE | 1 X 30 EN CL SE REALIZO DESGANCHE | A23042800063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-04-28 | 1639 | keep | 0 | Apr | 2023 | 0.0011163 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-04-28 14:34 | 2023-04-28 15:15 | 19 | 0:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23042800285 | New_Event | Secondary Wire Break | Include | Include | Equipment | 41 | 2023-04-28 | 779 | keep | 0 | Apr | 2023 | 0.00053057 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-04-28 14:35 | 2023-04-28 14:36 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-04-28 14:36 | 2023-04-28 14:37 | 2858 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUTOR | B2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 2858 | keep | 0 | Apr | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
FAJARDO | 2023-04-28 14:40 | 2023-04-28 14:51 | 1 | 0:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R23042800197 | New_Event | Cutout Failure | Include | Include | Equipment | 11 | 2023-04-28 | 11 | keep | 0 | Apr | 2023 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-28 14:41 | 2023-04-28 14:42 | 2858 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304280000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 2858 | keep | 0 | Apr | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
BAYAMON | 2023-04-28 14:42 | 2023-04-28 15:32 | 120 | 0:50 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA | B23042800134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-04-28 | 6000 | keep | 0 | Apr | 2023 | 0.0040866 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-04-28 14:43 | 2023-04-28 14:44 | 1647 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23042800136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 1647 | keep | 0 | Apr | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
CANOVANAS | 2023-04-28 14:52 | 2023-04-28 17:59 | 69 | 3:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO PIN POLE TOP PARTIDO | R23042800201 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 187 | 2023-04-28 | 12903 | keep | 0 | Apr | 2023 | 0.0087882 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
PONCE | 2023-04-28 14:54 | 2023-04-28 16:14 | 11 | 1:20 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA NIDO DE AVES | P23042800283 | New_Event | Animals | Include | Include | Wildlife | 80 | 2023-04-28 | 880 | keep | 0 | Apr | 2023 | 0.00059936 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-04-28 15:00 | 2023-04-29 19:30 | 50 | 28:30 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | B23042800163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1710 | 2023-04-28 | 85500 | keep | 0 | Apr | 2023 | 0.058234 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-28 15:11 | 2023-04-28 15:12 | 1131 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23042800124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 1131 | keep | 0 | Apr | 2023 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
MAYAGÃœEZ | 2023-04-28 15:12 | 2023-04-29 08:21 | 20 | 17:09 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA REPARAR PUENTE PRIMARIO ABIERTO VERIFICO INFORMACION EN OMS | M23042800103 | New_Event | Primary Wire Break | Include | Include | Equipment | 1029 | 2023-04-28 | 20580 | keep | 0 | Apr | 2023 | 0.014017 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-04-28 15:14 | 2023-04-28 15:15 | 1131 | 0:01 | T | ARBOL SOBRE LINEA | RECIERRE | C23042800125 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1 | 2023-04-28 | 1131 | keep | 0 | Apr | 2023 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
BARRANQUITAS | 2023-04-28 15:15 | 2023-04-29 11:40 | 341 | 20:25 | P | ARBOL SOBRE LINEA | SE SECCIONALIZO ALIMENTADOR ARBOL CAYO SOBRE LAS LINEAS Y SE REPARO PUENTE ABIERTO MEDIANTE GOI CG-230429-02 | C23042800128 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 1225 | 2023-04-28 | 417725 | keep | 0 | Apr | 2023 | 0.28451 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
BARRANQUITAS | 2023-04-28 15:20 | 2023-04-28 17:22 | 10 | 2:02 | P | NO SE REPORTO CAUSA | 2 X 10 XMR | C23042800126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2023-04-28 | 1220 | keep | 0 | Apr | 2023 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-28 15:21 | 2023-04-28 16:14 | 25 | 0:53 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR LIQUEANDO DE 75 X 75KVA | R23042800204 | New_Event | Service Transformer Failure | Include | Include | Equipment | 53 | 2023-04-28 | 1325 | keep | 0 | Apr | 2023 | 0.00090245 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-28 15:28 | 2023-04-28 16:58 | 10 | 1:30 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE DE FASE POR AVE | M23042800108 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-04-28 | 900 | keep | 0 | Apr | 2023 | 0.00061299 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-28 15:31 | 2023-04-28 16:31 | 39 | 1:00 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | R23042800206 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-04-28 | 2340 | keep | 0 | Apr | 2023 | 0.0015938 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2023-04-28 15:32 | 2023-04-28 15:33 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 SUB. 9502 FUNDIÃ“ 1 FUSIBLE | B23042800162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-04-28 15:32 | 2023-04-28 15:33 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 SUB. 9502 FUNDIÃ“ 1 FUSIBLE | B23042800162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 2735 | keep | 0 | Apr | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-04-28 15:32 | 2023-04-28 15:33 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 SUB. 9502 FUNDIÃ“ 1 FUSIBLE | B23042800162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 1070 | keep | 0 | Apr | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2023-04-28 15:32 | 2023-04-28 15:33 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 SUB. 9502 FUNDIÃ“ 1 FUSIBLE | B23042800164 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 320 | keep | 0 | Apr | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-04-28 15:32 | 2023-04-28 15:33 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 SUB. 9502 FUNDIÃ“ 1 FUSIBLE | B23042800164 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 2234 | keep | 0 | Apr | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-04-28 15:33 | 2023-04-29 13:51 | 120 | 22:18 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA | B23042800134 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1338 | 2023-04-28 | 160560 | keep | 0 | Apr | 2023 | 0.10936 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-28 15:34 | 2023-04-28 17:31 | 60 | 1:57 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R23042800208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-04-28 | 7020 | keep | 0 | Apr | 2023 | 0.0047813 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-04-28 15:35 | 2023-04-28 18:55 | 15 | 3:20 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLACION | A23042800071 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 200 | 2023-04-28 | 3000 | keep | 0 | Apr | 2023 | 0.0020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-04-28 15:35 | 2023-04-28 17:40 | 1647 | 2:05 | S | POWER TRANSFORMER AVERIADO | SE REEMPLAZO FUSIBLE EN LA ALTA DEL MAIN XMR Y SE REEMPLAZARON 3 PARARRAYYO EN LA ALTA DEL XMR BY-230428-02 SE REALIZARON OPERACIONES SE TRANSFIRIO LA CARGA 9501-01 | B23042800163 | New_Event | Power Transformer Failure | Include | Include | Equipment | 125 | 2023-04-28 | 205875 | keep | 0 | Apr | 2023 | 0.14022 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-04-28 15:35 | 2023-04-29 04:21 | 3295 | 12:46 | S | POWER TRANSFORMER AVERIADO | SE REEMPLAZO FUSIBLE EN LA ALTA DEL MAIN XMR Y SE REEMPLAZARON 3 PARARRAYYO EN LA ALTA DEL XMR BY-230428-02 | B23042800163 | New_Event | Power Transformer Failure | Include | Include | Equipment | 766 | 2023-04-28 | 2523970 | keep | 0 | Apr | 2023 | 1.7191 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-04-28 15:35 | 2023-04-29 04:21 | 1180 | 12:46 | S | POWER TRANSFORMER AVERIADO | SE REEMPLAZO FUSIBLE EN LA ALTA DEL MAIN XMR Y SE REEMPLAZARON 3 PARARRAYYO EN LA ALTA DEL XMR BY-230428-02 | B23042800163 | New_Event | Power Transformer Failure | Include | Include | Equipment | 766 | 2023-04-28 | 903880 | keep | 0 | Apr | 2023 | 0.61563 | 0.00080369 | Sustained | FALSE | FALSE | Not_TMED_Event | 1180
BARRANQUITAS | 2023-04-28 15:38 | 2023-04-28 18:04 | 65 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIAS | C23042800129 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2023-04-28 | 9490 | keep | 0 | Apr | 2023 | 0.0064636 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BARRANQUITAS | 2023-04-28 15:46 | 2023-04-28 15:49 | 2192 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-28 | 6576 | keep | 0 | Apr | 2023 | 0.0044789 | 0.001493 | Momentary | FALSE | FALSE | Not_TMED_Event | 2192
BAYAMON | 2023-04-28 15:53 | 2023-04-29 18:40 | 12 | 26:47 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVICIONAL DE AEREO EXISTENTE A T513 | B23042700283 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1607 | 2023-04-28 | 19284 | keep | 0 | Apr | 2023 | 0.013134 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-28 15:55 | 2023-04-28 17:16 | 20 | 1:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042800113 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 81 | 2023-04-28 | 1620 | keep | 0 | Apr | 2023 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-28 16:06 | 2023-04-28 16:08 | 320 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23042800193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-28 | 640 | keep | 0 | Apr | 2023 | 0.0004359 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
SAN JUAN | 2023-04-28 16:18 | 2023-04-29 12:44 | 86 | 20:26 | P | DESGANCHE | 1 X 80 EN C/L DEGANCHE | S23042800299 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1226 | 2023-04-28 | 105436 | keep | 0 | Apr | 2023 | 0.071812 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
BAYAMON | 2023-04-28 16:21 | 2023-04-28 16:22 | 4028 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 4028 | keep | 0 | Apr | 2023 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2023-04-28 16:23 | 2023-04-28 20:24 | 26 | 4:01 | P | DESGANCHE | 1 X 100 EN C/L | B23042800206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 241 | 2023-04-28 | 6266 | keep | 0 | Apr | 2023 | 0.0042677 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
HUMACAO | 2023-04-28 16:25 | 2023-04-28 19:04 | 1 | 2:39 | P | ANIMAL | 2 X 65 EN RISER CRUCE X AVE | C23042800145 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-04-28 | 159 | keep | 0 | Apr | 2023 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-04-28 16:30 | 2023-04-28 17:00 | 9 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23042800016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-04-28 | 270 | keep | 0 | Apr | 2023 | 0.0001839 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-04-28 16:35 | 2023-04-28 16:36 | 215 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 215 | keep | 0 | Apr | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BARRANQUITAS | 2023-04-28 16:36 | 2023-04-29 15:19 | 7 | 22:43 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C23042800151 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1363 | 2023-04-28 | 9541 | keep | 0 | Apr | 2023 | 0.0064983 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-04-28 16:40 | 2023-04-28 18:43 | 718 | 2:03 | T | ALIMENTADOR AMARRADO | SJ-230428-03 SE SECCIONALIZO ABRIENDO TRAMO DEL 1901-05 QUE ESTA ATRAVES DEL 1330-01 Y SE CERRO POR SCADA. 100% EN SERVICIO 1330-01 Y 40% EN SERVICIO DEL 1901-05 | S23042800305 | New_Event | Feeder Load Transferred | Include | Include | Other | 123 | 2023-04-28 | 88314 | keep | 0 | Apr | 2023 | 0.06015 | 0.00048903 | Sustained | FALSE | FALSE | Not_TMED_Event | 718
BAYAMON | 2023-04-28 16:40 | 2023-04-28 18:43 | 372 | 2:03 | P | DESGANCHE | SJ-230428-03 SE SECCIONALIZO ABRIENDO TRAMO DEL 1901-05 QUE ESTA ATRAVES DEL 1330-01 Y SE CERRO POR SCADA. 100% EN SERVICIO 1330-01 Y 40% EN SERVICIO DEL 1901-05 | S23042800305 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-04-28 | 45756 | keep | 0 | Apr | 2023 | 0.031164 | 0.00025337 | Sustained | FALSE | FALSE | Not_TMED_Event | 372
HUMACAO | 2023-04-28 16:41 | 2023-04-28 18:30 | 40 | 1:49 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23042800153 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-04-28 | 4360 | keep | 0 | Apr | 2023 | 0.0029696 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-04-28 16:43 | 2023-04-29 04:05 | 50 | 11:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23042800306 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 682 | 2023-04-28 | 34100 | keep | 0 | Apr | 2023 | 0.023225 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-28 16:46 | 2023-04-28 18:37 | 8 | 1:51 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R23042800218 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 111 | 2023-04-28 | 888 | keep | 0 | Apr | 2023 | 0.00060481 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-28 16:50 | 2023-04-28 16:51 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 1362 | keep | 0 | Apr | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
MAYAGÃœEZ | 2023-04-28 16:51 | 2023-04-28 21:00 | 30 | 4:09 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23042800126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-04-28 | 7470 | keep | 0 | Apr | 2023 | 0.0050878 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-04-28 16:52 | 2023-04-28 17:42 | 40 | 0:50 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA TIGUERO FUERA DE LUGAR POR LINEAS ARRIADAS | P23042800313 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 50 | 2023-04-28 | 2000 | keep | 0 | Apr | 2023 | 0.0013622 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-28 17:01 | 2023-04-28 17:02 | 341 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | B2304280000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-28 | 341 | keep | 0 | Apr | 2023 | 0.00023225 | 0.00023225 | Momentary | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2023-04-28 17:02 | 2023-04-28 17:44 | 30 | 0:42 | P | ANIMAL | 1 X 50 EN RISER CRUCE POR AVE | B23042800065 | 1st_after_momentary | Animals | Include | Include | Wildlife | 42 | 2023-04-28 | 1260 | keep | 0 | Apr | 2023 | 0.00085818 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-28 17:04 | 2023-04-28 19:30 | 7 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23042800084 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2023-04-28 | 1022 | keep | 0 | Apr | 2023 | 0.00069608 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-04-28 17:11 | 2023-04-29 09:30 | 22 | 16:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN RISER LLUVIA | R23042800224 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 979 | 2023-04-28 | 21538 | keep | 0 | Apr | 2023 | 0.014669 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-04-28 17:13 | 2023-04-28 19:34 | 186 | 2:21 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | B23042800250 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-04-28 | 26226 | keep | 0 | Apr | 2023 | 0.017862 | 0.00012668 | Sustained | FALSE | FALSE | Not_TMED_Event | 186
YAUCO | 2023-04-28 17:16 | 2023-04-28 17:28 | 1339 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23042800132 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-04-28 | 16068 | keep | 0 | Apr | 2023 | 0.010944 | 0.00091199 | Sustained | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-04-28 17:16 | 2023-04-28 17:28 | 470 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23042800132 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-04-28 | 5640 | keep | 0 | Apr | 2023 | 0.0038414 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-04-28 17:16 | 2023-04-28 17:28 | 2483 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23042800132 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-04-28 | 29796 | keep | 0 | Apr | 2023 | 0.020294 | 0.0016912 | Sustained | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-04-28 17:16 | 2023-04-28 17:28 | 2190 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23042800132 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-04-28 | 26280 | keep | 0 | Apr | 2023 | 0.017899 | 0.0014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-04-28 17:16 | 2023-04-28 17:28 | 3006 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23042800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-04-28 | 36072 | keep | 0 | Apr | 2023 | 0.024568 | 0.0020474 | Sustained | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-04-28 17:16 | 2023-04-28 17:28 | 179 | 0:12 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 13400 | M23042800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-04-28 | 2148 | keep | 0 | Apr | 2023 | 0.001463 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
SAN JUAN | 2023-04-28 17:27 | 2023-04-29 16:29 | 28 | 23:02 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23042800315 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1382 | 2023-04-28 | 38696 | keep | 0 | Apr | 2023 | 0.026356 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
YAUCO | 2023-04-28 17:28 | 2023-04-28 18:29 | 20 | 1:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042800113 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 61 | 2023-04-28 | 1220 | keep | 0 | Apr | 2023 | 0.00083094 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-04-28 17:30 | 2023-04-28 18:42 | 60 | 1:12 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE | P23042800324 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-04-28 | 4320 | keep | 0 | Apr | 2023 | 0.0029423 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-04-28 17:48 | 2023-04-28 19:33 | 112 | 1:45 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | C23042800168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 105 | 2023-04-28 | 11760 | keep | 0 | Apr | 2023 | 0.0080097 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
VEGA BAJA | 2023-04-28 17:50 | 2023-04-28 19:57 | 31 | 2:07 | P | DESGANCHE | 2 X 100 EN C/L Y 1 X 30 EN OTRO C/L | B23042800287 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-04-28 | 3937 | keep | 0 | Apr | 2023 | 0.0026815 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CANOVANAS | 2023-04-28 17:53 | 2023-04-28 17:54 | 2708 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | R2304280000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-28 | 2708 | keep | 0 | Apr | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-04-28 17:54 | 2023-04-28 19:41 | 240 | 1:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 30 EN CORTES DE LINEA LLUVIAS | R23042800230 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 107 | 2023-04-28 | 25680 | keep | 0 | Apr | 2023 | 0.017491 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
MAYAGÃœEZ | 2023-04-28 17:58 | 2023-04-28 20:55 | 200 | 2:57 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CL SE REMPLAZO PARARRAYOS | M23042800164 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 177 | 2023-04-28 | 35400 | keep | 0 | Apr | 2023 | 0.024111 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-28 18:00 | 2023-04-28 21:06 | 100 | 3:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | B23042800293 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 186 | 2023-04-28 | 18600 | keep | 0 | Apr | 2023 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-04-28 18:16 | 2023-04-30 09:05 | 1 | 38:49 | P | DESGANCHE | 2 X 15 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS VERIFICADO EN OMS SIN SERVICO DESDE 4/28/2023 | A23042800093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2329 | 2023-04-28 | 2329 | keep | 0 | Apr | 2023 | 0.0015863 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-04-28 18:29 | 2023-04-28 18:30 | 1448 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 1448 | keep | 0 | Apr | 2023 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
BAYAMON | 2023-04-28 18:33 | 2023-04-28 22:10 | 143 | 3:37 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23042800332 | New_Event | Primary Wire Break | Include | Include | Equipment | 217 | 2023-04-28 | 31031 | keep | 0 | Apr | 2023 | 0.021135 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
VEGA BAJA | 2023-04-28 18:34 | 2023-04-29 13:57 | 2 | 19:23 | P | DESGANCHE | 1 X 15 EN TRANSORMADOR RAMA CRUZA CAJA PRIMARIA | A23042800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1163 | 2023-04-28 | 2326 | keep | 0 | Apr | 2023 | 0.0015842 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-04-28 18:38 | 2023-04-28 18:39 | 3699 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23042800235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 3699 | keep | 0 | Apr | 2023 | 0.0025194 | 0.0025194 | Momentary | FALSE | FALSE | Not_TMED_Event | 3699
SAN JUAN | 2023-04-28 18:39 | 2023-04-28 18:40 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
CAGUAS | 2023-04-28 18:42 | 2023-04-28 18:43 | 1228 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 LLUVIA INTENSA | C23042800181 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 1228 | keep | 0 | Apr | 2023 | 0.00083639 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2023-04-28 18:42 | 2023-04-28 18:43 | 1271 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 LLUVIA INTENSA | C23042800181 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 1271 | keep | 0 | Apr | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2023-04-28 18:42 | 2023-04-28 18:43 | 1893 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 LLUVIA INTENSA | C23042800181 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 1893 | keep | 0 | Apr | 2023 | 0.0012893 | 0.0012893 | Momentary | FALSE | FALSE | Not_TMED_Event | 1893
CAGUAS | 2023-04-28 18:42 | 2023-04-28 18:43 | 473 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 14400 LLUVIA INTENSA | C23042800181 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-28 | 473 | keep | 0 | Apr | 2023 | 0.00032216 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
BAYAMON | 2023-04-28 18:43 | 2023-04-28 18:59 | 124 | 0:16 | P | DESGANCHE | SJ-230428-03 SE SECCIONALIZO OTRO TRAMO DEL 1901-05 QUE Y SE CERRO MACHETES ANTERIORES PARA REALIZAR DESGANCHE 80% EN SERVICIO | S23042800305 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 16 | 2023-04-28 | 1984 | keep | 0 | Apr | 2023 | 0.0013513 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-04-28 18:43 | 2023-04-29 16:08 | 65 | 21:25 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CL SE REPARO LINEA PRIMARIA | A23042800095 | New_Event | Primary Wire Break | Include | Include | Equipment | 1285 | 2023-04-28 | 83525 | keep | 0 | Apr | 2023 | 0.056888 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-04-28 18:58 | 2023-04-28 22:47 | 318 | 3:49 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 100 EN C/L POR LINEAS CRUZADAS | B23042800347 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 229 | 2023-04-28 | 72822 | keep | 0 | Apr | 2023 | 0.049599 | 0.00021659 | Sustained | FALSE | FALSE | Not_TMED_Event | 318
BAYAMON | 2023-04-28 18:59 | 2023-04-28 20:30 | 62 | 1:31 | P | DESGANCHE | SJ-230428-03 SE REALIZO DESGANCHE MASIVO DE ARBOL Y SE CERRO MACHETES DEL 1901-05 QUE ESTA ATRAVES DEL 1330-01 Y ENTRO TODA LA CARGA | S23042800305 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 91 | 2023-04-28 | 5642 | keep | 0 | Apr | 2023 | 0.0038427 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-28 19:07 | 2023-04-28 19:08 | 222 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1909-09 | B2304280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-28 | 222 | keep | 0 | Apr | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-04-28 19:07 | 2023-04-28 19:08 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR CARGA POR EL 1907-03 | B2304280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-28 | 4456 | keep | 0 | Apr | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
VEGA BAJA | 2023-04-28 19:10 | 2023-04-29 13:26 | 37 | 18:16 | P | CAUSAS EXTERNAS | 1X65 EN C/L POR PERSONAL AJENO A LUMA REALIZANDO DESGANCHE | B23042800368 | New_Event | Damage From Public | Include | Include | Public | 1096 | 2023-04-28 | 40552 | keep | 0 | Apr | 2023 | 0.02762 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
CANOVANAS | 2023-04-28 19:26 | 2023-04-28 22:28 | 5 | 3:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23042800262 | New_Event | Primary Wire Break | Include | Include | Equipment | 182 | 2023-04-28 | 910 | keep | 0 | Apr | 2023 | 0.0006198 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-04-28 19:40 | 2023-04-29 18:25 | 75 | 22:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL FUERTE LLUVIA | A23042800106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1365 | 2023-04-28 | 102375 | keep | 0 | Apr | 2023 | 0.069727 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2023-04-28 19:47 | 2023-04-29 08:41 | 90 | 12:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P23042800188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 774 | 2023-04-28 | 69660 | keep | 0 | Apr | 2023 | 0.047445 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-04-28 20:04 | 2023-04-29 08:43 | 200 | 12:39 | P | TERMINACION SOTERRADA AVERIADA | 2X140 DE RISER @ SU-1 SE REMPLAZO CAJA PRIMARIA | B23042800420 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 759 | 2023-04-28 | 151800 | keep | 0 | Apr | 2023 | 0.10339 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2023-04-28 20:12 | 2023-04-29 09:29 | 70 | 13:17 | P | DESGANCHE | 1 X 50 Y 1 X 25 EN C/LS | R23042800279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 797 | 2023-04-28 | 55790 | keep | 0 | Apr | 2023 | 0.037998 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-04-28 20:12 | 2023-04-29 09:57 | 60 | 13:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23042800110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 825 | 2023-04-28 | 49500 | keep | 0 | Apr | 2023 | 0.033714 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-28 20:18 | 2023-04-29 08:04 | 80 | 11:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REEMPLAZO CAJA QUEMADA | R23042800303 | New_Event | Cutout Failure | Include | Include | Equipment | 706 | 2023-04-28 | 56480 | keep | 0 | Apr | 2023 | 0.038468 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-04-28 20:48 | 2023-04-29 12:58 | 100 | 16:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN C/L Y 1X40 EN SU-5 SE REMPLAZO CAJA PRIMARIA | B23042800440 | New_Event | Cutout Failure | Include | Include | Equipment | 970 | 2023-04-28 | 97000 | keep | 0 | Apr | 2023 | 0.066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-28 20:59 | 2023-04-29 09:57 | 54 | 12:58 | P | DESGANCHE | 2X80 EN C/L DESGANCHE | B23042800446 | New_Event | Vegetation Contact | Include | Include | Vegetation | 778 | 2023-04-28 | 42012 | keep | 0 | Apr | 2023 | 0.028614 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
ARECIBO | 2023-04-28 21:02 | 2023-04-29 09:30 | 60 | 12:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES | A23042800115 | New_Event | Cutout Failure | Include | Include | Equipment | 748 | 2023-04-28 | 44880 | keep | 0 | Apr | 2023 | 0.030568 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-04-28 22:28 | 2023-04-29 00:19 | 1862 | 1:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC, SE SECCIONALIZO HIDRANTE ROTO LANZANDO AGUA A LA LINEA | R23042800342 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2023-04-28 | 206682 | keep | 0 | Apr | 2023 | 0.14077 | 0.0012682 | Sustained | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-04-28 22:28 | 2023-04-29 00:19 | 1613 | 1:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC, SE SECCIONALIZO HIDRANTE ROTO LANZANDO AGUA A LA LINEA | R23042800342 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2023-04-28 | 179043 | keep | 0 | Apr | 2023 | 0.12195 | 0.0010986 | Sustained | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-04-28 22:28 | 2023-04-29 00:19 | 1448 | 1:51 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 DE SABANA LLANA A CANOVANAS TC, SE SECCIONALIZO HIDRANTE ROTO LANZANDO AGUA A LA LINEA | R23042800342 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 111 | 2023-04-28 | 160728 | keep | 0 | Apr | 2023 | 0.10947 | 0.00098623 | Sustained | FALSE | FALSE | Not_TMED_Event | 1448
CANOVANAS | 2023-04-28 22:49 | 2023-04-29 16:16 | 24 | 17:27 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN C/L CONSTRUYO TENSOR Y ENDEREZO POSTE | R23042800318 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1047 | 2023-04-28 | 25128 | keep | 0 | Apr | 2023 | 0.017115 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-04-28 22:53 | 2023-04-29 16:29 | 14 | 17:36 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 75X 75KVA | B23042800477 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1056 | 2023-04-28 | 14784 | keep | 0 | Apr | 2023 | 0.010069 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-04-28 23:06 | 2023-04-29 01:47 | 546 | 2:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA TOTAL PARA LEVANTAR CONDUCTOR PRIMARIO | R23042800244 | New_Event | Primary Wire Break | Include | Include | Equipment | 161 | 2023-04-28 | 87906 | keep | 0 | Apr | 2023 | 0.059872 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
CANOVANAS | 2023-04-29 00:19 | 2023-04-29 11:35 | 5 | 11:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23042800262 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 676 | 2023-04-29 | 3380 | keep | 0 | Apr | 2023 | 0.0023021 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-29 01:31 | 2023-04-29 11:25 | 7 | 9:54 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25KVA POR LA MISMA CAPACIDAD | A23042900012 | New_Event | Service Transformer Failure | Include | Include | Equipment | 594 | 2023-04-29 | 4158 | keep | 0 | Apr | 2023 | 0.002832 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-04-29 02:50 | 2023-04-29 09:27 | 16 | 6:37 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN XMR SE CERRO PUENTE PUENTE DE LINEA A CAJA | C23042900003 | New_Event | Primary Wire Break | Include | Include | Equipment | 397 | 2023-04-29 | 6352 | keep | 0 | Apr | 2023 | 0.0043263 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-04-29 02:57 | 2023-04-29 12:02 | 29 | 9:05 | P | ANIMAL | 1 SMU 20 DE 25A EN EL SU - 4A CRUCE X RATA | R23042900004 | New_Event | Animals | Include | Include | Wildlife | 545 | 2023-04-29 | 15805 | keep | 0 | Apr | 2023 | 0.010765 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
FAJARDO | 2023-04-29 03:15 | 2023-04-29 03:16 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23042900005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 2722 | keep | 0 | Apr | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2023-04-29 04:04 | 2023-04-29 04:14 | 320 | 0:10 | S | OTRAS CAUSAS | AUTORIZO RANGEL VAZQUES A RETIRAR CARGA DE LA 9503-00 PARA QUE TRANSMISION REALICE OPERACIONES BY- 230428-02 | B23042900008 | New_Event | Other Causes | Include | Include | Other | 10 | 2023-04-29 | 3200 | keep | 0 | Apr | 2023 | 0.0021795 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-04-29 04:04 | 2023-04-29 04:14 | 2234 | 0:10 | S | OTRAS CAUSAS | AUTORIZO RANGEL VAZQUES A RETIRAR CARGA DE LA 9503-00 PARA QUE TRANSMISION REALICE OPERACIONES BY- 230428-02 | B23042900008 | New_Event | Other Causes | Include | Include | Other | 10 | 2023-04-29 | 22340 | keep | 0 | Apr | 2023 | 0.015216 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2023-04-29 04:05 | 2023-04-29 04:07 | 946 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1525-05 | S2304290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-29 | 1892 | keep | 0 | Apr | 2023 | 0.0012886 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2023-04-29 04:05 | 2023-04-29 04:07 | 937 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1525-02 | S2304290000X | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-29 | 1874 | keep | 0 | Apr | 2023 | 0.0012764 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-04-29 04:05 | 2023-04-29 04:06 | 1839 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 NO SE CREO EL EVENTO, NO HAY OMS | R2304290000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-29 | 1839 | keep | 0 | Apr | 2023 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2023-04-29 04:05 | 2023-04-29 04:06 | 1778 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 NO SE CREO EL EVENTO, NO HAY OMS | R2304290000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-29 | 1778 | keep | 0 | Apr | 2023 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2023-04-29 04:05 | 2023-04-29 04:06 | 1376 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 NO SE CREO EL EVENTO, NO HAY OMS | R2304290000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-29 | 1376 | keep | 0 | Apr | 2023 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2023-04-29 04:05 | 2023-04-29 04:06 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 NO SE CREO EL EVENTO, NO HAY OMS | R2304290000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-29 | 293 | keep | 0 | Apr | 2023 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2023-04-29 04:05 | 2023-04-29 04:06 | 1215 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 NO SE CREO EL EVENTO, NO HAY OMS | R2304290000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-04-29 | 1215 | keep | 0 | Apr | 2023 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
SAN JUAN | 2023-04-29 04:07 | 2023-04-29 14:45 | 50 | 10:38 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23042800306 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 638 | 2023-04-29 | 31900 | keep | 0 | Apr | 2023 | 0.021727 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-29 04:54 | 2023-04-29 08:16 | 250 | 3:22 | P | ALIMENTADOR AMARRADO | SJ-230429-01 SE SECCIONALIZO ALIMENTADOR 1401-08 QUE SOLO LLEVA 10% DE SU CARGA Y SE CERRO POR SCADA. LLEVA 1348-08 Y 20% DEL 1348-06. ENTRO 20% DEL 1348-06 | S23042900003 | New_Event | Feeder Load Transferred | Include | Include | Other | 202 | 2023-04-29 | 50500 | keep | 0 | Apr | 2023 | 0.034395 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-04-29 04:54 | 2023-04-29 08:16 | 1290 | 3:22 | T | DESGANCHE | SJ-230429-01 SE SECCIONALIZO ALIMENTADOR 1401-08 QUE SOLO LLEVA 10% DE SU CARGA Y SE CERRO POR SCADA. LLEVA 1348-08 Y 20% DEL 1348-06. ENTRO 50% DEL 1348-08 | S23042900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-04-29 | 260580 | keep | 0 | Apr | 2023 | 0.17748 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-04-29 04:54 | 2023-04-29 08:16 | 13 | 3:22 | P | ALIMENTADOR AMARRADO | SJ-230429-01 SE SECCIONALIZO ALIMENTADOR 1401-08 QUE SOLO LLEVA 10% DE SU CARGA Y SE CERRO POR SCADA. LLEVA 1348-08 Y 20% DEL 1348-06 | S23042900003 | New_Event | Feeder Load Transferred | Include | Include | Other | 202 | 2023-04-29 | 2626 | keep | 0 | Apr | 2023 | 0.0017886 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-04-29 05:04 | 2023-04-29 05:05 | 1526 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B23042900012 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-29 | 1526 | keep | 0 | Apr | 2023 | 0.0010394 | 0.0010394 | Momentary | FALSE | FALSE | Not_TMED_Event | 1526
SAN JUAN | 2023-04-29 05:14 | 2023-04-29 05:15 | 1447 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1419-09 | S2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 1447 | keep | 0 | Apr | 2023 | 0.00098555 | 0.00098555 | Momentary | FALSE | FALSE | Not_TMED_Event | 1447
SAN JUAN | 2023-04-29 05:14 | 2023-04-29 05:15 | 266 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1112-04 | S2304290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 266 | keep | 0 | Apr | 2023 | 0.00018117 | 0.00018117 | Momentary | FALSE | FALSE | Not_TMED_Event | 266
BAYAMON | 2023-04-29 06:04 | 2023-04-29 12:20 | 763 | 6:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO FASE PRIMARIA ABIERTA EN MACHETE MEDIANTE G.O.I. BY-230429-02 | B23042900021 | New_Event | Primary Wire Break | Include | Include | Equipment | 376 | 2023-04-29 | 286888 | keep | 0 | Apr | 2023 | 0.1954 | 0.00051968 | Sustained | FALSE | FALSE | Not_TMED_Event | 763
BARRANQUITAS | 2023-04-29 06:21 | 2023-04-29 06:22 | 2435 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR | C23042900004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-04-29 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BARRANQUITAS | 2023-04-29 06:22 | 2023-04-29 09:52 | 1847 | 3:30 | P | PARARRAYOS DEFECTUOSO | SE SECCIONALIZO ALIEMANTADOR Y SE REEMPLAZO PARRARAYOS MEDIANTGE GOI CG-230429-01 | C23042900026 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 210 | 2023-04-29 | 387870 | keep | 0 | Apr | 2023 | 0.26418 | 0.001258 | Sustained | FALSE | FALSE | Not_TMED_Event | 1847
UTUADO | 2023-04-29 06:34 | 2023-04-29 08:55 | 1 | 2:21 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | A23042900016 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 141 | 2023-04-29 | 141 | keep | 0 | Apr | 2023 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-04-29 06:41 | 2023-04-29 09:00 | 100 | 2:19 | P | NO SE REPORTO CAUSA | 2 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23042900007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2023-04-29 | 13900 | keep | 0 | Apr | 2023 | 0.0094672 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-29 06:44 | 2023-04-29 13:51 | 80 | 7:07 | P | DESGANCHE | 1 X 50 EN CORTES DE LINEA | B23042900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 427 | 2023-04-29 | 34160 | keep | 0 | Apr | 2023 | 0.023266 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-04-29 06:51 | 2023-04-29 10:31 | 4 | 3:40 | P | PARARRAYOS DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE DESCONECTO PARARRAYOS AVERIADO | M23042900009 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 220 | 2023-04-29 | 880 | keep | 0 | Apr | 2023 | 0.00059936 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-04-29 06:59 | 2023-04-29 07:00 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23042900022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 3973 | keep | 0 | Apr | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
CANOVANAS | 2023-04-29 07:02 | 2023-04-29 13:42 | 6 | 6:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23042900013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 400 | 2023-04-29 | 2400 | keep | 0 | Apr | 2023 | 0.0016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-04-29 07:04 | 2023-04-29 08:50 | 125 | 1:46 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M23042900010 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-04-29 | 13250 | keep | 0 | Apr | 2023 | 0.0090245 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-04-29 07:09 | 2023-04-29 07:11 | 2364 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | SE CERRO POR CONTROL | S23042900082 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-04-29 | 4728 | keep | 0 | Apr | 2023 | 0.0032202 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BAYAMON | 2023-04-29 07:11 | 2023-04-29 08:49 | 400 | 1:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIAS | S23042900088 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 98 | 2023-04-29 | 39200 | keep | 0 | Apr | 2023 | 0.026699 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-04-29 07:11 | 2023-04-29 10:51 | 59 | 3:40 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23042900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-04-29 | 12980 | keep | 0 | Apr | 2023 | 0.0088406 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
ARECIBO | 2023-04-29 07:12 | 2023-04-29 07:13 | 2201 | 0:01 | T | OTRAS CAUSAS | RECIERRE DE INTERRUPTOR | A23042900025 | New_Event | Other Causes | Include | Include | Other | 1 | 2023-04-29 | 2201 | keep | 0 | Apr | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-04-29 07:13 | 2023-04-29 10:10 | 40 | 2:57 | P | OTRAS CAUSAS | 1 X 40 EN CORTE DE LINEA FUSIBLE CORROIDO | A23042900028 | 1st_after_momentary | Other Causes | Include | Include | Other | 177 | 2023-04-29 | 7080 | keep | 0 | Apr | 2023 | 0.0048222 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-29 07:17 | 2023-04-29 07:18 | 2366 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23042900026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 2366 | keep | 0 | Apr | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
CANOVANAS | 2023-04-29 07:32 | 2023-04-29 11:28 | 10 | 3:56 | P | TERMINACION SOTERRADA AVERIADA | 1 X 15 EN RISER REEMPLAZO TERMINACION TIPO PISTOLA EN EL T - 46 | R23042900016 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 236 | 2023-04-29 | 2360 | keep | 0 | Apr | 2023 | 0.0016074 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-04-29 07:32 | 2023-04-29 07:33 | 1362 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23042900044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 1362 | keep | 0 | Apr | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
CAGUAS | 2023-04-29 07:47 | 2023-04-29 10:34 | 12 | 2:47 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | C23042900010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-04-29 | 2004 | keep | 0 | Apr | 2023 | 0.0013649 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-04-29 07:50 | 2023-04-29 07:51 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23042900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 2450 | keep | 0 | Apr | 2023 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
CANOVANAS | 2023-04-29 07:52 | 2023-04-29 07:53 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23042900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 4085 | keep | 0 | Apr | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
BAYAMON | 2023-04-29 07:57 | 2023-04-29 09:25 | 104 | 1:28 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23042900052 | New_Event | Animals | Include | Include | Wildlife | 88 | 2023-04-29 | 9152 | keep | 0 | Apr | 2023 | 0.0062334 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
CANOVANAS | 2023-04-29 08:04 | 2023-04-29 08:05 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 40% DEL 2402-02 | R23042900024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-29 08:04 | 2023-04-29 08:05 | 1675 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 2302-03 | R23042900024 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 1675 | keep | 0 | Apr | 2023 | 0.0011408 | 0.0011408 | Momentary | FALSE | FALSE | Not_TMED_Event | 1675
CANOVANAS | 2023-04-29 08:05 | 2023-04-29 08:40 | 80 | 0:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REEMPLAZO CAJA QUEMADA | R23042800303 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 35 | 2023-04-29 | 2800 | keep | 0 | Apr | 2023 | 0.0019071 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-04-29 08:10 | 2023-04-29 09:58 | 8 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23042900026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-04-29 | 864 | keep | 0 | Apr | 2023 | 0.00058847 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-04-29 08:10 | 2023-04-29 13:28 | 50 | 5:18 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | B23042900056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 318 | 2023-04-29 | 15900 | keep | 0 | Apr | 2023 | 0.010829 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-04-29 08:16 | 2023-04-29 09:24 | 645 | 1:08 | P | DESGANCHE | SJ-230429-01 HACIENDO OPERACIONES DISPARO EL ALIMENTADOR SE SECCIONALIZO ALIMENTADOR 1401-08 QUE SOLO LLEVA 10% DE SU CARGA Y SE CERRO POR SCADA. LLEVA 1348-08 Y 20% DEL 1348-06. ENTRO 50% DEL 1348-08 | S23042900003 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-04-29 | 43860 | keep | 0 | Apr | 2023 | 0.029873 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-29 08:17 | 2023-04-29 08:18 | 215 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23042900058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 215 | keep | 0 | Apr | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-04-29 08:18 | 2023-04-29 11:24 | 80 | 3:06 | P | NO SE REPORTO CAUSA | 1X100 EN C/L | B23042900061 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 186 | 2023-04-29 | 14880 | keep | 0 | Apr | 2023 | 0.010135 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-04-29 08:21 | 2023-04-30 11:47 | 40 | 27:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA PUENTE PRIMARIO Y SE CIERRA CORTE DE LINEA | M23042800103 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1646 | 2023-04-29 | 65840 | keep | 0 | Apr | 2023 | 0.044843 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-29 08:24 | 2023-04-29 11:01 | 40 | 2:37 | P | ANIMAL | 2 X 40 EN CORTE DE LINEA AVE CRUZO FASES A TIERRA | A23042900036 | New_Event | Animals | Include | Include | Wildlife | 157 | 2023-04-29 | 6280 | keep | 0 | Apr | 2023 | 0.0042773 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-04-29 08:25 | 2023-04-29 09:10 | 10 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | P23042900020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-04-29 | 450 | keep | 0 | Apr | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-29 08:40 | 2023-04-29 08:41 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 40% DEL 2402-0 | R23042900035 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-04-29 08:40 | 2023-04-29 08:41 | 1675 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 2302-03 | R23042900035 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 1675 | keep | 0 | Apr | 2023 | 0.0011408 | 0.0011408 | Momentary | FALSE | FALSE | Not_TMED_Event | 1675
CAGUAS | 2023-04-29 08:40 | 2023-04-29 11:51 | 8 | 3:11 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23042900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2023-04-29 | 1528 | keep | 0 | Apr | 2023 | 0.0010407 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-04-29 08:41 | 2023-04-29 09:44 | 80 | 1:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L REEMPLAZO CAJA QUEMADA | R23042800303 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 63 | 2023-04-29 | 5040 | keep | 0 | Apr | 2023 | 0.0034327 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-29 08:43 | 2023-04-29 13:20 | 3 | 4:37 | P | TERMINACION SOTERRADA AVERIADA | SE REMPLAZARON TERMINACIONES QUEMADAS DEL SU-1 HACIA EL SU-1A MEDIANTE G.O.I. BY-230429-01 EN SERVICIO LOS (3) CLIENTES QUE FALTABAN POR ENTRAR | B23042800420 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 277 | 2023-04-29 | 831 | keep | 0 | Apr | 2023 | 0.00056599 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-29 08:44 | 2023-04-29 13:49 | 50 | 5:05 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23042900069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 305 | 2023-04-29 | 15250 | keep | 0 | Apr | 2023 | 0.010387 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-29 09:09 | 2023-04-29 11:00 | 30 | 1:51 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23042900025 | New_Event | Animals | Include | Include | Wildlife | 111 | 2023-04-29 | 3330 | keep | 0 | Apr | 2023 | 0.002268 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-29 09:13 | 2023-04-29 13:57 | 40 | 4:44 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CL SE REPARO LINEA PRIMARIA | A23042900079 | New_Event | Primary Wire Break | Include | Include | Equipment | 284 | 2023-04-29 | 11360 | keep | 0 | Apr | 2023 | 0.0077372 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-04-29 09:15 | 2023-04-29 19:09 | 1 | 9:54 | P | MAL TIEMPO/RAYOS | 1 X 20 EN MONTURA DESCARGAS ELECTRICAS | A23042900054 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 594 | 2023-04-29 | 594 | keep | 0 | Apr | 2023 | 0.00040457 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-29 09:24 | 2023-04-29 09:25 | 250 | 0:01 | P | ALIMENTADOR AMARRADO | SJ-230429-01 HACIENDO OPERACIONES DISPARO ALIMENTADOR Y SE CERRO POR SCADA. SE SECCIONALIZO ALIMENTADOR 1401-08 QUE SOLO LLEVA 10% DE SU CARGA Y SE CERRO POR SCADA. LLEVA 1348-08 Y 20% DEL 1348-06. ENTRO 20% DEL 1348-06 | S23042900003 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 250 | keep | 0 | Apr | 2023 | 0.00017027 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-29 09:24 | 2023-04-29 09:25 | 1290 | 0:01 | T | DESGANCHE | SJ-230429-01 HACIENDO OPERACIONES DISPARO EL ALIMENTADOR SE SECCIONALIZO ALIMENTADOR 1401-08 QUE SOLO LLEVA 10% DE SU CARGA Y SE CERRO POR SCADA. LLEVA 1348-08 Y 20% DEL 1348-06. ENTRO 50% DEL 1348-08 | S23042900003 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-04-29 | 1290 | keep | 0 | Apr | 2023 | 0.00087861 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-29 09:24 | 2023-04-29 09:25 | 13 | 0:01 | P | ALIMENTADOR AMARRADO | SJ-230429-01 HACIENDO OPERACIONES DISPARO 1401-08 SE SECCIONALIZO ALIMENTADOR 1401-08 QUE SOLO LLEVA 10% DE SU CARGA Y SE CERRO POR SCADA. LLEVA 1348-08 Y 20% DEL 1348-06 | S23042900003 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 13 | keep | 0 | Apr | 2023 | 8.8542e-06 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-29 09:25 | 2023-04-29 10:23 | 690 | 0:58 | P | DESGANCHE | SJ-230429-01 SE DESGANCHO TRAMO, SE SECCIONALIZO ALIMENTADOR 1348-08 Y SE CERRO MACHETES, ENTRO 100% DEL 1348-08 | S23042900003 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-04-29 | 40020 | keep | 0 | Apr | 2023 | 0.027257 | 0.00046996 | Sustained | FALSE | FALSE | Not_TMED_Event | 690
BARRANQUITAS | 2023-04-29 09:26 | 2023-04-29 10:49 | 30 | 1:23 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | C23042900028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-04-29 | 2490 | keep | 0 | Apr | 2023 | 0.0016959 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-29 09:39 | 2023-04-29 13:00 | 240 | 3:21 | P | DESGANCHE | 2 X 100 C/L DEGANCHE | S23042900162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 201 | 2023-04-29 | 48240 | keep | 0 | Apr | 2023 | 0.032856 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
VEGA BAJA | 2023-04-29 09:45 | 2023-04-29 13:10 | 5 | 3:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | A23042900059 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 205 | 2023-04-29 | 1025 | keep | 0 | Apr | 2023 | 0.00069812 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-04-29 09:59 | 2023-04-29 10:52 | 65 | 0:53 | P | DESGANCHE | 1 X 100 EN C/L | R23042900049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2023-04-29 | 3445 | keep | 0 | Apr | 2023 | 0.0023464 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-04-29 10:06 | 2023-04-29 12:13 | 3597 | 2:07 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | INTERRUPTOR NO CERRO POR CONTROL NI LOCALMENTE/SE TRANSFIRIO CARGA AL 9405-05 MEDIANTE G.O.I. BY-230325-03 Y SE REFIRIO A PERSONAL DE CDS | B23042900010 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 127 | 2023-04-29 | 456819 | keep | 0 | Apr | 2023 | 0.31114 | 0.0024499 | Sustained | FALSE | FALSE | Not_TMED_Event | 3597
SAN JUAN | 2023-04-29 10:07 | 2023-04-29 10:08 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 733 | keep | 0 | Apr | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
BAYAMON | 2023-04-29 10:27 | 2023-04-29 13:51 | 120 | 3:24 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA | B23042800134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-04-29 | 24480 | keep | 0 | Apr | 2023 | 0.016673 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-04-29 10:32 | 2023-04-29 11:55 | 4 | 1:23 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | P23042900042 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 83 | 2023-04-29 | 332 | keep | 0 | Apr | 2023 | 0.00022612 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-29 10:39 | 2023-04-29 10:45 | 5662 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1717-02 LLEVA 95% DEL 1713-05 SE CERRO POR CONTROL | B23042900164 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-04-29 | 33972 | keep | 0 | Apr | 2023 | 0.023138 | 0.0038564 | Sustained | FALSE | FALSE | Not_TMED_Event | 5662
BAYAMON | 2023-04-29 10:39 | 2023-04-29 10:45 | 911 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1717-02 LLEVA 95% DEL 1713-05 SE CERRO POR CONTROL | B23042900164 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-04-29 | 5466 | keep | 0 | Apr | 2023 | 0.0037229 | 0.00062048 | Sustained | FALSE | FALSE | Not_TMED_Event | 911
FAJARDO | 2023-04-29 10:48 | 2023-04-29 12:00 | 10 | 1:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR LLUVIAS FUERTES | R23042900065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 72 | 2023-04-29 | 720 | keep | 0 | Apr | 2023 | 0.00049039 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-04-29 10:50 | 2023-04-29 13:31 | 32 | 2:41 | P | DESGANCHE | 1 X 25 EN C/L | R23042900067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-04-29 | 5152 | keep | 0 | Apr | 2023 | 0.003509 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CANOVANAS | 2023-04-29 11:16 | 2023-04-29 11:19 | 2179 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | R23042900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-29 | 6537 | keep | 0 | Apr | 2023 | 0.0044523 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
SAN JUAN | 2023-04-29 11:31 | 2023-04-29 11:34 | 72 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO 1404-07 QUE LLEVA 5% DEL 1112-04 Y SE CERRO POR SCADA | S23042900185 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-29 | 216 | keep | 0 | Apr | 2023 | 0.00014712 | 4.9039e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-04-29 11:31 | 2023-04-29 11:34 | 1357 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO 1404-07 QUE LLEVA 5% DEL 1112-04 Y SE CERRO POR SCADA | S23042900185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-29 | 4071 | keep | 0 | Apr | 2023 | 0.0027727 | 0.00092425 | Momentary | FALSE | FALSE | Not_TMED_Event | 1357
HUMACAO | 2023-04-29 11:31 | 2023-04-29 11:32 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 2354 | keep | 0 | Apr | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2023-04-29 11:36 | 2023-04-30 16:02 | 20 | 28:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 37.5KVA | S23042900186 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1706 | 2023-04-29 | 34120 | keep | 0 | Apr | 2023 | 0.023239 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-29 11:36 | 2023-04-29 15:43 | 1 | 4:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN RISER FUERTES LLUVIAS | R23042900081 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 247 | 2023-04-29 | 247 | keep | 0 | Apr | 2023 | 0.00016823 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-04-29 11:40 | 2023-04-29 11:41 | 2410 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23042900043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 2410 | keep | 0 | Apr | 2023 | 0.0016414 | 0.0016414 | Momentary | FALSE | FALSE | Not_TMED_Event | 2410
PONCE | 2023-04-29 11:55 | 2023-04-29 13:14 | 45 | 1:19 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA PAJARO CRUZO FASE | P23042900055 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-04-29 | 3555 | keep | 0 | Apr | 2023 | 0.0024213 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-04-29 11:57 | 2023-04-29 13:45 | 25 | 1:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23042900045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-04-29 | 2700 | keep | 0 | Apr | 2023 | 0.001839 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-04-29 12:08 | 2023-04-29 13:45 | 25 | 1:37 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23042900045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-04-29 | 2425 | keep | 0 | Apr | 2023 | 0.0016517 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-29 12:09 | 2023-04-29 12:11 | 726 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 1303-03 LLEVA 1346-04 SE CERRO POR SCADA | S23042900194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-29 | 1452 | keep | 0 | Apr | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-04-29 12:09 | 2023-04-29 12:11 | 3932 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO 1303-03 LLEVA 1346-04 SE CERRO POR SCADA | S23042900194 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-29 | 7864 | keep | 0 | Apr | 2023 | 0.0053561 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
FAJARDO | 2023-04-29 12:28 | 2023-04-29 13:45 | 88 | 1:17 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO TERMINACION SOTERRADA NO FUNDIO | R23042900086 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 77 | 2023-04-29 | 6776 | keep | 0 | Apr | 2023 | 0.0046151 | 5.9936e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 88
SAN JUAN | 2023-04-29 12:40 | 2023-04-29 19:04 | 12 | 6:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO SECUNDARIA | S23042900204 | New_Event | Secondary Wire Break | Include | Include | Equipment | 384 | 2023-04-29 | 4608 | keep | 0 | Apr | 2023 | 0.0031385 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-04-29 12:47 | 2023-04-29 17:24 | 70 | 4:37 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | S23042900207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 277 | 2023-04-29 | 19390 | keep | 0 | Apr | 2023 | 0.013206 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-04-29 12:49 | 2023-04-29 16:29 | 10 | 3:40 | P | DESGANCHE | 1 X 30 EN C/L | R23042900089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-04-29 | 2200 | keep | 0 | Apr | 2023 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-04-29 12:53 | 2023-04-29 16:15 | 90 | 3:22 | P | DESGANCHE | 1 X 100 EN CL DESGANCHE | A23042900084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-04-29 | 18180 | keep | 0 | Apr | 2023 | 0.012382 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2023-04-29 13:05 | 2023-04-29 16:20 | 80 | 3:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIAS | B23042900296 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2023-04-29 | 15600 | keep | 0 | Apr | 2023 | 0.010625 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-04-29 13:14 | 2023-04-29 16:48 | 8 | 3:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR REPARO SECUNDARIA AVERIADA | R23042900091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 214 | 2023-04-29 | 1712 | keep | 0 | Apr | 2023 | 0.001166 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-04-29 13:24 | 2023-04-29 15:53 | 27 | 2:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23042900063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-04-29 | 4023 | keep | 0 | Apr | 2023 | 0.00274 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-04-29 13:32 | 2023-04-29 15:24 | 200 | 1:52 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R23042900093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-04-29 | 22400 | keep | 0 | Apr | 2023 | 0.015257 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-04-29 13:37 | 2023-04-29 13:38 | 1467 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23042900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 1467 | keep | 0 | Apr | 2023 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2023-04-29 13:37 | 2023-04-29 13:51 | 140 | 0:14 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B23042900313 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2023-04-29 | 1960 | keep | 0 | Apr | 2023 | 0.0013349 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2023-04-29 13:43 | 2023-04-29 18:49 | 48 | 5:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | B23042900315 | New_Event | Cutout Failure | Include | Include | Equipment | 306 | 2023-04-29 | 14688 | keep | 0 | Apr | 2023 | 0.010004 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
VEGA BAJA | 2023-04-29 13:44 | 2023-04-29 16:07 | 69 | 2:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B23042900316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-04-29 | 9867 | keep | 0 | Apr | 2023 | 0.0067204 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2023-04-29 13:49 | 2023-04-29 18:15 | 100 | 4:26 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | B23042900318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-04-29 | 26600 | keep | 0 | Apr | 2023 | 0.018117 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-29 13:51 | 2023-04-29 13:52 | 4456 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE CARGA POR EL 1907-03 | B2304290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 4456 | keep | 0 | Apr | 2023 | 0.003035 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2023-04-29 13:53 | 2023-04-29 13:54 | 959 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 959 | keep | 0 | Apr | 2023 | 0.00065317 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
PONCE | 2023-04-29 14:00 | 2023-04-29 15:35 | 8 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | P23042900081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-04-29 | 760 | keep | 0 | Apr | 2023 | 0.00051763 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-04-29 14:00 | 2023-04-29 14:27 | 12 | 0:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO | P23042900081 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 27 | 2023-04-29 | 324 | keep | 0 | Apr | 2023 | 0.00022067 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-04-29 14:01 | 2023-04-29 17:25 | 40 | 3:24 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CL SE REPARO LINEA PRIMARIA | A23042900079 | New_Event | Primary Wire Break | Include | Include | Equipment | 204 | 2023-04-29 | 8160 | keep | 0 | Apr | 2023 | 0.0055577 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-29 14:01 | 2023-04-29 15:16 | 120 | 1:15 | P | DESGANCHE | 2 X 80 EN CORTES DE LINEA | B23042800134 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-04-29 | 9000 | keep | 0 | Apr | 2023 | 0.0061299 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-29 14:01 | 2023-04-29 16:23 | 140 | 2:22 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | B23042900313 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-04-29 | 19880 | keep | 0 | Apr | 2023 | 0.01354 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-04-29 14:01 | 2023-04-29 17:10 | 80 | 3:09 | P | DESGANCHE | 1 X 50 EN CORTES DE LINEA | B23042900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 189 | 2023-04-29 | 15120 | keep | 0 | Apr | 2023 | 0.010298 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-04-29 14:02 | 2023-04-29 15:08 | 2 | 1:06 | P | DESGANCHE | 1 X 15 EN TRANSORMADOR RAMA CRUZA CAJA PRIMARIA | A23042800094 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-04-29 | 132 | keep | 0 | Apr | 2023 | 8.9905e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-04-29 14:45 | 2023-04-29 16:35 | 30 | 1:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042900085 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 110 | 2023-04-29 | 3300 | keep | 0 | Apr | 2023 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-04-29 15:01 | 2023-04-29 18:33 | 4 | 3:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 8 EN XMR REMPLAZO 2 CAJAS AVERIADAS | R23042900164 | New_Event | Cutout Failure | Include | Include | Equipment | 212 | 2023-04-29 | 848 | keep | 0 | Apr | 2023 | 0.00057757 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-29 15:09 | 2023-04-29 16:08 | 33 | 0:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | B23042900377 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-04-29 | 1947 | keep | 0 | Apr | 2023 | 0.0013261 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-04-29 15:10 | 2023-04-29 17:03 | 219 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA LLUVIAS | B23042900382 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2023-04-29 | 24747 | keep | 0 | Apr | 2023 | 0.016855 | 0.00014916 | Sustained | FALSE | FALSE | Not_TMED_Event | 219
GUAYAMA | 2023-04-29 15:14 | 2023-04-29 16:10 | 20 | 0:56 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | P23042900111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-04-29 | 1120 | keep | 0 | Apr | 2023 | 0.00076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-04-29 15:15 | 2023-04-29 18:03 | 68 | 2:48 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | C23042900211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-04-29 | 11424 | keep | 0 | Apr | 2023 | 0.0077808 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
ARECIBO | 2023-04-29 15:17 | 2023-04-29 17:30 | 150 | 2:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 EN CL SE REPARO BAJANTE PRIMARIA A CAJA CORTE LINEA | A23042900122 | New_Event | Primary Wire Break | Include | Include | Equipment | 133 | 2023-04-29 | 19950 | keep | 0 | Apr | 2023 | 0.013588 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-04-29 15:24 | 2023-04-29 18:08 | 250 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN C/L SE REEMPLAZO CAJA | C23042900216 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2023-04-29 | 41000 | keep | 0 | Apr | 2023 | 0.027925 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
UTUADO | 2023-04-29 15:27 | 2023-04-29 17:45 | 2 | 2:18 | P | DESGANCHE | 2 X 40 EN CL BAMBU | A23042900128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-04-29 | 276 | keep | 0 | Apr | 2023 | 0.00018798 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-04-29 15:33 | 2023-04-29 16:46 | 6 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | R23042900174 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-04-29 | 438 | keep | 0 | Apr | 2023 | 0.00029832 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-04-29 15:49 | 2023-04-29 15:50 | 8679 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE 1206-03 LLEVA 85% DEL 1204-05 Y LLEVA 84% DE SU CARGA | S2304290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 8679 | keep | 0 | Apr | 2023 | 0.0059112 | 0.0059112 | Momentary | FALSE | FALSE | Not_TMED_Event | 8679
SAN JUAN | 2023-04-29 15:49 | 2023-04-29 15:50 | 3471 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 1206-03 LLEVA 85% DEL 1204-05 Y LLEVA 84% DE SU CARGA | S2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 3471 | keep | 0 | Apr | 2023 | 0.0023641 | 0.0023641 | Momentary | FALSE | FALSE | Not_TMED_Event | 3471
MAYAGÃœEZ | 2023-04-29 15:50 | 2023-04-29 17:20 | 400 | 1:30 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23042900106 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 90 | 2023-04-29 | 36000 | keep | 0 | Apr | 2023 | 0.024519 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BARRANQUITAS | 2023-04-29 15:59 | 2023-04-30 16:32 | 207 | 24:33 | P | CONDUCTOR ROTO O ABIERTO | 3 X 50 EN C/L SE LEVANTO CONDUCTORES DEL SUELO | C23042900223 | New_Event | Primary Wire Break | Include | Include | Equipment | 1473 | 2023-04-29 | 304911 | keep | 0 | Apr | 2023 | 0.20767 | 0.00014099 | Sustained | FALSE | FALSE | Not_TMED_Event | 207
YAUCO | 2023-04-29 16:11 | 2023-04-29 17:15 | 4 | 1:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23042900109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 64 | 2023-04-29 | 256 | keep | 0 | Apr | 2023 | 0.00017436 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-04-29 16:16 | 2023-04-29 16:17 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 4981 | keep | 0 | Apr | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
BAYAMON | 2023-04-29 16:21 | 2023-04-29 17:16 | 90 | 0:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 80 EN CORTE DE LINE Y RISER LLUVIAS | B23042900409 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 55 | 2023-04-29 | 4950 | keep | 0 | Apr | 2023 | 0.0033714 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2023-04-29 16:21 | 2023-04-29 19:10 | 193 | 2:49 | P | ANIMAL | 1 X 65 EN C/L SE RETIRO AVE | C23042900230 | New_Event | Animals | Include | Include | Wildlife | 169 | 2023-04-29 | 32617 | keep | 0 | Apr | 2023 | 0.022215 | 0.00013145 | Sustained | FALSE | FALSE | Not_TMED_Event | 193
BAYAMON | 2023-04-29 16:25 | 2023-04-29 18:06 | 49 | 1:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIAS | B23042900410 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 101 | 2023-04-29 | 4949 | keep | 0 | Apr | 2023 | 0.0033707 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
BAYAMON | 2023-04-29 16:41 | 2023-04-29 19:00 | 30 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN CORTE DE LINEA LLUVIAS | B23042900414 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-04-29 | 4170 | keep | 0 | Apr | 2023 | 0.0028402 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-04-29 16:49 | 2023-04-29 16:50 | 766 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE | B23042900418 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-04-29 | 766 | keep | 0 | Apr | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-04-29 16:50 | 2023-04-30 08:10 | 26 | 15:20 | P | DESGANCHE | 2 X 40 EN C/L | B23042900416 | New_Event | Vegetation Contact | Include | Include | Vegetation | 920 | 2023-04-29 | 23920 | keep | 0 | Apr | 2023 | 0.016292 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
MAYAGÃœEZ | 2023-04-29 17:00 | 2023-04-29 17:01 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23042900117 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 4641 | keep | 0 | Apr | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
SAN JUAN | 2023-04-29 17:05 | 2023-04-29 17:07 | 946 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1525-05 | S2304290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-29 | 1892 | keep | 0 | Apr | 2023 | 0.0012886 | 0.00064432 | Momentary | FALSE | FALSE | Not_TMED_Event | 946
SAN JUAN | 2023-04-29 17:05 | 2023-04-29 17:07 | 937 | 0:02 | T | PARARRAYOS DEFECTUOSO | HACIENDO PRUEBA EN RISER PROBO MALO Y OCASIONO DISPARO DE ALIMENTADOR 1525-05 QUE LLEVA 1525-02 | S2304290000X | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 2 | 2023-04-29 | 1874 | keep | 0 | Apr | 2023 | 0.0012764 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
SAN JUAN | 2023-04-29 17:07 | 2023-04-29 17:45 | 38 | 0:38 | P | PARARRAYOS DEFECTUOSO | HACIENDO PRUEBA EN RISER PROBO MALO Y OCASIONO DISPARO DE ALIMENTADOR. 1 X 65 EN RISER SE ELIMINO PARARRAYO | S23042900318 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 38 | 2023-04-29 | 1444 | keep | 0 | Apr | 2023 | 0.0009835 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CAGUAS | 2023-04-29 17:15 | 2023-04-30 10:58 | 7 | 17:43 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | C23042900236 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1063 | 2023-04-29 | 7441 | keep | 0 | Apr | 2023 | 0.005068 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-29 17:36 | 2023-04-29 20:08 | 90 | 2:32 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | B23042900428 | New_Event | Animals | Include | Include | Wildlife | 152 | 2023-04-29 | 13680 | keep | 0 | Apr | 2023 | 0.0093174 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
CAGUAS | 2023-04-29 17:52 | 2023-04-30 17:41 | 22 | 23:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C23042900240 | New_Event | Cutout Failure | Include | Include | Equipment | 1429 | 2023-04-29 | 31438 | keep | 0 | Apr | 2023 | 0.021412 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
SAN JUAN | 2023-04-29 18:01 | 2023-04-29 18:08 | 53 | 0:07 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S23042900328 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-04-29 | 371 | keep | 0 | Apr | 2023 | 0.00025269 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
HUMACAO | 2023-04-29 18:10 | 2023-04-29 18:11 | 3833 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 3833 | keep | 0 | Apr | 2023 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2023-04-29 18:11 | 2023-04-29 19:17 | 40 | 1:06 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23042900243 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 66 | 2023-04-29 | 2640 | keep | 0 | Apr | 2023 | 0.0017981 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-04-29 18:26 | 2023-04-29 20:00 | 200 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23042900156 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-04-29 | 18800 | keep | 0 | Apr | 2023 | 0.012805 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-04-29 18:28 | 2023-04-29 20:38 | 25 | 2:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23042900157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-04-29 | 3250 | keep | 0 | Apr | 2023 | 0.0022136 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-04-29 18:47 | 2023-04-30 12:52 | 3 | 18:05 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE XMR 25KVA X 25 KVA EVENTO TRANSFERIDO DE ARECIBO | A23042900161 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1085 | 2023-04-29 | 3255 | keep | 0 | Apr | 2023 | 0.002217 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2023-04-29 18:51 | 2023-04-29 20:10 | 75 | 1:19 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | P23042900132 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-04-29 | 5925 | keep | 0 | Apr | 2023 | 0.0040355 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-04-29 18:51 | 2023-04-30 16:20 | 200 | 21:29 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS | A23042900162 | New_Event | Primary Wire Break | Include | Include | Equipment | 1289 | 2023-04-29 | 257800 | keep | 0 | Apr | 2023 | 0.17559 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-04-29 19:03 | 2023-04-30 13:30 | 3 | 18:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO PORTAFUSIBLE QUEMADO | B23042900436 | New_Event | Cutout Failure | Include | Include | Equipment | 1107 | 2023-04-29 | 3321 | keep | 0 | Apr | 2023 | 0.0022619 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-04-29 19:06 | 2023-04-29 19:07 | 2228 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 8007-05 REALIZA UNA OPERACION Y QUEDA EN SERVICIO TIENE LA CARGA DEL 8007-03 Y 8007-04 | A23042900177 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 2228 | keep | 0 | Apr | 2023 | 0.0015175 | 0.0015175 | Momentary | FALSE | FALSE | Not_TMED_Event | 2228
ARECIBO | 2023-04-29 19:06 | 2023-04-29 19:07 | 438 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 8007-05 REALIZA UNA OPERACION Y QUEDA EN SERVICIO TIENE LA CARGA DEL 8007-03 Y 8007-04 | A23042900177 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-29 | 438 | keep | 0 | Apr | 2023 | 0.00029832 | 0.00029832 | Momentary | FALSE | FALSE | Not_TMED_Event | 438
CAGUAS | 2023-04-29 19:11 | 2023-04-29 19:12 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 2608 | keep | 0 | Apr | 2023 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2023-04-29 19:13 | 2023-04-29 19:14 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 6197 | keep | 0 | Apr | 2023 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
BARRANQUITAS | 2023-04-29 19:20 | 2023-04-30 10:19 | 5 | 14:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR LLUVIAS | C23042900251 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 899 | 2023-04-29 | 4495 | keep | 0 | Apr | 2023 | 0.0030615 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-04-29 19:39 | 2023-04-29 21:20 | 69 | 1:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REPARO CAJA SAFADA | B23042900439 | New_Event | Cutout Failure | Include | Include | Equipment | 101 | 2023-04-29 | 6969 | keep | 0 | Apr | 2023 | 0.0047466 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
BAYAMON | 2023-04-29 19:43 | 2023-04-30 20:31 | 25 | 24:48 | P | CABLE SOTERRADO AVERIADO | TRABAJAR INSTALANDO PROVISIONAL BY-230530-02 | B23052900017 | New_Event | UG Cable Fault | Include | Include | Equipment | 1488 | 2023-04-29 | 37200 | keep | 0 | Apr | 2023 | 0.025337 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-29 19:50 | 2023-04-29 23:04 | 138 | 3:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 2 X 100 EN C/L Y SE REEMPLAZO AISLADOR | S23042900335 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2023-04-29 | 26772 | keep | 0 | Apr | 2023 | 0.018234 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
BAYAMON | 2023-04-29 20:11 | 2023-04-30 07:55 | 1 | 11:44 | P | NO SE REPORTO CAUSA | SE ABRIO EN XMR PARA REPARAR BAJANTE SECUNDARIO | B23042900444 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 704 | 2023-04-29 | 704 | keep | 0 | Apr | 2023 | 0.00047949 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-04-29 20:17 | 2023-04-29 21:20 | 45 | 1:03 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | A23042900181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-04-29 | 2835 | keep | 0 | Apr | 2023 | 0.0019309 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-04-29 20:28 | 2023-04-29 22:50 | 490 | 2:22 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SOLO LLEVA 490 CLIENTES DE SU CARGA. SE HICIERON OPERACIONES CON SJ-230429-50. SE CERRO N/O CONTRA 2403-02. ENTRARON 489 | R23042900191 | New_Event | Primary Wire Break | Include | Include | Equipment | 142 | 2023-04-29 | 69580 | keep | 0 | Apr | 2023 | 0.047391 | 0.00033374 | Sustained | FALSE | FALSE | Not_TMED_Event | 490
AGUADILLA | 2023-04-29 20:44 | 2023-04-29 22:27 | 200 | 1:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBL | M23042900138 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2023-04-29 | 20600 | keep | 0 | Apr | 2023 | 0.014031 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-04-29 20:50 | 2023-04-30 09:30 | 50 | 12:40 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | A23042900188 | New_Event | Primary Wire Break | Include | Include | Equipment | 760 | 2023-04-29 | 38000 | keep | 0 | Apr | 2023 | 0.025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-04-29 20:52 | 2023-04-30 14:12 | 1 | 17:20 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23042900189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1040 | 2023-04-29 | 1040 | keep | 0 | Apr | 2023 | 0.00070834 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-04-29 21:24 | 2023-04-30 16:50 | 25 | 19:26 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | A23042900193 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1166 | 2023-04-29 | 29150 | keep | 0 | Apr | 2023 | 0.019854 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-04-29 21:54 | 2023-04-30 08:58 | 30 | 11:04 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE SE REEMPLAZO CAJA PRIMARIA | R23042900201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 664 | 2023-04-29 | 19920 | keep | 0 | Apr | 2023 | 0.013567 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-04-29 22:23 | 2023-04-30 01:55 | 170 | 3:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y SE RREMPLAZO CAJA PRIMARIA AVERIADA | M23042900153 | New_Event | Cutout Failure | Include | Include | Equipment | 212 | 2023-04-29 | 36040 | keep | 0 | Apr | 2023 | 0.024547 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
CANOVANAS | 2023-04-29 22:29 | 2023-04-30 10:44 | 40 | 12:15 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23042900203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 735 | 2023-04-29 | 29400 | keep | 0 | Apr | 2023 | 0.020024 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-04-29 22:32 | 2023-04-30 07:32 | 100 | 9:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | B23042900453 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 540 | 2023-04-29 | 54000 | keep | 0 | Apr | 2023 | 0.036779 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-04-29 22:50 | 2023-04-29 23:18 | 3 | 0:28 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR SOLO LLEVA 490 CLIENTES DE SU CARGA. SE HICIERON OPERACIONES CON SJ-230429-50. SE CERRO N/O CONTRA 2403-02. ENTRARON 489 | R23042900191 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 28 | 2023-04-29 | 84 | keep | 0 | Apr | 2023 | 5.7212e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-29 23:18 | 2023-04-29 23:21 | 2579 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR 2403-02 HACIENDO OPERACIONES DE AMARRE CONTRA 2403-01 CON SJ-230429-50. QUEDA 3 CLIENTE FUERA | R23042900191 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 3 | 2023-04-29 | 7737 | keep | 0 | Apr | 2023 | 0.0052696 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-04-29 23:18 | 2023-04-29 23:21 | 500 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR HACIENDO OPERACIONES DE AMARRE CONTRA 2403-01 CON SJ-230429-50. LLEVA EL 99.9% DE LA CARGA DEL 2403-01. 3 SOLO CLIENTE FUERA | R23042900191 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-29 | 1500 | keep | 0 | Apr | 2023 | 0.0010216 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-04-29 23:21 | 2023-04-30 14:12 | 3 | 14:51 | P | CONDUCTOR ROTO O ABIERTO | SE DEJO SECCIONALIZADO ALAMBRE EN EL PISO CON PUENTE ABIERTOS ANTES Y DESPUES. NO HAY CLIENTES FUERA. SJ-230429-50 | R23042900191 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 891 | 2023-04-29 | 2673 | keep | 0 | Apr | 2023 | 0.0018206 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-04-29 23:24 | 2023-04-29 23:25 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 1859 | keep | 0 | Apr | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
SAN JUAN | 2023-04-29 23:26 | 2023-04-29 23:29 | 10211 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-29 | 30633 | keep | 0 | Apr | 2023 | 0.020864 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2023-04-29 23:26 | 2023-04-29 23:27 | 3471 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 16% POR EL 1620-02 | S2304290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-29 | 3471 | keep | 0 | Apr | 2023 | 0.0023641 | 0.0023641 | Momentary | FALSE | FALSE | Not_TMED_Event | 3471
BAYAMON | 2023-04-30 01:36 | 2023-04-30 01:37 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2304300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 652 | keep | 0 | Apr | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
BARRANQUITAS | 2023-04-30 02:04 | 2023-04-30 11:08 | 19 | 9:04 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN XMR TOMA AVERIADA | C23043000002 | New_Event | Customer-Related Interruption | Include | Include | Public | 544 | 2023-04-30 | 10336 | keep | 0 | Apr | 2023 | 0.0070398 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
YAUCO | 2023-04-30 02:04 | 2023-04-30 07:42 | 125 | 5:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23043000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2023-04-30 | 42250 | keep | 0 | Apr | 2023 | 0.028776 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BARRANQUITAS | 2023-04-30 02:04 | 2023-04-30 08:55 | 35 | 6:51 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L REEMPLAZO PARARRAYO | C23043000006 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 411 | 2023-04-30 | 14385 | keep | 0 | Apr | 2023 | 0.0097976 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-04-30 02:34 | 2023-04-30 02:35 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2304300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 853 | keep | 0 | Apr | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
AGUADILLA | 2023-04-30 02:52 | 2023-04-30 06:00 | 80 | 3:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C SE ABRIERON PUENTES PRIMARIOS DEBIDO A LINEA PARTIDA | M23043000010 | New_Event | Primary Wire Break | Include | Include | Equipment | 188 | 2023-04-30 | 15040 | keep | 0 | Apr | 2023 | 0.010244 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-04-30 03:09 | 2023-04-30 03:11 | 1802 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2304300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-30 | 3604 | keep | 0 | Apr | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2023-04-30 03:20 | 2023-04-30 12:13 | 200 | 8:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 2 X 65 EN C/LS FUERTES LLUVIAS | C23043000008 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 533 | 2023-04-30 | 106600 | keep | 0 | Apr | 2023 | 0.072605 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-04-30 05:31 | 2023-04-30 05:32 | 485 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23043000002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 485 | keep | 0 | Apr | 2023 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
BARRANQUITAS | 2023-04-30 05:35 | 2023-04-30 13:38 | 370 | 8:03 | P | DESGANCHE | 1 X 65 EN C/L | C23043000017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 483 | 2023-04-30 | 178710 | keep | 0 | Apr | 2023 | 0.12172 | 0.00025201 | Sustained | FALSE | FALSE | Not_TMED_Event | 370
CAGUAS | 2023-04-30 05:46 | 2023-04-30 05:47 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2304300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 1702 | keep | 0 | Apr | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2023-04-30 05:47 | 2023-04-30 09:46 | 75 | 3:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | R23043000006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2023-04-30 | 17925 | keep | 0 | Apr | 2023 | 0.012209 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-04-30 05:57 | 2023-04-30 08:08 | 747 | 2:11 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE RADIAL Y SE REPARO CONDUCTOR EN EL SUELO | B23043000008 | New_Event | Primary Wire Break | Include | Include | Equipment | 131 | 2023-04-30 | 97857 | keep | 0 | Apr | 2023 | 0.06665 | 0.00050878 | Sustained | FALSE | FALSE | Not_TMED_Event | 747
AGUADILLA | 2023-04-30 06:00 | 2023-04-30 14:10 | 12 | 8:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PARTIDA Y SE CERRO PUENTES | M23043000035 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 490 | 2023-04-30 | 5880 | keep | 0 | Apr | 2023 | 0.0040048 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-04-30 06:07 | 2023-04-30 08:54 | 47 | 2:47 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | R23043000008 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-04-30 | 7849 | keep | 0 | Apr | 2023 | 0.0053459 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-04-30 06:24 | 2023-04-30 10:18 | 244 | 3:54 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23043000016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 234 | 2023-04-30 | 57096 | keep | 0 | Apr | 2023 | 0.038888 | 0.00016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 244
FAJARDO | 2023-04-30 06:30 | 2023-04-30 08:15 | 75 | 1:45 | P | ANIMAL | 2 X 50 EN C/L CRUCE X AVE | R23043000010 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-04-30 | 7875 | keep | 0 | Apr | 2023 | 0.0053636 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2023-04-30 07:15 | 2023-04-30 10:10 | 50 | 2:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN CORTE DE LINEA | A23043000007 | New_Event | Primary Wire Break | Include | Include | Equipment | 175 | 2023-04-30 | 8750 | keep | 0 | Apr | 2023 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-30 07:38 | 2023-04-30 11:59 | 14 | 4:21 | P | ANIMAL | 1 X 25 EN C/L CRUCE X IGUANA | R23043000015 | New_Event | Animals | Include | Include | Wildlife | 261 | 2023-04-30 | 3654 | keep | 0 | Apr | 2023 | 0.0024887 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-04-30 07:41 | 2023-04-30 11:18 | 57 | 3:37 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23043000016 | New_Event | Animals | Include | Include | Wildlife | 217 | 2023-04-30 | 12369 | keep | 0 | Apr | 2023 | 0.0084245 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 1222 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 7332 | keep | 0 | Apr | 2023 | 0.0049938 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 2756 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 16536 | keep | 0 | Apr | 2023 | 0.011263 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 2833 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 16998 | keep | 0 | Apr | 2023 | 0.011577 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 1218 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 7308 | keep | 0 | Apr | 2023 | 0.0049774 | 0.00082957 | Sustained | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 1345 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 8070 | keep | 0 | Apr | 2023 | 0.0054964 | 0.00091607 | Sustained | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 1265 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 7590 | keep | 0 | Apr | 2023 | 0.0051695 | 0.00086159 | Sustained | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 2071 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 12426 | keep | 0 | Apr | 2023 | 0.0084633 | 0.0014105 | Sustained | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 760 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000016 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 4560 | keep | 0 | Apr | 2023 | 0.0031058 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 509 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 3054 | keep | 0 | Apr | 2023 | 0.0020801 | 0.00034668 | Sustained | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 2620 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 15720 | keep | 0 | Apr | 2023 | 0.010707 | 0.0017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2023-04-30 07:46 | 2023-04-30 07:52 | 1916 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2100 PUENTE ABIERTO EN ACB #1 SUB 7475 COLISEO RAYMOND DALMAU | A23043000017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-04-30 | 11496 | keep | 0 | Apr | 2023 | 0.0078299 | 0.001305 | Sustained | FALSE | FALSE | Not_TMED_Event | 1916
VEGA BAJA | 2023-04-30 07:46 | 2023-04-30 17:15 | 3 | 9:29 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23043000012 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 569 | 2023-04-30 | 1707 | keep | 0 | Apr | 2023 | 0.0011626 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-04-30 07:47 | 2023-04-30 13:10 | 20 | 5:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23043000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-04-30 | 6460 | keep | 0 | Apr | 2023 | 0.0043999 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-30 07:50 | 2023-04-30 07:51 | 1648 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23043000018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 1648 | keep | 0 | Apr | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
BAYAMON | 2023-04-30 07:55 | 2023-04-30 07:56 | 2605 | 0:01 | T | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | RECIERRE DE INTERRUPTOR | B2304300000X | New_Event | Secondary Wire Break | Include | Include | Equipment | 1 | 2023-04-30 | 2605 | keep | 0 | Apr | 2023 | 0.0017743 | 0.0017743 | Momentary | FALSE | FALSE | Not_TMED_Event | 2605
BAYAMON | 2023-04-30 07:55 | 2023-04-30 07:56 | 1859 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | B23043000062 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-30 | 1859 | keep | 0 | Apr | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-04-30 07:56 | 2023-04-30 08:53 | 1 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR BAJANTE SECUNDARIO | B23042900444 | 1st_after_momentary | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-04-30 | 57 | keep | 0 | Apr | 2023 | 3.8822e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-30 07:56 | 2023-04-30 11:54 | 100 | 3:58 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE LINEA A CAJA DE RISER | B23043000204 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 238 | 2023-04-30 | 23800 | keep | 0 | Apr | 2023 | 0.01621 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-04-30 07:59 | 2023-04-30 08:00 | 1089 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 50% DE LA CARGA X 3015-07 | C23043000031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 1089 | keep | 0 | Apr | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
BARRANQUITAS | 2023-04-30 08:06 | 2023-04-30 15:53 | 115 | 7:47 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23043000033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 467 | 2023-04-30 | 53705 | keep | 0 | Apr | 2023 | 0.036578 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
VEGA BAJA | 2023-04-30 08:08 | 2023-04-30 10:39 | 4027 | 2:31 | S | PROTECCION DEFECTUOSA | PERSONAL DE SUBESTACION CONFIRMA QUE EL 9101-03 TIENE PROBLEMAS CON LA PROTECCION Y FUNDIO FUSIBLE EN LA ALTA DEL TRANSFORMADOR | B23043000261 | New_Event | Protection Miscoordination | Include | Include | Other | 151 | 2023-04-30 | 608077 | keep | 0 | Apr | 2023 | 0.41416 | 0.0027428 | Sustained | FALSE | FALSE | Not_TMED_Event | 4027
VEGA BAJA | 2023-04-30 08:08 | 2023-04-30 10:39 | 2468 | 2:31 | S | PROTECCION DEFECTUOSA | PERSONAL DE SUBESTACION CONFIRMA QUE EL 9101-03 TIENE PROBLEMAS CON LA PROTECCION Y FUNDIO FUSIBLE EN LA ALTA DEL TRANSFORMADOR | B23043000261 | New_Event | Protection Miscoordination | Include | Include | Other | 151 | 2023-04-30 | 372668 | keep | 0 | Apr | 2023 | 0.25382 | 0.0016809 | Sustained | FALSE | FALSE | Not_TMED_Event | 2468
VEGA BAJA | 2023-04-30 08:08 | 2023-04-30 10:39 | 1494 | 2:31 | S | PROTECCION DEFECTUOSA | PERSONAL DE SUBESTACION CONFIRMA QUE EL 9101-03 TIENE PROBLEMAS CON LA PROTECCION Y FUNDIO FUSIBLE EN LA ALTA DEL TRANSFORMADOR | B23043000261 | New_Event | Protection Miscoordination | Include | Include | Other | 151 | 2023-04-30 | 225594 | keep | 0 | Apr | 2023 | 0.15365 | 0.0010176 | Sustained | FALSE | FALSE | Not_TMED_Event | 1494
ARECIBO | 2023-04-30 08:13 | 2023-04-30 12:30 | 30 | 4:17 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23043000046 | New_Event | Primary Wire Break | Include | Include | Equipment | 257 | 2023-04-30 | 7710 | keep | 0 | Apr | 2023 | 0.0052512 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-04-30 08:16 | 2023-04-30 13:48 | 7 | 5:32 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23043000034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 332 | 2023-04-30 | 2324 | keep | 0 | Apr | 2023 | 0.0015829 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-30 08:45 | 2023-04-30 10:42 | 43 | 1:57 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | B23043000100 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-04-30 | 5031 | keep | 0 | Apr | 2023 | 0.0034266 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
FAJARDO | 2023-04-30 08:50 | 2023-04-30 10:14 | 50 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN C/L MAL TIEMPO LLUVIAS | R23043000026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2023-04-30 | 4200 | keep | 0 | Apr | 2023 | 0.0028606 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-04-30 08:51 | 2023-04-30 13:42 | 48 | 4:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 Y 1 X 40 FUERTE LLUVIAS | M23043000025 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 291 | 2023-04-30 | 13968 | keep | 0 | Apr | 2023 | 0.0095135 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2023-04-30 08:56 | 2023-04-30 11:08 | 30 | 2:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23042900351 | New_Event | Secondary Wire Break | Include | Include | Equipment | 132 | 2023-04-30 | 3960 | keep | 0 | Apr | 2023 | 0.0026971 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-04-30 08:56 | 2023-04-30 12:30 | 25 | 3:34 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA PAJARO CRUZO | P23043000028 | New_Event | Animals | Include | Include | Wildlife | 214 | 2023-04-30 | 5350 | keep | 0 | Apr | 2023 | 0.0036439 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-04-30 08:56 | 2023-04-30 12:39 | 6 | 3:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR LLUVIAS FUERTES | C23043000041 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 223 | 2023-04-30 | 1338 | keep | 0 | Apr | 2023 | 0.00091131 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-04-30 08:57 | 2023-04-30 11:00 | 100 | 2:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | R23043000029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 123 | 2023-04-30 | 12300 | keep | 0 | Apr | 2023 | 0.0083775 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-30 08:58 | 2023-04-30 09:28 | 478 | 0:30 | T | CAUSAS EXTERNAS | DISPARO DE INTERRUPTOR .SE RETIRA GLOBO QUE CRUZO LAS TRES FASES DEL ALIMENTADOR SWF BY-230430-02 | B23043000187 | New_Event | Damage From Public | Include | Include | Public | 30 | 2023-04-30 | 14340 | keep | 0 | Apr | 2023 | 0.0097669 | 0.00032556 | Sustained | FALSE | FALSE | Not_TMED_Event | 478
AGUADILLA | 2023-04-30 09:00 | 2023-04-30 10:30 | 9 | 1:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE 50 KVA X 50 KVA | A23043000055 | New_Event | Service Transformer Failure | Include | Include | Equipment | 90 | 2023-04-30 | 810 | keep | 0 | Apr | 2023 | 0.00055169 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2023-04-30 09:03 | 2023-04-30 11:10 | 20 | 2:07 | P | MAL TIEMPO/RAYOS | 1 X 40 EN COVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | M23043000057 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 127 | 2023-04-30 | 2540 | keep | 0 | Apr | 2023 | 0.00173 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-30 09:05 | 2023-04-30 16:56 | 50 | 7:51 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23043000034 | New_Event | Animals | Include | Include | Wildlife | 471 | 2023-04-30 | 23550 | keep | 0 | Apr | 2023 | 0.01604 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-04-30 09:11 | 2023-04-30 12:50 | 30 | 3:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LA SALIDA DEL CORTE DE LINEA | A23043000059 | New_Event | Primary Wire Break | Include | Include | Equipment | 219 | 2023-04-30 | 6570 | keep | 0 | Apr | 2023 | 0.0044748 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-04-30 09:17 | 2023-04-30 16:25 | 1 | 7:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN MONTURA DE TRANSFORMADORES SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23043000063 | New_Event | Cutout Failure | Include | Include | Equipment | 428 | 2023-04-30 | 428 | keep | 0 | Apr | 2023 | 0.00029151 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-30 09:39 | 2023-04-30 12:10 | 65 | 2:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIAS | S23043000025 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 151 | 2023-04-30 | 9815 | keep | 0 | Apr | 2023 | 0.006685 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-04-30 09:44 | 2023-04-30 09:45 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POE SCADA | B23043000227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 320 | keep | 0 | Apr | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
CAGUAS | 2023-04-30 09:58 | 2023-04-30 18:37 | 82 | 8:39 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23043000070 | New_Event | Animals | Include | Include | Wildlife | 519 | 2023-04-30 | 42558 | keep | 0 | Apr | 2023 | 0.028986 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
BAYAMON | 2023-04-30 10:00 | 2023-05-01 12:31 | 50 | 26:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L 1 X 30 EN C/L SE REMPLAZO CAJA PRIMARIA | S23043000026 | New_Event | Cutout Failure | Include | Include | Equipment | 1591 | 2023-04-30 | 79550 | keep | 0 | Apr | 2023 | 0.054181 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-30 10:26 | 2023-04-30 11:25 | 4 | 0:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23043000076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 59 | 2023-04-30 | 236 | keep | 0 | Apr | 2023 | 0.00016074 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-04-30 10:26 | 2023-04-30 13:05 | 60 | 2:39 | P | ANIMAL | 2 X 50 EN CL CRUCE DE FASES POR AVE | M23043000030 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-04-30 | 9540 | keep | 0 | Apr | 2023 | 0.0064977 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-04-30 10:33 | 2023-04-30 10:34 | 2873 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23043000081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 2873 | keep | 0 | Apr | 2023 | 0.0019568 | 0.0019568 | Momentary | FALSE | FALSE | Not_TMED_Event | 2873
CANOVANAS | 2023-04-30 10:36 | 2023-04-30 10:37 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR 1646-03 LLEVA 1647-10 Y 25% DEL 1647-09 | R2304300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 3046 | keep | 0 | Apr | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-04-30 10:36 | 2023-04-30 10:37 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1646-03 LLEVA 1647-10 Y 25% DEL 1647-09 | R2304300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-30 | 513 | keep | 0 | Apr | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
CANOVANAS | 2023-04-30 10:36 | 2023-04-30 10:37 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1646-03 LLEVA 1647-10 Y 25% DEL 1647-09 | R2304300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-30 | 61 | keep | 0 | Apr | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
VEGA BAJA | 2023-04-30 10:39 | 2023-04-30 18:50 | 747 | 8:11 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | B23043000105 | New_Event | Primary Wire Break | Include | Include | Equipment | 491 | 2023-04-30 | 366777 | keep | 0 | Apr | 2023 | 0.24981 | 0.00050878 | Sustained | FALSE | FALSE | Not_TMED_Event | 747
CANOVANAS | 2023-04-30 10:43 | 2023-04-30 14:48 | 60 | 4:05 | P | DESGANCHE | 1 X 25 EN RISER, 1 X 65 EN C/L SE REEMPLAZO CAJA PRIMARIA, DEGANCHE | R23043000049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-04-30 | 14700 | keep | 0 | Apr | 2023 | 0.010012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-04-30 10:46 | 2023-04-30 15:15 | 70 | 4:29 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23043000077 | New_Event | Animals | Include | Include | Wildlife | 269 | 2023-04-30 | 18830 | keep | 0 | Apr | 2023 | 0.012825 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2023-04-30 10:58 | 2023-04-30 13:45 | 35 | 2:47 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA TRANSFORMADOR DE 50 KVA AVERIADO | P23043000031 | New_Event | Service Transformer Failure | Include | Include | Equipment | 167 | 2023-04-30 | 5845 | keep | 0 | Apr | 2023 | 0.003981 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-04-30 11:12 | 2023-04-30 13:21 | 100 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 80 EN C/L Y 1 X 10 EN XMR SE ELIMINO SECUNDARIA DE ALUMBRADO PUBLICO EN EL SUELO | C23043000088 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2023-04-30 | 12900 | keep | 0 | Apr | 2023 | 0.0087861 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-04-30 11:29 | 2023-04-30 12:42 | 1 | 1:13 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | B23043000264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-04-30 | 73 | keep | 0 | Apr | 2023 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-04-30 11:32 | 2023-04-30 11:46 | 12 | 0:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN RISER MAL TIEMPO LLUVIAS | S23043000034 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 14 | 2023-04-30 | 168 | keep | 0 | Apr | 2023 | 0.00011442 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-04-30 11:32 | 2023-04-30 14:55 | 20 | 3:23 | P | ARBOL SOBRE LINEA | 1 X 30 EN CONVERTIDOR SE RETIRO ARBOL SOBRE LAS LINEAS | A23043000085 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 203 | 2023-04-30 | 4060 | keep | 0 | Apr | 2023 | 0.0027652 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-30 11:40 | 2023-04-30 17:51 | 114 | 6:11 | P | ANIMAL | 1 X 100 EN EL SU-8A CRUCE X IGUANA | R23043000051 | New_Event | Animals | Include | Include | Wildlife | 371 | 2023-04-30 | 42294 | keep | 0 | Apr | 2023 | 0.028806 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
VEGA BAJA | 2023-04-30 11:57 | 2023-04-30 15:09 | 144 | 3:12 | P | DESGANCHE | 2 X 40 Y 2 X65 EN CORTES EN LINEA DESGANCHE | B23043000271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2023-04-30 | 27648 | keep | 0 | Apr | 2023 | 0.018831 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
SAN JUAN | 2023-04-30 12:19 | 2023-04-30 12:44 | 8 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S23042900331 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-04-30 | 200 | keep | 0 | Apr | 2023 | 0.00013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-04-30 12:27 | 2023-04-30 16:53 | 4 | 4:26 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR AVERIADO DE 25 KVA X 25 KVA | C23043000114 | New_Event | Service Transformer Failure | Include | Include | Equipment | 266 | 2023-04-30 | 1064 | keep | 0 | Apr | 2023 | 0.00072469 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-04-30 12:34 | 2023-04-30 12:37 | 726 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-03 LLEVA LA CARGA DEL 1346-04 SE CERRO POR CONTROL | S23043000038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-30 | 2178 | keep | 0 | Apr | 2023 | 0.0014834 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-04-30 12:34 | 2023-04-30 12:37 | 3932 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-03 LLEVA LA CARGA DEL 1346-04 SE CERRO POR CONTROL | S23043000038 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-04-30 | 11796 | keep | 0 | Apr | 2023 | 0.0080342 | 0.0026781 | Momentary | FALSE | FALSE | Not_TMED_Event | 3932
BAYAMON | 2023-04-30 12:43 | 2023-04-30 12:44 | 60 | 0:01 | P | ANIMAL | 1 X 125 EN SU-2 CRUCE X CULEBRA | B23043000248 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-04-30 | 60 | keep | 0 | Apr | 2023 | 4.0866e-05 | 4.0866e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-04-30 12:55 | 2023-04-30 15:43 | 5 | 2:48 | P | SECUNDARIA/DESGANCHE | 1 X 5 EN TRANSFORMADOR DESGANCHE | M23043000042 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 168 | 2023-04-30 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-04-30 12:58 | 2023-04-30 13:01 | 4381 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN "ON" NO RECERRO SE VERIFICO NO PERSONAL EN LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23043000043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-04-30 | 13143 | keep | 0 | Apr | 2023 | 0.0089516 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
VEGA BAJA | 2023-04-30 13:00 | 2023-04-30 16:12 | 20 | 3:12 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23043000285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2023-04-30 | 3840 | keep | 0 | Apr | 2023 | 0.0026154 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-04-30 13:02 | 2023-04-30 14:56 | 120 | 1:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO VIENTO | R23043000058 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 114 | 2023-04-30 | 13680 | keep | 0 | Apr | 2023 | 0.0093174 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-04-30 13:16 | 2023-04-30 14:53 | 80 | 1:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CL | M23043000044 | New_Event | Cutout Failure | Include | Include | Equipment | 97 | 2023-04-30 | 7760 | keep | 0 | Apr | 2023 | 0.0052853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-04-30 13:38 | 2023-04-30 20:54 | 327 | 7:16 | S | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD GROUND WIRE CRUZADO CON LA DISTRIBUCION OVERHEAD GROUND SOBRE LA LINEA | C23043000123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 436 | 2023-04-30 | 142572 | keep | 0 | Apr | 2023 | 0.097105 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
BARRANQUITAS | 2023-04-30 13:38 | 2023-04-30 20:53 | 1843 | 7:15 | S | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD GROUND WIRE CRUZADO CON LA DISTRIBUCION OVERHEAD GROUND SOBRE LA LINEA | C23043000123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 435 | 2023-04-30 | 801705 | keep | 0 | Apr | 2023 | 0.54604 | 0.0012553 | Sustained | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-04-30 13:38 | 2023-04-30 20:52 | 2203 | 7:14 | S | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD GROUND WIRE CRUZADO CON LA DISTRIBUCION OVERHEAD GROUND SOBRE LA LINEA | C23043000123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 434 | 2023-04-30 | 956102 | keep | 0 | Apr | 2023 | 0.6512 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
BARRANQUITAS | 2023-04-30 13:38 | 2023-04-30 20:50 | 2457 | 7:12 | S | LINEA DE TRANSMISION 38KV | SE RETIRO OVER HEAD GROUND WIRE CRUZADO CON LA DISTRIBUCION OVERHEAD GROUND SOBRE LA LINEA | C23043000123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 432 | 2023-04-30 | 1061424 | keep | 0 | Apr | 2023 | 0.72293 | 0.0016735 | Sustained | FALSE | FALSE | Not_TMED_Event | 2457
BAYAMON | 2023-04-30 13:42 | 2023-04-30 16:06 | 15 | 2:24 | P | ANIMAL | CRUCE POR AVE 1 X 40 EN C/L | B23043000294 | New_Event | Animals | Include | Include | Wildlife | 144 | 2023-04-30 | 2160 | keep | 0 | Apr | 2023 | 0.0014712 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-04-30 13:45 | 2023-04-30 16:00 | 7 | 2:15 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 50 KVA A 2.4KV AVERIADO | P23043000031 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 135 | 2023-04-30 | 945 | keep | 0 | Apr | 2023 | 0.00064364 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-04-30 13:56 | 2023-04-30 19:42 | 10 | 5:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23043000107 | New_Event | Primary Wire Break | Include | Include | Equipment | 346 | 2023-04-30 | 3460 | keep | 0 | Apr | 2023 | 0.0023566 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-04-30 13:59 | 2023-04-30 14:19 | 40 | 0:20 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L MAQUINA LIMPIANDO TERRENO SACUDIO LAS LINEAS | C23043000127 | New_Event | Damage From Public | Include | Include | Public | 20 | 2023-04-30 | 800 | keep | 0 | Apr | 2023 | 0.00054488 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-04-30 14:11 | 2023-04-30 14:14 | 2696 | 0:03 | T | PROBLEMA DEL CLIENTE | AL CERRAR HACIA SUBESTACION PRIVADA DE HOTEL FOX DELICIAS DISPARA ALIMENTADOR | P23043000042 | New_Event | Customer-Related Interruption | Include | Include | Public | 3 | 2023-04-30 | 8088 | keep | 0 | Apr | 2023 | 0.0055087 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
BAYAMON | 2023-04-30 14:33 | 2023-04-30 14:54 | 40 | 0:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 80 EN C/L | B23043000301 | New_Event | Cutout Failure | Include | Include | Equipment | 21 | 2023-04-30 | 840 | keep | 0 | Apr | 2023 | 0.00057212 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-04-30 14:55 | 2023-04-30 18:12 | 20 | 3:17 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23043000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-04-30 | 3940 | keep | 0 | Apr | 2023 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-04-30 14:58 | 2023-04-30 15:05 | 2 | 0:07 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B23043000305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-04-30 | 14 | keep | 0 | Apr | 2023 | 9.5353e-06 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-04-30 15:05 | 2023-04-30 18:05 | 25 | 3:00 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23043000306 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-04-30 | 4500 | keep | 0 | Apr | 2023 | 0.0030649 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-04-30 15:10 | 2023-04-30 18:48 | 200 | 3:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y REMPLAZO DE CAJA PRIMARIA | S23043000054 | New_Event | Cutout Failure | Include | Include | Equipment | 218 | 2023-04-30 | 43600 | keep | 0 | Apr | 2023 | 0.029696 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-04-30 15:13 | 2023-04-30 21:23 | 27 | 6:10 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L 1X 50 EN XMR | S23043000055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 370 | 2023-04-30 | 9990 | keep | 0 | Apr | 2023 | 0.0068041 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
MAYAGÃœEZ | 2023-04-30 15:14 | 2023-04-30 19:40 | 50 | 4:26 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | M23043000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-04-30 | 13300 | keep | 0 | Apr | 2023 | 0.0090586 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-04-30 15:15 | 2023-04-30 17:44 | 14 | 2:29 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA NO FUNDIO | C23043000143 | New_Event | Primary Wire Break | Include | Include | Equipment | 149 | 2023-04-30 | 2086 | keep | 0 | Apr | 2023 | 0.0014208 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-04-30 15:24 | 2023-04-30 17:52 | 9 | 2:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO PORTAFUSIBLE QUEMADO | C23043000145 | New_Event | Cutout Failure | Include | Include | Equipment | 148 | 2023-04-30 | 1332 | keep | 0 | Apr | 2023 | 0.00090722 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2023-04-30 15:30 | 2023-04-30 16:28 | 25 | 0:58 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | P23043000049 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-04-30 | 1450 | keep | 0 | Apr | 2023 | 0.00098759 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-04-30 15:32 | 2023-04-30 15:33 | 1986 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23043000126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 1986 | keep | 0 | Apr | 2023 | 0.0013527 | 0.0013527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1986
HUMACAO | 2023-04-30 15:47 | 2023-04-30 16:37 | 12 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIO XMR PARA REMPLAZAR EL BAJANTE SECUNDARIO | C23043000155 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-04-30 | 600 | keep | 0 | Apr | 2023 | 0.00040866 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-04-30 15:51 | 2023-04-30 18:13 | 50 | 2:22 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 50 EN C/LS | C23043000157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2023-04-30 | 7100 | keep | 0 | Apr | 2023 | 0.0048358 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-04-30 15:52 | 2023-04-30 18:15 | 4 | 2:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMEPLAZO PORTAFUSIBLE | R23043000077 | New_Event | Cutout Failure | Include | Include | Equipment | 143 | 2023-04-30 | 572 | keep | 0 | Apr | 2023 | 0.00038959 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
FAJARDO | 2023-04-30 16:02 | 2023-04-30 21:20 | 1 | 5:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REEMPLAZO CAJA RPIMARIA | R23043000078 | New_Event | Cutout Failure | Include | Include | Equipment | 318 | 2023-04-30 | 318 | keep | 0 | Apr | 2023 | 0.00021659 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-04-30 16:03 | 2023-04-30 22:26 | 200 | 6:23 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA POR DESGANCHE | P23043000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 383 | 2023-04-30 | 76600 | keep | 0 | Apr | 2023 | 0.052172 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
ARECIBO | 2023-04-30 16:04 | 2023-04-30 19:10 | 100 | 3:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23043000130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-04-30 | 18600 | keep | 0 | Apr | 2023 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-04-30 16:18 | 2023-04-30 18:50 | 40 | 2:32 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23043000139 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 152 | 2023-04-30 | 6080 | keep | 0 | Apr | 2023 | 0.0041411 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-04-30 16:21 | 2023-05-01 17:21 | 7 | 25:00 | P | DESGANCHE | 1 X 30 EN RISER DASGANCHE | B23043000459 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1500 | 2023-04-30 | 10500 | keep | 0 | Apr | 2023 | 0.0071515 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-04-30 16:24 | 2023-04-30 16:25 | 2435 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR CARGA POR EL 1909-08 | S2304300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-30 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-30 16:24 | 2023-04-30 16:25 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1907-05 | S2304300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 2956 | keep | 0 | Apr | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-04-30 16:25 | 2023-04-30 16:26 | 2435 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR CARGA POR EL 1909-08 | S2304300000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-30 | 2435 | keep | 0 | Apr | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-04-30 16:25 | 2023-04-30 16:26 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 1907-05 | S2304300000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 2956 | keep | 0 | Apr | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
AGUADILLA | 2023-04-30 16:38 | 2023-04-30 17:20 | 80 | 0:42 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23043000053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 42 | 2023-04-30 | 3360 | keep | 0 | Apr | 2023 | 0.0022885 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-04-30 16:52 | 2023-04-30 18:09 | 100 | 1:17 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23043000146 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 77 | 2023-04-30 | 7700 | keep | 0 | Apr | 2023 | 0.0052444 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-04-30 17:05 | 2023-04-30 18:45 | 25 | 1:40 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23043000149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 100 | 2023-04-30 | 2500 | keep | 0 | Apr | 2023 | 0.0017027 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-04-30 17:27 | 2023-05-01 13:40 | 31 | 20:13 | P | ANIMAL | 1 X 65 C/L SE REMOVIO AVE | S23043000351 | New_Event | Animals | Include | Include | Wildlife | 1213 | 2023-04-30 | 37603 | keep | 0 | Apr | 2023 | 0.025611 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-04-30 17:28 | 2023-04-30 18:40 | 61 | 1:12 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA REALIZAR DESGANCHE BY-230430-03 | B23043000363 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-04-30 | 4392 | keep | 0 | Apr | 2023 | 0.0029914 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
ARECIBO | 2023-04-30 18:09 | 2023-04-30 18:10 | 1986 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23043000162 | Additional_clients | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-04-30 | 1986 | keep | 0 | Apr | 2023 | 0.0013527 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-30 18:10 | 2023-04-30 21:43 | 100 | 3:33 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23043000146 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 213 | 2023-04-30 | 21300 | keep | 0 | Apr | 2023 | 0.014507 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-04-30 18:33 | 2023-04-30 21:17 | 4 | 2:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 Y SE REMPLAZO CAJA PRIMARIA | S23043000085 | New_Event | Cutout Failure | Include | Include | Equipment | 164 | 2023-04-30 | 656 | keep | 0 | Apr | 2023 | 0.0004468 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-04-30 18:40 | 2023-04-30 19:45 | 24 | 1:05 | P | DESGANCHE | SE SECCIONALIZO TRAMO Y SE REALIZO DESGANCHE PRIMARIO BY-230430-03 | B23043000363 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 65 | 2023-04-30 | 1560 | keep | 0 | Apr | 2023 | 0.0010625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-04-30 19:31 | 2023-04-30 21:00 | 50 | 1:29 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A23043000184 | New_Event | Primary Wire Break | Include | Include | Equipment | 89 | 2023-04-30 | 4450 | keep | 0 | Apr | 2023 | 0.0030309 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-04-30 19:42 | 2023-04-30 19:43 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2304300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 2466 | keep | 0 | Apr | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-04-30 19:53 | 2023-04-30 19:54 | 3070 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 9502-01 | B2304300000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-04-30 | 3070 | keep | 0 | Apr | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-04-30 19:53 | 2023-04-30 19:54 | 1647 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 9501-01 | B2304300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-30 | 1647 | keep | 0 | Apr | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-04-30 19:55 | 2023-04-30 19:57 | 3070 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR LLEVA LA CARGA DEL 9502-01 | B2304300000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 2 | 2023-04-30 | 6140 | keep | 0 | Apr | 2023 | 0.0041819 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-04-30 19:55 | 2023-04-30 19:57 | 1647 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR CARGA POR EL 9501-01 | B2304300000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-30 | 3294 | keep | 0 | Apr | 2023 | 0.0022435 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-04-30 20:14 | 2023-05-01 00:02 | 3070 | 3:48 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA Y SE CERRO POR SCADA BY-230430-04 | B23043000440 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 228 | 2023-04-30 | 699960 | keep | 0 | Apr | 2023 | 0.47674 | 0.002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-04-30 20:14 | 2023-04-30 23:42 | 1647 | 3:28 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA Y SE CERRO POR SCADA BY-230430-04 ESTA CARGA ESTABA POR EL 9501-01 EN LAS OPERACIONES SE NORMALIZO LA CARGA | B23043000440 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 208 | 2023-04-30 | 342576 | keep | 0 | Apr | 2023 | 0.23333 | 0.0011218 | Sustained | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-04-30 20:19 | 2023-05-01 03:34 | 394 | 7:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN TRAMO RADIAL | S23043000119 | New_Event | Primary Wire Break | Include | Include | Equipment | 435 | 2023-04-30 | 171390 | keep | 0 | Apr | 2023 | 0.11673 | 0.00026835 | Sustained | FALSE | FALSE | Not_TMED_Event | 394
BAYAMON | 2023-04-30 20:31 | 2023-05-01 09:26 | 77 | 12:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DSGANCHE BAMBUAS | B23043000124 | New_Event | Vegetation Contact | Include | Include | Vegetation | 775 | 2023-04-30 | 59675 | keep | 0 | Apr | 2023 | 0.040644 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
CANOVANAS | 2023-04-30 20:53 | 2023-04-30 22:45 | 324 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA EN C/L | R23043000096 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2023-04-30 | 36288 | keep | 0 | Apr | 2023 | 0.024716 | 0.00022067 | Sustained | FALSE | FALSE | Not_TMED_Event | 324
BARRANQUITAS | 2023-04-30 20:53 | 2023-04-30 22:20 | 170 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C23043000218 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-04-30 | 14790 | keep | 0 | Apr | 2023 | 0.010073 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
AGUADILLA | 2023-04-30 20:55 | 2023-04-30 22:44 | 50 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M23043000084 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-04-30 | 5450 | keep | 0 | Apr | 2023 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-04-30 21:23 | 2023-04-30 23:20 | 194 | 1:57 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C23043000235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2023-04-30 | 22698 | keep | 0 | Apr | 2023 | 0.01546 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
CANOVANAS | 2023-04-30 21:43 | 2023-05-01 10:18 | 1 | 12:35 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R23043000098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 755 | 2023-04-30 | 755 | keep | 0 | Apr | 2023 | 0.00051423 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-04-30 21:48 | 2023-04-30 22:54 | 4944 | 1:06 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO PARA LEVANTAR CONDUCTO PRIMARIO Y SE CERRO POR SCADA SJ-230430-01 | S23043000277 | New_Event | Primary Wire Break | Include | Include | Equipment | 66 | 2023-04-30 | 326304 | keep | 0 | Apr | 2023 | 0.22224 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
PONCE | 2023-04-30 22:37 | 2023-04-30 22:38 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23043000147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 3744 | keep | 0 | Apr | 2023 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
ARECIBO | 2023-04-30 22:39 | 2023-05-01 09:20 | 30 | 10:41 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER AVERIA SOTERRADA | A23043000207 | New_Event | UG Cable Fault | Include | Include | Equipment | 641 | 2023-04-30 | 19230 | keep | 0 | Apr | 2023 | 0.013097 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-04-30 22:54 | 2023-05-01 01:09 | 3955 | 2:15 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO SJ-230430-01 | S23043000277 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 135 | 2023-04-30 | 533925 | keep | 0 | Apr | 2023 | 0.36365 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-04-30 23:13 | 2023-04-30 23:15 | 72 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1404-07 LLEVA 5% DEL 1112-04 | S23043000388 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-04-30 | 144 | keep | 0 | Apr | 2023 | 9.8078e-05 | 4.9039e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-04-30 23:13 | 2023-04-30 23:15 | 1357 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 5% DEL 1112-04 | S23043000388 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-04-30 | 2714 | keep | 0 | Apr | 2023 | 0.0018485 | 0.00092425 | Momentary | FALSE | FALSE | Not_TMED_Event | 1357
HUMACAO | 2023-04-30 23:20 | 2023-04-30 23:21 | 800 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR 800 CLIENTES POR EL 3205-07 | C23043000249 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-04-30 | 800 | keep | 0 | Apr | 2023 | 0.00054488 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
CAGUAS | 2023-04-30 23:20 | 2023-04-30 23:21 | 3026 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA 800 CLIENTES DEL 2603-08 Y 1608 CLIENTES DE SU CARGA ESTAN POR EL 3201-01 | C23043000249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-04-30 | 3026 | keep | 0 | Apr | 2023 | 0.002061 | 0.002061 | Momentary | FALSE | FALSE | Not_TMED_Event | 3026
BAYAMON | 2023-05-01 00:02 | 2023-05-01 00:44 | 2149 | 0:42 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES PARA SECCIONALIZAR AVERIA Y SE CERRO POR SCADA BY-230430-04 | B23043000440 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 42 | 2023-05-01 | 90258 | keep | 0 | May | 2023 | 0.061474 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-05-01 00:08 | 2023-05-01 10:20 | 40 | 10:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M23050100001 | New_Event | Cutout Failure | Include | Include | Equipment | 612 | 2023-05-01 | 24480 | keep | 0 | May | 2023 | 0.016673 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-05-01 00:22 | 2023-05-01 18:33 | 30 | 18:11 | P | CONDUCTOR ROTO O ABIERTO | 2 X 40 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS ROTAS NOTA: FID 19499514 ES DEL 7902-03 Y ADJUNTAS NO APARECE EN ESE ALIMENTADOR EN EL PROGRAMA DE INTERRUPCIONES | A23050100001 | New_Event | Primary Wire Break | Include | Include | Equipment | 1091 | 2023-05-01 | 32730 | keep | 0 | May | 2023 | 0.022292 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-01 00:31 | 2023-05-01 00:33 | 81 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 5% POR EL 1404-07 | S2305010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-01 | 162 | keep | 0 | May | 2023 | 0.00011034 | 5.5169e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 81
SAN JUAN | 2023-05-01 00:31 | 2023-05-01 00:33 | 1357 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 5% DEL 1112-04 | S2305010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-01 | 2714 | keep | 0 | May | 2023 | 0.0018485 | 0.00092425 | Momentary | FALSE | FALSE | Not_TMED_Event | 1357
BAYAMON | 2023-05-01 00:41 | 2023-05-01 00:44 | 1647 | 0:03 | T | ALIMENTADOR AMARRADO | SE DISPARO ALIMENTADOR A PETICION DE WILFREDO VALLESCORBO PARA PODER CERRAR NO QUE ESTABA INOPERANTE BY-230430-04 | B23043000440 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-01 | 4941 | keep | 0 | May | 2023 | 0.0033653 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-01 00:44 | 2023-05-01 11:56 | 614 | 11:12 | P | CONDUCTOR ROTO O ABIERTO | BY-230430-04 LUEGO DE SECCIONALIZADO SE LEVANTO CONDUCTOR Y SE NORMALIZO LAS CARGAS | B23043000440 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 672 | 2023-05-01 | 412608 | keep | 0 | May | 2023 | 0.28103 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-01 02:39 | 2023-05-01 11:20 | 1 | 8:41 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | R23050100002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2023-05-01 | 521 | keep | 0 | May | 2023 | 0.00035485 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-01 03:01 | 2023-05-01 10:05 | 199 | 7:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN CORTE DE LINEA POSTE PRIMARIO PARTIDO POR ACCIDENTE DE AUTO FID13791195 | P23050100021 | New_Event | Primary Pole Failure | Include | Include | Equipment | 424 | 2023-05-01 | 84376 | keep | 0 | May | 2023 | 0.057468 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
FAJARDO | 2023-05-01 04:35 | 2023-05-01 08:39 | 296 | 4:04 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23050100009 | New_Event | Animals | Include | Include | Wildlife | 244 | 2023-05-01 | 72224 | keep | 0 | May | 2023 | 0.049191 | 0.0002016 | Sustained | FALSE | FALSE | Not_TMED_Event | 296
AGUADILLA | 2023-05-01 05:26 | 2023-05-01 07:43 | 3315 | 2:17 | T | DESGANCHE | SE RETIRO RAMA SE CERRO INTERRUPTOR | M23050100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-05-01 | 454155 | keep | 0 | May | 2023 | 0.30932 | 0.0022578 | Sustained | FALSE | FALSE | Not_TMED_Event | 3315
SAN JUAN | 2023-05-01 05:30 | 2023-05-01 12:36 | 274 | 7:06 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA QUEMADA EN RISER | S23050100098 | New_Event | Cutout Failure | Include | Include | Equipment | 426 | 2023-05-01 | 116724 | keep | 0 | May | 2023 | 0.0795 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
BAYAMON | 2023-05-01 05:39 | 2023-05-01 08:21 | 301 | 2:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 80 EN C/L MAL TIEMPO LLUVIAS | B23050100021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 162 | 2023-05-01 | 48762 | keep | 0 | May | 2023 | 0.033212 | 0.00020501 | Sustained | FALSE | FALSE | Not_TMED_Event | 301
BARRANQUITAS | 2023-05-01 06:03 | 2023-05-01 10:35 | 43 | 4:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23050100014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2023-05-01 | 11696 | keep | 0 | May | 2023 | 0.0079661 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CAGUAS | 2023-05-01 06:04 | 2023-05-01 12:13 | 123 | 6:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | C23050100017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 369 | 2023-05-01 | 45387 | keep | 0 | May | 2023 | 0.030913 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
CAGUAS | 2023-05-01 06:04 | 2023-05-01 11:31 | 24 | 5:27 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO DE LINEA A CAJA DEL RISER, SE CERRO N/O EN T-88 HACIA T-89, SE DEJO ABIERTO DEL RISER HACIA T-91 CG-230501-01 | C23050100016 | New_Event | Primary Wire Break | Include | Include | Equipment | 327 | 2023-05-01 | 7848 | keep | 0 | May | 2023 | 0.0053452 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-05-01 06:21 | 2023-05-02 06:36 | 4 | 24:15 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO ENTRE T 2 Y T 1 Y SE DIO SERVICIO | B23050100027 | New_Event | UG Cable Fault | Include | Include | Equipment | 1455 | 2023-05-01 | 5820 | keep | 0 | May | 2023 | 0.003964 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-05-01 06:59 | 2023-05-01 07:00 | 243 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23050100007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 243 | keep | 0 | May | 2023 | 0.00016551 | 0.00016551 | Momentary | FALSE | FALSE | Not_TMED_Event | 243
CANOVANAS | 2023-05-01 07:01 | 2023-05-01 09:21 | 40 | 2:20 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | R23050100011 | New_Event | Animals | Include | Include | Wildlife | 140 | 2023-05-01 | 5600 | keep | 0 | May | 2023 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-05-01 07:12 | 2023-05-01 07:13 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2305010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-01 07:14 | 2023-05-01 07:15 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23050100021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 2608 | keep | 0 | May | 2023 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
BAYAMON | 2023-05-01 07:25 | 2023-05-01 10:00 | 25 | 2:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA Y 1 X 65 EN RISER SE REEMPLAZO CAJA PRIMARIA | B23050100037 | New_Event | Cutout Failure | Include | Include | Equipment | 155 | 2023-05-01 | 3875 | keep | 0 | May | 2023 | 0.0026392 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-05-01 07:37 | 2023-05-01 07:38 | 327 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 5200 DE CAGUAS A AGUAS BUENAS | C23050100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-01 | 327 | keep | 0 | May | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BARRANQUITAS | 2023-05-01 07:37 | 2023-05-01 07:38 | 1843 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 5200 DE CAGUAS A AGUAS BUENAS | C23050100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-01 | 1843 | keep | 0 | May | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-05-01 07:37 | 2023-05-01 07:38 | 2203 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 5200 DE CAGUAS A AGUAS BUENAS | C23050100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-01 | 2203 | keep | 0 | May | 2023 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BARRANQUITAS | 2023-05-01 07:37 | 2023-05-01 07:38 | 2457 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 5200 DE CAGUAS A AGUAS BUENAS | C23050100023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-01 | 2457 | keep | 0 | May | 2023 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
SAN JUAN | 2023-05-01 08:05 | 2023-05-01 08:06 | 10211 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA ABRIR MACHETE Y SECCIONALIZAR NEUTRAL PRIMARIO EN EL PISO 2% EN SERVICIO | S23050100120 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-01 | 10211 | keep | 0 | May | 2023 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2023-05-01 08:05 | 2023-05-01 22:03 | 15 | 13:58 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER | S23050100115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 838 | 2023-05-01 | 12570 | keep | 0 | May | 2023 | 0.0085614 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-01 08:06 | 2023-05-01 09:38 | 10000 | 1:32 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO NEUTRAL PRIMARIO TRONCAL ALIMENTADOR Y SE CERRO MACHETE 100% EN SERVICIO | S23050100120 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 92 | 2023-05-01 | 920000 | keep | 0 | May | 2023 | 0.62661 | 0.006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 10000
CANOVANAS | 2023-05-01 08:06 | 2023-05-01 12:45 | 22 | 4:39 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R23050100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 279 | 2023-05-01 | 6138 | keep | 0 | May | 2023 | 0.0041806 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CANOVANAS | 2023-05-01 08:09 | 2023-05-01 09:15 | 91 | 1:06 | P | ANIMAL | 1 X 50 EN C/L CRUE POR AVE | R23050100015 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-05-01 | 6006 | keep | 0 | May | 2023 | 0.0040907 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
HUMACAO | 2023-05-01 08:09 | 2023-05-01 10:46 | 6 | 2:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | C23050100033 | New_Event | Cutout Failure | Include | Include | Equipment | 157 | 2023-05-01 | 942 | keep | 0 | May | 2023 | 0.00064159 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-05-01 08:29 | 2023-05-01 12:40 | 80 | 4:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23050100043 | New_Event | Cutout Failure | Include | Include | Equipment | 251 | 2023-05-01 | 20080 | keep | 0 | May | 2023 | 0.013676 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-05-01 08:30 | 2023-05-01 15:40 | 1 | 7:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REEMPLAZO 3 CAJAS PRIMARIAS DE BANCO DE XMR Y 3 PARARRAYOS | C23050100037 | New_Event | Cutout Failure | Include | Include | Equipment | 430 | 2023-05-01 | 430 | keep | 0 | May | 2023 | 0.00029287 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-01 08:42 | 2023-05-01 08:43 | 2132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23050100030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 2132 | keep | 0 | May | 2023 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
BAYAMON | 2023-05-01 08:47 | 2023-05-01 14:42 | 1 | 5:55 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23050100060 | New_Event | Animals | Include | Include | Wildlife | 355 | 2023-05-01 | 355 | keep | 0 | May | 2023 | 0.00024179 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-01 08:54 | 2023-05-01 17:30 | 1 | 8:36 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | S23050100172 | New_Event | Primary Pole Failure | Include | Include | Equipment | 516 | 2023-05-01 | 516 | keep | 0 | May | 2023 | 0.00035145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-01 08:58 | 2023-05-01 16:20 | 40 | 7:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M23050100053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 442 | 2023-05-01 | 17680 | keep | 0 | May | 2023 | 0.012042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-01 08:59 | 2023-05-01 09:50 | 425 | 0:51 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10700, EN SERVICIO SE SECCIONALIZO 10700 Y SE ENERGIZO LA VIRGENCITA 9404-00 DESDE DORADO TC CONDUCTOR AVERIADO | B23050100068 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 51 | 2023-05-01 | 21675 | keep | 0 | May | 2023 | 0.014763 | 0.00028947 | Sustained | FALSE | FALSE | Not_TMED_Event | 425
BAYAMON | 2023-05-01 09:03 | 2023-05-01 12:24 | 471 | 3:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN RISER MAL TIEMPO LLUVIA | S23050100231 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 201 | 2023-05-01 | 94671 | keep | 0 | May | 2023 | 0.06448 | 0.0003208 | Sustained | FALSE | FALSE | Not_TMED_Event | 471
ARECIBO | 2023-05-01 09:20 | 2023-05-01 15:00 | 50 | 5:40 | P | CABLE SOTERRADO AVERIADO | CABLE SOTERRADO AVERIADO SE CREO LINEA PROVISIONAL AEREA | A23043000207 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 340 | 2023-05-01 | 17000 | keep | 0 | May | 2023 | 0.011579 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-01 09:48 | 2023-05-01 13:21 | 6 | 3:33 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZARON PARARRAYOS | S23050100284 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 213 | 2023-05-01 | 1278 | keep | 0 | May | 2023 | 0.00087044 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-01 09:52 | 2023-05-01 10:12 | 2 | 0:20 | P | DESGANCHE | 1 X 40 Y 1 X 25 EN C/L SE REALIZO DESGANCHE | B23050100078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2023-05-01 | 40 | keep | 0 | May | 2023 | 2.7244e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-05-01 09:54 | 2023-05-02 10:10 | 50 | 24:16 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23050100034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1456 | 2023-05-01 | 72800 | keep | 0 | May | 2023 | 0.049584 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-01 09:55 | 2023-05-01 10:15 | 8 | 0:20 | P | CONDUCTOR ARRIADO O CRUZADO | SE REMPLAZO BAJANTES PRIMARIOS EN MALAS CONDICIONES EN TRANSFORMADOR CLIENTE CON SERVICIO SE ABRIO EL DIA 5/01 AUNQUE EVENTO ES DIA 30 | M23043000092 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 20 | 2023-05-01 | 160 | keep | 0 | May | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-05-01 10:00 | 2023-05-01 12:22 | 10 | 2:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 3 BARRAS EN PEDESTAL | C23043000128 | New_Event | Secondary Wire Break | Include | Include | Equipment | 142 | 2023-05-01 | 1420 | keep | 0 | May | 2023 | 0.00096716 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-05-01 10:05 | 2023-05-01 14:50 | 33 | 4:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECIONALIZO AVERIA SE REPARO POSTE PARTIDOS Y LINEAS FID100462001 | P23050100021 | New_Event | Primary Pole Failure | Include | Include | Equipment | 285 | 2023-05-01 | 9405 | keep | 0 | May | 2023 | 0.0064057 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
SAN JUAN | 2023-05-01 10:06 | 2023-05-01 12:21 | 1 | 2:15 | P | NO SE REPORTO CAUSA | 2 X 30 EN CORTE DE LINEA | S23050100290 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 135 | 2023-05-01 | 135 | keep | 0 | May | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-01 10:10 | 2023-05-01 18:11 | 7 | 8:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | S23050100293 | New_Event | Cutout Failure | Include | Include | Equipment | 481 | 2023-05-01 | 3367 | keep | 0 | May | 2023 | 0.0022932 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-05-01 10:30 | 2023-05-01 10:55 | 20 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23043000093 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-01 | 500 | keep | 0 | May | 2023 | 0.00034055 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-01 10:31 | 2023-05-01 19:12 | 50 | 8:41 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23050100298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2023-05-01 | 26050 | keep | 0 | May | 2023 | 0.017743 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-01 10:33 | 2023-05-01 13:55 | 30 | 3:22 | P | TRANSFORMADOR AVERIADO | 1 X 25 EN CORTE DE LINEA TRANSFORMADOR AVERIADO 37.5 KVA | M23050100080 | New_Event | Service Transformer Failure | Include | Include | Equipment | 202 | 2023-05-01 | 6060 | keep | 0 | May | 2023 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-01 10:37 | 2023-05-01 12:10 | 1 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23050100082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-05-01 | 93 | keep | 0 | May | 2023 | 6.3342e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-01 10:45 | 2023-05-01 11:40 | 90 | 0:55 | P | DESGANCHE | SE ABRIO CORTE DE LINEA TOTAL PARA RETIRAR BAMBUA SOBRE LINEA Y SE REPUSO 1 X 80 EN CORTE DE LINEA | C23050100184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-05-01 | 4950 | keep | 0 | May | 2023 | 0.0033714 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
AGUADILLA | 2023-05-01 10:45 | 2023-05-01 13:40 | 60 | 2:55 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M23050100087 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 175 | 2023-05-01 | 10500 | keep | 0 | May | 2023 | 0.0071515 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
UTUADO | 2023-05-01 10:47 | 2023-05-01 17:10 | 130 | 6:23 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTE DE CORTE DE LINEA | A23050100055 | New_Event | Primary Wire Break | Include | Include | Equipment | 383 | 2023-05-01 | 49790 | keep | 0 | May | 2023 | 0.033912 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2023-05-01 11:14 | 2023-05-01 11:18 | 1381 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23050100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-01 | 5524 | keep | 0 | May | 2023 | 0.0037624 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
HUMACAO | 2023-05-01 11:27 | 2023-05-01 12:35 | 12 | 1:08 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA CRUCE POR PITIRRE | C23050100077 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-05-01 | 816 | keep | 0 | May | 2023 | 0.00055577 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-01 11:40 | 2023-05-01 13:34 | 20 | 1:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23050100082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2023-05-01 | 2280 | keep | 0 | May | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-01 11:41 | 2023-05-01 13:25 | 20 | 1:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23050100107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 104 | 2023-05-01 | 2080 | keep | 0 | May | 2023 | 0.0014167 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-01 11:49 | 2023-05-01 14:30 | 361 | 2:41 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARARON LINEAS ARRIADAS | S23050100332 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 161 | 2023-05-01 | 58121 | keep | 0 | May | 2023 | 0.039586 | 0.00024588 | Sustained | FALSE | FALSE | Not_TMED_Event | 361
CANOVANAS | 2023-05-01 11:54 | 2023-05-01 14:34 | 40 | 2:40 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN C/L DESGANCHE | R23050100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-05-01 | 6400 | keep | 0 | May | 2023 | 0.004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-01 11:55 | 2023-05-01 17:44 | 70 | 5:49 | P | DESGANCHE | 3 X 40 Y 1 X 50 EN C/LS SE REALIZO DESGANCHE DE BAMBUA | C23050100088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2023-05-01 | 24430 | keep | 0 | May | 2023 | 0.016639 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-05-01 11:55 | 2023-05-01 12:55 | 8 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES EN LINEA SECUNDARIA | P23050100105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-05-01 | 480 | keep | 0 | May | 2023 | 0.00032693 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-05-01 12:07 | 2023-05-01 13:15 | 458 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 AISLADOR PARTIDO EN ACB 6913C | A23050100118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-05-01 | 31144 | keep | 0 | May | 2023 | 0.021212 | 0.00031194 | Sustained | FALSE | FALSE | Not_TMED_Event | 458
ARECIBO | 2023-05-01 12:07 | 2023-05-01 13:15 | 437 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 AISLADOR PARTIDO EN ACB 6913C | A23050100118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-05-01 | 29716 | keep | 0 | May | 2023 | 0.020239 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2023-05-01 12:07 | 2023-05-01 13:15 | 1185 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 AISLADOR PARTIDO EN ACB 6913C | A23050100118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-05-01 | 80580 | keep | 0 | May | 2023 | 0.054883 | 0.0008071 | Sustained | FALSE | FALSE | Not_TMED_Event | 1185
ARECIBO | 2023-05-01 12:07 | 2023-05-01 13:15 | 63 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 AISLADOR PARTIDO EN ACB 6913C | A23050100118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-05-01 | 4284 | keep | 0 | May | 2023 | 0.0029178 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
ARECIBO | 2023-05-01 12:07 | 2023-05-01 13:15 | 232 | 1:08 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 6900 AISLADOR PARTIDO EN ACB 6913C | A23050100118 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 68 | 2023-05-01 | 15776 | keep | 0 | May | 2023 | 0.010745 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
HUMACAO | 2023-05-01 12:09 | 2023-05-01 13:46 | 2 | 1:37 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | C23050100092 | New_Event | Animals | Include | Include | Wildlife | 97 | 2023-05-01 | 194 | keep | 0 | May | 2023 | 0.00013213 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-01 12:10 | 2023-05-01 13:50 | 30 | 1:40 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23050100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-05-01 | 3000 | keep | 0 | May | 2023 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-01 12:11 | 2023-05-01 18:16 | 15 | 6:05 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23050100093 | New_Event | Animals | Include | Include | Wildlife | 365 | 2023-05-01 | 5475 | keep | 0 | May | 2023 | 0.003729 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-01 12:14 | 2023-05-01 12:15 | 2610 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 2610 | keep | 0 | May | 2023 | 0.0017777 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
ARECIBO | 2023-05-01 12:22 | 2023-05-01 16:09 | 100 | 3:47 | P | CONDUCTOR ARRIADO O CRUZADO | 3 X 65 EN CORTE DE LINEA SE REPARO LINEAS CRUZADAS | A23050100098 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 227 | 2023-05-01 | 22700 | keep | 0 | May | 2023 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-01 12:30 | 2023-05-02 11:00 | 2 | 22:30 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23050100126 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1350 | 2023-05-01 | 2700 | keep | 0 | May | 2023 | 0.001839 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-01 12:36 | 2023-05-01 13:36 | 4944 | 1:00 | T | ARBOL SOBRE LINEA | DISPARO ALIMENTADOR SE ABRIO MACHETE PARA SECCIONALIZAR 80% EN SERVICIO | S23050100381 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 60 | 2023-05-01 | 296640 | keep | 0 | May | 2023 | 0.20204 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
PONCE | 2023-05-01 13:00 | 2023-05-01 13:52 | 13 | 0:52 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO HOT CLAMP EN TRANSFORMADOR | P23050100012 | New_Event | Primary Wire Break | Include | Include | Equipment | 52 | 2023-05-01 | 676 | keep | 0 | May | 2023 | 0.00046042 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-05-01 13:05 | 2023-05-01 13:45 | 70 | 0:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050100125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2023-05-01 | 2800 | keep | 0 | May | 2023 | 0.0019071 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2023-05-01 13:12 | 2023-05-01 14:46 | 20 | 1:34 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R23050100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-05-01 | 1880 | keep | 0 | May | 2023 | 0.0012805 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-01 13:17 | 2023-05-01 13:52 | 118 | 0:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA AVERIADA DE RISER FID 17290975 | M23050100126 | New_Event | Cutout Failure | Include | Include | Equipment | 35 | 2023-05-01 | 4130 | keep | 0 | May | 2023 | 0.0028129 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
SAN JUAN | 2023-05-01 13:32 | 2023-05-01 14:12 | 6 | 0:40 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR DESGANCHE Y SE REMPLAZO BAJANTE SECUNDARIO | S23050100465 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 40 | 2023-05-01 | 240 | keep | 0 | May | 2023 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-01 13:36 | 2023-05-01 14:44 | 989 | 1:08 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO MACHETE 100% EN SERVICIO | S23050100381 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 68 | 2023-05-01 | 67252 | keep | 0 | May | 2023 | 0.045805 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-01 13:36 | 2023-05-01 18:33 | 274 | 4:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA QUEMADA EN RISER | S23050100098 | New_Event | Cutout Failure | Include | Include | Equipment | 297 | 2023-05-01 | 81378 | keep | 0 | May | 2023 | 0.055426 | 0.00018662 | Sustained | FALSE | FALSE | Not_TMED_Event | 274
SAN JUAN | 2023-05-01 13:47 | 2023-05-01 15:02 | 1 | 1:15 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO ALIMENTADOR SE VERIFICO BKR.1 TENIA BUSHING AVERIADO Y CERAMICA Y SE RETIRO PARARRAYO Y SE PASO CARGA AL 1346-02 | S23050100493 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 75 | 2023-05-01 | 75 | keep | 0 | May | 2023 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-01 13:55 | 2023-05-01 17:00 | 8 | 3:05 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR QUEMADO 37.5KVA SE ABRIO CORTE DE LINEA PARA PODER REMPLAZARLO | M23050100080 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 185 | 2023-05-01 | 1480 | keep | 0 | May | 2023 | 0.001008 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-01 14:01 | 2023-05-01 14:04 | 1381 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2305010000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-01 | 4143 | keep | 0 | May | 2023 | 0.0028218 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
MAYAGÃœEZ | 2023-05-01 14:01 | 2023-05-01 15:10 | 1 | 1:09 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23050100133 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2023-05-01 | 69 | keep | 0 | May | 2023 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-01 14:07 | 2023-05-01 15:40 | 100 | 1:33 | P | ANIMAL | 1 X 80 EN RISER AVE | R23050100068 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-05-01 | 9300 | keep | 0 | May | 2023 | 0.0063342 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-05-01 14:19 | 2023-05-01 14:27 | 70 | 0:08 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA IGUANA CRUZO LINEAS | A23050100142 | New_Event | Animals | Include | Include | Wildlife | 8 | 2023-05-01 | 560 | keep | 0 | May | 2023 | 0.00038141 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-05-01 14:27 | 2023-05-01 15:42 | 5 | 1:15 | P | PROBLEMA DEL CLIENTE | SE REPARO CONECTORES Y DESGANCHE PROBLMEA INTERNO | B23050100145 | New_Event | Customer-Related Interruption | Include | Include | Public | 75 | 2023-05-01 | 375 | keep | 0 | May | 2023 | 0.00025541 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-01 14:30 | 2023-05-01 15:25 | 512 | 0:55 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE RETEZO LINEA | S23050100332 | Additional_clients | Primary To Primary Contact | Include | Include | Equipment | 55 | 2023-05-01 | 28160 | keep | 0 | May | 2023 | 0.01918 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-01 14:34 | 2023-05-01 17:00 | 30 | 2:26 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23050100077 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-05-01 | 4380 | keep | 0 | May | 2023 | 0.0029832 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-01 14:42 | 2023-05-01 17:50 | 10 | 3:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23050100136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-05-01 | 1880 | keep | 0 | May | 2023 | 0.0012805 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-01 14:48 | 2023-05-01 15:15 | 7 | 0:27 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS SECUNDARIAS | A23050100155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 27 | 2023-05-01 | 189 | keep | 0 | May | 2023 | 0.00012873 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-05-01 14:50 | 2023-05-01 21:00 | 3 | 6:10 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO 500 PIES DE LINEA SECUNDARIA 3/2 | P23050100021 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 370 | 2023-05-01 | 1110 | keep | 0 | May | 2023 | 0.00075602 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-01 14:54 | 2023-05-01 15:56 | 5 | 1:02 | P | ANIMAL | 1 X 30 C/L CRUCE POR AVE | B23050100143 | New_Event | Animals | Include | Include | Wildlife | 62 | 2023-05-01 | 310 | keep | 0 | May | 2023 | 0.00021114 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-01 15:17 | 2023-05-02 06:06 | 30 | 14:49 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23050100154 | New_Event | Animals | Include | Include | Wildlife | 889 | 2023-05-01 | 26670 | keep | 0 | May | 2023 | 0.018165 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-05-01 15:17 | 2023-05-01 17:14 | 50 | 1:57 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR AVES CRUZARON LINEAS | A23050100158 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-05-01 | 5850 | keep | 0 | May | 2023 | 0.0039844 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-01 15:42 | 2023-05-01 17:10 | 1381 | 1:28 | T | DESCONECTIVO DEFECTUOSO | DISPARO ALIMENTADOR SE REMPLAZO MACHETE SALIDA RISER | S23050100567 | New_Event | Switch Failure | Include | Include | Equipment | 88 | 2023-05-01 | 121528 | keep | 0 | May | 2023 | 0.082772 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
CAGUAS | 2023-05-01 15:44 | 2023-05-01 17:41 | 1 | 1:57 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23050100126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2023-05-01 | 117 | keep | 0 | May | 2023 | 7.9688e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-01 15:44 | 2023-05-01 17:42 | 20 | 1:58 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23050100143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-05-01 | 2360 | keep | 0 | May | 2023 | 0.0016074 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-05-01 16:02 | 2023-05-01 16:52 | 25 | 0:50 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | R23050100090 | New_Event | Animals | Include | Include | Wildlife | 50 | 2023-05-01 | 1250 | keep | 0 | May | 2023 | 0.00085137 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-05-01 16:02 | 2023-05-01 18:05 | 174 | 2:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER HACIA SU-02 | R23050100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 123 | 2023-05-01 | 21402 | keep | 0 | May | 2023 | 0.014577 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
CANOVANAS | 2023-05-01 16:03 | 2023-05-01 18:52 | 206 | 2:49 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23050100091 | New_Event | Animals | Include | Include | Wildlife | 169 | 2023-05-01 | 34814 | keep | 0 | May | 2023 | 0.023712 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
CANOVANAS | 2023-05-01 16:09 | 2023-05-01 20:57 | 8 | 4:48 | P | NO SE REPORTO CAUSA | 1 X 10 EN PM | R23050100092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2023-05-01 | 2304 | keep | 0 | May | 2023 | 0.0015692 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-01 16:19 | 2023-05-01 16:49 | 15 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR BARRAS EN PEDESTAL SECUNDARIO | C23050100138 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-05-01 | 450 | keep | 0 | May | 2023 | 0.00030649 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-01 16:24 | 2023-05-01 20:24 | 138 | 4:00 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23050100593 | New_Event | Vegetation Contact | Include | Include | Vegetation | 240 | 2023-05-01 | 33120 | keep | 0 | May | 2023 | 0.022558 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
CANOVANAS | 2023-05-01 16:24 | 2023-05-01 17:42 | 53 | 1:18 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23050100096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-05-01 | 4134 | keep | 0 | May | 2023 | 0.0028156 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
CAGUAS | 2023-05-01 16:35 | 2023-05-01 19:29 | 3 | 2:54 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 50 EN RISER CRUCE X AVE | C23050100144 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-05-01 | 522 | keep | 0 | May | 2023 | 0.00035553 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-05-01 16:42 | 2023-05-01 20:20 | 40 | 3:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050100168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-05-01 | 8720 | keep | 0 | May | 2023 | 0.0059392 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-01 16:42 | 2023-05-01 19:54 | 8 | 3:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23050100172 | New_Event | Secondary Wire Break | Include | Include | Equipment | 192 | 2023-05-01 | 1536 | keep | 0 | May | 2023 | 0.0010462 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-01 16:52 | 2023-05-01 16:53 | 4089 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B23050100173 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-01 | 4089 | keep | 0 | May | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2023-05-01 16:53 | 2023-05-01 23:35 | 1363 | 6:42 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO N/O CONTRA 1801-05 POR PUENTE ABIERTO A LA SALIDA 1806-03 100% EN SERVICIO BY-230501-01 | B23050100174 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 402 | 2023-05-01 | 547926 | keep | 0 | May | 2023 | 0.37319 | 0.00092833 | Sustained | FALSE | FALSE | Not_TMED_Event | 1363
AGUADILLA | 2023-05-01 16:56 | 2023-05-01 18:03 | 10 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23050100169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2023-05-01 | 670 | keep | 0 | May | 2023 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-01 16:57 | 2023-05-01 16:59 | 1116 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2305010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-01 | 2232 | keep | 0 | May | 2023 | 0.0015202 | 0.0007601 | Momentary | FALSE | FALSE | Not_TMED_Event | 1116
MAYAGÃœEZ | 2023-05-01 17:00 | 2023-05-01 18:00 | 30 | 1:00 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO 37.5 KVA X 37.5 KVA Y SE CERRO CORTE DE LINEA | M23050100080 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 60 | 2023-05-01 | 1800 | keep | 0 | May | 2023 | 0.001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-01 17:16 | 2023-05-01 19:19 | 25 | 2:03 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23050100156 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-05-01 | 3075 | keep | 0 | May | 2023 | 0.0020944 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-05-01 17:16 | 2023-05-01 18:23 | 150 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23050100192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2023-05-01 | 10050 | keep | 0 | May | 2023 | 0.006845 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-01 17:17 | 2023-05-01 17:19 | 921 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL 70% POR 9502-01 | B23050100190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-01 | 1842 | keep | 0 | May | 2023 | 0.0012546 | 0.00062729 | Momentary | FALSE | FALSE | Not_TMED_Event | 921
CANOVANAS | 2023-05-01 17:33 | 2023-05-01 19:29 | 53 | 1:56 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23050100111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-05-01 | 6148 | keep | 0 | May | 2023 | 0.0041874 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BAYAMON | 2023-05-01 17:55 | 2023-05-01 17:56 | 2147 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23050100216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 2147 | keep | 0 | May | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
SAN JUAN | 2023-05-01 17:56 | 2023-05-01 20:14 | 138 | 2:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO CAUSA | S23050100638 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 138 | 2023-05-01 | 19044 | keep | 0 | May | 2023 | 0.012971 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
CANOVANAS | 2023-05-01 17:57 | 2023-05-01 19:07 | 124 | 1:10 | P | ANIMAL | 1 X 50 CRUCE POR AVE | R23050100139 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-05-01 | 8680 | keep | 0 | May | 2023 | 0.0059119 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
ARECIBO | 2023-05-01 18:07 | 2023-05-01 19:43 | 50 | 1:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050100204 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-05-01 | 4800 | keep | 0 | May | 2023 | 0.0032693 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-01 18:08 | 2023-05-02 11:08 | 45 | 17:00 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23050100642 | New_Event | Primary Wire Break | Include | Include | Equipment | 1020 | 2023-05-01 | 45900 | keep | 0 | May | 2023 | 0.031262 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-05-01 18:09 | 2023-05-01 18:10 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23050100184 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 312 | keep | 0 | May | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
MAYAGÃœEZ | 2023-05-01 18:09 | 2023-05-01 18:10 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23050100185 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 4641 | keep | 0 | May | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
AGUADILLA | 2023-05-01 18:13 | 2023-05-01 18:14 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23050100186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 3041 | keep | 0 | May | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
SAN JUAN | 2023-05-01 18:14 | 2023-05-02 04:26 | 155 | 10:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23050100645 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 612 | 2023-05-01 | 94860 | keep | 0 | May | 2023 | 0.064609 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
BARRANQUITAS | 2023-05-01 18:29 | 2023-05-02 12:05 | 13 | 17:36 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR | C23050100169 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1056 | 2023-05-01 | 13728 | keep | 0 | May | 2023 | 0.0093501 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-05-01 18:52 | 2023-05-01 18:53 | 4079 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 10% DE SU CARGA ESTA X 1801-02 | B2305010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 4079 | keep | 0 | May | 2023 | 0.0027782 | 0.0027782 | Momentary | FALSE | FALSE | Not_TMED_Event | 4079
CAGUAS | 2023-05-01 18:59 | 2023-05-01 19:00 | 3005 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050100172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-01 | 3005 | keep | 0 | May | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CANOVANAS | 2023-05-01 19:07 | 2023-05-01 19:08 | 2708 | 0:01 | T | ANIMAL | RECIERRE | R2305010000X | Additional_clients | Animals | Include | Include | Wildlife | 1 | 2023-05-01 | 2708 | keep | 0 | May | 2023 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-01 19:08 | 2023-05-02 02:30 | 124 | 7:22 | P | ANIMAL | 1 X 50 CRUCE POR AVE | R23050100139 | 1st_after_momentary | Animals | Include | Include | Wildlife | 442 | 2023-05-01 | 54808 | keep | 0 | May | 2023 | 0.037329 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
CAGUAS | 2023-05-01 19:39 | 2023-05-01 20:50 | 80 | 1:11 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23050100183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2023-05-01 | 5680 | keep | 0 | May | 2023 | 0.0038686 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-01 19:47 | 2023-05-01 21:57 | 20 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | S23050100662 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-05-01 | 2600 | keep | 0 | May | 2023 | 0.0017708 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-01 19:52 | 2023-05-01 22:13 | 250 | 2:21 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | A23050100231 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2023-05-01 | 35250 | keep | 0 | May | 2023 | 0.024009 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-05-01 19:58 | 2023-05-02 05:10 | 34 | 9:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA Y 1 X 10 EN XMR | B23050100344 | New_Event | Secondary Wire Break | Include | Include | Equipment | 552 | 2023-05-01 | 18768 | keep | 0 | May | 2023 | 0.012783 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
UTUADO | 2023-05-01 20:17 | 2023-05-01 20:55 | 90 | 0:38 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050100239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 38 | 2023-05-01 | 3420 | keep | 0 | May | 2023 | 0.0023293 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
ARECIBO | 2023-05-01 20:24 | 2023-05-01 23:28 | 60 | 3:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23050100245 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 184 | 2023-05-01 | 11040 | keep | 0 | May | 2023 | 0.0075193 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-01 20:25 | 2023-05-02 03:00 | 402 | 6:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23050100693 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 395 | 2023-05-01 | 158790 | keep | 0 | May | 2023 | 0.10815 | 0.0002738 | Sustained | FALSE | FALSE | Not_TMED_Event | 402
SAN JUAN | 2023-05-01 20:33 | 2023-05-01 23:23 | 200 | 2:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23050100703 | New_Event | Primary Wire Break | Include | Include | Equipment | 170 | 2023-05-01 | 34000 | keep | 0 | May | 2023 | 0.023157 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-05-01 20:50 | 2023-05-01 22:22 | 25 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO SEC | R23050100130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2023-05-01 | 2300 | keep | 0 | May | 2023 | 0.0015665 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-01 20:51 | 2023-05-02 14:02 | 12 | 17:11 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | S23050100730 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1031 | 2023-05-01 | 12372 | keep | 0 | May | 2023 | 0.0084265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-05-01 20:51 | 2023-05-02 05:00 | 100 | 8:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN C/L SE REMPLAZO CAJA EN C/L | P23050100197 | New_Event | Cutout Failure | Include | Include | Equipment | 489 | 2023-05-01 | 48900 | keep | 0 | May | 2023 | 0.033306 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-05-01 20:58 | 2023-05-02 | 100 | 3:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 140 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | A23050100257 | New_Event | Primary Wire Break | Include | Include | Equipment | 182 | 2023-05-01 | 18200 | keep | 0 | May | 2023 | 0.012396 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-01 21:02 | 2023-05-02 09:40 | 25 | 12:38 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE RETEZO LINEA MONOFASICA PEGANDO A FOCO | C23050100192 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 758 | 2023-05-01 | 18950 | keep | 0 | May | 2023 | 0.012907 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-05-01 21:17 | 2023-05-02 17:22 | 68 | 20:05 | P | DESGANCHE | 1 X 50 EN C/L SE ENDEREZO POSTE SE INSTALO TENSOR SE LEVANTO LINEA Y NEUTRAL PRIMARIO Y SE DESGANCHO | C23050100193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1205 | 2023-05-01 | 81940 | keep | 0 | May | 2023 | 0.055809 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
AGUADILLA | 2023-05-01 21:22 | 2023-05-02 02:39 | 300 | 5:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23050100220 | New_Event | Cutout Failure | Include | Include | Equipment | 317 | 2023-05-01 | 95100 | keep | 0 | May | 2023 | 0.064772 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-05-01 21:39 | 2023-05-02 12:30 | 12 | 14:51 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR SE RETEZO LINEA SECUNDARIA | S23050100777 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 891 | 2023-05-01 | 10692 | keep | 0 | May | 2023 | 0.0072823 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-05-01 22:03 | 2023-05-02 01:16 | 100 | 3:13 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | M23050100231 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-05-01 | 19300 | keep | 0 | May | 2023 | 0.013145 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-01 23:18 | 2023-05-02 01:14 | 177 | 1:56 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23050100454 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-05-01 | 20532 | keep | 0 | May | 2023 | 0.013984 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
BARRANQUITAS | 2023-05-01 23:22 | 2023-05-01 23:24 | 1403 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | C23050100201 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-01 | 2806 | keep | 0 | May | 2023 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
CANOVANAS | 2023-05-01 23:31 | 2023-05-02 10:02 | 10 | 10:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE LEVANTO Y REPARO CONDUCTOR SECUNDARIO DEL SUELO. | R23050100141 | New_Event | Secondary Wire Break | Include | Include | Equipment | 631 | 2023-05-01 | 6310 | keep | 0 | May | 2023 | 0.0042977 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-01 23:35 | 2023-05-02 07:35 | 21 | 8:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE DEJO SECUNDARIA AVERIADA FUERA | C23050100203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 480 | 2023-05-01 | 10080 | keep | 0 | May | 2023 | 0.0068654 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
AGUADILLA | 2023-05-02 | 2023-05-02 02:22 | 80 | 2:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | M23050200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2023-05-02 | 11360 | keep | 0 | May | 2023 | 0.0077372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-05-02 00:17 | 2023-05-02 06:20 | 15 | 6:03 | P | ANIMAL | 1 X 30 ENTRANSFORMADOR PAJARO CRUZO FASE | P23050200001 | New_Event | Animals | Include | Include | Wildlife | 363 | 2023-05-02 | 5445 | keep | 0 | May | 2023 | 0.0037086 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-02 01:57 | 2023-05-02 01:58 | 1834 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
MAYAGÃœEZ | 2023-05-02 02:17 | 2023-05-02 08:19 | 200 | 6:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 200 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M23050200004 | New_Event | Cutout Failure | Include | Include | Equipment | 362 | 2023-05-02 | 72400 | keep | 0 | May | 2023 | 0.049311 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-05-02 03:17 | 2023-05-02 03:19 | 4304 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M23050200007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-02 | 8608 | keep | 0 | May | 2023 | 0.0058629 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2023-05-02 03:40 | 2023-05-02 08:22 | 160 | 4:42 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN C/L Y SE DESENREDO LAS LINEAS | B23050200012 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 282 | 2023-05-02 | 45120 | keep | 0 | May | 2023 | 0.030731 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
CAGUAS | 2023-05-02 04:09 | 2023-05-02 04:10 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 853 | keep | 0 | May | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
PONCE | 2023-05-02 04:42 | 2023-05-02 08:35 | 16 | 3:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES EN LINEA SECUNDARIA | P23050200012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 233 | 2023-05-02 | 3728 | keep | 0 | May | 2023 | 0.0025391 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-05-02 05:04 | 2023-05-02 05:05 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23050200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 2126 | keep | 0 | May | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-05-02 05:19 | 2023-05-02 12:47 | 100 | 7:28 | P | DESGANCHE | 1 X 80 1 X 40 EN C/L DESGANCHE | C23050200002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2023-05-02 | 44800 | keep | 0 | May | 2023 | 0.030513 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-02 05:30 | 2023-05-02 05:31 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23050200017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 4381 | keep | 0 | May | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2023-05-02 05:57 | 2023-05-02 07:54 | 4 | 1:57 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN TRANSFORMADOR SE ELIMINO PARARRAYO | S23050200002 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 117 | 2023-05-02 | 468 | keep | 0 | May | 2023 | 0.00031875 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-05-02 06:24 | 2023-05-02 09:25 | 50 | 3:01 | P | ANIMAL | 2 X 80 EN CORTE DE LINEA AVE CRUZO FASES | M23050200018 | New_Event | Animals | Include | Include | Wildlife | 181 | 2023-05-02 | 9050 | keep | 0 | May | 2023 | 0.0061639 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-02 06:36 | 2023-05-02 06:37 | 308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 308 | keep | 0 | May | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-05-02 06:37 | 2023-05-02 15:47 | 4 | 9:10 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO AVERIADO ENTRE T 2 Y T 1 Y SE DIO SERVICIO | B23050100027 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 550 | 2023-05-02 | 2200 | keep | 0 | May | 2023 | 0.0014984 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-02 06:59 | 2023-05-02 07:02 | 1785 | 0:03 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1801-02, LLEVA 1711-04 90% Y 1717-01 10% | B2305020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-02 | 5355 | keep | 0 | May | 2023 | 0.0036473 | 0.0012158 | Momentary | FALSE | FALSE | Not_TMED_Event | 1785
BAYAMON | 2023-05-02 06:59 | 2023-05-02 07:02 | 453 | 0:03 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1801-02, LLEVA 1711-04 90% Y 1717-01 10% | B2305020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-02 | 1359 | keep | 0 | May | 2023 | 0.00092561 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-05-02 06:59 | 2023-05-02 07:02 | 186 | 0:03 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR LLEVA 1711-04 90% Y 1717-01 10% | B2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-02 | 558 | keep | 0 | May | 2023 | 0.00038005 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
MAYAGÃœEZ | 2023-05-02 07:14 | 2023-05-02 11:15 | 40 | 4:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA | M23050200026 | New_Event | Cutout Failure | Include | Include | Equipment | 241 | 2023-05-02 | 9640 | keep | 0 | May | 2023 | 0.0065658 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-05-02 07:25 | 2023-05-02 09:25 | 87 | 2:00 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | C23050200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 120 | 2023-05-02 | 10440 | keep | 0 | May | 2023 | 0.0071106 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
SAN JUAN | 2023-05-02 07:32 | 2023-05-02 07:33 | 181 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | S23050200000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-02 | 181 | keep | 0 | May | 2023 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2023-05-02 07:32 | 2023-05-02 07:35 | 513 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% POR 1118-10 | S23050200008 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-02 | 1539 | keep | 0 | May | 2023 | 0.0010482 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-05-02 07:32 | 2023-05-02 07:35 | 2782 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% DEL 1111-01 | S23050200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-02 | 8346 | keep | 0 | May | 2023 | 0.0056844 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
HUMACAO | 2023-05-02 07:32 | 2023-05-02 10:20 | 37 | 2:48 | P | ANIMAL | 2 X 80 EN CORTE DE LINEA CRUCE POR AVE | C23050200012 | New_Event | Animals | Include | Include | Wildlife | 168 | 2023-05-02 | 6216 | keep | 0 | May | 2023 | 0.0042337 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-05-02 07:33 | 2023-05-02 21:50 | 51 | 14:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | S23050200051 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 857 | 2023-05-02 | 43707 | keep | 0 | May | 2023 | 0.029769 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2023-05-02 07:34 | 2023-05-02 12:50 | 20 | 5:16 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER NO SE REPORTO CAUSA | M23050200031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 316 | 2023-05-02 | 6320 | keep | 0 | May | 2023 | 0.0043045 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-02 07:35 | 2023-05-02 13:42 | 21 | 6:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO CABLE SOTERRADO | C23050200203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 367 | 2023-05-02 | 7707 | keep | 0 | May | 2023 | 0.0052492 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-05-02 07:36 | 2023-05-02 10:56 | 10 | 3:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23050200018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 200 | 2023-05-02 | 2000 | keep | 0 | May | 2023 | 0.0013622 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-02 07:38 | 2023-05-02 09:40 | 80 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO SE REPORTO CAUSA | B23050200019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2023-05-02 | 9760 | keep | 0 | May | 2023 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-05-02 07:42 | 2023-05-02 07:43 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23050200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
MAYAGÃœEZ | 2023-05-02 07:42 | 2023-05-02 07:43 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23050200037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 990 | keep | 0 | May | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
BARRANQUITAS | 2023-05-02 07:46 | 2023-05-02 13:40 | 30 | 5:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L DISCO PARTIDO SE REMPLAZO | C23050200017 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 354 | 2023-05-02 | 10620 | keep | 0 | May | 2023 | 0.0072332 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-02 07:48 | 2023-05-02 17:25 | 110 | 9:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA 1 X 50 EN RISER 1 X 30 EN PROVISIONAL 1 X 25 EN T-10 | S23050200035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 577 | 2023-05-02 | 63470 | keep | 0 | May | 2023 | 0.043229 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2023-05-02 07:48 | 2023-05-02 16:25 | 71 | 8:37 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 Y 1 X 50 EN CORTE DE LINEA, CONDUCTOR ABIERTO EN TRONCAL | S23050200011 | New_Event | Primary Wire Break | Include | Include | Equipment | 517 | 2023-05-02 | 36707 | keep | 0 | May | 2023 | 0.025001 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
FAJARDO | 2023-05-02 07:50 | 2023-05-02 07:51 | 1571 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23050200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 1571 | keep | 0 | May | 2023 | 0.00107 | 0.00107 | Momentary | FALSE | FALSE | Not_TMED_Event | 1571
PONCE | 2023-05-02 08:10 | 2023-05-02 10:30 | 114 | 2:20 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PALOMA CRUZO FASE | P23050200024 | New_Event | Animals | Include | Include | Wildlife | 140 | 2023-05-02 | 15960 | keep | 0 | May | 2023 | 0.01087 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
BAYAMON | 2023-05-02 08:16 | 2023-05-02 09:42 | 30 | 1:26 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23050200026 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-05-02 | 2580 | keep | 0 | May | 2023 | 0.0017572 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-02 08:17 | 2023-05-02 08:18 | 4085 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE | R23050200013 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-02 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-05-02 08:18 | 2023-05-02 13:25 | 2 | 5:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA CAJA DEFECTUOSA | R23050200015 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 307 | 2023-05-02 | 614 | keep | 0 | May | 2023 | 0.00041819 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-05-02 08:19 | 2023-05-02 12:22 | 3147 | 4:03 | S | ANIMAL | SE REPARO MACHETE QUEMADO DE BARRA DE INTERRUPTOR A CAUSA DE AVE 6704-03 | M23050200050 | New_Event | Animals | Include | Include | Wildlife | 243 | 2023-05-02 | 764721 | keep | 0 | May | 2023 | 0.52085 | 0.0021434 | Sustained | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2023-05-02 08:19 | 2023-05-02 12:22 | 4304 | 4:03 | S | ANIMAL | SE REPARO MACHETE QUEMADO DE BARRA DE INTERRUPTOR A CAUSA DE AVE 6704-03 | M23050200050 | New_Event | Animals | Include | Include | Wildlife | 243 | 2023-05-02 | 1045872 | keep | 0 | May | 2023 | 0.71234 | 0.0029314 | Sustained | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2023-05-02 08:42 | 2023-05-02 10:44 | 5 | 2:02 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA DESGANCHE | B23050200029 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 122 | 2023-05-02 | 610 | keep | 0 | May | 2023 | 0.00041547 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-02 08:48 | 2023-05-02 12:44 | 12 | 3:56 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | B23050200032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 236 | 2023-05-02 | 2832 | keep | 0 | May | 2023 | 0.0019289 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-02 08:50 | 2023-05-02 08:51 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2023-05-02 08:55 | 2023-05-02 14:00 | 1 | 5:05 | P | MAL TIEMPO/RAYOS | 3 X 15 EN MONTURA DE TRANSFORMADORES MAL TIEMPO DESCARGAS ELECTRICAS | A23050200027 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 305 | 2023-05-02 | 305 | keep | 0 | May | 2023 | 0.00020773 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-05-02 09:00 | 2023-05-02 17:15 | 175 | 8:15 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA REPARAR LINEA PRIMARIA ENERGIZADA EN EL SUELO AVERIA CAUSADA POR ARBOL SE REALIZO DESGANCHE MASIVO | A23050200162 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 495 | 2023-05-02 | 86625 | keep | 0 | May | 2023 | 0.059 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
SAN JUAN | 2023-05-02 09:21 | 2023-05-02 09:23 | 220 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 | S23050200026 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-02 | 440 | keep | 0 | May | 2023 | 0.00029968 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-05-02 09:21 | 2023-05-02 09:23 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR LLEVA 98% DEL 1303-04 | S23050200026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-02 | 1740 | keep | 0 | May | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CANOVANAS | 2023-05-02 09:22 | 2023-05-02 14:43 | 10 | 5:21 | P | NO SE REPORTO CAUSA | 1 X 15 EN RISER 1 X 80 EN C/L | R23050200024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 321 | 2023-05-02 | 3210 | keep | 0 | May | 2023 | 0.0021863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-02 09:24 | 2023-05-02 13:00 | 2 | 3:36 | P | ANIMAL | 1 X 80, 1 X 65 Y 3 X 10 EN CORTES DE LINEA Y BANCO DE TRANSFORMADOR CRUCE POR AVE | R23050200025 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-05-02 | 432 | keep | 0 | May | 2023 | 0.00029423 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-05-02 09:30 | 2023-05-02 11:30 | 10 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO RISER SECUNDARIO SE CERRO CAJAS DE TRANSFORMADOR | M23050200083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-05-02 | 1200 | keep | 0 | May | 2023 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-02 09:37 | 2023-05-02 11:01 | 100 | 1:24 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23050200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-05-02 | 8400 | keep | 0 | May | 2023 | 0.0057212 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-05-02 09:37 | 2023-05-02 13:00 | 35 | 3:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN CORTE DE LINEA | P23050200037 | New_Event | Cutout Failure | Include | Include | Equipment | 203 | 2023-05-02 | 7105 | keep | 0 | May | 2023 | 0.0048392 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-05-02 09:55 | 2023-05-02 10:35 | 6 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA AJUSTAR VOLTAJE SECUNDARIO Y SE REMPLAZO BAJANTES SECUNDARIOS EN MALAS CONDICIONES | M23050200099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-05-02 | 240 | keep | 0 | May | 2023 | 0.00016346 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-05-02 10:04 | 2023-05-02 12:50 | 1 | 2:46 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO SE REPORTO CAUSA | M23050200111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 166 | 2023-05-02 | 166 | keep | 0 | May | 2023 | 0.00011306 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-02 10:15 | 2023-05-02 12:25 | 1 | 2:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 DESGANCHE SE DESCONTAMINARON CAJAS SULFATADAS | R23050200036 | New_Event | Cutout Failure | Include | Include | Equipment | 130 | 2023-05-02 | 130 | keep | 0 | May | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-02 10:17 | 2023-05-02 14:40 | 60 | 4:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A23050200046 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2023-05-02 | 15780 | keep | 0 | May | 2023 | 0.010748 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-02 10:26 | 2023-05-02 12:54 | 1 | 2:28 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23050200043 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-05-02 | 148 | keep | 0 | May | 2023 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-02 10:28 | 2023-05-02 19:12 | 8 | 8:44 | P | ANIMAL | 1 X 15 EN XMR LAGARTIJO CRUZO CAJA PRIMARIA | B23050200044 | New_Event | Animals | Include | Include | Wildlife | 524 | 2023-05-02 | 4192 | keep | 0 | May | 2023 | 0.0028552 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-02 10:29 | 2023-05-02 12:11 | 1648 | 1:42 | T | ALIMENTADOR AMARRADO | DISPARO 2302-03 LLEVA 2402-02 SJ-230502-50 SE SECCIONALIZO TRAMOS PARA REMPLAZO CE AISLADOR ROTO 10% EN SERVICIO DEL 2302-03 | R23050200039 | New_Event | Feeder Load Transferred | Include | Include | Other | 102 | 2023-05-02 | 168096 | keep | 0 | May | 2023 | 0.11449 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-05-02 10:29 | 2023-05-02 14:44 | 1675 | 4:15 | P | AISLADOR ROTO, PARTIDO O SAFADO | SJ-230502-50 SE REMPLAZO AISLADOR ROTO 40% X 2302-03 | R23050200039 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 255 | 2023-05-02 | 427125 | keep | 0 | May | 2023 | 0.29091 | 0.0011408 | Sustained | FALSE | FALSE | Not_TMED_Event | 1675
PONCE | 2023-05-02 10:39 | 2023-05-02 10:40 | 3114 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050200049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 3114 | keep | 0 | May | 2023 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
SAN JUAN | 2023-05-02 10:40 | 2023-05-02 10:43 | 661 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 16% POR 1620-02 | S23050200045 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-02 | 1983 | keep | 0 | May | 2023 | 0.0013506 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-05-02 10:40 | 2023-05-02 10:43 | 3718 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 16% DEL 1206-03 | S23050200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-02 | 11154 | keep | 0 | May | 2023 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
ARECIBO | 2023-05-02 10:41 | 2023-05-02 10:42 | 2201 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23050200054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 2201 | keep | 0 | May | 2023 | 0.0014991 | 0.0014991 | Momentary | FALSE | FALSE | Not_TMED_Event | 2201
VEGA BAJA | 2023-05-02 10:46 | 2023-05-02 16:20 | 8 | 5:34 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO LINEAS | A23050200055 | New_Event | Animals | Include | Include | Wildlife | 334 | 2023-05-02 | 2672 | keep | 0 | May | 2023 | 0.0018199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-02 10:47 | 2023-05-02 16:52 | 12 | 6:05 | P | ANIMAL | 1 X 20 EN SMU 20 CRUCE X AVE | R23050200042 | New_Event | Animals | Include | Include | Wildlife | 365 | 2023-05-02 | 4380 | keep | 0 | May | 2023 | 0.0029832 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-02 10:56 | 2023-05-02 17:43 | 12 | 6:47 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE REEMPLAZO BAJANTE EN XMR Y SE REEMPLAZO PARARRAYO | C23050200077 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 407 | 2023-05-02 | 4884 | keep | 0 | May | 2023 | 0.0033265 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-02 11:03 | 2023-05-02 12:36 | 30 | 1:33 | P | ANIMAL | 1 X 20 EN C/L CRUCE POR AVE | R23050200080 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-05-02 | 2790 | keep | 0 | May | 2023 | 0.0019003 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-02 12:03 | 2023-05-02 14:20 | 4 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE IDENTIFICO CAUSA | M23050200149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2023-05-02 | 548 | keep | 0 | May | 2023 | 0.00037324 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-05-02 12:11 | 2023-05-02 12:26 | 1483 | 0:15 | P | ALIMENTADOR AMARRADO | LLEVA 2402-02 SJ-230502-50 SE SECCIONALIZO TRAMOS PARA REMPLAZO DE AISLADOR ROTO 100% EN SERVICIO DEL 2302-03 | R23050200039 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 15 | 2023-05-02 | 22245 | keep | 0 | May | 2023 | 0.015151 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-02 12:13 | 2023-05-02 17:27 | 1 | 5:14 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B23050200080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 314 | 2023-05-02 | 314 | keep | 0 | May | 2023 | 0.00021386 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-02 12:19 | 2023-05-02 16:10 | 2 | 3:51 | P | DESCONECTIVO DEFECTUOSO | SJ-230429-50 REEMPLAZO DE DESCONECTIVOS DEL LOS 2403-01 Y 2403-02 | R23050200126 | New_Event | Switch Failure | Include | Include | Equipment | 231 | 2023-05-02 | 462 | keep | 0 | May | 2023 | 0.00031467 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-05-02 12:21 | 2023-05-02 14:36 | 8 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR REEMPLAZARON BAJANTES EN XMR Y CONECTORES EN SECUNDARIA | C23050200042 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2023-05-02 | 1080 | keep | 0 | May | 2023 | 0.00073558 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-05-02 12:22 | 2023-05-02 17:45 | 80 | 5:23 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050200156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-05-02 | 25840 | keep | 0 | May | 2023 | 0.0176 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-05-02 12:26 | 2023-05-02 14:00 | 4 | 1:34 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO AISLADORES ROTOS | M23050200157 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 94 | 2023-05-02 | 376 | keep | 0 | May | 2023 | 0.00025609 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-05-02 12:33 | 2023-05-02 15:15 | 20 | 2:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | M23050200159 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 162 | 2023-05-02 | 3240 | keep | 0 | May | 2023 | 0.0022067 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-02 12:36 | 2023-05-02 13:12 | 10 | 0:36 | P | SECUNDARIA/OTROS | SE REMPLAZO PEDESTAL | R23050200060 | New_Event |  |  |  |  | 36 | 2023-05-02 | 360 | keep | 0 | May | 2023 | 0.00024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-02 12:40 | 2023-05-02 14:38 | 50 | 1:58 | P | DESGANCHE | 2 X 80 EN C/L Y DESGANCHE | R23050200071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-05-02 | 5900 | keep | 0 | May | 2023 | 0.0040185 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-02 12:40 | 2023-05-02 13:28 | 5 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA SOBRE TRANSFORMADOR | M23050200161 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2023-05-02 | 240 | keep | 0 | May | 2023 | 0.00016346 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-02 12:59 | 2023-05-02 13:13 | 2 | 0:14 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23050200086 | New_Event | Animals | Include | Include | Wildlife | 14 | 2023-05-02 | 28 | keep | 0 | May | 2023 | 1.9071e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-05-02 13:09 | 2023-05-02 14:05 | 100 | 0:56 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050200166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-05-02 | 5600 | keep | 0 | May | 2023 | 0.0038141 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-02 13:26 | 2023-05-02 15:35 | 6 | 2:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE | R23050200084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 129 | 2023-05-02 | 774 | keep | 0 | May | 2023 | 0.00052717 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-05-02 13:29 | 2023-05-02 13:31 | 1475 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR | P23050200092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-02 | 2950 | keep | 0 | May | 2023 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
SAN JUAN | 2023-05-02 13:30 | 2023-05-03 18:15 | 35 | 28:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO Y SE TRANSFIRIERON LINIEAS | S23050200183 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1725 | 2023-05-02 | 60375 | keep | 0 | May | 2023 | 0.041121 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-05-02 13:38 | 2023-05-02 15:54 | 6 | 2:16 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN BANCO DE XMR PROBLEMA DEL CLIENTE | C23050200113 | New_Event | Customer-Related Interruption | Include | Include | Public | 136 | 2023-05-02 | 816 | keep | 0 | May | 2023 | 0.00055577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-02 13:38 | 2023-05-02 14:00 | 1 | 0:22 | P | ERROR HUMANO | SE CERRO FUSIBLE ABIERTO POR PERSONAL DE CAMPO QUE OLVIDO CERRARLO | C23050200112 | New_Event | Human Error | Include | Include | Other | 22 | 2023-05-02 | 22 | keep | 0 | May | 2023 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-02 13:40 | 2023-05-02 15:05 | 60 | 1:25 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO AISLADOR | C23050200114 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 85 | 2023-05-02 | 5100 | keep | 0 | May | 2023 | 0.0034736 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-02 13:51 | 2023-05-02 13:53 | 1381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23050200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-02 | 2762 | keep | 0 | May | 2023 | 0.0018812 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
GUAYAMA | 2023-05-02 13:52 | 2023-05-02 17:21 | 50 | 3:29 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23050200097 | New_Event | Animals | Include | Include | Wildlife | 209 | 2023-05-02 | 10450 | keep | 0 | May | 2023 | 0.0071174 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-02 14:33 | 2023-05-02 14:36 | 590 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23050200104 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-02 | 1770 | keep | 0 | May | 2023 | 0.0012055 | 0.00040185 | Momentary | FALSE | FALSE | Not_TMED_Event | 590
CANOVANAS | 2023-05-02 14:37 | 2023-05-02 19:15 | 7 | 4:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y SECUANDARIA | R23050200099 | New_Event | Cutout Failure | Include | Include | Equipment | 278 | 2023-05-02 | 1946 | keep | 0 | May | 2023 | 0.0013254 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-05-02 14:45 | 2023-05-02 14:46 | 4641 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | M23050200188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-02 | 4641 | keep | 0 | May | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
YAUCO | 2023-05-02 14:46 | 2023-05-02 17:21 | 10 | 2:35 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23050200107 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-05-02 | 1550 | keep | 0 | May | 2023 | 0.0010557 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-02 14:46 | 2023-05-02 16:06 | 20 | 1:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23050200190 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 80 | 2023-05-02 | 1600 | keep | 0 | May | 2023 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-02 15:01 | 2023-05-02 15:55 | 8 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BARRA EN PEDESTAL | B23050200011 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-05-02 | 432 | keep | 0 | May | 2023 | 0.00029423 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-05-02 15:10 | 2023-05-02 18:27 | 30 | 3:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23050200131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2023-05-02 | 5910 | keep | 0 | May | 2023 | 0.0040253 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-02 15:25 | 2023-05-02 16:20 | 50 | 0:55 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | M23050200192 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2023-05-02 | 2750 | keep | 0 | May | 2023 | 0.001873 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-02 15:30 | 2023-05-02 20:50 | 100 | 5:20 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA SE REPARO PUENTES PRIMARIOS | M23050200206 | New_Event | Primary Wire Break | Include | Include | Equipment | 320 | 2023-05-02 | 32000 | keep | 0 | May | 2023 | 0.021795 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-05-02 15:38 | 2023-05-02 16:11 | 1 | 0:33 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN RISER PARARRAYO DEFECTUOSO | B23050200118 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 33 | 2023-05-02 | 33 | keep | 0 | May | 2023 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-02 15:41 | 2023-05-03 03:49 | 53 | 12:08 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | S23050200119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 728 | 2023-05-02 | 38584 | keep | 0 | May | 2023 | 0.026279 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
MAYAGÃœEZ | 2023-05-02 15:41 | 2023-05-02 15:42 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23050200199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 2999 | keep | 0 | May | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2023-05-02 15:45 | 2023-05-02 15:46 | 1444 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M23050200202 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 1444 | keep | 0 | May | 2023 | 0.0009835 | 0.0009835 | Momentary | FALSE | FALSE | Not_TMED_Event | 1444
CANOVANAS | 2023-05-02 15:50 | 2023-05-02 18:00 | 1 | 2:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA 1 X 15 EN XMR | R23050200110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 130 | 2023-05-02 | 130 | keep | 0 | May | 2023 | 8.8542e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-02 15:50 | 2023-05-02 18:15 | 50 | 2:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23050200099 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 145 | 2023-05-02 | 7250 | keep | 0 | May | 2023 | 0.0049379 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-02 16:07 | 2023-05-02 16:08 | 450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 450 | keep | 0 | May | 2023 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2023-05-02 16:13 | 2023-05-02 17:14 | 1 | 1:01 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | S23050200141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-05-02 | 61 | keep | 0 | May | 2023 | 4.1547e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-02 16:15 | 2023-05-02 20:19 | 60 | 4:04 | P | CAUSAS EXTERNAS | 2 X 50 EN C/L SE ENDEREZO POSTE IMPACTADO POR CAMION | B23050200124 | New_Event | Damage From Public | Include | Include | Public | 244 | 2023-05-02 | 14640 | keep | 0 | May | 2023 | 0.0099712 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-05-02 16:20 | 2023-05-02 17:55 | 200 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE TERMINO DE ABRIR CORTE DE LINEA PARA REPARAR ALAMBRE PARTIDO | M23050200192 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 95 | 2023-05-02 | 19000 | keep | 0 | May | 2023 | 0.012941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-02 16:25 | 2023-05-02 16:28 | 1420 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA SECCIONALIZAR Y ESTABLECER GOI PARA CERRAR PUENTE PRIMARIO EN TRONCAL Y SE CERRO INTERRUPTOR 1% EN SERVICIO QUEDA FUERA 99% DEL 1526-2 Y LA CARGA DEL 1530-6 | S23050200150 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-05-02 | 4260 | keep | 0 | May | 2023 | 0.0029015 | 0.00096716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-05-02 16:25 | 2023-05-02 17:37 | 437 | 1:12 | T | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR PARA CERRAR MACHETE Y RESTABLECER SERVICIO 1526-2 Y 1530-6 100% EN SERVICIO SE REPARO PUENTE PRIMARIO EN TRONCAL DEL 1526-02. | S23050200166 | New_Event | Feeder Load Transferred | Include | Include | Other | 72 | 2023-05-02 | 31464 | keep | 0 | May | 2023 | 0.02143 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
ARECIBO | 2023-05-02 16:27 | 2023-05-02 17:30 | 30 | 1:03 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23050200105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 63 | 2023-05-02 | 1890 | keep | 0 | May | 2023 | 0.0012873 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-02 16:28 | 2023-05-02 17:36 | 1406 | 1:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE ABRE INTERRUPTOR PARA CERRAR MACHETE TRONCAL ALIMENTADOR | S23050200150 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 68 | 2023-05-02 | 95608 | keep | 0 | May | 2023 | 0.065118 | 0.00095762 | Sustained | FALSE | FALSE | Not_TMED_Event | 1406
MAYAGÃœEZ | 2023-05-02 16:35 | 2023-05-02 18:10 | 15 | 1:35 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23050200224 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 95 | 2023-05-02 | 1425 | keep | 0 | May | 2023 | 0.00097056 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-02 16:47 | 2023-05-02 18:11 | 10 | 1:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | R23050200118 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 84 | 2023-05-02 | 840 | keep | 0 | May | 2023 | 0.00057212 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-02 17:07 | 2023-05-02 17:08 | 478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 478 | keep | 0 | May | 2023 | 0.00032556 | 0.00032556 | Momentary | FALSE | FALSE | Not_TMED_Event | 478
BAYAMON | 2023-05-02 17:07 | 2023-05-02 17:16 | 5663 | 0:09 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 1717-02 LLEVA 95% 1703-05 PUENTE ABIERTO TRAMO HATO TEJAS - CREA. | B23050200201 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-02 | 50967 | keep | 0 | May | 2023 | 0.034713 | 0.003857 | Sustained | FALSE | FALSE | Not_TMED_Event | 5663
BAYAMON | 2023-05-02 17:07 | 2023-05-02 17:16 | 4080 | 0:09 | P | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 1717-01 TIENE 10% POR 1801-02 1717-02 LLEVA 95% 1713-05 PUENTE ABIERTO TRAMO HATO TEJAS - CREA. | B23050200201 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-02 | 36720 | keep | 0 | May | 2023 | 0.02501 | 0.0027789 | Sustained | FALSE | FALSE | Not_TMED_Event | 4080
BAYAMON | 2023-05-02 17:07 | 2023-05-02 17:16 | 911 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 1717-01 TIENE 10% POR 1801-02 1717-02 LLEVA 95% 1713-05 PUENTE ABIERTO TRAMO HATO TEJAS - CREA. | B23050200201 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-02 | 8199 | keep | 0 | May | 2023 | 0.0055843 | 0.00062048 | Sustained | FALSE | FALSE | Not_TMED_Event | 911
BAYAMON | 2023-05-02 17:07 | 2023-05-02 17:16 | 4431 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 1717-01 TIENE 10% POR 1801-02 1717-02 LLEVA 95% 1713-05 PUENTE ABIERTO TRAMO HATO TEJAS - CREA. | B23050200201 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-02 | 39879 | keep | 0 | May | 2023 | 0.027161 | 0.0030179 | Sustained | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-05-02 17:07 | 2023-05-02 17:16 | 1362 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 1717-01 TIENE 10% POR 1801-02 1717-02 LLEVA 95% 1713-05 PUENTE ABIERTO TRAMO HATO TEJAS - CREA. | B23050200201 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-02 | 12258 | keep | 0 | May | 2023 | 0.0083489 | 0.00092765 | Sustained | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2023-05-02 17:07 | 2023-05-02 17:16 | 341 | 0:09 | S | LINEA DE TRANSMISION 115KV | DISPARO LINEA 37400 1717-01 TIENE 10% POR 1801-02 1717-02 LLEVA 95% 1713-05 PUENTE ABIERTO TRAMO HATO TEJAS - CREA. | B23050200201 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-02 | 3069 | keep | 0 | May | 2023 | 0.0020903 | 0.00023225 | Sustained | FALSE | FALSE | Not_TMED_Event | 341
BAYAMON | 2023-05-02 17:08 | 2023-05-02 17:09 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-05-02 17:14 | 2023-05-02 17:17 | 4028 | 0:03 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRIO INTERRUPTOR A PETICION CCE POR SOBRECARGA EN LINEA 36100 A CONSECUENCIA DE DISPARO LINEA 37400 | B2305020000X | New_Event |  |  |  |  | 3 | 2023-05-02 | 12084 | keep | 0 | May | 2023 | 0.0082304 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BAYAMON | 2023-05-02 17:14 | 2023-05-02 17:17 | 2617 | 0:03 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRIO INTERRUPTOR A PETICION CCE POR SOBRECARGA EN LINEA 36100 A CONSECUENCIA DE DISPARO LINEA 37400 | B2305020000X | New_Event |  |  |  |  | 3 | 2023-05-02 | 7851 | keep | 0 | May | 2023 | 0.0053473 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2023-05-02 17:14 | 2023-05-02 17:17 | 3511 | 0:03 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRIO INTERRUPTOR A PETICION CCE POR SOBRECARGA EN LINEA 36100 A CONSECUENCIA DE DISPARO LINEA 37400 | B23050200217 | New_Event |  |  |  |  | 3 | 2023-05-02 | 10533 | keep | 0 | May | 2023 | 0.007174 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-05-02 17:15 | 2023-05-02 17:17 | 5191 | 0:02 | T | RELEVO DE CARGA CONTINGENCIA - TRANSMISION | SE ABRIO INTERRUPTOR A PETICION CCE POR SOBRECARGA EN LINEA 36100 A CONSECUENCIA DE DISPARO LINEA 37400 | B2305020000X | New_Event |  |  |  |  | 2 | 2023-05-02 | 10382 | keep | 0 | May | 2023 | 0.0070711 | 0.0035356 | Momentary | FALSE | FALSE | Not_TMED_Event | 5191
SAN JUAN | 2023-05-02 17:32 | 2023-05-02 17:34 | 1381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23050200000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-02 | 2762 | keep | 0 | May | 2023 | 0.0018812 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
SAN JUAN | 2023-05-02 17:36 | 2023-05-02 17:37 | 1420 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA CERRAR MACHETE Y RESTABLECER SERVICIO 95% 1526-2 Y 1530-6 100% EN SERVICIO | S23050200166 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-02 | 1420 | keep | 0 | May | 2023 | 0.00096716 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-02 17:37 | 2023-05-02 21:32 | 51 | 3:55 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 Y 1 X 50 EN CORTE DE LINEACONDUCTOR ABIERTO EN TRONCAL | S23050200011 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 235 | 2023-05-02 | 11985 | keep | 0 | May | 2023 | 0.0081629 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
PONCE | 2023-05-02 17:54 | 2023-05-02 19:30 | 15 | 1:36 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23050200125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 96 | 2023-05-02 | 1440 | keep | 0 | May | 2023 | 0.00098078 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-02 18:14 | 2023-05-03 12:41 | 8 | 18:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE SECUNDARIO | A23050200121 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1107 | 2023-05-02 | 8856 | keep | 0 | May | 2023 | 0.0060318 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-02 18:15 | 2023-05-02 19:00 | 10 | 0:45 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO FASE | S23050200175 | New_Event | Animals | Include | Include | Wildlife | 45 | 2023-05-02 | 450 | keep | 0 | May | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-02 18:15 | 2023-05-02 19:30 | 1 | 1:15 | P | DESGANCHE | 1 X 15 EN C/L DESGANCHE | C23050200160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-05-02 | 75 | keep | 0 | May | 2023 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-02 18:44 | 2023-05-02 22:55 | 150 | 4:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23050200261 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 251 | 2023-05-02 | 37650 | keep | 0 | May | 2023 | 0.025643 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-02 18:49 | 2023-05-02 22:02 | 35 | 3:13 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE LEVANTO CONDUCTOR | S23050200183 | New_Event | Primary Wire Break | Include | Include | Equipment | 193 | 2023-05-02 | 6755 | keep | 0 | May | 2023 | 0.0046008 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2023-05-02 18:50 | 2023-05-02 20:36 | 653 | 1:46 | T | DESGANCHE | SE REALISO DESGANCHE | P23050200137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-02 | 69218 | keep | 0 | May | 2023 | 0.047144 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
PONCE | 2023-05-02 18:55 | 2023-05-02 21:40 | 100 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 Y 1 X 65 EN DIFERENTES C/L MAL TIEMPO LLUVIAS | P23050200138 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-05-02 | 16500 | keep | 0 | May | 2023 | 0.011238 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-05-02 19:16 | 2023-05-03 09:29 | 20 | 14:13 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | R23050200128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 853 | 2023-05-02 | 17060 | keep | 0 | May | 2023 | 0.011619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-02 19:21 | 2023-05-02 21:45 | 647 | 2:24 | P | CONDUCTOR ROTO O ABIERTO | SE AMARRO 7006-01 Y 7006-03 POR PUENTE ABIERTO EN SALIDA DEL 7006-01 | M23050200272 | New_Event | Primary Wire Break | Include | Include | Equipment | 144 | 2023-05-02 | 93168 | keep | 0 | May | 2023 | 0.063456 | 0.00044067 | Sustained | FALSE | FALSE | Not_TMED_Event | 647
BARRANQUITAS | 2023-05-02 19:26 | 2023-05-02 20:20 | 4 | 0:54 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23050200169 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 54 | 2023-05-02 | 216 | keep | 0 | May | 2023 | 0.00014712 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-05-02 19:32 | 2023-05-03 09:45 | 202 | 14:13 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA RAMA SOBRE LINEA | P23050200150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 853 | 2023-05-02 | 172306 | keep | 0 | May | 2023 | 0.11736 | 0.00013758 | Sustained | FALSE | FALSE | Not_TMED_Event | 202
CANOVANAS | 2023-05-02 19:37 | 2023-05-02 20:06 | 7 | 0:29 | P | CAUSAS EXTERNAS | SE ABRIO XMR SE RETIRO GUY VACANTE CRUZADO | R23050200130 | New_Event | Damage From Public | Include | Include | Public | 29 | 2023-05-02 | 203 | keep | 0 | May | 2023 | 0.00013826 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-02 19:47 | 2023-05-02 23:39 | 362 | 3:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23050200278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-05-02 | 83984 | keep | 0 | May | 2023 | 0.057201 | 0.00024656 | Sustained | FALSE | FALSE | Not_TMED_Event | 362
YAUCO | 2023-05-02 19:56 | 2023-05-02 23:07 | 2 | 3:11 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23050200329 | New_Event | Primary Wire Break | Include | Include | Equipment | 191 | 2023-05-02 | 382 | keep | 0 | May | 2023 | 0.00026018 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-05-02 19:56 | 2023-05-03 09:28 | 25 | 13:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA RAMA SOBRE LINEA | A23050200131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 812 | 2023-05-02 | 20300 | keep | 0 | May | 2023 | 0.013826 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-02 20:18 | 2023-05-03 15:15 | 26 | 18:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | DESGANCHE DE ENREDADERA Y SE CERRO PUENTE SECUNDARIO DE LINEA A CAJA | S23050200220 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1137 | 2023-05-02 | 29562 | keep | 0 | May | 2023 | 0.020135 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
AGUADILLA | 2023-05-02 20:53 | 2023-05-02 23:05 | 100 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA | M23050200404 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2023-05-02 | 13200 | keep | 0 | May | 2023 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-02 20:57 | 2023-05-02 20:58 | 4188 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 40% POR 2302-03 | R2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 4188 | keep | 0 | May | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2023-05-02 21:00 | 2023-05-03 08:48 | 40 | 11:48 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | R23050200140 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 708 | 2023-05-02 | 28320 | keep | 0 | May | 2023 | 0.019289 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-02 21:19 | 2023-05-03 05:50 | 15 | 8:31 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | S23050200239 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 511 | 2023-05-02 | 7665 | keep | 0 | May | 2023 | 0.0052206 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-02 21:29 | 2023-05-02 21:31 | 817 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23050200184 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-02 | 1634 | keep | 0 | May | 2023 | 0.0011129 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
HUMACAO | 2023-05-02 21:31 | 2023-05-03 07:47 | 3 | 10:16 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE DEXCRUZO LINEA SECUNDARIA | C23050200185 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 616 | 2023-05-02 | 1848 | keep | 0 | May | 2023 | 0.0012587 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-05-02 21:31 | 2023-05-03 01:32 | 272 | 4:01 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN EL RISER DE SALIDA DEL ALIMENTADOR SE TRANSFIRIO LA CARGA AL 3006-03 | C23050200203 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 241 | 2023-05-02 | 65552 | keep | 0 | May | 2023 | 0.044647 | 0.00018526 | Sustained | FALSE | FALSE | Not_TMED_Event | 272
BAYAMON | 2023-05-02 21:34 | 2023-05-03 05:51 | 17 | 8:17 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23050200247 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2023-05-02 | 8449 | keep | 0 | May | 2023 | 0.0057546 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
SAN JUAN | 2023-05-02 22:00 | 2023-05-03 00:39 | 177 | 2:39 | P | ANIMAL | X 65 EN C/L CRUCE POR AVE | 23050200257 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-05-02 | 28143 | keep | 0 | May | 2023 | 0.019168 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
PONCE | 2023-05-02 22:07 | 2023-05-02 22:08 | 396 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050200186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 396 | keep | 0 | May | 2023 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
VEGA BAJA | 2023-05-02 22:10 | 2023-05-03 00:09 | 504 | 1:59 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23050200304 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-05-02 | 59976 | keep | 0 | May | 2023 | 0.040849 | 0.00034327 | Sustained | FALSE | FALSE | Not_TMED_Event | 504
BAYAMON | 2023-05-02 22:18 | 2023-05-03 01:29 | 300 | 3:11 | P | DESGANCHE | 1 X 80 EN C/L | B23050200311 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-05-02 | 57300 | keep | 0 | May | 2023 | 0.039027 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2023-05-02 22:20 | 2023-05-03 01:19 | 80 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23050200313 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-05-02 | 14320 | keep | 0 | May | 2023 | 0.0097533 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-05-02 22:22 | 2023-05-03 07:18 | 243 | 8:56 | P | DESGANCHE | SE HIZO DESGANCHE DE ARBOL SE LEVANTO CONDUCTOR PRIMARIO 2 X 100 EN CORTE DE LINEA | P23050200188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 536 | 2023-05-02 | 130248 | keep | 0 | May | 2023 | 0.088711 | 0.00016551 | Sustained | FALSE | FALSE | Not_TMED_Event | 243
CAGUAS | 2023-05-02 22:26 | 2023-05-03 10:42 | 100 | 12:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23050200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 736 | 2023-05-02 | 73600 | keep | 0 | May | 2023 | 0.050129 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-02 23:11 | 2023-05-03 02:35 | 53 | 3:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 65 EN C/L | S23050200265 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2023-05-02 | 10812 | keep | 0 | May | 2023 | 0.007364 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2023-05-02 23:21 | 2023-05-02 23:22 | 761 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1421-01 | S2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 761 | keep | 0 | May | 2023 | 0.00051831 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2023-05-02 23:21 | 2023-05-02 23:22 | 1498 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1310-04 | S2305020000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-02 | 1498 | keep | 0 | May | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
CANOVANAS | 2023-05-02 23:28 | 2023-05-03 09:47 | 25 | 10:19 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | R23050200148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 619 | 2023-05-02 | 15475 | keep | 0 | May | 2023 | 0.01054 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-05-02 23:29 | 2023-05-02 23:30 | 776 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRIPTOR | B2305020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-02 | 776 | keep | 0 | May | 2023 | 0.00052853 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
ARECIBO | 2023-05-03 00:22 | 2023-05-03 01:06 | 2201 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 DISCO ZAFADO ENTRE 6929C - 6907C | A23050300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-03 | 96844 | keep | 0 | May | 2023 | 0.06596 | 0.0014991 | Sustained | FALSE | FALSE | Not_TMED_Event | 2201
ARECIBO | 2023-05-03 00:22 | 2023-05-03 01:06 | 1986 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 DISCO ZAFADO ENTRE 6929C - 6907C | A23050300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-03 | 87384 | keep | 0 | May | 2023 | 0.059517 | 0.0013527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1986
ARECIBO | 2023-05-03 00:22 | 2023-05-03 01:06 | 199 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 DISCO ZAFADO ENTRE 6929C - 6907C | A23050300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-03 | 8756 | keep | 0 | May | 2023 | 0.0059637 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
ARECIBO | 2023-05-03 00:22 | 2023-05-03 01:06 | 24 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 6900 DISCO ZAFADO ENTRE 6929C - 6907C | A23050300014 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-03 | 1056 | keep | 0 | May | 2023 | 0.00071924 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-05-03 01:39 | 2023-05-03 04:14 | 215 | 2:35 | P | OTRAS CAUSAS | 1 X 50 EN C/L TENIA FUSIBLE DE 25 EN LUGAR DE 50 | B23050300003 | New_Event | Other Causes | Include | Include | Other | 155 | 2023-05-03 | 33325 | keep | 0 | May | 2023 | 0.022698 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
BAYAMON | 2023-05-03 02:48 | 2023-05-03 07:39 | 72 | 4:51 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR A PETICION DE JUAN CARRASQUILLO POR MACHETE QUEMADO EN LA SALIDA DEL RISER LLEVA 70% 1924-04 | S23050300012 | New_Event | Switch Failure | Include | Include | Equipment | 291 | 2023-05-03 | 20952 | keep | 0 | May | 2023 | 0.01427 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2023-05-03 02:48 | 2023-05-03 07:39 | 11 | 4:51 | P | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR A PETICION DE PERSONAL EN EL CAMPO POR MACHETE QUEMADO EN LA SALIDA DE RISER DEL 1903-03 | S23050300012 | New_Event | Feeder Load Transferred | Include | Include | Other | 291 | 2023-05-03 | 3201 | keep | 0 | May | 2023 | 0.0021802 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-05-03 03:18 | 2023-05-03 04:12 | 1368 | 0:54 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA SE PATRULLO NO SE ENCONTRO NADA SE BORRARON BANDERAS | S23050300013 | New_Event | Primary Wire Break | Include | Include | Equipment | 54 | 2023-05-03 | 73872 | keep | 0 | May | 2023 | 0.050314 | 0.00093174 | Sustained | FALSE | FALSE | Not_TMED_Event | 1368
BARRANQUITAS | 2023-05-03 03:55 | 2023-05-03 11:02 | 75 | 7:07 | P | NO SE REPORTO CAUSA | 1 X 10 Y 1 X 50 EN TRANSFORMADOR Y CORTE DE LINEA | C23050300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 427 | 2023-05-03 | 32025 | keep | 0 | May | 2023 | 0.021812 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-05-03 04:12 | 2023-05-03 12:41 | 205 | 8:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE EN RISER Y SE REEMPLAZO AISLADOR | S23050300023 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 509 | 2023-05-03 | 104345 | keep | 0 | May | 2023 | 0.071069 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-03 04:30 | 2023-05-03 04:31 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050300006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2023-05-03 04:31 | 2023-05-03 09:54 | 129 | 5:23 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C23050300008 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 323 | 2023-05-03 | 41667 | keep | 0 | May | 2023 | 0.028379 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
MAYAGÃœEZ | 2023-05-03 04:38 | 2023-05-03 18:20 | 1 | 13:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR LLUVIA Y FUERTES VIENTOS | M23050300175 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 822 | 2023-05-03 | 822 | keep | 0 | May | 2023 | 0.00055986 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-03 04:44 | 2023-05-03 04:46 | 1 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERO POR SCADA | S23050300018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-03 | 2 | keep | 0 | May | 2023 | 1.3622e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-03 05:38 | 2023-05-03 10:10 | 40 | 4:32 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23050300039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 272 | 2023-05-03 | 10880 | keep | 0 | May | 2023 | 0.0074103 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-03 05:55 | 2023-05-03 05:56 | 77 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 77 | keep | 0 | May | 2023 | 5.2444e-05 | 5.2444e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 77
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 2571 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE L-4800 | P23050300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 2571 | keep | 0 | May | 2023 | 0.0017511 | 0.0017511 | Momentary | FALSE | FALSE | Not_TMED_Event | 2571
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 2235 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE L-4800 | P23050300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 2235 | keep | 0 | May | 2023 | 0.0015222 | 0.0015222 | Momentary | FALSE | FALSE | Not_TMED_Event | 2235
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 713 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE L-4800 | P23050300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 713 | keep | 0 | May | 2023 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 1067 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE L-4800 | P23050300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 1067 | keep | 0 | May | 2023 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 1293 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23050300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 1293 | keep | 0 | May | 2023 | 0.00088066 | 0.00088066 | Momentary | FALSE | FALSE | Not_TMED_Event | 1293
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 426 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23050300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 426 | keep | 0 | May | 2023 | 0.00029015 | 0.00029015 | Momentary | FALSE | FALSE | Not_TMED_Event | 426
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 907 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23050300028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 907 | keep | 0 | May | 2023 | 0.00061775 | 0.00061775 | Momentary | FALSE | FALSE | Not_TMED_Event | 907
GUAYAMA | 2023-05-03 05:57 | 2023-05-03 05:58 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050300027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BAYAMON | 2023-05-03 05:57 | 2023-05-03 05:58 | 1859 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | B2305030000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-03 | 1859 | keep | 0 | May | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
BAYAMON | 2023-05-03 05:58 | 2023-05-03 13:01 | 1169 | 7:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L SE REEMPLAZARON DOS CAJAS PRIMARIAS | B23050300017 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 423 | 2023-05-03 | 494487 | keep | 0 | May | 2023 | 0.33679 | 0.0007962 | Sustained | FALSE | FALSE | Not_TMED_Event | 1169
SAN JUAN | 2023-05-03 06:03 | 2023-05-03 06:05 | 362 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 90% POR 1620-01 | S23050300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-03 | 724 | keep | 0 | May | 2023 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-05-03 06:03 | 2023-05-03 06:05 | 36 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 90% 1336-10 Y 60% DEL 1620-02 | S23050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-03 | 72 | keep | 0 | May | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-03 06:03 | 2023-05-03 06:05 | 2226 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 60% POR 1620-01 | S23050300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-03 | 4452 | keep | 0 | May | 2023 | 0.0030322 | 0.0015161 | Momentary | FALSE | FALSE | Not_TMED_Event | 2226
YAUCO | 2023-05-03 06:10 | 2023-05-03 08:18 | 120 | 2:08 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO | M23050300021 | New_Event | Primary Wire Break | Include | Include | Equipment | 128 | 2023-05-03 | 15360 | keep | 0 | May | 2023 | 0.010462 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-05-03 06:17 | 2023-05-03 06:18 | 2179 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | R23050300005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 2179 | keep | 0 | May | 2023 | 0.0014841 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
MAYAGÃœEZ | 2023-05-03 06:24 | 2023-05-03 08:45 | 25 | 2:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23050300024 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-05-03 | 3525 | keep | 0 | May | 2023 | 0.0024009 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-03 06:30 | 2023-05-03 08:50 | 40 | 2:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23050300026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 140 | 2023-05-03 | 5600 | keep | 0 | May | 2023 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-03 06:44 | 2023-05-03 06:45 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 20% POR 1118-10 | S23050300000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-03 | 513 | keep | 0 | May | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-05-03 06:44 | 2023-05-03 06:45 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 20% DEL 1111-01 | S23050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 2782 | keep | 0 | May | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
GUAYAMA | 2023-05-03 06:45 | 2023-05-03 09:10 | 5 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN CAJA PRIMARIA 1 X 50 EN CORTE DE LINEA | P23050300030 | New_Event | Primary Wire Break | Include | Include | Equipment | 145 | 2023-05-03 | 725 | keep | 0 | May | 2023 | 0.00049379 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-05-03 06:50 | 2023-05-03 11:41 | 15 | 4:51 | P | NO SE REPORTO CAUSA | 1X25 EN C/L | R23050300007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2023-05-03 | 4365 | keep | 0 | May | 2023 | 0.002973 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-03 06:58 | 2023-05-03 10:11 | 40 | 3:13 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | R23050300009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-05-03 | 7720 | keep | 0 | May | 2023 | 0.0052581 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-03 07:18 | 2023-05-03 09:17 | 1 | 1:59 | P | PROBLEMA DEL CLIENTE | 2 X 50 EN CORTE DE LINEA PROBLEMA DEL CLIENTE | C23050300018 | New_Event | Customer-Related Interruption | Include | Include | Public | 119 | 2023-05-03 | 119 | keep | 0 | May | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-03 07:21 | 2023-05-04 13:43 | 20 | 30:22 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERADO AVERIADO | S23050300032 | New_Event | UG Cable Fault | Include | Include | Equipment | 1822 | 2023-05-03 | 36440 | keep | 0 | May | 2023 | 0.024819 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-03 07:32 | 2023-05-03 15:39 | 50 | 8:07 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | S23050300034 | New_Event | Animals | Include | Include | Wildlife | 487 | 2023-05-03 | 24350 | keep | 0 | May | 2023 | 0.016585 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-03 07:34 | 2023-05-03 13:18 | 22 | 5:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA @ CAJA NO FUNDIO | R23050300011 | New_Event | Primary Wire Break | Include | Include | Equipment | 344 | 2023-05-03 | 7568 | keep | 0 | May | 2023 | 0.0051545 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-05-03 07:39 | 2023-05-03 10:03 | 216 | 2:24 | T | DESCONECTIVO DEFECTUOSO | BY-230503-01 SE ABRIO BKR Y SE REEMPLAZO MACHETE QUEMADO EN RISER DE SALIDA LLEVA 70% 1924-04 | S23050300037 | Additional_clients | Switch Failure | Include | Include | Equipment | 144 | 2023-05-03 | 31104 | keep | 0 | May | 2023 | 0.021185 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-03 07:39 | 2023-05-03 10:03 | 32 | 2:24 | P | ALIMENTADOR AMARRADO | BY-230503-01 SE ABRIO BKR Y SE REEMPLAZO MACHETE QUEMADO EN RISER DE SALIDA | S23050300037 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 144 | 2023-05-03 | 4608 | keep | 0 | May | 2023 | 0.0031385 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-03 07:52 | 2023-05-03 13:54 | 51 | 6:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PRIMARIA | B23050300026 | New_Event | Cutout Failure | Include | Include | Equipment | 362 | 2023-05-03 | 18462 | keep | 0 | May | 2023 | 0.012574 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
YAUCO | 2023-05-03 07:58 | 2023-05-03 07:59 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050300043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 1352 | keep | 0 | May | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
PONCE | 2023-05-03 08:01 | 2023-05-03 08:02 | 5069 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050300045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 5069 | keep | 0 | May | 2023 | 0.0034525 | 0.0034525 | Momentary | FALSE | FALSE | Not_TMED_Event | 5069
MAYAGÃœEZ | 2023-05-03 08:08 | 2023-05-03 14:25 | 30 | 6:17 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23050300048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 377 | 2023-05-03 | 11310 | keep | 0 | May | 2023 | 0.0077032 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-03 08:09 | 2023-05-03 09:16 | 100 | 1:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | P23050300023 | New_Event | Cutout Failure | Include | Include | Equipment | 67 | 2023-05-03 | 6700 | keep | 0 | May | 2023 | 0.0045633 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-05-03 08:11 | 2023-05-03 15:30 | 12 | 7:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO 50 KVA @ 4160 VOLT | P23050300048 | New_Event | Service Transformer Failure | Include | Include | Equipment | 439 | 2023-05-03 | 5268 | keep | 0 | May | 2023 | 0.003588 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-03 08:13 | 2023-05-03 20:33 | 44 | 12:20 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN C/L SE RETEZO LINEA PRIMARIA | C23050300032 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 740 | 2023-05-03 | 32560 | keep | 0 | May | 2023 | 0.022176 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
HUMACAO | 2023-05-03 08:15 | 2023-05-03 12:28 | 8 | 4:13 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C23050300033 | New_Event | Animals | Include | Include | Wildlife | 253 | 2023-05-03 | 2024 | keep | 0 | May | 2023 | 0.0013785 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-05-03 08:18 | 2023-05-03 09:46 | 200 | 1:28 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M23050300021 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 88 | 2023-05-03 | 17600 | keep | 0 | May | 2023 | 0.011987 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-03 08:23 | 2023-05-03 16:08 | 5 | 7:45 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | C23050300037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 465 | 2023-05-03 | 2325 | keep | 0 | May | 2023 | 0.0015835 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-05-03 08:26 | 2023-05-03 11:45 | 8 | 3:19 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCOTRO CAUSA | A23050300049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2023-05-03 | 1592 | keep | 0 | May | 2023 | 0.0010843 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-05-03 08:30 | 2023-05-03 09:36 | 4035 | 1:06 | T | ANIMAL | ALIMENTADOR FUERA DE SERVICIO PALOMA CRUZO FASE | P23050300097 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-05-03 | 266310 | keep | 0 | May | 2023 | 0.18138 | 0.0027482 | Sustained | FALSE | FALSE | Not_TMED_Event | 4035
MAYAGÃœEZ | 2023-05-03 08:30 | 2023-05-03 13:15 | 12 | 4:45 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | ABRIR TRANSFORMASDOR PARA REPARACIONES SECUNDARIAS | M23050300082 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 285 | 2023-05-03 | 3420 | keep | 0 | May | 2023 | 0.0023293 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-03 08:32 | 2023-05-03 15:51 | 1 | 7:19 | P | ANIMAL | 2 X 15 EN MONTURA SE RETIRO NIDO DE AVE | B23050300032 | New_Event | Animals | Include | Include | Wildlife | 439 | 2023-05-03 | 439 | keep | 0 | May | 2023 | 0.000299 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-03 08:47 | 2023-05-03 09:00 | 3 | 0:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO MONTURA PARA REPARAR BAJANTES SECUNDARIOS | B23050200075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 13 | 2023-05-03 | 39 | keep | 0 | May | 2023 | 2.6563e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-03 08:52 | 2023-05-03 16:07 | 28 | 7:15 | P | ANIMAL | 1 X 65 EN RISER Y 1 X 25 EN SU-6 SE RETIRO CULEBRA DE SU-6 | B23050300037 | New_Event | Animals | Include | Include | Wildlife | 435 | 2023-05-03 | 12180 | keep | 0 | May | 2023 | 0.0082957 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2023-05-03 08:52 | 2023-05-03 13:27 | 10 | 4:35 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA POR AVE | A23050300053 | New_Event | Animals | Include | Include | Wildlife | 275 | 2023-05-03 | 2750 | keep | 0 | May | 2023 | 0.001873 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-03 09:09 | 2023-05-04 08:57 | 1 | 23:48 | P | ANIMAL | 2X15 EN BANCO DE XMRS CRUCE POR AVE | B23050300041 | New_Event | Animals | Include | Include | Wildlife | 1428 | 2023-05-03 | 1428 | keep | 0 | May | 2023 | 0.0009726 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-03 09:13 | 2023-05-03 12:28 | 14 | 3:15 | P | SECUNDARIA/OTROS | SE ABRIO XMR SE REPARO PEDESTAL SOTERRADO | C23050300055 | New_Event |  |  |  |  | 195 | 2023-05-03 | 2730 | keep | 0 | May | 2023 | 0.0018594 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BAYAMON | 2023-05-03 09:16 | 2023-05-03 11:24 | 205 | 2:08 | P | CAUSAS EXTERNAS | 1 X 100 EN C/L SE RETIRO GLOBO METALICO | B23050300042 | New_Event | Damage From Public | Include | Include | Public | 128 | 2023-05-03 | 26240 | keep | 0 | May | 2023 | 0.017872 | 0.00013962 | Sustained | FALSE | FALSE | Not_TMED_Event | 205
CANOVANAS | 2023-05-03 09:30 | 2023-05-03 10:20 | 35 | 0:50 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | R23050300023 | New_Event | Animals | Include | Include | Wildlife | 50 | 2023-05-03 | 1750 | keep | 0 | May | 2023 | 0.0011919 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-03 09:40 | 2023-05-03 12:13 | 64 | 2:33 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23050300047 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-05-03 | 9792 | keep | 0 | May | 2023 | 0.0066693 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
MAYAGÃœEZ | 2023-05-03 09:41 | 2023-05-03 12:15 | 40 | 2:34 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | M23050300079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-05-03 | 6160 | keep | 0 | May | 2023 | 0.0041955 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-03 09:53 | 2023-05-03 09:58 | 34 | 0:05 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1116-02 | S23050300000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-05-03 | 170 | keep | 0 | May | 2023 | 0.00011579 | 2.3157e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 34
FAJARDO | 2023-05-03 09:58 | 2023-05-03 14:36 | 1 | 4:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 75KVA X 50KVA Y OTRO XMR 50KVA X 50KVA EN BANCO DE XMRS POR ESCAPE DE ACEITE | R23050300017 | New_Event | Service Transformer Failure | Include | Include | Equipment | 278 | 2023-05-03 | 278 | keep | 0 | May | 2023 | 0.00018934 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-03 10:18 | 2023-05-03 12:19 | 5 | 2:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO 100' LINEA SECUNDARIA | C23050300076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 121 | 2023-05-03 | 605 | keep | 0 | May | 2023 | 0.00041206 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
PONCE | 2023-05-03 10:22 | 2023-05-03 11:40 | 1 | 1:18 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA PAJARO CRUZO FASE | P23050300110 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-05-03 | 78 | keep | 0 | May | 2023 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-03 10:52 | 2023-05-03 12:23 | 150 | 1:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 140 EN CORTE DE LINEA POR VIENTO | A23050300069 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 91 | 2023-05-03 | 13650 | keep | 0 | May | 2023 | 0.009297 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2023-05-03 10:54 | 2023-05-03 14:30 | 75 | 3:36 | P | ANIMAL | 2 X 65 EN C/L AVE CRUZO LINEAS | P23050300121 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-05-03 | 16200 | keep | 0 | May | 2023 | 0.011034 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
YAUCO | 2023-05-03 11:02 | 2023-05-03 11:03 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050300125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 3973 | keep | 0 | May | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
BAYAMON | 2023-05-03 11:10 | 2023-05-03 15:45 | 1 | 4:35 | P | CONDUCTOR ROTO O ABIERTO | 2 X 50 EN C/L Y SE REPARO PUENTE DE CAJA A LINEA | B23050300073 | New_Event | Primary Wire Break | Include | Include | Equipment | 275 | 2023-05-03 | 275 | keep | 0 | May | 2023 | 0.0001873 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-03 11:14 | 2023-05-03 12:06 | 15 | 0:52 | P | ANIMAL | 1X10 EN XMR CRUCE POR AVE | C23050300093 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-05-03 | 780 | keep | 0 | May | 2023 | 0.00053125 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-03 11:23 | 2023-05-04 06:37 | 1 | 19:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | S23050300086 | New_Event | Cutout Failure | Include | Include | Equipment | 1154 | 2023-05-03 | 1154 | keep | 0 | May | 2023 | 0.00078598 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-03 11:29 | 2023-05-03 11:31 | 476 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 HABÃA PERSONAL DE LA COMPAÃ‘ÃA WTS DESGANCHANDO | C23050300121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-03 | 952 | keep | 0 | May | 2023 | 0.0006484 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-05-03 11:29 | 2023-05-03 11:31 | 1655 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 HABÃA PERSONAL DE LA COMPAÃ‘ÃA WTS DESGANCHANDO | C23050300121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-03 | 3310 | keep | 0 | May | 2023 | 0.0022544 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-05-03 11:29 | 2023-05-03 11:31 | 361 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 HABÃA PERSONAL DE LA COMPAÃ‘ÃA WTS DESGANCHANDO | C23050300121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-03 | 722 | keep | 0 | May | 2023 | 0.00049175 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-05-03 11:29 | 2023-05-03 11:31 | 2842 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 HABÃA PERSONAL DE LA COMPAÃ‘ÃA WTS DESGANCHANDO | C23050300121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-03 | 5684 | keep | 0 | May | 2023 | 0.0038713 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-05-03 11:29 | 2023-05-03 11:31 | 1702 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 HABÃA PERSONAL DE LA COMPAÃ‘ÃA WTS DESGANCHANDO | C23050300122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-03 | 3404 | keep | 0 | May | 2023 | 0.0023184 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CAGUAS | 2023-05-03 11:29 | 2023-05-03 11:31 | 918 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 HABÃA PERSONAL DE LA COMPAÃ‘ÃA WTS DESGANCHANDO | C23050300122 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-03 | 1836 | keep | 0 | May | 2023 | 0.0012505 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-03 11:29 | 2023-05-03 11:31 | 1725 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 HABÃA PERSONAL DE LA COMPAÃ‘ÃA WTS DESGANCHANDO | C23050300123 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-03 | 3450 | keep | 0 | May | 2023 | 0.0023498 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
HUMACAO | 2023-05-03 11:36 | 2023-05-03 14:38 | 2 | 3:02 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23050300099 | New_Event | Animals | Include | Include | Wildlife | 182 | 2023-05-03 | 364 | keep | 0 | May | 2023 | 0.00024792 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-05-03 11:36 | 2023-05-03 11:37 | 1089 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 50% DE LA CARGA POR EL 3015-07 | C2305030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 1089 | keep | 0 | May | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
ARECIBO | 2023-05-03 11:54 | 2023-05-04 11:30 | 8 | 23:36 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO 37.5 KVA POR 37.5 KVA | A23050300081 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1416 | 2023-05-03 | 11328 | keep | 0 | May | 2023 | 0.0077154 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-03 11:57 | 2023-05-03 16:42 | 11 | 4:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA X 37.5KVA TRANSFORMADOR NO REGULABA | S23050300094 | New_Event | Service Transformer Failure | Include | Include | Equipment | 285 | 2023-05-03 | 3135 | keep | 0 | May | 2023 | 0.0021352 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-05-03 11:58 | 2023-05-04 10:17 | 4 | 22:19 | P | ARBOL SOBRE LINEA | 3 X 30 EN RISER | S23050300096 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1339 | 2023-05-03 | 5356 | keep | 0 | May | 2023 | 0.0036479 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-05-03 12:10 | 2023-05-03 14:03 | 1 | 1:53 | P | NO SE REPORTO CAUSA | 1X40 EN RISER | R23050300038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 113 | 2023-05-03 | 113 | keep | 0 | May | 2023 | 7.6964e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-03 12:10 | 2023-05-03 14:40 | 1 | 2:30 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 25 KVA 2400 VOLT | P23050300138 | New_Event | Service Transformer Failure | Include | Include | Equipment | 150 | 2023-05-03 | 150 | keep | 0 | May | 2023 | 0.00010216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-03 12:13 | 2023-05-03 12:15 | 1702 | 0:02 | T | SOBRECARGA | SE ABRIO INTERRUPTOR PARA TRANSFERIR CARGA AL 3103-02 POR SOBRE CARGA AL 101% DEL TRANSFORMADOR EN MVA | C23050300104 | New_Event | Trip Due To Overload | Include | Include | Other | 2 | 2023-05-03 | 3404 | keep | 0 | May | 2023 | 0.0023184 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
AGUADILLA | 2023-05-03 12:14 | 2023-05-03 13:50 | 100 | 1:36 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIERON MACHETES SECCIONALIZAR LINEA PRIMARIA ROTA E INSTALAR TAG | M23050300119 | New_Event | Primary Wire Break | Include | Include | Equipment | 96 | 2023-05-03 | 9600 | keep | 0 | May | 2023 | 0.0065385 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-03 12:14 | 2023-05-03 16:20 | 15 | 4:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR REEMPLAZAR CONECTORES SECUNDARIOS | C23050300105 | New_Event | Secondary Wire Break | Include | Include | Equipment | 246 | 2023-05-03 | 3690 | keep | 0 | May | 2023 | 0.0025132 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-03 12:15 | 2023-05-03 12:33 | 861 | 0:18 | P | SOBRECARGA | SE ABRIO INTERRUPTOR PARA TRANSFERIR CARGA AL 3103-02 POR SOBRE CARGA DEL TRANSFORMADOR EN MVA | C23050300104 | 1st_after_momentary | Trip Due To Overload | Include | Include | Other | 18 | 2023-05-03 | 15498 | keep | 0 | May | 2023 | 0.010556 | 0.00058642 | Sustained | FALSE | FALSE | Not_TMED_Event | 861
BARRANQUITAS | 2023-05-03 12:17 | 2023-05-03 18:15 | 12 | 5:58 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23050300107 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 358 | 2023-05-03 | 4296 | keep | 0 | May | 2023 | 0.002926 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-05-03 12:38 | 2023-05-03 14:30 | 15 | 1:52 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23050300142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-05-03 | 1680 | keep | 0 | May | 2023 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-03 12:45 | 2023-05-03 15:26 | 8 | 2:41 | P | ANIMAL | 1X15 EN XMR CRUCE POR AVE | R23050300043 | New_Event | Animals | Include | Include | Wildlife | 161 | 2023-05-03 | 1288 | keep | 0 | May | 2023 | 0.00087725 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-05-03 12:45 | 2023-05-03 18:22 | 80 | 5:37 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN C/L SE ELIMININO PARARRAYO | C23050300115 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 337 | 2023-05-03 | 26960 | keep | 0 | May | 2023 | 0.018362 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-05-03 13:25 | 2023-05-03 15:23 | 10 | 1:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN PROVISIONAL AEREO PARA REMPLAZAR BARRAS EN PEDESTAL | R23050300050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 118 | 2023-05-03 | 1180 | keep | 0 | May | 2023 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-03 13:32 | 2023-05-03 15:26 | 13 | 1:54 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE REEMPLAZO TRAMO DE SECUNDARIA QUE CAMION TIRO AL PISO | B23050300086 | New_Event | Damage From Public | Include | Include | Public | 114 | 2023-05-03 | 1482 | keep | 0 | May | 2023 | 0.0010094 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
GUAYAMA | 2023-05-03 13:41 | 2023-05-03 16:30 | 40 | 2:49 | P | PARARRAYOS DEFECTUOSO | 2 X 65 EN C/L SE REMPLAZO PARARRAYO DEFECTUOSO | P23050300150 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 169 | 2023-05-03 | 6760 | keep | 0 | May | 2023 | 0.0046042 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-03 13:44 | 2023-05-03 15:49 | 50 | 2:05 | P | ANIMAL | 1 X 10 EN C/L SE REEMPLAZO PORTAFUSIBLE Y X 80 EN C/L CRUCE X AVE | C23050300126 | New_Event | Animals | Include | Include | Wildlife | 125 | 2023-05-03 | 6250 | keep | 0 | May | 2023 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-03 13:48 | 2023-05-03 18:10 | 191 | 4:22 | P | ANIMAL | 2 X 80 EN C/L AVE CRUZO LINEAS | B23050300092 | New_Event | Animals | Include | Include | Wildlife | 262 | 2023-05-03 | 50042 | keep | 0 | May | 2023 | 0.034083 | 0.00013009 | Sustained | FALSE | FALSE | Not_TMED_Event | 191
AGUADILLA | 2023-05-03 13:50 | 2023-05-03 20:30 | 400 | 6:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA REPARAR LINEA PRIMARIA ROTA | M23050300119 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 400 | 2023-05-03 | 160000 | keep | 0 | May | 2023 | 0.10898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-03 13:54 | 2023-05-04 07:55 | 1 | 18:01 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23050300097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1081 | 2023-05-03 | 1081 | keep | 0 | May | 2023 | 0.00073626 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-03 13:55 | 2023-05-03 14:48 | 3 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARAN CONEXIONES | A23050200136 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-05-03 | 159 | keep | 0 | May | 2023 | 0.00010829 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2023-05-03 14:03 | 2023-05-03 15:55 | 30 | 1:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23050300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-05-03 | 3360 | keep | 0 | May | 2023 | 0.0022885 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-03 14:04 | 2023-05-03 14:05 | 2900 | 0:01 | T | ANIMAL | RECERRO | C23050300133 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-03 | 2900 | keep | 0 | May | 2023 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2023-05-03 14:05 | 2023-05-03 17:10 | 6 | 3:05 | P | ANIMAL | 1 X 100 EN XMR CRUCE X AVE | C23050300133 | 1st_after_momentary | Animals | Include | Include | Wildlife | 185 | 2023-05-03 | 1110 | keep | 0 | May | 2023 | 0.00075602 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-03 14:18 | 2023-05-04 16:05 | 1 | 25:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1X15 EN BANCO DE XMRS SE REMPLAZO AISLADOR PRIMARIO | B23050300097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1547 | 2023-05-03 | 1547 | keep | 0 | May | 2023 | 0.0010537 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-03 14:23 | 2023-05-03 17:21 | 3 | 2:58 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | B23050300098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-05-03 | 534 | keep | 0 | May | 2023 | 0.0003637 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-05-03 14:27 | 2023-05-03 18:30 | 171 | 4:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 1 X 80 EN C/L | S23050300128 | New_Event | Cutout Failure | Include | Include | Equipment | 243 | 2023-05-03 | 41553 | keep | 0 | May | 2023 | 0.028302 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
BAYAMON | 2023-05-03 14:53 | 2023-05-03 16:22 | 7 | 1:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA | B23050300102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 89 | 2023-05-03 | 623 | keep | 0 | May | 2023 | 0.00042432 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-03 15:00 | 2023-05-03 18:52 | 200 | 3:52 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23050300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-05-03 | 46400 | keep | 0 | May | 2023 | 0.031603 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-05-03 15:20 | 2023-05-03 18:53 | 25 | 3:33 | P | CAUSAS EXTERNAS | 1 X 30 EN CORTE DE LINEA CAMION IMPACTO POSTE | A23050300110 | New_Event | Damage From Public | Include | Include | Public | 213 | 2023-05-03 | 5325 | keep | 0 | May | 2023 | 0.0036268 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-05-03 15:48 | 2023-05-03 17:35 | 7 | 1:47 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A23050300115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-05-03 | 749 | keep | 0 | May | 2023 | 0.00051014 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2023-05-03 15:55 | 2023-05-03 21:00 | 12 | 5:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR Y SE REEMPLAZO LINEA SECUNDARIA | A23050300119 | New_Event | Secondary Wire Break | Include | Include | Equipment | 305 | 2023-05-03 | 3660 | keep | 0 | May | 2023 | 0.0024928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-03 16:11 | 2023-05-04 10:15 | 7 | 18:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 10 EN TRANSFORMADOR SE REEMPLAZARON CAJAS QUEMADAS | C23050300151 | New_Event | Cutout Failure | Include | Include | Equipment | 1084 | 2023-05-03 | 7588 | keep | 0 | May | 2023 | 0.0051682 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-05-03 17:10 | 2023-05-03 17:25 | 6 | 0:15 | P | SECUNDARIA/OTROS | SE ABRIO TRANSFORMADOR PARA INSTALAR BARRA DE TIERRA POR PROBLEMAS DE FLUCTUACION DE VOLTAJE | M23050300176 | New_Event |  |  |  |  | 15 | 2023-05-03 | 90 | keep | 0 | May | 2023 | 6.1299e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-03 17:10 | 2023-05-03 18:19 | 7 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO Y SE LEVANTO SECUNDARIA | B23050300121 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-05-03 | 483 | keep | 0 | May | 2023 | 0.00032897 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-03 17:11 | 2023-05-03 22:57 | 285 | 5:46 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23050300162 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2023-05-03 | 98610 | keep | 0 | May | 2023 | 0.067163 | 0.00019411 | Sustained | FALSE | FALSE | Not_TMED_Event | 285
HUMACAO | 2023-05-03 17:17 | 2023-05-04 01:50 | 154 | 8:33 | P | CAUSAS EXTERNAS | SE ABRIO C/L TOTAL PARA SE REEMPLAZO DE POSTE PARTIDO POR IMPACTO DE VEHICULO | C23050300161 | New_Event | Damage From Public | Include | Include | Public | 513 | 2023-05-03 | 79002 | keep | 0 | May | 2023 | 0.053808 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
CAGUAS | 2023-05-03 17:41 | 2023-05-03 18:06 | 8 | 0:25 | P | TRANSFORMADOR AVERIADO | SE TRANSFIRIERON LAS CARGAS DEL XMR FID 3077686 QUE TIENE BUSHING DANADO Y SE LE PASO LA CARGA DE 8 CLIENTES AL XMR FID 3077651 | C23050300096 | New_Event | Service Transformer Failure | Include | Include | Equipment | 25 | 2023-05-03 | 200 | keep | 0 | May | 2023 | 0.00013622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-03 17:44 | 2023-05-04 08:18 | 8 | 14:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | B23050300124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 874 | 2023-05-03 | 6992 | keep | 0 | May | 2023 | 0.0047622 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-05-03 17:48 | 2023-05-03 18:46 | 6 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C23050300167 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2023-05-03 | 348 | keep | 0 | May | 2023 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-03 17:53 | 2023-05-03 17:54 | 652 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B23050300126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 652 | keep | 0 | May | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
VEGA BAJA | 2023-05-03 17:53 | 2023-05-03 17:54 | 2704 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 7800 | B23050300126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-03 | 2704 | keep | 0 | May | 2023 | 0.0018417 | 0.0018417 | Momentary | FALSE | FALSE | Not_TMED_Event | 2704
MAYAGÃœEZ | 2023-05-03 18:03 | 2023-05-03 18:04 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23050300192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 2999 | keep | 0 | May | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
BAYAMON | 2023-05-03 18:13 | 2023-05-03 19:17 | 43 | 1:04 | P | ANIMAL | 1 X 40 EN C/L AVE | B23050300128 | New_Event | Animals | Include | Include | Wildlife | 64 | 2023-05-03 | 2752 | keep | 0 | May | 2023 | 0.0018744 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2023-05-03 18:22 | 2023-05-03 18:28 | 598 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 3405-03 LLEVA EL 3403-01 PERSONAL PROBANDO EN EL CORTE DE LINEA DISPARO EL BKR, SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL. | C23050300178 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-03 | 3588 | keep | 0 | May | 2023 | 0.0024438 | 0.0004073 | Sustained | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2023-05-03 18:22 | 2023-05-03 18:28 | 1001 | 0:06 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR LLEVA EL 3403-01 PERSONAL PROBANDO EN EL CORTE DE LINEA DISPARO EL BKR, SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL. | C23050300178 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 6 | 2023-05-03 | 6006 | keep | 0 | May | 2023 | 0.0040907 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-03 18:26 | 2023-05-04 12:16 | 123 | 17:50 | P | ANIMAL | 1 X 40 EN C/L Y 1 X 15 EN XMR CRUCE POR AVE | R23050300064 | New_Event | Animals | Include | Include | Wildlife | 1070 | 2023-05-03 | 131610 | keep | 0 | May | 2023 | 0.089639 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
BARRANQUITAS | 2023-05-03 18:28 | 2023-05-03 20:02 | 80 | 1:34 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN C/L SE ELIMININO PARARRAYO | C23050300115 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 94 | 2023-05-03 | 7520 | keep | 0 | May | 2023 | 0.0051218 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-03 18:48 | 2023-05-04 10:45 | 15 | 15:57 | P | CABLE SOTERRADO AVERIADO | 1 X 15 RBA EN SU-15 @ T-57 | R23050300066 | New_Event | UG Cable Fault | Include | Include | Equipment | 957 | 2023-05-03 | 14355 | keep | 0 | May | 2023 | 0.0097771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-03 18:56 | 2023-05-04 02:00 | 414 | 7:04 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 100 EN C/L 1 X 65 EN RISER 1 X 65 EN RISER PARARAYO AVERIADO EN SU-2 | S23050300174 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 424 | 2023-05-03 | 175536 | keep | 0 | May | 2023 | 0.11956 | 0.00028197 | Sustained | FALSE | FALSE | Not_TMED_Event | 414
BAYAMON | 2023-05-03 19:06 | 2023-05-03 19:33 | 20 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON 2 BARRAS SECUNDARIAS EN PEDESTAL | S23050300176 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-05-03 | 540 | keep | 0 | May | 2023 | 0.00036779 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-03 19:14 | 2023-05-04 14:40 | 12 | 19:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR PARA REPARAR SECUNDARIA Y SE REMEPLAZO CAJA PRIMARIA | R23050300067 | New_Event | Cutout Failure | Include | Include | Equipment | 1166 | 2023-05-03 | 13992 | keep | 0 | May | 2023 | 0.0095299 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-03 19:20 | 2023-05-03 22:51 | 2608 | 3:31 | S | AVERIA EN BARRA DE DISTRIBUCION | DISPARO DE MAIN BREAKER SE ELIMINO LOS 3 BAJANTES QUE VAN HACIA LA MEDICION REMOTA POR AVERIA EN PARARRAYO Y 2 PUENTES AVERIADOS. SE QUEDA FUERA LA MEDICION REMOTA. | C23050300286 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 211 | 2023-05-03 | 550288 | keep | 0 | May | 2023 | 0.3748 | 0.0017763 | Sustained | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2023-05-03 19:20 | 2023-05-03 22:51 | 845 | 3:31 | S | AVERIA EN BARRA DE DISTRIBUCION | DISPARO DE MAIN BREAKER SE ELIMINO LOS 3 BAJANTES QUE VAN HACIA LA MEDICION REMOTA POR AVERIA EN PARARRAYO Y 2 PUENTES AVERIADOS. SE QUEDA FUERA LA MEDICION REMOTA. | C23050300287 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 211 | 2023-05-03 | 178295 | keep | 0 | May | 2023 | 0.12144 | 0.00057553 | Sustained | FALSE | FALSE | Not_TMED_Event | 845
BAYAMON | 2023-05-03 19:31 | 2023-05-03 19:34 | 1785 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y 10% 1717-01 SE CERRO PPOR SCADA | B2305030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-03 | 5355 | keep | 0 | May | 2023 | 0.0036473 | 0.0012158 | Momentary | FALSE | FALSE | Not_TMED_Event | 1785
BAYAMON | 2023-05-03 19:31 | 2023-05-03 19:34 | 453 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y 10% 1717-01 SE CERRO PPOR SCADA | B2305030000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-03 | 1359 | keep | 0 | May | 2023 | 0.00092561 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-05-03 19:31 | 2023-05-03 19:34 | 186 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVANDO 90% 1711-04 Y 10% 1717-01 SE CERRO PPOR SCADA | B2305030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-03 | 558 | keep | 0 | May | 2023 | 0.00038005 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2023-05-03 19:34 | 2023-05-04 14:46 | 10 | 19:12 | P | NO SE REPORTO CAUSA | 3X80 EN C/L | B23050300137 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1152 | 2023-05-03 | 11520 | keep | 0 | May | 2023 | 0.0078462 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-03 19:47 | 2023-05-04 06:11 | 30 | 10:24 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23050300139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 624 | 2023-05-03 | 18720 | keep | 0 | May | 2023 | 0.01275 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-03 19:51 | 2023-05-04 07:43 | 80 | 11:52 | P | CONDUCTOR ARRIADO O CRUZADO | SE RETESO LINEA PRIMARIA Y 2 X 80 EN CORTE DE LINEA | P23050300197 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 712 | 2023-05-03 | 56960 | keep | 0 | May | 2023 | 0.038795 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-05-03 19:51 | 2023-05-03 20:40 | 150 | 0:49 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR RAMA | A23050300138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2023-05-03 | 7350 | keep | 0 | May | 2023 | 0.0050061 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-05-03 19:56 | 2023-05-03 21:05 | 100 | 1:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23050300225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 69 | 2023-05-03 | 6900 | keep | 0 | May | 2023 | 0.0046996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-05-03 20:00 | 2023-05-03 21:42 | 150 | 1:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO PORTAFUSIBLE | B23050300153 | New_Event | Cutout Failure | Include | Include | Equipment | 102 | 2023-05-03 | 15300 | keep | 0 | May | 2023 | 0.010421 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-05-03 20:02 | 2023-05-03 20:06 | 598 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 3405-03 LLEVA EL 3403-01 PERSONAL PROBANDO EN EL CORTE DE LINEA DISPARO EL BKR, SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL. | C23050300178 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-03 | 2392 | keep | 0 | May | 2023 | 0.0016292 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-03 20:02 | 2023-05-03 20:06 | 1001 | 0:04 | T | PARARRAYOS DEFECTUOSO | DISPARO DE INTERRUPTOR 3405-03 LLEVA EL 3403-01 PERSONAL PROBANDO EN EL CORTE DE LINEA DISPARO EL BKR, SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL. | C23050300178 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 4 | 2023-05-03 | 4004 | keep | 0 | May | 2023 | 0.0027271 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-03 20:06 | 2023-05-03 21:15 | 80 | 1:09 | P | PARARRAYOS DEFECTUOSO | 1 X 140 EN C/L SE ELIMININO PARARRAYO | C23050300115 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 69 | 2023-05-03 | 5520 | keep | 0 | May | 2023 | 0.0037596 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-03 20:13 | 2023-05-03 21:53 | 673 | 1:40 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23050300193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 100 | 2023-05-03 | 67300 | keep | 0 | May | 2023 | 0.045838 | 0.00045838 | Sustained | FALSE | FALSE | Not_TMED_Event | 673
BARRANQUITAS | 2023-05-03 20:22 | 2023-05-03 23:10 | 80 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23050300292 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-05-03 | 13440 | keep | 0 | May | 2023 | 0.0091539 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-03 20:30 | 2023-05-03 21:52 | 2000 | 1:22 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA REPARAR PUENTE PRIMARIO ABIERTO | M23050300119 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 82 | 2023-05-03 | 164000 | keep | 0 | May | 2023 | 0.1117 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-03 20:43 | 2023-05-04 08:36 | 20 | 11:53 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | M23050300239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 713 | 2023-05-03 | 14260 | keep | 0 | May | 2023 | 0.0097124 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-03 20:56 | 2023-05-03 22:00 | 100 | 1:04 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23050300153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-05-03 | 6400 | keep | 0 | May | 2023 | 0.004359 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-03 21:21 | 2023-05-04 00:31 | 300 | 3:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23050300262 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 190 | 2023-05-03 | 57000 | keep | 0 | May | 2023 | 0.038822 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-05-03 21:28 | 2023-05-04 00:58 | 60 | 3:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050300174 | New_Event | Vegetation Contact | Include | Include | Vegetation | 210 | 2023-05-03 | 12600 | keep | 0 | May | 2023 | 0.0085818 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-03 21:39 | 2023-05-04 04:05 | 175 | 6:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA | S23050300212 | New_Event | Cutout Failure | Include | Include | Equipment | 386 | 2023-05-03 | 67550 | keep | 0 | May | 2023 | 0.046008 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
MAYAGÃœEZ | 2023-05-03 21:42 | 2023-05-04 12:50 | 16 | 15:08 | P | CONDUCTOR ROTO O ABIERTO | SE FIJA BAJANTE PRIMARIO A TRANSFORMADOR | M23050300279 | New_Event | Primary Wire Break | Include | Include | Equipment | 908 | 2023-05-03 | 14528 | keep | 0 | May | 2023 | 0.009895 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
ARECIBO | 2023-05-03 21:49 | 2023-05-03 23:21 | 150 | 1:32 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23050300176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-05-03 | 13800 | keep | 0 | May | 2023 | 0.0093991 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 591 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 POR APARENTE OPERACIÃ“N LENTA DEL BKR 8310 DISPARA LINEA 0700 EN SOUCO Y BKR 8120 EN YAUCO 1 | P23050300263 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 5910 | keep | 0 | May | 2023 | 0.0040253 | 0.00040253 | Sustained | FALSE | FALSE | Not_TMED_Event | 591
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 1924 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 POR APARENTE OPERACIÃ“N LENTA DEL BKR 8310 DISPARA LINEA 0700 EN SOUCO Y BKR 8120 EN YAUCO 1 | P23050300264 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 19240 | keep | 0 | May | 2023 | 0.013104 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 968 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 POR APARENTE OPERACIÃ“N LENTA DEL BKR 8310 DISPARA LINEA 0700 EN SOUCO Y BKR 8120 EN YAUCO 1 | P23050300264 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 9680 | keep | 0 | May | 2023 | 0.006593 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 680 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 POR APARENTE OPERACIÃ“N LENTA DEL BKR 8310 DISPARA LINEA 0700 EN SOUCO Y BKR 8120 EN YAUCO 1 | P23050300264 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 6800 | keep | 0 | May | 2023 | 0.0046314 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 2246 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 POR APARENTE OPERACIÃ“N LENTA DEL BKR 8310 DISPARA LINEA 0700 EN SOUCO Y BKR 8120 EN YAUCO 1 | P23050300264 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 22460 | keep | 0 | May | 2023 | 0.015297 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 2011 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 POR APARENTE OPERACIÃ“N LENTA DEL BKR 8310 DISPARA LINEA 0700 EN SOUCO Y BKR 8120 EN YAUCO 1 | P23050300265 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 20110 | keep | 0 | May | 2023 | 0.013697 | 0.0013697 | Sustained | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 339 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 700 POR APARENTE OPERACIÃ“N LENTA DEL BKR 8310 DISPARA LINEA 0700 EN SOUCO Y BKR 8120 EN YAUCO 1 | P23050300265 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 3390 | keep | 0 | May | 2023 | 0.0023089 | 0.00023089 | Sustained | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 1352 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8300 CONDUCTOR AVERIADO EN LINEA 8300 | P23050300266 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 13520 | keep | 0 | May | 2023 | 0.0092084 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 3973 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8300 CONDUCTOR AVERIADO EN LINEA 8300 | P23050300266 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 39730 | keep | 0 | May | 2023 | 0.02706 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2023-05-03 22:13 | 2023-05-03 22:23 | 2484 | 0:10 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8300 CONDUCTOR AVERIADO EN LINEA 8300 | P23050300266 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 10 | 2023-05-03 | 24840 | keep | 0 | May | 2023 | 0.016918 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
MAYAGÃœEZ | 2023-05-03 22:21 | 2023-05-03 22:24 | 4381 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR | M23050300290 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-03 | 13143 | keep | 0 | May | 2023 | 0.0089516 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
CANOVANAS | 2023-05-03 23:30 | 2023-05-03 23:31 | 4 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2305030000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-03 | 4 | keep | 0 | May | 2023 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-05-04 00:12 | 2023-05-04 04:33 | 70 | 4:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO PORTAFUSIBLE QUEMADO | C23050400001 | New_Event | Cutout Failure | Include | Include | Equipment | 261 | 2023-05-04 | 18270 | keep | 0 | May | 2023 | 0.012444 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-05-04 01:06 | 2023-05-04 05:11 | 60 | 4:05 | P | CABLE SOTERRADO AVERIADO | 2 X 40 EN PROVISIONAL AEREO SE SECCIONALIZO TRAMO SOTERRADO AVERIADO | S23050400005 | New_Event | UG Cable Fault | Include | Include | Equipment | 245 | 2023-05-04 | 14700 | keep | 0 | May | 2023 | 0.010012 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 591 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400070 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 4728 | keep | 0 | May | 2023 | 0.0032202 | 0.00040253 | Sustained | FALSE | FALSE | Not_TMED_Event | 591
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 1924 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 15392 | keep | 0 | May | 2023 | 0.010483 | 0.0013104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 968 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 7744 | keep | 0 | May | 2023 | 0.0052744 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 680 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 5440 | keep | 0 | May | 2023 | 0.0037052 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 2246 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 17968 | keep | 0 | May | 2023 | 0.012238 | 0.0015297 | Sustained | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 2011 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 16088 | keep | 0 | May | 2023 | 0.010957 | 0.0013697 | Sustained | FALSE | FALSE | Not_TMED_Event | 2011
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 339 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 2712 | keep | 0 | May | 2023 | 0.0018471 | 0.00023089 | Sustained | FALSE | FALSE | Not_TMED_Event | 339
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 1569 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 12552 | keep | 0 | May | 2023 | 0.0085491 | 0.0010686 | Sustained | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 2309 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 18472 | keep | 0 | May | 2023 | 0.012581 | 0.0015726 | Sustained | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 2179 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 17432 | keep | 0 | May | 2023 | 0.011873 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2023-05-04 01:20 | 2023-05-04 01:28 | 2440 | 0:08 | S | LINEA DE TRANSMISION 38KV | TOC SUR ABRE LINEA TRANSMISION 700 PARA CERRAR GOAB EN LINEA 8300 VLE PARA REPARAR CONDUCTOR AVERIADO EN LINEA 8300 | P23050400073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 8 | 2023-05-04 | 19520 | keep | 0 | May | 2023 | 0.013295 | 0.0016619 | Sustained | FALSE | FALSE | Not_TMED_Event | 2440
CANOVANAS | 2023-05-04 02:00 | 2023-05-04 02:01 | 4 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2305040000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 4 | keep | 0 | May | 2023 | 2.7244e-06 | 2.7244e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-05-04 02:10 | 2023-05-04 10:49 | 50 | 8:39 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA Y SE REEMPLAZO CAJA PRIMARIA | M23050400010 | New_Event | Cutout Failure | Include | Include | Equipment | 519 | 2023-05-04 | 25950 | keep | 0 | May | 2023 | 0.017674 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-04 02:22 | 2023-05-04 10:05 | 15 | 7:43 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA POR DESGANCHE | M23050400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 463 | 2023-05-04 | 6945 | keep | 0 | May | 2023 | 0.0047302 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-04 03:30 | 2023-05-04 12:53 | 6 | 9:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA | S23050400018 | New_Event | Cutout Failure | Include | Include | Equipment | 563 | 2023-05-04 | 3378 | keep | 0 | May | 2023 | 0.0023007 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-05-04 03:46 | 2023-05-04 07:16 | 50 | 3:30 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | P23050400123 | New_Event | Animals | Include | Include | Wildlife | 210 | 2023-05-04 | 10500 | keep | 0 | May | 2023 | 0.0071515 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-04 05:11 | 2023-05-04 11:35 | 12 | 6:24 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO AVERIADO DEL T-37 @ T-38 GOI SJ-230504-01 | S23050400005 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 384 | 2023-05-04 | 4608 | keep | 0 | May | 2023 | 0.0031385 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-04 05:20 | 2023-05-04 05:21 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2305040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 1225 | keep | 0 | May | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-05-04 05:22 | 2023-05-04 16:18 | 50 | 10:56 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23050400020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 656 | 2023-05-04 | 32800 | keep | 0 | May | 2023 | 0.02234 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-05-04 05:23 | 2023-05-04 10:56 | 60 | 5:33 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C23050400019 | New_Event | Animals | Include | Include | Wildlife | 333 | 2023-05-04 | 19980 | keep | 0 | May | 2023 | 0.013608 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-05-04 06:13 | 2023-05-04 06:20 | 1891 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 3700 | C23050400022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-04 | 13237 | keep | 0 | May | 2023 | 0.0090157 | 0.001288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2023-05-04 06:13 | 2023-05-04 06:20 | 1250 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 3700 | C23050400022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-04 | 8750 | keep | 0 | May | 2023 | 0.0059596 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2023-05-04 06:13 | 2023-05-04 06:20 | 2141 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 3700 | C23050400022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-04 | 14987 | keep | 0 | May | 2023 | 0.010208 | 0.0014582 | Sustained | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2023-05-04 06:13 | 2023-05-04 06:20 | 1827 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA DE TRANSMISION 3700 | C23050400022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-04 | 12789 | keep | 0 | May | 2023 | 0.0087105 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
CANOVANAS | 2023-05-04 06:27 | 2023-05-04 10:09 | 65 | 3:42 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | R23050400005 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-05-04 | 14430 | keep | 0 | May | 2023 | 0.0098282 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2023-05-04 06:36 | 2023-05-04 09:23 | 3 | 2:47 | P | ANIMAL | 2 X 50 EN RISER POR AVE | M2305040001 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-05-04 | 501 | keep | 0 | May | 2023 | 0.00034123 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-05-04 06:44 | 2023-05-04 06:45 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 906 | keep | 0 | May | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
MAYAGÃœEZ | 2023-05-04 07:05 | 2023-05-04 07:06 | 2067 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23050400020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 2067 | keep | 0 | May | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
AGUADILLA | 2023-05-04 07:18 | 2023-05-04 11:00 | 30 | 3:42 | P | DESGANCHE | 1 X 65 EN CL CRUCE DE LINEA PRIMARIA POR BAMBU | M23050400021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-05-04 | 6660 | keep | 0 | May | 2023 | 0.0045361 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-04 07:20 | 2023-05-04 10:48 | 10 | 3:28 | P | ANIMAL | 1 X 30 EN CL CRUCE POR AVE | M23050400022 | New_Event | Animals | Include | Include | Wildlife | 208 | 2023-05-04 | 2080 | keep | 0 | May | 2023 | 0.0014167 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-04 07:26 | 2023-05-04 10:12 | 5 | 2:46 | P | ANIMAL | 2 X 10 EN TRANSFORMADOR POR AVE | M23050400023 | New_Event | Animals | Include | Include | Wildlife | 166 | 2023-05-04 | 830 | keep | 0 | May | 2023 | 0.00056531 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-05-04 07:27 | 2023-05-04 11:30 | 50 | 4:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P23050400144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-05-04 | 12150 | keep | 0 | May | 2023 | 0.0082753 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-04 07:28 | 2023-05-04 07:30 | 1746 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23050400012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-04 | 3492 | keep | 0 | May | 2023 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
GUAYAMA | 2023-05-04 07:33 | 2023-05-04 12:38 | 35 | 5:05 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA POR AVE | P23050400146 | New_Event | Animals | Include | Include | Wildlife | 305 | 2023-05-04 | 10675 | keep | 0 | May | 2023 | 0.0072707 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CANOVANAS | 2023-05-04 07:34 | 2023-05-04 14:16 | 92 | 6:42 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23050400011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 402 | 2023-05-04 | 36984 | keep | 0 | May | 2023 | 0.02519 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
VEGA BAJA | 2023-05-04 07:49 | 2023-05-04 14:22 | 1 | 6:33 | P | ANIMAL | 1X15 EN MONTURA DE XMRS CRUCE POR AVE | B23050400017 | New_Event | Animals | Include | Include | Wildlife | 393 | 2023-05-04 | 393 | keep | 0 | May | 2023 | 0.00026767 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-04 07:52 | 2023-05-04 15:06 | 1 | 7:14 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23050400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 434 | 2023-05-04 | 434 | keep | 0 | May | 2023 | 0.0002956 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-04 07:55 | 2023-05-04 10:50 | 130 | 2:55 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | C23050400047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 175 | 2023-05-04 | 22750 | keep | 0 | May | 2023 | 0.015495 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
AGUADILLA | 2023-05-04 07:58 | 2023-05-04 13:40 | 5 | 5:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN TRANSFORMADOR | A23050400019 | New_Event | Primary Wire Break | Include | Include | Equipment | 342 | 2023-05-04 | 1710 | keep | 0 | May | 2023 | 0.0011647 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-04 08:11 | 2023-05-04 10:30 | 10 | 2:19 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA RETIRAR RAMA DE ARBOL Y REPARAR SECUNDARIA CRUZADA | B23050400019 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 139 | 2023-05-04 | 1390 | keep | 0 | May | 2023 | 0.00094672 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-04 08:11 | 2023-05-04 08:15 | 21 | 0:04 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23050400051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-04 | 84 | keep | 0 | May | 2023 | 5.7212e-05 | 1.4303e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2023-05-04 08:11 | 2023-05-04 15:00 | 70 | 6:49 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE | A23050400024 | New_Event | Animals | Include | Include | Wildlife | 409 | 2023-05-04 | 28630 | keep | 0 | May | 2023 | 0.0195 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2023-05-04 08:15 | 2023-05-04 20:50 | 8 | 12:35 | P | CABLE SOTERRADO AVERIADO | SE REEEMPLAZO CAJA PRIMARIA PARARRAYO CABLE SOTERRADO SE REMEPLAZO EL XMR 100KVA X 100KVA. | R23050400018 | New_Event | UG Cable Fault | Include | Include | Equipment | 755 | 2023-05-04 | 6040 | keep | 0 | May | 2023 | 0.0041138 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-05-04 08:15 | 2023-05-04 08:16 | 554 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | C23050400054 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-05-04 | 554 | keep | 0 | May | 2023 | 0.00037733 | 0.00037733 | Momentary | FALSE | FALSE | Not_TMED_Event | 554
CAGUAS | 2023-05-04 08:16 | 2023-05-04 13:55 | 100 | 5:39 | P | CAUSAS EXTERNAS | 3 X 50 EN CORTE DE LINEA CRUCE CON GLOBO | C23050400057 | 1st_after_momentary | Damage From Public | Include | Include | Public | 339 | 2023-05-04 | 33900 | keep | 0 | May | 2023 | 0.023089 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-04 08:16 | 2023-05-04 19:11 | 21 | 10:55 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23050400051 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 655 | 2023-05-04 | 13755 | keep | 0 | May | 2023 | 0.0093685 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
HUMACAO | 2023-05-04 08:27 | 2023-05-04 08:28 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 2354 | keep | 0 | May | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2023-05-04 08:34 | 2023-05-04 09:24 | 6 | 0:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA Y PARARRAYO | S23050400045 | New_Event | Cutout Failure | Include | Include | Equipment | 50 | 2023-05-04 | 300 | keep | 0 | May | 2023 | 0.00020433 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-05-04 08:42 | 2023-05-04 11:04 | 8 | 2:22 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR POR AVE | M23050400039 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-05-04 | 1136 | keep | 0 | May | 2023 | 0.00077372 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-05-04 08:45 | 2023-05-04 13:13 | 21 | 4:28 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REMPLAZO POSTE | C23050400065 | New_Event | Primary Pole Failure | Include | Include | Equipment | 268 | 2023-05-04 | 5628 | keep | 0 | May | 2023 | 0.0038332 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-05-04 08:46 | 2023-05-04 21:23 | 3 | 12:37 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y REMPLAZO E CAJA PRIMARIA | S23050400049 | New_Event | Cutout Failure | Include | Include | Equipment | 757 | 2023-05-04 | 2271 | keep | 0 | May | 2023 | 0.0015468 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-05-04 08:55 | 2023-05-04 10:17 | 17 | 1:22 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR POR ESCAPE DE ACEITE DE 50KVA POR UNO DE LA MISMA CAPACIDAD | R23050400024 | New_Event | Service Transformer Failure | Include | Include | Equipment | 82 | 2023-05-04 | 1394 | keep | 0 | May | 2023 | 0.00094945 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
GUAYAMA | 2023-05-04 08:57 | 2023-05-04 10:04 | 8 | 1:07 | P | ANIMAL | 1 X 15 EN TRANBSFORMADOR POR AVE | P23050400165 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-05-04 | 536 | keep | 0 | May | 2023 | 0.00036507 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-04 09:03 | 2023-05-04 11:14 | 12 | 2:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA TRASPATIO | B23050400029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 131 | 2023-05-04 | 1572 | keep | 0 | May | 2023 | 0.0010707 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-05-04 09:20 | 2023-05-04 13:08 | 80 | 3:48 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23050400075 | New_Event | Animals | Include | Include | Wildlife | 228 | 2023-05-04 | 18240 | keep | 0 | May | 2023 | 0.012423 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-04 09:24 | 2023-05-04 09:30 | 1368 | 0:06 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO ALIMENTADOR SE VERIFICO CON PERSONAL FUERA SE PROBO QUEDO EN SERVICIO | S23050400061 | Additional_clients | Cutout Failure | Include | Include | Equipment | 6 | 2023-05-04 | 8208 | keep | 0 | May | 2023 | 0.0055904 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-04 09:27 | 2023-05-04 09:29 | 513 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE PROBO QUEDO EN SERVICIO 20% POR 1118-10 | S23050400061 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-04 | 1026 | keep | 0 | May | 2023 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-05-04 09:27 | 2023-05-04 09:29 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE PROBO QUEDO EN SERVICIO LLEVA 20% DEL 1111-01 | S23050400061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-04 | 5564 | keep | 0 | May | 2023 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
BAYAMON | 2023-05-04 09:30 | 2023-05-04 10:45 | 6 | 1:15 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA Y PARARRAYO | S23050400045 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 75 | 2023-05-04 | 450 | keep | 0 | May | 2023 | 0.00030649 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-04 09:30 | 2023-05-04 13:18 | 20 | 3:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA | S23050400065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 228 | 2023-05-04 | 4560 | keep | 0 | May | 2023 | 0.0031058 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-04 09:33 | 2023-05-04 10:38 | 3 | 1:05 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23050400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 65 | 2023-05-04 | 195 | keep | 0 | May | 2023 | 0.00013281 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2023-05-04 09:46 | 2023-05-04 16:40 | 200 | 6:54 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050400036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2023-05-04 | 82800 | keep | 0 | May | 2023 | 0.056395 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
GUAYAMA | 2023-05-04 09:56 | 2023-05-04 12:04 | 15 | 2:08 | P | DESGANCHE | DESGANCHE 1 X 80 EN CORTE DE LINEA | P23050400182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-05-04 | 1920 | keep | 0 | May | 2023 | 0.0013077 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-05-04 10:21 | 2023-05-04 12:13 | 150 | 1:52 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE CON AVE | C23050400095 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-05-04 | 16800 | keep | 0 | May | 2023 | 0.011442 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-05-04 10:29 | 2023-05-04 10:30 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 800 CLIENTES POR EL 3205-07 | C23050400097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 4830 | keep | 0 | May | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
HUMACAO | 2023-05-04 10:29 | 2023-05-04 10:35 | 2126 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C23050400096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-05-04 | 12756 | keep | 0 | May | 2023 | 0.0086881 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-05-04 10:32 | 2023-05-04 17:39 | 1089 | 7:07 | T | CONDUCTOR ARRIADO O CRUZADO | SE RETEZO CONDUCTORES DEL TRONCAL QUE ESTABAN AL ALCANCE DA LA MANO | C23050400099 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 427 | 2023-05-04 | 465003 | keep | 0 | May | 2023 | 0.31671 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
CAGUAS | 2023-05-04 10:34 | 2023-05-04 20:34 | 32 | 10:00 | P | DESGANCHE | 1 X 50 EN C/L | C23050400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 600 | 2023-05-04 | 19200 | keep | 0 | May | 2023 | 0.013077 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2023-05-04 10:35 | 2023-05-04 15:40 | 109 | 5:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | S23050400083 | New_Event | Cutout Failure | Include | Include | Equipment | 305 | 2023-05-04 | 33245 | keep | 0 | May | 2023 | 0.022643 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
MAYAGÃœEZ | 2023-05-04 10:37 | 2023-05-04 14:20 | 40 | 3:43 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23050400063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 223 | 2023-05-04 | 8920 | keep | 0 | May | 2023 | 0.0060754 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-05-04 10:37 | 2023-05-04 19:05 | 8 | 8:28 | P | TRANSFORMADOR AVERIADO | REMPLAZAR TRANSFORMADOR AVERIADO DE 5 KVA POR 37.5 KVA | A23050400047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 508 | 2023-05-04 | 4064 | keep | 0 | May | 2023 | 0.002768 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-05-04 10:44 | 2023-05-04 14:50 | 60 | 4:06 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050400048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 246 | 2023-05-04 | 14760 | keep | 0 | May | 2023 | 0.010053 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-04 10:45 | 2023-05-04 10:46 | 1894 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR EN SERVICIO | R23050400037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 1894 | keep | 0 | May | 2023 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2023-05-04 10:46 | 2023-05-04 11:23 | 12 | 0:37 | P | CABLE SOTERRADO AVERIADO | 1 X 15 RBA EN SU-15 @ T-57 | R23050300066 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 37 | 2023-05-04 | 444 | keep | 0 | May | 2023 | 0.00030241 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-04 10:56 | 2023-05-04 13:41 | 361 | 2:45 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23050400090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-05-04 | 59565 | keep | 0 | May | 2023 | 0.040569 | 0.00024588 | Sustained | FALSE | FALSE | Not_TMED_Event | 361
CANOVANAS | 2023-05-04 11:08 | 2023-05-04 13:26 | 138 | 2:18 | P | ANIMAL | 1 X 50 Y 1 X 40 EN C/L CRUCE POR AVE | R23050400040 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-05-04 | 19044 | keep | 0 | May | 2023 | 0.012971 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
CANOVANAS | 2023-05-04 11:11 | 2023-05-04 12:17 | 47 | 1:06 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL PARA LEVANTAR CONDUCTOR EN EL SUELO | R23050400041 | New_Event | Primary Wire Break | Include | Include | Equipment | 66 | 2023-05-04 | 3102 | keep | 0 | May | 2023 | 0.0021128 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CAGUAS | 2023-05-04 11:20 | 2023-05-04 18:19 | 86 | 6:59 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L Y 1 X 10 EN XMR RAYO | C23050400113 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 419 | 2023-05-04 | 36034 | keep | 0 | May | 2023 | 0.024543 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
CANOVANAS | 2023-05-04 11:23 | 2023-05-04 11:24 | 1894 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR EN SERVICIO | R2305040000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 1894 | keep | 0 | May | 2023 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2023-05-04 11:24 | 2023-05-04 12:07 | 15 | 0:43 | P | CABLE SOTERRADO AVERIADO | 1 X 15 RBA EN SU-15 @ T-57 | R23050300066 | Additional_clients | UG Cable Fault | Include | Include | Equipment | 43 | 2023-05-04 | 645 | keep | 0 | May | 2023 | 0.00043931 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-04 11:35 | 2023-05-04 11:45 | 1381 | 0:10 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE VERIFICO PERSONAL FUERA SE PROBO QUEDO EN SERVICIO | S23050400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-05-04 | 13810 | keep | 0 | May | 2023 | 0.0094059 | 0.00094059 | Sustained | FALSE | FALSE | Not_TMED_Event | 1381
BARRANQUITAS | 2023-05-04 11:42 | 2023-05-04 14:42 | 165 | 3:00 | P | DESGANCHE | 2 X 50 Y 1 X 65 EN C/L | C23050400121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-05-04 | 29700 | keep | 0 | May | 2023 | 0.020229 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
SAN JUAN | 2023-05-04 11:45 | 2023-05-04 22:15 | 12 | 10:30 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO AVERIADO DEL T-37 @ T-38 GOI SJ-230504-01 | S23050400005 | New_Event | UG Cable Fault | Include | Include | Equipment | 630 | 2023-05-04 | 7560 | keep | 0 | May | 2023 | 0.0051491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-04 11:59 | 2023-05-04 18:12 | 50 | 6:13 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23050400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-05-04 | 18650 | keep | 0 | May | 2023 | 0.012702 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-04 12:07 | 2023-05-04 21:28 | 12 | 9:21 | P | CABLE SOTERRADO AVERIADO | SE INSTALO PROVISIONAL AEREO DE T-59 @ T-58 | R23050300066 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 561 | 2023-05-04 | 6732 | keep | 0 | May | 2023 | 0.0045851 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-05-04 12:08 | 2023-05-04 15:00 | 25 | 2:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23050400061 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 172 | 2023-05-04 | 4300 | keep | 0 | May | 2023 | 0.0029287 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-05-04 12:23 | 2023-05-04 14:14 | 1 | 1:51 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | C23050400129 | New_Event | Primary Wire Break | Include | Include | Equipment | 111 | 2023-05-04 | 111 | keep | 0 | May | 2023 | 7.5602e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-04 12:33 | 2023-05-04 16:35 | 45 | 4:02 | P | DESGANCHE | 1 X 65 EN C/L | C23050400132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 242 | 2023-05-04 | 10890 | keep | 0 | May | 2023 | 0.0074171 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-05-04 12:34 | 2023-05-04 18:54 | 1 | 6:20 | P | ANIMAL | 1X25 EN C/L Y 1X15 EN BANCO DE XMRS CRUCE POR AVE | B23050400061 | New_Event | Animals | Include | Include | Wildlife | 380 | 2023-05-04 | 380 | keep | 0 | May | 2023 | 0.00025882 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-04 12:45 | 2023-05-04 14:24 | 150 | 1:39 | P | DESGANCHE | 2 X 50 Y 2 X 40 EN C/L | C23050400137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-05-04 | 14850 | keep | 0 | May | 2023 | 0.010114 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-05-04 12:45 | 2023-05-04 15:05 | 40 | 2:20 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | M23050400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-05-04 | 5600 | keep | 0 | May | 2023 | 0.0038141 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-05-04 12:54 | 2023-05-04 18:40 | 1 | 5:46 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE TRANSFORMADORES NO SE ENCONTRO CAUSA | M23050400097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 346 | 2023-05-04 | 346 | keep | 0 | May | 2023 | 0.00023566 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-04 12:58 | 2023-05-04 16:42 | 269 | 3:44 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23050400130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-05-04 | 60256 | keep | 0 | May | 2023 | 0.04104 | 0.00018321 | Sustained | FALSE | FALSE | Not_TMED_Event | 269
SAN JUAN | 2023-05-04 13:15 | 2023-05-04 15:00 | 14 | 1:45 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE RELOCALIZO LINEA QUE ESTABA EN POSTE PARTIDO DE COMUNICACIONES | S23050400131 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 105 | 2023-05-04 | 1470 | keep | 0 | May | 2023 | 0.0010012 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-05-04 13:21 | 2023-05-04 13:35 | 8 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABREN CAJAS EN TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | A23050400072 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-05-04 | 112 | keep | 0 | May | 2023 | 7.6283e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-05-04 13:23 | 2023-05-04 16:25 | 15 | 3:02 | P | CABLE SOTERRADO AVERIADO | 1 SMU 20 X 20 SE REPARO AVERIA SOTERRADA DE SU-2 A T-5 | R23050400053 | New_Event | UG Cable Fault | Include | Include | Equipment | 182 | 2023-05-04 | 2730 | keep | 0 | May | 2023 | 0.0018594 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-04 13:27 | 2023-05-04 15:46 | 110 | 2:19 | P | ANIMAL | 1 X 65 Y 1 X 50 EN C/L CRUCE X AVE | R23050400055 | New_Event | Animals | Include | Include | Wildlife | 139 | 2023-05-04 | 15290 | keep | 0 | May | 2023 | 0.010414 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
GUAYAMA | 2023-05-04 13:35 | 2023-05-04 13:36 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050400224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 449 | keep | 0 | May | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
BAYAMON | 2023-05-04 13:47 | 2023-05-04 15:01 | 40 | 1:14 | P | ANIMAL | 1X15 EN C/L CRUCE XPOR AVE | B23050400074 | New_Event | Animals | Include | Include | Wildlife | 74 | 2023-05-04 | 2960 | keep | 0 | May | 2023 | 0.002016 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-04 13:58 | 2023-05-04 15:26 | 12 | 1:28 | P | ANIMAL | 1 X 50 EN C/L CURCE X AVE | R23050400061 | New_Event | Animals | Include | Include | Wildlife | 88 | 2023-05-04 | 1056 | keep | 0 | May | 2023 | 0.00071924 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-04 14:18 | 2023-05-04 16:50 | 7 | 2:32 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR REMPLAZO BUSHING SECUNDARIO DE XMR | C23050400163 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2023-05-04 | 1064 | keep | 0 | May | 2023 | 0.00072469 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-04 14:19 | 2023-05-04 14:20 | 1452 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | S2305040000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-04 | 1452 | keep | 0 | May | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-05-04 14:19 | 2023-05-04 15:58 | 65 | 1:39 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23050400145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-05-04 | 6435 | keep | 0 | May | 2023 | 0.0043828 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-05-04 14:20 | 2023-05-04 16:07 | 13 | 1:47 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23050400146 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-05-04 | 1391 | keep | 0 | May | 2023 | 0.0009474 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2023-05-04 14:47 | 2023-05-04 17:10 | 5 | 2:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23050400084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-05-04 | 715 | keep | 0 | May | 2023 | 0.00048698 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-04 14:56 | 2023-05-04 18:11 | 50 | 3:15 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23050400159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-05-04 | 9750 | keep | 0 | May | 2023 | 0.0066407 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-05-04 15:05 | 2023-05-04 16:55 | 125 | 1:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-05-04 | 13750 | keep | 0 | May | 2023 | 0.0093651 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CAGUAS | 2023-05-04 15:11 | 2023-05-04 17:48 | 50 | 2:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23050400182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 157 | 2023-05-04 | 7850 | keep | 0 | May | 2023 | 0.0053466 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-05-04 15:13 | 2023-05-04 18:00 | 12 | 2:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P23050400239 | New_Event | Cutout Failure | Include | Include | Equipment | 167 | 2023-05-04 | 2004 | keep | 0 | May | 2023 | 0.0013649 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-05-04 15:17 | 2023-05-04 16:59 | 60 | 1:42 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE | M23050400142 | New_Event | Animals | Include | Include | Wildlife | 102 | 2023-05-04 | 6120 | keep | 0 | May | 2023 | 0.0041683 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-04 15:20 | 2023-05-04 17:37 | 300 | 2:17 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA PRINCIPAL 1 X 80 EN C/L Y 1 X 50 EN C/L DESGANCHE | S23050400168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-05-04 | 41100 | keep | 0 | May | 2023 | 0.027993 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2023-05-04 15:25 | 2023-05-04 18:20 | 45 | 2:55 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23050400185 | New_Event | Animals | Include | Include | Wildlife | 175 | 2023-05-04 | 7875 | keep | 0 | May | 2023 | 0.0053636 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-05-04 15:40 | 2023-05-04 17:00 | 3 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA PASAR LINEAS A POSTE NUEVO | M23050400146 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-05-04 | 240 | keep | 0 | May | 2023 | 0.00016346 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-04 15:43 | 2023-05-04 18:44 | 30 | 3:01 | P | ANIMAL | 1X65 EN C/L PRINCIPAL 1X50 EN PROVISIONAL AEREO CRUCE POR AVE | B23050400094 | New_Event | Animals | Include | Include | Wildlife | 181 | 2023-05-04 | 5430 | keep | 0 | May | 2023 | 0.0036983 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-04 15:50 | 2023-05-04 16:14 | 50 | 0:24 | P | ARBOL SOBRE LINEA | 3 X 100 EN C/L SE REMOVIO ARBOL ENCIMA DE LAS LINEAS | R23050400070 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 24 | 2023-05-04 | 1200 | keep | 0 | May | 2023 | 0.00081731 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-04 15:54 | 2023-05-04 16:46 | 10 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR SECUNDARIA QUEMADA | B23050400096 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-05-04 | 520 | keep | 0 | May | 2023 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-04 16:04 | 2023-05-04 17:20 | 7 | 1:16 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050400100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-05-04 | 532 | keep | 0 | May | 2023 | 0.00036234 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-04 16:05 | 2023-05-04 18:21 | 83 | 2:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L | S23050400183 | New_Event | Cutout Failure | Include | Include | Equipment | 136 | 2023-05-04 | 11288 | keep | 0 | May | 2023 | 0.0076882 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
FAJARDO | 2023-05-04 16:15 | 2023-05-04 19:12 | 40 | 2:57 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23050400081 | New_Event | Animals | Include | Include | Wildlife | 177 | 2023-05-04 | 7080 | keep | 0 | May | 2023 | 0.0048222 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-04 16:20 | 2023-05-04 16:21 | 3701 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23050400199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 3701 | keep | 0 | May | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
FAJARDO | 2023-05-04 16:22 | 2023-05-04 18:41 | 29 | 2:19 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R23050400082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-04 | 4031 | keep | 0 | May | 2023 | 0.0027455 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
GUAYAMA | 2023-05-04 16:30 | 2023-05-04 17:00 | 40 | 0:30 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23050400253 | New_Event | Animals | Include | Include | Wildlife | 30 | 2023-05-04 | 1200 | keep | 0 | May | 2023 | 0.00081731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-05-04 16:59 | 2023-05-04 17:00 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | M23050400158 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-04 | 4304 | keep | 0 | May | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
MAYAGÃœEZ | 2023-05-04 17:00 | 2023-05-05 10:35 | 60 | 17:35 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE | M23050400142 | Partial_restoration | Animals | Include | Include | Wildlife | 1055 | 2023-05-04 | 63300 | keep | 0 | May | 2023 | 0.043113 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-04 17:06 | 2023-05-04 17:08 | 1802 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S23050400204 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-04 | 3604 | keep | 0 | May | 2023 | 0.0024547 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
SAN JUAN | 2023-05-04 17:08 | 2023-05-04 19:44 | 47 | 2:36 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE MACHETE A LINEA | S23050400205 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 156 | 2023-05-04 | 7332 | keep | 0 | May | 2023 | 0.0049938 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BARRANQUITAS | 2023-05-04 17:10 | 2023-05-05 14:02 | 1 | 20:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | C23050400215 | New_Event | Cutout Failure | Include | Include | Equipment | 1252 | 2023-05-04 | 1252 | keep | 0 | May | 2023 | 0.00085273 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-04 17:36 | 2023-05-04 22:45 | 100 | 5:09 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23050400166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 309 | 2023-05-04 | 30900 | keep | 0 | May | 2023 | 0.021046 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-04 17:39 | 2023-05-05 10:11 | 40 | 16:32 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23050400219 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 992 | 2023-05-04 | 39680 | keep | 0 | May | 2023 | 0.027026 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-05-04 17:41 | 2023-05-04 17:44 | 817 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO POR CONTROL | C2305040000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-04 | 2451 | keep | 0 | May | 2023 | 0.0016694 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
SAN JUAN | 2023-05-04 18:09 | 2023-05-04 21:11 | 40 | 3:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMIARIA | S23050400237 | New_Event | Cutout Failure | Include | Include | Equipment | 182 | 2023-05-04 | 7280 | keep | 0 | May | 2023 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-05-04 18:33 | 2023-05-04 22:00 | 8 | 3:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23050400113 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2023-05-04 | 1656 | keep | 0 | May | 2023 | 0.0011279 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-05-04 18:54 | 2023-05-05 06:56 | 996 | 12:02 | P | TERMINACION SOTERRADA AVERIADA | AVERIA EN MH-80 SE HICIERON MANIOBRAS Y SOLO QUEDAN 4 CLIENTES COMERCIALES FUERA DE SERVICIO | P23050400280 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 722 | 2023-05-04 | 719112 | keep | 0 | May | 2023 | 0.48978 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
MAYAGÃœEZ | 2023-05-04 18:58 | 2023-05-04 20:40 | 100 | 1:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | M23050400181 | New_Event | Primary Wire Break | Include | Include | Equipment | 102 | 2023-05-04 | 10200 | keep | 0 | May | 2023 | 0.0069472 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-04 19:05 | 2023-05-05 09:46 | 22 | 14:41 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | C23050400233 | New_Event | Primary Wire Break | Include | Include | Equipment | 881 | 2023-05-04 | 19382 | keep | 0 | May | 2023 | 0.013201 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2023-05-04 19:09 | 2023-05-05 07:46 | 48 | 12:37 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | C23050400023 | New_Event | Animals | Include | Include | Wildlife | 757 | 2023-05-04 | 36336 | keep | 0 | May | 2023 | 0.024748 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
BAYAMON | 2023-05-04 19:20 | 2023-05-05 10:51 | 79 | 15:31 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23050400126 | New_Event | Animals | Include | Include | Wildlife | 931 | 2023-05-04 | 73549 | keep | 0 | May | 2023 | 0.050094 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2023-05-04 19:23 | 2023-05-05 15:12 | 50 | 19:49 | P | CONDUCTOR ROTO O ABIERTO | 1X100 EN C/L Y 2X65 EN OTRO C/L SE REPARO BAJANTE PRIMARIO | S23050400256 | New_Event | Primary Wire Break | Include | Include | Equipment | 1189 | 2023-05-04 | 59450 | keep | 0 | May | 2023 | 0.040491 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-04 19:39 | 2023-05-04 23:38 | 300 | 3:59 | P | PARARRAYOS DEFECTUOSO | 2 X 80 EN C/L SE ELIMINO PARARAYO | B23050400130 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 239 | 2023-05-04 | 71700 | keep | 0 | May | 2023 | 0.048835 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-05-04 19:51 | 2023-05-05 17:15 | 15 | 21:24 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE LINEA A CAJA DE XMR | S23050400265 | New_Event | Primary Wire Break | Include | Include | Equipment | 1284 | 2023-05-04 | 19260 | keep | 0 | May | 2023 | 0.013118 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-04 20:28 | 2023-05-04 23:35 | 759 | 3:07 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE NO FUNDIO | C23050400248 | New_Event | Primary Wire Break | Include | Include | Equipment | 187 | 2023-05-04 | 141933 | keep | 0 | May | 2023 | 0.09667 | 0.00051695 | Sustained | FALSE | FALSE | Not_TMED_Event | 759
CANOVANAS | 2023-05-04 20:32 | 2023-05-05 08:53 | 1 | 12:21 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R23050400097 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 741 | 2023-05-04 | 741 | keep | 0 | May | 2023 | 0.00050469 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-04 20:34 | 2023-05-04 23:11 | 3387 | 2:37 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO Y SE CERRO BKR EN SERVICIO 60% DE SU CARGA | B23050400142 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2023-05-04 | 531759 | keep | 0 | May | 2023 | 0.36218 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
CANOVANAS | 2023-05-04 20:41 | 2023-05-04 21:09 | 6 | 0:28 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | R23050400098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2023-05-04 | 168 | keep | 0 | May | 2023 | 0.00011442 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-04 20:51 | 2023-05-04 22:41 | 2231 | 1:50 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR SECUNDARIO DE SUBESTACION PORTATIL #3 INTERRUPTOR 8401-03 AVERIADO | A23050400159 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 110 | 2023-05-04 | 245410 | keep | 0 | May | 2023 | 0.16715 | 0.0015195 | Sustained | FALSE | FALSE | Not_TMED_Event | 2231
VEGA BAJA | 2023-05-04 20:51 | 2023-05-04 22:41 | 1923 | 1:50 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR SECUNDARIO DE SUBESTACION PORTATIL #3 INTERRUPTOR 8401-03 AVERIADO | A23050400159 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 110 | 2023-05-04 | 211530 | keep | 0 | May | 2023 | 0.14407 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-05-04 20:51 | 2023-05-04 22:41 | 1066 | 1:50 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR SECUNDARIO DE SUBESTACION PORTATIL #3 INTERRUPTOR 8401-03 AVERIADO | A23050400159 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 110 | 2023-05-04 | 117260 | keep | 0 | May | 2023 | 0.079865 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
VEGA BAJA | 2023-05-04 20:51 | 2023-05-04 22:41 | 141 | 1:50 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | DISPARO DE INTERRUPTOR SECUNDARIO DE SUBESTACION PORTATIL #3 INTERRUPTOR 8401-03 AVERIADO | A23050400159 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 110 | 2023-05-04 | 15510 | keep | 0 | May | 2023 | 0.010564 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
BAYAMON | 2023-05-04 21:40 | 2023-05-05 12:07 | 150 | 14:27 | P | DESGANCHE | 2X50 EN C/L DESGANCHE | B23050400188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 867 | 2023-05-04 | 130050 | keep | 0 | May | 2023 | 0.088576 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
GUAYAMA | 2023-05-04 21:59 | 2023-05-05 05:00 | 130 | 7:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO UTILIZANDO CAJA PORTATIL | P23050400351 | New_Event | Primary Wire Break | Include | Include | Equipment | 421 | 2023-05-04 | 54730 | keep | 0 | May | 2023 | 0.037276 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
BARRANQUITAS | 2023-05-04 22:27 | 2023-05-05 14:50 | 138 | 16:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA EN C/L | C23050400276 | New_Event | Primary Wire Break | Include | Include | Equipment | 983 | 2023-05-04 | 135654 | keep | 0 | May | 2023 | 0.092393 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
VEGA BAJA | 2023-05-04 22:41 | 2023-05-05 02:23 | 1066 | 3:42 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO. INTERRUPTOR PASO LA AVERIA AL INTERRUPTOR DE SUBESTACION PORTATIL. SE PASO LA CARGA AL 8401-02 | A23050400231 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-05-04 | 236652 | keep | 0 | May | 2023 | 0.16118 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
SAN JUAN | 2023-05-04 23:01 | 2023-05-05 18:20 | 31 | 19:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO DE CAJA PRIMARIA | S23050400296 | New_Event | Cutout Failure | Include | Include | Equipment | 1159 | 2023-05-04 | 35929 | keep | 0 | May | 2023 | 0.024471 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
VEGA BAJA | 2023-05-04 23:11 | 2023-05-04 23:32 | 1185 | 0:21 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR Y SE TRANSFIRIO EL 35% DE SU CARGA AL 8404-04 | B23050400142 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 21 | 2023-05-04 | 24885 | keep | 0 | May | 2023 | 0.016949 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-05-04 23:17 | 2023-05-05 09:40 | 40 | 10:23 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A23050400235 | New_Event | Animals | Include | Include | Wildlife | 623 | 2023-05-04 | 24920 | keep | 0 | May | 2023 | 0.016973 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-04 23:32 | 2023-05-05 01:40 | 169 | 2:08 | P | CONDUCTOR ROTO O ABIERTO | CON GOI BY-230504-02 SE REPARO CONDUCTOR PRIMARIO Y SE NORMALIZARON LAS CARGAS ENTRO EN SERVICIO 5% DE SU CARGA | B23050400142 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 128 | 2023-05-04 | 21632 | keep | 0 | May | 2023 | 0.014733 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-05-05 00:23 | 2023-05-05 11:05 | 50 | 10:42 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 642 | 2023-05-05 | 32100 | keep | 0 | May | 2023 | 0.021863 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-05-05 00:32 | 2023-05-05 19:35 | 28 | 19:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR NO FUNDIO FUSIBLE | R23050500001 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1143 | 2023-05-05 | 32004 | keep | 0 | May | 2023 | 0.021798 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
HUMACAO | 2023-05-05 04:56 | 2023-05-05 07:56 | 40 | 3:00 | P | DESGANCHE | 1 X 30 EN C/L | C23050500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-05-05 | 7200 | keep | 0 | May | 2023 | 0.0049039 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-05 05:09 | 2023-05-05 05:10 | 2364 | 0:01 | T | CAUSAS EXTERNAS | SE CERRO POR CONTROL | S23050500015 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-05-05 | 2364 | keep | 0 | May | 2023 | 0.0016101 | 0.0016101 | Momentary | FALSE | FALSE | Not_TMED_Event | 2364
BARRANQUITAS | 2023-05-05 05:09 | 2023-05-05 11:30 | 40 | 6:21 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN C/L Y SE ELIMINO PARARRAYO | C23050500011 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 381 | 2023-05-05 | 15240 | keep | 0 | May | 2023 | 0.01038 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-05 05:15 | 2023-05-05 06:41 | 2364 | 1:26 | T | CAUSAS EXTERNAS | SE SECCIONALIZO AVERIA POR POSTE PRIMARIO IMPACTADO POR AUTOMOVIL PRIVADO EN MARCHA GOI BY-230505-01 - 40% EN SERVICIO | S23050500020 | 1st_after_momentary | Damage From Public | Include | Include | Public | 86 | 2023-05-05 | 203304 | keep | 0 | May | 2023 | 0.13847 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
CANOVANAS | 2023-05-05 05:16 | 2023-05-05 17:55 | 21 | 12:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y 1 X 15 EN XMR | R23050500016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 759 | 2023-05-05 | 15939 | keep | 0 | May | 2023 | 0.010856 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BARRANQUITAS | 2023-05-05 05:20 | 2023-05-05 07:23 | 40 | 2:03 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23050500013 | New_Event | Animals | Include | Include | Wildlife | 123 | 2023-05-05 | 4920 | keep | 0 | May | 2023 | 0.003351 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-05 06:00 | 2023-05-05 07:42 | 40 | 1:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23050500022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2023-05-05 | 4080 | keep | 0 | May | 2023 | 0.0027789 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-05 06:41 | 2023-05-05 14:30 | 1418 | 7:49 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTE PRIMARIO IMPACTADO POR AUTOMOVIL PRIVADO EN MARCHA GOI BY-230505-01 - 100% EN SERVICIO | S23050500020 | Partial_restoration | Damage From Public | Include | Include | Public | 469 | 2023-05-05 | 665042 | keep | 0 | May | 2023 | 0.45296 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-05 06:42 | 2023-05-05 13:00 | 40 | 6:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050500008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 378 | 2023-05-05 | 15120 | keep | 0 | May | 2023 | 0.010298 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-05 06:51 | 2023-05-05 07:06 | 1 | 0:15 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | B23050500055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 15 | 2023-05-05 | 15 | keep | 0 | May | 2023 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-05 06:56 | 2023-05-05 06:58 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO POR SCADA | C23050500039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-05 | 3758 | keep | 0 | May | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
PONCE | 2023-05-05 06:56 | 2023-05-05 10:40 | 4 | 3:44 | P | TERMINACION SOTERRADA AVERIADA | SE CORRIGIO AVERIA EN MH 80 PISTOLA DE 200A Y BARRAS SECAS | P23050500033 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 224 | 2023-05-05 | 896 | keep | 0 | May | 2023 | 0.00061026 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-05 07:04 | 2023-05-05 09:15 | 20 | 2:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23050500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 131 | 2023-05-05 | 2620 | keep | 0 | May | 2023 | 0.0017845 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-05 07:13 | 2023-05-05 07:14 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2305050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-05-05 07:22 | 2023-05-05 07:41 | 30 | 0:19 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | B23050500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-05-05 | 570 | keep | 0 | May | 2023 | 0.00038822 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-05 07:25 | 2023-05-05 14:54 | 1 | 7:29 | P | DESGANCHE | 1 X 15 EN XMR Y 1X 25 EN C/L DESGANCHE | R23050500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 449 | 2023-05-05 | 449 | keep | 0 | May | 2023 | 0.00030581 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-05 07:25 | 2023-05-06 14:18 | 1 | 30:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN RISER SE REEMPLAZO CAJA PRIMARIA QUEMADA REFERENCIA EVENTO P23050500194 | P23050500037 | New_Event | Cutout Failure | Include | Include | Equipment | 1853 | 2023-05-05 | 1853 | keep | 0 | May | 2023 | 0.0012621 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-05 07:30 | 2023-05-05 10:28 | 40 | 2:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23050500012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-05-05 | 7120 | keep | 0 | May | 2023 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-05-05 07:37 | 2023-05-05 12:46 | 32 | 5:09 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | P23050500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2023-05-05 | 9888 | keep | 0 | May | 2023 | 0.0067347 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
GUAYAMA | 2023-05-05 08:02 | 2023-05-05 08:03 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 4279 | keep | 0 | May | 2023 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
CANOVANAS | 2023-05-05 08:20 | 2023-05-05 10:00 | 86 | 1:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA LLUVIA Y VIENTO | R23050500012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 100 | 2023-05-05 | 8600 | keep | 0 | May | 2023 | 0.0058574 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
GUAYAMA | 2023-05-05 08:42 | 2023-05-05 16:04 | 1 | 7:22 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA Y SE LEVANTARON ALAMBRES PRIMARIOS | P23050500155 | New_Event | Primary Wire Break | Include | Include | Equipment | 442 | 2023-05-05 | 442 | keep | 0 | May | 2023 | 0.00030104 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-05 08:42 | 2023-05-05 10:45 | 3 | 2:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050500014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-05-05 | 369 | keep | 0 | May | 2023 | 0.00025132 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-05-05 09:15 | 2023-05-05 10:25 | 7 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR REMPLAZO BARRAS SECUNDARIAS | M23050500015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-05-05 | 490 | keep | 0 | May | 2023 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-05-05 09:18 | 2023-05-05 09:19 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 2354 | keep | 0 | May | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
SAN JUAN | 2023-05-05 09:19 | 2023-05-05 09:28 | 1825 | 0:09 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SU CARGA POR 1118-09 SE VERIFICO CON PERSONAL QUE TENIA V.L. PERO NO HABIAN COMENZADO SE PROBO QUEDO EN SERVICIO | S23050500166 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-05-05 | 16425 | keep | 0 | May | 2023 | 0.011187 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-05-05 09:19 | 2023-05-05 09:28 | 4398 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR LLEVA 1118-08 SE VERIFICO CON PERSONAL QUE TENIA V.L. PERO NO HABIAN COMENZADO SE PROBO QUEDO EN SERVICIO | S23050500166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-05-05 | 39582 | keep | 0 | May | 2023 | 0.026959 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
AGUADILLA | 2023-05-05 09:25 | 2023-05-05 13:05 | 1 | 3:40 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23050500020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2023-05-05 | 220 | keep | 0 | May | 2023 | 0.00014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-05 09:29 | 2023-05-05 11:54 | 6 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON BARRAS EN PEDESTAL | C23050500079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-05-05 | 870 | keep | 0 | May | 2023 | 0.00059255 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-05 09:33 | 2023-05-06 10:43 | 25 | 25:10 | P | DESGANCHE | DESGANCHE/1X50/1X65 EN SERVICIO | S23050500184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1510 | 2023-05-05 | 37750 | keep | 0 | May | 2023 | 0.025711 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-05-05 09:50 | 2023-05-06 01:05 | 5 | 15:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230505-50 SE REMPLAZO POSTE PRIMARIO PARTIDO | R23050500031 | New_Event | Primary Pole Failure | Include | Include | Equipment | 915 | 2023-05-05 | 4575 | keep | 0 | May | 2023 | 0.003116 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-05-05 09:50 | 2023-05-06 01:16 | 35 | 15:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SJ-230505-50 SE REMPLAZO POSTE PRIMARIO PARTIDO | R23050500033 | New_Event | Primary Pole Failure | Include | Include | Equipment | 926 | 2023-05-05 | 32410 | keep | 0 | May | 2023 | 0.022074 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-05-05 09:51 | 2023-05-05 10:49 | 12 | 0:58 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN C/L PARA REPARAR NEUTRAL PRIMARIO | B23050500122 | New_Event | Primary Wire Break | Include | Include | Equipment | 58 | 2023-05-05 | 696 | keep | 0 | May | 2023 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-05 10:00 | 2023-05-05 14:50 | 8 | 4:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZO DE POSTE PRIMARIO EN MAL ESTADO 22-003-HC FIONA | S23050500155 | New_Event | Primary Pole Failure | Include | Include | Equipment | 290 | 2023-05-05 | 2320 | keep | 0 | May | 2023 | 0.0015801 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-05 10:18 | 2023-05-05 11:26 | 21 | 1:08 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA | R23050500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-05-05 | 1428 | keep | 0 | May | 2023 | 0.0009726 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2023-05-05 10:18 | 2023-05-05 12:15 | 12 | 1:57 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23050500030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 117 | 2023-05-05 | 1404 | keep | 0 | May | 2023 | 0.00095626 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-05 10:21 | 2023-05-05 11:08 | 10 | 0:47 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR/RELOCALIZAR SECUNDARIA POR POSTE SECUNDARIO PARTIDO EN EL SUELO | C23050500093 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 47 | 2023-05-05 | 470 | keep | 0 | May | 2023 | 0.00032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-05 10:24 | 2023-05-05 10:59 | 2 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA RETIRAR TENSOR SOBRE LINEA SECUNDARIA | R23050500022 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-05-05 | 70 | keep | 0 | May | 2023 | 4.7677e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-05-05 10:24 | 2023-05-05 12:40 | 12 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BARRA EN PEDESTAL SECUNARIO | P23050500083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-05-05 | 1632 | keep | 0 | May | 2023 | 0.0011115 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-05 10:26 | 2023-05-05 11:58 | 1 | 1:32 | P | NO SE REPORTO CAUSA | 2 X 15 EN RISER | R23050500023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2023-05-05 | 92 | keep | 0 | May | 2023 | 6.2661e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-05 10:27 | 2023-05-05 13:09 | 50 | 2:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 EN C/L POR LLUVIAS | S23050500204 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 162 | 2023-05-05 | 8100 | keep | 0 | May | 2023 | 0.0055169 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-05 10:36 | 2023-05-05 13:42 | 9 | 3:06 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZARON BARRAS EN PEDESTAL | C23050500098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 186 | 2023-05-05 | 1674 | keep | 0 | May | 2023 | 0.0011402 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2023-05-05 10:52 | 2023-05-06 10:03 | 1 | 23:11 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRARON PUENTES PRIMARIOS | M23050500094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1391 | 2023-05-05 | 1391 | keep | 0 | May | 2023 | 0.0009474 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-05 11:00 | 2023-05-05 12:51 | 400 | 1:51 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZARON (2) MACHETES PRIMARIOS QUEMADOS MEDIANTE GOI BY-230505-02 (EVENTO CAYO POR REGION BY - ESTA AVERIA ES INDEPENDIENTE A LA DEL EVENTO S23050500020/GOI BY-230505-01) | B23050500128 | New_Event | Switch Failure | Include | Include | Equipment | 111 | 2023-05-05 | 44400 | keep | 0 | May | 2023 | 0.030241 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CANOVANAS | 2023-05-05 11:32 | 2023-05-05 13:17 | 1 | 1:45 | P | CAUSAS EXTERNAS | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO LINEA SECUNDARIA DERRIBADA POR CAMION | R23050500039 | New_Event | Damage From Public | Include | Include | Public | 105 | 2023-05-05 | 105 | keep | 0 | May | 2023 | 7.1515e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-05 11:38 | 2023-05-05 13:08 | 12 | 1:30 | P | ANIMAL | 2 X 20 EN TRANSFORMADOR POR ANIMAL | P23050500110 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-05-05 | 1080 | keep | 0 | May | 2023 | 0.00073558 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-05 11:39 | 2023-05-05 11:40 | 1452 | 0:01 | T | DESGANCHE | RECERRO | S23050500000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-05 | 1452 | keep | 0 | May | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
HUMACAO | 2023-05-05 11:39 | 2023-05-05 13:24 | 31 | 1:45 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | C23050500116 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-05-05 | 3255 | keep | 0 | May | 2023 | 0.002217 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-05-05 11:40 | 2023-05-05 19:24 | 245 | 7:44 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X 100 EN C/L DESGANCHE | S23050500230 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 464 | 2023-05-05 | 113680 | keep | 0 | May | 2023 | 0.077427 | 0.00016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 245
BAYAMON | 2023-05-05 11:40 | 2023-05-05 12:19 | 10 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR/LEVANTAR SECUNDARIA DEL SUELO | B23050500050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-05-05 | 390 | keep | 0 | May | 2023 | 0.00026563 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-05 11:42 | 2023-05-05 13:21 | 12 | 1:39 | P | DESGANCHE | 2X100 EN C/L DESGANCHE | S23050500227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-05-05 | 1188 | keep | 0 | May | 2023 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-05 11:49 | 2023-05-05 11:50 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 75% DEL 1203-03 | S23050500000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 1225 | keep | 0 | May | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-05-05 11:49 | 2023-05-05 11:50 | 462 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 75% POR 1203-01 | S23050500000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-05 | 462 | keep | 0 | May | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
ARECIBO | 2023-05-05 11:49 | 2023-05-05 14:14 | 1 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23050500051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-05-05 | 145 | keep | 0 | May | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-05 12:00 | 2023-05-05 12:01 | 1467 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050500124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 1467 | keep | 0 | May | 2023 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
SAN JUAN | 2023-05-05 12:05 | 2023-05-05 14:53 | 30 | 2:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23050500240 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-05-05 | 5040 | keep | 0 | May | 2023 | 0.0034327 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-05 12:07 | 2023-05-05 14:48 | 12 | 2:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23050500243 | New_Event | Secondary Wire Break | Include | Include | Equipment | 161 | 2023-05-05 | 1932 | keep | 0 | May | 2023 | 0.0013159 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-05-05 12:12 | 2023-05-05 13:33 | 130 | 1:21 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P23050500117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-05-05 | 10530 | keep | 0 | May | 2023 | 0.0071719 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
UTUADO | 2023-05-05 12:15 | 2023-05-05 19:00 | 70 | 6:45 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050500055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2023-05-05 | 28350 | keep | 0 | May | 2023 | 0.019309 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-05-05 12:19 | 2023-05-05 12:20 | 1225 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 75% DEL 1203-03 | S23050500000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 1225 | keep | 0 | May | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-05-05 12:19 | 2023-05-05 12:20 | 462 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 75% POR 1203-01 | S23050500000 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-05 | 462 | keep | 0 | May | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
HUMACAO | 2023-05-05 12:21 | 2023-05-05 14:30 | 7 | 2:09 | P | DESGANCHE | 1 X 40 EN C/L | C23050500127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-05-05 | 903 | keep | 0 | May | 2023 | 0.00061503 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-05 12:23 | 2023-05-05 17:10 | 111 | 4:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN C/L SE REMPLAZO CAJA PRIMARIA | B23050500172 | New_Event | Cutout Failure | Include | Include | Equipment | 287 | 2023-05-05 | 31857 | keep | 0 | May | 2023 | 0.021698 | 7.5602e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 111
MAYAGÃœEZ | 2023-05-05 12:30 | 2023-05-05 18:20 | 50 | 5:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23050500072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 350 | 2023-05-05 | 17500 | keep | 0 | May | 2023 | 0.011919 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-05 12:36 | 2023-05-05 13:37 | 8 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA LEVANTAR LINEA SECUNDARIA | S23050400200 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-05-05 | 488 | keep | 0 | May | 2023 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-05 12:53 | 2023-05-05 14:13 | 45 | 1:20 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | C23050500136 | New_Event | Animals | Include | Include | Wildlife | 80 | 2023-05-05 | 3600 | keep | 0 | May | 2023 | 0.0024519 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CAGUAS | 2023-05-05 13:16 | 2023-05-05 14:17 | 8 | 1:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO NEUTRAL Y LINEA SECUNDARIA | C23050500142 | New_Event | Secondary Wire Break | Include | Include | Equipment | 61 | 2023-05-05 | 488 | keep | 0 | May | 2023 | 0.00033237 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-05-05 13:21 | 2023-05-05 19:39 | 8 | 6:18 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEA ENREDADA | P23050500136 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 378 | 2023-05-05 | 3024 | keep | 0 | May | 2023 | 0.0020596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-05-05 13:33 | 2023-05-05 17:40 | 575 | 4:07 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN TRONCAL DEL ALIMENTADOR SE ABRIO INTERRUPTOR PARA CERRAR PUENTE PRIMARIO | A23050500068 | New_Event | Primary Wire Break | Include | Include | Equipment | 247 | 2023-05-05 | 142025 | keep | 0 | May | 2023 | 0.096733 | 0.00039163 | Sustained | FALSE | FALSE | Not_TMED_Event | 575
MAYAGÃœEZ | 2023-05-05 13:36 | 2023-05-05 15:05 | 1428 | 1:29 | T | NO SE REPORTO CAUSA | DENNYS RUIZ INFORMO QUE PATRULLO EL ALIMENTADOR Y NO ENCONTRO CAUSA PARA EL DISPARO DEL INTERRUPTOR SOLICITO QUE SE LE HICIERA UNA PRUEBA SE CERRO Y QUEDO EN SERVICIO | M23050500087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 89 | 2023-05-05 | 127092 | keep | 0 | May | 2023 | 0.086562 | 0.0009726 | Sustained | FALSE | FALSE | Not_TMED_Event | 1428
BAYAMON | 2023-05-05 13:41 | 2023-05-05 14:20 | 3 | 0:39 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B23050500190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2023-05-05 | 117 | keep | 0 | May | 2023 | 7.9688e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-05-05 13:42 | 2023-05-05 20:23 | 75 | 6:41 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23050500255 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 401 | 2023-05-05 | 30075 | keep | 0 | May | 2023 | 0.020484 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-05-05 13:53 | 2023-05-05 15:20 | 8 | 1:27 | P | CAUSAS EXTERNAS | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS POR MAQUINARIA | M23050500093 | New_Event | Damage From Public | Include | Include | Public | 87 | 2023-05-05 | 696 | keep | 0 | May | 2023 | 0.00047404 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-05 14:02 | 2023-05-06 09:35 | 40 | 19:33 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | M23050500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1173 | 2023-05-05 | 46920 | keep | 0 | May | 2023 | 0.031957 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-05-05 14:10 | 2023-05-05 14:11 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050500153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
PONCE | 2023-05-05 14:10 | 2023-05-05 16:36 | 130 | 2:26 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P2305050152 | New_Event | Animals | Include | Include | Wildlife | 146 | 2023-05-05 | 18980 | keep | 0 | May | 2023 | 0.012927 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
AGUADILLA | 2023-05-05 14:13 | 2023-05-05 14:14 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23050500099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 1827 | keep | 0 | May | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BARRANQUITAS | 2023-05-05 14:25 | 2023-05-05 17:24 | 1 | 2:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 2 X 10 EN MONTURA XMR | C23050500153 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2023-05-05 | 179 | keep | 0 | May | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-05 14:30 | 2023-05-05 16:52 | 16 | 2:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON CONEXIONES SECUNDARIAS | C23050500155 | New_Event | Secondary Wire Break | Include | Include | Equipment | 142 | 2023-05-05 | 2272 | keep | 0 | May | 2023 | 0.0015474 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-05-05 14:36 | 2023-05-05 17:44 | 336 | 3:08 | P | DESGANCHE | 2 X 80 EN C/L SE REALIZO DESGANCHE | C23050500157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-05-05 | 63168 | keep | 0 | May | 2023 | 0.043023 | 0.00022885 | Sustained | FALSE | FALSE | Not_TMED_Event | 336
BAYAMON | 2023-05-05 14:38 | 2023-05-05 16:49 | 25 | 2:11 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23050500303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-05-05 | 3275 | keep | 0 | May | 2023 | 0.0022306 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-05-05 14:43 | 2023-05-05 16:12 | 75 | 1:29 | T | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO SPACER PARTIDO Y PEGADO A AISLADOR. SE PUSO EL BKR EN SERVICIO | P23050500161 | New_Event | Primary Wire Break | Include | Include | Equipment | 89 | 2023-05-05 | 6675 | keep | 0 | May | 2023 | 0.0045463 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-05-05 14:56 | 2023-05-05 15:30 | 7 | 0:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23050500052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 34 | 2023-05-05 | 238 | keep | 0 | May | 2023 | 0.0001621 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-05-05 15:00 | 2023-05-05 16:53 | 8 | 1:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO PORTAFUSIBLE | C23050500161 | New_Event | Cutout Failure | Include | Include | Equipment | 113 | 2023-05-05 | 904 | keep | 0 | May | 2023 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-05 15:06 | 2023-05-05 15:08 | 3295 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23050500207 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-05 | 6590 | keep | 0 | May | 2023 | 0.0044884 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-05-05 15:10 | 2023-05-05 16:03 | 10 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO/LEVANTO SECUNDARIA DEL SUELO | B23050500208 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-05-05 | 530 | keep | 0 | May | 2023 | 0.00036098 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-05-05 15:18 | 2023-05-05 17:36 | 28 | 2:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23050500165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-05-05 | 3864 | keep | 0 | May | 2023 | 0.0026318 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
SAN JUAN | 2023-05-05 15:20 | 2023-05-05 18:36 | 80 | 3:16 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23050500314 | New_Event | Vegetation Contact | Include | Include | Vegetation | 196 | 2023-05-05 | 15680 | keep | 0 | May | 2023 | 0.01068 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-05 15:20 | 2023-05-05 18:27 | 75 | 3:07 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23050500316 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-05-05 | 14025 | keep | 0 | May | 2023 | 0.0095524 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2023-05-05 15:23 | 2023-05-05 15:24 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050500166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 1746 | keep | 0 | May | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
ARECIBO | 2023-05-05 15:29 | 2023-05-05 16:40 | 50 | 1:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050500114 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-05-05 | 3550 | keep | 0 | May | 2023 | 0.0024179 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-05 15:31 | 2023-05-05 19:01 | 25 | 3:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA NO FUNDIO | B23050500213 | New_Event | Cutout Failure | Include | Include | Equipment | 210 | 2023-05-05 | 5250 | keep | 0 | May | 2023 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-05 15:33 | 2023-05-05 15:34 | 3041 | 0:01 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23050500123 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1 | 2023-05-05 | 3041 | keep | 0 | May | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2023-05-05 15:34 | 2023-05-05 20:00 | 40 | 4:26 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADORES | M23050500135 | 1st_after_momentary | Insulator/ Pin Failure | Include | Include | Equipment | 266 | 2023-05-05 | 10640 | keep | 0 | May | 2023 | 0.0072469 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-05 15:36 | 2023-05-05 15:56 | 14 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | B23050500216 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-05-05 | 280 | keep | 0 | May | 2023 | 0.00019071 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-05-05 15:45 | 2023-05-05 15:46 | 2266 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23050500105 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 2266 | keep | 0 | May | 2023 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-05-05 15:46 | 2023-05-05 18:59 | 755 | 3:13 | P | DESGANCHE | LINEA PRIMARIA PARTIDA EN TRONCAL DEL ALIMENTADOR DEBIDO A DESGANCHE SE ABRIO INTERRUPTOR PARA REPARAR | A23050500125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 193 | 2023-05-05 | 145715 | keep | 0 | May | 2023 | 0.099246 | 0.00051423 | Sustained | FALSE | FALSE | Not_TMED_Event | 755
SAN JUAN | 2023-05-05 16:20 | 2023-05-05 16:50 | 5 | 0:30 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REEMPLAZO PEDESTAL | S23050500330 | New_Event |  |  |  |  | 30 | 2023-05-05 | 150 | keep | 0 | May | 2023 | 0.00010216 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-05 16:30 | 2023-05-05 18:56 | 100 | 2:26 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23050500339 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-05-05 | 14600 | keep | 0 | May | 2023 | 0.009944 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-05 16:31 | 2023-05-05 16:36 | 3630 | 0:05 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR CON EL RECIERRE EN OFF SE VERIFICO PERSONAL FUERA DE LAS LINEAS Y SE CERRO EL INTERRUPTOR | M23050500145 | New_Event | Cutout Failure | Include | Include | Equipment | 5 | 2023-05-05 | 18150 | keep | 0 | May | 2023 | 0.012362 | 0.0024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 3630
MAYAGÃœEZ | 2023-05-05 16:35 | 2023-05-05 17:00 | 20 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23050500127 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-05 | 500 | keep | 0 | May | 2023 | 0.00034055 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 874 | 1:14 | P | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 3604-06 LLEVA 20% 3010-01 | C23050500180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 64676 | keep | 0 | May | 2023 | 0.044051 | 0.00059528 | Sustained | FALSE | FALSE | Not_TMED_Event | 874
BARRANQUITAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 1565 | 1:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C23050500178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 115810 | keep | 0 | May | 2023 | 0.078878 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 976 | 1:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C23050500178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 72224 | keep | 0 | May | 2023 | 0.049191 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 548 | 1:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C23050500178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 40552 | keep | 0 | May | 2023 | 0.02762 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 315 | 1:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C23050500179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 23310 | keep | 0 | May | 2023 | 0.015876 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 870 | 1:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 | C23050500179 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 64380 | keep | 0 | May | 2023 | 0.043849 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 2906 | 1:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 3604-06 LLEVA 20% 3010-01 | C23050500180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 215044 | keep | 0 | May | 2023 | 0.14647 | 0.0019793 | Sustained | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-05 16:36 | 2023-05-05 17:50 | 2343 | 1:14 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 800 3604-06 LLEVA 20% 3010-01 | C23050500180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 74 | 2023-05-05 | 173382 | keep | 0 | May | 2023 | 0.11809 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
MAYAGÃœEZ | 2023-05-05 16:36 | 2023-05-06 09:40 | 1 | 17:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN RISER SE REMPLAZARON DOS CAJAS PRIMARIAS EN RISER | M23050500154 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 1024 | 2023-05-05 | 1024 | keep | 0 | May | 2023 | 0.00069744 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-05 16:39 | 2023-05-05 20:15 | 20 | 3:36 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 65 EN CORTE DE LINEA SE SECCIONALIZO POSTE PRIMARIO | M23050500147 | New_Event | Primary Pole Failure | Include | Include | Equipment | 216 | 2023-05-05 | 4320 | keep | 0 | May | 2023 | 0.0029423 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-05-05 16:51 | 2023-05-05 18:37 | 25 | 1:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LINEAS | A23050500150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-05 | 2650 | keep | 0 | May | 2023 | 0.0018049 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-05-05 16:59 | 2023-05-05 17:43 | 1 | 0:44 | P | PROBLEMA DEL CLIENTE | 1 X 15 EN RISER POR PROBLEMA INTERNO | P23050500186 | New_Event | Customer-Related Interruption | Include | Include | Public | 44 | 2023-05-05 | 44 | keep | 0 | May | 2023 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-05 17:07 | 2023-05-05 19:51 | 5 | 2:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA SPACER Y SE CERRO CORTE DE LINEA | P23050500189 | New_Event | Primary Wire Break | Include | Include | Equipment | 164 | 2023-05-05 | 820 | keep | 0 | May | 2023 | 0.0005585 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-05-05 17:08 | 2023-05-06 08:35 | 20 | 15:27 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | M23050500158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 927 | 2023-05-05 | 18540 | keep | 0 | May | 2023 | 0.012628 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-05 17:11 | 2023-05-06 14:00 | 120 | 20:49 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO Y SE LEVANTO CONDUCTOR | A23050500155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1249 | 2023-05-05 | 149880 | keep | 0 | May | 2023 | 0.10208 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2023-05-05 17:40 | 2023-05-05 18:35 | 1722 | 0:55 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO EN TRONCAL DEL ALIMENTADOR SE CERRO INTERRUPTOR | A23050500171 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 55 | 2023-05-05 | 94710 | keep | 0 | May | 2023 | 0.064507 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-05 17:44 | 2023-05-05 20:31 | 29 | 2:47 | P | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO TRAMO DE ALIMENTADOR PARA PODER TRABAJAR CON CONDUCTOR ROTO DE LINEA 800 CG-230505-02 | C23050500229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 167 | 2023-05-05 | 4843 | keep | 0 | May | 2023 | 0.0032985 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
VEGA BAJA | 2023-05-05 17:48 | 2023-05-05 19:06 | 14 | 1:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X15 EN XMR SE REPARO SECUNDARIA | B23050500247 | New_Event | Secondary Wire Break | Include | Include | Equipment | 78 | 2023-05-05 | 1092 | keep | 0 | May | 2023 | 0.00074376 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-05-05 17:58 | 2023-05-05 21:45 | 8 | 3:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 20 EN XMR Y SE REMPLAZO CAJA PRIMARIA | S23050500344 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2023-05-05 | 1816 | keep | 0 | May | 2023 | 0.0012369 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-05-05 18:03 | 2023-05-05 18:04 | 1089 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 3015-07 LLEVANDO 50% 3103-05 | C2305050000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 1089 | keep | 0 | May | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
MAYAGÃœEZ | 2023-05-05 18:03 | 2023-05-06 09:20 | 15 | 15:17 | P | ANIMAL | 1 X 40 EN CL CRUCE DE FASE PRIMARIA POR AVE | M23050500177 | New_Event | Animals | Include | Include | Wildlife | 917 | 2023-05-05 | 13755 | keep | 0 | May | 2023 | 0.0093685 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-05 18:19 | 2023-05-05 18:20 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO | B23050500255 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 766 | keep | 0 | May | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-05-05 18:41 | 2023-05-05 18:42 | 298 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 95% DE SU CARGA TRANSFERIDA AL 1717-02 | B23050500259 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 298 | keep | 0 | May | 2023 | 0.00020297 | 0.00020297 | Momentary | FALSE | FALSE | Not_TMED_Event | 298
ARECIBO | 2023-05-05 18:59 | 2023-05-05 21:06 | 2266 | 2:07 | T | DESGANCHE | SE REALIZO DESGANCHE MASIVO Y SE REPARO LINEA PRIMARIA SE CERRO INTERRUPTOR | A23050500203 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-05-05 | 287782 | keep | 0 | May | 2023 | 0.19601 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-05-05 19:00 | 2023-05-05 20:10 | 175 | 1:10 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | A23050500139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-05-05 | 12250 | keep | 0 | May | 2023 | 0.0083434 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
GUAYAMA | 2023-05-05 19:19 | 2023-05-06 08:23 | 15 | 13:04 | P | CAUSAS EXTERNAS | 1 X 20 EN TRANSFORMADOR POR CONTAMINACION | P23050500203 | New_Event | Damage From Public | Include | Include | Public | 784 | 2023-05-05 | 11760 | keep | 0 | May | 2023 | 0.0080097 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-05 19:20 | 2023-05-06 09:07 | 2 | 13:47 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR LINEA SECUNDARIA CRUZADA CON FOCO | M23050500190 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 827 | 2023-05-05 | 1654 | keep | 0 | May | 2023 | 0.0011265 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-05-05 19:27 | 2023-05-06 09:15 | 30 | 13:48 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO RAYOS EVENTO TRANSFERIDO DE PONCE A BARRANQUITAS | P23050500207 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 828 | 2023-05-05 | 24840 | keep | 0 | May | 2023 | 0.016918 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-05 19:58 | 2023-05-06 12:17 | 12 | 16:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER Y SE REMPLAZO CAJA PRIMARIA | B23050500276 | New_Event | Cutout Failure | Include | Include | Equipment | 979 | 2023-05-05 | 11748 | keep | 0 | May | 2023 | 0.0080015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-05-05 19:58 | 2023-05-06 07:47 | 15 | 11:49 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR POR AVE | P23050500212 | New_Event | Animals | Include | Include | Wildlife | 709 | 2023-05-05 | 10635 | keep | 0 | May | 2023 | 0.0072435 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-05-05 20:11 | 2023-05-06 12:00 | 53 | 15:49 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE RISER | C23050500256 | New_Event | Primary Wire Break | Include | Include | Equipment | 949 | 2023-05-05 | 50297 | keep | 0 | May | 2023 | 0.034257 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
HUMACAO | 2023-05-05 20:15 | 2023-05-05 20:16 | 640 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23050500257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-05 | 640 | keep | 0 | May | 2023 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
AGUADILLA | 2023-05-05 20:15 | 2023-05-06 19:50 | 10 | 23:35 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | POSTE PARTIDO SE PASO TRANSFORMADOR A POSTE CERCANO | M23050500147 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1415 | 2023-05-05 | 14150 | keep | 0 | May | 2023 | 0.0096375 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-05-05 20:35 | 2023-05-05 23:15 | 80 | 2:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA PERSONAL REPORTO OXIDACION COMO CAUSA | A23050500226 | New_Event | Cutout Failure | Include | Include | Equipment | 160 | 2023-05-05 | 12800 | keep | 0 | May | 2023 | 0.008718 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-05 20:46 | 2023-05-06 13:55 | 7 | 17:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA | B23050500278 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1029 | 2023-05-05 | 7203 | keep | 0 | May | 2023 | 0.0049059 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-05-05 20:49 | 2023-05-06 08:35 | 3 | 11:46 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA CRUCE POR AVE | C23050500259 | New_Event | Animals | Include | Include | Wildlife | 706 | 2023-05-05 | 2118 | keep | 0 | May | 2023 | 0.0014426 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-05 21:42 | 2023-05-06 01:42 | 298 | 4:00 | P | CONDUCTOR ROTO O ABIERTO | BY-230505-03 SE LEVANTO CONDUCTOR PRIMARIO | B23050500272 | New_Event | Primary Wire Break | Include | Include | Equipment | 240 | 2023-05-05 | 71520 | keep | 0 | May | 2023 | 0.048712 | 0.00020297 | Sustained | FALSE | FALSE | Not_TMED_Event | 298
BAYAMON | 2023-05-05 23:06 | 2023-05-06 10:04 | 80 | 10:58 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE DE BAMBUA | B23050500295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 658 | 2023-05-05 | 52640 | keep | 0 | May | 2023 | 0.035853 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-05-05 23:10 | 2023-05-06 02:00 | 60 | 2:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050500235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-05-05 | 10200 | keep | 0 | May | 2023 | 0.0069472 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-05 23:12 | 2023-05-06 07:47 | 18 | 8:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | B23050500282 | New_Event | Cutout Failure | Include | Include | Equipment | 515 | 2023-05-05 | 9270 | keep | 0 | May | 2023 | 0.0063138 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-05-05 23:21 | 2023-05-06 07:46 | 64 | 8:25 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23050500260 | New_Event | Vegetation Contact | Include | Include | Vegetation | 505 | 2023-05-05 | 32320 | keep | 0 | May | 2023 | 0.022013 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
CANOVANAS | 2023-05-05 23:24 | 2023-05-06 13:05 | 170 | 13:41 | P | ANIMAL | 1 X 50 Y 1 X 40 EN CORTES DE LINEA CRUCE CON LAGARTO | R23050500075 | New_Event | Animals | Include | Include | Wildlife | 821 | 2023-05-05 | 139570 | keep | 0 | May | 2023 | 0.09506 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
VEGA BAJA | 2023-05-06 01:01 | 2023-05-06 10:50 | 10 | 9:49 | P | DESGANCHE | 1 X 30 Y 1 X 25 EN CORTE DE LINEA Y SE REALIZO DESGANCHE | A23050600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 589 | 2023-05-06 | 5890 | keep | 0 | May | 2023 | 0.0040117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-06 02:00 | 2023-05-06 09:26 | 100 | 7:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | R23050600006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 446 | 2023-05-06 | 44600 | keep | 0 | May | 2023 | 0.030377 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-06 02:50 | 2023-05-06 11:00 | 35 | 8:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23050600003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 490 | 2023-05-06 | 17150 | keep | 0 | May | 2023 | 0.011681 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-05-06 03:03 | 2023-05-06 07:19 | 1 | 4:16 | P | NO SE REPORTO CAUSA | 1 X 15 Y 1 X 25 EN XMR | B23050600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 256 | 2023-05-06 | 256 | keep | 0 | May | 2023 | 0.00017436 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-06 03:06 | 2023-05-06 03:07 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 733 | keep | 0 | May | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
FAJARDO | 2023-05-06 03:45 | 2023-05-06 03:46 | 1902 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23050600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1902 | keep | 0 | May | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-05-06 03:45 | 2023-05-06 03:46 | 970 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2305060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 970 | keep | 0 | May | 2023 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-05-06 03:45 | 2023-05-06 03:46 | 3003 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23050600008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 3003 | keep | 0 | May | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
CAGUAS | 2023-05-06 04:36 | 2023-05-06 04:37 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BAYAMON | 2023-05-06 04:47 | 2023-05-06 06:28 | 107 | 1:41 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23050600019 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-05-06 | 10807 | keep | 0 | May | 2023 | 0.0073606 | 7.2877e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 107
BAYAMON | 2023-05-06 04:53 | 2023-05-06 11:11 | 13 | 6:18 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23050600023 | New_Event | Animals | Include | Include | Wildlife | 378 | 2023-05-06 | 4914 | keep | 0 | May | 2023 | 0.0033469 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
AGUADILLA | 2023-05-06 05:25 | 2023-05-06 09:23 | 10 | 3:58 | P | DESGANCHE | 1 X 30 EN CL DESGANCHE | M23050600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 238 | 2023-05-06 | 2380 | keep | 0 | May | 2023 | 0.001621 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-06 05:56 | 2023-05-06 05:57 | 1467 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23050600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1467 | keep | 0 | May | 2023 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
CAGUAS | 2023-05-06 06:40 | 2023-05-06 08:55 | 145 | 2:15 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR PALOMA | C23050600013 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-05-06 | 19575 | keep | 0 | May | 2023 | 0.013332 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
CAGUAS | 2023-05-06 06:42 | 2023-05-06 06:43 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2305060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1342 | keep | 0 | May | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
BARRANQUITAS | 2023-05-06 06:48 | 2023-05-06 15:25 | 56 | 8:37 | P | DESGANCHE | 1 X 50 EN C/L Y DESGANCHE | C23050600019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2023-05-06 | 28952 | keep | 0 | May | 2023 | 0.019719 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
MAYAGÃœEZ | 2023-05-06 06:58 | 2023-05-06 10:35 | 200 | 3:37 | P | ANIMAL | 1 X 140 EN CL CRUCE DE FASE PRIMARIA POR AVE | M23050600003 | New_Event | Animals | Include | Include | Wildlife | 217 | 2023-05-06 | 43400 | keep | 0 | May | 2023 | 0.02956 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-06 06:58 | 2023-05-06 13:55 | 8 | 6:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN XMR EVENTO TRANSFERIDO DE CAGUAS | C23050600022 | New_Event | Cutout Failure | Include | Include | Equipment | 417 | 2023-05-06 | 3336 | keep | 0 | May | 2023 | 0.0022721 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-05-06 07:02 | 2023-05-06 07:03 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050600009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 3718 | keep | 0 | May | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2023-05-06 07:08 | 2023-05-06 13:17 | 3 | 6:09 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO DE XMR 15KVA X 25 KVA | B23050600037 | New_Event | Service Transformer Failure | Include | Include | Equipment | 369 | 2023-05-06 | 1107 | keep | 0 | May | 2023 | 0.00075397 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-05-06 07:08 | 2023-05-06 10:28 | 8 | 3:20 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE DE FASES POR AVE | M23050600005 | New_Event | Animals | Include | Include | Wildlife | 200 | 2023-05-06 | 1600 | keep | 0 | May | 2023 | 0.0010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-06 07:22 | 2023-05-06 07:23 | 2720 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR CARGA POR EL 1115-01 BRAKER SPARE | S2305060000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-06 | 2720 | keep | 0 | May | 2023 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
SAN JUAN | 2023-05-06 07:23 | 2023-05-06 11:12 | 32 | 3:49 | P | ANIMAL | 1 X 50 EN RISER CRUCE POR AVE | S23050600018 | 1st_after_momentary | Animals | Include | Include | Wildlife | 229 | 2023-05-06 | 7328 | keep | 0 | May | 2023 | 0.0049911 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
CANOVANAS | 2023-05-06 07:25 | 2023-05-06 17:56 | 30 | 10:31 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | R23050600012 | New_Event | Animals | Include | Include | Wildlife | 631 | 2023-05-06 | 18930 | keep | 0 | May | 2023 | 0.012893 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-05-06 07:38 | 2023-05-06 07:39 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
SAN JUAN | 2023-05-06 07:53 | 2023-05-06 14:50 | 300 | 6:57 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO TRAMO Y SE REEMPLAZO POSTE PRIMARIO D2023-3822 LA VIA LIBRE CONTEMPLABA TRANSFERENCIAS LAS CUAL NO SE REALIZARON POR ESO LA CAUSA ES POSTE | S23050600032 | New_Event | Primary Pole Failure | Include | Include | Equipment | 417 | 2023-05-06 | 125100 | keep | 0 | May | 2023 | 0.085205 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-05-06 07:54 | 2023-05-06 15:00 | 200 | 7:06 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO TRAMO Y SE REEMPLAZO POSTE PRIMARIO D2023-3822 LA VIA LIBRE CONTEMPLABA TRANSFERENCIAS LAS CUAL NO SE REALIZARON POR ESO LA CAUSA ES POSTE | S23050600033 | New_Event | Primary Pole Failure | Include | Include | Equipment | 426 | 2023-05-06 | 85200 | keep | 0 | May | 2023 | 0.058029 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-05-06 08:12 | 2023-05-06 12:43 | 5 | 4:31 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23050600026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 271 | 2023-05-06 | 1355 | keep | 0 | May | 2023 | 0.00092288 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-05-06 08:12 | 2023-05-06 10:25 | 1 | 2:13 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA A CAJA | C23050600033 | New_Event | Primary Wire Break | Include | Include | Equipment | 133 | 2023-05-06 | 133 | keep | 0 | May | 2023 | 9.0586e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-06 08:22 | 2023-05-06 16:25 | 50 | 8:03 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA Y 1 X 25 EN RISER AVE CRUZO FASE A TIERRA | A23050600009 | New_Event | Animals | Include | Include | Wildlife | 483 | 2023-05-06 | 24150 | keep | 0 | May | 2023 | 0.016448 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-06 08:44 | 2023-05-06 12:25 | 140 | 3:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN RISER MAL TIEMPO LLUVIA | C23050600036 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 221 | 2023-05-06 | 30940 | keep | 0 | May | 2023 | 0.021073 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
MAYAGÃœEZ | 2023-05-06 09:11 | 2023-05-06 13:45 | 30 | 4:34 | P | DESGANCHE | 2 X 40 EN CL BAMBU | M23050600032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2023-05-06 | 8220 | keep | 0 | May | 2023 | 0.0055986 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-06 09:34 | 2023-05-06 09:56 | 5 | 0:22 | P | NO SE REPORTO CAUSA | 1 X 10 EN CORTE DE LINEA | R23050600021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2023-05-06 | 110 | keep | 0 | May | 2023 | 7.492e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-06 09:44 | 2023-05-06 10:59 | 1 | 1:15 | P | ANIMAL | 1 X 30 EN C/L Y 1 X 35 EN BANCO DE XMR DE CRUCE X RATON | B23050600052 | New_Event | Animals | Include | Include | Wildlife | 75 | 2023-05-06 | 75 | keep | 0 | May | 2023 | 5.1082e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-06 09:47 | 2023-05-06 17:55 | 25 | 8:08 | P | DESGANCHE | 1 X 30 Y 1 X 25 EN DIFERENTES CORTES DE LINEAS SE REALIZO DESGANCHE PERO SE NECESITA MAS DESGANCHE | A23050600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 488 | 2023-05-06 | 12200 | keep | 0 | May | 2023 | 0.0083094 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-05-06 09:48 | 2023-05-06 17:49 | 33 | 8:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO EN PROVISIONAL AEREO MEDIANTE G.O.I. SJ-230506-50 | R23050600027 | New_Event | Primary Wire Break | Include | Include | Equipment | 481 | 2023-05-06 | 15873 | keep | 0 | May | 2023 | 0.010811 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
CANOVANAS | 2023-05-06 09:56 | 2023-05-07 09:01 | 20 | 23:05 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23050600030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1385 | 2023-05-06 | 27700 | keep | 0 | May | 2023 | 0.018866 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-06 10:03 | 2023-05-06 11:43 | 40 | 1:40 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE | P23050600032 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-05-06 | 4000 | keep | 0 | May | 2023 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-06 10:31 | 2023-05-06 12:55 | 20 | 2:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONECTORES SULFATADOS | R23050600032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 144 | 2023-05-06 | 2880 | keep | 0 | May | 2023 | 0.0019616 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-06 10:43 | 2023-05-06 10:44 | 1047 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23050600063 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-06 | 1047 | keep | 0 | May | 2023 | 0.00071311 | 0.00071311 | Momentary | FALSE | FALSE | Not_TMED_Event | 1047
AGUADILLA | 2023-05-06 10:44 | 2023-05-06 13:45 | 80 | 3:01 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA IGUANA CRUZO LINEAS | M23050600067 | 1st_after_momentary | Animals | Include | Include | Wildlife | 181 | 2023-05-06 | 14480 | keep | 0 | May | 2023 | 0.0098623 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-05-06 10:51 | 2023-05-06 10:52 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050600039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1615 | keep | 0 | May | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
AGUADILLA | 2023-05-06 11:10 | 2023-05-06 13:43 | 40 | 2:33 | P | DESGANCHE | 1 X 140 EN CL DESGANCHE | M23050600068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-05-06 | 6120 | keep | 0 | May | 2023 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-06 11:25 | 2023-05-06 14:51 | 1 | 3:26 | P | NO SE REPORTO CAUSA | 3 X 65 EN RISER | R23050600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 206 | 2023-05-06 | 206 | keep | 0 | May | 2023 | 0.00014031 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-06 11:25 | 2023-05-06 17:00 | 50 | 5:35 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M23050600070 | New_Event | Animals | Include | Include | Wildlife | 335 | 2023-05-06 | 16750 | keep | 0 | May | 2023 | 0.011408 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-06 11:40 | 2023-05-06 14:43 | 10 | 3:03 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | R23050600037 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-05-06 | 1830 | keep | 0 | May | 2023 | 0.0012464 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-06 12:10 | 2023-05-06 16:00 | 80 | 3:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23050600055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2023-05-06 | 18400 | keep | 0 | May | 2023 | 0.012532 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-06 12:16 | 2023-05-06 14:18 | 18 | 2:02 | P | OTRAS CAUSAS | SE ABRIO RISER SE COLOCO PISTOLA EN PM Y SE CERRO RISER PM HABIA BOTADO PISTOLA | S23050600117 | New_Event | Other Causes | Include | Include | Other | 122 | 2023-05-06 | 2196 | keep | 0 | May | 2023 | 0.0014957 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
FAJARDO | 2023-05-06 12:16 | 2023-05-06 17:38 | 50 | 5:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO TRAMO PRIMARIO DEL SUELO NO FUNDIO | R23050600039 | New_Event | Primary Wire Break | Include | Include | Equipment | 322 | 2023-05-06 | 16100 | keep | 0 | May | 2023 | 0.010966 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-05-06 12:18 | 2023-05-07 10:32 | 30 | 22:14 | P | DESGANCHE | 1 X 40 EN C/L Y SE REPARO SECUNDARIA | C23050600067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1334 | 2023-05-06 | 40020 | keep | 0 | May | 2023 | 0.027257 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-06 12:23 | 2023-05-06 16:15 | 15 | 3:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LINEAS | M23050600075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-05-06 | 3480 | keep | 0 | May | 2023 | 0.0023702 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-06 12:26 | 2023-05-07 09:05 | 100 | 20:39 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050600076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1239 | 2023-05-06 | 123900 | keep | 0 | May | 2023 | 0.084388 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-06 12:30 | 2023-05-06 17:21 | 379 | 4:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23050600070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 291 | 2023-05-06 | 110289 | keep | 0 | May | 2023 | 0.075117 | 0.00025814 | Sustained | FALSE | FALSE | Not_TMED_Event | 379
MAYAGÃœEZ | 2023-05-06 12:30 | 2023-05-06 16:39 | 2999 | 4:09 | S | ANIMAL | SE REMPLAZO PARARRAYOS AVERIADO EN TRANSFORMADOR HACIA MEDICION REMOTA CAUSADO POR AVE Y SE RESTABLECIO CARGA | M23050600077 | New_Event | Animals | Include | Include | Wildlife | 249 | 2023-05-06 | 746751 | keep | 0 | May | 2023 | 0.50861 | 0.0020426 | Sustained | FALSE | FALSE | Not_TMED_Event | 2999
MAYAGÃœEZ | 2023-05-06 12:30 | 2023-05-06 16:39 | 1597 | 4:09 | S | ANIMAL | SE REMPLAZO PARARRAYOS AVERIADO EN TRANSFORMADOR HACIA MEDICION REMOTA CAUSADO POR AVE Y SE RESTABLECIO CARGA | M23050600077 | New_Event | Animals | Include | Include | Wildlife | 249 | 2023-05-06 | 397653 | keep | 0 | May | 2023 | 0.27084 | 0.0010877 | Sustained | FALSE | FALSE | Not_TMED_Event | 1597
GUAYAMA | 2023-05-06 12:31 | 2023-05-06 12:32 | 4035 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050600054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 4035 | keep | 0 | May | 2023 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
VEGA BAJA | 2023-05-06 12:53 | 2023-05-08 16:25 | 3 | 51:32 | P | ARBOL SOBRE LINEA | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | A23050600059 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 3092 | 2023-05-06 | 9276 | keep | 0 | May | 2023 | 0.0063178 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2023-05-06 12:56 | 2023-05-06 14:43 | 12 | 1:47 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23050600057 | New_Event | Animals | Include | Include | Wildlife | 107 | 2023-05-06 | 1284 | keep | 0 | May | 2023 | 0.00087453 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-05-06 12:57 | 2023-05-06 16:15 | 8 | 3:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | M23050600092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 198 | 2023-05-06 | 1584 | keep | 0 | May | 2023 | 0.0010789 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-06 13:00 | 2023-05-06 15:30 | 30 | 2:30 | P | ANIMAL | 1 X 50 EN C/L SE RETIRO AVE | B23050600077 | New_Event | Animals | Include | Include | Wildlife | 150 | 2023-05-06 | 4500 | keep | 0 | May | 2023 | 0.0030649 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-06 13:06 | 2023-05-06 13:07 | 766 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1909-07 LLEVA 50% 1709-03 | B2305060000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-06 | 766 | keep | 0 | May | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-05-06 13:06 | 2023-05-06 13:07 | 1139 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1909-07 LLEVA 50% 1709-03 | B2305060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1139 | keep | 0 | May | 2023 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2023-05-06 13:09 | 2023-05-07 17:48 | 12 | 28:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO 150 PIES DE SECUNDARIA AVERIADA | B23050600078 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1719 | 2023-05-06 | 20628 | keep | 0 | May | 2023 | 0.01405 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-06 13:19 | 2023-05-06 15:35 | 15 | 2:16 | P | ANIMAL | 1 X 100 EN C/L SE RETIRO IGUANA | B23050600079 | New_Event | Animals | Include | Include | Wildlife | 136 | 2023-05-06 | 2040 | keep | 0 | May | 2023 | 0.0013894 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-05-06 13:20 | 2023-05-06 14:00 | 16 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REGULO VOLTAJE SE REPARARON CONEXIONES SECUNDARIAS | P23050600063 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-05-06 | 640 | keep | 0 | May | 2023 | 0.0004359 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-05-06 13:21 | 2023-05-06 13:22 | 766 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR LLEVA 50% DEL 1709-03 | B2305060000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-06 | 766 | keep | 0 | May | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-05-06 13:21 | 2023-05-06 13:22 | 1139 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 50% DEL 1709-03 | B2305060000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1139 | keep | 0 | May | 2023 | 0.00077577 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
MAYAGÃœEZ | 2023-05-06 13:28 | 2023-05-06 15:10 | 200 | 1:42 | P | DESGANCHE | 1 X 100 Y 2 X 80 EN CORTES DE LINEA DISTINTOS REQUIERE DESGANCHE | M23050600111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-05-06 | 20400 | keep | 0 | May | 2023 | 0.013894 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
UTUADO | 2023-05-06 13:29 | 2023-05-06 16:15 | 40 | 2:46 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 30 EN CORTE DE LINEA SE REFIRIO PARA REMPLAZAR POSTE CON PERILLA ROTA | A23050600064 | New_Event | Primary Pole Failure | Include | Include | Equipment | 166 | 2023-05-06 | 6640 | keep | 0 | May | 2023 | 0.0045225 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-06 13:32 | 2023-05-06 13:45 | 67 | 0:13 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R23050600015 | New_Event | Animals | Include | Include | Wildlife | 13 | 2023-05-06 | 871 | keep | 0 | May | 2023 | 0.00059323 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
CANOVANAS | 2023-05-06 13:35 | 2023-05-06 17:14 | 8 | 3:39 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | R23050600046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 219 | 2023-05-06 | 1752 | keep | 0 | May | 2023 | 0.0011933 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-06 13:45 | 2023-05-06 19:32 | 63 | 5:47 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | S23050600141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 347 | 2023-05-06 | 21861 | keep | 0 | May | 2023 | 0.014889 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
PONCE | 2023-05-06 13:45 | 2023-05-06 13:46 | 2308 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050600067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 2308 | keep | 0 | May | 2023 | 0.001572 | 0.001572 | Momentary | FALSE | FALSE | Not_TMED_Event | 2308
CANOVANAS | 2023-05-06 14:22 | 2023-05-06 16:08 | 12 | 1:46 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23050600050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-06 | 1272 | keep | 0 | May | 2023 | 0.00086635 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-05-06 14:30 | 2023-05-06 17:10 | 12 | 2:40 | P | ANIMAL | 1 X 25 EN TRANSFORMADOR IGUANA CRUZO CAJA | M23050600140 | New_Event | Animals | Include | Include | Wildlife | 160 | 2023-05-06 | 1920 | keep | 0 | May | 2023 | 0.0013077 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-06 14:31 | 2023-05-06 14:32 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2305060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 652 | keep | 0 | May | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
BAYAMON | 2023-05-06 15:08 | 2023-05-06 19:25 | 51 | 4:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA | S23050600149 | New_Event | Cutout Failure | Include | Include | Equipment | 257 | 2023-05-06 | 13107 | keep | 0 | May | 2023 | 0.0089271 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
HUMACAO | 2023-05-06 15:15 | 2023-05-06 15:53 | 13 | 0:38 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE RETIRO PELIGRO DE POSTE SECUNDARIO PARTIDO POR ACCIDENTE DE CAMION | C23050600081 | New_Event | Damage From Public | Include | Include | Public | 38 | 2023-05-06 | 494 | keep | 0 | May | 2023 | 0.00033646 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
MAYAGÃœEZ | 2023-05-06 15:15 | 2023-05-06 16:20 | 17 | 1:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REMPLAZO DE BAJANTES SECUNDARIOS EN MALAS CONDICIONES | M23050600142 | New_Event | Secondary Wire Break | Include | Include | Equipment | 65 | 2023-05-06 | 1105 | keep | 0 | May | 2023 | 0.00075261 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-05-06 15:25 | 2023-05-06 16:40 | 60 | 1:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LINEAS | M23050600161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-05-06 | 4500 | keep | 0 | May | 2023 | 0.0030649 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-05-06 15:31 | 2023-05-06 16:22 | 12 | 0:51 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR PAJARO CRUZO FASE | P23050600086 | New_Event | Animals | Include | Include | Wildlife | 51 | 2023-05-06 | 612 | keep | 0 | May | 2023 | 0.00041683 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-06 15:38 | 2023-05-06 17:40 | 124 | 2:02 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23050600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-05-06 | 15128 | keep | 0 | May | 2023 | 0.010304 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
CAGUAS | 2023-05-06 15:39 | 2023-05-06 17:03 | 38 | 1:24 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23050600087 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-05-06 | 3192 | keep | 0 | May | 2023 | 0.0021741 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
BARRANQUITAS | 2023-05-06 15:45 | 2023-05-06 15:46 | 1131 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305060000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1131 | keep | 0 | May | 2023 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
VEGA BAJA | 2023-05-06 15:59 | 2023-05-07 09:48 | 25 | 17:49 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23050600077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1069 | 2023-05-06 | 26725 | keep | 0 | May | 2023 | 0.018202 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-06 16:23 | 2023-05-06 17:28 | 1 | 1:05 | P | ANIMAL | 1 X 50 EN C/L SE RETIRO AVE | B23050600091 | New_Event | Animals | Include | Include | Wildlife | 65 | 2023-05-06 | 65 | keep | 0 | May | 2023 | 4.4271e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-06 16:29 | 2023-05-06 18:13 | 18 | 1:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO BANCO DE XMR Y SE REPARO SECUNDARIA | S23050600153 | New_Event | Secondary Wire Break | Include | Include | Equipment | 104 | 2023-05-06 | 1872 | keep | 0 | May | 2023 | 0.001275 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
AGUADILLA | 2023-05-06 16:41 | 2023-05-06 21:35 | 300 | 4:54 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050600182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-05-06 | 88200 | keep | 0 | May | 2023 | 0.060073 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2023-05-06 17:08 | 2023-05-06 18:34 | 176 | 1:26 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23050600100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-05-06 | 15136 | keep | 0 | May | 2023 | 0.010309 | 0.00011987 | Sustained | FALSE | FALSE | Not_TMED_Event | 176
BARRANQUITAS | 2023-05-06 17:21 | 2023-05-07 11:50 | 216 | 18:29 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C23050600103 | New_Event | Primary Wire Break | Include | Include | Equipment | 1109 | 2023-05-06 | 239544 | keep | 0 | May | 2023 | 0.16315 | 0.00014712 | Sustained | FALSE | FALSE | Not_TMED_Event | 216
BARRANQUITAS | 2023-05-06 17:27 | 2023-05-06 22:47 | 92 | 5:20 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L GRUA IMPACTO CABLE DEL TELEFONO Y SACUDIO LAS LINEAS | C23050600104 | New_Event | Damage From Public | Include | Include | Public | 320 | 2023-05-06 | 29440 | keep | 0 | May | 2023 | 0.020051 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
AGUADILLA | 2023-05-06 17:44 | 2023-05-06 19:30 | 80 | 1:46 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23050600194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-06 | 8480 | keep | 0 | May | 2023 | 0.0057757 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-05-06 17:46 | 2023-05-07 09:34 | 97 | 15:48 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL PARA CERRAR PUENTE ABIERTO EN TRONCAL Y SE ENERGIZO | C23050600109 | New_Event | Primary Wire Break | Include | Include | Equipment | 948 | 2023-05-06 | 91956 | keep | 0 | May | 2023 | 0.062631 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
VEGA BAJA | 2023-05-06 18:12 | 2023-05-06 19:00 | 20 | 0:48 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | A23050600090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-05-06 | 960 | keep | 0 | May | 2023 | 0.00065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-05-06 18:15 | 2023-05-06 19:18 | 7 | 1:03 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | A23050600091 | New_Event | Animals | Include | Include | Wildlife | 63 | 2023-05-06 | 441 | keep | 0 | May | 2023 | 0.00030036 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-05-06 18:42 | 2023-05-06 19:42 | 2 | 1:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L Y REEMPLAZO DE PORTAFUSIBLE | C23050600119 | New_Event | Cutout Failure | Include | Include | Equipment | 60 | 2023-05-06 | 120 | keep | 0 | May | 2023 | 8.1731e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-05-06 18:54 | 2023-05-06 18:55 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050600101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 2379 | keep | 0 | May | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
HUMACAO | 2023-05-06 19:11 | 2023-05-06 20:46 | 77 | 1:35 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23050600128 | New_Event | Animals | Include | Include | Wildlife | 95 | 2023-05-06 | 7315 | keep | 0 | May | 2023 | 0.0049822 | 5.2444e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 77
YAUCO | 2023-05-06 19:26 | 2023-05-07 08:03 | 10 | 12:37 | P | ANIMAL | 1 X 25 EN TRANSFORMER IGUANA CRUZO FASE A TIERRA | M23050600221 | New_Event | Animals | Include | Include | Wildlife | 757 | 2023-05-06 | 7570 | keep | 0 | May | 2023 | 0.0051559 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-06 19:26 | 2023-05-07 14:42 | 20 | 19:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO EL CORTE DE LINEA | M23050600220 | New_Event | Primary Wire Break | Include | Include | Equipment | 1156 | 2023-05-06 | 23120 | keep | 0 | May | 2023 | 0.015747 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-06 19:34 | 2023-05-07 08:29 | 13 | 12:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23050600071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 775 | 2023-05-06 | 10075 | keep | 0 | May | 2023 | 0.006862 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-05-06 19:39 | 2023-05-07 09:34 | 30 | 13:55 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23050600131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 835 | 2023-05-06 | 25050 | keep | 0 | May | 2023 | 0.017061 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-05-06 19:57 | 2023-05-07 13:16 | 20 | 17:19 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23050600103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1039 | 2023-05-06 | 20780 | keep | 0 | May | 2023 | 0.014153 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-06 20:10 | 2023-05-07 14:45 | 10 | 18:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA DE TRANSFORMADOR | A23050600105 | New_Event | Primary Wire Break | Include | Include | Equipment | 1115 | 2023-05-06 | 11150 | keep | 0 | May | 2023 | 0.0075942 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-06 20:25 | 2023-05-06 23:24 | 150 | 2:59 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050600108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-05-06 | 26850 | keep | 0 | May | 2023 | 0.018287 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-05-06 20:46 | 2023-05-06 21:05 | 32 | 0:19 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23050600153 | Partial_restoration | Animals | Include | Include | Wildlife | 19 | 2023-05-06 | 608 | keep | 0 | May | 2023 | 0.00041411 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-06 20:57 | 2023-05-06 20:58 | 1984 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23050600175 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1984 | keep | 0 | May | 2023 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
PONCE | 2023-05-06 21:18 | 2023-05-06 21:19 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050600116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-06 | 1746 | keep | 0 | May | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
AGUADILLA | 2023-05-06 22:30 | 2023-05-07 11:11 | 1483 | 12:41 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN EL 38KV PUENTE ABIERTO EN ACB 2701A | M23050600293 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 761 | 2023-05-06 | 1128563 | keep | 0 | May | 2023 | 0.76866 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
AGUADILLA | 2023-05-06 22:30 | 2023-05-07 11:11 | 89 | 12:41 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO EN EL 38KV PUENTE ABIERTO EN ACB 2701A | M23050600293 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 761 | 2023-05-06 | 67729 | keep | 0 | May | 2023 | 0.04613 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
ARECIBO | 2023-05-06 23:21 | 2023-05-07 00:38 | 50 | 1:17 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23050600159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 77 | 2023-05-06 | 3850 | keep | 0 | May | 2023 | 0.0026222 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-07 00:12 | 2023-05-07 02:51 | 6 | 2:39 | P | CAUSAS EXTERNAS | ABRIO XMR PARA SECCIONALIZAR 2 POSTES SECUNDARIOS PARTIDOS POR AUTOMOVIL | C23050700003 | New_Event | Damage From Public | Include | Include | Public | 159 | 2023-05-07 | 954 | keep | 0 | May | 2023 | 0.00064977 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-05-07 00:12 | 2023-05-07 00:14 | 650 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO SE CERRO POR SCADA NO SE REPORTO CAUSA | A23050700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-07 | 1300 | keep | 0 | May | 2023 | 0.00088542 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2023-05-07 01:09 | 2023-05-07 04:16 | 1633 | 3:07 | T | ALIMENTADOR AMARRADO | DISPARO DEL INTERRUPTOR 8103-02 POR AISLADOR ROTO EN TRONCAL EL 8103-02 LLEVA LA CARGA DEL 8103-01 | A23050700008 | New_Event | Feeder Load Transferred | Include | Include | Other | 187 | 2023-05-07 | 305371 | keep | 0 | May | 2023 | 0.20799 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-05-07 01:09 | 2023-05-07 04:16 | 1624 | 3:07 | T | AISLADOR ROTO, PARTIDO O SAFADO | AISLADOR ROTO EN TRONCAL SE ABRIO PUENTES PARA SECCIONALIZAR. LLEVA LA CARGA DEL 8103-01.SOLO ENTRO 100 CLIENTES | A23050700008 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 187 | 2023-05-07 | 303688 | keep | 0 | May | 2023 | 0.20684 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
SAN JUAN | 2023-05-07 01:57 | 2023-05-07 10:24 | 4 | 8:27 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23050700002 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 507 | 2023-05-07 | 2028 | keep | 0 | May | 2023 | 0.0013813 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-05-07 04:16 | 2023-05-07 10:33 | 1524 | 6:17 | P | AISLADOR ROTO, PARTIDO O SAFADO | REEMPLAZO DE AISLADOR PARTIDO EN TRONCAL | A23050700024 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 377 | 2023-05-07 | 574548 | keep | 0 | May | 2023 | 0.39132 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-07 05:04 | 2023-05-07 05:05 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23050700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 1192 | keep | 0 | May | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
GUAYAMA | 2023-05-07 05:51 | 2023-05-07 05:52 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA DOS OPERACIONES Y QUEDA EN SERVICIO | P23050700013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 4279 | keep | 0 | May | 2023 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
VEGA BAJA | 2023-05-07 06:04 | 2023-05-07 06:05 | 3000 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23050700005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 3000 | keep | 0 | May | 2023 | 0.0020433 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
AGUADILLA | 2023-05-07 06:19 | 2023-05-07 06:20 | 1827 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23050700009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-07 | 1827 | keep | 0 | May | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-05-07 06:20 | 2023-05-07 12:00 | 60 | 5:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23050700061 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 340 | 2023-05-07 | 20400 | keep | 0 | May | 2023 | 0.013894 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-07 06:23 | 2023-05-07 06:24 | 4232 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 20% DE SU CARGA TRANSFERIDA AL 1424-08 SE CERRO POR CONTROL | S2305070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 4232 | keep | 0 | May | 2023 | 0.0028824 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
BAYAMON | 2023-05-07 06:23 | 2023-05-07 09:33 | 100 | 3:10 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23050700003 | New_Event | Animals | Include | Include | Wildlife | 190 | 2023-05-07 | 19000 | keep | 0 | May | 2023 | 0.012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-05-07 06:43 | 2023-05-07 06:44 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050700015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 449 | keep | 0 | May | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
SAN JUAN | 2023-05-07 07:06 | 2023-05-07 08:59 | 15 | 1:53 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO EN XMR PARA REPARAR PUENTE ABIERTO DE LINEA @ LA ENTRADA DE LA CAJA EN XMR | S23050700005 | New_Event | Primary Wire Break | Include | Include | Equipment | 113 | 2023-05-07 | 1695 | keep | 0 | May | 2023 | 0.0011545 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-05-07 07:14 | 2023-05-07 07:15 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2305070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 2722 | keep | 0 | May | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
CAGUAS | 2023-05-07 07:16 | 2023-05-07 07:17 | 1191 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 70 % DE SU CARGA | C2305070000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 1191 | keep | 0 | May | 2023 | 0.00081118 | 0.00081118 | Momentary | FALSE | FALSE | Not_TMED_Event | 1191
BAYAMON | 2023-05-07 07:57 | 2023-05-07 11:01 | 5 | 3:04 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE REALIZO DESGANCHE | S23050700008 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 184 | 2023-05-07 | 920 | keep | 0 | May | 2023 | 0.00062661 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-05-07 08:10 | 2023-05-07 10:40 | 1 | 2:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23050700029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 150 | 2023-05-07 | 150 | keep | 0 | May | 2023 | 0.00010216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-07 08:32 | 2023-05-07 09:52 | 80 | 1:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE 100A Y 1 X 65 EN CORTE DE LINEA | P23050700022 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2023-05-07 | 6400 | keep | 0 | May | 2023 | 0.004359 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-07 08:47 | 2023-05-07 12:33 | 70 | 3:46 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23050700012 | New_Event | Animals | Include | Include | Wildlife | 226 | 2023-05-07 | 15820 | keep | 0 | May | 2023 | 0.010775 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-05-07 09:26 | 2023-05-07 12:50 | 1 | 3:24 | P | NO SE REPORTO CAUSA | 1 X 20 EN SU-1 | S23050700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 204 | 2023-05-07 | 204 | keep | 0 | May | 2023 | 0.00013894 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-07 09:34 | 2023-05-07 11:07 | 290 | 1:33 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L TOTAL PARA CERRAR PUENTE ABIERTO EN TRONCAL Y SE ENERGIZO | C23050600109 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 93 | 2023-05-07 | 26970 | keep | 0 | May | 2023 | 0.018369 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-07 09:36 | 2023-05-07 11:38 | 2 | 2:02 | P | DESGANCHE | 1 X 65 EN C/L SE REFIRIO PARA DESGANCHE | S23050700015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-05-07 | 244 | keep | 0 | May | 2023 | 0.00016619 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-05-07 09:39 | 2023-05-07 12:30 | 35 | 2:51 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23050700028 | New_Event | Animals | Include | Include | Wildlife | 171 | 2023-05-07 | 5985 | keep | 0 | May | 2023 | 0.0040764 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
YAUCO | 2023-05-07 09:42 | 2023-05-07 10:00 | 17 | 0:18 | P | TRANSFORMADOR AVERIADO | SE CAMBIO TRANSFORMADOR DE 25KVA A 4160 POR UNO MISMA CAPACIDAD | P23050700027 | New_Event | Service Transformer Failure | Include | Include | Equipment | 18 | 2023-05-07 | 306 | keep | 0 | May | 2023 | 0.00020842 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
PONCE | 2023-05-07 10:22 | 2023-05-07 10:23 | 1478 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE | P23050700032 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-05-07 | 1478 | keep | 0 | May | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
PONCE | 2023-05-07 10:23 | 2023-05-07 12:27 | 64 | 2:04 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 EN PROVISIONAL POR PISTOLA EN PM FID 11220519 AVERIADA | P23050700035 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 124 | 2023-05-07 | 7936 | keep | 0 | May | 2023 | 0.0054052 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
BARRANQUITAS | 2023-05-07 10:42 | 2023-05-07 13:10 | 30 | 2:28 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23050700042 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-05-07 | 4440 | keep | 0 | May | 2023 | 0.0030241 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-07 10:45 | 2023-05-07 12:28 | 50 | 1:43 | P | ANIMAL | 1 X 65 EN RISER Y 1 X 65 EN OTRO RISER CRUCE X AVE | B23050700025 | New_Event | Animals | Include | Include | Wildlife | 103 | 2023-05-07 | 5150 | keep | 0 | May | 2023 | 0.0035076 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-07 11:10 | 2023-05-07 12:05 | 7 | 0:55 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y REEMPLAZO EL BUSHING SECUNDARIO | C23050700045 | New_Event | Service Transformer Failure | Include | Include | Equipment | 55 | 2023-05-07 | 385 | keep | 0 | May | 2023 | 0.00026222 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-05-07 11:13 | 2023-05-07 13:02 | 9 | 1:49 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23050700046 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-05-07 | 981 | keep | 0 | May | 2023 | 0.00066815 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
FAJARDO | 2023-05-07 11:22 | 2023-05-07 12:20 | 3 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REEMPLAZO BUSHING SECUNDARIO | R23050700009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2023-05-07 | 174 | keep | 0 | May | 2023 | 0.00011851 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-05-07 11:22 | 2023-05-07 16:45 | 80 | 5:23 | P | DESGANCHE | 1 X 100 EN C/L SE DESGANCHO | B23050700030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-05-07 | 25840 | keep | 0 | May | 2023 | 0.0176 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-05-07 11:37 | 2023-05-07 12:58 | 7 | 1:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTORES EN BAJANTE SECUNDARIOS DE TRANSFORMADOR Y SE REPARA LINEA SECUNDARIA | P23050700041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 81 | 2023-05-07 | 567 | keep | 0 | May | 2023 | 0.00038618 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-07 12:16 | 2023-05-07 12:51 | 6244 | 0:35 | T | CABLE SOTERRADO AVERIADO | SE SECCIONALIZO TRAMO SOTERRADO AVERIADO DEL SU-24 @ SU-25 MEDIANTE GOI SJ-230507-01 - 85% EN SERVICIO | S23050700022 | New_Event | UG Cable Fault | Include | Include | Equipment | 35 | 2023-05-07 | 218540 | keep | 0 | May | 2023 | 0.14885 | 0.0042528 | Sustained | FALSE | FALSE | Not_TMED_Event | 6244
CANOVANAS | 2023-05-07 12:37 | 2023-05-07 13:33 | 43 | 0:56 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | R23050700012 | New_Event | Animals | Include | Include | Wildlife | 56 | 2023-05-07 | 2408 | keep | 0 | May | 2023 | 0.0016401 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BARRANQUITAS | 2023-05-07 12:47 | 2023-05-07 13:24 | 7 | 0:37 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ABRIO XMR Y SE ELIMINO LA CRUCETA PODRIDA A PUNTO DE CAERSE, SE REEMPLAZO CAJA PRIMARIA, ASILADOR Y SE REINSTALO EL XMR. | C23050700040 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 37 | 2023-05-07 | 259 | keep | 0 | May | 2023 | 0.0001764 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-07 12:51 | 2023-05-07 13:29 | 937 | 0:38 | P | CABLE SOTERRADO AVERIADO | SE TRANSFIRIO EL 15% DE LA CARGA, QUE FALTABA POR ENTRAR EN SERVICIO, AL 1336-08 PARA REPARAR TRAMO SOTERRADO AVERIADO DEL SU-24 @ SU-25 MEDIANTE GOI SJ-230507-01 - 100% EN SERVICIO | S23050700022 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 38 | 2023-05-07 | 35606 | keep | 0 | May | 2023 | 0.024251 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-07 12:58 | 2023-05-07 13:38 | 1 | 0:40 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23050700063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2023-05-07 | 40 | keep | 0 | May | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-07 13:22 | 2023-05-07 16:06 | 60 | 2:44 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | C23050700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-05-07 | 9840 | keep | 0 | May | 2023 | 0.006702 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-05-07 13:22 | 2023-05-07 13:23 | 1922 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR | C23050700060 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-07 | 1922 | keep | 0 | May | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2023-05-07 13:23 | 2023-05-07 16:57 | 142 | 3:34 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN C/L Y SE CERRO PUENTE DE LINEA A RISER | R23050700061 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 214 | 2023-05-07 | 30388 | keep | 0 | May | 2023 | 0.020697 | 9.6716e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 142
HUMACAO | 2023-05-07 13:29 | 2023-05-07 14:20 | 776 | 0:51 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | DISPARO DE BKR POR POSTE PRIMARIO PARTIDO. SE HICIERON OPERACIONES CON CG-230507-01. ENTRO UN 90% EN SERVICIO | C23050700063 | New_Event | Primary Pole Failure | Include | Include | Equipment | 51 | 2023-05-07 | 39576 | keep | 0 | May | 2023 | 0.026955 | 0.00052853 | Sustained | FALSE | FALSE | Not_TMED_Event | 776
HUMACAO | 2023-05-07 13:32 | 2023-05-07 20:04 | 11 | 6:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23050700064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 392 | 2023-05-07 | 4312 | keep | 0 | May | 2023 | 0.0029369 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-05-07 13:39 | 2023-05-07 17:00 | 30 | 3:21 | P | NO SE REPORTO CAUSA | 1 X 20 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23050700111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 201 | 2023-05-07 | 6030 | keep | 0 | May | 2023 | 0.004107 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-07 13:47 | 2023-05-07 16:14 | 12 | 2:27 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REQUIERE DESGANCHE | M23050700113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-05-07 | 1764 | keep | 0 | May | 2023 | 0.0012015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-05-07 14:20 | 2023-05-07 19:05 | 73 | 4:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | DISPARO DE BKR . SE HICIERON OPERACIONES CON CG-230507-01. SE RETIRO PELIGRO Y SE SECIONALIZO POSTE PARTIDO. ENTRO UN 97% EN SERVICIO | C23050700063 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 285 | 2023-05-07 | 20805 | keep | 0 | May | 2023 | 0.01417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-05-07 14:23 | 2023-05-07 16:55 | 1 | 2:32 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA DE RISER | A23050700146 | New_Event | Primary Wire Break | Include | Include | Equipment | 152 | 2023-05-07 | 152 | keep | 0 | May | 2023 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-07 14:49 | 2023-05-07 15:24 | 10 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA DAR CONECTORES SECUNDARIOS | S23050700076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-05-07 | 350 | keep | 0 | May | 2023 | 0.00023838 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-07 15:30 | 2023-05-07 15:31 | 181 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23050700081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 181 | keep | 0 | May | 2023 | 0.00012328 | 0.00012328 | Momentary | FALSE | FALSE | Not_TMED_Event | 181
SAN JUAN | 2023-05-07 15:30 | 2023-05-07 15:33 | 2052 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA TRANSFERIDA AL 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S23050700082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-07 | 6156 | keep | 0 | May | 2023 | 0.0041928 | 0.0013976 | Momentary | FALSE | FALSE | Not_TMED_Event | 2052
SAN JUAN | 2023-05-07 15:30 | 2023-05-07 15:33 | 134 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA TRANSFERIDA AL 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S23050700082 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-07 | 402 | keep | 0 | May | 2023 | 0.0002738 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
SAN JUAN | 2023-05-07 15:33 | 2023-05-07 17:52 | 27 | 2:19 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23050700083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 139 | 2023-05-07 | 3753 | keep | 0 | May | 2023 | 0.0025562 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-07 15:38 | 2023-05-07 16:37 | 50 | 0:59 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B23050700041 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-05-07 | 2950 | keep | 0 | May | 2023 | 0.0020092 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-07 15:41 | 2023-05-08 10:06 | 10 | 18:25 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR SE REEMPLAZO XMR DE 37.5KVA X 37.5KVA | R23050700018 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1105 | 2023-05-07 | 11050 | keep | 0 | May | 2023 | 0.0075261 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-05-07 15:49 | 2023-05-07 17:15 | 276 | 1:26 | P | ANIMAL | 1 X 100 Y 3 X 100 EN DISTINTOS CORTES DE LINEAS AVE CRUZO FASE | P23050700049 | New_Event | Animals | Include | Include | Wildlife | 86 | 2023-05-07 | 23736 | keep | 0 | May | 2023 | 0.016166 | 0.00018798 | Sustained | FALSE | FALSE | Not_TMED_Event | 276
UTUADO | 2023-05-07 15:59 | 2023-05-07 18:15 | 70 | 2:16 | P | ANIMAL | 1 X 140 EN CORTE DE LINEA AVE CRUZO LINEAS | A23050700150 | New_Event | Animals | Include | Include | Wildlife | 136 | 2023-05-07 | 9520 | keep | 0 | May | 2023 | 0.006484 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-05-07 16:40 | 2023-05-07 18:40 | 7 | 2:00 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA QUEMADA EN TRANSFORMADOR | A23050700153 | New_Event | Cutout Failure | Include | Include | Equipment | 120 | 2023-05-07 | 840 | keep | 0 | May | 2023 | 0.00057212 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-05-07 16:50 | 2023-05-07 19:06 | 25 | 2:16 | P | SECUNDARIA/DESGANCHE | 1 X 1O EN XMR DESGANCHE SECUNDARIO | R23050700022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 136 | 2023-05-07 | 3400 | keep | 0 | May | 2023 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-07 17:10 | 2023-05-07 19:19 | 50 | 2:09 | P | NO SE REPORTO CAUSA | 2 X 80 DEL SU-25 @ BOVEDA DEL CONDOMINIO | S23050700098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 129 | 2023-05-07 | 6450 | keep | 0 | May | 2023 | 0.0043931 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-07 17:23 | 2023-05-07 20:35 | 1 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA A XMR | C23050700083 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2023-05-07 | 192 | keep | 0 | May | 2023 | 0.00013077 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-07 17:40 | 2023-05-07 19:39 | 10 | 1:59 | P | NO SE REPORTO CAUSA | 1 X 140 EN CONVERTIDOR | B23050700046 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2023-05-07 | 1190 | keep | 0 | May | 2023 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-07 17:41 | 2023-05-07 20:08 | 300 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M23050700125 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2023-05-07 | 44100 | keep | 0 | May | 2023 | 0.030036 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
YAUCO | 2023-05-07 17:50 | 2023-05-07 18:45 | 10 | 0:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA | M23050700124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 55 | 2023-05-07 | 550 | keep | 0 | May | 2023 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-05-07 18:36 | 2023-05-07 18:37 | 1405 | 0:01 | T | DESGANCHE | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23050700159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-07 | 1405 | keep | 0 | May | 2023 | 0.00095694 | 0.00095694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2023-05-07 18:37 | 2023-05-07 22:30 | 150 | 3:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23050700161 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-05-07 | 34950 | keep | 0 | May | 2023 | 0.023804 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-05-07 19:05 | 2023-05-07 19:20 | 15 | 0:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | DISPARO DE BKR . SE HICIERON OPERACIONES CON CG-230507-01. SE RETIRO PELIGRO Y SE SECIONALIZO POSTE PARTIDO. SE CERRO N/O CONTRA EL 2801-02. ENTRO UN 3% EN SERVICIO. 100% EN SERVICIOI | C23050700063 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 15 | 2023-05-07 | 225 | keep | 0 | May | 2023 | 0.00015325 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-07 19:46 | 2023-05-07 19:47 | 742 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23050700116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 742 | keep | 0 | May | 2023 | 0.00050537 | 0.00050537 | Momentary | FALSE | FALSE | Not_TMED_Event | 742
GUAYAMA | 2023-05-07 19:56 | 2023-05-08 09:31 | 10 | 13:35 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO Y SE CERRO RISER NO FUNDIO FUSIBLE | P23050700054 | New_Event | Primary Wire Break | Include | Include | Equipment | 815 | 2023-05-07 | 8150 | keep | 0 | May | 2023 | 0.0055509 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-07 20:01 | 2023-05-08 00:14 | 10 | 4:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23050700072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2023-05-07 | 2530 | keep | 0 | May | 2023 | 0.0017232 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-07 20:23 | 2023-05-07 21:31 | 26 | 1:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23050700188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-05-07 | 1768 | keep | 0 | May | 2023 | 0.0012042 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
UTUADO | 2023-05-07 20:29 | 2023-05-08 00:45 | 5 | 4:16 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050700175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 256 | 2023-05-07 | 1280 | keep | 0 | May | 2023 | 0.0008718 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-05-07 20:32 | 2023-05-08 01:01 | 80 | 4:29 | P | DESGANCHE | 1 X50 2 X 40 1X 30 3 X 25 2 X 20 DESGANCHE | B23050700097 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 269 | 2023-05-07 | 21520 | keep | 0 | May | 2023 | 0.014657 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-07 20:51 | 2023-05-08 11:18 | 129 | 14:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIO 1 X 15 EN XMR | B23050700112 | New_Event | Cutout Failure | Include | Include | Equipment | 867 | 2023-05-07 | 111843 | keep | 0 | May | 2023 | 0.076176 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
BARRANQUITAS | 2023-05-07 20:55 | 2023-05-07 20:56 | 2486 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23050700096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 2486 | keep | 0 | May | 2023 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
ARECIBO | 2023-05-07 21:00 | 2023-05-08 00:46 | 15 | 3:46 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR CORROSION EN EL FUSIBLE | A23050700184 | New_Event | Other Causes | Include | Include | Other | 226 | 2023-05-07 | 3390 | keep | 0 | May | 2023 | 0.0023089 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-07 21:15 | 2023-05-08 17:10 | 1 | 19:55 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REEMPLAZO PM 50KVA X 100KVA | S23050700214 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1195 | 2023-05-07 | 1195 | keep | 0 | May | 2023 | 0.00081391 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-07 21:20 | 2023-05-07 21:21 | 3833 | 0:01 | T | DESGANCHE | RECIERRE | C23050700098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-07 | 3833 | keep | 0 | May | 2023 | 0.0026106 | 0.0026106 | Momentary | FALSE | FALSE | Not_TMED_Event | 3833
HUMACAO | 2023-05-07 21:21 | 2023-05-08 07:25 | 32 | 10:04 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C23050700101 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 604 | 2023-05-07 | 19328 | keep | 0 | May | 2023 | 0.013164 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
FAJARDO | 2023-05-07 21:27 | 2023-05-08 09:56 | 54 | 12:29 | P | ANIMAL | 1 X 25 EN C/L CRUCE X AVE | R23050700119 | New_Event | Animals | Include | Include | Wildlife | 749 | 2023-05-07 | 40446 | keep | 0 | May | 2023 | 0.027548 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
CANOVANAS | 2023-05-07 21:35 | 2023-05-07 23:31 | 130 | 1:56 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 Y 1 X 65 EN C/LS DESPEGO PUENTE PRIMARIO DEL POSTE | R23050700120 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 116 | 2023-05-07 | 15080 | keep | 0 | May | 2023 | 0.010271 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
ARECIBO | 2023-05-07 21:52 | 2023-05-08 08:25 | 8 | 10:33 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENRREDADERA | A23050700190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 633 | 2023-05-07 | 5064 | keep | 0 | May | 2023 | 0.0034491 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-07 22:15 | 2023-05-07 22:16 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23050700142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 3458 | keep | 0 | May | 2023 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
VEGA BAJA | 2023-05-07 22:30 | 2023-05-07 22:32 | 3387 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | B23050700135 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-07 | 6774 | keep | 0 | May | 2023 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
AGUADILLA | 2023-05-07 22:35 | 2023-05-08 00:45 | 250 | 2:10 | P | CAUSAS EXTERNAS | SE ABRIO MACHETES PARA RETIRAR POSTE PARTIDO POR IMPACTO DE AUTOMOVIL | M23050700143 | New_Event | Damage From Public | Include | Include | Public | 130 | 2023-05-07 | 32500 | keep | 0 | May | 2023 | 0.022136 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2023-05-07 22:47 | 2023-05-08 00:07 | 40 | 1:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23050700192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-05-07 | 3200 | keep | 0 | May | 2023 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-07 23:25 | 2023-05-07 23:26 | 1834 | 0:01 | T | NO SE REPORTO CAUSA | RECIIERE | B23050700149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-07 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2023-05-08 01:00 | 2023-05-08 02:29 | 109 | 1:29 | P | CAUSAS EXTERNAS | 1 X 50 E C/L 1 X 65 C/L CARRO IMPACTO POSTE | B23050800004 | New_Event | Damage From Public | Include | Include | Public | 89 | 2023-05-08 | 9701 | keep | 0 | May | 2023 | 0.0066073 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
VEGA BAJA | 2023-05-08 01:43 | 2023-05-08 18:35 | 25 | 16:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1012 | 2023-05-08 | 25300 | keep | 0 | May | 2023 | 0.017232 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-08 02:00 | 2023-05-08 11:15 | 20 | 9:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23050800003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 555 | 2023-05-08 | 11100 | keep | 0 | May | 2023 | 0.0075602 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-08 03:34 | 2023-05-08 04:18 | 154 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-08 | 6776 | keep | 0 | May | 2023 | 0.0046151 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2023-05-08 03:34 | 2023-05-08 04:18 | 1261 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-08 | 55484 | keep | 0 | May | 2023 | 0.03779 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2023-05-08 03:34 | 2023-05-08 04:18 | 3894 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-08 | 171336 | keep | 0 | May | 2023 | 0.1167 | 0.0026522 | Sustained | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2023-05-08 03:34 | 2023-05-08 04:18 | 997 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-08 | 43868 | keep | 0 | May | 2023 | 0.029878 | 0.00067905 | Sustained | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-05-08 03:34 | 2023-05-08 04:18 | 1497 | 0:44 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800013 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 44 | 2023-05-08 | 65868 | keep | 0 | May | 2023 | 0.044862 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
YAUCO | 2023-05-08 04:40 | 2023-05-08 07:07 | 20 | 2:27 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | P23050800013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-05-08 | 2940 | keep | 0 | May | 2023 | 0.0020024 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-08 04:52 | 2023-05-08 04:53 | 154 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 15900 | M23050800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 154 | keep | 0 | May | 2023 | 0.00010489 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-08 04:52 | 2023-05-08 04:53 | 1261 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1261 | keep | 0 | May | 2023 | 0.00085886 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-08 04:52 | 2023-05-08 04:53 | 3894 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 3894 | keep | 0 | May | 2023 | 0.0026522 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-08 04:52 | 2023-05-08 04:53 | 997 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 997 | keep | 0 | May | 2023 | 0.00067905 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-08 04:52 | 2023-05-08 04:53 | 1497 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 15900 AISLADOR EN EL #1 DE PORTÃTIL #5 AGUADA. | M23050800030 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1497 | keep | 0 | May | 2023 | 0.0010196 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 574 | keep | 0 | May | 2023 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 2493 | keep | 0 | May | 2023 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1415 | keep | 0 | May | 2023 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1428 | keep | 0 | May | 2023 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800032 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1036 | keep | 0 | May | 2023 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 382 | keep | 0 | May | 2023 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800031 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 39 | keep | 0 | May | 2023 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 2366 | keep | 0 | May | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2023-05-08 04:52 | 2023-05-08 04:53 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1337 | keep | 0 | May | 2023 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-05-08 04:52 | 2023-05-08 04:53 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 EXPLOSIÃ“N EN AISLADOR POSTE SALIDA VICTORIA TC. FOGONAZO | M23050800033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 709 | keep | 0 | May | 2023 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
HUMACAO | 2023-05-08 05:42 | 2023-05-08 09:11 | 1074 | 3:29 | P | CAUSAS EXTERNAS | DISPARO DE INTELLIRRUPTER 2604-03G SE REEMPLAZO AISLADOR AVERIADO POR GLOBO DE HELIO CG-230508-01 | C2305080000X | New_Event | Damage From Public | Include | Include | Public | 209 | 2023-05-08 | 224466 | keep | 0 | May | 2023 | 0.15288 | 0.0007315 | Sustained | FALSE | FALSE | Not_TMED_Event | 1074
GUAYAMA | 2023-05-08 05:44 | 2023-05-08 05:45 | 527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23050800014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 527 | keep | 0 | May | 2023 | 0.00035894 | 0.00035894 | Momentary | FALSE | FALSE | Not_TMED_Event | 527
VEGA BAJA | 2023-05-08 05:56 | 2023-05-08 20:55 | 50 | 14:59 | P | CAUSAS EXTERNAS | 1 X 50 EN CORTE DE LINEA GLOBO CRUZO LINEA | A23050800002 | New_Event | Damage From Public | Include | Include | Public | 899 | 2023-05-08 | 44950 | keep | 0 | May | 2023 | 0.030615 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-08 05:58 | 2023-05-08 09:12 | 2422 | 3:14 | T | NO SE REPORTO CAUSA | SE REPUSO 2 X 100 EN C/L URB CALDAS AL OPERAR C/L APARENTEMENTE OPERO BKR (NO CONTROL). SE CERRO BKR 1346-03 EN PORTATIL EN SUBESTACION | S23050800013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2023-05-08 | 469868 | keep | 0 | May | 2023 | 0.32002 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
CAGUAS | 2023-05-08 06:07 | 2023-05-08 10:12 | 108 | 4:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO AISLADOR QUEMADO | C23050800013 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2023-05-08 | 26460 | keep | 0 | May | 2023 | 0.018022 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2023-05-08 06:15 | 2023-05-08 06:16 | 1802 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23050800017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 1802 | keep | 0 | May | 2023 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
YAUCO | 2023-05-08 06:18 | 2023-05-08 06:19 | 3973 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050800015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 3973 | keep | 0 | May | 2023 | 0.002706 | 0.002706 | Momentary | FALSE | FALSE | Not_TMED_Event | 3973
HUMACAO | 2023-05-08 06:19 | 2023-05-08 06:20 | 3025 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2305080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 3025 | keep | 0 | May | 2023 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
YAUCO | 2023-05-08 06:23 | 2023-05-08 07:56 | 30 | 1:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P23050800016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 93 | 2023-05-08 | 2790 | keep | 0 | May | 2023 | 0.0019003 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-08 06:40 | 2023-05-08 09:15 | 102 | 2:35 | P | ANIMAL | 1 X 50 Y 1 X 65 EN C/L CRUCE X AVE | R23050800008 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-05-08 | 15810 | keep | 0 | May | 2023 | 0.010768 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
PONCE | 2023-05-08 06:41 | 2023-05-08 08:54 | 50 | 2:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO | P23050800021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 133 | 2023-05-08 | 6650 | keep | 0 | May | 2023 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-08 06:53 | 2023-05-08 09:38 | 57 | 2:45 | P | ANIMAL | 1 X 40 EN C/L SE INSTALO RIGIDO CRUCE X AVE | R23050800009 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-05-08 | 9405 | keep | 0 | May | 2023 | 0.0064057 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
GUAYAMA | 2023-05-08 07:19 | 2023-05-08 07:20 | 1173 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050800027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 1173 | keep | 0 | May | 2023 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
VEGA BAJA | 2023-05-08 07:23 | 2023-05-08 13:31 | 70 | 6:08 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR 1 X 65 Y 1 X 100 EN CORTES DE LINEA | B23050800022 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 368 | 2023-05-08 | 25760 | keep | 0 | May | 2023 | 0.017545 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-05-08 07:24 | 2023-05-08 07:25 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
BAYAMON | 2023-05-08 07:40 | 2023-05-08 13:57 | 8 | 6:17 | P | DESGANCHE | 1 X 40 Y 1 X 50 EN CORTE DE LINEA DESGANCHE | B23050800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 377 | 2023-05-08 | 3016 | keep | 0 | May | 2023 | 0.0020542 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-08 07:45 | 2023-05-08 10:17 | 19 | 2:32 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S23050800027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 152 | 2023-05-08 | 2888 | keep | 0 | May | 2023 | 0.001967 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CAGUAS | 2023-05-08 07:45 | 2023-05-08 07:46 | 918 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C2305080000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-08 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-08 07:46 | 2023-05-08 13:14 | 86 | 5:28 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23050800042 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 328 | 2023-05-08 | 28208 | keep | 0 | May | 2023 | 0.019212 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
CANOVANAS | 2023-05-08 07:53 | 2023-05-08 07:54 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305080000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
ARECIBO | 2023-05-08 07:57 | 2023-05-08 14:15 | 15 | 6:18 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A23050800005 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 378 | 2023-05-08 | 5670 | keep | 0 | May | 2023 | 0.0038618 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-08 08:24 | 2023-05-08 10:10 | 144 | 1:46 | P | DESGANCHE | 1 X 65 EN C/L SE ENCONTRO PARARRAYOS AVERIADO Y DESGANCHE | B23050800038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-08 | 15264 | keep | 0 | May | 2023 | 0.010396 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
MAYAGÃœEZ | 2023-05-08 08:42 | 2023-05-08 13:45 | 80 | 5:03 | P | NO SE REPORTO CAUSA | 2 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23050800085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 303 | 2023-05-08 | 24240 | keep | 0 | May | 2023 | 0.01651 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-08 08:48 | 2023-05-08 08:49 | 6012 | 0:01 | P | ANIMAL | RECERRO INTERRUPTOR 3% DE LA CARGA POR EL 3010-03 EN SERVICIO | C2305080000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-08 | 6012 | keep | 0 | May | 2023 | 0.0040947 | 0.0040947 | Momentary | FALSE | FALSE | Not_TMED_Event | 6012
YAUCO | 2023-05-08 08:48 | 2023-05-08 12:40 | 10 | 3:52 | P | DESGANCHE | DESGANCHE MASIVO INTERIOR 2 X 50 EN CORTE DE LINEA | P23050800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-05-08 | 2320 | keep | 0 | May | 2023 | 0.0015801 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-08 08:49 | 2023-05-08 12:06 | 102 | 3:17 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR PALOMA | C23050800071 | 1st_after_momentary | Animals | Include | Include | Wildlife | 197 | 2023-05-08 | 20094 | keep | 0 | May | 2023 | 0.013686 | 6.9472e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 102
BARRANQUITAS | 2023-05-08 08:54 | 2023-05-08 11:42 | 66 | 2:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C23050800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 168 | 2023-05-08 | 11088 | keep | 0 | May | 2023 | 0.007552 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
VEGA BAJA | 2023-05-08 08:57 | 2023-05-08 14:11 | 10 | 5:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | B23058000051 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 314 | 2023-05-08 | 3140 | keep | 0 | May | 2023 | 0.0021386 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-08 09:11 | 2023-05-08 09:51 | 200 | 0:40 | P | CAUSAS EXTERNAS | CG-230508-01 SE REEMPLAZO AISLADOR ROTO POR GLOBO DE HELIO | C23050800003 | Partial_restoration | Damage From Public | Include | Include | Public | 40 | 2023-05-08 | 8000 | keep | 0 | May | 2023 | 0.0054488 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 873 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA EL 20% DEL 3010-01 POR EL 3604-06 BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 873 | keep | 0 | May | 2023 | 0.0005946 | 0.0005946 | Momentary | FALSE | FALSE | Not_TMED_Event | 873
BARRANQUITAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1565 | keep | 0 | May | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 976 | keep | 0 | May | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 548 | keep | 0 | May | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 315 | keep | 0 | May | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800084 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 870 | keep | 0 | May | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA LLEVA EL 20% DEL 3010-01 BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 2906 | keep | 0 | May | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-08 09:16 | 2023-05-08 09:17 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800085 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 2343 | keep | 0 | May | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
GUAYAMA | 2023-05-08 09:16 | 2023-05-08 11:33 | 8 | 2:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA 1 X 15 EN TRANSFORMADOR Y DESGANCHE | P23050800054 | New_Event | Secondary Wire Break | Include | Include | Equipment | 137 | 2023-05-08 | 1096 | keep | 0 | May | 2023 | 0.00074648 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 873 | 1:09 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 0800 DE COMSAT A CIDRA EL 20% DEL 3010-01 POR EL 3604-06 SE SECCIONALIZO LA LINEA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800085 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 60237 | keep | 0 | May | 2023 | 0.041027 | 0.0005946 | Sustained | FALSE | FALSE | Not_TMED_Event | 873
BARRANQUITAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 1565 | 1:09 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800082 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 107985 | keep | 0 | May | 2023 | 0.073548 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 976 | 1:09 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800082 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 67344 | keep | 0 | May | 2023 | 0.045868 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 548 | 1:09 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800082 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 37812 | keep | 0 | May | 2023 | 0.025754 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 315 | 1:09 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800084 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 21735 | keep | 0 | May | 2023 | 0.014804 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 870 | 1:09 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800084 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 60030 | keep | 0 | May | 2023 | 0.040886 | 0.00059255 | Sustained | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 2906 | 1:09 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800085 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 200514 | keep | 0 | May | 2023 | 0.13657 | 0.0019793 | Sustained | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-08 09:20 | 2023-05-08 10:29 | 2343 | 1:09 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 0800 DE COMSAT A CIDRA BAJANTE DE TIERRA DE POSTE SE ZAFO SOBRE AISLADOR. | C23050800085 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 69 | 2023-05-08 | 161667 | keep | 0 | May | 2023 | 0.11011 | 0.0015958 | Sustained | FALSE | FALSE | Not_TMED_Event | 2343
MAYAGÃœEZ | 2023-05-08 09:25 | 2023-05-08 19:32 | 30 | 10:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | M23050800095 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 607 | 2023-05-08 | 18210 | keep | 0 | May | 2023 | 0.012403 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-05-08 09:26 | 2023-05-08 11:04 | 10 | 1:38 | P | CAUSAS EXTERNAS | 1 X 8 EN XMR A CAUSA DE CAMION ENREDADO EN CABLES DE TELEFONO MOVIENDO ASI EL POSTE | R23050800024 | New_Event | Damage From Public | Include | Include | Public | 98 | 2023-05-08 | 980 | keep | 0 | May | 2023 | 0.00066747 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-08 09:30 | 2023-05-08 12:56 | 18 | 3:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA | S23050800047 | New_Event | Cutout Failure | Include | Include | Equipment | 206 | 2023-05-08 | 3708 | keep | 0 | May | 2023 | 0.0025255 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
GUAYAMA | 2023-05-08 09:34 | 2023-05-08 09:46 | 1 | 0:12 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23050800020 | New_Event | Animals | Include | Include | Wildlife | 12 | 2023-05-08 | 12 | keep | 0 | May | 2023 | 8.1731e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-08 09:40 | 2023-05-08 12:30 | 23 | 2:50 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA RELOCALIZAR SECUNDARIA A POSTE PRIMARIO NUEVO CG-230507-01 | C23050800106 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 170 | 2023-05-08 | 3910 | keep | 0 | May | 2023 | 0.0026631 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
HUMACAO | 2023-05-08 09:51 | 2023-05-08 09:52 | 1593 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 1593 | keep | 0 | May | 2023 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
HUMACAO | 2023-05-08 09:52 | 2023-05-08 10:25 | 200 | 0:33 | P | CAUSAS EXTERNAS | CG-230508-01 SE REEMPLAZO AISLADOR ROTO POR GLOBO DE HELIO | C23050800003 | Partial_restoration | Damage From Public | Include | Include | Public | 33 | 2023-05-08 | 6600 | keep | 0 | May | 2023 | 0.0044952 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-08 10:15 | 2023-05-08 13:16 | 233 | 3:01 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L SE RETIRO GLOBO DE LINEA | B23050800071 | New_Event | Damage From Public | Include | Include | Public | 181 | 2023-05-08 | 42173 | keep | 0 | May | 2023 | 0.028724 | 0.0001587 | Sustained | FALSE | FALSE | Not_TMED_Event | 233
PONCE | 2023-05-08 10:37 | 2023-05-08 11:25 | 60 | 0:48 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA EL MISMO PERSONAL DE LUMA HACIENDO TRABAJO PREVENTIVO CRUZO FASES | P23050800083 | New_Event | Damage From Public | Include | Include | Public | 48 | 2023-05-08 | 2880 | keep | 0 | May | 2023 | 0.0019616 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-08 10:47 | 2023-05-08 15:03 | 16 | 4:16 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA Y SE RETIRO PARARRAYO | S23050800066 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 256 | 2023-05-08 | 4096 | keep | 0 | May | 2023 | 0.0027898 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-05-08 10:50 | 2023-05-08 14:01 | 50 | 3:11 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L 1 X 50 EN C/L | S23050800069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2023-05-08 | 9550 | keep | 0 | May | 2023 | 0.0065045 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-08 11:09 | 2023-05-08 16:36 | 30 | 5:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23050800125 | New_Event | Primary Wire Break | Include | Include | Equipment | 327 | 2023-05-08 | 9810 | keep | 0 | May | 2023 | 0.0066815 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-08 11:17 | 2023-05-08 13:20 | 20 | 2:03 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS | M23050800132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-05-08 | 2460 | keep | 0 | May | 2023 | 0.0016755 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-08 11:26 | 2023-05-08 15:00 | 55 | 3:34 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA LINEAS CRUZADAS | P23050800093 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 214 | 2023-05-08 | 11770 | keep | 0 | May | 2023 | 0.0080165 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
ARECIBO | 2023-05-08 11:26 | 2023-05-09 19:17 | 1 | 31:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 37.5 KVA RELACIONADO AL EVENTO A23050800039 | A23050900095 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1911 | 2023-05-08 | 1911 | keep | 0 | May | 2023 | 0.0013016 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-08 11:29 | 2023-05-08 14:51 | 30 | 3:22 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23050800083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-05-08 | 6060 | keep | 0 | May | 2023 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-08 11:30 | 2023-05-08 13:32 | 6 | 2:02 | P | DESGANCHE | DESGANCHE 1 X 50 EN CORTE DE LINEA | P23050800094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-05-08 | 732 | keep | 0 | May | 2023 | 0.00049856 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-08 11:33 | 2023-05-08 14:08 | 1 | 2:35 | P | OTRAS CAUSAS | 1 X 65 TRANSCLOSURE SE REALIZO BYPASS A EQUIPOS DE MEDICION. | S23050800085 | New_Event | Other Causes | Include | Include | Other | 155 | 2023-05-08 | 155 | keep | 0 | May | 2023 | 0.00010557 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-08 11:35 | 2023-05-08 16:32 | 953 | 4:57 | P | LINEA DE TRANSMISION 38KV | CG-230508-02 SE SECCIONALIZO TRAMO DE LINEA PARA REEMPLAZO DE AISLADOR ROTO EN LINEA 0800 DE COMSAT A CIDRA | C23050800157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 297 | 2023-05-08 | 283041 | keep | 0 | May | 2023 | 0.19278 | 0.00064908 | Sustained | FALSE | FALSE | Not_TMED_Event | 953
BARRANQUITAS | 2023-05-08 11:40 | 2023-05-08 15:13 | 85 | 3:33 | P | ANIMAL | 1 X 40 Y 1 X 50 EN CORTES DE LINEA CRUCE POR AVE | C23050800160 | New_Event | Animals | Include | Include | Wildlife | 213 | 2023-05-08 | 18105 | keep | 0 | May | 2023 | 0.012331 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
PONCE | 2023-05-08 11:55 | 2023-05-08 12:13 | 10 | 0:18 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN RISER LINEAS ENREDADAS | P23050800100 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 18 | 2023-05-08 | 180 | keep | 0 | May | 2023 | 0.0001226 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-08 12:16 | 2023-05-08 14:35 | 2 | 2:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23050800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-08 | 278 | keep | 0 | May | 2023 | 0.00018934 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-08 12:20 | 2023-05-08 16:31 | 24 | 4:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDARIOS | S23050800100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 251 | 2023-05-08 | 6024 | keep | 0 | May | 2023 | 0.0041029 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
FAJARDO | 2023-05-08 12:22 | 2023-05-08 13:02 | 12 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R23050800038 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-05-08 | 480 | keep | 0 | May | 2023 | 0.00032693 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-08 12:23 | 2023-05-08 15:49 | 340 | 3:26 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | B23050800106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-05-08 | 70040 | keep | 0 | May | 2023 | 0.047704 | 0.00023157 | Sustained | FALSE | FALSE | Not_TMED_Event | 340
PONCE | 2023-05-08 12:36 | 2023-05-08 12:38 | 900 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23050800108 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-08 | 1800 | keep | 0 | May | 2023 | 0.001226 | 0.00061299 | Momentary | FALSE | FALSE | Not_TMED_Event | 900
CANOVANAS | 2023-05-08 12:47 | 2023-05-08 13:14 | 14 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | R23050800041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-05-08 | 378 | keep | 0 | May | 2023 | 0.00025745 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-05-08 13:00 | 2023-05-09 09:18 | 4 | 20:18 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23050800103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1218 | 2023-05-08 | 4872 | keep | 0 | May | 2023 | 0.0033183 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-08 13:15 | 2023-05-09 09:57 | 1 | 20:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIO Y 1 X 40 EN RISER | B23050800120 | New_Event | Cutout Failure | Include | Include | Equipment | 1242 | 2023-05-08 | 1242 | keep | 0 | May | 2023 | 0.00084592 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-08 13:18 | 2023-05-08 13:19 | 3046 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR LLEVA 1647-10 Y LLEVA 15% 1647-09 | R2305080000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-08 | 3046 | keep | 0 | May | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-05-08 13:18 | 2023-05-08 13:19 | 308 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1646-03 LLEVA 1647-10 Y LLEVA 15% 1647-09 | R2305080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-08 | 308 | keep | 0 | May | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-05-08 13:18 | 2023-05-08 13:19 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1646-03 LLEVA 1647-10 Y LLEVA 15% 1647-09 | R2305080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-08 | 61 | keep | 0 | May | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-05-08 13:19 | 2023-05-08 14:35 | 50 | 1:16 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | R23050800047 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-05-08 | 3800 | keep | 0 | May | 2023 | 0.0025882 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-08 13:19 | 2023-05-08 16:28 | 12 | 3:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | S23050800108 | New_Event | Secondary Wire Break | Include | Include | Equipment | 189 | 2023-05-08 | 2268 | keep | 0 | May | 2023 | 0.0015447 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-05-08 13:23 | 2023-05-09 14:00 | 10 | 24:37 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE DESGANCHO EN LINEAS SECUNDARIAS | A23050800062 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1477 | 2023-05-08 | 14770 | keep | 0 | May | 2023 | 0.01006 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-08 13:36 | 2023-05-08 19:32 | 9 | 5:56 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE LEVANTO LINEA PRIMARIA | B23050800125 | New_Event | Primary Wire Break | Include | Include | Equipment | 356 | 2023-05-08 | 3204 | keep | 0 | May | 2023 | 0.0021822 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
GUAYAMA | 2023-05-08 13:55 | 2023-05-08 15:05 | 11 | 1:10 | P | SECUNDARIA/OTROS | 1 X 20 EN TRANSFORMADOR FUSIBLE SULFATADO | P23050800126 | New_Event |  |  |  |  | 70 | 2023-05-08 | 770 | keep | 0 | May | 2023 | 0.00052444 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
YAUCO | 2023-05-08 13:55 | 2023-05-08 17:30 | 46 | 3:35 | P | CONDUCTOR ROTO O ABIERTO | CONECCION ROTA EN CORTE DE LINEA | P23050800125 | New_Event | Primary Wire Break | Include | Include | Equipment | 215 | 2023-05-08 | 9890 | keep | 0 | May | 2023 | 0.006736 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
BARRANQUITAS | 2023-05-08 13:59 | 2023-05-08 16:04 | 327 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | CG-230508-03 DISPARO DE BARRA SE DESPEGO BAJANTE DE PARARRAYO DE LA BARRA AL DISPARAR EL BKR 5250 AGUAS BUENAS SE APAGA LA BARRA | C23050800189 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-05-08 | 40875 | keep | 0 | May | 2023 | 0.02784 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
BARRANQUITAS | 2023-05-08 13:59 | 2023-05-08 16:04 | 1843 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | CG-230508-03 DISPARO DE BARRA SE DESPEGO BAJANTE DE PARARRAYO DE LA BARRA AL DISPARAR EL BKR 5250 AGUAS BUENAS SE APAGA LA BARRA | C23050800189 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-05-08 | 230375 | keep | 0 | May | 2023 | 0.15691 | 0.0012553 | Sustained | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-05-08 13:59 | 2023-05-08 16:04 | 2203 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | CG-230508-03 DISPARO DE BARRA SE DESPEGO BAJANTE DE PARARRAYO DE LA BARRA AL DISPARAR EL BKR 5250 AGUAS BUENAS SE APAGA LA BARRA | C23050800189 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-05-08 | 275375 | keep | 0 | May | 2023 | 0.18756 | 0.0015005 | Sustained | FALSE | FALSE | Not_TMED_Event | 2203
BARRANQUITAS | 2023-05-08 13:59 | 2023-05-08 16:04 | 2457 | 2:05 | S | DISPARO DE BARRA DE TRANSMISION | CG-230508-03 DISPARO DE BARRA SE DESPEGO BAJANTE DE PARARRAYO DE LA BARRA AL DISPARAR EL BKR 5250 AGUAS BUENAS SE APAGA LA BARRA | C23050800189 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 125 | 2023-05-08 | 307125 | keep | 0 | May | 2023 | 0.20918 | 0.0016735 | Sustained | FALSE | FALSE | Not_TMED_Event | 2457
ARECIBO | 2023-05-08 14:04 | 2023-05-08 16:23 | 15 | 2:19 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | A23050800067 | New_Event | Primary Wire Break | Include | Include | Equipment | 139 | 2023-05-08 | 2085 | keep | 0 | May | 2023 | 0.0014201 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-08 14:07 | 2023-05-08 14:30 | 9 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REPARAR BAJANTE SECUNDARIO | C23050800192 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-05-08 | 207 | keep | 0 | May | 2023 | 0.00014099 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-05-08 14:07 | 2023-05-08 14:58 | 1141 | 0:51 | P | DESGANCHE | SE ABRIO SALIDA DEL CONVERTIDOR PARA RETIRAR BAMBUA DE LA LINEA Y SE CERRO PUENTE | C23050800120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-05-08 | 58191 | keep | 0 | May | 2023 | 0.039634 | 0.00077713 | Sustained | FALSE | FALSE | Not_TMED_Event | 1141
SAN JUAN | 2023-05-08 14:10 | 2023-05-08 16:35 | 30 | 2:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23050800116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 145 | 2023-05-08 | 4350 | keep | 0 | May | 2023 | 0.0029628 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-08 14:15 | 2023-05-08 14:24 | 3114 | 0:09 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL | P23050800129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 9 | 2023-05-08 | 28026 | keep | 0 | May | 2023 | 0.019088 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
HUMACAO | 2023-05-08 14:46 | 2023-05-09 14:20 | 1 | 23:34 | P | LINEA DE TRANSMISION 38KV | 1 X 10 EN XMR Y SE CERRO C/L QUE ESTABA EL TRAMO SECCIONALIZADO DEBIDO A CAUSA DE AVERIA EN LA LINEA DEL 38KV DE CLIENTE PRIVADO AAA | C23050800205 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1414 | 2023-05-08 | 1414 | keep | 0 | May | 2023 | 0.00096307 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-08 14:52 | 2023-05-09 09:10 | 50 | 18:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050800073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1098 | 2023-05-08 | 54900 | keep | 0 | May | 2023 | 0.037392 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-08 15:10 | 2023-05-08 16:25 | 8 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA | B23050800012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-05-08 | 600 | keep | 0 | May | 2023 | 0.00040866 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-08 15:15 | 2023-05-08 17:07 | 40 | 1:52 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23050800219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-05-08 | 4480 | keep | 0 | May | 2023 | 0.0030513 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-08 15:18 | 2023-05-08 20:40 | 15 | 5:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A23050800078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 322 | 2023-05-08 | 4830 | keep | 0 | May | 2023 | 0.0032897 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-08 15:33 | 2023-05-08 15:34 | 363 | 0:01 | P | ALIMENTADOR AMARRADO | SE CERRO POR SCADA 90% DE SU CARGA POR EL 1620-01 | S2305080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-08 | 363 | keep | 0 | May | 2023 | 0.00024724 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
SAN JUAN | 2023-05-08 15:33 | 2023-05-08 15:34 | 36 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR SCADA EN SERVICIO LLEVA 1336-10 90% LLEVA 1620-02 60% | S2305080000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 36 | keep | 0 | May | 2023 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-08 15:33 | 2023-05-08 15:34 | 2231 | 0:01 | P | ALIMENTADOR AMARRADO | SE CERRO POR SCADA 60% DE SU CARGA POR EL 1620-01 | S2305080000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-08 | 2231 | keep | 0 | May | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
ARECIBO | 2023-05-08 15:41 | 2023-05-08 15:58 | 1 | 0:17 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE IDENTIFICO CAUSA | A23050800085 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-05-08 | 17 | keep | 0 | May | 2023 | 1.1579e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-08 15:46 | 2023-05-08 15:48 | 2524 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R2305080000X | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-08 | 5048 | keep | 0 | May | 2023 | 0.0034382 | 0.0017191 | Momentary | FALSE | FALSE | Not_TMED_Event | 2524
CANOVANAS | 2023-05-08 15:48 | 2023-05-09 09:05 | 19 | 17:17 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE DE LINEA A MACHETE | R23050800102 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1037 | 2023-05-08 | 19703 | keep | 0 | May | 2023 | 0.01342 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
PONCE | 2023-05-08 16:00 | 2023-05-08 16:10 | 1746 | 0:10 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR CON RECIERRE EN OFF SE CERRO POR CONTROL | P23050800151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-05-08 | 17460 | keep | 0 | May | 2023 | 0.011892 | 0.0011892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 959 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800152 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 3836 | keep | 0 | May | 2023 | 0.0026127 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 1382 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800152 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 5528 | keep | 0 | May | 2023 | 0.0037651 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 663 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800152 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 2652 | keep | 0 | May | 2023 | 0.0018063 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 1514 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 6056 | keep | 0 | May | 2023 | 0.0041247 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 1105 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 4420 | keep | 0 | May | 2023 | 0.0030104 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 4176 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 16704 | keep | 0 | May | 2023 | 0.011377 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 252 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 1008 | keep | 0 | May | 2023 | 0.00068654 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 2147 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800150 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 8588 | keep | 0 | May | 2023 | 0.0058492 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-05-08 16:11 | 2023-05-08 16:15 | 2858 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO L-10000 | B23050800151 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-08 | 11432 | keep | 0 | May | 2023 | 0.0077863 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
ARECIBO | 2023-05-08 16:23 | 2023-05-08 16:36 | 70 | 0:13 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO SE CERRO CORTED DE LINEA | A23050800067 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 13 | 2023-05-08 | 910 | keep | 0 | May | 2023 | 0.0006198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-08 16:31 | 2023-05-08 18:50 | 90 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | R23050800063 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-05-08 | 12510 | keep | 0 | May | 2023 | 0.0085205 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-05-08 16:43 | 2023-05-08 20:12 | 12 | 3:29 | P | DESGANCHE | 1 X 20 XMR DESGANCHE | S23050800136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 209 | 2023-05-08 | 2508 | keep | 0 | May | 2023 | 0.0017082 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-05-08 16:53 | 2023-05-08 18:25 | 150 | 1:32 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050800188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-05-08 | 13800 | keep | 0 | May | 2023 | 0.0093991 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-05-08 16:59 | 2023-05-08 19:05 | 75 | 2:06 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE CORTE DE LINEA | A23050800091 | New_Event | Primary Wire Break | Include | Include | Equipment | 126 | 2023-05-08 | 9450 | keep | 0 | May | 2023 | 0.0064364 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-05-08 17:54 | 2023-05-09 11:40 | 20 | 17:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | M23050800196 | New_Event | Cutout Failure | Include | Include | Equipment | 1066 | 2023-05-08 | 21320 | keep | 0 | May | 2023 | 0.014521 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-08 17:57 | 2023-05-08 17:59 | 1862 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23050800086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-08 | 3724 | keep | 0 | May | 2023 | 0.0025364 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-05-08 17:57 | 2023-05-08 17:59 | 1613 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23050800086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-08 | 3226 | keep | 0 | May | 2023 | 0.0021972 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-05-08 17:57 | 2023-05-08 17:59 | 1448 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23050800086 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-08 | 2896 | keep | 0 | May | 2023 | 0.0019725 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
CAGUAS | 2023-05-08 17:59 | 2023-05-08 21:25 | 753 | 3:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO CORTE DE LINEA PARA LEVANTAR LINEA PRIMARIA, SE REFIERE AL DTTO PARA INSTALAR POSTE EN MONTURA PASANTE. QUEDARON 4 CLIENTES FUERA SE CREO EL EVENTO C23050800309 EN COORDINACION CON SERVICIO | C23050800243 | New_Event | Primary Pole Failure | Include | Include | Equipment | 206 | 2023-05-08 | 155118 | keep | 0 | May | 2023 | 0.10565 | 0.00051286 | Sustained | FALSE | FALSE | Not_TMED_Event | 753
SAN JUAN | 2023-05-08 18:10 | 2023-05-09 14:05 | 1 | 19:55 | P | DESGANCHE | SE REALIZO DESGANCHE 1 X 15 EN TRANSFORMADOR SE ELIMINO MONTURA TRIFASICO Y PUSO IGLESIA POR MONOFASICA | S23050800145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1195 | 2023-05-08 | 1195 | keep | 0 | May | 2023 | 0.00081391 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-08 18:22 | 2023-05-08 18:44 | 11 | 0:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA PARA REPARAR BAJANTE SECUNDARIO | C23050800245 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2023-05-08 | 242 | keep | 0 | May | 2023 | 0.00016483 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-05-08 18:40 | 2023-05-08 18:41 | 1131 | 0:01 | T | PROBLEMA DEL CLIENTE | RECIERRE PERSONAL REALIZANDO PRUEBA EN RISER PROBO MALO EL RISER. SE LE DEJO DESCONECTADO AL CLIENTE PARA QUE REPARE | C23050800270 | New_Event | Customer-Related Interruption | Include | Include | Public | 1 | 2023-05-08 | 1131 | keep | 0 | May | 2023 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
AGUADILLA | 2023-05-08 18:47 | 2023-05-08 22:00 | 250 | 3:13 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23050800100 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 193 | 2023-05-08 | 48250 | keep | 0 | May | 2023 | 0.032863 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
ARECIBO | 2023-05-08 18:57 | 2023-05-08 20:05 | 75 | 1:08 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23050800106 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 68 | 2023-05-08 | 5100 | keep | 0 | May | 2023 | 0.0034736 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-05-08 19:00 | 2023-05-09 09:20 | 66 | 14:20 | P | DESGANCHE | ABRIR CORTE DE LINEA PARA REALIZAR DESGANCHE (PRIVADA) | S23050800171 | New_Event | Vegetation Contact | Include | Include | Vegetation | 860 | 2023-05-08 | 56760 | keep | 0 | May | 2023 | 0.038659 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
BARRANQUITAS | 2023-05-08 19:00 | 2023-05-09 09:30 | 10 | 14:30 | P | DESGANCHE | 3 X 50 EN C/L SE RETIRO RAMA SOBRE LA LINEA Y SE REMEPLAZO AISLADOR PARTIDO | C23050800274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 870 | 2023-05-08 | 8700 | keep | 0 | May | 2023 | 0.0059255 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-08 19:05 | 2023-05-09 11:36 | 62 | 16:31 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER NO CAUSA | S23050800155 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 991 | 2023-05-08 | 61442 | keep | 0 | May | 2023 | 0.041848 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
SAN JUAN | 2023-05-08 19:07 | 2023-05-08 21:27 | 30 | 2:20 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23050800157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-05-08 | 4200 | keep | 0 | May | 2023 | 0.0028606 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-08 19:07 | 2023-05-08 19:08 | 1593 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23050800276 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 1593 | keep | 0 | May | 2023 | 0.001085 | 0.001085 | Momentary | FALSE | FALSE | Not_TMED_Event | 1593
BARRANQUITAS | 2023-05-08 19:07 | 2023-05-09 09:05 | 12 | 13:58 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | C23050800275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 838 | 2023-05-08 | 10056 | keep | 0 | May | 2023 | 0.0068491 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-08 19:08 | 2023-05-09 09:43 | 12 | 14:35 | P | DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE PRIMARIO | C23050800277 | New_Event | Vegetation Contact | Include | Include | Vegetation | 875 | 2023-05-08 | 10500 | keep | 0 | May | 2023 | 0.0071515 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-05-08 19:18 | 2023-05-08 19:19 | 1 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 PUNTO CALIENTE EN AUXILIAR 2620A. SE CORRIGIO EL 5/14/2023. | A23050800126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1 | keep | 0 | May | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-08 19:18 | 2023-05-08 19:19 | 2266 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 PUNTO CALIENTE EN AUXILIAR 2620A. SE CORRIGIO EL 5/14/2023. | A23050800126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 2266 | keep | 0 | May | 2023 | 0.0015434 | 0.0015434 | Momentary | FALSE | FALSE | Not_TMED_Event | 2266
ARECIBO | 2023-05-08 19:18 | 2023-05-08 19:19 | 1399 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2600 PUNTO CALIENTE EN AUXILIAR 2620A. SE CORRIGIO EL 5/14/2023. | A23050800126 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-08 | 1399 | keep | 0 | May | 2023 | 0.00095285 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
AGUADILLA | 2023-05-08 19:21 | 2023-05-08 21:05 | 175 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO NEUTRAL PRIMARIO PARTIDO | M23050800206 | New_Event | Primary Wire Break | Include | Include | Equipment | 104 | 2023-05-08 | 18200 | keep | 0 | May | 2023 | 0.012396 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
BAYAMON | 2023-05-08 19:23 | 2023-05-09 07:00 | 27 | 11:37 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | S23050800166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 697 | 2023-05-08 | 18819 | keep | 0 | May | 2023 | 0.012818 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-05-08 19:24 | 2023-05-08 20:53 | 30 | 1:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | R23050800103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 89 | 2023-05-08 | 2670 | keep | 0 | May | 2023 | 0.0018185 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-05-08 19:39 | 2023-05-09 09:35 | 45 | 13:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA Y 1 X 40 EN RISER | R23050800105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 836 | 2023-05-08 | 37620 | keep | 0 | May | 2023 | 0.025623 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-05-08 19:41 | 2023-05-08 20:47 | 10 | 1:06 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23050800128 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 66 | 2023-05-08 | 660 | keep | 0 | May | 2023 | 0.00044952 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-08 20:00 | 2023-05-09 14:10 | 7 | 18:10 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 37.5 KVA X 37.5 KVA | M23050800208 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1090 | 2023-05-08 | 7630 | keep | 0 | May | 2023 | 0.0051968 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-05-08 20:21 | 2023-05-09 07:39 | 20 | 11:18 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR Y 1 X 30 EN C/L | C23050800287 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 678 | 2023-05-08 | 13560 | keep | 0 | May | 2023 | 0.0092357 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-08 20:48 | 2023-05-08 23:17 | 50 | 2:29 | P | MAL TIEMPO/RAYOS | 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23050800216 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 149 | 2023-05-08 | 7450 | keep | 0 | May | 2023 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-08 20:53 | 2023-05-08 20:54 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | B23050800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
SAN JUAN | 2023-05-08 20:59 | 2023-05-09 10:47 | 75 | 13:48 | P | ANIMAL | 1 X 65 1 X 80 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | S23050800194 | New_Event | Animals | Include | Include | Wildlife | 828 | 2023-05-08 | 62100 | keep | 0 | May | 2023 | 0.042296 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-05-08 21:02 | 2023-05-09 16:34 | 12 | 19:32 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | B23050800189 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1172 | 2023-05-08 | 14064 | keep | 0 | May | 2023 | 0.0095789 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-08 21:03 | 2023-05-09 14:10 | 5 | 17:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO LINEAS SECUNDARIAS ROTAS | A23050800139 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1027 | 2023-05-08 | 5135 | keep | 0 | May | 2023 | 0.0034974 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-05-08 21:21 | 2023-05-08 21:23 | 3387 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | B23050800194 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-08 | 6774 | keep | 0 | May | 2023 | 0.0046137 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2023-05-08 21:23 | 2023-05-08 23:35 | 1132 | 2:12 | P | CONDUCTOR ROTO O ABIERTO | BY-230508-01 SE SECCIONALIZO PARA REPARAR PUENTE | B23050800206 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 132 | 2023-05-08 | 149424 | keep | 0 | May | 2023 | 0.10177 | 0.000771 | Sustained | FALSE | FALSE | Not_TMED_Event | 1132
VEGA BAJA | 2023-05-08 21:35 | 2023-05-09 01:40 | 50 | 4:05 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23050800144 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2023-05-08 | 12250 | keep | 0 | May | 2023 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-05-08 21:36 | 2023-05-09 09:55 | 4 | 12:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A23050800145 | New_Event | Cutout Failure | Include | Include | Equipment | 739 | 2023-05-08 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-05-08 21:40 | 2023-05-09 16:55 | 4 | 19:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE PRIMARIO Y XMR DE 25KVA X 25KVA | C23050800309 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1155 | 2023-05-08 | 4620 | keep | 0 | May | 2023 | 0.0031467 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-05-08 22:40 | 2023-05-09 01:36 | 231 | 2:56 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23050800316 | New_Event | Animals | Include | Include | Wildlife | 176 | 2023-05-08 | 40656 | keep | 0 | May | 2023 | 0.027691 | 0.00015733 | Sustained | FALSE | FALSE | Not_TMED_Event | 231
CAGUAS | 2023-05-08 23:21 | 2023-05-08 23:22 | 1725 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050800321 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-08 | 1725 | keep | 0 | May | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
AGUADILLA | 2023-05-08 23:23 | 2023-05-09 01:58 | 1485 | 2:35 | T | CAUSAS EXTERNAS | POSTES PRIMARIOS PARTIDOS POR CAMION. SE ABRIO PUENTES PARA SECCIONALIZAR LA AVERIA. | M23050800235 | New_Event | Damage From Public | Include | Include | Public | 155 | 2023-05-08 | 230175 | keep | 0 | May | 2023 | 0.15677 | 0.0010114 | Sustained | FALSE | FALSE | Not_TMED_Event | 1485
YAUCO | 2023-05-08 23:32 | 2023-05-09 08:30 | 66 | 8:58 | P | ARBOL SOBRE LINEA | 1 X 100 EN CORTE DE LINEA SE RETIRO ARBOL | P23050800366 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 538 | 2023-05-08 | 35508 | keep | 0 | May | 2023 | 0.024184 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
VEGA BAJA | 2023-05-08 23:35 | 2023-05-09 00:34 | 1251 | 0:59 | P | CONDUCTOR ROTO O ABIERTO | BY-230508-01 SE REPARO PUENTE ABIERTO | B23050800206 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 59 | 2023-05-08 | 73809 | keep | 0 | May | 2023 | 0.050271 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-09 00:13 | 2023-05-09 00:16 | 327 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO POR CONTROL | C2305090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-09 | 981 | keep | 0 | May | 2023 | 0.00066815 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
VEGA BAJA | 2023-05-09 00:34 | 2023-05-09 00:45 | 3387 | 0:11 | T | DESCONECTIVO DEFECTUOSO | BY-230508-01 SE DISPARO BKR PARA CERRAR MACHETE CON PUNTO CALIENTE | B23050800206 | New_Event | Switch Failure | Include | Include | Equipment | 11 | 2023-05-09 | 37257 | keep | 0 | May | 2023 | 0.025376 | 0.0023069 | Sustained | FALSE | FALSE | Not_TMED_Event | 3387
CAGUAS | 2023-05-09 01:05 | 2023-05-09 01:06 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050900006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
AGUADILLA | 2023-05-09 01:58 | 2023-05-09 18:30 | 750 | 16:32 | P | CAUSAS EXTERNAS | SE REMPLAZO POSTES SE ABRIO MACHETES PARA CERRAR PUENTES PRIMARIOS | M23050900011 | New_Event | Damage From Public | Include | Include | Public | 992 | 2023-05-09 | 744000 | keep | 0 | May | 2023 | 0.50674 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
FAJARDO | 2023-05-09 03:20 | 2023-05-09 11:55 | 145 | 8:35 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 40 EN CORTE DE LINEA SE DESCRUZO LINEA | R23050900003 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 515 | 2023-05-09 | 74675 | keep | 0 | May | 2023 | 0.050861 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
MAYAGÃœEZ | 2023-05-09 05:44 | 2023-05-09 05:45 | 4304 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M2305090018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 4304 | keep | 0 | May | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
BAYAMON | 2023-05-09 05:51 | 2023-05-09 07:49 | 54 | 1:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN RISER Y SE REEMPLAZO PORTAFUSIBLE QUEMADO | S23050900006 | New_Event | Cutout Failure | Include | Include | Equipment | 118 | 2023-05-09 | 6372 | keep | 0 | May | 2023 | 0.0043399 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
MAYAGÃœEZ | 2023-05-09 06:00 | 2023-05-09 14:05 | 15 | 8:05 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050900072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 485 | 2023-05-09 | 7275 | keep | 0 | May | 2023 | 0.004955 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-09 06:31 | 2023-05-09 11:00 | 40 | 4:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23050900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2023-05-09 | 10760 | keep | 0 | May | 2023 | 0.0073286 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-09 07:00 | 2023-05-09 07:01 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23050900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
CAGUAS | 2023-05-09 07:11 | 2023-05-09 07:14 | 1879 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C2305090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-09 | 5637 | keep | 0 | May | 2023 | 0.0038393 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
SAN JUAN | 2023-05-09 07:17 | 2023-05-09 13:37 | 40 | 6:20 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA DESGANCHE | S23050900013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 380 | 2023-05-09 | 15200 | keep | 0 | May | 2023 | 0.010353 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-09 07:17 | 2023-05-09 12:00 | 30 | 4:43 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23050900012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 283 | 2023-05-09 | 8490 | keep | 0 | May | 2023 | 0.0057825 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-09 07:20 | 2023-05-09 09:53 | 25 | 2:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C23050900016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 153 | 2023-05-09 | 3825 | keep | 0 | May | 2023 | 0.0026052 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-05-09 07:39 | 2023-05-09 09:28 | 50 | 1:49 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR PALOMA | R23050900015 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-05-09 | 5450 | keep | 0 | May | 2023 | 0.003712 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-09 07:43 | 2023-05-09 11:10 | 40 | 3:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA ZAFADA DE AISLADOR | M23050900036 | New_Event | Primary Wire Break | Include | Include | Equipment | 207 | 2023-05-09 | 8280 | keep | 0 | May | 2023 | 0.0056395 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-05-09 08:03 | 2023-05-09 08:04 | 2608 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050900021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 2608 | keep | 0 | May | 2023 | 0.0017763 | 0.0017763 | Momentary | FALSE | FALSE | Not_TMED_Event | 2608
BAYAMON | 2023-05-09 08:04 | 2023-05-09 16:37 | 101 | 8:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L FUERTES VIENTOS | S23050900018 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 513 | 2023-05-09 | 51813 | keep | 0 | May | 2023 | 0.03529 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
BARRANQUITAS | 2023-05-09 08:04 | 2023-05-09 08:06 | 598 | 0:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 CARGA X 3405-03 | C23050900023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-09 | 1196 | keep | 0 | May | 2023 | 0.00081459 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2023-05-09 08:04 | 2023-05-09 08:06 | 2486 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C23050900023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-09 | 4972 | keep | 0 | May | 2023 | 0.0033864 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
BARRANQUITAS | 2023-05-09 08:04 | 2023-05-09 08:06 | 1403 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 | C23050900023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-09 | 2806 | keep | 0 | May | 2023 | 0.0019112 | 0.00095558 | Momentary | FALSE | FALSE | Not_TMED_Event | 1403
BARRANQUITAS | 2023-05-09 08:04 | 2023-05-09 08:06 | 1001 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3800 LLEVA EL 3403-01 | C23050900023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-09 | 2002 | keep | 0 | May | 2023 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2023-05-09 08:06 | 2023-05-09 08:57 | 726 | 0:51 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR LLEVA 1346-04 SE ABRIO N/O EN SU-4 Y SE CERRO 100% 1303-03 QUEDA FUERA 1346-04 CONTINUAN PATRULLANDO | S23050900057 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2023-05-09 | 37026 | keep | 0 | May | 2023 | 0.025218 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-05-09 08:06 | 2023-05-09 10:32 | 3932 | 2:26 | T | ALIMENTADOR AMARRADO | DISPARO 1303-03 Y SE ABRIO N/O EN SU-4 Y SE PATRULLO NO SE REPORTO CAUSA Y SE PASO CARGA AL 1346-03 CERRANDO N/O CARR.176 ESQ. CARR.1 100% EN SERVICIO | S23050900182 | New_Event | Feeder Load Transferred | Include | Include | Other | 146 | 2023-05-09 | 574072 | keep | 0 | May | 2023 | 0.391 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
AGUADILLA | 2023-05-09 08:10 | 2023-05-09 17:05 | 60 | 8:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 Y 1 X 30 EN CORTES DE LINEA DISTINTOS MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23050900037 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 535 | 2023-05-09 | 32100 | keep | 0 | May | 2023 | 0.021863 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-09 08:34 | 2023-05-09 09:27 | 766 | 0:53 | P | ALIMENTADOR AMARRADO | DISPARO DEL MAIN BKR DE LA 1909-00 POR PROTECCION DEFECTUOSA EN EL 1909-09 50% DE SU CARGA POR EL 1909-07 BY-230509-01 | S23050900062 | New_Event | Feeder Load Transferred | Include | Include | Other | 53 | 2023-05-09 | 40598 | keep | 0 | May | 2023 | 0.027651 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-05-09 08:34 | 2023-05-09 09:27 | 2435 | 0:53 | T | ALIMENTADOR AMARRADO | DISPARO DEL MAIN BKR DE LA 1909-00 POR PROTECCION DEFECTUOSA EN EL 1909-09 CARGA POR EL 1909-08 BY-230509-01 | S23050900062 | New_Event | Feeder Load Transferred | Include | Include | Other | 53 | 2023-05-09 | 129055 | keep | 0 | May | 2023 | 0.087899 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-09 08:34 | 2023-05-09 09:27 | 1139 | 0:53 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER SE CERRO TIE BREAKER CONTRA LA 1907-00 Y QUEDO EN SERVICIO BY-230509-01 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 53 | 2023-05-09 | 60367 | keep | 0 | May | 2023 | 0.041116 | 0.00077577 | Sustained | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2023-05-09 08:34 | 2023-05-09 09:27 | 2956 | 0:53 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER SE CERRO TIE BREAKER CONTRA LA 1907-00 Y QUEDO EN SERVICIO BY-230509-01 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 53 | 2023-05-09 | 156668 | keep | 0 | May | 2023 | 0.10671 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-05-09 08:34 | 2023-05-09 09:57 | 4456 | 1:23 | S | CONDUCTOR ROTO O ABIERTO | DISPARO DE MAIN BREAKER SE CERRO TIE BREAKER CONTRA LA 1907-00 SE SECCIONALIZO Y QUEDO 70% EN SERVICIO BY-230509-01 | S23050900062 | New_Event | Primary Wire Break | Include | Include | Equipment | 83 | 2023-05-09 | 369848 | keep | 0 | May | 2023 | 0.2519 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
ARECIBO | 2023-05-09 08:36 | 2023-05-09 10:49 | 50 | 2:13 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23050900016 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-05-09 | 6650 | keep | 0 | May | 2023 | 0.0045293 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-09 08:40 | 2023-05-09 08:41 | 2708 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR EN SERVICIO | R23050900036 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-09 | 2708 | keep | 0 | May | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-05-09 08:41 | 2023-05-09 10:43 | 80 | 2:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L SE REEMPLAZO CAJA EN RISER | R23050900042 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 122 | 2023-05-09 | 9760 | keep | 0 | May | 2023 | 0.0066475 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-09 08:53 | 2023-05-09 13:23 | 4 | 4:30 | P | PROBLEMA DEL CLIENTE | 1 X 65 EN C/L Y SE DEJO FUERA 1 CLIENTE POR AVERIA EN PARARAYO PROBLEMA DE CLIENTE | C23050900029 | New_Event | Customer-Related Interruption | Include | Include | Public | 270 | 2023-05-09 | 1080 | keep | 0 | May | 2023 | 0.00073558 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-05-09 09:10 | 2023-05-09 13:01 | 1 | 3:51 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | A23050900026 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 231 | 2023-05-09 | 231 | keep | 0 | May | 2023 | 0.00015733 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-09 09:10 | 2023-05-09 14:00 | 8 | 4:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23050900027 | New_Event | Primary Wire Break | Include | Include | Equipment | 290 | 2023-05-09 | 2320 | keep | 0 | May | 2023 | 0.0015801 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-09 09:15 | 2023-05-09 16:46 | 47 | 7:31 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE DE 45' 1X25 EN C/L Y 1X10 EN XMR | R23050900047 | New_Event | Primary Pole Failure | Include | Include | Equipment | 451 | 2023-05-09 | 21197 | keep | 0 | May | 2023 | 0.014437 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
GUAYAMA | 2023-05-09 09:15 | 2023-05-09 11:50 | 12 | 2:35 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR 15KVA A 4160VOLTS POR 37.5 KVA A 4160 VOLTS | P23050900061 | New_Event | Service Transformer Failure | Include | Include | Equipment | 155 | 2023-05-09 | 1860 | keep | 0 | May | 2023 | 0.0012668 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-09 09:20 | 2023-05-10 16:00 | 200 | 30:40 | P | DESGANCHE | ABRIR CORTE DE LINEA PARA REALIZAR DESGANCHE (PRIVADA) | S23050800171 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1840 | 2023-05-09 | 368000 | keep | 0 | May | 2023 | 0.25064 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-09 09:28 | 2023-05-09 09:30 | 766 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE MAIN BREAKER AL CERRAR EL 1909-09 SE CERRO QUEDO EN SERVICIO BY-230509-01 CARGA POR EL 1909-07 | S23050900062 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-09 | 1532 | keep | 0 | May | 2023 | 0.0010434 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-09 09:28 | 2023-05-09 09:30 | 222 | 0:02 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER AL CERRAR EL 1909-09 SE CERRO QUEDO EN SERVICIO BY-230509-01 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 2 | 2023-05-09 | 444 | keep | 0 | May | 2023 | 0.00030241 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-05-09 09:28 | 2023-05-09 09:30 | 2466 | 0:02 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER AL CERRAR EL 1909-09 SE CERRO QUEDO EN SERVICIO BY-230509-01 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 2 | 2023-05-09 | 4932 | keep | 0 | May | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-05-09 09:28 | 2023-05-09 09:30 | 2435 | 0:02 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER AL CERRAR EL 1909-09 SE CERRO QUEDO EN SERVICIO BY-230509-01 CARGA POR EL 1909-08 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 2 | 2023-05-09 | 4870 | keep | 0 | May | 2023 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-09 09:28 | 2023-05-09 09:30 | 1139 | 0:02 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER AL CERRAR EL 1909-09 SE CERRO QUEDO EN SERVICIO BY-230509-01 LLEVA 50% DEL 1709-03 | S23050900062 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 2 | 2023-05-09 | 2278 | keep | 0 | May | 2023 | 0.0015515 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-09 09:28 | 2023-05-09 09:30 | 2956 | 0:02 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER AL CERRAR EL 1909-09 SE CERRO QUEDO EN SERVICIO BY-230509-01 LLEVA 1907-05 | S23050900062 | Partial_restoration | Protection Miscoordination | Include | Include | Other | 2 | 2023-05-09 | 5912 | keep | 0 | May | 2023 | 0.0040266 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-09 09:28 | 2023-05-09 12:00 | 150 | 2:32 | P | ANIMAL | 2 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M23050900058 | New_Event | Animals | Include | Include | Wildlife | 152 | 2023-05-09 | 22800 | keep | 0 | May | 2023 | 0.015529 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-05-09 09:29 | 2023-05-09 16:12 | 5 | 6:43 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN RISER SE ENCONTRO AVERIA SOTERRADA DEL SU-3 @ SU-2. 100% EN SERVICIO | C23050900103 | New_Event | UG Cable Fault | Include | Include | Equipment | 403 | 2023-05-09 | 2015 | keep | 0 | May | 2023 | 0.0013724 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-05-09 09:44 | 2023-05-09 11:55 | 11 | 2:11 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA PAJARO CRUZO FASE | P23050900066 | New_Event | Animals | Include | Include | Wildlife | 131 | 2023-05-09 | 1441 | keep | 0 | May | 2023 | 0.00098146 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
AGUADILLA | 2023-05-09 09:45 | 2023-05-09 18:40 | 1 | 8:55 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23050900063 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 535 | 2023-05-09 | 535 | keep | 0 | May | 2023 | 0.00036439 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-09 09:48 | 2023-05-09 12:27 | 22 | 2:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA LAVANTAR SECUNDARIA | R23050900053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 159 | 2023-05-09 | 3498 | keep | 0 | May | 2023 | 0.0023825 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
ARECIBO | 2023-05-09 09:49 | 2023-05-09 14:55 | 80 | 5:06 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23050900036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 306 | 2023-05-09 | 24480 | keep | 0 | May | 2023 | 0.016673 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-09 09:57 | 2023-05-09 11:05 | 1336 | 1:08 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE MAIN BREAKER SE CERRO DE LA 1907-00 POR AVERIA EN EL 1909-09 - EN SERVICIO EL OTRO 30% QUE FALTABA BY-230509-01 | S23050900062 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 68 | 2023-05-09 | 90848 | keep | 0 | May | 2023 | 0.061876 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-09 10:08 | 2023-05-09 19:00 | 20 | 8:52 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA DESGANCHE COMPANIA PRIVADA | S23050900358 | New_Event | Vegetation Contact | Include | Include | Vegetation | 532 | 2023-05-09 | 10640 | keep | 0 | May | 2023 | 0.0072469 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-09 10:10 | 2023-05-09 10:45 | 13 | 0:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75 KVA X 75 KVA CON DERRAME DE ACEITE | R23050900054 | New_Event | Service Transformer Failure | Include | Include | Equipment | 35 | 2023-05-09 | 455 | keep | 0 | May | 2023 | 0.0003099 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-05-09 10:15 | 2023-05-09 12:19 | 30 | 2:04 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S23050900048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2023-05-09 | 3720 | keep | 0 | May | 2023 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-09 10:20 | 2023-05-09 12:16 | 13 | 1:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | P23050900074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-05-09 | 1508 | keep | 0 | May | 2023 | 0.0010271 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-05-09 10:25 | 2023-05-09 10:26 | 5668 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | R23050900059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 5668 | keep | 0 | May | 2023 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
HUMACAO | 2023-05-09 10:30 | 2023-05-09 16:30 | 10 | 6:00 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO BANCO DE XMR PARA REEMPLAZAR POSTE PRIMARIO | C23050900112 | New_Event | Primary Pole Failure | Include | Include | Equipment | 360 | 2023-05-09 | 3600 | keep | 0 | May | 2023 | 0.0024519 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-09 10:41 | 2023-05-09 11:57 | 4 | 1:16 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR DESPEJE DE LINEA | R23050900063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-05-09 | 304 | keep | 0 | May | 2023 | 0.00020705 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-05-09 10:44 | 2023-05-09 10:47 | 661 | 0:03 | P | DESGANCHE | DISPARO ALIMENTADOR SE PROBO QUEDO EN SERVICIO 16% POR 1620-02 | S23050900378 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-05-09 | 1983 | keep | 0 | May | 2023 | 0.0013506 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-05-09 10:44 | 2023-05-09 10:47 | 3718 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE PROBO QUEDO EN SERVICIO LLEVA 16% DEL 1206-03 | S23050900378 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-09 | 11154 | keep | 0 | May | 2023 | 0.0075969 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
HUMACAO | 2023-05-09 10:49 | 2023-05-09 14:21 | 19 | 3:32 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23050900055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2023-05-09 | 4028 | keep | 0 | May | 2023 | 0.0027435 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BARRANQUITAS | 2023-05-09 10:49 | 2023-05-09 14:31 | 14 | 3:42 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23050900056 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-05-09 | 3108 | keep | 0 | May | 2023 | 0.0021168 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-05-09 10:59 | 2023-05-09 12:25 | 10 | 1:26 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE IDENTIFICO CAUSA | M23050900075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 86 | 2023-05-09 | 860 | keep | 0 | May | 2023 | 0.00058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-09 11:05 | 2023-05-09 11:39 | 766 | 0:34 | P | ALIMENTADOR AMARRADO | SE ABRIO TIE BREAKER CONTRA LA 1907-00 SE ENERGIZO EL MAIN XMR DE LA 1909-00 BY-230509-01 50% DEL 1709-03 POR 1909-07 | S23050900062 | New_Event | Feeder Load Transferred | Include | Include | Other | 34 | 2023-05-09 | 26044 | keep | 0 | May | 2023 | 0.017738 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-05-09 11:05 | 2023-05-09 11:17 | 222 | 0:12 | S | PROTECCION DEFECTUOSA | SE ABRIO TIE BREAKER CONTRA LA 1909-09 Y SE CERRO MAIN BRAKER DE LA 1907-00 POR AVERIA EN EL 1909-09 Y PROTECCION DEFECTUOSA DEL MISMO BY-230509-01 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 12 | 2023-05-09 | 2664 | keep | 0 | May | 2023 | 0.0018144 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-05-09 11:05 | 2023-05-09 11:17 | 2466 | 0:12 | S | PROTECCION DEFECTUOSA | SE ABRIO TIE BREAKER CONTRA LA 1909-09 Y SE CERRO MAIN BRAKER DE LA 1907-00 POR AVERIA EN EL 1909-09 Y PROTECCION DEFECTUOSA DEL MISMO BY-230509-01 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 12 | 2023-05-09 | 29592 | keep | 0 | May | 2023 | 0.020155 | 0.0016796 | Sustained | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-05-09 11:05 | 2023-05-09 11:39 | 2435 | 0:34 | S | PROTECCION DEFECTUOSA | DISPARO DE MAIN BREAKER AL CERRAR EL 1909-09 SE CERRO QUEDO EN SERVICIO BY-230509-01 CARGA POR EL 1909-08 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 34 | 2023-05-09 | 82790 | keep | 0 | May | 2023 | 0.056388 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-09 11:05 | 2023-05-09 11:39 | 1139 | 0:34 | S | PROTECCION DEFECTUOSA | SE ABRIO TIE BREAKER CONTRA LA 1907-00 SE ENERGIZO EL MAIN XMR DE LA 1909-00 BY-230509-01 LLEVA 50% DEL 1709-03 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 34 | 2023-05-09 | 38726 | keep | 0 | May | 2023 | 0.026376 | 0.00077577 | Sustained | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2023-05-09 11:05 | 2023-05-09 11:39 | 2956 | 0:34 | S | PROTECCION DEFECTUOSA | SE ABRIO TIE BREAKER CONTRA LA 1907-00 SE ENERGIZO EL MAIN XMR DE LA 1909-00 BY-230509-01 | S23050900062 | New_Event | Protection Miscoordination | Include | Include | Other | 34 | 2023-05-09 | 100504 | keep | 0 | May | 2023 | 0.068453 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-05-09 11:05 | 2023-05-09 12:14 | 4456 | 1:09 | T | CONDUCTOR ROTO O ABIERTO | VOLVIO A DISPARAR MAIN BKR SE SECCIONALIZO TRAMO PARA LEVANTAR CONDUCTOR PRIMARIO BY-230509-01 60% EN SERVICIO | S23050900062 | New_Event | Primary Wire Break | Include | Include | Equipment | 69 | 2023-05-09 | 307464 | keep | 0 | May | 2023 | 0.20941 | 0.003035 | Sustained | FALSE | FALSE | Not_TMED_Event | 4456
BARRANQUITAS | 2023-05-09 11:17 | 2023-05-09 15:29 | 1 | 4:12 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO DE LINEA A CAJA EN EL RISER | C23050900065 | New_Event | Primary Wire Break | Include | Include | Equipment | 252 | 2023-05-09 | 252 | keep | 0 | May | 2023 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-09 11:22 | 2023-05-09 11:24 | 661 | 0:02 | P | DESGANCHE | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 16% POR 1620-02 | S23050900432 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-05-09 | 1322 | keep | 0 | May | 2023 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-05-09 11:22 | 2023-05-09 11:24 | 3718 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 16% DEL 1206-03 | S23050900432 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-09 | 7436 | keep | 0 | May | 2023 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2023-05-09 11:23 | 2023-05-09 19:25 | 9 | 8:02 | P | ARBOL SOBRE LINEA | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS ROTAS POR ARBOL QUE CAYO SOBRE ELLAS | A23050900052 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 482 | 2023-05-09 | 4338 | keep | 0 | May | 2023 | 0.0029546 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-05-09 11:25 | 2023-05-09 14:40 | 643 | 3:15 | T | ALIMENTADOR AMARRADO | DISPARO SE ABRIO N/O Y SE SECCIONALIZO ALAMBRE EN EL PISO 1530-09 | S23050900440 | New_Event | Feeder Load Transferred | Include | Include | Other | 195 | 2023-05-09 | 125385 | keep | 0 | May | 2023 | 0.085399 | 0.00043794 | Sustained | FALSE | FALSE | Not_TMED_Event | 643
SAN JUAN | 2023-05-09 11:25 | 2023-05-09 12:20 | 1310 | 0:55 | T | CONDUCTOR ROTO O ABIERTO | DISPARO ALIMENTADOR SE ENCONTRO ALAMBRE EN EL PISO TRAS PATIO | S23050900516 | New_Event | Primary Wire Break | Include | Include | Equipment | 55 | 2023-05-09 | 72050 | keep | 0 | May | 2023 | 0.049073 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
SAN JUAN | 2023-05-09 11:26 | 2023-05-09 11:32 | 1825 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO QUEDO EN SERVICIO SU CARGA 1118-9 | S23050900443 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-09 | 10950 | keep | 0 | May | 2023 | 0.007458 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-05-09 11:26 | 2023-05-09 11:32 | 4398 | 0:06 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 1118-08 | S23050900443 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-05-09 | 26388 | keep | 0 | May | 2023 | 0.017973 | 0.0029955 | Sustained | FALSE | FALSE | Not_TMED_Event | 4398
FAJARDO | 2023-05-09 11:38 | 2023-05-09 12:56 | 158 | 1:18 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR PALOMA | R23050900071 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-05-09 | 12324 | keep | 0 | May | 2023 | 0.0083938 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
CANOVANAS | 2023-05-09 11:44 | 2023-05-09 13:10 | 6 | 1:26 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA CON DERRAME DE ACEITE | R23050900073 | New_Event | Service Transformer Failure | Include | Include | Equipment | 86 | 2023-05-09 | 516 | keep | 0 | May | 2023 | 0.00035145 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-09 12:00 | 2023-05-09 13:09 | 6 | 1:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA CON PERSONAL LOW VOLTAGE | S23050900498 | New_Event | Secondary Wire Break | Include | Include | Equipment | 69 | 2023-05-09 | 414 | keep | 0 | May | 2023 | 0.00028197 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-09 12:10 | 2023-05-09 12:12 | 661 | 0:02 | P | DESGANCHE | DISAPRO INTERRUPTOR SE PROBO QUEDO EN SERVICIO 16% POR 1620-02 | S23050900520 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-05-09 | 1322 | keep | 0 | May | 2023 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-05-09 12:10 | 2023-05-09 12:12 | 3718 | 0:02 | T | ALIMENTADOR AMARRADO | DISAPRO INTERRUPTOR SE PROBO QUEDO EN SERVICIO LLEVA 16% DEL 1206-03 | S23050900520 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-09 | 7436 | keep | 0 | May | 2023 | 0.0050646 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
BAYAMON | 2023-05-09 12:14 | 2023-05-09 13:44 | 1782 | 1:30 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE LEVANTO CONDUCTOR PRIMARIO BY-230509-01 | S23050900062 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 90 | 2023-05-09 | 160380 | keep | 0 | May | 2023 | 0.10923 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-09 12:20 | 2023-05-09 12:23 | 437 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | DISPARO SE ENCONTRO ALAMBRE EN EL PISO TRAS PATIO SE ABRIO N/O CONTRA 1530-07 | S23050900440 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 3 | 2023-05-09 | 1311 | keep | 0 | May | 2023 | 0.00089292 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-09 12:22 | 2023-05-09 13:15 | 150 | 0:53 | P | DESGANCHE | 2 X 140 EN CORTE DE LINEA SE RETIRO BAMBU | M23050900097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2023-05-09 | 7950 | keep | 0 | May | 2023 | 0.0054147 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-09 12:23 | 2023-05-09 14:40 | 1310 | 2:17 | T | CONDUCTOR ROTO O ABIERTO | DISPARO SE ENCONTRO ALAMBRE EN EL PISO TRAS PATIO SE ABRIO N/O CONTRA 1530-07 | S23050900440 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 137 | 2023-05-09 | 179470 | keep | 0 | May | 2023 | 0.12224 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
HUMACAO | 2023-05-09 12:35 | 2023-05-09 13:10 | 15 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23050900077 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-05-09 | 525 | keep | 0 | May | 2023 | 0.00035758 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-09 12:43 | 2023-05-09 14:36 | 661 | 1:53 | P | DESGANCHE | SE RETIRO RAMA SOBRE LINEA Y SE DEVOLVIO 16% DE SU CARGA QUE ESTABA POR 1620-2 AL 1206-03 | S23050900540 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-05-09 | 74693 | keep | 0 | May | 2023 | 0.050873 | 0.0004502 | Sustained | FALSE | FALSE | Not_TMED_Event | 661
SAN JUAN | 2023-05-09 12:43 | 2023-05-09 13:21 | 3718 | 0:38 | T | ALIMENTADOR AMARRADO | DISPARO SE ABRIO N/O CONTRA 1206-03 Y SE CERRO INTERRUPTOR 100% EN SERVICIO SE DEJO FUERA 16% DEL 1206-03 RAMA SOBRE LINEA | S23050900540 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 38 | 2023-05-09 | 141284 | keep | 0 | May | 2023 | 0.096228 | 0.0025323 | Sustained | FALSE | FALSE | Not_TMED_Event | 3718
VEGA BAJA | 2023-05-09 12:50 | 2023-05-09 16:35 | 60 | 3:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23050900070 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 225 | 2023-05-09 | 13500 | keep | 0 | May | 2023 | 0.0091948 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-05-09 12:58 | 2023-05-09 14:56 | 15 | 1:58 | P | NO SE REPORTO CAUSA | 1 X 20 EN TRANSFORMADOR NO SE REPORTO CAUSA | A23050900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2023-05-09 | 1770 | keep | 0 | May | 2023 | 0.0012055 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-05-09 12:59 | 2023-05-09 14:15 | 10 | 1:16 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 25 KVA X 25 KVA | M23050900123 | New_Event | Service Transformer Failure | Include | Include | Equipment | 76 | 2023-05-09 | 760 | keep | 0 | May | 2023 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-09 13:00 | 2023-05-09 22:03 | 558 | 9:03 | P | CONDUCTOR ROTO O ABIERTO | SJ-230509-05 SE TRANSFIRIO 90% DEL 1422-05 AL 1328-02 POR PUENTE ABIERTO TRASPATIO ENTRO EN SERVICIO 99% DEL 1422-05 | S23050900563 | New_Event | Primary Wire Break | Include | Include | Equipment | 543 | 2023-05-09 | 302994 | keep | 0 | May | 2023 | 0.20637 | 0.00038005 | Sustained | FALSE | FALSE | Not_TMED_Event | 558
HUMACAO | 2023-05-09 13:03 | 2023-05-09 18:13 | 39 | 5:10 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN C/L SE REEMPLAZO DISCO PARTIDO | C23050900080 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 310 | 2023-05-09 | 12090 | keep | 0 | May | 2023 | 0.0082344 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
UTUADO | 2023-05-09 13:06 | 2023-05-09 18:00 | 40 | 4:54 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE CORRIGIO LINEAS CRUZADAS | A23050900077 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 294 | 2023-05-09 | 11760 | keep | 0 | May | 2023 | 0.0080097 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-09 13:09 | 2023-05-09 13:10 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | S23050900578 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 1271 | keep | 0 | May | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
HUMACAO | 2023-05-09 13:09 | 2023-05-09 17:03 | 1 | 3:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA AVERIADA | C23050900081 | New_Event | Cutout Failure | Include | Include | Equipment | 234 | 2023-05-09 | 234 | keep | 0 | May | 2023 | 0.00015938 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-09 13:10 | 2023-05-09 14:07 | 6 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA CON PERSONAL LOW VOLTAGE | S23050900498 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-05-09 | 342 | keep | 0 | May | 2023 | 0.00023293 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-09 13:11 | 2023-05-09 14:58 | 17 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA CONSTRUIR TOMA NUEVA SOTERRADA | R23050900075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-05-09 | 1819 | keep | 0 | May | 2023 | 0.0012389 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-05-09 13:11 | 2023-05-09 18:45 | 12 | 5:34 | P | CAUSAS EXTERNAS | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA CAMION SE LLEVO SECUNDARIA | B23050900057 | New_Event | Damage From Public | Include | Include | Public | 334 | 2023-05-09 | 4008 | keep | 0 | May | 2023 | 0.0027298 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-09 13:26 | 2023-05-10 09:15 | 50 | 19:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | S23050900599 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1189 | 2023-05-09 | 59450 | keep | 0 | May | 2023 | 0.040491 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-09 13:30 | 2023-05-09 14:43 | 390 | 1:13 | T | DESGANCHE | SE ABRE MACHETE Y SE CERRO INTERRUPTOR 50% EN SERVICIO | S23050900607 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-05-09 | 28470 | keep | 0 | May | 2023 | 0.019391 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
SAN JUAN | 2023-05-09 13:32 | 2023-05-09 13:34 | 1751 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 95% DE LA CARGA POR EL 1907-04 | S2305090000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-09 | 3502 | keep | 0 | May | 2023 | 0.0023852 | 0.0011926 | Momentary | FALSE | FALSE | Not_TMED_Event | 1751
BAYAMON | 2023-05-09 13:32 | 2023-05-09 13:34 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 95% DEL 1346-02 | S2305090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-09 | 4932 | keep | 0 | May | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-05-09 14:15 | 2023-05-09 15:24 | 50 | 1:09 | P | PARARRAYOS DEFECTUOSO | 2 X 140 EN C/L PARARRAYO DEFECTUOSO | S23050900634 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 69 | 2023-05-09 | 3450 | keep | 0 | May | 2023 | 0.0023498 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-09 14:16 | 2023-05-09 16:08 | 25 | 1:52 | P | ANIMAL | 1 X 65 C/L CRUCE POR AVE | B23050900066 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-05-09 | 2800 | keep | 0 | May | 2023 | 0.0019071 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-09 14:32 | 2023-05-09 17:22 | 1 | 2:50 | P | PROBLEMA DEL CLIENTE | 1 X 20 EN XMR POR CONTAMINACION EN SUBESTACION PRIVADA | B23050900071 | New_Event | Customer-Related Interruption | Include | Include | Public | 170 | 2023-05-09 | 170 | keep | 0 | May | 2023 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-09 14:33 | 2023-05-09 15:46 | 10 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA SECUNDARIA AVERIADA | P23050900129 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-05-09 | 730 | keep | 0 | May | 2023 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-09 14:43 | 2023-05-09 15:39 | 117 | 0:56 | P | DESGANCHE | SE ABRE MACHETE Y SE CERRO SECCIONALIZO 60% EN SERVICIO | S23050900607 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-05-09 | 6552 | keep | 0 | May | 2023 | 0.0044625 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-05-09 14:45 | 2023-05-09 15:16 | 16 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23050100201 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-05-09 | 496 | keep | 0 | May | 2023 | 0.00033782 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-05-09 14:47 | 2023-05-09 16:04 | 3 | 1:17 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR SE REALIZO DESGANCHE Y SE REPARO SECUNDARIA | B23050900073 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 77 | 2023-05-09 | 231 | keep | 0 | May | 2023 | 0.00015733 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-05-09 14:59 | 2023-05-10 11:03 | 86 | 20:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA Y PUENTE | S23050900670 | New_Event | Cutout Failure | Include | Include | Equipment | 1204 | 2023-05-09 | 103544 | keep | 0 | May | 2023 | 0.070523 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
AGUADILLA | 2023-05-09 15:14 | 2023-05-09 16:56 | 15 | 1:42 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23050900144 | New_Event | Vegetation Contact | Include | Include | Vegetation | 102 | 2023-05-09 | 1530 | keep | 0 | May | 2023 | 0.0010421 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-09 15:25 | 2023-05-09 15:26 | 1452 | 0:01 | T | DESGANCHE | RECERRO | S23050900000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-09 | 1452 | keep | 0 | May | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
SAN JUAN | 2023-05-09 15:29 | 2023-05-09 21:42 | 362 | 6:13 | P | DESGANCHE | 1 X 100 Y 1 X 80 EN CORTE DE LINEA DESGANCHE | S23050900680 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-05-09 | 135026 | keep | 0 | May | 2023 | 0.091966 | 0.00024656 | Sustained | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-05-09 15:34 | 2023-05-10 13:14 | 7 | 21:40 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | S23050900685 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1300 | 2023-05-09 | 9100 | keep | 0 | May | 2023 | 0.006198 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-09 15:36 | 2023-05-10 01:58 | 15 | 10:22 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | S23050900687 | New_Event | Vegetation Contact | Include | Include | Vegetation | 622 | 2023-05-09 | 9330 | keep | 0 | May | 2023 | 0.0063546 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-09 15:38 | 2023-05-10 14:11 | 47 | 22:33 | P | DESGANCHE | 3 X 100 EN CORTE DE LINEA DESGANCHE | S23050900691 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1353 | 2023-05-09 | 63591 | keep | 0 | May | 2023 | 0.043312 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-05-09 15:39 | 2023-05-09 15:59 | 93 | 0:20 | P | DESGANCHE | SE ABRE MACHETE Y SE CERRO SECCIONALIZO 80% EN SERVICIO | S23050900607 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 20 | 2023-05-09 | 1860 | keep | 0 | May | 2023 | 0.0012668 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-09 15:44 | 2023-05-09 19:06 | 126 | 3:22 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23050900099 | New_Event | Animals | Include | Include | Wildlife | 202 | 2023-05-09 | 25452 | keep | 0 | May | 2023 | 0.017335 | 8.5818e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 126
CAGUAS | 2023-05-09 15:44 | 2023-05-09 18:35 | 60 | 2:51 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23050900098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-05-09 | 10260 | keep | 0 | May | 2023 | 0.006988 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-09 15:59 | 2023-05-09 16:05 | 74 | 0:06 | P | DESGANCHE | SE RETIRO RAMA DE PISO CON VARETAY SE CERRO MACHETE 100% EN SERVICIO | S23050900607 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 6 | 2023-05-09 | 444 | keep | 0 | May | 2023 | 0.00030241 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-09 16:04 | 2023-05-09 16:05 | 5668 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | R2005090000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 5668 | keep | 0 | May | 2023 | 0.0038604 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2023-05-09 16:05 | 2023-05-10 14:30 | 70 | 22:25 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZA PARA LEVANTAR LINEA PRIMARIA | S23050900978 | New_Event | Primary Wire Break | Include | Include | Equipment | 1345 | 2023-05-09 | 94150 | keep | 0 | May | 2023 | 0.064125 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
HUMACAO | 2023-05-09 16:12 | 2023-05-09 16:13 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050900106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 676 | keep | 0 | May | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
BARRANQUITAS | 2023-05-09 16:12 | 2023-05-09 16:13 | 2486 | 0:01 | T | CABLE SOTERRADO AVERIADO | RECIERRE DE INTERRUPTOR A CAUSA DE PERSONAL PROBANDO EN RISER | C23050900105 | New_Event | UG Cable Fault | Include | Include | Equipment | 1 | 2023-05-09 | 2486 | keep | 0 | May | 2023 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
BARRANQUITAS | 2023-05-09 16:13 | 2023-05-09 16:30 | 5 | 0:17 | P | CABLE SOTERRADO AVERIADO | 1 X 100 EN RISER SE ENCONTRO AVERIA SOTERRADA DEL SU-3 @ SU-2. 100% EN SERVICIO | C23050900103 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 17 | 2023-05-09 | 85 | keep | 0 | May | 2023 | 5.7893e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-05-09 16:15 | 2023-05-09 18:12 | 11 | 1:57 | P | CRUCETA DEFECTUOSA O AVERIADA | SE ELIMINO CRUCETA, SE INSTALO UN AISLADOR RIGIDO Y SE ENERGIZO EL XMR | C23050900108 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 117 | 2023-05-09 | 1287 | keep | 0 | May | 2023 | 0.00087657 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-05-09 16:16 | 2023-05-10 09:28 | 124 | 17:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | S23050900717 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1032 | 2023-05-09 | 127968 | keep | 0 | May | 2023 | 0.087158 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
BAYAMON | 2023-05-09 16:27 | 2023-05-09 17:25 | 6 | 0:58 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23050800134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-05-09 | 348 | keep | 0 | May | 2023 | 0.00023702 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-09 16:29 | 2023-05-09 16:57 | 137 | 0:28 | S | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PUENTE ABIERTO LINEA 3100 SE PASO CARGA 1201-01 AL 1342-04 | S23050900729 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 28 | 2023-05-09 | 3836 | keep | 0 | May | 2023 | 0.0026127 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-05-09 16:29 | 2023-05-09 18:27 | 760 | 1:58 | S | LINEA DE TRANSMISION 38KV | SE RETIRA CARGA PUENTE ABIERTO LINEA 3100 SE ENERGIZO ALIMENTADOR PERO SE RETIRO CARGA BKR.2 TIENE CAMARA INTERNA ABIERTA | S23050900729 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 118 | 2023-05-09 | 89680 | keep | 0 | May | 2023 | 0.061081 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
SAN JUAN | 2023-05-09 16:39 | 2023-05-10 17:59 | 1 | 25:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN PM SE REMPLAZO CAJA EN RISER | S23050900731 | New_Event | Cutout Failure | Include | Include | Equipment | 1520 | 2023-05-09 | 1520 | keep | 0 | May | 2023 | 0.0010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-09 16:57 | 2023-05-10 11:45 | 94 | 18:48 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUMADO | R23050900104 | New_Event | Switch Failure | Include | Include | Equipment | 1128 | 2023-05-09 | 106032 | keep | 0 | May | 2023 | 0.072218 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
VEGA BAJA | 2023-05-09 17:00 | 2023-05-09 18:23 | 7 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23050900089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2023-05-09 | 581 | keep | 0 | May | 2023 | 0.00039572 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-09 17:10 | 2023-05-09 17:47 | 10 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23050900763 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-05-09 | 370 | keep | 0 | May | 2023 | 0.00025201 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-09 17:14 | 2023-05-09 19:18 | 170 | 2:04 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23050900109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-05-09 | 21080 | keep | 0 | May | 2023 | 0.014357 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
BAYAMON | 2023-05-09 17:18 | 2023-05-09 20:00 | 300 | 2:42 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE CERRO PUENTE PRIMARIO | B23050900093 | New_Event | Primary Wire Break | Include | Include | Equipment | 162 | 2023-05-09 | 48600 | keep | 0 | May | 2023 | 0.033101 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2023-05-09 17:25 | 2023-05-09 20:06 | 15 | 2:41 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | C23050900117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-05-09 | 2415 | keep | 0 | May | 2023 | 0.0016448 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-05-09 17:31 | 2023-05-10 16:00 | 30 | 22:29 | P | DESGANCHE | 1 X 30 EN CL SE REALIZO DESGANCHE | M23050900156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1349 | 2023-05-09 | 40470 | keep | 0 | May | 2023 | 0.027564 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-09 17:31 | 2023-05-09 19:30 | 60 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA PARTIDA EN EL MONTE | M23050900156 | New_Event | Primary Wire Break | Include | Include | Equipment | 119 | 2023-05-09 | 7140 | keep | 0 | May | 2023 | 0.004863 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-09 17:38 | 2023-05-09 17:42 | 767 | 0:04 | P | ALIMENTADOR AMARRADO | RECIERRE DE BKR 1909-07 | S23050900788 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-09 | 3068 | keep | 0 | May | 2023 | 0.0020896 | 0.0005224 | Momentary | FALSE | FALSE | Not_TMED_Event | 767
BAYAMON | 2023-05-09 17:38 | 2023-05-09 17:42 | 1139 | 0:04 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR LLEVA 1909-09 LLEVA 50% 1709-03 | S23050900788 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-09 | 4556 | keep | 0 | May | 2023 | 0.0031031 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2023-05-09 17:38 | 2023-05-09 17:42 | 4456 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE BREAKER CARGA POR 1909-07 SE CERRO POR CONTROL | S23050900788 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-09 | 17824 | keep | 0 | May | 2023 | 0.01214 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
HUMACAO | 2023-05-09 17:39 | 2023-05-09 17:40 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23050900119 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 676 | keep | 0 | May | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
MAYAGÃœEZ | 2023-05-09 17:42 | 2023-05-10 18:30 | 65 | 24:48 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE HIZO DESGANCHE MASIVO Y SE REPARARON LINEAS PRIMARIAS ROTAS | M23050900160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1488 | 2023-05-09 | 96720 | keep | 0 | May | 2023 | 0.065876 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-05-09 17:43 | 2023-05-09 20:03 | 55 | 2:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER Y SE REEMPLAZO CAJA PRIMARIA | S23050900795 | New_Event | Cutout Failure | Include | Include | Equipment | 140 | 2023-05-09 | 7700 | keep | 0 | May | 2023 | 0.0052444 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
BARRANQUITAS | 2023-05-09 17:55 | 2023-05-09 21:21 | 163 | 3:26 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 C/L SE LEVANTO CONDUCTOR PRIMARIO | C23050900123 | New_Event | Primary Wire Break | Include | Include | Equipment | 206 | 2023-05-09 | 33578 | keep | 0 | May | 2023 | 0.02287 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
AGUADILLA | 2023-05-09 18:05 | 2023-05-09 18:20 | 12 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23050900083 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-05-09 | 180 | keep | 0 | May | 2023 | 0.0001226 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-09 18:14 | 2023-05-10 15:32 | 7 | 21:18 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | R23050900122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1278 | 2023-05-09 | 8946 | keep | 0 | May | 2023 | 0.0060931 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-05-09 18:26 | 2023-05-09 19:15 | 50 | 0:49 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | A23050900122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2023-05-09 | 2450 | keep | 0 | May | 2023 | 0.0016687 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-09 18:27 | 2023-05-09 18:39 | 760 | 0:12 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SE ABRE INTERRUPTOR PARA TRANSFERIRLO AL 1201-01 BKR. 2 TIENE FASE ABIERTA INTERNAMENTE | S23050900729 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 12 | 2023-05-09 | 9120 | keep | 0 | May | 2023 | 0.0062116 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
AGUADILLA | 2023-05-09 18:29 | 2023-05-09 20:19 | 25 | 1:50 | P | OTRAS CAUSAS | 1 X 20 EN TRANSFORMADOR FUSIBLE CORROIDO | A23050900124 | New_Event | Other Causes | Include | Include | Other | 110 | 2023-05-09 | 2750 | keep | 0 | May | 2023 | 0.001873 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-09 18:30 | 2023-05-09 18:54 | 900 | 0:24 | P | CAUSAS EXTERNAS | SE CERRO PUENTES Y SE CERRO MACHETES | M23050900011 | New_Event | Damage From Public | Include | Include | Public | 24 | 2023-05-09 | 21600 | keep | 0 | May | 2023 | 0.014712 | 0.00061299 | Sustained | FALSE | FALSE | Not_TMED_Event | 900
YAUCO | 2023-05-09 18:33 | 2023-05-09 18:46 | 6 | 0:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23050100218 | New_Event | Secondary Wire Break | Include | Include | Equipment | 13 | 2023-05-09 | 78 | keep | 0 | May | 2023 | 5.3125e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-09 18:56 | 2023-05-09 18:57 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | C23050900134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-09 | 2725 | keep | 0 | May | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-05-09 18:56 | 2023-05-09 18:57 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | C23050900134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-09 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-05-09 18:56 | 2023-05-09 18:57 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | C23050900134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-09 | 1437 | keep | 0 | May | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-05-09 18:56 | 2023-05-09 18:57 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | C23050900135 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-09 | 2565 | keep | 0 | May | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-05-09 18:56 | 2023-05-09 18:57 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 4800 | C23050900135 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-09 | 3565 | keep | 0 | May | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
GUAYAMA | 2023-05-09 18:56 | 2023-05-09 18:57 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23050900177 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
PONCE | 2023-05-09 19:04 | 2023-05-09 20:00 | 25 | 0:56 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR RAMAS DE ARBOL EN LINEA SECUNDARIA | P23050900178 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 56 | 2023-05-09 | 1400 | keep | 0 | May | 2023 | 0.00095353 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
ARECIBO | 2023-05-09 19:17 | 2023-05-09 19:18 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23050900125 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 1227 | keep | 0 | May | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
ARECIBO | 2023-05-09 19:18 | 2023-05-09 22:15 | 1 | 2:57 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 37.5 KVA RELACIONADO AL EVENTO A23050800039 | A23050900095 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 177 | 2023-05-09 | 177 | keep | 0 | May | 2023 | 0.00012055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-09 19:28 | 2023-05-09 21:50 | 500 | 2:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M23050900182 | New_Event | Primary Wire Break | Include | Include | Equipment | 142 | 2023-05-09 | 71000 | keep | 0 | May | 2023 | 0.048358 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2023-05-09 19:29 | 2023-05-09 21:05 | 200 | 1:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23050900131 | New_Event | Cutout Failure | Include | Include | Equipment | 96 | 2023-05-09 | 19200 | keep | 0 | May | 2023 | 0.013077 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-09 19:30 | 2023-05-10 10:12 | 8 | 14:42 | P | DESGANCHE | 1 X 100 EN C/L | S23050900876 | New_Event | Vegetation Contact | Include | Include | Vegetation | 882 | 2023-05-09 | 7056 | keep | 0 | May | 2023 | 0.0048058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-09 19:35 | 2023-05-10 11:15 | 8 | 15:40 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | M23050900184 | New_Event | Animals | Include | Include | Wildlife | 940 | 2023-05-09 | 7520 | keep | 0 | May | 2023 | 0.0051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-09 19:46 | 2023-05-09 19:47 | 4089 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23050900093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 4089 | keep | 0 | May | 2023 | 0.002785 | 0.002785 | Momentary | FALSE | FALSE | Not_TMED_Event | 4089
BAYAMON | 2023-05-09 19:49 | 2023-05-10 09:39 | 51 | 13:50 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23050900132 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 830 | 2023-05-09 | 42330 | keep | 0 | May | 2023 | 0.028831 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-05-09 19:59 | 2023-05-10 09:38 | 19 | 13:39 | P | ANIMAL | 1 X 40 EN RISER CRUCE POR AVE | B23050900138 | New_Event | Animals | Include | Include | Wildlife | 819 | 2023-05-09 | 15561 | keep | 0 | May | 2023 | 0.010599 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
BAYAMON | 2023-05-09 20:07 | 2023-05-10 12:12 | 5 | 16:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B23050900144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 965 | 2023-05-09 | 4825 | keep | 0 | May | 2023 | 0.0032863 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-05-09 20:07 | 2023-05-10 09:23 | 78 | 13:16 | P | ANIMAL | 1 X 25 EN C/L AVE CRUZO LINEAS | R23050900137 | New_Event | Animals | Include | Include | Wildlife | 796 | 2023-05-09 | 62088 | keep | 0 | May | 2023 | 0.042288 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
HUMACAO | 2023-05-09 20:08 | 2023-05-09 20:41 | 8 | 0:33 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23050900140 | New_Event | Animals | Include | Include | Wildlife | 33 | 2023-05-09 | 264 | keep | 0 | May | 2023 | 0.00017981 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-09 20:24 | 2023-05-09 23:10 | 115 | 2:46 | P | DESGANCHE | 1 X 65 EN C/ Y DESGANCHE | B23050900921 | New_Event | Vegetation Contact | Include | Include | Vegetation | 166 | 2023-05-09 | 19090 | keep | 0 | May | 2023 | 0.013002 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
PONCE | 2023-05-09 20:36 | 2023-05-09 22:05 | 200 | 1:29 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS ENREDADAS | P23050900200 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 89 | 2023-05-09 | 17800 | keep | 0 | May | 2023 | 0.012123 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-09 20:37 | 2023-05-10 01:00 | 89 | 4:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REAMPLAZO CAJA PRIMARIA Y 3 X 50 EN C/L | B23050900157 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2023-05-09 | 23407 | keep | 0 | May | 2023 | 0.015942 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
YAUCO | 2023-05-09 20:39 | 2023-05-09 23:29 | 200 | 2:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P23050900202 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 170 | 2023-05-09 | 34000 | keep | 0 | May | 2023 | 0.023157 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-05-09 20:49 | 2023-05-10 15:23 | 60 | 18:34 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE PRIMARIO ABIERTO EN N/O CONTRA 1201-02 | S23050900949 | New_Event | Primary Wire Break | Include | Include | Equipment | 1114 | 2023-05-09 | 66840 | keep | 0 | May | 2023 | 0.045524 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-09 20:49 | 2023-05-10 15:23 | 253 | 18:34 | P | ALIMENTADOR AMARRADO | SE ENCONTRO PUENTE PRIMARIO ABIERTO EN N/O CONTRA 1201-02 | S23050900949 | New_Event | Feeder Load Transferred | Include | Include | Other | 1114 | 2023-05-09 | 281842 | keep | 0 | May | 2023 | 0.19196 | 0.00017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 253
SAN JUAN | 2023-05-09 20:49 | 2023-05-10 19:06 | 25 | 22:17 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23050900949 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1337 | 2023-05-09 | 33425 | keep | 0 | May | 2023 | 0.022766 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-09 21:07 | 2023-05-09 21:08 | 1943 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA POR 7006-03 | M23050900216 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-09 | 1943 | keep | 0 | May | 2023 | 0.0013234 | 0.0013234 | Momentary | FALSE | FALSE | Not_TMED_Event | 1943
AGUADILLA | 2023-05-09 21:07 | 2023-05-09 21:08 | 1024 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7006-01 | M23050900216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-09 | 1024 | keep | 0 | May | 2023 | 0.00069744 | 0.00069744 | Momentary | FALSE | FALSE | Not_TMED_Event | 1024
SAN JUAN | 2023-05-09 21:09 | 2023-05-10 16:00 | 60 | 18:51 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | S23050900985 | New_Event | Animals | Include | Include | Wildlife | 1131 | 2023-05-09 | 67860 | keep | 0 | May | 2023 | 0.046219 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-05-09 21:11 | 2023-05-10 00:19 | 443 | 3:08 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO EN MACHETES DE AMARRE (N/O) SE ABRIO EL INTERRUPTOR PARA REPARARLO | M23050900234 | New_Event | Primary Wire Break | Include | Include | Equipment | 188 | 2023-05-09 | 83284 | keep | 0 | May | 2023 | 0.056724 | 0.00030173 | Sustained | FALSE | FALSE | Not_TMED_Event | 443
ARECIBO | 2023-05-09 21:24 | 2023-05-09 22:10 | 25 | 0:46 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CULEBRA CRUZO LINEAS | A23050900142 | New_Event | Animals | Include | Include | Wildlife | 46 | 2023-05-09 | 1150 | keep | 0 | May | 2023 | 0.00078326 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-05-09 21:42 | 2023-05-10 06:50 | 28 | 9:08 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO CAUSA | P23050900227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 548 | 2023-05-09 | 15344 | keep | 0 | May | 2023 | 0.010451 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
CAGUAS | 2023-05-09 21:48 | 2023-05-09 23:54 | 195 | 2:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C23050900155 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-05-09 | 24570 | keep | 0 | May | 2023 | 0.016735 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
SAN JUAN | 2023-05-09 22:03 | 2023-05-10 13:43 | 15 | 15:40 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO SE SECCIONALIZA PARA CERRAR PUENTE | S23050900563 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 940 | 2023-05-09 | 14100 | keep | 0 | May | 2023 | 0.0096034 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-09 22:11 | 2023-05-10 09:00 | 4 | 10:49 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | C23050900156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 649 | 2023-05-09 | 2596 | keep | 0 | May | 2023 | 0.0017681 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-05-09 22:27 | 2023-05-10 13:04 | 50 | 14:37 | P | DESGANCHE | 1 X 65 EN RISER DESGANCHE | C23050900159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 877 | 2023-05-09 | 43850 | keep | 0 | May | 2023 | 0.029866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-09 22:32 | 2023-05-10 09:20 | 12 | 10:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | P23050900233 | New_Event | Primary Wire Break | Include | Include | Equipment | 648 | 2023-05-09 | 7776 | keep | 0 | May | 2023 | 0.0052962 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
UTUADO | 2023-05-09 23:52 | 2023-05-10 15:00 | 4 | 15:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN MONTURA DE TRANSFORMADOR | A23050900146 | New_Event | Cutout Failure | Include | Include | Equipment | 908 | 2023-05-09 | 3632 | keep | 0 | May | 2023 | 0.0024737 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-05-10 00:18 | 2023-05-10 08:00 | 37 | 7:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REEMPLAZO PORTAFUSIBLE | C23051000004 | New_Event | Cutout Failure | Include | Include | Equipment | 462 | 2023-05-10 | 17094 | keep | 0 | May | 2023 | 0.011643 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
AGUADILLA | 2023-05-10 00:19 | 2023-05-10 02:05 | 1943 | 1:46 | T | ALIMENTADOR AMARRADO | SU CARGA POR EL 7006-03 EL CUAL SE ABRIO PARA REPARAR PUENTE ABIERTO | M23051000003 | New_Event | Feeder Load Transferred | Include | Include | Other | 106 | 2023-05-10 | 205958 | keep | 0 | May | 2023 | 0.14028 | 0.0013234 | Sustained | FALSE | FALSE | Not_TMED_Event | 1943
AGUADILLA | 2023-05-10 00:19 | 2023-05-10 02:05 | 1024 | 1:46 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA REPARAR PUENTE ABIERTO LLEVA LA CARGA DEL 7006-01 | M23051000003 | New_Event | Primary Wire Break | Include | Include | Equipment | 106 | 2023-05-10 | 108544 | keep | 0 | May | 2023 | 0.073929 | 0.00069744 | Sustained | FALSE | FALSE | Not_TMED_Event | 1024
CANOVANAS | 2023-05-10 00:35 | 2023-05-10 03:15 | 60 | 2:40 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R23051000007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-05-10 | 9600 | keep | 0 | May | 2023 | 0.0065385 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-05-10 01:04 | 2023-05-10 15:16 | 20 | 14:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051000005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 852 | 2023-05-10 | 17040 | keep | 0 | May | 2023 | 0.011606 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-10 01:24 | 2023-05-10 11:38 | 10 | 10:14 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | M23051000007 | New_Event | Primary Wire Break | Include | Include | Equipment | 614 | 2023-05-10 | 6140 | keep | 0 | May | 2023 | 0.0041819 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-10 02:24 | 2023-05-10 13:40 | 100 | 11:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | S23051000012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 676 | 2023-05-10 | 67600 | keep | 0 | May | 2023 | 0.046042 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-05-10 03:35 | 2023-05-10 10:05 | 50 | 6:30 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051000014 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 390 | 2023-05-10 | 19500 | keep | 0 | May | 2023 | 0.013281 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-10 04:03 | 2023-05-10 13:28 | 200 | 9:25 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | S23051000018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 565 | 2023-05-10 | 113000 | keep | 0 | May | 2023 | 0.076964 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-05-10 04:48 | 2023-05-10 12:20 | 25 | 7:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23051000019 | New_Event | Cutout Failure | Include | Include | Equipment | 452 | 2023-05-10 | 11300 | keep | 0 | May | 2023 | 0.0076964 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-10 04:49 | 2023-05-10 08:00 | 250 | 3:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051000020 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 191 | 2023-05-10 | 47750 | keep | 0 | May | 2023 | 0.032522 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-05-10 04:52 | 2023-05-10 12:47 | 58 | 7:55 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23051000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2023-05-10 | 27550 | keep | 0 | May | 2023 | 0.018764 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
UTUADO | 2023-05-10 05:15 | 2023-05-10 11:05 | 25 | 5:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEAS | A23051000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 350 | 2023-05-10 | 8750 | keep | 0 | May | 2023 | 0.0059596 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-05-10 05:25 | 2023-05-10 11:01 | 80 | 5:36 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23051000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 336 | 2023-05-10 | 26880 | keep | 0 | May | 2023 | 0.018308 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-10 05:44 | 2023-05-10 12:18 | 60 | 6:34 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23051000013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 394 | 2023-05-10 | 23640 | keep | 0 | May | 2023 | 0.016101 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-05-10 05:59 | 2023-05-10 14:50 | 1 | 8:51 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | A23051000006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 531 | 2023-05-10 | 531 | keep | 0 | May | 2023 | 0.00036166 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-10 06:06 | 2023-05-10 08:27 | 2422 | 2:21 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE CERRO LOCALMENTE LLEVA 1346-04 | S23051000056 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2023-05-10 | 341502 | keep | 0 | May | 2023 | 0.2326 | 0.0016496 | Sustained | FALSE | FALSE | Not_TMED_Event | 2422
SAN JUAN | 2023-05-10 06:06 | 2023-05-10 08:27 | 3932 | 2:21 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE CERRO LOCALMENTE SU CARGA POR 1346-03 | S23051000056 | New_Event | Feeder Load Transferred | Include | Include | Other | 141 | 2023-05-10 | 554412 | keep | 0 | May | 2023 | 0.37761 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
BAYAMON | 2023-05-10 06:56 | 2023-05-10 11:08 | 59 | 4:12 | P | ANIMAL | CRUCE POR AVER 1 X 5 EN XMR Y 1 X 50 EN C/L | B23051000011 | New_Event | Animals | Include | Include | Wildlife | 252 | 2023-05-10 | 14868 | keep | 0 | May | 2023 | 0.010127 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
AGUADILLA | 2023-05-10 07:10 | 2023-05-10 11:58 | 100 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | M23051000040 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2023-05-10 | 28800 | keep | 0 | May | 2023 | 0.019616 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-10 07:22 | 2023-05-10 07:24 | 1356 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23051000129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-10 | 2712 | keep | 0 | May | 2023 | 0.0018471 | 0.00092357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1356
VEGA BAJA | 2023-05-10 07:42 | 2023-05-11 08:19 | 8 | 24:37 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A23051000014 | New_Event | Animals | Include | Include | Wildlife | 1477 | 2023-05-10 | 11816 | keep | 0 | May | 2023 | 0.0080478 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-05-10 07:58 | 2023-05-10 11:45 | 21 | 3:47 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | C23051000025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-05-10 | 4767 | keep | 0 | May | 2023 | 0.0032468 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CANOVANAS | 2023-05-10 08:04 | 2023-05-10 19:07 | 7 | 11:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23051000012 | New_Event | Secondary Wire Break | Include | Include | Equipment | 663 | 2023-05-10 | 4641 | keep | 0 | May | 2023 | 0.003161 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-05-10 08:10 | 2023-05-10 09:10 | 25 | 1:00 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA PAJARO CRUZO FASE | P23051000027 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-05-10 | 1500 | keep | 0 | May | 2023 | 0.0010216 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-05-10 08:19 | 2023-05-10 11:04 | 8 | 2:45 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23051000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 165 | 2023-05-10 | 1320 | keep | 0 | May | 2023 | 0.00089905 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-10 08:46 | 2023-05-10 09:51 | 10 | 1:05 | P | ANIMAL | 1 X 15 EN XMR SE REEMPLAZO PORTAFUSIBLE A CAUSA DE CRUCE X AVE | C23051000017 | New_Event | Animals | Include | Include | Wildlife | 65 | 2023-05-10 | 650 | keep | 0 | May | 2023 | 0.00044271 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-10 08:46 | 2023-05-10 18:35 | 5 | 9:49 | P | CONDUCTOR ROTO O ABIERTO | 1 X 15 EN TRANSFORMADOR SE REPARA BAJANTE PRIMARIO | A23051000023 | New_Event | Primary Wire Break | Include | Include | Equipment | 589 | 2023-05-10 | 2945 | keep | 0 | May | 2023 | 0.0020058 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-10 08:56 | 2023-05-10 16:42 | 1 | 7:46 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE 1 X 20 EN TRANSFORMADOR | S23051000222 | New_Event | Primary Wire Break | Include | Include | Equipment | 466 | 2023-05-10 | 466 | keep | 0 | May | 2023 | 0.00031739 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-10 09:12 | 2023-05-10 11:40 | 1 | 2:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A23051000031 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 148 | 2023-05-10 | 148 | keep | 0 | May | 2023 | 0.0001008 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-10 09:17 | 2023-05-10 13:58 | 150 | 4:41 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA DESGANCHE | S23051000238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 281 | 2023-05-10 | 42150 | keep | 0 | May | 2023 | 0.028708 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-05-10 09:18 | 2023-05-10 13:50 | 1 | 4:32 | P | CONDUCTOR ROTO O ABIERTO | REEMPLAZO DE BAJANTE PRIMARIO EN MONTURA DE ESCUELA JUANITA RAMIREZ | A23051000032 | New_Event | Primary Wire Break | Include | Include | Equipment | 272 | 2023-05-10 | 272 | keep | 0 | May | 2023 | 0.00018526 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-10 09:20 | 2023-05-10 12:45 | 8 | 3:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES EN PEDESTAL | P23051000053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 205 | 2023-05-10 | 1640 | keep | 0 | May | 2023 | 0.001117 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-05-10 09:20 | 2023-05-10 11:33 | 76 | 2:13 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA PAJARO CRUZO FASE | P23051000039 | New_Event | Animals | Include | Include | Wildlife | 133 | 2023-05-10 | 10108 | keep | 0 | May | 2023 | 0.0068845 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
SAN JUAN | 2023-05-10 09:44 | 2023-05-10 22:38 | 17 | 12:54 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REEMPLAZARON DISCOS PARTIDOS | S23051000261 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 774 | 2023-05-10 | 13158 | keep | 0 | May | 2023 | 0.0089619 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2023-05-10 10:00 | 2023-05-10 13:30 | 5 | 3:30 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE XMR AVERIADO 15KVA X 25KVA | C23051000044 | New_Event | Service Transformer Failure | Include | Include | Equipment | 210 | 2023-05-10 | 1050 | keep | 0 | May | 2023 | 0.00071515 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-05-10 10:01 | 2023-05-10 11:53 | 12 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | SE RECONECTO PUENTE SAFADO EN TRANSFORMADOR | P23051000052 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2023-05-10 | 1344 | keep | 0 | May | 2023 | 0.00091539 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-10 10:35 | 2023-05-10 10:37 | 2106 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | R2305100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-10 | 4212 | keep | 0 | May | 2023 | 0.0028688 | 0.0014344 | Momentary | FALSE | FALSE | Not_TMED_Event | 2106
VEGA BAJA | 2023-05-10 10:41 | 2023-05-10 12:15 | 90 | 1:34 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | A23051000052 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-05-10 | 8460 | keep | 0 | May | 2023 | 0.0057621 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
HUMACAO | 2023-05-10 10:44 | 2023-05-10 13:55 | 30 | 3:11 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23051000058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 191 | 2023-05-10 | 5730 | keep | 0 | May | 2023 | 0.0039027 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-10 10:47 | 2023-05-10 15:24 | 8 | 4:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS | P23051000064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 277 | 2023-05-10 | 2216 | keep | 0 | May | 2023 | 0.0015093 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-10 10:51 | 2023-05-10 19:21 | 20 | 8:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 10 EN AEREO PROVISIONAL SE CONSTRUYO POSTE EN AEREO PROVISIONAL | R23051000059 | New_Event | Primary Pole Failure | Include | Include | Equipment | 510 | 2023-05-10 | 10200 | keep | 0 | May | 2023 | 0.0069472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-05-10 10:52 | 2023-05-10 11:40 | 1 | 0:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO LINEA A CAJA EN RISER | R23051000061 | New_Event | Primary Wire Break | Include | Include | Equipment | 48 | 2023-05-10 | 48 | keep | 0 | May | 2023 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-05-10 11:03 | 2023-05-10 21:04 | 15 | 10:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTE PARA SECCIONALIZAR TRABAJOS DE PASAR LINEAS A POSTE NUEVO | A23051000060 | New_Event | Primary Pole Failure | Include | Include | Equipment | 601 | 2023-05-10 | 9015 | keep | 0 | May | 2023 | 0.0061401 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-10 11:11 | 2023-05-10 11:12 | 869 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051000000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-10 | 869 | keep | 0 | May | 2023 | 0.00059187 | 0.00059187 | Momentary | FALSE | FALSE | Not_TMED_Event | 869
GUAYAMA | 2023-05-10 11:14 | 2023-05-10 11:15 | 610 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051000073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-10 | 610 | keep | 0 | May | 2023 | 0.00041547 | 0.00041547 | Momentary | FALSE | FALSE | Not_TMED_Event | 610
BAYAMON | 2023-05-10 11:34 | 2023-05-10 14:18 | 4 | 2:44 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23051000053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-05-10 | 656 | keep | 0 | May | 2023 | 0.0004468 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-05-10 11:45 | 2023-05-10 13:24 | 10 | 1:39 | P | DESGANCHE | 1 X 30 Y 1 X 20 EN C/L DESGANCHE | R23051000069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-05-10 | 990 | keep | 0 | May | 2023 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-10 12:00 | 2023-05-10 14:25 | 2 | 2:25 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23051000077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 145 | 2023-05-10 | 290 | keep | 0 | May | 2023 | 0.00019752 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-05-10 12:09 | 2023-05-10 17:47 | 10 | 5:38 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA DE XMR | C23051000080 | New_Event | Primary Wire Break | Include | Include | Equipment | 338 | 2023-05-10 | 3380 | keep | 0 | May | 2023 | 0.0023021 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-10 12:11 | 2023-05-10 14:13 | 10 | 2:02 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23051000075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-05-10 | 1220 | keep | 0 | May | 2023 | 0.00083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-10 12:11 | 2023-05-10 14:10 | 30 | 1:59 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CL LINEA PRIMARIA CRUZADA CON TENSOR SE AISLO LINEA | M23051000132 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 119 | 2023-05-10 | 3570 | keep | 0 | May | 2023 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-05-10 12:24 | 2023-05-10 14:50 | 40 | 2:26 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA Y 1 X 40 EN CONVERTIDOR SE RETIRO RAMA SOBRE LINEA | A23051000075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-05-10 | 5840 | keep | 0 | May | 2023 | 0.0039776 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-05-10 12:36 | 2023-05-10 18:00 | 40 | 5:24 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | C23051000086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2023-05-10 | 12960 | keep | 0 | May | 2023 | 0.008827 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-05-10 12:50 | 2023-05-10 15:09 | 60 | 2:19 | P | DESGANCHE | 1 X 30 1 X 50 EN C/L DESGANCHE | R23051000089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-10 | 8340 | keep | 0 | May | 2023 | 0.0056803 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-10 12:53 | 2023-05-10 14:06 | 1 | 1:13 | P | ANIMAL | 1 X 20 EN C/L CRUCE POR AVE | R23051000090 | New_Event | Animals | Include | Include | Wildlife | 73 | 2023-05-10 | 73 | keep | 0 | May | 2023 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-10 12:56 | 2023-05-10 15:05 | 524 | 2:09 | P | CAUSAS EXTERNAS | 3 X 100 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA CAUSADO POR PERSONAL DEL MUNICIPIO DE GUAYAMA REALIZANDO DESGANCHE | P23051000092 | New_Event | Damage From Public | Include | Include | Public | 129 | 2023-05-10 | 67596 | keep | 0 | May | 2023 | 0.046039 | 0.00035689 | Sustained | FALSE | FALSE | Not_TMED_Event | 524
VEGA BAJA | 2023-05-10 12:58 | 2023-05-10 19:45 | 16 | 6:47 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | A23051000082 | New_Event | Animals | Include | Include | Wildlife | 407 | 2023-05-10 | 6512 | keep | 0 | May | 2023 | 0.0044353 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-05-10 13:00 | 2023-05-10 13:59 | 1 | 0:59 | P | CAUSAS EXTERNAS | 1 X 50 EN C/L SE DESPEGO TENSOR DE LINEA | C23051000092 | New_Event | Damage From Public | Include | Include | Public | 59 | 2023-05-10 | 59 | keep | 0 | May | 2023 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-10 13:07 | 2023-05-10 17:30 | 50 | 4:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051000143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-05-10 | 13150 | keep | 0 | May | 2023 | 0.0089564 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-10 13:13 | 2023-05-10 13:47 | 6 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE BAJO TAP DEL 3 AL 2 SE DEJO EN 122V POR FASE Y SE REEMPLAZO BAJANTE SECUNDARIO | B23051000061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-05-10 | 204 | keep | 0 | May | 2023 | 0.00013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
FAJARDO | 2023-05-10 13:16 | 2023-05-10 16:27 | 7 | 3:11 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23051000096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 191 | 2023-05-10 | 1337 | keep | 0 | May | 2023 | 0.00091062 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-05-10 13:18 | 2023-05-10 14:35 | 1923 | 1:17 | T | LINEA DE TRANSMISION 38KV | SE ABRE MACHETES DE AMARRE CON 8401-03 PARA SECCIONALIZAR AVERIA DE LINEA PRIMARIA PARTIDA A CAUSA DE LINEA 2200 VACANTE Y SE CIERRA INTERRUPTOR | A23051000101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 77 | 2023-05-10 | 148071 | keep | 0 | May | 2023 | 0.10085 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-05-10 13:18 | 2023-05-10 22:42 | 1066 | 9:24 | T | LINEA DE TRANSMISION 38KV | SE REPARO LINEA PRIMARIA PARTIDA POR TRAMO DE LINEA 2200 VACANTE QUE CAYO SOBRE EL ALIMENTADOR Y SE CERRARON MACHETES CONTRA EL 8401-02 | A23051000101 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 564 | 2023-05-10 | 601224 | keep | 0 | May | 2023 | 0.40949 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
SAN JUAN | 2023-05-10 13:22 | 2023-05-11 12:24 | 35 | 23:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y SE CERRO PUENTE | S23051000411 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1382 | 2023-05-10 | 48370 | keep | 0 | May | 2023 | 0.032945 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-05-10 13:24 | 2023-05-10 13:28 | 220 | 0:04 | P | ALIMENTADOR AMARRADO | SE PROBO QUEDO EN SERVICIO 1303-05 LLEVA 98% DEL 1303-04 | S23051000414 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-10 | 880 | keep | 0 | May | 2023 | 0.00059936 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-05-10 13:24 | 2023-05-10 13:28 | 870 | 0:04 | T | ARBOL SOBRE LINEA | SE PROBO QUEDO EN SERVICIO LLEVA 98% DEL 1303-04 | S23051000414 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 4 | 2023-05-10 | 3480 | keep | 0 | May | 2023 | 0.0023702 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-05-10 13:28 | 2023-05-10 20:56 | 150 | 7:28 | P | ARBOL SOBRE LINEA | 2 X 65 Y 1 X 80 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | S23051000516 | 1st_after_momentary | Vegetation Uprooted Tree | Include | Include | Vegetation | 448 | 2023-05-10 | 67200 | keep | 0 | May | 2023 | 0.04577 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-10 13:30 | 2023-05-10 14:00 | 29 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23050900703 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-05-10 | 870 | keep | 0 | May | 2023 | 0.00059255 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
MAYAGÃœEZ | 2023-05-10 13:34 | 2023-05-10 17:17 | 50 | 3:43 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGA ELECTRICA | M23051000150 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 223 | 2023-05-10 | 11150 | keep | 0 | May | 2023 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-10 13:37 | 2023-05-10 13:39 | 61 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2305100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-10 | 122 | keep | 0 | May | 2023 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
FAJARDO | 2023-05-10 13:40 | 2023-05-11 12:15 | 1 | 22:35 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO DE 50KVA Y 1 X 15 EN XMR | R23051000102 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1355 | 2023-05-10 | 1355 | keep | 0 | May | 2023 | 0.00092288 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-10 13:43 | 2023-05-10 14:25 | 150 | 0:42 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO N/O PARA CERRAR PUENTE PRIMARIO TRONCAL Y TRAS PATIO | S23050900563 | New_Event | Primary Wire Break | Include | Include | Equipment | 42 | 2023-05-10 | 6300 | keep | 0 | May | 2023 | 0.0042909 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-05-10 13:43 | 2023-05-10 17:00 | 46 | 3:17 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | C23051000100 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-05-10 | 9062 | keep | 0 | May | 2023 | 0.0061721 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
VEGA BAJA | 2023-05-10 13:51 | 2023-05-11 10:08 | 30 | 20:17 | P | NO SE REPORTO CAUSA | 1X30 EN C/L | B23051000064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1217 | 2023-05-10 | 36510 | keep | 0 | May | 2023 | 0.024867 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-05-10 14:00 | 2023-05-10 16:00 | 10 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA SECUNDARIA PARTIDA | A23051000073 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-05-10 | 1200 | keep | 0 | May | 2023 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-10 14:07 | 2023-05-10 14:08 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-10 | 2402 | keep | 0 | May | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
UTUADO | 2023-05-10 14:24 | 2023-05-11 12:45 | 50 | 22:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN CORTE DE LINEA SE REMPLAZARON AISLADORES ROTOS | A23051000116 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1341 | 2023-05-10 | 67050 | keep | 0 | May | 2023 | 0.045667 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-05-10 14:25 | 2023-05-10 16:30 | 15 | 2:05 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A23051000117 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-05-10 | 1875 | keep | 0 | May | 2023 | 0.0012771 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-10 14:27 | 2023-05-10 18:26 | 1 | 3:59 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | S23051000449 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-05-10 | 239 | keep | 0 | May | 2023 | 0.00016278 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-10 14:28 | 2023-05-10 14:29 | 2858 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-10 | 2858 | keep | 0 | May | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
SAN JUAN | 2023-05-10 14:30 | 2023-05-10 15:26 | 150 | 0:56 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO PRIMARIA | S23050900978 | New_Event | Primary Wire Break | Include | Include | Equipment | 56 | 2023-05-10 | 8400 | keep | 0 | May | 2023 | 0.0057212 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-10 14:35 | 2023-05-10 16:27 | 7 | 1:52 | P | SECUNDARIA/DESGANCHE | DESGANCHE EN XMR Y 1 X 15 EN XMR | B23051000071 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 112 | 2023-05-10 | 784 | keep | 0 | May | 2023 | 0.00053398 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-10 14:46 | 2023-05-10 19:20 | 100 | 4:34 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | S23051000460 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2023-05-10 | 27400 | keep | 0 | May | 2023 | 0.018662 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-05-10 14:50 | 2023-05-10 15:25 | 12 | 0:35 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABREN CAJAS EN TRANSFORMADOR PARA REPARAR NEUTRAL SECUNDARIO | M23051000165 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 35 | 2023-05-10 | 420 | keep | 0 | May | 2023 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-10 14:53 | 2023-05-10 16:00 | 50 | 1:07 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A23051000130 | New_Event | Primary Wire Break | Include | Include | Equipment | 67 | 2023-05-10 | 3350 | keep | 0 | May | 2023 | 0.0022817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-10 14:55 | 2023-05-11 09:16 | 60 | 18:21 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 1 X 40 EN SU-2 CONTAMINACION EN SU-2 | S23051000466 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1101 | 2023-05-10 | 66060 | keep | 0 | May | 2023 | 0.044993 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-05-10 15:01 | 2023-05-10 16:15 | 50 | 1:14 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23051000135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 74 | 2023-05-10 | 3700 | keep | 0 | May | 2023 | 0.0025201 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-10 15:02 | 2023-05-10 23:16 | 300 | 8:14 | P | TERMINACION SOTERRADA AVERIADA | 1 X 100 Y 1 X 65 EN RISER'S SE SECCIONALIZO HACIA MH-15-A | S23051000472 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 494 | 2023-05-10 | 148200 | keep | 0 | May | 2023 | 0.10094 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-05-10 15:02 | 2023-05-10 15:03 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23051000168 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-10 | 3041 | keep | 0 | May | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
BAYAMON | 2023-05-10 15:02 | 2023-05-10 15:53 | 10 | 0:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE XMR Y SE REGULO VOLTAGE SE SUBIO TAP 2 AL 3 Y SE REPARO BAJANTE SECUNDARIO 123V POR FASE | B23051000074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 51 | 2023-05-10 | 510 | keep | 0 | May | 2023 | 0.00034736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-05-10 15:04 | 2023-05-10 16:54 | 30 | 1:50 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PAJARO CRUZO FASE | P23051000115 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-05-10 | 3300 | keep | 0 | May | 2023 | 0.0022476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-10 15:13 | 2023-05-10 17:45 | 12 | 2:32 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR CON BUSHING AVERIADOS DE 25 KVA POR 25 KVA FID-21251085 | M23051000170 | New_Event | Service Transformer Failure | Include | Include | Equipment | 152 | 2023-05-10 | 1824 | keep | 0 | May | 2023 | 0.0012423 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-10 15:18 | 2023-05-10 15:20 | 1751 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 95% DE LA CARGA POR EL 1907-04 | S2305100000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-10 | 3502 | keep | 0 | May | 2023 | 0.0023852 | 0.0011926 | Momentary | FALSE | FALSE | Not_TMED_Event | 1751
BAYAMON | 2023-05-10 15:18 | 2023-05-10 15:20 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 95% DE LA CARGA DEL 1346-02 | S2305100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-10 | 4932 | keep | 0 | May | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
SAN JUAN | 2023-05-10 15:23 | 2023-05-10 16:36 | 137 | 1:13 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN N/O CONTRA 1201-02 | S23050900949 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2023-05-10 | 10001 | keep | 0 | May | 2023 | 0.0068116 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
SAN JUAN | 2023-05-10 15:23 | 2023-05-10 16:36 | 760 | 1:13 | T | ALIMENTADOR AMARRADO | SE ABRE INTERRUPTOR PARA CERRAR PUENTE PRIMARIO EN N/O CONTRA 1201-01 | S23050900949 | New_Event | Feeder Load Transferred | Include | Include | Other | 73 | 2023-05-10 | 55480 | keep | 0 | May | 2023 | 0.037787 | 0.00051763 | Sustained | FALSE | FALSE | Not_TMED_Event | 760
BAYAMON | 2023-05-10 15:32 | 2023-05-11 11:11 | 12 | 19:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5KVA X 37.5KVA FASE @ TIERRA | B23051000098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1179 | 2023-05-10 | 14148 | keep | 0 | May | 2023 | 0.0096361 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-10 15:34 | 2023-05-10 18:41 | 12 | 3:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | B23051000075 | New_Event | Secondary Wire Break | Include | Include | Equipment | 187 | 2023-05-10 | 2244 | keep | 0 | May | 2023 | 0.0015284 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-05-10 15:41 | 2023-05-10 17:20 | 12 | 1:39 | P | DESGANCHE | 1 X 20 EN C/L SE DESGANCHO | C23051000123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-05-10 | 1188 | keep | 0 | May | 2023 | 0.00080914 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-10 15:43 | 2023-05-11 09:14 | 15 | 17:31 | P | NO SE REPORTO CAUSA | 1 X 25 EN TRANSFORMADOR NO CAUSA | S23051000506 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1051 | 2023-05-10 | 15765 | keep | 0 | May | 2023 | 0.010737 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-10 15:43 | 2023-05-10 17:15 | 25 | 1:32 | P | DESGANCHE | 1 X 25 CORTE DE LINEA SE RETIRO BAMBUA | A23051000148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-05-10 | 2300 | keep | 0 | May | 2023 | 0.0015665 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-05-10 15:53 | 2023-05-10 15:54 | 4188 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R2305100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-10 | 4188 | keep | 0 | May | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
VEGA BAJA | 2023-05-10 15:53 | 2023-05-11 09:27 | 9 | 17:34 | P | ANIMAL | 2 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23051000151 | New_Event | Animals | Include | Include | Wildlife | 1054 | 2023-05-10 | 9486 | keep | 0 | May | 2023 | 0.0064609 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-05-10 16:20 | 2023-05-10 17:42 | 2 | 1:22 | T | NO SE REPORTO CAUSA | SE PATRULLO NO SE ENCONTRO CAUSA SE CERRO INTERRUPTOR LOCALMENTE 100% EN SERVICIO | S23051000562 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 82 | 2023-05-10 | 164 | keep | 0 | May | 2023 | 0.0001117 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-10 16:23 | 2023-05-10 19:28 | 271 | 3:05 | S | NO SE REPORTO CAUSA | DISPARO 0050 SE FUE A LOCKOUT TRIP SE INSPECCIONO Y SE AUTORIZO ENERGIZAR | S23051000530 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 185 | 2023-05-10 | 50135 | keep | 0 | May | 2023 | 0.034147 | 0.00018458 | Sustained | FALSE | FALSE | Not_TMED_Event | 271
SAN JUAN | 2023-05-10 16:23 | 2023-05-10 19:36 | 74 | 3:13 | S | NO SE REPORTO CAUSA | DISPARO 0050 SE FUE A LOCKOUT TRIP SE INSPECCIONO Y SE AUTORIZO ENERGIZAR | S23051000530 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 193 | 2023-05-10 | 14282 | keep | 0 | May | 2023 | 0.0097274 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
CANOVANAS | 2023-05-10 16:28 | 2023-05-10 16:54 | 80 | 0:26 | P | DESGANCHE | 1 X 100 EN RISER DESGANCHE | R23051000121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 26 | 2023-05-10 | 2080 | keep | 0 | May | 2023 | 0.0014167 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-05-10 16:28 | 2023-05-10 18:53 | 15 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | A23051000157 | New_Event | Primary Wire Break | Include | Include | Equipment | 145 | 2023-05-10 | 2175 | keep | 0 | May | 2023 | 0.0014814 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-10 16:48 | 2023-05-10 20:25 | 30 | 3:37 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | A23051000162 | New_Event | Primary Wire Break | Include | Include | Equipment | 217 | 2023-05-10 | 6510 | keep | 0 | May | 2023 | 0.0044339 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-10 16:55 | 2023-05-10 18:10 | 15 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR REPARAR SECUNDARIA | M23051000183 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-05-10 | 1125 | keep | 0 | May | 2023 | 0.00076623 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-10 16:55 | 2023-05-11 00:10 | 60 | 7:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR -1 X 25/1 X 65 Y 1 X 100 EN CORTES DE LINEA MAL TIEMPO VIENTOS FUERTES | A23051000165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 435 | 2023-05-10 | 26100 | keep | 0 | May | 2023 | 0.017777 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-05-10 16:59 | 2023-05-10 17:49 | 10 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23051000123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-05-10 | 500 | keep | 0 | May | 2023 | 0.00034055 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-10 17:09 | 2023-05-11 11:12 | 3 | 18:03 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR AVERIADO DE 15KVA X 37.5 KVA | A23051000176 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1083 | 2023-05-10 | 3249 | keep | 0 | May | 2023 | 0.0022129 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-05-10 17:09 | 2023-05-10 23:25 | 150 | 6:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23051000177 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 376 | 2023-05-10 | 56400 | keep | 0 | May | 2023 | 0.038414 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-05-10 17:10 | 2023-05-10 18:50 | 30 | 1:40 | P | ANIMAL | 1 X 40 EN C/L SE RETIRO AVE | C23051000133 | New_Event | Animals | Include | Include | Wildlife | 100 | 2023-05-10 | 3000 | keep | 0 | May | 2023 | 0.0020433 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-10 17:16 | 2023-05-10 20:17 | 20 | 3:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO CAJA | M23051000186 | New_Event | Cutout Failure | Include | Include | Equipment | 181 | 2023-05-10 | 3620 | keep | 0 | May | 2023 | 0.0024656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-10 17:20 | 2023-05-11 09:51 | 65 | 16:31 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | R23051000125 | New_Event | Animals | Include | Include | Wildlife | 991 | 2023-05-10 | 64415 | keep | 0 | May | 2023 | 0.043873 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2023-05-10 17:29 | 2023-05-11 11:20 | 11 | 17:51 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 75 KVA AVERIADO POR 50 KVA | R23051000126 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1071 | 2023-05-10 | 11781 | keep | 0 | May | 2023 | 0.008024 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-05-10 17:36 | 2023-05-10 17:38 | 2126 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | C2305100000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-10 | 4252 | keep | 0 | May | 2023 | 0.002896 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
BAYAMON | 2023-05-10 17:40 | 2023-05-10 21:20 | 10 | 3:40 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO CON VOLTAGE SIN CARGA | S23051000576 | New_Event | Primary Wire Break | Include | Include | Equipment | 220 | 2023-05-10 | 2200 | keep | 0 | May | 2023 | 0.0014984 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-10 17:42 | 2023-05-10 19:59 | 49 | 2:17 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | R23051000127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-05-10 | 6713 | keep | 0 | May | 2023 | 0.0045722 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
BAYAMON | 2023-05-10 17:42 | 2023-05-10 18:50 | 148 | 1:08 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE SECCIONALIZO TRAMO Y SE REALIZO JUMPER EN EL SU-01 POR DESCONECTIVO AVERIADO EN SU-01 BY-230510-01 | B23051000086 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 68 | 2023-05-10 | 10064 | keep | 0 | May | 2023 | 0.0068545 | 0.0001008 | Sustained | FALSE | FALSE | Not_TMED_Event | 148
MAYAGÃœEZ | 2023-05-10 17:56 | 2023-05-10 20:27 | 150 | 2:31 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 40 EN CL LINEAS PRIMARIAS ARRIADAS | M23051000194 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 151 | 2023-05-10 | 22650 | keep | 0 | May | 2023 | 0.015427 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-05-10 18:01 | 2023-05-10 19:11 | 1 | 1:10 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA DE XMR | C23051000138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 70 | 2023-05-10 | 70 | keep | 0 | May | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-10 18:52 | 2023-05-10 20:27 | 50 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23051000198 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-05-10 | 4750 | keep | 0 | May | 2023 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-10 19:52 | 2023-05-10 19:53 | 4188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE BKR | R2305100000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-10 | 4188 | keep | 0 | May | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
CANOVANAS | 2023-05-10 20:08 | 2023-05-10 20:09 | 4188 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE BKR | R2305100000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-10 | 4188 | keep | 0 | May | 2023 | 0.0028524 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
MAYAGÃœEZ | 2023-05-10 20:08 | 2023-05-11 15:10 | 20 | 19:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA EN TRANSFORMADOR Y SE AJUSTO VOLTAJE SECUNDARIO | M23051000200 | New_Event | Cutout Failure | Include | Include | Equipment | 1142 | 2023-05-10 | 22840 | keep | 0 | May | 2023 | 0.015556 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-10 20:22 | 2023-05-11 07:33 | 15 | 11:11 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR POR AVE | P23051000169 | New_Event | Animals | Include | Include | Wildlife | 671 | 2023-05-10 | 10065 | keep | 0 | May | 2023 | 0.0068552 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-10 20:30 | 2023-05-10 21:30 | 75 | 1:00 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A23051000217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 60 | 2023-05-10 | 4500 | keep | 0 | May | 2023 | 0.0030649 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-05-10 20:34 | 2023-05-10 21:19 | 4188 | 0:45 | T | CONDUCTOR ROTO O ABIERTO | SJ-230510-51 SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 40% EN SERVICIO. | R23051000261 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 45 | 2023-05-10 | 188460 | keep | 0 | May | 2023 | 0.12836 | 0.0028524 | Sustained | FALSE | FALSE | Not_TMED_Event | 4188
HUMACAO | 2023-05-10 20:39 | 2023-05-10 22:34 | 300 | 1:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23051000152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2023-05-10 | 34500 | keep | 0 | May | 2023 | 0.023498 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2023-05-10 20:47 | 2023-05-11 10:00 | 15 | 13:13 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA LINEA | C23051000157 | New_Event | Primary Wire Break | Include | Include | Equipment | 793 | 2023-05-10 | 11895 | keep | 0 | May | 2023 | 0.0081016 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-10 20:52 | 2023-05-10 22:37 | 200 | 1:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REQUIERE CAMBIAR CAJA PRIMARIA DEFECTUOSA | A23051000238 | New_Event | Cutout Failure | Include | Include | Equipment | 105 | 2023-05-10 | 21000 | keep | 0 | May | 2023 | 0.014303 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-05-10 21:08 | 2023-05-10 22:45 | 200 | 1:37 | P | DESGANCHE | 1 X 100 EN CORTE LINEA DESGANCHE | P23051000178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-05-10 | 19400 | keep | 0 | May | 2023 | 0.013213 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-05-10 21:19 | 2023-05-10 21:44 | 2513 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | SJ-230510-51 SE SECCIONALIZO ALIMENTADOR Y SE CERRO MACHETE 50% EN SERVICIO. | R23051000261 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 25 | 2023-05-10 | 62825 | keep | 0 | May | 2023 | 0.04279 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-10 21:32 | 2023-05-11 00:02 | 588 | 2:30 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23051000161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-05-10 | 88200 | keep | 0 | May | 2023 | 0.060073 | 0.00040048 | Sustained | FALSE | FALSE | Not_TMED_Event | 588
CANOVANAS | 2023-05-10 21:44 | 2023-05-10 22:50 | 2094 | 1:06 | P | CONDUCTOR ROTO O ABIERTO | SJ-230510-51 SE SECCIONALIZO ALIMENTADOR Y SE PASO LA CARGA 2302-03 70% EN SERVICIO | R23051000261 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 66 | 2023-05-10 | 138204 | keep | 0 | May | 2023 | 0.09413 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-10 21:56 | 2023-05-11 10:19 | 1 | 12:23 | P | ANIMAL | 2X25 EN XMR CRUCE POR AVE | B23051000100 | New_Event | Animals | Include | Include | Wildlife | 743 | 2023-05-10 | 743 | keep | 0 | May | 2023 | 0.00050605 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-10 22:02 | 2023-05-10 22:03 | 1839 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 CULEBRA CRUZO AISLACION EN TERCER POSTE SALIENDO DE DAGUAO | R23051000432 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-10 | 1839 | keep | 0 | May | 2023 | 0.0012525 | 0.0012525 | Momentary | FALSE | FALSE | Not_TMED_Event | 1839
FAJARDO | 2023-05-10 22:02 | 2023-05-10 22:03 | 1778 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 CULEBRA CRUZO AISLACION EN TERCER POSTE SALIENDO DE DAGUAO | R23051000432 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-10 | 1778 | keep | 0 | May | 2023 | 0.001211 | 0.001211 | Momentary | FALSE | FALSE | Not_TMED_Event | 1778
FAJARDO | 2023-05-10 22:02 | 2023-05-10 22:03 | 1376 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 CULEBRA CRUZO AISLACION EN TERCER POSTE SALIENDO DE DAGUAO | R23051000432 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-10 | 1376 | keep | 0 | May | 2023 | 0.00093719 | 0.00093719 | Momentary | FALSE | FALSE | Not_TMED_Event | 1376
FAJARDO | 2023-05-10 22:02 | 2023-05-10 22:03 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 CULEBRA CRUZO AISLACION EN TERCER POSTE SALIENDO DE DAGUAO | R23051000428 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-10 | 293 | keep | 0 | May | 2023 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
FAJARDO | 2023-05-10 22:02 | 2023-05-10 22:03 | 1215 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 CULEBRA CRUZO AISLACION EN TERCER POSTE SALIENDO DE DAGUAO | R23051000428 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-10 | 1215 | keep | 0 | May | 2023 | 0.00082753 | 0.00082753 | Momentary | FALSE | FALSE | Not_TMED_Event | 1215
AGUADILLA | 2023-05-10 22:16 | 2023-05-11 00:57 | 150 | 2:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051000215 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 161 | 2023-05-10 | 24150 | keep | 0 | May | 2023 | 0.016448 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-05-10 22:31 | 2023-05-11 11:18 | 40 | 12:47 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23051000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 767 | 2023-05-10 | 30680 | keep | 0 | May | 2023 | 0.020896 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-10 22:50 | 2023-05-11 01:13 | 698 | 2:23 | P | CONDUCTOR ROTO O ABIERTO | SJ-230510-51 SE SECCIONALIZO ALIMENTADOR Y SE REPARO PUENTE DE LINEA MACHETE Y SE CERRO MACHETE 100% EN SERVICIO | R23051000261 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 143 | 2023-05-10 | 99814 | keep | 0 | May | 2023 | 0.067983 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-10 22:53 | 2023-05-11 10:03 | 6 | 11:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LA CAJA DE TRANSFORMADOR | P23051000194 | New_Event | Primary Wire Break | Include | Include | Equipment | 670 | 2023-05-10 | 4020 | keep | 0 | May | 2023 | 0.002738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-10 23:16 | 2023-05-11 18:49 | 207 | 19:33 | P | TERMINACION SOTERRADA AVERIADA | SE REPARO PISTOLA 2 X 65 EN CORTE DE LINEA 2 X 100 EN PARALELA | S23051000472 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 1173 | 2023-05-10 | 242811 | keep | 0 | May | 2023 | 0.16538 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-05-10 23:16 | 2023-05-11 07:40 | 30 | 8:24 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051000229 | New_Event | Vegetation Contact | Include | Include | Vegetation | 504 | 2023-05-10 | 15120 | keep | 0 | May | 2023 | 0.010298 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-05-10 23:55 | 2023-05-11 12:11 | 80 | 12:16 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23051000104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 736 | 2023-05-10 | 58880 | keep | 0 | May | 2023 | 0.040103 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-05-11 03:55 | 2023-05-11 08:56 | 10 | 5:01 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23051100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 301 | 2023-05-11 | 3010 | keep | 0 | May | 2023 | 0.0020501 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-11 04:32 | 2023-05-11 11:17 | 50 | 6:45 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23051100006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2023-05-11 | 20250 | keep | 0 | May | 2023 | 0.013792 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-05-11 05:56 | 2023-05-11 08:10 | 40 | 2:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23051100011 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 134 | 2023-05-11 | 5360 | keep | 0 | May | 2023 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-11 06:32 | 2023-05-11 10:40 | 248 | 4:08 | P | ANIMAL | SE RETIRO CULEBRA DE LINEA 1 X 40 Y 1 X 80 EN C/L | R23051100016 | New_Event | Animals | Include | Include | Wildlife | 248 | 2023-05-11 | 61504 | keep | 0 | May | 2023 | 0.04189 | 0.00016891 | Sustained | FALSE | FALSE | Not_TMED_Event | 248
UTUADO | 2023-05-11 06:32 | 2023-05-11 09:15 | 30 | 2:43 | P | DESGANCHE | 1 X 40 EN CONVERTIDOR SE NECESITA DESGANCHE | P23051100032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-05-11 | 4890 | keep | 0 | May | 2023 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-11 06:46 | 2023-05-11 06:47 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-11 | 2113 | keep | 0 | May | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2023-05-11 06:54 | 2023-05-11 09:51 | 179 | 2:57 | P | ANIMAL | SE REEMPLAZO AISLADOR, SE REALIZO DESGANCHE 1 X 15 EN XMR Y 1 X 40, 1 X 50 Y 1 X 65 EN RISER CRUCE POR AVE | R23051100019 | New_Event | Animals | Include | Include | Wildlife | 177 | 2023-05-11 | 31683 | keep | 0 | May | 2023 | 0.021579 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
CANOVANAS | 2023-05-11 07:05 | 2023-05-11 07:06 | 1615 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S2305110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-11 | 1615 | keep | 0 | May | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-05-11 07:06 | 2023-05-11 13:30 | 100 | 6:24 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REFIRIO PARA DESGANCHE MASIVO | R23051100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2023-05-11 | 38400 | keep | 0 | May | 2023 | 0.026154 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-05-11 07:10 | 2023-05-11 08:30 | 149 | 1:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO 1 X 65 EN CORTE DE LINEA | P23051100035 | New_Event | Primary Wire Break | Include | Include | Equipment | 80 | 2023-05-11 | 11920 | keep | 0 | May | 2023 | 0.0081187 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
CAGUAS | 2023-05-11 07:19 | 2023-05-11 07:20 | 1362 | 0:01 | P | ANIMAL | RECIERRE DE INTERRUPTOR LLEVA 80% DE SU CARGA | C23051100011 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-11 | 1362 | keep | 0 | May | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
CAGUAS | 2023-05-11 07:29 | 2023-05-11 07:51 | 6 | 0:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23051000114 | New_Event | Secondary Wire Break | Include | Include | Equipment | 22 | 2023-05-11 | 132 | keep | 0 | May | 2023 | 8.9905e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-05-11 07:43 | 2023-05-11 09:21 | 40 | 1:38 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23051100017 | New_Event | Animals | Include | Include | Wildlife | 98 | 2023-05-11 | 3920 | keep | 0 | May | 2023 | 0.0026699 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-11 07:43 | 2023-05-11 14:45 | 1 | 7:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 8 EN TRANSFORMADOR SE REPARO NEUTRAL | M23051100008 | New_Event | Primary Wire Break | Include | Include | Equipment | 422 | 2023-05-11 | 422 | keep | 0 | May | 2023 | 0.00028742 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-11 07:45 | 2023-05-11 13:23 | 1 | 5:38 | P | DESGANCHE | 1X30 EN C/L DESGANCHE DE BAMBUAS | B23051100023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 338 | 2023-05-11 | 338 | keep | 0 | May | 2023 | 0.00023021 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-11 07:50 | 2023-05-12 14:17 | 1 | 30:27 | P | CONDUCTOR ROTO O ABIERTO | REPARAR BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | A23051100017 | New_Event | Primary Wire Break | Include | Include | Equipment | 1827 | 2023-05-11 | 1827 | keep | 0 | May | 2023 | 0.0012444 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-11 07:54 | 2023-05-11 07:55 | 1381 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23051100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-11 | 1381 | keep | 0 | May | 2023 | 0.00094059 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
BAYAMON | 2023-05-11 07:57 | 2023-05-11 10:18 | 10 | 2:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REMPLAZAR CONECTORES SECUNDARIO | S23051100020 | New_Event | Secondary Wire Break | Include | Include | Equipment | 141 | 2023-05-11 | 1410 | keep | 0 | May | 2023 | 0.00096034 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-11 08:00 | 2023-05-11 15:10 | 1 | 7:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X 40 EN TRANSFORMADOR POR MAL TIEMPO | A23051100088 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 430 | 2023-05-11 | 430 | keep | 0 | May | 2023 | 0.00029287 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-11 08:03 | 2023-05-11 11:43 | 174 | 3:40 | P | DESGANCHE | SE REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L DESGANCHE | R23051100029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-05-11 | 38280 | keep | 0 | May | 2023 | 0.026072 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
VEGA BAJA | 2023-05-11 08:18 | 2023-05-11 13:30 | 80 | 5:12 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A23051100019 | New_Event | Animals | Include | Include | Wildlife | 312 | 2023-05-11 | 24960 | keep | 0 | May | 2023 | 0.017 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-05-11 08:24 | 2023-05-11 11:30 | 22 | 3:06 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | P23051100044 | New_Event | Animals | Include | Include | Wildlife | 186 | 2023-05-11 | 4092 | keep | 0 | May | 2023 | 0.002787 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2023-05-11 08:39 | 2023-05-11 09:11 | 327 | 0:32 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO EL BKR 2603-07 AL CERRAR EL N/O (CONVERTIDOR) CONTRA EL 2602-03. A CAUSA DE 3 CAJAS QUEMADAS EN EL CONVERTIDOR. RELACIONADO A VIA LIBRE D2023-3897_REV.2 NO FASEAN. | C23051100034 | New_Event | Cutout Failure | Include | Include | Equipment | 32 | 2023-05-11 | 10464 | keep | 0 | May | 2023 | 0.007127 | 0.00022272 | Sustained | FALSE | FALSE | Not_TMED_Event | 327
PONCE | 2023-05-11 08:46 | 2023-05-11 12:34 | 1 | 3:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA DE TRANSFORMADOR 1 X 15 | P23051100047 | New_Event | Cutout Failure | Include | Include | Equipment | 228 | 2023-05-11 | 228 | keep | 0 | May | 2023 | 0.00015529 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-11 08:47 | 2023-05-11 10:14 | 45 | 1:27 | P | ANIMAL | 2 X 50 EN C/L CRUCE POR AVE | R23051100035 | New_Event | Animals | Include | Include | Wildlife | 87 | 2023-05-11 | 3915 | keep | 0 | May | 2023 | 0.0026665 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-05-11 08:57 | 2023-05-11 11:22 | 7 | 2:25 | P | TRANSFORMADOR AVERIADO | SE ABRIO EN XMR PARA REMPLAZO DE XMR 37.5KVA X 37.5KVA FASE @ TIERRA | B23051100039 | New_Event | Service Transformer Failure | Include | Include | Equipment | 145 | 2023-05-11 | 1015 | keep | 0 | May | 2023 | 0.00069131 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-05-11 09:03 | 2023-05-11 12:52 | 10 | 3:49 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | A23051100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 229 | 2023-05-11 | 2290 | keep | 0 | May | 2023 | 0.0015597 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-11 09:08 | 2023-05-11 09:11 | 5042 | 0:03 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR POR THREE WIRE PARTIDO RELAY RECLOSER SE ENCONTRABA DESACTIVADO (OFF) POR VIA LIBRE D2023-3887 | A23051100032 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-05-11 | 15126 | keep | 0 | May | 2023 | 0.010302 | 0.0034341 | Momentary | FALSE | FALSE | Not_TMED_Event | 5042
BARRANQUITAS | 2023-05-11 09:27 | 2023-05-11 11:52 | 1 | 2:25 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23051100043 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-05-11 | 145 | keep | 0 | May | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-11 09:34 | 2023-05-11 12:21 | 1 | 2:47 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA 2 X 30 EN TRANSFORMADOR DESGANCHE | S23051100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-05-11 | 167 | keep | 0 | May | 2023 | 0.00011374 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-11 09:45 | 2023-05-11 13:20 | 1 | 3:35 | P | ANIMAL | 1 X 20 EN MONTURA DE BOMBA POR ANIMAL | P23051100058 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-05-11 | 215 | keep | 0 | May | 2023 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-11 09:46 | 2023-05-11 13:34 | 50 | 3:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23051100038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-05-11 | 11400 | keep | 0 | May | 2023 | 0.0077645 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-11 09:50 | 2023-05-11 14:20 | 50 | 4:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23051100062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 270 | 2023-05-11 | 13500 | keep | 0 | May | 2023 | 0.0091948 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-11 10:00 | 2023-05-11 15:00 | 8 | 5:00 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR 1 X 50 EN CORTE DE LINEA DESGANCHE | S23051100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 300 | 2023-05-11 | 2400 | keep | 0 | May | 2023 | 0.0016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-05-11 10:14 | 2023-05-11 13:33 | 10 | 3:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DE TRANSFORMADOR | P23051100067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 199 | 2023-05-11 | 1990 | keep | 0 | May | 2023 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-11 10:20 | 2023-05-11 11:23 | 10 | 1:03 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR PUENTE SECUNDARIO | S23051000605 | New_Event | Secondary Wire Break | Include | Include | Equipment | 63 | 2023-05-11 | 630 | keep | 0 | May | 2023 | 0.00042909 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-11 10:20 | 2023-05-11 15:27 | 10 | 5:07 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23051100067 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-05-11 | 3070 | keep | 0 | May | 2023 | 0.002091 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-11 10:29 | 2023-05-11 10:30 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051100036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-11 | 3458 | keep | 0 | May | 2023 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
AGUADILLA | 2023-05-11 10:30 | 2023-05-11 10:31 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051100037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-11 | 1827 | keep | 0 | May | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
AGUADILLA | 2023-05-11 10:30 | 2023-05-11 12:15 | 2 | 1:45 | P | CONDUCTOR ARRIADO O CRUZADO | SE ABRIO CORTE DE LINEA PARA RETEZAR LINEA CERCA DE RESIDENCIA | M23051100034 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 105 | 2023-05-11 | 210 | keep | 0 | May | 2023 | 0.00014303 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-05-11 10:30 | 2023-05-11 14:10 | 50 | 3:40 | P | ARBOL SOBRE LINEA | 1 X 30 EN CORTE DE LINEA POR ARBOL SOBRE LINEA | A23051100049 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 220 | 2023-05-11 | 11000 | keep | 0 | May | 2023 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-05-11 10:35 | 2023-05-11 12:29 | 9 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA Y TOMA | R23051100034 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2023-05-11 | 1026 | keep | 0 | May | 2023 | 0.0006988 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-05-11 10:58 | 2023-05-11 12:27 | 178 | 1:29 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23051100077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-05-11 | 15842 | keep | 0 | May | 2023 | 0.01079 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
BARRANQUITAS | 2023-05-11 10:58 | 2023-05-11 14:00 | 3 | 3:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTES SECUNDARIOS Y SE REGULO VOLTAJE DEL TAP 2 AL 3 SE DEJO EN 122V/FASE | C23051100076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 182 | 2023-05-11 | 546 | keep | 0 | May | 2023 | 0.00037188 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-11 11:00 | 2023-05-11 16:02 | 8 | 5:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO DEL T-18 @ PEDESTAL Y SE REMPLAZO BARRA QUEMADA EN PEDESTAL | B23051100070 | New_Event | Secondary Wire Break | Include | Include | Equipment | 302 | 2023-05-11 | 2416 | keep | 0 | May | 2023 | 0.0016455 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-11 11:07 | 2023-05-11 18:27 | 1 | 7:20 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23051100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 440 | 2023-05-11 | 440 | keep | 0 | May | 2023 | 0.00029968 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-11 11:32 | 2023-05-11 11:34 | 1825 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1118-09 | S23051100060 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-11 | 3650 | keep | 0 | May | 2023 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-05-11 11:32 | 2023-05-11 11:34 | 4398 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1118-08 | S23051100060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-11 | 8796 | keep | 0 | May | 2023 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
CAGUAS | 2023-05-11 11:36 | 2023-05-11 11:56 | 15 | 0:20 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARA SECUNDARIA A CAUSA DE IMPACTO DE ESCABADORA | C23051100049 | New_Event | Damage From Public | Include | Include | Public | 20 | 2023-05-11 | 300 | keep | 0 | May | 2023 | 0.00020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-11 11:42 | 2023-05-11 13:04 | 10 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR/LEVANTAR SECUNDARIA DEL SUELO TRASPATIO | S23051100067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-05-11 | 820 | keep | 0 | May | 2023 | 0.0005585 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-11 11:45 | 2023-05-11 17:25 | 80 | 5:40 | P | NO SE REPORTO CAUSA | SE CERRO RISER AHACIA COND. BILBAO QUEDO EN SERVICIO | S23051100069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2023-05-11 | 27200 | keep | 0 | May | 2023 | 0.018526 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-11 11:45 | 2023-05-11 13:37 | 10 | 1:52 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23051100096 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-05-11 | 1120 | keep | 0 | May | 2023 | 0.00076283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-11 11:48 | 2023-05-11 16:03 | 16 | 4:15 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PARARRAYO | S23051100070 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 255 | 2023-05-11 | 4080 | keep | 0 | May | 2023 | 0.0027789 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
GUAYAMA | 2023-05-11 11:59 | 2023-05-11 14:38 | 4 | 2:39 | P | PROBLEMA DEL CLIENTE | 1 X 18 NX EN SU PROBLEMA DEL CLIENTE | P23051100085 | New_Event | Customer-Related Interruption | Include | Include | Public | 159 | 2023-05-11 | 636 | keep | 0 | May | 2023 | 0.00043318 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-05-11 12:07 | 2023-05-11 17:05 | 1 | 4:58 | P | CONDUCTOR ROTO O ABIERTO | 3 X 50 EN CORTE DE LINEA SE LEVANTO NEUTRAL | S23051100075 | New_Event | Primary Wire Break | Include | Include | Equipment | 298 | 2023-05-11 | 298 | keep | 0 | May | 2023 | 0.00020297 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-11 12:10 | 2023-05-11 14:31 | 50 | 2:21 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23051100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-05-11 | 7050 | keep | 0 | May | 2023 | 0.0048017 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-11 12:15 | 2023-05-11 18:28 | 260 | 6:13 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYOS/BAJANTE PRIMARIO EN LA ENTRADA DEL CONVERTIDOR. 100% EN SERVICIO | C23051100128 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 373 | 2023-05-11 | 96980 | keep | 0 | May | 2023 | 0.066053 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
BAYAMON | 2023-05-11 12:37 | 2023-05-11 16:09 | 6 | 3:32 | P | OTRAS CAUSAS | 1X65 EN C/L CT AVERIADO | B23051100088 | New_Event | Other Causes | Include | Include | Other | 212 | 2023-05-11 | 1272 | keep | 0 | May | 2023 | 0.00086635 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-05-11 12:48 | 2023-05-11 13:07 | 1 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23051100014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-05-11 | 19 | keep | 0 | May | 2023 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-11 13:58 | 2023-05-11 16:51 | 14 | 2:53 | P | PARARRAYOS DEFECTUOSO | SE REEMPLAZO PARARRAYOS/BAJANTE PRIMARIO EN LA ENTRADA DEL CONVERTIDOR. 14 CLIENTES ENTRARON EN SERVICIO DEL 2603-09. LLEVA 260 CLIENTES DEL 2602-01 | C23051100128 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 173 | 2023-05-11 | 2422 | keep | 0 | May | 2023 | 0.0016496 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
AGUADILLA | 2023-05-11 14:16 | 2023-05-11 14:55 | 8 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA CONEXION | A23051100084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-05-11 | 312 | keep | 0 | May | 2023 | 0.0002125 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-05-11 14:20 | 2023-05-11 17:13 | 40 | 2:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO | P23051100101 | New_Event | Primary Wire Break | Include | Include | Equipment | 173 | 2023-05-11 | 6920 | keep | 0 | May | 2023 | 0.0047132 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-11 14:24 | 2023-05-11 14:25 | 1825 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | S23051100105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 1825 | keep | 0 | May | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-05-11 14:24 | 2023-05-11 14:25 | 47 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | S23051100105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 47 | keep | 0 | May | 2023 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-05-11 14:24 | 2023-05-11 14:25 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | S23051100105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 315 | keep | 0 | May | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-05-11 14:24 | 2023-05-11 14:25 | 2 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | S23051100105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 2 | keep | 0 | May | 2023 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-11 14:24 | 2023-05-11 14:25 | 2391 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3000 | S23051100105 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 2391 | keep | 0 | May | 2023 | 0.0016285 | 0.0016285 | Momentary | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2023-05-11 14:24 | 2023-05-11 14:25 | 2276 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051100230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 2276 | keep | 0 | May | 2023 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-05-11 14:24 | 2023-05-11 14:25 | 777 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051100230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 777 | keep | 0 | May | 2023 | 0.00052921 | 0.00052921 | Momentary | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-05-11 14:24 | 2023-05-11 14:25 | 12 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051100230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 12 | keep | 0 | May | 2023 | 8.1731e-06 | 8.1731e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-11 14:24 | 2023-05-11 14:25 | 1290 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051100230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 1290 | keep | 0 | May | 2023 | 0.00087861 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
MAYAGÃœEZ | 2023-05-11 14:36 | 2023-05-11 19:37 | 100 | 5:01 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO TRANSFORMADOR EN CONVERTIDOR | M23051100076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 301 | 2023-05-11 | 30100 | keep | 0 | May | 2023 | 0.020501 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-11 14:41 | 2023-05-11 16:20 | 20 | 1:39 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L NO CAUSA | C23051100137 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-05-11 | 1980 | keep | 0 | May | 2023 | 0.0013486 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-11 15:00 | 2023-05-11 16:58 | 10 | 1:58 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTE | M23051100078 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 118 | 2023-05-11 | 1180 | keep | 0 | May | 2023 | 0.00080369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-05-11 15:03 | 2023-05-11 17:00 | 1 | 1:57 | P | PROBLEMA DEL CLIENTE | 2 X 50 EN RISER POR FALTA DE MANTENIMIENTO DEL CLIENTE | P23051100109 | New_Event | Customer-Related Interruption | Include | Include | Public | 117 | 2023-05-11 | 117 | keep | 0 | May | 2023 | 7.9688e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-11 15:03 | 2023-05-11 18:25 | 6 | 3:22 | P | ANIMAL | 1 X 5 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M23051100082 | New_Event | Animals | Include | Include | Wildlife | 202 | 2023-05-11 | 1212 | keep | 0 | May | 2023 | 0.00082549 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-11 15:17 | 2023-05-12 20:09 | 18 | 28:52 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRE CORTE DE LINEA POR POSTE PRIMARIO PARTIDO TRAS PATIO | A23051100097 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1732 | 2023-05-11 | 31176 | keep | 0 | May | 2023 | 0.021234 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CAGUAS | 2023-05-11 15:20 | 2023-05-11 18:13 | 178 | 2:53 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | C23051100143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2023-05-11 | 30794 | keep | 0 | May | 2023 | 0.020974 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
CANOVANAS | 2023-05-11 15:52 | 2023-05-11 17:04 | 43 | 1:12 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR IGUANA | R23051100085 | New_Event | Animals | Include | Include | Wildlife | 72 | 2023-05-11 | 3096 | keep | 0 | May | 2023 | 0.0021087 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
AGUADILLA | 2023-05-11 15:52 | 2023-05-11 19:14 | 63 | 3:22 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23051100103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-05-11 | 12726 | keep | 0 | May | 2023 | 0.0086676 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
MAYAGÃœEZ | 2023-05-11 15:53 | 2023-05-11 18:45 | 100 | 2:52 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051100085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-05-11 | 17200 | keep | 0 | May | 2023 | 0.011715 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-05-11 16:08 | 2023-05-11 22:00 | 53 | 5:52 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A23051100105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2023-05-11 | 18656 | keep | 0 | May | 2023 | 0.012707 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
SAN JUAN | 2023-05-11 16:13 | 2023-05-11 16:16 | 1487 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO LLEVA 40% DE SU CARGA | S23051100122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-11 | 4461 | keep | 0 | May | 2023 | 0.0030384 | 0.0010128 | Momentary | FALSE | FALSE | Not_TMED_Event | 1487
BAYAMON | 2023-05-11 16:31 | 2023-05-11 17:44 | 280 | 1:13 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO EN TRONCAL DE ALIMENTADOR MEDIANTE G.O.I. BY-230511-01 | B23051100092 | New_Event | Primary Wire Break | Include | Include | Equipment | 73 | 2023-05-11 | 20440 | keep | 0 | May | 2023 | 0.013922 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
VEGA BAJA | 2023-05-11 16:46 | 2023-05-11 19:58 | 40 | 3:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR Y 1 X 25 EN CORTE DE LINEA SE REEMPLAZARON PORTAFUSIBLES | A23051100112 | New_Event | Cutout Failure | Include | Include | Equipment | 192 | 2023-05-11 | 7680 | keep | 0 | May | 2023 | 0.0052308 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-11 16:50 | 2023-05-11 19:05 | 20 | 2:15 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | S23051100130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-05-11 | 2700 | keep | 0 | May | 2023 | 0.001839 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-05-11 16:53 | 2023-05-11 17:44 | 300 | 0:51 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23051100193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2023-05-11 | 15300 | keep | 0 | May | 2023 | 0.010421 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
MAYAGÃœEZ | 2023-05-11 16:54 | 2023-05-12 11:15 | 10 | 18:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23051100093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1101 | 2023-05-11 | 11010 | keep | 0 | May | 2023 | 0.0074989 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-11 17:15 | 2023-05-11 17:16 | 4390 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C23051100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 4390 | keep | 0 | May | 2023 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2023-05-11 17:15 | 2023-05-11 17:16 | 2092 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C23051100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 2092 | keep | 0 | May | 2023 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2023-05-11 17:15 | 2023-05-11 17:16 | 540 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C23051100219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 540 | keep | 0 | May | 2023 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2023-05-11 17:15 | 2023-05-11 17:16 | 131 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C23051100220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 131 | keep | 0 | May | 2023 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2023-05-11 17:15 | 2023-05-11 17:16 | 2281 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C23051100220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 2281 | keep | 0 | May | 2023 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2023-05-11 17:15 | 2023-05-11 17:16 | 1569 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C23051100220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 1569 | keep | 0 | May | 2023 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2023-05-11 17:15 | 2023-05-11 17:16 | 2417 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 9300 | C23051100220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-11 | 2417 | keep | 0 | May | 2023 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
CANOVANAS | 2023-05-11 17:26 | 2023-05-11 19:50 | 7 | 2:24 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23051100087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 144 | 2023-05-11 | 1008 | keep | 0 | May | 2023 | 0.00068654 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-05-11 17:38 | 2023-05-11 17:43 | 2531 | 0:05 | P | NO SE REPORTO CAUSA | DISPARO DE BKR 50% DE SU CARGA TRANSFERIDA | R2305110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-05-11 | 12655 | keep | 0 | May | 2023 | 0.0086193 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
FAJARDO | 2023-05-11 18:08 | 2023-05-11 19:05 | 40 | 0:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN C/L SE REEMPLAZO CAJA PRIMARIA | R23051100092 | New_Event | Cutout Failure | Include | Include | Equipment | 57 | 2023-05-11 | 2280 | keep | 0 | May | 2023 | 0.0015529 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-11 18:23 | 2023-05-11 18:25 | 1979 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23051100131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-11 | 3958 | keep | 0 | May | 2023 | 0.0026958 | 0.0013479 | Momentary | FALSE | FALSE | Not_TMED_Event | 1979
FAJARDO | 2023-05-11 18:30 | 2023-05-11 19:10 | 30 | 0:40 | P | DESGANCHE | 1 X 15 EN XMR Y 1 X 25 EN C/L DESGANCHE | R23051100097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 40 | 2023-05-11 | 1200 | keep | 0 | May | 2023 | 0.00081731 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-11 18:56 | 2023-05-11 21:15 | 50 | 2:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA CAJA QUEMADA | S23051100140 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2023-05-11 | 6950 | keep | 0 | May | 2023 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-05-11 18:56 | 2023-05-11 19:47 | 2 | 0:51 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23051100100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 51 | 2023-05-11 | 102 | keep | 0 | May | 2023 | 6.9472e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-05-11 18:59 | 2023-05-11 19:00 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | S2305110000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-11 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
BAYAMON | 2023-05-11 19:12 | 2023-05-12 12:23 | 52 | 17:11 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23051100020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1031 | 2023-05-11 | 53612 | keep | 0 | May | 2023 | 0.036515 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
BAYAMON | 2023-05-11 19:16 | 2023-05-11 20:32 | 2364 | 1:16 | T | CABLE SOTERRADO AVERIADO | CABLE SOTERRADO DESDE EL INTERRUPTOR HACIA EL RISER DE SALIDA AVERIADO SE TRANSFIRIO LA CARGA AL 1709-03 MEDIANTE G.O.I BY-230511-02 | S23051100210 | New_Event | UG Cable Fault | Include | Include | Equipment | 76 | 2023-05-11 | 179664 | keep | 0 | May | 2023 | 0.12237 | 0.0016101 | Sustained | FALSE | FALSE | Not_TMED_Event | 2364
UTUADO | 2023-05-11 19:28 | 2023-05-12 12:30 | 17 | 17:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO DE CAJA A TRANSFORMADOR | A23051100126 | New_Event | Primary Wire Break | Include | Include | Equipment | 1022 | 2023-05-11 | 17374 | keep | 0 | May | 2023 | 0.011833 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
HUMACAO | 2023-05-11 19:38 | 2023-05-12 07:59 | 13 | 12:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR Y SE ELIMINIO SECUNDARIA VACANTE EN EL SUELO | C23051100232 | New_Event | Secondary Wire Break | Include | Include | Equipment | 741 | 2023-05-11 | 9633 | keep | 0 | May | 2023 | 0.006561 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-05-11 19:48 | 2023-05-12 19:41 | 10 | 23:53 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | S23051100215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1433 | 2023-05-11 | 14330 | keep | 0 | May | 2023 | 0.0097601 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-11 19:52 | 2023-05-12 09:20 | 25 | 13:28 | P | ANIMAL | 1X30 EN C/L CRUCE POR AVE | B23051100250 | New_Event | Animals | Include | Include | Wildlife | 808 | 2023-05-11 | 20200 | keep | 0 | May | 2023 | 0.013758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-05-11 19:58 | 2023-05-11 21:10 | 90 | 1:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA DE 100A Y 1 X 100 CORTE DE LINEA | P23051100139 | New_Event | Cutout Failure | Include | Include | Equipment | 72 | 2023-05-11 | 6480 | keep | 0 | May | 2023 | 0.0044135 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-05-11 20:04 | 2023-05-11 20:23 | 20 | 0:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X25 EN C/L POR VIENTO FUERTE | B23051100260 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 19 | 2023-05-11 | 380 | keep | 0 | May | 2023 | 0.00025882 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-05-11 20:11 | 2023-05-12 07:40 | 9 | 11:29 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR FUSIBLE PODRIDO | A23051100129 | New_Event | Other Causes | Include | Include | Other | 689 | 2023-05-11 | 6201 | keep | 0 | May | 2023 | 0.0042235 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-05-11 20:45 | 2023-05-12 00:15 | 25 | 3:30 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR AVE CRUZO FASE A TIERRA | M23051100120 | New_Event | Animals | Include | Include | Wildlife | 210 | 2023-05-11 | 5250 | keep | 0 | May | 2023 | 0.0035758 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-11 20:52 | 2023-05-11 22:00 | 200 | 1:08 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23051100122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-05-11 | 13600 | keep | 0 | May | 2023 | 0.0092629 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-05-11 21:09 | 2023-05-11 23:25 | 1000 | 2:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23051100157 | New_Event | Cutout Failure | Include | Include | Equipment | 136 | 2023-05-11 | 136000 | keep | 0 | May | 2023 | 0.092629 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
ARECIBO | 2023-05-11 21:19 | 2023-05-12 10:48 | 70 | 13:29 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO | A23051100136 | New_Event | Primary Wire Break | Include | Include | Equipment | 809 | 2023-05-11 | 56630 | keep | 0 | May | 2023 | 0.03857 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-05-11 21:27 | 2023-05-11 23:10 | 300 | 1:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M23051100171 | New_Event | Cutout Failure | Include | Include | Equipment | 103 | 2023-05-11 | 30900 | keep | 0 | May | 2023 | 0.021046 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BARRANQUITAS | 2023-05-11 21:28 | 2023-05-11 21:29 | 2457 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051100243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-11 | 2457 | keep | 0 | May | 2023 | 0.0016735 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
VEGA BAJA | 2023-05-11 21:32 | 2023-05-12 08:45 | 30 | 11:13 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A23051100139 | New_Event | Vegetation Contact | Include | Include | Vegetation | 673 | 2023-05-11 | 20190 | keep | 0 | May | 2023 | 0.013751 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-05-11 21:36 | 2023-05-12 17:30 | 540 | 19:54 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L PARA REPAPAR POSTE PRIMARIO PARTIDO. | C23051100246 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1194 | 2023-05-11 | 644760 | keep | 0 | May | 2023 | 0.43914 | 0.00036779 | Sustained | FALSE | FALSE | Not_TMED_Event | 540
ARECIBO | 2023-05-11 21:44 | 2023-05-12 10:00 | 70 | 12:16 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A23051100151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 736 | 2023-05-11 | 51520 | keep | 0 | May | 2023 | 0.03509 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-05-11 21:50 | 2023-05-11 23:55 | 300 | 2:05 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23051100197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-05-11 | 37500 | keep | 0 | May | 2023 | 0.025541 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
SAN JUAN | 2023-05-11 21:58 | 2023-05-12 00:13 | 514 | 2:15 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1520-05 LLEVA 1520-01 Y LLEVA 1520-04 SE SECCIONALIZA 1520-04 POR CONDUCTOR PRIMARIO EN EL SUELO MEDIANTE GOI SJ-230511-01 | S23051100260 | New_Event | Feeder Load Transferred | Include | Include | Other | 135 | 2023-05-11 | 69390 | keep | 0 | May | 2023 | 0.047261 | 0.00035008 | Sustained | FALSE | FALSE | Not_TMED_Event | 514
SAN JUAN | 2023-05-11 21:58 | 2023-05-12 00:13 | 752 | 2:15 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1520-05 LLEVA 1520-01 Y LLEVA 1520-04 SE SECCIONALIZA 1520-04 POR CONDUCTOR PRIMARIO EN EL SUELO Y ENTRA 90% EN SERVICIO MEDIANTE GOI SJ-230511-01 | S23051100260 | New_Event | Primary Wire Break | Include | Include | Equipment | 135 | 2023-05-11 | 101520 | keep | 0 | May | 2023 | 0.069145 | 0.00051218 | Sustained | FALSE | FALSE | Not_TMED_Event | 752
SAN JUAN | 2023-05-11 21:58 | 2023-05-12 00:13 | 68 | 2:15 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1520-05 LLEVA 1520-01 Y LLEVA 1520-04 SE SECCIONALIZA 1520-04 POR CONDUCTOR PRIMARIO EN EL SUELO MEDIANTE GOI SJ-230511-01 | S23051100260 | New_Event | Feeder Load Transferred | Include | Include | Other | 135 | 2023-05-11 | 9180 | keep | 0 | May | 2023 | 0.0062525 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
YAUCO | 2023-05-11 22:09 | 2023-05-12 01:00 | 150 | 2:51 | P | SOBRECARGA | 1 X 65 EN CORTE DE LINEA SOBRECARGA | P23051100166 | New_Event | Trip Due To Overload | Include | Include | Other | 171 | 2023-05-11 | 25650 | keep | 0 | May | 2023 | 0.01747 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
VEGA BAJA | 2023-05-11 22:15 | 2023-05-12 13:35 | 30 | 15:20 | P | DESGANCHE | 1 X 25 Y 1 X 30 EN DIFERENTES CORTES DE LINEA SE REALIZO DESGANCHE | A23051100166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 920 | 2023-05-11 | 27600 | keep | 0 | May | 2023 | 0.018798 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-05-11 22:53 | 2023-05-12 09:46 | 116 | 10:53 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23051100290 | New_Event | Vegetation Contact | Include | Include | Vegetation | 653 | 2023-05-11 | 75748 | keep | 0 | May | 2023 | 0.051592 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
VEGA BAJA | 2023-05-11 23:03 | 2023-05-12 09:29 | 51 | 10:26 | P | NO SE REPORTO CAUSA | 1X40 EN C/L | B23051100292 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 626 | 2023-05-11 | 31926 | keep | 0 | May | 2023 | 0.021745 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2023-05-11 23:55 | 2023-05-12 09:30 | 50 | 9:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | M23051100242 | New_Event | Vegetation Contact | Include | Include | Vegetation | 575 | 2023-05-11 | 28750 | keep | 0 | May | 2023 | 0.019581 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-12 00:13 | 2023-05-12 02:49 | 75 | 2:36 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR Y SE LEVANTO CONDUCTOR PRIMARIO EN EL SUELO 100% EN SERVICIO MEDIANTE GOI SJ-230511-01 | S23051100260 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 156 | 2023-05-12 | 11700 | keep | 0 | May | 2023 | 0.0079688 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-12 01:25 | 2023-05-12 09:20 | 5 | 7:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CAJA A BUSHING DE TRANSFORMADOR | M23051200003 | New_Event | Primary Wire Break | Include | Include | Equipment | 475 | 2023-05-12 | 2375 | keep | 0 | May | 2023 | 0.0016176 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-05-12 01:30 | 2023-05-12 01:31 | 2720 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A23051200005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-12 | 2720 | keep | 0 | May | 2023 | 0.0018526 | 0.0018526 | Momentary | FALSE | FALSE | Not_TMED_Event | 2720
ARECIBO | 2023-05-12 01:31 | 2023-05-12 08:40 | 100 | 7:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA | A23051200007 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 429 | 2023-05-12 | 42900 | keep | 0 | May | 2023 | 0.029219 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-05-12 02:20 | 2023-05-12 07:48 | 100 | 5:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA NO FUNDIO | B23051200002 | New_Event | Cutout Failure | Include | Include | Equipment | 328 | 2023-05-12 | 32800 | keep | 0 | May | 2023 | 0.02234 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-12 03:23 | 2023-05-12 15:40 | 20 | 12:17 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA INSTALAR POSTE SECUNDARIO AVERIADO | M23051200005 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 737 | 2023-05-12 | 14740 | keep | 0 | May | 2023 | 0.010039 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-12 03:48 | 2023-05-12 14:38 | 100 | 10:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P23051200006 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 650 | 2023-05-12 | 65000 | keep | 0 | May | 2023 | 0.044271 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-05-12 04:08 | 2023-05-12 04:09 | 2450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23051200008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2450 | keep | 0 | May | 2023 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-05-12 04:08 | 2023-05-12 04:13 | 640 | 0:05 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | C23051200007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-05-12 | 3200 | keep | 0 | May | 2023 | 0.0021795 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
AGUADILLA | 2023-05-12 04:35 | 2023-05-12 04:36 | 1827 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051200012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 1827 | keep | 0 | May | 2023 | 0.0012444 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
BARRANQUITAS | 2023-05-12 05:13 | 2023-05-12 10:20 | 60 | 5:07 | P | CONDUCTOR ROTO O ABIERTO | SE AISLO CABLE DE CERCA DE CRUCETA Y SE REPUSO 1 X 80 EN C/L | C23051200010 | New_Event | Primary Wire Break | Include | Include | Equipment | 307 | 2023-05-12 | 18420 | keep | 0 | May | 2023 | 0.012546 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-05-12 06:36 | 2023-05-12 06:37 | 640 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23051200015 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 640 | keep | 0 | May | 2023 | 0.0004359 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-12 07:03 | 2023-05-12 13:35 | 5 | 6:32 | P | ARBOL SOBRE LINEA | SE ABRIO XMR SE REMOVIO ARBOL. SE REALIZO DESGANCHE Y SE REPARO LINEA SECUNDARIA | C23051200021 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 392 | 2023-05-12 | 1960 | keep | 0 | May | 2023 | 0.0013349 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-05-12 07:10 | 2023-05-12 10:50 | 100 | 3:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | M23051200021 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 220 | 2023-05-12 | 22000 | keep | 0 | May | 2023 | 0.014984 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-05-12 07:15 | 2023-05-12 09:57 | 236 | 2:42 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23051200023 | New_Event | Animals | Include | Include | Wildlife | 162 | 2023-05-12 | 38232 | keep | 0 | May | 2023 | 0.02604 | 0.00016074 | Sustained | FALSE | FALSE | Not_TMED_Event | 236
ARECIBO | 2023-05-12 07:30 | 2023-05-12 07:31 | 1227 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23051200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 1227 | keep | 0 | May | 2023 | 0.0008357 | 0.0008357 | Momentary | FALSE | FALSE | Not_TMED_Event | 1227
AGUADILLA | 2023-05-12 07:31 | 2023-05-12 10:35 | 70 | 3:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE AVERIADO | M23051200031 | New_Event | Cutout Failure | Include | Include | Equipment | 184 | 2023-05-12 | 12880 | keep | 0 | May | 2023 | 0.0087725 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-05-12 07:34 | 2023-05-12 19:27 | 15 | 11:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051200037 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 713 | 2023-05-12 | 10695 | keep | 0 | May | 2023 | 0.0072843 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-12 07:38 | 2023-05-12 10:17 | 10 | 2:39 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR DESGANCHE SECUNDARIO | B23051200019 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 159 | 2023-05-12 | 1590 | keep | 0 | May | 2023 | 0.0010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-12 07:40 | 2023-05-12 08:46 | 7 | 1:06 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23051200032 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-05-12 | 462 | keep | 0 | May | 2023 | 0.00031467 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-05-12 07:44 | 2023-05-12 13:34 | 3 | 5:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN XMR Y 1 X 15 EN XMR | C23051200034 | New_Event | Cutout Failure | Include | Include | Equipment | 350 | 2023-05-12 | 1050 | keep | 0 | May | 2023 | 0.00071515 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-05-12 07:55 | 2023-05-12 10:54 | 1 | 2:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA EN RISER Y 1 X 65 EN C/L | C23051200036 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2023-05-12 | 179 | keep | 0 | May | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-12 08:13 | 2023-05-12 08:14 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 906 | keep | 0 | May | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
SAN JUAN | 2023-05-12 08:22 | 2023-05-12 17:06 | 1 | 8:44 | P | NO SE REPORTO CAUSA | 1 X 18 NX EN BOVEDA NO CAUSA | S23051200018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 524 | 2023-05-12 | 524 | keep | 0 | May | 2023 | 0.00035689 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-12 08:29 | 2023-05-12 18:16 | 5 | 9:47 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | S23051200020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 587 | 2023-05-12 | 2935 | keep | 0 | May | 2023 | 0.001999 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-12 08:34 | 2023-05-12 08:35 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2402 | keep | 0 | May | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
MAYAGÃœEZ | 2023-05-12 08:35 | 2023-05-12 13:10 | 15 | 4:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M23051200002 | New_Event | Secondary Wire Break | Include | Include | Equipment | 275 | 2023-05-12 | 4125 | keep | 0 | May | 2023 | 0.0028095 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-05-12 08:44 | 2023-05-12 11:20 | 100 | 2:36 | P | ANIMAL | 1 X 40 Y 1 X 50 EN C/LS CRUCE X AVE | R23051200011 | New_Event | Animals | Include | Include | Wildlife | 156 | 2023-05-12 | 15600 | keep | 0 | May | 2023 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-12 08:47 | 2023-05-12 09:54 | 6 | 1:07 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REALIZAR DESGANCHE SECUNDARIO REPARAR/SUBIR LINEA SECUNDARIA PARTIDA DEL SUELO | B23051200003 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 67 | 2023-05-12 | 402 | keep | 0 | May | 2023 | 0.0002738 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-05-12 09:04 | 2023-05-12 12:18 | 4 | 3:14 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23051200050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 194 | 2023-05-12 | 776 | keep | 0 | May | 2023 | 0.00052853 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-05-12 09:07 | 2023-05-12 09:55 | 1 | 0:48 | P | ANIMAL | 2 X 15 EN TRANSFORMADOR SE RETIOR NIDO DE AVE | A23051200039 | New_Event | Animals | Include | Include | Wildlife | 48 | 2023-05-12 | 48 | keep | 0 | May | 2023 | 3.2693e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-12 09:16 | 2023-05-12 12:14 | 105 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE BRISA | P23051200053 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-05-12 | 18690 | keep | 0 | May | 2023 | 0.01273 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
BAYAMON | 2023-05-12 09:29 | 2023-05-12 11:17 | 100 | 1:48 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | B23051200038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-05-12 | 10800 | keep | 0 | May | 2023 | 0.0073558 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-12 09:41 | 2023-05-12 10:12 | 87 | 0:31 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN C/L FIJO CONDUCTOR | R23051200019 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 31 | 2023-05-12 | 2697 | keep | 0 | May | 2023 | 0.0018369 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
PONCE | 2023-05-12 09:53 | 2023-05-12 12:30 | 70 | 2:37 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | P23051200061 | New_Event | Animals | Include | Include | Wildlife | 157 | 2023-05-12 | 10990 | keep | 0 | May | 2023 | 0.0074852 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-05-12 10:00 | 2023-05-12 10:01 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23051200062 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2697 | keep | 0 | May | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-05-12 10:01 | 2023-05-12 15:21 | 1 | 5:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 30 EN C/L SE REMPLAZO PORTA FUSIBLE | B23051200041 | New_Event | Cutout Failure | Include | Include | Equipment | 320 | 2023-05-12 | 320 | keep | 0 | May | 2023 | 0.00021795 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-12 10:12 | 2023-05-12 11:52 | 11 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA | C23051200065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2023-05-12 | 1100 | keep | 0 | May | 2023 | 0.0007492 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-05-12 10:20 | 2023-05-12 10:40 | 15 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR LINEA SECUNDARIA AVERIADA | M23051200095 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-05-12 | 300 | keep | 0 | May | 2023 | 0.00020433 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-05-12 10:28 | 2023-05-12 13:10 | 4 | 2:42 | P | OTRAS CAUSAS | 1 X 20 EN TRANSFORMADOR FUSIBLE PODRIDO | A23051200068 | New_Event | Other Causes | Include | Include | Other | 162 | 2023-05-12 | 648 | keep | 0 | May | 2023 | 0.00044135 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-05-12 10:30 | 2023-05-12 11:40 | 25 | 1:10 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L Y SE REPARO ALAMBRE PRIMARIO EN EL SUELO | C23051200073 | New_Event | Primary Wire Break | Include | Include | Equipment | 70 | 2023-05-12 | 1750 | keep | 0 | May | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-12 10:34 | 2023-05-12 11:35 | 1588 | 1:01 | T | ALIMENTADOR AMARRADO | CARGA TRANSFERIDA AL 1716-03 DISPARO FUE POR PROTECCION DE DIFERENCIAL DEL TIE-BREAKER 1716-00 CON LA 1711-00, SE REPARO LA CONDICION POR PERSONAL CDS | B23051200048 | New_Event | Feeder Load Transferred | Include | Include | Other | 61 | 2023-05-12 | 96868 | keep | 0 | May | 2023 | 0.065976 | 0.0010816 | Sustained | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-05-12 10:34 | 2023-05-12 11:35 | 13 | 1:01 | T | ALIMENTADOR AMARRADO | CARGA TRANSFERIDA AL 1716-03 DISPARO FUE POR PROTECCION DE DIFERENCIAL DEL TIE-BREAKER 1716-00 CON LA 1711-00, SE REPARO LA CONDICION POR PERSONAL CDS | B23051200048 | New_Event | Feeder Load Transferred | Include | Include | Other | 61 | 2023-05-12 | 793 | keep | 0 | May | 2023 | 0.00054011 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-05-12 10:34 | 2023-05-12 11:24 | 450 | 0:50 | S | PROTECCION DEFECTUOSA | DISPARO FUE POR PROTECCION DE DIFERENCIAL DEL TIE-BREAKER 1716-00 CON LA 1711-00, SE REPARO LA CONDICION POR PERSONAL CDS | B23051200048 | New_Event | Protection Miscoordination | Include | Include | Other | 50 | 2023-05-12 | 22500 | keep | 0 | May | 2023 | 0.015325 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
BAYAMON | 2023-05-12 10:34 | 2023-05-12 11:24 | 651 | 0:50 | S | PROTECCION DEFECTUOSA | DISPARO FUE POR PROTECCION DE DIFERENCIAL DEL TIE-BREAKER 1716-00 CON LA 1711-00, SE REPARO LA CONDICION POR PERSONAL CDS | B23051200048 | New_Event | Protection Miscoordination | Include | Include | Other | 50 | 2023-05-12 | 32550 | keep | 0 | May | 2023 | 0.02217 | 0.00044339 | Sustained | FALSE | FALSE | Not_TMED_Event | 651
BAYAMON | 2023-05-12 10:34 | 2023-05-12 11:35 | 1812 | 1:01 | S | PROTECCION DEFECTUOSA | DISPARO FUE POR PROTECCION DE DIFERENCIAL DEL TIE-BREAKER 1716-00 CON LA 1711-00, SE REPARO LA CONDICION POR PERSONAL CDS LLEVA CARGA DEL 1711-01 Y DEL 1711-03 | B23051200048 | New_Event | Protection Miscoordination | Include | Include | Other | 61 | 2023-05-12 | 110532 | keep | 0 | May | 2023 | 0.075283 | 0.0012341 | Sustained | FALSE | FALSE | Not_TMED_Event | 1812
ARECIBO | 2023-05-12 10:48 | 2023-05-12 12:45 | 200 | 1:57 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR PUENTE ABIERTO | A23051100136 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 117 | 2023-05-12 | 23400 | keep | 0 | May | 2023 | 0.015938 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-12 10:53 | 2023-05-13 11:49 | 72 | 24:56 | P | DESGANCHE | 2 X 100 Y DESGANCHE | S23051200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1496 | 2023-05-12 | 107712 | keep | 0 | May | 2023 | 0.073362 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
VEGA BAJA | 2023-05-12 10:53 | 2023-05-12 10:54 | 2697 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23051200072 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2697 | keep | 0 | May | 2023 | 0.0018369 | 0.0018369 | Momentary | FALSE | FALSE | Not_TMED_Event | 2697
VEGA BAJA | 2023-05-12 11:10 | 2023-05-12 15:29 | 119 | 4:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO CAJA | B23051200077 | New_Event | Cutout Failure | Include | Include | Equipment | 259 | 2023-05-12 | 30821 | keep | 0 | May | 2023 | 0.020992 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
AGUADILLA | 2023-05-12 11:13 | 2023-05-12 13:30 | 80 | 2:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051200106 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 137 | 2023-05-12 | 10960 | keep | 0 | May | 2023 | 0.0074648 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-12 11:23 | 2023-05-12 14:33 | 169 | 3:10 | P | ANIMAL | 1 X 100 EN RISER CRUCE POR AVE | S23051200056 | New_Event | Animals | Include | Include | Wildlife | 190 | 2023-05-12 | 32110 | keep | 0 | May | 2023 | 0.02187 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
CAGUAS | 2023-05-12 11:27 | 2023-05-12 15:18 | 40 | 3:51 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C23051200099 | New_Event | Animals | Include | Include | Wildlife | 231 | 2023-05-12 | 9240 | keep | 0 | May | 2023 | 0.0062933 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-12 11:30 | 2023-05-12 18:20 | 6 | 6:50 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA BAJANTE PRIMARIO | A23051200079 | New_Event | Primary Wire Break | Include | Include | Equipment | 410 | 2023-05-12 | 2460 | keep | 0 | May | 2023 | 0.0016755 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-12 11:42 | 2023-05-12 17:18 | 1 | 5:36 | P | ANIMAL | 1 X 25 EN RISER CHANGO CRUZO FASE | S23051200065 | New_Event | Animals | Include | Include | Wildlife | 336 | 2023-05-12 | 336 | keep | 0 | May | 2023 | 0.00022885 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-12 11:55 | 2023-05-12 21:46 | 70 | 9:51 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | S23051200066 | New_Event | Primary Wire Break | Include | Include | Equipment | 591 | 2023-05-12 | 41370 | keep | 0 | May | 2023 | 0.028177 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-05-12 12:15 | 2023-05-12 12:35 | 3 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR REPARAR SECUNDARIA | M23051200091 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-05-12 | 60 | keep | 0 | May | 2023 | 4.0866e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-12 12:32 | 2023-05-13 14:26 | 10 | 25:54 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23051200101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1554 | 2023-05-12 | 15540 | keep | 0 | May | 2023 | 0.010584 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-12 12:33 | 2023-05-12 12:34 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23051200115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 676 | keep | 0 | May | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2023-05-12 12:43 | 2023-05-12 12:59 | 19 | 0:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTES SECUNDARIOS | C23051200100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 16 | 2023-05-12 | 304 | keep | 0 | May | 2023 | 0.00020705 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2023-05-12 12:46 | 2023-05-12 14:16 | 20 | 1:30 | P | DESGANCHE | 1 X 40 EN C/L | R23051200029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-05-12 | 1800 | keep | 0 | May | 2023 | 0.001226 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-05-12 12:50 | 2023-05-12 14:14 | 40 | 1:24 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | C23051200118 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-05-12 | 3360 | keep | 0 | May | 2023 | 0.0022885 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-05-12 12:51 | 2023-05-12 15:09 | 1142 | 2:18 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO POSTE PRIMARIO AVERIADO | M23051200101 | New_Event | Primary Pole Failure | Include | Include | Equipment | 138 | 2023-05-12 | 157596 | keep | 0 | May | 2023 | 0.10734 | 0.00077781 | Sustained | FALSE | FALSE | Not_TMED_Event | 1142
CANOVANAS | 2023-05-12 12:58 | 2023-05-12 13:22 | 1 | 0:24 | P | NO SE REPORTO CAUSA | 1 X 10 NX EN EL T - PARQUE | R23051200030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2023-05-12 | 24 | keep | 0 | May | 2023 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-12 13:02 | 2023-05-12 14:52 | 31 | 1:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REPARAR LINEA SECUNDARIA Y REPONER FUSIBLE EN CORTE DE LINEA 2 X 65 | P23051200099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 110 | 2023-05-12 | 3410 | keep | 0 | May | 2023 | 0.0023225 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
HUMACAO | 2023-05-12 13:06 | 2023-05-12 13:07 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23051200122 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 676 | keep | 0 | May | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
SAN JUAN | 2023-05-12 13:15 | 2023-05-12 14:49 | 8 | 1:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO Y SE REMPLAZO CAJA | S23051200059 | New_Event | Cutout Failure | Include | Include | Equipment | 94 | 2023-05-12 | 752 | keep | 0 | May | 2023 | 0.00051218 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-12 13:33 | 2023-05-12 17:57 | 2530 | 4:24 | T | CONDUCTOR ARRIADO O CRUZADO | LINEAS PRIMARIAS CRUZADAS | M23051200129 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 264 | 2023-05-12 | 667920 | keep | 0 | May | 2023 | 0.45492 | 0.0017232 | Sustained | FALSE | FALSE | Not_TMED_Event | 2530
MAYAGÃœEZ | 2023-05-12 13:33 | 2023-05-12 13:34 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE INTERRUPTOR | M23051200128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 199 | keep | 0 | May | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
AGUADILLA | 2023-05-12 13:51 | 2023-05-13 09:50 | 20 | 19:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23051200090 | New_Event | Cutout Failure | Include | Include | Equipment | 1199 | 2023-05-12 | 23980 | keep | 0 | May | 2023 | 0.016333 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-05-12 13:54 | 2023-05-12 17:12 | 10 | 3:18 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN CAJA PRIMARIA DE CORTE DE LINEA | P23051200107 | New_Event | Primary Wire Break | Include | Include | Equipment | 198 | 2023-05-12 | 1980 | keep | 0 | May | 2023 | 0.0013486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-05-12 14:05 | 2023-05-12 15:52 | 30 | 1:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE BAMBUAS | P23051200112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 107 | 2023-05-12 | 3210 | keep | 0 | May | 2023 | 0.0021863 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-05-12 14:26 | 2023-05-12 16:27 | 40 | 2:01 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23051200141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-05-12 | 4840 | keep | 0 | May | 2023 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-12 14:31 | 2023-05-12 19:14 | 30 | 4:43 | P | ARBOL SOBRE LINEA | 3 X 100 EN CORTE DE LINEA POR ARBOL SOBRE LINEA | A23051200099 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 283 | 2023-05-12 | 8490 | keep | 0 | May | 2023 | 0.0057825 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-12 14:33 | 2023-05-12 14:34 | 2126 | 0:01 | T | NO SE REPORTO CAUSA | DISPARPO DE BKR CERRADO POR SCADA | C23051200143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2126 | keep | 0 | May | 2023 | 0.001448 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
MAYAGÃœEZ | 2023-05-12 14:33 | 2023-05-12 16:05 | 30 | 1:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CL LLUVIA | M23051200146 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 92 | 2023-05-12 | 2760 | keep | 0 | May | 2023 | 0.0018798 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 1399 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y FUSE HOLDER AVERIADO EN #3 | B23051200147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 4197 | keep | 0 | May | 2023 | 0.0028586 | 0.00095285 | Momentary | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 302 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y FUSE HOLDER AVERIADO EN #3 | B23051200147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 906 | keep | 0 | May | 2023 | 0.00061707 | 0.00020569 | Momentary | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 1048 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y FUSE HOLDER AVERIADO EN #3 | B23051200147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 3144 | keep | 0 | May | 2023 | 0.0021414 | 0.00071379 | Momentary | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 573 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y FUSE HOLDER AVERIADO EN #3 | B23051200147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 1719 | keep | 0 | May | 2023 | 0.0011708 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 1313 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y FUSE HOLDER AVERIADO EN #3 | B23051200147 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 3939 | keep | 0 | May | 2023 | 0.0026828 | 0.00089428 | Momentary | FALSE | FALSE | Not_TMED_Event | 1313
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 1715 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 5145 | keep | 0 | May | 2023 | 0.0035042 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 1498 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 4494 | keep | 0 | May | 2023 | 0.0030608 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 1221 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 3663 | keep | 0 | May | 2023 | 0.0024949 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-05-12 14:35 | 2023-05-12 14:38 | 1100 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200141 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-12 | 3300 | keep | 0 | May | 2023 | 0.0022476 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
CANOVANAS | 2023-05-12 14:43 | 2023-05-12 21:29 | 45 | 6:46 | P | TRANSFORMADOR AVERIADO | 1 X 40 EN SU - 2 Y 1 X 25 EN SU - 1 SE DEJO T-7 FUERA, SE ABRIO EN T-6 Y T-7 Y SE CERRO NO EN SU - 1 @ T-6 | R23051200042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 406 | 2023-05-12 | 18270 | keep | 0 | May | 2023 | 0.012444 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-05-12 14:45 | 2023-05-12 23:09 | 50 | 8:24 | P | CONDUCTOR ROTO O ABIERTO | 1 X 20 EN XMR, 1 X 100 EN C/L Y SE CERRO PUENTE DE CAJA A LINEA | S23051200080 | New_Event | Primary Wire Break | Include | Include | Equipment | 504 | 2023-05-12 | 25200 | keep | 0 | May | 2023 | 0.017164 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-12 14:45 | 2023-05-12 21:08 | 1399 | 6:23 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN AVERIA DE PUENTE ABIERTO EN BKR 1704-04 ESTE SE AVERIO Y NO OPERO FUNDIENDO DOS FUSIBLES LA ALTA DEL XMR | B23051200196 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 383 | 2023-05-12 | 535817 | keep | 0 | May | 2023 | 0.36494 | 0.00095285 | Sustained | FALSE | FALSE | Not_TMED_Event | 1399
BAYAMON | 2023-05-12 14:45 | 2023-05-12 21:08 | 302 | 6:23 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN AVERIA DE PUENTE ABIERTO EN BKR 1704-04 ESTE SE AVERIO Y NO OPERO FUNDIENDO DOS FUSIBLES LA ALTA DEL XMR | B23051200196 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 383 | 2023-05-12 | 115666 | keep | 0 | May | 2023 | 0.07878 | 0.00020569 | Sustained | FALSE | FALSE | Not_TMED_Event | 302
BAYAMON | 2023-05-12 14:45 | 2023-05-12 21:08 | 1048 | 6:23 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN AVERIA DE PUENTE ABIERTO EN BKR 1704-04 ESTE SE AVERIO Y NO OPERO FUNDIENDO DOS FUSIBLES LA ALTA DEL XMR | B23051200196 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 383 | 2023-05-12 | 401384 | keep | 0 | May | 2023 | 0.27338 | 0.00071379 | Sustained | FALSE | FALSE | Not_TMED_Event | 1048
BAYAMON | 2023-05-12 14:45 | 2023-05-12 21:45 | 573 | 7:00 | S | ARBOL SOBRE LINEA | EN AVERIA DE PUENTE ABIERTO CAUSADO POR CAIDA DE ARBOL EN BKR 1704-04 ESTE SE AVERIO Y NO OPERO FUNDIENDO DOS FUSIBLES LA ALTA DEL XMR 50% TRANSFERIDO AL 1704-05 | B23051200196 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 420 | 2023-05-12 | 240660 | keep | 0 | May | 2023 | 0.16391 | 0.00039027 | Sustained | FALSE | FALSE | Not_TMED_Event | 573
BAYAMON | 2023-05-12 14:45 | 2023-05-12 21:08 | 1313 | 6:23 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | EN AVERIA DE PUENTE ABIERTO EN BKR 1704-04 ESTE SE AVERIO Y NO OPERO FUNDIENDO DOS FUSIBLES LA ALTA DEL XMR | B23051200196 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 383 | 2023-05-12 | 502879 | keep | 0 | May | 2023 | 0.34251 | 0.00089428 | Sustained | FALSE | FALSE | Not_TMED_Event | 1313
BAYAMON | 2023-05-12 14:45 | 2023-05-12 14:47 | 959 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B2305120000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 1918 | keep | 0 | May | 2023 | 0.0013063 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-05-12 14:45 | 2023-05-12 14:47 | 1382 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B2305120000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 2764 | keep | 0 | May | 2023 | 0.0018825 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-05-12 14:45 | 2023-05-12 14:47 | 663 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B2305120000X | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 1326 | keep | 0 | May | 2023 | 0.00090313 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-05-12 14:45 | 2023-05-12 16:10 | 1715 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B2305120000X | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-05-12 | 145775 | keep | 0 | May | 2023 | 0.099287 | 0.0011681 | Sustained | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-05-12 14:45 | 2023-05-12 16:10 | 1498 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B2305120000X | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-05-12 | 127330 | keep | 0 | May | 2023 | 0.086724 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-05-12 14:45 | 2023-05-12 16:10 | 1221 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B2305120000X | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-05-12 | 103785 | keep | 0 | May | 2023 | 0.070687 | 0.00083162 | Sustained | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-05-12 14:45 | 2023-05-12 16:10 | 1100 | 1:25 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B2305120000X | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 85 | 2023-05-12 | 93500 | keep | 0 | May | 2023 | 0.063682 | 0.0007492 | Sustained | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-05-12 14:45 | 2023-05-12 14:46 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 4176 | keep | 0 | May | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-05-12 14:45 | 2023-05-12 14:46 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 252 | keep | 0 | May | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-05-12 14:45 | 2023-05-12 14:46 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200199 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 2147 | keep | 0 | May | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-05-12 14:45 | 2023-05-12 14:46 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 SUB 1704 SIERRA LINDA FUNDIO 2 FUSIBLES Y BUS SUPPORT AVERIADO EN #3 | B23051200201 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 2858 | keep | 0 | May | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
HUMACAO | 2023-05-12 14:48 | 2023-05-12 14:49 | 676 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051200147 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 676 | keep | 0 | May | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
HUMACAO | 2023-05-12 14:52 | 2023-05-12 17:39 | 295 | 2:47 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 65 EN C/L SE REEMPLAZO AISLADOR | C23051200149 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 167 | 2023-05-12 | 49265 | keep | 0 | May | 2023 | 0.033554 | 0.00020092 | Sustained | FALSE | FALSE | Not_TMED_Event | 295
SAN JUAN | 2023-05-12 14:55 | 2023-05-12 18:01 | 50 | 3:06 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23051200082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-05-12 | 9300 | keep | 0 | May | 2023 | 0.0063342 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-12 15:05 | 2023-05-12 17:45 | 80 | 2:40 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR DESGANCHE | A23051200106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-05-12 | 12800 | keep | 0 | May | 2023 | 0.008718 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-12 15:06 | 2023-05-12 15:07 | 3522 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1900 DESGANCHE CRITICO SEGUN PATRULLAJE AEREO 5/16/2023. | M23051200166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 3522 | keep | 0 | May | 2023 | 0.0023988 | 0.0023988 | Momentary | FALSE | FALSE | Not_TMED_Event | 3522
AGUADILLA | 2023-05-12 15:06 | 2023-05-12 15:07 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1900 DESGANCHE CRITICO SEGUN PATRULLAJE AEREO 5/16/2023. | M23051200166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 1337 | keep | 0 | May | 2023 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-05-12 15:06 | 2023-05-12 15:07 | 2825 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1900 DESGANCHE CRITICO SEGUN PATRULLAJE AEREO 5/16/2023. | M23051200166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 2825 | keep | 0 | May | 2023 | 0.0019241 | 0.0019241 | Momentary | FALSE | FALSE | Not_TMED_Event | 2825
AGUADILLA | 2023-05-12 15:06 | 2023-05-12 15:07 | 1287 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA DESGANCHE CRITICO SEGUN PATRULLAJE AEREO 5/16/2023. | M23051200166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 1287 | keep | 0 | May | 2023 | 0.00087657 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
AGUADILLA | 2023-05-12 15:06 | 2023-05-12 15:07 | 1417 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1900 DESGANCHE CRITICO SEGUN PATRULLAJE AEREO 5/16/2023. | M23051200167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 1417 | keep | 0 | May | 2023 | 0.00096511 | 0.00096511 | Momentary | FALSE | FALSE | Not_TMED_Event | 1417
AGUADILLA | 2023-05-12 15:06 | 2023-05-12 15:07 | 80 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1900 DESGANCHE CRITICO SEGUN PATRULLAJE AEREO 5/16/2023. | M23051200167 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 80 | keep | 0 | May | 2023 | 5.4488e-05 | 5.4488e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-05-12 15:07 | 2023-05-12 17:09 | 1 | 2:02 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23051200153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 122 | 2023-05-12 | 122 | keep | 0 | May | 2023 | 8.3094e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-12 15:08 | 2023-05-12 16:09 | 11 | 1:01 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23051200047 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-05-12 | 671 | keep | 0 | May | 2023 | 0.00045702 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-05-12 15:09 | 2023-05-13 10:33 | 643 | 19:24 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REMPLAZO DE POSTE PRIMARIO | M23051200283 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1164 | 2023-05-12 | 748452 | keep | 0 | May | 2023 | 0.50977 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-05-12 15:10 | 2023-05-13 10:55 | 50 | 19:45 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23051200112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1185 | 2023-05-12 | 59250 | keep | 0 | May | 2023 | 0.040355 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-05-12 15:13 | 2023-05-12 17:34 | 40 | 2:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23051200116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-05-12 | 5640 | keep | 0 | May | 2023 | 0.0038414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-05-12 15:16 | 2023-05-12 19:44 | 30 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR 13800529 1 X 50 EN CORTE DE LINEA MAL TIEMPO | P23051200121 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-05-12 | 8040 | keep | 0 | May | 2023 | 0.005476 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-12 15:20 | 2023-05-12 15:40 | 21 | 0:20 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO PUENTES EN NEUTRAL PRIMARIO Y SE RESTABLECIO CARGA | M23051200154 | New_Event | Primary Wire Break | Include | Include | Equipment | 20 | 2023-05-12 | 420 | keep | 0 | May | 2023 | 0.00028606 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
VEGA BAJA | 2023-05-12 15:20 | 2023-05-12 20:30 | 10 | 5:10 | P | TRANSFORMADOR AVERIADO | CAMBIO DE TRANSFORMADOR DE 37.5KVA @ 4,160 X 37.5 @ 4,800 TRANSFORMADOR SE INSTALO LUEGO DE MARIA UTILIZANDO EL DISPONIBLE AL MOMENTO | A23051200118 | New_Event | Service Transformer Failure | Include | Include | Equipment | 310 | 2023-05-12 | 3100 | keep | 0 | May | 2023 | 0.0021114 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-12 15:24 | 2023-05-13 15:38 | 18 | 24:14 | P | DESGANCHE | 1 X 80 EN C/L Y 1 X 65 EN C/L DESGANCHE | S23051200087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1454 | 2023-05-12 | 26172 | keep | 0 | May | 2023 | 0.017826 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-05-12 15:26 | 2023-05-12 18:19 | 65 | 2:53 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | S23051200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-05-12 | 11245 | keep | 0 | May | 2023 | 0.0076589 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
HUMACAO | 2023-05-12 15:29 | 2023-05-12 15:30 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2354 | keep | 0 | May | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
AGUADILLA | 2023-05-12 15:37 | 2023-05-12 18:00 | 100 | 2:23 | P | MAL TIEMPO/RAYOS | 2 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051200193 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 143 | 2023-05-12 | 14300 | keep | 0 | May | 2023 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-12 15:39 | 2023-05-13 10:33 | 300 | 18:54 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO EN TRONCAL DEL ALIMENTADOR SE ABRIO INTERRUPTOR PARA REPARAR | M23051200196 | New_Event | Primary Wire Break | Include | Include | Equipment | 1134 | 2023-05-12 | 340200 | keep | 0 | May | 2023 | 0.23171 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 1405 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 118020 | keep | 0 | May | 2023 | 0.080383 | 0.00095694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 669 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 56196 | keep | 0 | May | 2023 | 0.038275 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 1527 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 128268 | keep | 0 | May | 2023 | 0.087363 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 1054 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 88536 | keep | 0 | May | 2023 | 0.060301 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 932 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 78288 | keep | 0 | May | 2023 | 0.053322 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 705 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 59220 | keep | 0 | May | 2023 | 0.040334 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 1521 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 127764 | keep | 0 | May | 2023 | 0.087019 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2023-05-12 15:41 | 2023-05-12 17:05 | 882 | 1:24 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2400 | A23051200120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 84 | 2023-05-12 | 74088 | keep | 0 | May | 2023 | 0.050461 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
MAYAGÃœEZ | 2023-05-12 15:50 | 2023-05-12 16:38 | 1612 | 0:48 | P | NO SE REPORTO CAUSA | SE PATRULLO Y NO SE ENCONTRO CAUSA SE ACTIVO INTELLIRRUPTER | M23051200215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 48 | 2023-05-12 | 77376 | keep | 0 | May | 2023 | 0.0527 | 0.0010979 | Sustained | FALSE | FALSE | Not_TMED_Event | 1612
AGUADILLA | 2023-05-12 15:51 | 2023-05-13 14:21 | 60 | 22:30 | P | CONDUCTOR ROTO O ABIERTO | SE CIERRA PUENTE Y SE CIERRA CORTE DE LINEA | M23051200216 | New_Event | Primary Wire Break | Include | Include | Equipment | 1350 | 2023-05-12 | 81000 | keep | 0 | May | 2023 | 0.055169 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-05-12 15:52 | 2023-05-12 15:53 | 2276 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051200161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2276 | keep | 0 | May | 2023 | 0.0015502 | 0.0015502 | Momentary | FALSE | FALSE | Not_TMED_Event | 2276
AGUADILLA | 2023-05-12 15:58 | 2023-05-12 18:15 | 20 | 2:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051200227 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 137 | 2023-05-12 | 2740 | keep | 0 | May | 2023 | 0.0018662 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-12 16:00 | 2023-05-12 16:14 | 5 | 0:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR CONECTORES SECUNDARIOS | S23051200029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 14 | 2023-05-12 | 70 | keep | 0 | May | 2023 | 4.7677e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 1935 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | B23051200608 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 23220 | keep | 0 | May | 2023 | 0.015815 | 0.0013179 | Sustained | FALSE | FALSE | Not_TMED_Event | 1935
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 3 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | B23051200608 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 36 | keep | 0 | May | 2023 | 2.4519e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 61 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | B23051200608 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 732 | keep | 0 | May | 2023 | 0.00049856 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 1501 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | B23051200608 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 18012 | keep | 0 | May | 2023 | 0.012268 | 0.0010223 | Sustained | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 546 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | B23051200608 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 6552 | keep | 0 | May | 2023 | 0.0044625 | 0.00037188 | Sustained | FALSE | FALSE | Not_TMED_Event | 546
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 959 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | S23051200355 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 11508 | keep | 0 | May | 2023 | 0.007838 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 1297 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | S23051200355 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 15564 | keep | 0 | May | 2023 | 0.010601 | 0.00088338 | Sustained | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 451 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | S23051200355 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 5412 | keep | 0 | May | 2023 | 0.0036861 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 1264 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | S23051200355 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 15168 | keep | 0 | May | 2023 | 0.010331 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-05-12 16:03 | 2023-05-12 16:15 | 620 | 0:12 | S | LINEA DE TRANSMISION 38KV | PUENTE ABIERTO LINEA 9800 NO HUBO DISPARO DE LINEA. AREA OPERA RADIAL DE LINEA 9800. SE COMPLETO FASE AL CERRAR EL BKR 3440 GUAYNABO. PUENTE ABIERTO SALIENDO DE BTC. | S23051200355 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 12 | 2023-05-12 | 7440 | keep | 0 | May | 2023 | 0.0050674 | 0.00042228 | Sustained | FALSE | FALSE | Not_TMED_Event | 620
BAYAMON | 2023-05-12 16:04 | 2023-05-13 09:12 | 195 | 17:08 | P | DESGANCHE | 1X100 EN SALIDA DE CONVERTIDOR DESGANCHE | S23051200111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1028 | 2023-05-12 | 200460 | keep | 0 | May | 2023 | 0.13653 | 0.00013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 195
YAUCO | 2023-05-12 16:07 | 2023-05-12 17:56 | 15 | 1:49 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO TRANSFORMADOR Y NEUTRAL SECUNDARIO | P23051200138 | New_Event | Service Transformer Failure | Include | Include | Equipment | 109 | 2023-05-12 | 1635 | keep | 0 | May | 2023 | 0.0011136 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-12 16:09 | 2023-05-12 17:35 | 40 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | R23051200054 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2023-05-12 | 3440 | keep | 0 | May | 2023 | 0.002343 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-05-12 16:11 | 2023-05-12 17:13 | 46 | 1:02 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23051200058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-05-12 | 2852 | keep | 0 | May | 2023 | 0.0019425 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
FAJARDO | 2023-05-12 16:15 | 2023-05-12 17:30 | 40 | 1:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES LLUVIAS | R23051200059 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 75 | 2023-05-12 | 3000 | keep | 0 | May | 2023 | 0.0020433 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-12 16:21 | 2023-05-12 20:00 | 100 | 3:39 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS PARTIDAS | A23051200193 | New_Event | Primary Wire Break | Include | Include | Equipment | 219 | 2023-05-12 | 21900 | keep | 0 | May | 2023 | 0.014916 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-12 16:25 | 2023-05-12 17:07 | 1 | 0:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA S23051200046 | S23051200133 | New_Event | Cutout Failure | Include | Include | Equipment | 42 | 2023-05-12 | 42 | keep | 0 | May | 2023 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-12 16:32 | 2023-05-13 11:59 | 25 | 19:27 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23051200249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1167 | 2023-05-12 | 29175 | keep | 0 | May | 2023 | 0.019871 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-12 16:37 | 2023-05-12 21:05 | 300 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051200277 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-05-12 | 80400 | keep | 0 | May | 2023 | 0.05476 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-05-12 16:39 | 2023-05-12 16:49 | 1 | 0:10 | P | PROBLEMA DEL CLIENTE | 1 X 20 EN TRANSCLOSURE TRANSCLOSURE CON FALTA DE MANTENIMIENTO | B23051200254 | New_Event | Customer-Related Interruption | Include | Include | Public | 10 | 2023-05-12 | 10 | keep | 0 | May | 2023 | 6.811e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-12 16:41 | 2023-05-12 18:55 | 40 | 2:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A23051200229 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 134 | 2023-05-12 | 5360 | keep | 0 | May | 2023 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-12 16:49 | 2023-05-12 17:08 | 1 | 0:19 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA SECUNDARIA AVERIADA POR CAMION | P23051200147 | New_Event | Damage From Public | Include | Include | Public | 19 | 2023-05-12 | 19 | keep | 0 | May | 2023 | 1.2941e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-12 16:57 | 2023-05-13 10:25 | 15 | 17:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23051200254 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1048 | 2023-05-12 | 15720 | keep | 0 | May | 2023 | 0.010707 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-12 17:00 | 2023-05-13 11:51 | 25 | 18:51 | P | NO SE REPORTO CAUSA | 1 X 50 C/L 1 X 65 C/L | S23051200154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1131 | 2023-05-12 | 28275 | keep | 0 | May | 2023 | 0.019258 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-05-12 17:03 | 2023-05-12 20:36 | 548 | 3:33 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO C/L PARA CERRA PUENTE DE LINEA A CAJA | C23051200176 | New_Event | Primary Wire Break | Include | Include | Equipment | 213 | 2023-05-12 | 116724 | keep | 0 | May | 2023 | 0.0795 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
BAYAMON | 2023-05-12 17:05 | 2023-05-13 00:45 | 20 | 7:40 | P | ANIMAL | PRUEBA DE AEREO PROVISIONAL @ SU-22 SE RETIRO GALLINA DE PALO (IGUANA) | B23051200258 | New_Event | Animals | Include | Include | Wildlife | 460 | 2023-05-12 | 9200 | keep | 0 | May | 2023 | 0.0062661 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
UTUADO | 2023-05-12 17:05 | 2023-05-12 18:25 | 25 | 1:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | A23051200281 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 80 | 2023-05-12 | 2000 | keep | 0 | May | 2023 | 0.0013622 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-05-12 17:08 | 2023-05-12 20:56 | 81 | 3:48 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO ALAMBRE PRIMARIO Y DESGANCHE Y SECUNDARIA 2 X 65 EN CORTE DE LINEA | P23051200150 | New_Event | Primary Wire Break | Include | Include | Equipment | 228 | 2023-05-12 | 18468 | keep | 0 | May | 2023 | 0.012578 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2023-05-12 17:08 | 2023-05-12 17:09 | 4176 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 4176 | keep | 0 | May | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
CANOVANAS | 2023-05-12 17:09 | 2023-05-12 17:10 | 4981 | 0:01 | T | DESGANCHE | RECERRO LLEVA 50 % DE LA CARGA DEL 1619-03 | S23051200000 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-12 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
CANOVANAS | 2023-05-12 17:09 | 2023-05-12 17:10 | 2531 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1336-06 | S2305120000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-12 | 2531 | keep | 0 | May | 2023 | 0.0017239 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
MAYAGÃœEZ | 2023-05-12 17:16 | 2023-05-12 20:52 | 50 | 3:36 | P | DESGANCHE | 1 X 40 EN CL CRUCE DE FASE POR BAMBU | M23051200293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-05-12 | 10800 | keep | 0 | May | 2023 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-05-12 17:22 | 2023-05-12 17:23 | 1212 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051200163 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 1212 | keep | 0 | May | 2023 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
MAYAGÃœEZ | 2023-05-12 17:23 | 2023-05-13 10:33 | 8 | 17:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS RELACIONADO A EVENTO M23051200296 | M23051500175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1030 | 2023-05-12 | 8240 | keep | 0 | May | 2023 | 0.0056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-12 17:30 | 2023-05-12 18:15 | 49 | 0:45 | P | DESGANCHE | 1 X 100 EN C/L | R23051200072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2023-05-12 | 2205 | keep | 0 | May | 2023 | 0.0015018 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
MAYAGÃœEZ | 2023-05-12 17:32 | 2023-05-12 17:57 | 199 | 0:25 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | GOI MY-230512-01A SE TRANSFIERE CARGA DE INTERRUPTOR A ALIMENTADOR 6008-04 DEBIDO A BUSHING DE ENTRADA Y SALIDA AVERIADOS | M23051200328 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 25 | 2023-05-12 | 4975 | keep | 0 | May | 2023 | 0.0033884 | 0.00013554 | Sustained | FALSE | FALSE | Not_TMED_Event | 199
BARRANQUITAS | 2023-05-12 17:35 | 2023-05-12 18:36 | 540 | 1:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO C/L PARA REPAPAR POSTE PRIMARIO PARTIDO. | C23051100246 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 61 | 2023-05-12 | 32940 | keep | 0 | May | 2023 | 0.022435 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-12 17:36 | 2023-05-12 17:55 | 40 | 0:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L FUERTES LLUVIAS | R23051200059 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 19 | 2023-05-12 | 760 | keep | 0 | May | 2023 | 0.00051763 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-12 17:37 | 2023-05-12 20:02 | 181 | 2:25 | P | DESGANCHE | 1 X 65 Y 2 X 30 EN C/L | R23051200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2023-05-12 | 26245 | keep | 0 | May | 2023 | 0.017875 | 0.00012328 | Sustained | FALSE | FALSE | Not_TMED_Event | 181
CANOVANAS | 2023-05-12 17:38 | 2023-05-12 17:39 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23051200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 3046 | keep | 0 | May | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-05-12 17:38 | 2023-05-12 17:39 | 308 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1646-03 | R23051200079 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-12 | 308 | keep | 0 | May | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-05-12 17:38 | 2023-05-12 17:39 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1646-03 | R23051200079 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-12 | 61 | keep | 0 | May | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
BAYAMON | 2023-05-12 17:39 | 2023-05-12 19:53 | 3941 | 2:14 | T | DESGANCHE | SE DESGANCHO DE PISO A BARETA Y SE CERRO POR CONTROL | B2305120000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-05-12 | 528094 | keep | 0 | May | 2023 | 0.35968 | 0.0026842 | Sustained | FALSE | FALSE | Not_TMED_Event | 3941
BARRANQUITAS | 2023-05-12 17:39 | 2023-05-12 17:40 | 3463 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 3463 | keep | 0 | May | 2023 | 0.0023586 | 0.0023586 | Momentary | FALSE | FALSE | Not_TMED_Event | 3463
VEGA BAJA | 2023-05-12 17:48 | 2023-05-13 09:50 | 80 | 16:02 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051200275 | New_Event | Vegetation Contact | Include | Include | Vegetation | 962 | 2023-05-12 | 76960 | keep | 0 | May | 2023 | 0.052417 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-12 17:49 | 2023-05-12 18:16 | 12 | 0:27 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23051200277 | New_Event | Secondary Wire Break | Include | Include | Equipment | 27 | 2023-05-12 | 324 | keep | 0 | May | 2023 | 0.00022067 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-12 17:51 | 2023-05-12 18:03 | 10211 | 0:12 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2023-05-12 | 122532 | keep | 0 | May | 2023 | 0.083456 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
VEGA BAJA | 2023-05-12 17:52 | 2023-05-12 20:12 | 1310 | 2:20 | T | CONDUCTOR ROTO O ABIERTO | SE PATRULLO ALIMENTADOR Y NO SE REPORTO AVERIA | B23051200291 | New_Event | Primary Wire Break | Include | Include | Equipment | 140 | 2023-05-12 | 183400 | keep | 0 | May | 2023 | 0.12491 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
VEGA BAJA | 2023-05-12 17:56 | 2023-05-13 08:08 | 10 | 14:12 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051200279 | New_Event | Vegetation Contact | Include | Include | Vegetation | 852 | 2023-05-12 | 8520 | keep | 0 | May | 2023 | 0.0058029 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-12 18:02 | 2023-05-12 18:04 | 4154 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO SOLO | R23051200089 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-12 | 8308 | keep | 0 | May | 2023 | 0.0056585 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
CANOVANAS | 2023-05-12 18:04 | 2023-05-12 23:02 | 300 | 4:58 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN TRONCAL | R23051200591 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 298 | 2023-05-12 | 89400 | keep | 0 | May | 2023 | 0.06089 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CANOVANAS | 2023-05-12 18:21 | 2023-05-12 21:12 | 2000 | 2:51 | P | CONDUCTOR ROTO O ABIERTO | REPARO 2 BAJANTES DE LINEA A CAJA Y CERRO | R23051200104 | New_Event | Primary Wire Break | Include | Include | Equipment | 171 | 2023-05-12 | 342000 | keep | 0 | May | 2023 | 0.23293 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
VEGA BAJA | 2023-05-12 18:22 | 2023-05-12 18:23 | 4702 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 4702 | keep | 0 | May | 2023 | 0.0032025 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CANOVANAS | 2023-05-12 18:23 | 2023-05-12 18:25 | 2531 | 0:02 | P | DESGANCHE | DISPARO DE INTERRUPTOR 50% DE LA CARGA X 1336-06 CERRADO X CONTROL | R2305120000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-05-12 | 5062 | keep | 0 | May | 2023 | 0.0034477 | 0.0017239 | Momentary | FALSE | FALSE | Not_TMED_Event | 2531
HUMACAO | 2023-05-12 18:24 | 2023-05-12 18:25 | 3896 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 3896 | keep | 0 | May | 2023 | 0.0026535 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
SAN JUAN | 2023-05-12 18:25 | 2023-05-12 19:14 | 4133 | 0:49 | T | DESGANCHE | RECERRO 3 VECES QUEDO ABIERTO SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 95% EN SERVICIO | S23051200264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2023-05-12 | 202517 | keep | 0 | May | 2023 | 0.13793 | 0.002815 | Sustained | FALSE | FALSE | Not_TMED_Event | 4133
CANOVANAS | 2023-05-12 18:25 | 2023-05-12 21:12 | 4981 | 2:47 | T | DESGANCHE | RECERRO 3 VECES QUEDO ABIERTO SE HIZO DESGANCHE CON VARETA DE PISO Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO LLEVANDO CARGA DEL 50% DEL 1619-3 | S23051200000 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-05-12 | 831827 | keep | 0 | May | 2023 | 0.56655 | 0.0033925 | Sustained | FALSE | FALSE | Not_TMED_Event | 4981
CANOVANAS | 2023-05-12 18:25 | 2023-05-12 21:12 | 2531 | 2:47 | P | ALIMENTADOR AMARRADO | 50% DE LA CARGA POR EL 1336-06 | R23051200181 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 167 | 2023-05-12 | 422677 | keep | 0 | May | 2023 | 0.28788 | 0.0017239 | Sustained | FALSE | FALSE | Not_TMED_Event | 2531
HUMACAO | 2023-05-12 18:25 | 2023-05-12 19:32 | 1089 | 1:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051200348 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 67 | 2023-05-12 | 72963 | keep | 0 | May | 2023 | 0.049695 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2023-05-12 18:25 | 2023-05-12 19:32 | 3896 | 1:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051200348 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 67 | 2023-05-12 | 261032 | keep | 0 | May | 2023 | 0.17779 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2023-05-12 18:25 | 2023-05-12 19:32 | 1467 | 1:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051200348 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 67 | 2023-05-12 | 98289 | keep | 0 | May | 2023 | 0.066944 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
UTUADO | 2023-05-12 18:26 | 2023-05-12 19:15 | 30 | 0:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CONVERTIDOR POR LLUVIA | A23051200285 | Additional_clients | Bad Weather (Rain & Wind) | Include | Include | Weather | 49 | 2023-05-12 | 1470 | keep | 0 | May | 2023 | 0.0010012 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-12 18:30 | 2023-05-12 21:53 | 120 | 3:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A23051200286 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 203 | 2023-05-12 | 24360 | keep | 0 | May | 2023 | 0.016591 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-05-12 18:33 | 2023-05-12 18:35 | 1746 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-12 | 3492 | keep | 0 | May | 2023 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
SAN JUAN | 2023-05-12 18:34 | 2023-05-12 18:35 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051200000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 4291 | keep | 0 | May | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BAYAMON | 2023-05-12 18:39 | 2023-05-12 18:40 | 1362 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B2305120000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-12 | 1362 | keep | 0 | May | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
BAYAMON | 2023-05-12 18:40 | 2023-05-13 00:35 | 164 | 5:55 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L SE CERRO PUENTE ABIERTO | B23051200565 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 355 | 2023-05-12 | 58220 | keep | 0 | May | 2023 | 0.039653 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2023-05-12 18:42 | 2023-05-12 18:44 | 2435 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23051200235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-12 | 4870 | keep | 0 | May | 2023 | 0.0033169 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-05-12 18:42 | 2023-05-12 18:44 | 726 | 0:02 | T | DESGANCHE | DISPARO SE PROBO QUEDO EN SERVICIO | S23051200235 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-05-12 | 1452 | keep | 0 | May | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
VEGA BAJA | 2023-05-12 18:42 | 2023-05-12 18:44 | 3000 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B23051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 6000 | keep | 0 | May | 2023 | 0.0040866 | 0.0020433 | Momentary | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2023-05-12 18:42 | 2023-05-12 18:44 | 908 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B23051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 1816 | keep | 0 | May | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2023-05-12 18:42 | 2023-05-12 18:44 | 3332 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2200 | B23051200000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 6664 | keep | 0 | May | 2023 | 0.0045388 | 0.0022694 | Momentary | FALSE | FALSE | Not_TMED_Event | 3332
VEGA BAJA | 2023-05-12 18:42 | 2023-05-12 18:44 | 2610 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B23051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 5220 | keep | 0 | May | 2023 | 0.0035553 | 0.0017777 | Momentary | FALSE | FALSE | Not_TMED_Event | 2610
VEGA BAJA | 2023-05-12 18:42 | 2023-05-12 18:44 | 3076 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | B23051600000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 6152 | keep | 0 | May | 2023 | 0.0041901 | 0.002095 | Momentary | FALSE | FALSE | Not_TMED_Event | 3076
VEGA BAJA | 2023-05-12 18:47 | 2023-05-12 23:16 | 200 | 4:29 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 1 X 65 EN C/L SE REPORTA RAYOS EN EL AREA | B23051200388 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 269 | 2023-05-12 | 53800 | keep | 0 | May | 2023 | 0.036643 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-12 18:53 | 2023-05-12 18:54 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 3438 | keep | 0 | May | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-05-12 18:54 | 2023-05-12 18:56 | 1310 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | S2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-12 | 2620 | keep | 0 | May | 2023 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
YAUCO | 2023-05-12 18:55 | 2023-05-13 00:05 | 125 | 5:10 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REPARO LINEA PRIMARIA ROTA RELACIONADO EVENTO M230512000333 | M23051200453 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-05-12 | 38750 | keep | 0 | May | 2023 | 0.026392 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-05-12 18:56 | 2023-05-12 18:59 | 1058 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO 20% POR 1424-08 | S23051200257 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-12 | 3174 | keep | 0 | May | 2023 | 0.0021618 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-05-12 18:56 | 2023-05-12 18:59 | 1000 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO 80% POR 1424-08 | S23051200257 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-12 | 3000 | keep | 0 | May | 2023 | 0.0020433 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-05-12 18:56 | 2023-05-12 18:59 | 278 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO SU CARGA POR 1424-08 | S23051200257 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-12 | 834 | keep | 0 | May | 2023 | 0.00056803 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-12 18:56 | 2023-05-12 18:59 | 94 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO SU CARGA POR 1424-08 | S23051200257 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-12 | 282 | keep | 0 | May | 2023 | 0.00019207 | 6.4023e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 94
SAN JUAN | 2023-05-12 18:56 | 2023-05-12 18:59 | 1295 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO SU CARGA POR 1424-08 | S23051200257 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-12 | 3885 | keep | 0 | May | 2023 | 0.0026461 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-05-12 18:56 | 2023-05-12 18:59 | 9 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 100% 1348-07 LLEVA 80% 1348-06 20% DEL 1336-08 LLEVA 1401-10 LLEVA 70% 1401-08 | S23051200257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-12 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
UTUADO | 2023-05-12 18:59 | 2023-05-12 20:41 | 10 | 1:42 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | A23051200287 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 102 | 2023-05-12 | 1020 | keep | 0 | May | 2023 | 0.00069472 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-12 19:05 | 2023-05-12 19:06 | 1210 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECERRO | B2305120000X | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-05-12 | 1210 | keep | 0 | May | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2023-05-12 19:06 | 2023-05-13 02:56 | 128 | 7:50 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 65 EN C/L SE SECCIONALIZO POSTE EN FUEGO | B23051200569 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 470 | 2023-05-12 | 60160 | keep | 0 | May | 2023 | 0.040975 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
SAN JUAN | 2023-05-12 19:08 | 2023-05-12 20:49 | 726 | 1:41 | T | DESGANCHE | DISPARO ALIMENTADOR SE ABRIO MACHETE PARA SECCIONALIZAR Y SE CERRO INTERRUPTOR 10% EN SERVICIO | S23051200239 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 101 | 2023-05-12 | 73326 | keep | 0 | May | 2023 | 0.049942 | 0.00049448 | Sustained | FALSE | FALSE | Not_TMED_Event | 726
AGUADILLA | 2023-05-12 19:08 | 2023-05-12 21:18 | 1827 | 2:10 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABREN MACHETES PARA SECCIONALIZAR LINEA PRIMARIA SAFADA DE AISLADOR Y SE COLOCA INTERRUPTOR EN SERVICIO | M23051200342 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 130 | 2023-05-12 | 237510 | keep | 0 | May | 2023 | 0.16177 | 0.0012444 | Sustained | FALSE | FALSE | Not_TMED_Event | 1827
SAN JUAN | 2023-05-12 19:12 | 2023-05-12 19:13 | 601 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECERRO MAL TIEMPO LLEVA 1437-02 | S23051200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-12 | 601 | keep | 0 | May | 2023 | 0.00040934 | 0.00040934 | Momentary | FALSE | FALSE | Not_TMED_Event | 601
SAN JUAN | 2023-05-12 19:12 | 2023-05-12 19:13 | 640 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO MAL TIEMPO SU CARGA POR 1437-01 | S23051200000 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-12 | 640 | keep | 0 | May | 2023 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2023-05-12 19:14 | 2023-05-12 19:52 | 206 | 0:38 | P | DESGANCHE | SE RETIRO BAMBUA CON VARETA DE PISO Y SE CERRO MACHETE 100% EN SERVICIO | S23051200264 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 38 | 2023-05-12 | 7828 | keep | 0 | May | 2023 | 0.0053316 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-12 19:26 | 2023-05-13 09:33 | 85 | 14:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L REMPLAZO CAJA QUEMADA | C23051200340 | New_Event | Cutout Failure | Include | Include | Equipment | 847 | 2023-05-12 | 71995 | keep | 0 | May | 2023 | 0.049035 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
SAN JUAN | 2023-05-12 19:29 | 2023-05-12 20:19 | 743 | 0:50 | P | DESGANCHE | SE RETIRO BAMBUAS CON VARETA DE PISO Y SE PROBO QUEDO EN SERVICIO | S23051200292 | New_Event | Vegetation Contact | Include | Include | Vegetation | 50 | 2023-05-12 | 37150 | keep | 0 | May | 2023 | 0.025303 | 0.00050605 | Sustained | FALSE | FALSE | Not_TMED_Event | 743
YAUCO | 2023-05-12 19:31 | 2023-05-13 07:26 | 150 | 11:55 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P23051200199 | New_Event | Vegetation Contact | Include | Include | Vegetation | 715 | 2023-05-12 | 107250 | keep | 0 | May | 2023 | 0.073047 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-05-12 19:38 | 2023-05-12 19:41 | 1615 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO SE PROBO QUEDO EN SERVICIO | S23051200000 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2023-05-12 | 4845 | keep | 0 | May | 2023 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
VEGA BAJA | 2023-05-12 19:45 | 2023-05-12 19:46 | 2216 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 2216 | keep | 0 | May | 2023 | 0.0015093 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
SAN JUAN | 2023-05-12 19:49 | 2023-05-13 17:20 | 56 | 21:31 | P | DESGANCHE | 1 X 100 EN C/L SE RETIRO BAMBUAS | S23051200305 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1291 | 2023-05-12 | 72296 | keep | 0 | May | 2023 | 0.04924 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
MAYAGÃœEZ | 2023-05-12 20:01 | 2023-05-12 21:57 | 400 | 1:56 | P | MAL TIEMPO/RAYOS | 3 X 200 EN CL DESCARGA ELECTRICA | M23051200364 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 116 | 2023-05-12 | 46400 | keep | 0 | May | 2023 | 0.031603 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
BAYAMON | 2023-05-12 20:02 | 2023-05-13 12:19 | 14 | 16:17 | P | DESGANCHE | 2X40 EN C/L DESGANCHE | S23051200318 | New_Event | Vegetation Contact | Include | Include | Vegetation | 977 | 2023-05-12 | 13678 | keep | 0 | May | 2023 | 0.009316 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-05-12 20:12 | 2023-05-12 20:29 | 1310 | 0:17 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR POR CONTROL POR PUENTE ABIERTO EN MACHETE SE ABRIO MACHETE Y SE CERRO BKR 66% EN SERVICIO | B23051200291 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 17 | 2023-05-12 | 22270 | keep | 0 | May | 2023 | 0.015168 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-12 20:29 | 2023-05-12 23:18 | 436 | 2:49 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO PUENTE ABIERTO | B23051200291 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 169 | 2023-05-12 | 73684 | keep | 0 | May | 2023 | 0.050186 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-12 20:33 | 2023-05-13 13:52 | 41 | 17:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L POR LLUVIA | B23051200587 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1039 | 2023-05-12 | 42599 | keep | 0 | May | 2023 | 0.029014 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
SAN JUAN | 2023-05-12 20:40 | 2023-05-13 19:02 | 36 | 22:22 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23051200354 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1342 | 2023-05-12 | 48312 | keep | 0 | May | 2023 | 0.032905 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-12 20:49 | 2023-05-12 22:14 | 653 | 1:25 | P | DESGANCHE | SE REALIZARON OPERACIONES ENTRO 40% ADICIONAL PARA UN 50% EN SERVICIO | S23051200239 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-05-12 | 55505 | keep | 0 | May | 2023 | 0.037804 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-05-12 20:49 | 2023-05-13 09:25 | 40 | 12:36 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051200298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 756 | 2023-05-12 | 30240 | keep | 0 | May | 2023 | 0.020596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-12 21:11 | 2023-05-13 06:41 | 40 | 9:30 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L SE RETIRO PARARRAYO CRUZADO | S23051200382 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 570 | 2023-05-12 | 22800 | keep | 0 | May | 2023 | 0.015529 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-05-12 21:12 | 2023-05-12 22:40 | 20 | 1:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CONVERTIDOR LLUVIA Y VIENTO | A23051200301 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 88 | 2023-05-12 | 1760 | keep | 0 | May | 2023 | 0.0011987 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-12 21:18 | 2023-05-12 23:04 | 500 | 1:46 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR ROTO Y SE CERRO LOS MACHETES QUE SE HABIAN ABIERTO PARA SECCIONALIZAR LA AVERIA | M23051200436 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 106 | 2023-05-12 | 53000 | keep | 0 | May | 2023 | 0.036098 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-12 21:24 | 2023-05-13 08:05 | 12 | 10:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE LINEA A CAJA | R23051200490 | New_Event | Primary Wire Break | Include | Include | Equipment | 641 | 2023-05-12 | 7692 | keep | 0 | May | 2023 | 0.005239 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-12 21:25 | 2023-05-12 21:26 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERE DE BKR | C23051200363 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 853 | keep | 0 | May | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
VEGA BAJA | 2023-05-12 21:28 | 2023-05-12 23:41 | 3000 | 2:13 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION PARA CERRAR PUENTE ABIERTO EN LINEA 2200 PUENTE ABIERTO EN ACB #1 SAN DEMETRIO | B23051200726 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2023-05-12 | 399000 | keep | 0 | May | 2023 | 0.27176 | 0.0020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 3000
VEGA BAJA | 2023-05-12 21:28 | 2023-05-12 23:41 | 908 | 2:13 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION PARA CERRAR PUENTE ABIERTO EN LINEA 2200 PUENTE ABIERTO EN ACB #1 SAN DEMETRIO | B23051200726 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2023-05-12 | 120764 | keep | 0 | May | 2023 | 0.082252 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
VEGA BAJA | 2023-05-12 21:28 | 2023-05-12 23:41 | 3332 | 2:13 | S | LINEA DE TRANSMISION 38KV | SE RETIRO LA CARGA DE LA SUBESTACION PARA CERRAR PUENTE ABIERTO EN LINEA 2200 PUENTE ABIERTO EN ACB #1 SAN DEMETRIO | B23051200726 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 133 | 2023-05-12 | 443156 | keep | 0 | May | 2023 | 0.30183 | 0.0022694 | Sustained | FALSE | FALSE | Not_TMED_Event | 3332
CANOVANAS | 2023-05-12 21:29 | 2023-05-13 10:54 | 7 | 13:25 | P | TRANSFORMADOR AVERIADO | SJ-230513-50 SE REEMPLAZO PM 7 DE 50 KVA AVERIADO | R23051200042 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 805 | 2023-05-12 | 5635 | keep | 0 | May | 2023 | 0.003838 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-12 21:37 | 2023-05-12 21:38 | 1076 | 0:01 | T | DESGANCHE | DISPARO INTERRUPTOR SE LE DIO PRUEBA QUEDO EN SERVICIO | P23051200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-12 | 1076 | keep | 0 | May | 2023 | 0.00073286 | 0.00073286 | Momentary | FALSE | FALSE | Not_TMED_Event | 1076
PONCE | 2023-05-12 21:38 | 2023-05-13 07:54 | 200 | 10:16 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA POR DESGANCHE | P23051200218 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 616 | 2023-05-12 | 123200 | keep | 0 | May | 2023 | 0.083911 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-12 21:45 | 2023-05-12 22:08 | 286 | 0:23 | P | ARBOL SOBRE LINEA | EN AVERIA DE PUENTE ABIERTO A CAUSA DE ARBOL EN BKR 1704-04 ESTE SE AVERIO Y NO OPERO FUNDIENDO DOS FUSIBLES LA ALTA DEL XMR 50% TRANSFERIDO AL 1704-05 | B23051200196 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 23 | 2023-05-12 | 6578 | keep | 0 | May | 2023 | 0.0044802 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-12 22:07 | 2023-05-13 01:20 | 80 | 3:13 | P | ANIMAL | 2 X 65 EN CORTES DE LINEA CRUCE CON AVE | C23051200385 | New_Event | Animals | Include | Include | Wildlife | 193 | 2023-05-12 | 15440 | keep | 0 | May | 2023 | 0.010516 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-12 22:12 | 2023-05-13 16:34 | 4 | 18:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X25 EN C/L POR LLUVIA | S23051200434 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1102 | 2023-05-12 | 4408 | keep | 0 | May | 2023 | 0.0030023 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-05-12 22:14 | 2023-05-12 22:24 | 363 | 0:10 | P | DESGANCHE | SE REALIZARON OPERACIONES Y ENTRO 30% ADICIONAL PARA UN 80% EN SERVICIO | S23051200239 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 10 | 2023-05-12 | 3630 | keep | 0 | May | 2023 | 0.0024724 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-12 22:19 | 2023-05-13 11:04 | 221 | 12:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3X80 DEL SU-12 @ RISER, 2X50 DEL SU-J @ RISER Y SE REMPLAZO CAJA PRIMARIA EN RISER | B23051200820 | New_Event | Cutout Failure | Include | Include | Equipment | 765 | 2023-05-12 | 169065 | keep | 0 | May | 2023 | 0.11515 | 0.00015052 | Sustained | FALSE | FALSE | Not_TMED_Event | 221
FAJARDO | 2023-05-12 22:19 | 2023-05-13 01:00 | 110 | 2:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIAS | R23051200545 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 161 | 2023-05-12 | 17710 | keep | 0 | May | 2023 | 0.012062 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
SAN JUAN | 2023-05-12 22:24 | 2023-05-13 08:32 | 145 | 10:08 | P | DESGANCHE | HACIENDO PRUEBAS EN SU ALIMENTADOR DISPARO, SE DEJO TAGGED | S23051200239 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 608 | 2023-05-12 | 88160 | keep | 0 | May | 2023 | 0.060045 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-12 22:30 | 2023-05-13 07:50 | 30 | 9:20 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23051200310 | New_Event | Animals | Include | Include | Wildlife | 560 | 2023-05-12 | 16800 | keep | 0 | May | 2023 | 0.011442 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-05-12 22:38 | 2023-05-13 11:08 | 51 | 12:30 | P | DESGANCHE | SE REALIZO DESGANCHE Y 1 X65 EN C/L | C23051200404 | New_Event | Vegetation Contact | Include | Include | Vegetation | 750 | 2023-05-12 | 38250 | keep | 0 | May | 2023 | 0.026052 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BAYAMON | 2023-05-12 22:41 | 2023-05-12 22:42 | 308 | 0:01 | T | DESGANCHE | RECERRO | B2302120000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-12 | 308 | keep | 0 | May | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
BAYAMON | 2023-05-12 22:42 | 2023-05-13 18:47 | 20 | 20:05 | P | ANIMAL | 1X100 EN C/L CRUCE POR AVE | B23051200850 | New_Event | Animals | Include | Include | Wildlife | 1205 | 2023-05-12 | 24100 | keep | 0 | May | 2023 | 0.016414 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-12 22:42 | 2023-05-13 00:04 | 200 | 1:22 | P | DESGANCHE | 1 X 80 EN C/L SE DESGANCHO | B23051200514 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-05-12 | 16400 | keep | 0 | May | 2023 | 0.01117 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-12 22:44 | 2023-05-13 04:13 | 71 | 5:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA | B23051200853 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 329 | 2023-05-12 | 23359 | keep | 0 | May | 2023 | 0.01591 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
HUMACAO | 2023-05-12 22:47 | 2023-05-13 10:36 | 100 | 11:49 | P | DESGANCHE | 1 X 80 Y 1 X 65 EN C/LS DESGANCHO Y LEVANTO CONDUCTOR | C23051200409 | New_Event | Vegetation Contact | Include | Include | Vegetation | 709 | 2023-05-12 | 70900 | keep | 0 | May | 2023 | 0.04829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-05-12 23:07 | 2023-05-12 23:09 | 3701 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C23051200415 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 7402 | keep | 0 | May | 2023 | 0.0050415 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2023-05-12 23:07 | 2023-05-12 23:09 | 989 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C23051200415 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 1978 | keep | 0 | May | 2023 | 0.0013472 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2023-05-12 23:07 | 2023-05-12 23:09 | 1467 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 5400 | C23051200415 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 2934 | keep | 0 | May | 2023 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2023-05-12 23:08 | 2023-05-13 04:55 | 137 | 5:47 | P | DESGANCHE | 1 X 80 EN PROVISIONAL AEREO SE DESGANCHO | B23051200879 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2023-05-12 | 47539 | keep | 0 | May | 2023 | 0.032379 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BAYAMON | 2023-05-12 23:12 | 2023-05-12 23:13 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1912-07 | S2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-12 | 57 | keep | 0 | May | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
VEGA BAJA | 2023-05-12 23:13 | 2023-05-13 15:50 | 10 | 16:37 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE TRANSFORMADOR AVERIADO DE 50 KVA POR 50 KVA | A23051200312 | New_Event | Service Transformer Failure | Include | Include | Equipment | 997 | 2023-05-12 | 9970 | keep | 0 | May | 2023 | 0.0067905 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-12 23:14 | 2023-05-12 23:16 | 1541 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23051200313 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 3082 | keep | 0 | May | 2023 | 0.0020991 | 0.0010496 | Momentary | FALSE | FALSE | Not_TMED_Event | 1541
AGUADILLA | 2023-05-12 23:14 | 2023-05-12 23:16 | 307 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23051200313 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 614 | keep | 0 | May | 2023 | 0.00041819 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
AGUADILLA | 2023-05-12 23:14 | 2023-05-12 23:16 | 1277 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23051200313 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 2554 | keep | 0 | May | 2023 | 0.0017395 | 0.00086976 | Momentary | FALSE | FALSE | Not_TMED_Event | 1277
AGUADILLA | 2023-05-12 23:14 | 2023-05-12 23:16 | 1644 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23051200313 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 3288 | keep | 0 | May | 2023 | 0.0022394 | 0.0011197 | Momentary | FALSE | FALSE | Not_TMED_Event | 1644
AGUADILLA | 2023-05-12 23:14 | 2023-05-12 23:16 | 1831 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23051200313 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-12 | 3662 | keep | 0 | May | 2023 | 0.0024942 | 0.0012471 | Momentary | FALSE | FALSE | Not_TMED_Event | 1831
BAYAMON | 2023-05-12 23:15 | 2023-05-13 09:44 | 34 | 10:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X30 EN C/L POR LLUVIA | B23051200884 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 629 | 2023-05-12 | 21386 | keep | 0 | May | 2023 | 0.014566 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2023-05-12 23:16 | 2023-05-12 23:18 | 936 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 20% X 1424-08 Y LLEVA 15% 1336-07 SE CERRO POR SCADA | S2305120000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-12 | 1872 | keep | 0 | May | 2023 | 0.001275 | 0.00063751 | Momentary | FALSE | FALSE | Not_TMED_Event | 936
SAN JUAN | 2023-05-12 23:16 | 2023-05-12 23:18 | 4232 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 20% X 1424-08 Y LLEVA 15% 1336-07 SE CERRO POR SCADA | S2305120000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-12 | 8464 | keep | 0 | May | 2023 | 0.0057648 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
VEGA BAJA | 2023-05-12 23:18 | 2023-05-13 00:32 | 1310 | 1:14 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL 60% EN SERVICIO | B23051200291 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 74 | 2023-05-12 | 96940 | keep | 0 | May | 2023 | 0.066025 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-12 23:19 | 2023-05-13 07:06 | 937 | 7:47 | P | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL MALTIEMPO VIENTO 20% 1424-08 15% POR EL 1336-10 | S23051200591 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 467 | 2023-05-12 | 437579 | keep | 0 | May | 2023 | 0.29803 | 0.00063819 | Sustained | FALSE | FALSE | Not_TMED_Event | 937
SAN JUAN | 2023-05-12 23:19 | 2023-05-13 07:06 | 4232 | 7:47 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO CERRADO POR CONTROL MALTIEMPO VIENTO 20% 1424-08 LLEVA 15% DEL 1336-07 | S23051200591 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 467 | 2023-05-12 | 1976344 | keep | 0 | May | 2023 | 1.3461 | 0.0028824 | Sustained | FALSE | FALSE | Not_TMED_Event | 4232
CAGUAS | 2023-05-12 23:21 | 2023-05-13 14:05 | 51 | 14:44 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C23051200418 | New_Event | Vegetation Contact | Include | Include | Vegetation | 884 | 2023-05-12 | 45084 | keep | 0 | May | 2023 | 0.030707 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
BARRANQUITAS | 2023-05-12 23:25 | 2023-05-13 12:10 | 32 | 12:45 | P | DESGANCHE | 1 X 30 EN C/L | C23051200420 | New_Event | Vegetation Contact | Include | Include | Vegetation | 765 | 2023-05-12 | 24480 | keep | 0 | May | 2023 | 0.016673 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BARRANQUITAS | 2023-05-12 23:39 | 2023-05-12 23:40 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LLINEA 4800 | C23051200425 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 2725 | keep | 0 | May | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-05-12 23:39 | 2023-05-12 23:40 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LLINEA 4800 | C23051200425 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-05-12 23:39 | 2023-05-12 23:40 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LLINEA 4800 | C23051200425 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 1437 | keep | 0 | May | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-05-12 23:39 | 2023-05-12 23:40 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LLINEA 4800 | C23051200426 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 2565 | keep | 0 | May | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-05-12 23:39 | 2023-05-12 23:40 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LLINEA 4800 | C23051200426 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 3565 | keep | 0 | May | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
GUAYAMA | 2023-05-12 23:39 | 2023-05-12 23:40 | 2751 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23051200245 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 2751 | keep | 0 | May | 2023 | 0.0018737 | 0.0018737 | Momentary | FALSE | FALSE | Not_TMED_Event | 2751
GUAYAMA | 2023-05-12 23:39 | 2023-05-12 23:40 | 576 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23051200245 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 576 | keep | 0 | May | 2023 | 0.00039231 | 0.00039231 | Momentary | FALSE | FALSE | Not_TMED_Event | 576
GUAYAMA | 2023-05-12 23:39 | 2023-05-12 23:40 | 2584 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23051200245 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 2584 | keep | 0 | May | 2023 | 0.00176 | 0.00176 | Momentary | FALSE | FALSE | Not_TMED_Event | 2584
GUAYAMA | 2023-05-12 23:39 | 2023-05-12 23:40 | 1606 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23051200245 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
GUAYAMA | 2023-05-12 23:39 | 2023-05-12 23:40 | 29 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23051200245 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 29 | keep | 0 | May | 2023 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
GUAYAMA | 2023-05-12 23:39 | 2023-05-12 23:40 | 4035 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23051200246 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 4035 | keep | 0 | May | 2023 | 0.0027482 | 0.0027482 | Momentary | FALSE | FALSE | Not_TMED_Event | 4035
GUAYAMA | 2023-05-12 23:39 | 2023-05-12 23:40 | 3718 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 4800 | P23051200246 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-12 | 3718 | keep | 0 | May | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
CAGUAS | 2023-05-12 23:45 | 2023-05-13 03:53 | 250 | 4:08 | P | DESGANCHE | 2 X 65 EN CORTES DE LINEA | C23051200427 | New_Event | Vegetation Contact | Include | Include | Vegetation | 248 | 2023-05-12 | 62000 | keep | 0 | May | 2023 | 0.042228 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BARRANQUITAS | 2023-05-13 | 2023-05-13 00:01 | 1017 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1017 | keep | 0 | May | 2023 | 0.00069267 | 0.00069267 | Momentary | FALSE | FALSE | Not_TMED_Event | 1017
BAYAMON | 2023-05-13 00:01 | 2023-05-13 12:33 | 472 | 12:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIAS | S23051300003 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 752 | 2023-05-13 | 354944 | keep | 0 | May | 2023 | 0.24175 | 0.00032148 | Sustained | FALSE | FALSE | Not_TMED_Event | 472
SAN JUAN | 2023-05-13 00:21 | 2023-05-13 06:28 | 316 | 6:07 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SJ-230513-01 SUBESTACION EN LOCKOUT SE SECCIONALIZO 0060 Y SE TRANSFIRIO LA CARGA AL 1116-00 POR TIE BUS LLEVA 25% 1119-04 LLEVA 25 DEL 1119-02 | S23051300118 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 367 | 2023-05-13 | 115972 | keep | 0 | May | 2023 | 0.078988 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2023-05-13 00:21 | 2023-05-13 04:54 | 1356 | 4:33 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | SUBESTACION SE FUE LOCKOUT BKR 1117-11 SE TRANSFIRIO LA CARGA AL 1116-03 100% EN SERVICIO SE REALIZARON OPERACIONES CON SWF SJ-230513-01 | S23051300118 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 273 | 2023-05-13 | 370188 | keep | 0 | May | 2023 | 0.25213 | 0.00092357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1356
SAN JUAN | 2023-05-13 00:21 | 2023-05-13 06:28 | 215 | 6:07 | P | ALIMENTADOR AMARRADO | SJ-230513-01 SUBESTACION EN LOCKOUT SE SECCIONALIZO 0060 Y SE TRANSFIRIO LA CARGA AL 1116-00 POR TIE BUS 25 % POR 1117-09 | S23051300118 | New_Event | Feeder Load Transferred | Include | Include | Other | 367 | 2023-05-13 | 78905 | keep | 0 | May | 2023 | 0.053742 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-05-13 00:21 | 2023-05-13 06:28 | 680 | 6:07 | P | ALIMENTADOR AMARRADO | SJ-230513-01 SUBESTACION EN LOCKOUT SE SECCIONALIZO 0060 Y SE TRANSFIRIO LA CARGA AL 1116-00 POR TIE BUS 25 % POR 1117-09 | S23051300118 | New_Event | Feeder Load Transferred | Include | Include | Other | 367 | 2023-05-13 | 249560 | keep | 0 | May | 2023 | 0.16997 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
BAYAMON | 2023-05-13 00:32 | 2023-05-13 01:58 | 524 | 1:26 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN MACHETE ENTRO EN RESTANTE 40% | B23051200291 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 86 | 2023-05-13 | 45064 | keep | 0 | May | 2023 | 0.030693 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-13 00:45 | 2023-05-13 00:46 | 723 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1912-08 LLEVA 1711-02 LLEVA 1711-05 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 723 | keep | 0 | May | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-05-13 00:45 | 2023-05-13 00:46 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE 1912-08 LLEVA 1711-02 LLEVA 1711-05 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 1976 | keep | 0 | May | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-05-13 00:45 | 2023-05-13 00:46 | 577 | 0:01 | T | ANIMAL | RECIERRE 1912-08 LLEVA 1711-02 LLEVA 1711-05 | S2305130000X | Additional_clients | Animals | Include | Include | Wildlife | 1 | 2023-05-13 | 577 | keep | 0 | May | 2023 | 0.00039299 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-13 00:45 | 2023-05-13 00:46 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23051300004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1945 | keep | 0 | May | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
BAYAMON | 2023-05-13 00:46 | 2023-05-13 17:09 | 20 | 16:23 | P | ANIMAL | PRUEBA DE AEREO PROVISIONAL @ SU-22 SE RETIRO GALLINA DE PALO (IGUANA) | B23051200258 | 1st_after_momentary | Animals | Include | Include | Wildlife | 983 | 2023-05-13 | 19660 | keep | 0 | May | 2023 | 0.01339 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-13 00:51 | 2023-05-13 00:52 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
BAYAMON | 2023-05-13 01:10 | 2023-05-13 09:35 | 280 | 8:25 | P | DESGANCHE | 1X50 EN C/L Y 1X40 EN OTRO C/L DESGANCHE | B23051300032 | New_Event | Vegetation Contact | Include | Include | Vegetation | 505 | 2023-05-13 | 141400 | keep | 0 | May | 2023 | 0.096307 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
CAGUAS | 2023-05-13 01:24 | 2023-05-13 01:26 | 1116 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-13 | 2232 | keep | 0 | May | 2023 | 0.0015202 | 0.0007601 | Momentary | FALSE | FALSE | Not_TMED_Event | 1116
CAGUAS | 2023-05-13 01:30 | 2023-05-13 16:48 | 131 | 15:18 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN C/LS | C23051300029 | New_Event | Vegetation Contact | Include | Include | Vegetation | 918 | 2023-05-13 | 120258 | keep | 0 | May | 2023 | 0.081907 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2023-05-13 02:03 | 2023-05-13 02:04 | 841 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE PARTE DE LA CARGA POR EL 3103-02 | C23051300032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 841 | keep | 0 | May | 2023 | 0.0005728 | 0.0005728 | Momentary | FALSE | FALSE | Not_TMED_Event | 841
CAGUAS | 2023-05-13 02:28 | 2023-05-13 02:30 | 817 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-13 | 1634 | keep | 0 | May | 2023 | 0.0011129 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
VEGA BAJA | 2023-05-13 02:44 | 2023-05-13 10:12 | 100 | 7:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X40 EN C/L POR LLUVIAS | B23051300086 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 448 | 2023-05-13 | 44800 | keep | 0 | May | 2023 | 0.030513 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-13 02:56 | 2023-05-13 20:09 | 40 | 17:13 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO EN C/L Y SE REMPLAZO POSTE PRIMARIO (RADIAL) | B23051200569 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 1033 | 2023-05-13 | 41320 | keep | 0 | May | 2023 | 0.028143 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-13 03:08 | 2023-05-13 09:20 | 123 | 6:12 | P | ARBOL SOBRE LINEA | SJ-230513-02 SE SECCIONALIZO TRAMO PARA RETIRAR ARBOR SOBRE LINEA EN SERVICIO 95% | S23051300177 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 372 | 2023-05-13 | 45756 | keep | 0 | May | 2023 | 0.031164 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
SAN JUAN | 2023-05-13 03:19 | 2023-05-14 12:08 | 8 | 32:49 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 50KVA POR 50KVA | S23051300188 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1969 | 2023-05-13 | 15752 | keep | 0 | May | 2023 | 0.010729 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-13 03:57 | 2023-05-13 06:40 | 185 | 2:43 | P | DESGANCHE | 1 X 30 EN C/L 1 X 50 EN C/L SE DESGANCHO | S23051300217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-05-13 | 30155 | keep | 0 | May | 2023 | 0.020538 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
MAYAGÃœEZ | 2023-05-13 05:18 | 2023-05-13 17:30 | 15 | 12:12 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN SWICH UNIT POR AVERIA SOTERADA | M23051300045 | New_Event | UG Cable Fault | Include | Include | Equipment | 732 | 2023-05-13 | 10980 | keep | 0 | May | 2023 | 0.0074784 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-13 05:33 | 2023-05-13 11:18 | 29 | 5:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN RISER LLUVIA | R23051300125 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 345 | 2023-05-13 | 10005 | keep | 0 | May | 2023 | 0.0068144 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
UTUADO | 2023-05-13 05:35 | 2023-05-13 20:00 | 40 | 14:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA Y SE CERRO CORTE DE LINEA | A23051300000 | New_Event | Primary Wire Break | Include | Include | Equipment | 865 | 2023-05-13 | 34600 | keep | 0 | May | 2023 | 0.023566 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-13 05:41 | 2023-05-13 09:50 | 175 | 4:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23051300097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-05-13 | 43575 | keep | 0 | May | 2023 | 0.029679 | 0.00011919 | Sustained | FALSE | FALSE | Not_TMED_Event | 175
CANOVANAS | 2023-05-13 05:48 | 2023-05-13 09:12 | 151 | 3:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | R23051300132 | New_Event | Primary Wire Break | Include | Include | Equipment | 204 | 2023-05-13 | 30804 | keep | 0 | May | 2023 | 0.02098 | 0.00010285 | Sustained | FALSE | FALSE | Not_TMED_Event | 151
CAGUAS | 2023-05-13 05:55 | 2023-05-13 07:29 | 214 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L LLUVIA | C23051300090 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-05-13 | 20116 | keep | 0 | May | 2023 | 0.013701 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
BAYAMON | 2023-05-13 06:17 | 2023-05-13 09:56 | 242 | 3:39 | P | DESGANCHE | 1X100 EN C/L DESGANCHE TRASPATIO | B23051300185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2023-05-13 | 52998 | keep | 0 | May | 2023 | 0.036097 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
FAJARDO | 2023-05-13 06:19 | 2023-05-13 06:20 | 1830 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE BKR 2201-04 LLEVA 2201-02 | R23051300139 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-13 | 1830 | keep | 0 | May | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-05-13 06:19 | 2023-05-13 06:20 | 1197 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE BKR LLEVA 2201-02 | R23051300139 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 1197 | keep | 0 | May | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
FAJARDO | 2023-05-13 06:20 | 2023-05-13 11:02 | 494 | 4:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN RISER Y SE RETESO LINEA | R23051300143 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 282 | 2023-05-13 | 139308 | keep | 0 | May | 2023 | 0.094882 | 0.00033646 | Sustained | FALSE | FALSE | Not_TMED_Event | 494
VEGA BAJA | 2023-05-13 06:34 | 2023-05-13 06:36 | 776 | 0:02 | T | NO SE REPORTO CAUSA | RECERRO | B23051300190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-13 | 1552 | keep | 0 | May | 2023 | 0.0010571 | 0.00052853 | Momentary | FALSE | FALSE | Not_TMED_Event | 776
PONCE | 2023-05-13 06:37 | 2023-05-13 06:38 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051300030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 2379 | keep | 0 | May | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
CAGUAS | 2023-05-13 06:39 | 2023-05-13 06:40 | 125 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | C2305130000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-13 | 125 | keep | 0 | May | 2023 | 8.5137e-05 | 8.5137e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-05-13 06:40 | 2023-05-13 06:43 | 10211 | 0:03 | T | DESGANCHE | DISPARO CERRADO POR CONTROL | S2305130000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-05-13 | 30633 | keep | 0 | May | 2023 | 0.020864 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-13 06:40 | 2023-05-13 17:46 | 81 | 11:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIA | C23051300110 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 666 | 2023-05-13 | 53946 | keep | 0 | May | 2023 | 0.036742 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
SAN JUAN | 2023-05-13 06:41 | 2023-05-13 06:44 | 4133 | 0:03 | T | PARARRAYOS DEFECTUOSO | DISPARO CERRADO POR CONTROL | S2305130000X | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 3 | 2023-05-13 | 12399 | keep | 0 | May | 2023 | 0.0084449 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-13 06:43 | 2023-05-13 15:20 | 185 | 8:37 | P | DESGANCHE | 1 X 30 EN C/L 1 X 50 EN C/L SE DESGANCHO | S23051300217 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 517 | 2023-05-13 | 95645 | keep | 0 | May | 2023 | 0.065143 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
SAN JUAN | 2023-05-13 06:44 | 2023-05-13 19:17 | 40 | 12:33 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L SE RETIRO PARARRAYO CRUZADO | S23051200382 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 753 | 2023-05-13 | 30120 | keep | 0 | May | 2023 | 0.020515 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-13 06:46 | 2023-05-13 07:32 | 223 | 0:46 | P | DESGANCHE | 1X80 EN C/L | B23051300195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2023-05-13 | 10258 | keep | 0 | May | 2023 | 0.0069867 | 0.00015188 | Sustained | FALSE | FALSE | Not_TMED_Event | 223
PONCE | 2023-05-13 06:47 | 2023-05-13 10:00 | 100 | 3:13 | P | ANIMAL | 1 X 100 EN CORTE DE LIENA POR AVE | P23051300031 | New_Event | Animals | Include | Include | Wildlife | 193 | 2023-05-13 | 19300 | keep | 0 | May | 2023 | 0.013145 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-13 07:01 | 2023-05-14 13:20 | 58 | 30:19 | P | CABLE SOTERRADO AVERIADO | SE REPARO TRAMO SOTERRADO AVERIADO DESDE EL SU-2B @ T-35 MEDIANTE G.O.I. BY230513-01 | B23051300199 | New_Event | UG Cable Fault | Include | Include | Equipment | 1819 | 2023-05-13 | 105502 | keep | 0 | May | 2023 | 0.071857 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
UTUADO | 2023-05-13 07:02 | 2023-05-13 09:45 | 30 | 2:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051300011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-05-13 | 4890 | keep | 0 | May | 2023 | 0.0033306 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-13 07:03 | 2023-05-13 08:25 | 58 | 1:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER LLUVIA | C23051300123 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 82 | 2023-05-13 | 4756 | keep | 0 | May | 2023 | 0.0032393 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
SAN JUAN | 2023-05-13 07:09 | 2023-05-13 07:12 | 1681 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S23051300406 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-13 | 5043 | keep | 0 | May | 2023 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-05-13 07:09 | 2023-05-13 07:12 | 29 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL CARGA POR 1345-03 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-13 | 87 | keep | 0 | May | 2023 | 5.9255e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-05-13 07:09 | 2023-05-13 07:12 | 259 | 0:03 | T | NO SE REPORTO CAUSA | DESPARO CERRADO POR CONTROL LLEVA 1342-02 | S2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-13 | 777 | keep | 0 | May | 2023 | 0.00052921 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
GUAYAMA | 2023-05-13 07:09 | 2023-05-13 07:10 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051300036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
BARRANQUITAS | 2023-05-13 07:13 | 2023-05-13 14:36 | 100 | 7:23 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN C/L LEVANTO CONDUCTOR | C23051300127 | New_Event | Primary Wire Break | Include | Include | Equipment | 443 | 2023-05-13 | 44300 | keep | 0 | May | 2023 | 0.030173 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-13 07:24 | 2023-05-13 13:45 | 10 | 6:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X40 EN C/L POR LLUVIA | S23051300422 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 381 | 2023-05-13 | 3810 | keep | 0 | May | 2023 | 0.002595 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-13 07:28 | 2023-05-13 10:56 | 37 | 3:28 | P | DESGANCHE | 1X65 EN C/L Y 1X30 EN OTRO C/L DESGANCHE | B23051300205 | New_Event | Vegetation Contact | Include | Include | Vegetation | 208 | 2023-05-13 | 7696 | keep | 0 | May | 2023 | 0.0052417 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-05-13 07:35 | 2023-05-13 07:36 | 1802 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1802 | keep | 0 | May | 2023 | 0.0012273 | 0.0012273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1802
CAGUAS | 2023-05-13 07:38 | 2023-05-13 07:39 | 1320 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051300136 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1320 | keep | 0 | May | 2023 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2023-05-13 07:48 | 2023-05-13 11:14 | 114 | 3:26 | P | DESGANCHE | 1 X 65 EN C/L | C23051300140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-05-13 | 23484 | keep | 0 | May | 2023 | 0.015995 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
PONCE | 2023-05-13 08:05 | 2023-05-13 08:06 | 653 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | P23051300057 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-13 | 653 | keep | 0 | May | 2023 | 0.00044476 | 0.00044476 | Momentary | FALSE | FALSE | Not_TMED_Event | 653
PONCE | 2023-05-13 08:06 | 2023-05-13 11:49 | 10 | 3:43 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P23051300059 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 223 | 2023-05-13 | 2230 | keep | 0 | May | 2023 | 0.0015188 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-13 08:13 | 2023-05-13 08:49 | 1 | 0:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIAS | B23051300223 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 36 | 2023-05-13 | 36 | keep | 0 | May | 2023 | 2.4519e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-13 08:18 | 2023-05-13 14:47 | 164 | 6:29 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L | C23051300152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 389 | 2023-05-13 | 63796 | keep | 0 | May | 2023 | 0.043451 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
AGUADILLA | 2023-05-13 08:22 | 2023-05-13 19:30 | 178 | 11:08 | P | DESGANCHE | SE REALIZO DESGANCHE , SE REPARO LINEA PRIMARIA PARTIDA Y SE CERRO CORTE DE LINEA | M23051300082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 668 | 2023-05-13 | 118904 | keep | 0 | May | 2023 | 0.080985 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
CAGUAS | 2023-05-13 08:26 | 2023-05-13 08:27 | 1089 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE BKR SPARE 3015-07 LLEVA 50% 3103-05 | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1089 | keep | 0 | May | 2023 | 0.00074171 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
SAN JUAN | 2023-05-13 08:32 | 2023-05-13 08:33 | 726 | 0:01 | T | DESGANCHE | SJ-230512-02 HACIENDO PRUEBAS EN SU ALIMENTADOR DISPARO SE DEJO ABIERTO Y SE CERRO POR SCADA EN SERVICO 80% | S23051200239 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-13 | 726 | keep | 0 | May | 2023 | 0.00049448 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-13 08:33 | 2023-05-13 13:24 | 145 | 4:51 | P | DESGANCHE | SJ-230512-02 SE RETIRO RAMA SOBRE LINEA 100% EN SERVICIO | S23051200239 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 291 | 2023-05-13 | 42195 | keep | 0 | May | 2023 | 0.028739 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
VEGA BAJA | 2023-05-13 08:37 | 2023-05-13 14:58 | 113 | 6:21 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23051300236 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2023-05-13 | 43053 | keep | 0 | May | 2023 | 0.029323 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
VEGA BAJA | 2023-05-13 08:38 | 2023-05-13 15:57 | 40 | 7:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L POR LLUVIA | B23051300237 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 439 | 2023-05-13 | 17560 | keep | 0 | May | 2023 | 0.01196 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-13 08:39 | 2023-05-13 09:34 | 4 | 0:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8 EN XMR LLUVIA | C23051300162 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 55 | 2023-05-13 | 220 | keep | 0 | May | 2023 | 0.00014984 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-05-13 08:43 | 2023-05-13 08:44 | 1058 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL 20% POR 1424-08 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 1058 | keep | 0 | May | 2023 | 0.0007206 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-05-13 08:43 | 2023-05-13 08:44 | 1000 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL 80% POR 1424-08 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 1000 | keep | 0 | May | 2023 | 0.0006811 | 0.0006811 | Momentary | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-05-13 08:43 | 2023-05-13 08:44 | 278 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL CARGA POR 1424-08 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 278 | keep | 0 | May | 2023 | 0.00018934 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-13 08:43 | 2023-05-13 08:44 | 94 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL 70% POR 1424-08 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 94 | keep | 0 | May | 2023 | 6.4023e-05 | 6.4023e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 94
SAN JUAN | 2023-05-13 08:43 | 2023-05-13 08:44 | 1295 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL CARGA POR 1424-08 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 1295 | keep | 0 | May | 2023 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-05-13 08:43 | 2023-05-13 08:44 | 9 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 1401-10 LLEVA 70% 1401-08 | S2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 9 | keep | 0 | May | 2023 | 6.1299e-06 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-05-13 08:44 | 2023-05-13 08:45 | 2039 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | R2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 2039 | keep | 0 | May | 2023 | 0.0013888 | 0.0013888 | Momentary | FALSE | FALSE | Not_TMED_Event | 2039
CAGUAS | 2023-05-13 09:08 | 2023-05-13 09:12 | 817 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-13 | 3268 | keep | 0 | May | 2023 | 0.0022258 | 0.00055645 | Momentary | FALSE | FALSE | Not_TMED_Event | 817
BAYAMON | 2023-05-13 09:15 | 2023-05-13 09:17 | 1784 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CERRO POR CONTROL | B23051300249 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-13 | 3568 | keep | 0 | May | 2023 | 0.0024301 | 0.0012151 | Momentary | FALSE | FALSE | Not_TMED_Event | 1784
BAYAMON | 2023-05-13 09:15 | 2023-05-13 09:17 | 453 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CERRO POR CONTROL | B23051300249 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-13 | 906 | keep | 0 | May | 2023 | 0.00061707 | 0.00030854 | Momentary | FALSE | FALSE | Not_TMED_Event | 453
BAYAMON | 2023-05-13 09:15 | 2023-05-13 09:17 | 186 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1801-02 LLEVA 90% DEL 1711-04 LLEVA 10% DEL 1717-01 SE CERRO POR CONTROL | B23051300249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-13 | 372 | keep | 0 | May | 2023 | 0.00025337 | 0.00012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 186
BAYAMON | 2023-05-13 09:19 | 2023-05-13 11:49 | 133 | 2:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L PRINCIPAL, 1X40 EN C/L INTERMEDIO Y 1X25 EN OTRO C/L POR LLUVIAS | B23051300248 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 150 | 2023-05-13 | 19950 | keep | 0 | May | 2023 | 0.013588 | 9.0586e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 133
SAN JUAN | 2023-05-13 09:20 | 2023-05-13 10:20 | 3 | 1:00 | P | ARBOL SOBRE LINEA | SJ-230513-02 SE RETIRO ARBOL SOBRE SOBRE LINEA EN SERVICIO 100 % EN SERVICIO | S23051300177 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 60 | 2023-05-13 | 180 | keep | 0 | May | 2023 | 0.0001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-13 09:20 | 2023-05-13 20:20 | 30 | 11:00 | P | DESGANCHE | 1X65 DE RISER @ PROVISIONAL AEREO DESGANCHE | B23051300249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 660 | 2023-05-13 | 19800 | keep | 0 | May | 2023 | 0.013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-13 09:23 | 2023-05-13 09:24 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1342 | keep | 0 | May | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
PONCE | 2023-05-13 09:25 | 2023-05-13 09:28 | 2379 | 0:03 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR EN PASO ADICIONAL DE VIA LIBRE D2023-3946 POR PEDIDO DE CLAIRE BAREFIELD PARA ABRIR DESCONECTIVO | P23051300075 | New_Event | Switch Failure | Include | Include | Equipment | 3 | 2023-05-13 | 7137 | keep | 0 | May | 2023 | 0.004861 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2023-05-13 09:26 | 2023-05-13 14:29 | 30 | 5:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIA | S23051300623 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 303 | 2023-05-13 | 9090 | keep | 0 | May | 2023 | 0.0061912 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-13 09:28 | 2023-05-14 08:01 | 1 | 22:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X40 EN RISER SE REMPLAZO CAJA PRIMARIA QUEMADA | B23051300251 | New_Event | Cutout Failure | Include | Include | Equipment | 1353 | 2023-05-13 | 1353 | keep | 0 | May | 2023 | 0.00092152 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-13 09:30 | 2023-05-14 12:08 | 64 | 26:38 | P | DESGANCHE | 1 X 65 C/L Y DESGANCHE | S23051300030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1598 | 2023-05-13 | 102272 | keep | 0 | May | 2023 | 0.069657 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
VEGA BAJA | 2023-05-13 09:31 | 2023-05-13 12:46 | 40 | 3:15 | P | MAL TIEMPO/RAYOS | 1X65 EN C/L POR RAYO | B23051300254 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 195 | 2023-05-13 | 7800 | keep | 0 | May | 2023 | 0.0053125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-13 09:34 | 2023-05-13 16:02 | 40 | 6:28 | P | DESGANCHE | 1 X 65 EN C/L | C23051300186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2023-05-13 | 15520 | keep | 0 | May | 2023 | 0.010571 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-13 09:38 | 2023-05-13 12:39 | 20 | 3:01 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR POR AVE | P23051300079 | New_Event | Animals | Include | Include | Wildlife | 181 | 2023-05-13 | 3620 | keep | 0 | May | 2023 | 0.0024656 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-13 09:52 | 2023-05-13 13:29 | 15 | 3:37 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23051300177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2023-05-13 | 3255 | keep | 0 | May | 2023 | 0.002217 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-13 09:52 | 2023-05-13 13:15 | 10 | 3:23 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR Y 1 X 25 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A23051300029 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 203 | 2023-05-13 | 2030 | keep | 0 | May | 2023 | 0.0013826 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-13 09:53 | 2023-05-14 18:30 | 50 | 32:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE SECCIONALIZO AREA EN EL MONTE HAY QUE REALIZAR DESGANCHE | M23051300119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1957 | 2023-05-13 | 97850 | keep | 0 | May | 2023 | 0.066645 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-13 10:11 | 2023-05-13 18:04 | 104 | 7:53 | P | DESGANCHE | 1 X 100 EN C/L SE RETIRO RAMA | S23051300665 | New_Event | Vegetation Contact | Include | Include | Vegetation | 473 | 2023-05-13 | 49192 | keep | 0 | May | 2023 | 0.033504 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
MAYAGÃœEZ | 2023-05-13 10:12 | 2023-05-13 12:37 | 80 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | M23051300124 | New_Event | Primary Wire Break | Include | Include | Equipment | 145 | 2023-05-13 | 11600 | keep | 0 | May | 2023 | 0.0079007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-13 10:15 | 2023-05-13 10:31 | 10 | 0:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X15 EN XMR POR LLUVIAS | B23051300276 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 16 | 2023-05-13 | 160 | keep | 0 | May | 2023 | 0.00010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-13 10:19 | 2023-05-13 11:48 | 15 | 1:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN XMR MAL TIEMPO LLUVIA | R23051300186 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 89 | 2023-05-13 | 1335 | keep | 0 | May | 2023 | 0.00090926 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-13 10:33 | 2023-05-13 15:30 | 180 | 4:57 | P | ANIMAL | CRUCE POR AVE 1 X 50 EN C/L | R23051300189 | New_Event | Animals | Include | Include | Wildlife | 297 | 2023-05-13 | 53460 | keep | 0 | May | 2023 | 0.036411 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2023-05-13 10:33 | 2023-05-13 12:44 | 1142 | 2:11 | T | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO SE CERRO INTERRUPTOR | M23051300131 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 131 | 2023-05-13 | 149602 | keep | 0 | May | 2023 | 0.10189 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-13 10:42 | 2023-05-14 08:42 | 21 | 22:00 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S23051300699 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1320 | 2023-05-13 | 27720 | keep | 0 | May | 2023 | 0.01888 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
MAYAGÃœEZ | 2023-05-13 10:52 | 2023-05-13 11:32 | 3 | 0:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | M23051300134 | New_Event | Cutout Failure | Include | Include | Equipment | 40 | 2023-05-13 | 120 | keep | 0 | May | 2023 | 8.1731e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-13 10:53 | 2023-05-13 12:39 | 15 | 1:46 | P | DESGANCHE | 1X30 EN C/L 1X20 EN XMR DESGANCHE | B23051300298 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-13 | 1590 | keep | 0 | May | 2023 | 0.0010829 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-13 10:54 | 2023-05-13 10:55 | 2675 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO INTERRUPTOR | R23051300192 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-13 | 2675 | keep | 0 | May | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
VEGA BAJA | 2023-05-13 10:54 | 2023-05-13 11:50 | 10 | 0:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23051300040 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 56 | 2023-05-13 | 560 | keep | 0 | May | 2023 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-13 10:54 | 2023-05-13 13:47 | 170 | 2:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X50 EN C/L POR LLUVIAS | B23051300299 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 173 | 2023-05-13 | 29410 | keep | 0 | May | 2023 | 0.020031 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
CANOVANAS | 2023-05-13 10:55 | 2023-05-13 13:35 | 165 | 2:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X 100 EN C/L SE REEMPLAZO CAJA | R23051300205 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 160 | 2023-05-13 | 26400 | keep | 0 | May | 2023 | 0.017981 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
CANOVANAS | 2023-05-13 10:55 | 2023-05-13 12:30 | 7 | 1:35 | P | TRANSFORMADOR AVERIADO | SJ-230513-50 SE REEMPLAZO PM 7 DE 50 KVA AVERIADO | R23051200042 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 95 | 2023-05-13 | 665 | keep | 0 | May | 2023 | 0.00045293 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-13 10:56 | 2023-05-13 10:57 | 2900 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051300214 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 2900 | keep | 0 | May | 2023 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
ARECIBO | 2023-05-13 10:58 | 2023-05-13 12:23 | 20 | 1:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23051300041 | New_Event | Cutout Failure | Include | Include | Equipment | 85 | 2023-05-13 | 1700 | keep | 0 | May | 2023 | 0.0011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-05-13 11:05 | 2023-05-13 13:50 | 19 | 2:45 | P | DESGANCHE | 1 X 25 EN C/L | C23051300216 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-05-13 | 3135 | keep | 0 | May | 2023 | 0.0021352 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
VEGA BAJA | 2023-05-13 11:08 | 2023-05-13 16:44 | 15 | 5:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X10 EN XMR POR LLUVIA | B23051300306 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 336 | 2023-05-13 | 5040 | keep | 0 | May | 2023 | 0.0034327 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-13 11:09 | 2023-05-13 21:50 | 1 | 10:41 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA A 37.5 KVA | A23051300043 | New_Event | Service Transformer Failure | Include | Include | Equipment | 641 | 2023-05-13 | 641 | keep | 0 | May | 2023 | 0.00043658 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-13 11:10 | 2023-05-13 12:25 | 7 | 1:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23051300135 | New_Event | Secondary Wire Break | Include | Include | Equipment | 75 | 2023-05-13 | 525 | keep | 0 | May | 2023 | 0.00035758 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-05-13 11:11 | 2023-05-13 16:30 | 13 | 5:19 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23051300198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 319 | 2023-05-13 | 4147 | keep | 0 | May | 2023 | 0.0028245 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-05-13 11:14 | 2023-05-14 09:50 | 80 | 22:36 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S23051300750 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1356 | 2023-05-13 | 108480 | keep | 0 | May | 2023 | 0.073885 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-13 11:14 | 2023-05-13 11:15 | 4390 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 9320 | C23051300223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 4390 | keep | 0 | May | 2023 | 0.00299 | 0.00299 | Momentary | FALSE | FALSE | Not_TMED_Event | 4390
CAGUAS | 2023-05-13 11:14 | 2023-05-13 11:15 | 2092 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 9320 | C23051300223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 2092 | keep | 0 | May | 2023 | 0.0014249 | 0.0014249 | Momentary | FALSE | FALSE | Not_TMED_Event | 2092
CAGUAS | 2023-05-13 11:14 | 2023-05-13 11:15 | 540 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 9320 | C23051300223 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 540 | keep | 0 | May | 2023 | 0.00036779 | 0.00036779 | Momentary | FALSE | FALSE | Not_TMED_Event | 540
CAGUAS | 2023-05-13 11:14 | 2023-05-13 11:15 | 131 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 9320 | C23051300224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 131 | keep | 0 | May | 2023 | 8.9224e-05 | 8.9224e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 131
CAGUAS | 2023-05-13 11:14 | 2023-05-13 11:15 | 2281 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 9320 | C23051300224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 2281 | keep | 0 | May | 2023 | 0.0015536 | 0.0015536 | Momentary | FALSE | FALSE | Not_TMED_Event | 2281
CAGUAS | 2023-05-13 11:14 | 2023-05-13 11:15 | 1569 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 9320 | C23051300224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 1569 | keep | 0 | May | 2023 | 0.0010686 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
CAGUAS | 2023-05-13 11:14 | 2023-05-13 11:15 | 2417 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DEL 9320 | C23051300224 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 2417 | keep | 0 | May | 2023 | 0.0016462 | 0.0016462 | Momentary | FALSE | FALSE | Not_TMED_Event | 2417
CAGUAS | 2023-05-13 11:15 | 2023-05-13 15:26 | 114 | 4:11 | P | DESGANCHE | 1 X 65 EN C/L | C23051300140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2023-05-13 | 28614 | keep | 0 | May | 2023 | 0.019489 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
YAUCO | 2023-05-13 11:22 | 2023-05-13 13:06 | 60 | 1:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P23051300116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-05-13 | 6240 | keep | 0 | May | 2023 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-13 11:31 | 2023-05-14 09:02 | 66 | 21:31 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23051300315 | New_Event | Animals | Include | Include | Wildlife | 1291 | 2023-05-13 | 85206 | keep | 0 | May | 2023 | 0.058033 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
SAN JUAN | 2023-05-13 11:33 | 2023-05-14 08:50 | 23 | 21:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMPLAZO PORTAFUSIBLES | S23051300764 | New_Event | Cutout Failure | Include | Include | Equipment | 1277 | 2023-05-13 | 29371 | keep | 0 | May | 2023 | 0.020004 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
CAGUAS | 2023-05-13 11:40 | 2023-05-13 16:39 | 49 | 4:59 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23051300233 | New_Event | Animals | Include | Include | Wildlife | 299 | 2023-05-13 | 14651 | keep | 0 | May | 2023 | 0.0099787 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
SAN JUAN | 2023-05-13 11:51 | 2023-05-13 11:52 | 220 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL 98% POR 1303-05 | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 220 | keep | 0 | May | 2023 | 0.00014984 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-05-13 11:51 | 2023-05-13 11:52 | 870 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 98% 1303-04 | S2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 870 | keep | 0 | May | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-05-13 11:52 | 2023-05-13 13:36 | 25 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 50 C/L 1 X 65 C/L | S23051200154 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-05-13 | 2600 | keep | 0 | May | 2023 | 0.0017708 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-13 11:58 | 2023-05-13 12:25 | 100 | 0:27 | P | ANIMAL | 1X50 EN C/L CRUCE POR AVE | B23051300327 | New_Event | Animals | Include | Include | Wildlife | 27 | 2023-05-13 | 2700 | keep | 0 | May | 2023 | 0.001839 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-05-13 12:02 | 2023-05-13 23:35 | 200 | 11:33 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 Y 1 X 20 EN DISTINTOS CORTE DE LINEA Y 1 X15 EN TRANSFORMADOR SE REPARO LINEA PRIMARIA ROTA | A23051300051 | New_Event | Primary Wire Break | Include | Include | Equipment | 693 | 2023-05-13 | 138600 | keep | 0 | May | 2023 | 0.0944 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-05-13 12:15 | 2023-05-13 16:53 | 80 | 4:38 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO MEDIANTE SJ-230513-03 | S23051300784 | New_Event | Primary Wire Break | Include | Include | Equipment | 278 | 2023-05-13 | 22240 | keep | 0 | May | 2023 | 0.015148 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-13 12:15 | 2023-05-13 12:16 | 1105 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23051300339 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1105 | keep | 0 | May | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
CAGUAS | 2023-05-13 12:19 | 2023-05-13 22:32 | 100 | 10:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA LLUVIAS | C23051300244 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 613 | 2023-05-13 | 61300 | keep | 0 | May | 2023 | 0.041751 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-05-13 12:19 | 2023-05-13 14:53 | 100 | 2:34 | P | DESGANCHE | 1 X 80 EN RISER POR DESGANCHE | P23051300132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-05-13 | 15400 | keep | 0 | May | 2023 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-13 12:24 | 2023-05-13 17:06 | 600 | 4:42 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA POR RAMA SOBRE LINEA | M23051300153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-05-13 | 169200 | keep | 0 | May | 2023 | 0.11524 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
BARRANQUITAS | 2023-05-13 12:28 | 2023-05-13 12:46 | 1 | 0:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23051300248 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 18 | 2023-05-13 | 18 | keep | 0 | May | 2023 | 1.226e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 574 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 574 | keep | 0 | May | 2023 | 0.00039095 | 0.00039095 | Momentary | FALSE | FALSE | Not_TMED_Event | 574
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 2493 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 2493 | keep | 0 | May | 2023 | 0.001698 | 0.001698 | Momentary | FALSE | FALSE | Not_TMED_Event | 2493
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 1415 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 1415 | keep | 0 | May | 2023 | 0.00096375 | 0.00096375 | Momentary | FALSE | FALSE | Not_TMED_Event | 1415
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 1428 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 1428 | keep | 0 | May | 2023 | 0.0009726 | 0.0009726 | Momentary | FALSE | FALSE | Not_TMED_Event | 1428
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 1036 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300175 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 1036 | keep | 0 | May | 2023 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 382 | keep | 0 | May | 2023 | 0.00026018 | 0.00026018 | Momentary | FALSE | FALSE | Not_TMED_Event | 382
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 39 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300176 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 39 | keep | 0 | May | 2023 | 2.6563e-05 | 2.6563e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 39
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 2366 | keep | 0 | May | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
MAYAGÃœEZ | 2023-05-13 12:37 | 2023-05-13 12:38 | 1337 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 1337 | keep | 0 | May | 2023 | 0.00091062 | 0.00091062 | Momentary | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-05-13 12:37 | 2023-05-13 12:38 | 709 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 5600 | M23051300177 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-13 | 709 | keep | 0 | May | 2023 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
MAYAGÃœEZ | 2023-05-13 12:38 | 2023-05-13 13:20 | 80 | 0:42 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA SE CERRO CORTE DE LINEA | M23051300124 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 42 | 2023-05-13 | 3360 | keep | 0 | May | 2023 | 0.0022885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-13 12:41 | 2023-05-13 15:20 | 50 | 2:39 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE SECCIONALIZO LINEA PRIMARIA PARTIDA | M23051300197 | New_Event | Primary Wire Break | Include | Include | Equipment | 159 | 2023-05-13 | 7950 | keep | 0 | May | 2023 | 0.0054147 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-13 12:44 | 2023-05-15 15:25 | 8 | 50:41 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS RELACIONADO A EVENTO M23051200296 | M23051500175 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 3041 | 2023-05-13 | 24328 | keep | 0 | May | 2023 | 0.01657 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-13 12:44 | 2023-05-13 17:55 | 643 | 5:11 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO | M23051200283 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 311 | 2023-05-13 | 199973 | keep | 0 | May | 2023 | 0.1362 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-13 12:46 | 2023-05-13 17:45 | 250 | 4:59 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE PARA CERRAR PUENTE PRIMARIO DE LINEA @ CAJA (RADIAL) TRASPATIO | B23051300349 | New_Event | Primary Wire Break | Include | Include | Equipment | 299 | 2023-05-13 | 74750 | keep | 0 | May | 2023 | 0.050912 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CAGUAS | 2023-05-13 12:50 | 2023-05-13 14:58 | 1 | 2:08 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | C23051300258 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2023-05-13 | 128 | keep | 0 | May | 2023 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-13 12:59 | 2023-05-13 16:11 | 30 | 3:12 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE | P23051300144 | New_Event | Animals | Include | Include | Wildlife | 192 | 2023-05-13 | 5760 | keep | 0 | May | 2023 | 0.0039231 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-13 13:06 | 2023-05-13 15:00 | 1541 | 1:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 OVERHEAD GROUND WIRE SAFADO | A23051300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2023-05-13 | 175674 | keep | 0 | May | 2023 | 0.11965 | 0.0010496 | Sustained | FALSE | FALSE | Not_TMED_Event | 1541
AGUADILLA | 2023-05-13 13:06 | 2023-05-13 15:00 | 307 | 1:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 OVERHEAD GROUND WIRE SAFADO | A23051300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2023-05-13 | 34998 | keep | 0 | May | 2023 | 0.023837 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
AGUADILLA | 2023-05-13 13:06 | 2023-05-13 15:00 | 1277 | 1:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 OVERHEAD GROUND WIRE SAFADO | A23051300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2023-05-13 | 145578 | keep | 0 | May | 2023 | 0.099153 | 0.00086976 | Sustained | FALSE | FALSE | Not_TMED_Event | 1277
AGUADILLA | 2023-05-13 13:06 | 2023-05-13 15:00 | 1644 | 1:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 OVERHEAD GROUND WIRE SAFADO | A23051300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2023-05-13 | 187416 | keep | 0 | May | 2023 | 0.12765 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
AGUADILLA | 2023-05-13 13:06 | 2023-05-13 15:00 | 1831 | 1:54 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 2700 OVERHEAD GROUND WIRE SAFADO | A23051300057 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 114 | 2023-05-13 | 208734 | keep | 0 | May | 2023 | 0.14217 | 0.0012471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1831
BARRANQUITAS | 2023-05-13 13:07 | 2023-05-13 15:28 | 93 | 2:21 | P | DESGANCHE | 2 X 50 EN C/L | C23051300264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-05-13 | 13113 | keep | 0 | May | 2023 | 0.0089312 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
GUAYAMA | 2023-05-13 13:08 | 2023-05-13 14:38 | 30 | 1:30 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23051300148 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-05-13 | 2700 | keep | 0 | May | 2023 | 0.001839 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-13 13:09 | 2023-05-13 14:56 | 8 | 1:47 | P | MAL TIEMPO/RAYOS | 1 X 25 CORTE DE LINEA POR RAYOS | M23051300174 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 107 | 2023-05-13 | 856 | keep | 0 | May | 2023 | 0.00058302 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-13 13:20 | 2023-05-14 09:20 | 20 | 20:00 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051300186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1200 | 2023-05-13 | 24000 | keep | 0 | May | 2023 | 0.016346 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-13 13:23 | 2023-05-14 10:38 | 6 | 21:15 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | R23051300214 | New_Event | Animals | Include | Include | Wildlife | 1275 | 2023-05-13 | 7650 | keep | 0 | May | 2023 | 0.0052104 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-05-13 13:38 | 2023-05-13 15:37 | 10 | 1:59 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23051300221 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2023-05-13 | 1190 | keep | 0 | May | 2023 | 0.0008105 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-13 13:40 | 2023-05-13 17:21 | 100 | 3:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | R23051300224 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 221 | 2023-05-13 | 22100 | keep | 0 | May | 2023 | 0.015052 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-13 14:01 | 2023-05-13 15:55 | 108 | 1:54 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23051300367 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-05-13 | 12312 | keep | 0 | May | 2023 | 0.0083856 | 7.3558e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 108
CAGUAS | 2023-05-13 14:07 | 2023-05-14 10:27 | 10 | 20:20 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE XMR | C23051300283 | New_Event | Primary Wire Break | Include | Include | Equipment | 1220 | 2023-05-13 | 12200 | keep | 0 | May | 2023 | 0.0083094 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-05-13 14:10 | 2023-05-13 14:15 | 3502 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO NINGUN PERSONAL EN EL AREA | A23051300128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-05-13 | 17510 | keep | 0 | May | 2023 | 0.011926 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
SAN JUAN | 2023-05-13 14:29 | 2023-05-13 14:30 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1118-10 QUE LLEVA 20% DEL 1111-01 CERRADO POR SCADA | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 513 | keep | 0 | May | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-05-13 14:29 | 2023-05-13 14:30 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1118-10 QUE LLEVA 20% DEL 1111-01 CERRADO POR SCADA | S2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 2782 | keep | 0 | May | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
AGUADILLA | 2023-05-13 14:32 | 2023-05-14 13:06 | 50 | 22:34 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA | M23051300206 | New_Event | Primary Wire Break | Include | Include | Equipment | 1354 | 2023-05-13 | 67700 | keep | 0 | May | 2023 | 0.04611 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-13 14:37 | 2023-05-13 18:41 | 56 | 4:04 | P | DESGANCHE | 1 X 65 EN C/L | C23051300289 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-05-13 | 13664 | keep | 0 | May | 2023 | 0.0093065 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
ARECIBO | 2023-05-13 14:45 | 2023-05-13 16:50 | 50 | 2:05 | P | CONDUCTOR ARRIADO O CRUZADO | 3 X 30 EN CORTE DE LINEA SE INSTALARON AISLADORES POR TENDIDO ELECTRICO AL ALCANCE DE LAS MANOS | A23051300153 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 125 | 2023-05-13 | 6250 | keep | 0 | May | 2023 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-13 14:47 | 2023-05-13 16:38 | 100 | 1:51 | P | MAL TIEMPO/RAYOS | 3 X 65 EN CORTE DE LINEA Y 1 X 25 EN TRANSFORMADOR POR RAYOS | M23051300208 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 111 | 2023-05-13 | 11100 | keep | 0 | May | 2023 | 0.0075602 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-05-13 14:49 | 2023-05-13 17:10 | 80 | 2:21 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CORTE DE LINEA PARA CERRAR PUENTE PRIMARIO | P23051300168 | New_Event | Primary Wire Break | Include | Include | Equipment | 141 | 2023-05-13 | 11280 | keep | 0 | May | 2023 | 0.0076828 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-05-13 14:54 | 2023-05-14 11:09 | 1 | 20:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE LINEA PRIMARIA POR BAMBU | A23051300149 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1215 | 2023-05-13 | 1215 | keep | 0 | May | 2023 | 0.00082753 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-13 15:07 | 2023-05-13 16:16 | 1 | 1:09 | P | ANIMAL | 1 X 15 EN RISER POR AVE | P23051300176 | New_Event | Animals | Include | Include | Wildlife | 69 | 2023-05-13 | 69 | keep | 0 | May | 2023 | 4.6996e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-13 15:08 | 2023-05-13 17:41 | 30 | 2:33 | P | MAL TIEMPO/LLUVIA O VIENTO | 2X100 DE RISER 2 SU-1 POR LLUVIA | S23051300848 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 153 | 2023-05-13 | 4590 | keep | 0 | May | 2023 | 0.0031262 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-13 15:08 | 2023-05-13 18:11 | 7 | 3:03 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | R23051300235 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 183 | 2023-05-13 | 1281 | keep | 0 | May | 2023 | 0.00087248 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-05-13 15:10 | 2023-05-13 17:17 | 84 | 2:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA | C23051300299 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 127 | 2023-05-13 | 10668 | keep | 0 | May | 2023 | 0.0072659 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
SAN JUAN | 2023-05-13 15:14 | 2023-05-13 15:15 | 362 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE 1620-01 QUE LLEVA 90% DEL 1336-10 Y LLEVA 60% DEL 1620-02, CERRADO POR SCADA | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 362 | keep | 0 | May | 2023 | 0.00024656 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-05-13 15:14 | 2023-05-13 15:15 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-01 QUE LLEVA 90% DEL 1336-10 Y LLEVA 60% DEL 1620-02, CERRADO POR SCADA | S2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 36 | keep | 0 | May | 2023 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-13 15:14 | 2023-05-13 15:15 | 2230 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE 1620-01 QUE LLEVA 90% DEL 1336-10 Y LLEVA 60% DEL 1620-02, CERRADO POR SCADA | S2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 2230 | keep | 0 | May | 2023 | 0.0015188 | 0.0015188 | Momentary | FALSE | FALSE | Not_TMED_Event | 2230
CANOVANAS | 2023-05-13 15:17 | 2023-05-13 20:23 | 60 | 5:06 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | R23051300240 | New_Event | Animals | Include | Include | Wildlife | 306 | 2023-05-13 | 18360 | keep | 0 | May | 2023 | 0.012505 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-13 15:18 | 2023-05-13 17:44 | 20 | 2:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X65 EN C/L POR LLUVIA | S23051300855 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 146 | 2023-05-13 | 2920 | keep | 0 | May | 2023 | 0.0019888 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-05-13 15:18 | 2023-05-13 18:40 | 30 | 3:22 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051300165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-05-13 | 6060 | keep | 0 | May | 2023 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-13 15:20 | 2023-05-14 12:52 | 8 | 21:32 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA ROTA Y SE CERRO PUENTES | M23051300197 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1292 | 2023-05-13 | 10336 | keep | 0 | May | 2023 | 0.0070398 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-13 15:31 | 2023-05-13 15:32 | 2379 | 0:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRE INTERRUPTOR EN PASO ADICIONAL DE VIA LIBRE D2023-3946 POR PEDIDO DE CLAIRE BAREFIELD PARA CERRAR DESCONECTIVO | P23051300181 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-05-13 | 2379 | keep | 0 | May | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
FAJARDO | 2023-05-13 15:35 | 2023-05-13 15:36 | 956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 956 | keep | 0 | May | 2023 | 0.00065113 | 0.00065113 | Momentary | FALSE | FALSE | Not_TMED_Event | 956
VEGA BAJA | 2023-05-13 15:36 | 2023-05-13 16:17 | 1 | 0:41 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA 1 X 30 EN RISER CULEBRA | A23051300183 | New_Event | Animals | Include | Include | Wildlife | 41 | 2023-05-13 | 41 | keep | 0 | May | 2023 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-13 15:37 | 2023-05-13 17:34 | 117 | 1:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN C/L SE REMPLAZO CAJA PRIMARIA | B23051300391 | New_Event | Cutout Failure | Include | Include | Equipment | 117 | 2023-05-13 | 13689 | keep | 0 | May | 2023 | 0.0093235 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
HUMACAO | 2023-05-13 15:46 | 2023-05-13 16:46 | 7 | 1:00 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23051300310 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-05-13 | 420 | keep | 0 | May | 2023 | 0.00028606 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-05-13 16:01 | 2023-05-13 20:00 | 30 | 3:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051300188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-05-13 | 7170 | keep | 0 | May | 2023 | 0.0048835 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-13 16:04 | 2023-05-14 18:08 | 8 | 26:04 | P | NO SE REPORTO CAUSA | 2 X 65 EN C/L, 1 X 100 EN C/L | S23051300873 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1564 | 2023-05-13 | 12512 | keep | 0 | May | 2023 | 0.0085219 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-05-13 16:13 | 2023-05-13 17:38 | 3 | 1:25 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR DESGANCHE SECUNDARIO | B23051300400 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 85 | 2023-05-13 | 255 | keep | 0 | May | 2023 | 0.00017368 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-05-13 16:28 | 2023-05-13 16:29 | 234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 234 | keep | 0 | May | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
VEGA BAJA | 2023-05-13 16:29 | 2023-05-13 20:15 | 20 | 3:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23051300192 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 226 | 2023-05-13 | 4520 | keep | 0 | May | 2023 | 0.0030786 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-13 16:42 | 2023-05-13 16:44 | 1647 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23051300404 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-13 | 3294 | keep | 0 | May | 2023 | 0.0022435 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
MAYAGÃœEZ | 2023-05-13 16:50 | 2023-05-13 22:17 | 20 | 5:27 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA SE REPARO BAJANTES PRIMARIOS EN CORTE DE LINEA | M23051300253 | New_Event | Primary Wire Break | Include | Include | Equipment | 327 | 2023-05-13 | 6540 | keep | 0 | May | 2023 | 0.0044544 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-13 17:07 | 2023-05-13 21:06 | 223 | 3:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X80 EN C/L Y 1X65 EN OTRO C/L POR LLUVIA | B23051300413 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 239 | 2023-05-13 | 53297 | keep | 0 | May | 2023 | 0.0363 | 0.00015188 | Sustained | FALSE | FALSE | Not_TMED_Event | 223
MAYAGÃœEZ | 2023-05-13 17:11 | 2023-05-14 11:05 | 30 | 17:54 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23051300275 | New_Event | Primary Wire Break | Include | Include | Equipment | 1074 | 2023-05-13 | 32220 | keep | 0 | May | 2023 | 0.021945 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-13 17:18 | 2023-05-13 17:19 | 3046 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 1647-10 Y 15% DEL 1647-09 | R2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 3046 | keep | 0 | May | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-05-13 17:18 | 2023-05-13 17:19 | 308 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DEL 1646-03 | R2305160000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 308 | keep | 0 | May | 2023 | 0.00020978 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-05-13 17:18 | 2023-05-13 17:19 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1646-03 | R2305130000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 61 | keep | 0 | May | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
HUMACAO | 2023-05-13 17:34 | 2023-05-13 18:16 | 20 | 0:42 | P | DESGANCHE | 1 X 25 EN C/L | C23051300337 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2023-05-13 | 840 | keep | 0 | May | 2023 | 0.00057212 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-13 17:37 | 2023-05-13 21:14 | 18 | 3:37 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23051300899 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2023-05-13 | 3906 | keep | 0 | May | 2023 | 0.0026604 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
CANOVANAS | 2023-05-13 17:42 | 2023-05-14 18:02 | 200 | 24:20 | P | TERMINACION SOTERRADA AVERIADA | 1 X 140 EN RISER Y 1 SMU 20 DE 40A EN EL SU-2 AVERIA DE CABLE DEL T-24 @ T-25 SE ABRIO EN T-24 @ T-25 / T-25 @ T-24 SE HIZO TERMINACION NUEVA Y SE DIO SERVICIO | R23051300260 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1460 | 2023-05-13 | 292000 | keep | 0 | May | 2023 | 0.19888 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-13 17:45 | 2023-05-13 18:38 | 863 | 0:53 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE PARA CERRAR PUENTE PRIMARIO DE LINEA @ CAJA (RADIAL) TRASPATIO | B23051300349 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 53 | 2023-05-13 | 45739 | keep | 0 | May | 2023 | 0.031153 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-13 17:47 | 2023-05-13 19:03 | 10 | 1:16 | P | ANIMAL | 1 X 8 EN XMR CRUCE X AVE | C23051300340 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-05-13 | 760 | keep | 0 | May | 2023 | 0.00051763 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-13 17:49 | 2023-05-13 19:06 | 40 | 1:17 | P | ANIMAL | CRUCE POR AVE 2 X 40 EN C/L | R23051300261 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-05-13 | 3080 | keep | 0 | May | 2023 | 0.0020978 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-13 17:58 | 2023-05-14 16:09 | 100 | 22:11 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 100 EN C/L REMPLAZO POSTE PRIMARIO | R23051300262 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1331 | 2023-05-13 | 133100 | keep | 0 | May | 2023 | 0.090654 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-13 18:01 | 2023-05-13 21:24 | 104 | 3:23 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | R23051300263 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2023-05-13 | 21112 | keep | 0 | May | 2023 | 0.014379 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
MAYAGÃœEZ | 2023-05-13 18:07 | 2023-05-14 08:20 | 12 | 14:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER NO SE REPORTO CAUSA | M23051300299 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 853 | 2023-05-13 | 10236 | keep | 0 | May | 2023 | 0.0069717 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-05-13 18:07 | 2023-05-13 22:55 | 20 | 4:48 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN CORTE DE LINEA SE REPARO NEUTRAL PRIMARIO ROTO | M23051300354 | New_Event | Primary Wire Break | Include | Include | Equipment | 288 | 2023-05-13 | 5760 | keep | 0 | May | 2023 | 0.0039231 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-13 18:30 | 2023-05-13 22:12 | 40 | 3:42 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | B23051300441 | New_Event | Animals | Include | Include | Wildlife | 222 | 2023-05-13 | 8880 | keep | 0 | May | 2023 | 0.0060481 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-13 18:31 | 2023-05-13 22:15 | 500 | 3:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M23051300308 | New_Event | Cutout Failure | Include | Include | Equipment | 224 | 2023-05-13 | 112000 | keep | 0 | May | 2023 | 0.076283 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
VEGA BAJA | 2023-05-13 18:54 | 2023-05-14 07:24 | 12 | 12:30 | P | ANIMAL | 1X15 EN XMR CRUCE POR AVE | B23051300454 | New_Event | Animals | Include | Include | Wildlife | 750 | 2023-05-13 | 9000 | keep | 0 | May | 2023 | 0.0061299 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-05-13 19:02 | 2023-05-13 20:21 | 29 | 1:19 | P | ANIMAL | CRUCE POR AVE 1 X 100 EN C/L | R23051300278 | New_Event | Animals | Include | Include | Wildlife | 79 | 2023-05-13 | 2291 | keep | 0 | May | 2023 | 0.0015604 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-05-13 19:14 | 2023-05-13 19:15 | 362 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE 1620-01 QUE LLEVA 90% DEL 1336-10 Y LLEVA 60% DEL 1620-02, CERRADO POR SCADA | S2305130000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 362 | keep | 0 | May | 2023 | 0.00024656 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-05-13 19:14 | 2023-05-13 19:15 | 36 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE 1620-01 QUE LLEVA 90% DEL 1336-10 Y LLEVA 60% DEL 1620-02, CERRADO POR SCADA | S2305130000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 36 | keep | 0 | May | 2023 | 2.4519e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-13 19:14 | 2023-05-13 19:15 | 2230 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE 1620-01 QUE LLEVA 90% DEL 1336-10 Y LLEVA 60% DEL 1620-02, CERRADO POR SCADA | S2305130000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-13 | 2230 | keep | 0 | May | 2023 | 0.0015188 | 0.0015188 | Momentary | FALSE | FALSE | Not_TMED_Event | 2230
CANOVANAS | 2023-05-13 19:14 | 2023-05-13 22:17 | 93 | 3:03 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | R23051300285 | New_Event | Vegetation Contact | Include | Include | Vegetation | 183 | 2023-05-13 | 17019 | keep | 0 | May | 2023 | 0.011592 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
HUMACAO | 2023-05-13 19:18 | 2023-05-13 21:02 | 45 | 1:44 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23051300352 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-05-13 | 4680 | keep | 0 | May | 2023 | 0.0031875 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2023-05-13 19:19 | 2023-05-14 10:20 | 13 | 15:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTES SECUNDARIOS EN TRANSFORMADOR | P23051300205 | New_Event | Secondary Wire Break | Include | Include | Equipment | 901 | 2023-05-13 | 11713 | keep | 0 | May | 2023 | 0.0079777 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-05-13 19:33 | 2023-05-14 13:09 | 7 | 17:36 | P | DESGANCHE | 1 X 50 EN C/L | R23051300295 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1056 | 2023-05-13 | 7392 | keep | 0 | May | 2023 | 0.0050347 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-05-13 19:33 | 2023-05-13 21:35 | 30 | 2:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23051300216 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 122 | 2023-05-13 | 3660 | keep | 0 | May | 2023 | 0.0024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-05-13 19:45 | 2023-05-13 21:30 | 60 | 1:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23051300217 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 105 | 2023-05-13 | 6300 | keep | 0 | May | 2023 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-13 19:47 | 2023-05-14 08:42 | 10 | 12:55 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE CAJA @ LA ENTRADA DE XMR NO FUNDIO | B23051300466 | New_Event | Primary Wire Break | Include | Include | Equipment | 775 | 2023-05-13 | 7750 | keep | 0 | May | 2023 | 0.0052785 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-13 20:11 | 2023-05-14 08:35 | 50 | 12:24 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23051300328 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 744 | 2023-05-13 | 37200 | keep | 0 | May | 2023 | 0.025337 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-13 20:26 | 2023-05-13 21:13 | 27 | 0:47 | P | DESGANCHE | ABRIO C/L PARA SACAR BAMBUAS DE LA LINEA | C23051300358 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2023-05-13 | 1269 | keep | 0 | May | 2023 | 0.00086431 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
ARECIBO | 2023-05-13 20:27 | 2023-05-13 23:29 | 50 | 3:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23051300219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-05-13 | 9100 | keep | 0 | May | 2023 | 0.006198 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-13 20:28 | 2023-05-14 09:44 | 211 | 13:16 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO - TRASPATIO - MEDIANTE G.O.I. BY-230514-01 | B23051300470 | New_Event | Primary Wire Break | Include | Include | Equipment | 796 | 2023-05-13 | 167956 | keep | 0 | May | 2023 | 0.11439 | 0.00014371 | Sustained | FALSE | FALSE | Not_TMED_Event | 211
CANOVANAS | 2023-05-13 20:45 | 2023-05-14 09:54 | 32 | 13:09 | P | DESGANCHE | 1 X 50 EN C/L | R23051300413 | New_Event | Vegetation Contact | Include | Include | Vegetation | 789 | 2023-05-13 | 25248 | keep | 0 | May | 2023 | 0.017196 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
BAYAMON | 2023-05-13 20:48 | 2023-05-13 23:35 | 25 | 2:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | B23051300474 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 167 | 2023-05-13 | 4175 | keep | 0 | May | 2023 | 0.0028436 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-05-13 20:54 | 2023-05-14 08:39 | 10 | 11:45 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | R23051300326 | New_Event | Animals | Include | Include | Wildlife | 705 | 2023-05-13 | 7050 | keep | 0 | May | 2023 | 0.0048017 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-13 21:07 | 2023-05-13 21:08 | 2402 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECERRO | B23051300478 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-13 | 2402 | keep | 0 | May | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-05-13 21:08 | 2023-05-13 23:58 | 50 | 2:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L Y 2 X 100 EN C/L SE REMPLAZO CAJA PRIMARIA | S23051300930 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 170 | 2023-05-13 | 8500 | keep | 0 | May | 2023 | 0.0057893 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-05-13 21:25 | 2023-05-14 08:59 | 49 | 11:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X 50 EN CORTE DE LINEA PORTAFUSIBLE QUEMADO | P23051300218 | New_Event | Cutout Failure | Include | Include | Equipment | 694 | 2023-05-13 | 34006 | keep | 0 | May | 2023 | 0.023161 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
CANOVANAS | 2023-05-13 21:31 | 2023-05-14 12:18 | 35 | 14:47 | P | DESGANCHE | 1 X 50 EN C/L | R23051300335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 887 | 2023-05-13 | 31045 | keep | 0 | May | 2023 | 0.021145 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-13 21:40 | 2023-05-14 11:09 | 10 | 13:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L SE REMPLAZO CAJA PRIMARIA | B23051300489 | New_Event | Cutout Failure | Include | Include | Equipment | 809 | 2023-05-13 | 8090 | keep | 0 | May | 2023 | 0.0055101 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-13 21:45 | 2023-05-13 21:46 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-13 | 1709 | keep | 0 | May | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
AGUADILLA | 2023-05-13 22:09 | 2023-05-14 14:20 | 2 | 16:11 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | M23051300350 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 971 | 2023-05-13 | 1942 | keep | 0 | May | 2023 | 0.0013227 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-13 22:30 | 2023-05-13 22:32 | 867 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S2305130000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-13 | 1734 | keep | 0 | May | 2023 | 0.001181 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
CANOVANAS | 2023-05-13 23:22 | 2023-05-14 01:43 | 1648 | 2:21 | T | ALIMENTADOR AMARRADO | DISPARO VEHICULO IMPACTO POSTE AVERIA PERTENECE AL 2402-02 LLEVANDO PARTE DE LA CARGA DEL 2402-02 | R23051300339 | New_Event | Feeder Load Transferred | Include | Include | Other | 141 | 2023-05-13 | 232368 | keep | 0 | May | 2023 | 0.15826 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-05-13 23:22 | 2023-05-14 01:43 | 2094 | 2:21 | P | CAUSAS EXTERNAS | PARTE DE LA CARGA POR EL 2302-03 VEHICULO IMPACTO POSTE | R23051300339 | New_Event | Damage From Public | Include | Include | Public | 141 | 2023-05-13 | 295254 | keep | 0 | May | 2023 | 0.2011 | 0.0014262 | Sustained | FALSE | FALSE | Not_TMED_Event | 2094
CANOVANAS | 2023-05-13 23:22 | 2023-05-13 23:23 | 500 | 0:01 | T | CAUSAS EXTERNAS | RECIERRE | R23051300338 | New_Event | Damage From Public | Include | Include | Public | 1 | 2023-05-13 | 500 | keep | 0 | May | 2023 | 0.00034055 | 0.00034055 | Momentary | FALSE | FALSE | Not_TMED_Event | 500
BAYAMON | 2023-05-13 23:36 | 2023-05-14 17:59 | 12 | 18:23 | P | TRANSFORMADOR AVERIADO | 1X10 EN XMR SE REMPLAZO XMR 75KVA X 75KVA | B23051300500 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1103 | 2023-05-13 | 13236 | keep | 0 | May | 2023 | 0.009015 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-13 23:51 | 2023-05-13 23:53 | 867 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S2305130000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-13 | 1734 | keep | 0 | May | 2023 | 0.001181 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2023-05-14 00:10 | 2023-05-14 00:11 | 4882 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 4882 | keep | 0 | May | 2023 | 0.0033251 | 0.0033251 | Momentary | FALSE | FALSE | Not_TMED_Event | 4882
UTUADO | 2023-05-14 01:23 | 2023-05-14 09:18 | 85 | 7:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA REQUIERE DESGANCHE | A23051400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 475 | 2023-05-14 | 40375 | keep | 0 | May | 2023 | 0.027499 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2023-05-14 01:43 | 2023-05-14 03:02 | 419 | 1:19 | P | CAUSAS EXTERNAS | PARTE DE LA CARGA POR EL 2302-03 SE REEMPLAZARON PIN POLE TOPS PARTIDOS POR POSTE IMPACTADO POR VEHICULO | R23051400339 | Partial_restoration | Damage From Public | Include | Include | Public | 79 | 2023-05-14 | 33101 | keep | 0 | May | 2023 | 0.022545 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-14 01:52 | 2023-05-14 01:54 | 10211 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305140000X | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2023-05-14 | 20422 | keep | 0 | May | 2023 | 0.013909 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
CANOVANAS | 2023-05-14 02:08 | 2023-05-14 02:17 | 2322 | 0:09 | P | ALIMENTADOR AMARRADO | PARTE DE LA CARGA POR EL 2403-02 | R23051400026 | New_Event | Feeder Load Transferred | Include | Include | Other | 9 | 2023-05-14 | 20898 | keep | 0 | May | 2023 | 0.014234 | 0.0015815 | Sustained | FALSE | FALSE | Not_TMED_Event | 2322
CANOVANAS | 2023-05-14 02:08 | 2023-05-14 02:17 | 500 | 0:09 | T | CAUSAS EXTERNAS | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO POR POSTE IMPACTADO POR VEHICULO | R23051400026 | 1st_after_momentary | Damage From Public | Include | Include | Public | 9 | 2023-05-14 | 4500 | keep | 0 | May | 2023 | 0.0030649 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-05-14 02:17 | 2023-05-14 03:46 | 100 | 1:29 | P | CAUSAS EXTERNAS | SE LEVANTO CONDUCTOR DEL SUELO POR POSTE IMPACTADO POR VEHICULO | R23051400026 | Partial_restoration | Damage From Public | Include | Include | Public | 89 | 2023-05-14 | 8900 | keep | 0 | May | 2023 | 0.0060617 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-14 03:10 | 2023-05-14 11:01 | 30 | 7:51 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | R23051400035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 471 | 2023-05-14 | 14130 | keep | 0 | May | 2023 | 0.0096239 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-14 03:15 | 2023-05-14 03:17 | 867 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | S2305140000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-14 | 1734 | keep | 0 | May | 2023 | 0.001181 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
MAYAGÃœEZ | 2023-05-14 03:26 | 2023-05-14 03:27 | 2999 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051400005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 2999 | keep | 0 | May | 2023 | 0.0020426 | 0.0020426 | Momentary | FALSE | FALSE | Not_TMED_Event | 2999
BAYAMON | 2023-05-14 04:20 | 2023-05-14 10:41 | 61 | 6:21 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | B23051400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2023-05-14 | 23241 | keep | 0 | May | 2023 | 0.015829 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
AGUADILLA | 2023-05-14 05:20 | 2023-05-14 11:05 | 10 | 5:45 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR CRUCE DE LINEA PRIMARIA | A23051400013 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 345 | 2023-05-14 | 3450 | keep | 0 | May | 2023 | 0.0023498 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-14 05:49 | 2023-05-14 09:24 | 93 | 3:35 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23051400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-05-14 | 19995 | keep | 0 | May | 2023 | 0.013619 | 6.3342e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 93
VEGA BAJA | 2023-05-14 05:59 | 2023-05-14 08:14 | 50 | 2:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | A23051400016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 135 | 2023-05-14 | 6750 | keep | 0 | May | 2023 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-14 06:05 | 2023-05-14 09:09 | 315 | 3:04 | P | ANIMAL | 2X100 EN RISER CRUCE POR AVE | S23051400046 | New_Event | Animals | Include | Include | Wildlife | 184 | 2023-05-14 | 57960 | keep | 0 | May | 2023 | 0.039476 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
CAGUAS | 2023-05-14 06:08 | 2023-05-14 06:09 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23051400010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 906 | keep | 0 | May | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CANOVANAS | 2023-05-14 06:11 | 2023-05-14 08:08 | 75 | 1:57 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R23051400053 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-05-14 | 8775 | keep | 0 | May | 2023 | 0.0059766 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
ARECIBO | 2023-05-14 06:16 | 2023-05-14 08:45 | 50 | 2:29 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051400018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-05-14 | 7450 | keep | 0 | May | 2023 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-14 06:22 | 2023-05-14 06:23 | 3005 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 3005 | keep | 0 | May | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
BAYAMON | 2023-05-14 06:22 | 2023-05-14 06:23 | 1570 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23051400022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 1570 | keep | 0 | May | 2023 | 0.0010693 | 0.0010693 | Momentary | FALSE | FALSE | Not_TMED_Event | 1570
BAYAMON | 2023-05-14 06:28 | 2023-05-14 09:33 | 25 | 3:05 | P | ANIMAL | 1X30 EN C/L CRUCE POR AVE | B23051400023 | New_Event | Animals | Include | Include | Wildlife | 185 | 2023-05-14 | 4625 | keep | 0 | May | 2023 | 0.0031501 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-14 06:43 | 2023-05-14 06:44 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL 20% POR 1118-10 | S2301400000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-14 | 513 | keep | 0 | May | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-05-14 06:43 | 2023-05-14 06:44 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 20% DE 1111-01 | S230140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 2782 | keep | 0 | May | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2023-05-14 06:43 | 2023-05-14 12:39 | 30 | 5:56 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | R23051400064 | New_Event | Animals | Include | Include | Wildlife | 356 | 2023-05-14 | 10680 | keep | 0 | May | 2023 | 0.0072741 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-14 07:10 | 2023-05-14 16:44 | 3 | 9:34 | P | ANIMAL | 1 X 15 EN XMR CRUCE X REPTIL | R23051400070 | New_Event | Animals | Include | Include | Wildlife | 574 | 2023-05-14 | 1722 | keep | 0 | May | 2023 | 0.0011728 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-05-14 07:23 | 2023-05-14 12:54 | 32 | 5:31 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23051400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2023-05-14 | 10592 | keep | 0 | May | 2023 | 0.0072142 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
ARECIBO | 2023-05-14 08:02 | 2023-05-14 10:10 | 50 | 2:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23051400022 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-05-14 | 6400 | keep | 0 | May | 2023 | 0.004359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-14 08:09 | 2023-05-14 08:10 | 281 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | M23051400017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 281 | keep | 0 | May | 2023 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2023-05-14 08:09 | 2023-05-14 08:10 | 1252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | M23051400017 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 1252 | keep | 0 | May | 2023 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2023-05-14 08:09 | 2023-05-14 08:10 | 595 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | M23051400018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 595 | keep | 0 | May | 2023 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2023-05-14 08:09 | 2023-05-14 08:10 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | M23051400018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 51 | keep | 0 | May | 2023 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2023-05-14 08:09 | 2023-05-14 08:10 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | M23051400018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 721 | keep | 0 | May | 2023 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2023-05-14 08:09 | 2023-05-14 08:10 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 / 4700 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | A23051400023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 3502 | keep | 0 | May | 2023 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2023-05-14 08:09 | 2023-05-14 08:10 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 / 4700 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | A23051400023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 1241 | keep | 0 | May | 2023 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2023-05-14 08:09 | 2023-05-14 08:10 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 / 4700 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | A23051400023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 650 | keep | 0 | May | 2023 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2023-05-14 08:09 | 2023-05-14 08:10 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 / 4700 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | A23051400024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 1382 | keep | 0 | May | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2023-05-14 08:09 | 2023-05-14 08:10 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 / 4700 PUENTE ABIERTO EN LINEA 8100 ENTRE INDIERA Y BARTOLO. | A23051400024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-14 | 654 | keep | 0 | May | 2023 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
CAGUAS | 2023-05-14 08:15 | 2023-05-14 12:18 | 76 | 4:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO DE LINEA A LINEA | C23051400020 | New_Event | Primary Wire Break | Include | Include | Equipment | 243 | 2023-05-14 | 18468 | keep | 0 | May | 2023 | 0.012578 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
SAN JUAN | 2023-05-14 08:16 | 2023-05-14 14:30 | 67 | 6:14 | P | DESGANCHE | DESGANCHE Y 1 X 50 EN C/L | S23051400057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2023-05-14 | 25058 | keep | 0 | May | 2023 | 0.017067 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
FAJARDO | 2023-05-14 08:40 | 2023-05-14 09:29 | 76 | 0:49 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23051400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2023-05-14 | 3724 | keep | 0 | May | 2023 | 0.0025364 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CAGUAS | 2023-05-14 08:52 | 2023-05-14 13:13 | 51 | 4:21 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | C23051400028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-05-14 | 13311 | keep | 0 | May | 2023 | 0.0090661 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
VEGA BAJA | 2023-05-14 09:14 | 2023-05-14 10:20 | 50 | 1:06 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | A23051400031 | New_Event | Animals | Include | Include | Wildlife | 66 | 2023-05-14 | 3300 | keep | 0 | May | 2023 | 0.0022476 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-14 09:16 | 2023-05-14 09:40 | 6 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23051400016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-05-14 | 144 | keep | 0 | May | 2023 | 9.8078e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-05-14 09:22 | 2023-05-14 10:35 | 10 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | M23051400032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-05-14 | 730 | keep | 0 | May | 2023 | 0.0004972 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-14 09:26 | 2023-05-14 12:05 | 40 | 2:39 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHO Y REMPLAZO HERRAJE DE CAJA | R23051400098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2023-05-14 | 6360 | keep | 0 | May | 2023 | 0.0043318 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-05-14 09:39 | 2023-05-14 12:46 | 6 | 3:07 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN LINEA PRIMARIA | P23051400078 | New_Event | Primary Wire Break | Include | Include | Equipment | 187 | 2023-05-14 | 1122 | keep | 0 | May | 2023 | 0.00076419 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-05-14 09:43 | 2023-05-14 14:05 | 72 | 4:22 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | C23051400030 | New_Event | Animals | Include | Include | Wildlife | 262 | 2023-05-14 | 18864 | keep | 0 | May | 2023 | 0.012848 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2023-05-14 09:44 | 2023-05-14 09:50 | 1382 | 0:06 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO POR MACHETE ENDURECIDO (PERSONAL DE CAMPO INFORMO NO FUE NECESARIO REMPLAZAR EL MACHETE) BY-230514-01 | B23051400036 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 6 | 2023-05-14 | 8292 | keep | 0 | May | 2023 | 0.0056476 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-14 09:50 | 2023-05-14 11:34 | 211 | 1:44 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO - TRASPATIO - MEDIANTE G.O.I. BY-230514-01 | B23051300470 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 104 | 2023-05-14 | 21944 | keep | 0 | May | 2023 | 0.014946 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-14 09:54 | 2023-05-14 10:02 | 50 | 0:08 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | R23051400103 | New_Event | Animals | Include | Include | Wildlife | 8 | 2023-05-14 | 400 | keep | 0 | May | 2023 | 0.00027244 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-14 09:56 | 2023-05-14 12:55 | 300 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23051400028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-05-14 | 53700 | keep | 0 | May | 2023 | 0.036575 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2023-05-14 10:02 | 2023-05-14 13:34 | 105 | 3:32 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23051400035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 212 | 2023-05-14 | 22260 | keep | 0 | May | 2023 | 0.015161 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
BAYAMON | 2023-05-14 10:07 | 2023-05-14 14:51 | 2 | 4:44 | P | CONDUCTOR ARRIADO O CRUZADO | 1X65 EN BANCO DE XMRS SE DESPEGO PRIMARIA ARRIADA QUE SE HABIA CRUZADO | B23051400044 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 284 | 2023-05-14 | 568 | keep | 0 | May | 2023 | 0.00038686 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-14 10:11 | 2023-05-14 14:38 | 118 | 4:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 80 EN C/L SE REEMPLAZO PORTA FUSIBLE | S23051400075 | New_Event | Cutout Failure | Include | Include | Equipment | 267 | 2023-05-14 | 31506 | keep | 0 | May | 2023 | 0.021459 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
SAN JUAN | 2023-05-14 10:23 | 2023-05-14 10:25 | 10211 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CERRADO POR CONTROL | S2305140000X | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2023-05-14 | 20422 | keep | 0 | May | 2023 | 0.013909 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
BAYAMON | 2023-05-14 10:30 | 2023-05-14 11:29 | 5 | 0:59 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO Y SE REMPLAZO BAJANTE SECUNDARIO QUEMADO | B23051400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-05-14 | 295 | keep | 0 | May | 2023 | 0.00020092 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-05-14 10:38 | 2023-05-14 10:39 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23051400110 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-05-14 10:39 | 2023-05-14 14:15 | 6 | 3:36 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | R23051300214 | Partial_restoration | Animals | Include | Include | Wildlife | 216 | 2023-05-14 | 1296 | keep | 0 | May | 2023 | 0.0008827 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-14 10:40 | 2023-05-14 12:38 | 12 | 1:58 | P | DESGANCHE | 1X15 DE RISER @ T-1 DESGANCHE | B23051400059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 118 | 2023-05-14 | 1416 | keep | 0 | May | 2023 | 0.00096443 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-14 10:43 | 2023-05-14 10:46 | 1745 | 0:03 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL 15% DE SU CARGA ESTA POR EL 1646-03 | R23051400112 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-14 | 5235 | keep | 0 | May | 2023 | 0.0035655 | 0.0011885 | Momentary | FALSE | FALSE | Not_TMED_Event | 1745
BAYAMON | 2023-05-14 10:46 | 2023-05-14 14:33 | 38 | 3:47 | P | ANIMAL | 1X40 DE RISER @ T-35 SE RETIRO IGUANA | B23051400060 | New_Event | Animals | Include | Include | Wildlife | 227 | 2023-05-14 | 8626 | keep | 0 | May | 2023 | 0.0058751 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
SAN JUAN | 2023-05-14 10:47 | 2023-05-14 10:48 | 10211 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO CERRADO POR CONTROL | S2305140000X | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-14 | 10211 | keep | 0 | May | 2023 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
YAUCO | 2023-05-14 10:47 | 2023-05-14 16:07 | 1 | 5:20 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGA ELECTRICA | M23051400032 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 320 | 2023-05-14 | 320 | keep | 0 | May | 2023 | 0.00021795 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-14 10:49 | 2023-05-14 13:05 | 1 | 2:16 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER NO SE IDENTIFICO CAUSA | A23051400035 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 136 | 2023-05-14 | 136 | keep | 0 | May | 2023 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-14 10:50 | 2023-05-14 11:35 | 10211 | 0:45 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SJ-230514-01 SE SECCIONALIZO TRAMO PARA REMPLAZO DE CAJA PRIMARIA QUEMADA 80% EN SERVICIO | S23051400111 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 45 | 2023-05-14 | 459495 | keep | 0 | May | 2023 | 0.31296 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
BAYAMON | 2023-05-14 11:02 | 2023-05-14 19:09 | 13 | 8:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO DEL XMR | B23051400065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 487 | 2023-05-14 | 6331 | keep | 0 | May | 2023 | 0.004312 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2023-05-14 11:05 | 2023-05-14 11:28 | 32 | 0:23 | P | DESGANCHE | 1 X 100 EN C/L | R23051400116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-05-14 | 736 | keep | 0 | May | 2023 | 0.00050129 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
MAYAGÃœEZ | 2023-05-14 11:14 | 2023-05-14 13:09 | 6 | 1:55 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA POR UNO DE 37.5 KVA RELACIONADO A M23051200429 | M23051400035 | New_Event | Service Transformer Failure | Include | Include | Equipment | 115 | 2023-05-14 | 690 | keep | 0 | May | 2023 | 0.00046996 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-05-14 11:19 | 2023-05-14 14:14 | 1 | 2:55 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA Y SE RETIRO RAMA CRUZANDO LINEAS | A23051400038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-05-14 | 175 | keep | 0 | May | 2023 | 0.00011919 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-14 11:25 | 2023-05-14 12:18 | 30 | 0:53 | P | ANIMAL | 1X40 EN C/L CRUCE POR AVE | B23051400072 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-05-14 | 1590 | keep | 0 | May | 2023 | 0.0010829 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-14 11:29 | 2023-05-14 11:30 | 2234 | 0:01 | T | DESGANCHE | RECERRO | B2305140000X | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-14 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-14 11:30 | 2023-05-14 12:34 | 5 | 1:04 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO Y SE REMPLAZO BAJANTE SECUNDARIO QUEMADO | B23051400054 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-05-14 | 320 | keep | 0 | May | 2023 | 0.00021795 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-14 11:35 | 2023-05-14 14:17 | 2042 | 2:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE SECCIONALIZO TRAMO Y SE REEMPLAZARON 2 CAJAS PRIMARIAS SJ-230514-01 | S23051400111 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 162 | 2023-05-14 | 330804 | keep | 0 | May | 2023 | 0.22531 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-14 11:38 | 2023-05-14 14:34 | 5 | 2:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE AVERIADO | M23051400038 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2023-05-14 | 880 | keep | 0 | May | 2023 | 0.00059936 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-05-14 12:01 | 2023-05-14 14:10 | 8 | 2:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR PORTAFUSIBLE | A23051400040 | New_Event | Cutout Failure | Include | Include | Equipment | 129 | 2023-05-14 | 1032 | keep | 0 | May | 2023 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-14 12:11 | 2023-05-14 12:56 | 315 | 0:45 | T | DESGANCHE | SE RETIRO RAMA (A VARETA, DESDE EL SUELO) QUE ESTABA EN CONTACTO CON EL 4KV Y EL NEUTRAL DEL SISTEMA MEDIANTE SWITCHING-FORM BY-230514-02 Y SE CERRO POR CONTROL | S23051400162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 45 | 2023-05-14 | 14175 | keep | 0 | May | 2023 | 0.0096545 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
CANOVANAS | 2023-05-14 12:22 | 2023-05-14 13:50 | 95 | 1:28 | P | DESGANCHE | 1 X 80 EN C/L | R23051400127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-05-14 | 8360 | keep | 0 | May | 2023 | 0.005694 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
MAYAGÃœEZ | 2023-05-14 12:29 | 2023-05-14 15:00 | 40 | 2:31 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | M23051400046 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 151 | 2023-05-14 | 6040 | keep | 0 | May | 2023 | 0.0041138 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-14 12:45 | 2023-05-14 15:55 | 1 | 3:10 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | S23051400182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-05-14 | 190 | keep | 0 | May | 2023 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-14 12:56 | 2023-05-14 15:29 | 20 | 2:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | M23051400053 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-05-14 | 3060 | keep | 0 | May | 2023 | 0.0020842 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-14 12:57 | 2023-05-14 14:32 | 140 | 1:35 | P | ANIMAL | 1 X 80 EN RISER Y 1 X 100 EN C/L CRUCE X REPTIL | R23051400131 | New_Event | Animals | Include | Include | Wildlife | 95 | 2023-05-14 | 13300 | keep | 0 | May | 2023 | 0.0090586 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
VEGA BAJA | 2023-05-14 13:00 | 2023-05-14 13:40 | 15 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIR CAJAS DE TRANSFORMADOR PARA REPARAR SECUNDARIA AVERIADA | A23051400043 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-05-14 | 600 | keep | 0 | May | 2023 | 0.00040866 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-14 13:11 | 2023-05-14 19:03 | 59 | 5:52 | P | DESGANCHE | 1X50 DE RISER @ BOVEDA DESGANCHE | S23051400173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2023-05-14 | 20768 | keep | 0 | May | 2023 | 0.014145 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BARRANQUITAS | 2023-05-14 13:29 | 2023-05-14 13:31 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23051400063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-14 | 1740 | keep | 0 | May | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-05-14 13:54 | 2023-05-14 19:53 | 118 | 5:59 | P | DESGANCHE | 1 X 100 Y 1 X 40 EN CORTES DE LINEA DESGANCHE | S23051400179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 359 | 2023-05-14 | 42362 | keep | 0 | May | 2023 | 0.028853 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
BAYAMON | 2023-05-14 14:09 | 2023-05-14 15:24 | 20 | 1:15 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23051400087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 75 | 2023-05-14 | 1500 | keep | 0 | May | 2023 | 0.0010216 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-14 14:10 | 2023-05-14 17:54 | 8 | 3:44 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZA TRANSFORMADOR QUEMADO DE 50KVA X 25KVA | A23051400075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 224 | 2023-05-14 | 1792 | keep | 0 | May | 2023 | 0.0012205 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-05-14 14:15 | 2023-05-14 15:29 | 1 | 1:14 | P | SOBRECARGA | 2 X 20 EN MONTURA TRIFASICA POR CARGA | P23051400095 | New_Event | Trip Due To Overload | Include | Include | Other | 74 | 2023-05-14 | 74 | keep | 0 | May | 2023 | 5.0401e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-14 14:20 | 2023-05-14 16:50 | 290 | 2:30 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | S23051400182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-05-14 | 43500 | keep | 0 | May | 2023 | 0.029628 | 0.00019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 290
MAYAGÃœEZ | 2023-05-14 14:34 | 2023-05-14 17:30 | 150 | 2:56 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-05-14 | 26400 | keep | 0 | May | 2023 | 0.017981 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
FAJARDO | 2023-05-14 14:58 | 2023-05-14 15:40 | 18 | 0:42 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R23051400145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 42 | 2023-05-14 | 756 | keep | 0 | May | 2023 | 0.00051491 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-05-14 15:10 | 2023-05-14 15:11 | 513 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA20% DE SU CARGA POR EL 1118-10 | S2305140000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-14 | 513 | keep | 0 | May | 2023 | 0.0003494 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-05-14 15:10 | 2023-05-14 15:11 | 2782 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 20% DEL 1111-01 | S2305140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 2782 | keep | 0 | May | 2023 | 0.0018948 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
CANOVANAS | 2023-05-14 15:10 | 2023-05-14 16:08 | 84 | 0:58 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23051400149 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-05-14 | 4872 | keep | 0 | May | 2023 | 0.0033183 | 5.7212e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 84
PONCE | 2023-05-14 15:11 | 2023-05-14 16:09 | 12 | 0:58 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | P23051400097 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-05-14 | 696 | keep | 0 | May | 2023 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-14 15:15 | 2023-05-14 16:34 | 2 | 1:19 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO ENREDADERA | C23051400069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-05-14 | 158 | keep | 0 | May | 2023 | 0.00010761 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-05-14 15:29 | 2023-05-14 17:40 | 40 | 2:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051400071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-05-14 | 5240 | keep | 0 | May | 2023 | 0.0035689 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-14 15:31 | 2023-05-14 15:33 | 1381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305140000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-14 | 2762 | keep | 0 | May | 2023 | 0.0018812 | 0.00094059 | Momentary | FALSE | FALSE | Not_TMED_Event | 1381
CAGUAS | 2023-05-14 15:59 | 2023-05-14 17:18 | 65 | 1:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23051400073 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-05-14 | 5135 | keep | 0 | May | 2023 | 0.0034974 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
VEGA BAJA | 2023-05-14 15:59 | 2023-05-14 21:05 | 30 | 5:06 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | A23051400049 | New_Event | Primary Wire Break | Include | Include | Equipment | 306 | 2023-05-14 | 9180 | keep | 0 | May | 2023 | 0.0062525 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-05-14 16:01 | 2023-05-14 19:02 | 1 | 3:01 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR POR SECUNDARIA CRUZADA | A23051400050 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 181 | 2023-05-14 | 181 | keep | 0 | May | 2023 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-14 16:17 | 2023-05-14 19:48 | 500 | 3:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA PORTA FUSBLE AVERIADO | M23051400077 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2023-05-14 | 105500 | keep | 0 | May | 2023 | 0.071856 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2023-05-14 16:48 | 2023-05-15 09:16 | 12 | 16:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZARON 200 PIES DE SECUNDARIA QUEMADA 1 X 20 EN TRANSFORMADOR | P23051400100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 988 | 2023-05-14 | 11856 | keep | 0 | May | 2023 | 0.0080751 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-05-14 17:15 | 2023-05-14 18:54 | 10 | 1:39 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | M23051400105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 99 | 2023-05-14 | 990 | keep | 0 | May | 2023 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-14 17:16 | 2023-05-14 20:10 | 50 | 2:54 | P | DESGANCHE | 1 X 65 EN CORTE LINEA DESGANCHE | M23051400108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2023-05-14 | 8700 | keep | 0 | May | 2023 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-14 17:28 | 2023-05-14 17:29 | 2675 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23051400166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-14 | 2675 | keep | 0 | May | 2023 | 0.0018219 | 0.0018219 | Momentary | FALSE | FALSE | Not_TMED_Event | 2675
YAUCO | 2023-05-14 17:43 | 2023-05-14 18:35 | 60 | 0:52 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA AVE | M23051400115 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-05-14 | 3120 | keep | 0 | May | 2023 | 0.002125 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-05-14 17:48 | 2023-05-15 17:00 | 30 | 23:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051400116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1392 | 2023-05-14 | 41760 | keep | 0 | May | 2023 | 0.028443 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-14 18:17 | 2023-05-14 21:26 | 150 | 3:09 | P | CAUSAS EXTERNAS | 1X80 EN C/L SE RETIRO GLOBO DE HELIO DE LAS LINEAS | B23051400097 | New_Event | Damage From Public | Include | Include | Public | 189 | 2023-05-14 | 28350 | keep | 0 | May | 2023 | 0.019309 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2023-05-14 18:17 | 2023-05-14 18:48 | 40 | 0:31 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | A23051400062 | New_Event | Vegetation Contact | Include | Include | Vegetation | 31 | 2023-05-14 | 1240 | keep | 0 | May | 2023 | 0.00084456 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-14 18:27 | 2023-05-15 07:30 | 50 | 13:03 | P | ANIMAL | 1 X 65 EN CORTE LINEA CRUCE DE FASE PRIMARIA POR AVE | A23051400063 | New_Event | Animals | Include | Include | Wildlife | 783 | 2023-05-14 | 39150 | keep | 0 | May | 2023 | 0.026665 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-14 18:30 | 2023-05-15 15:50 | 12 | 21:20 | P | DESGANCHE | SE REALIZO DESGANCHE MASIVO Y SE RETEZO LINEA PRIMARIA CRUZADA CON NEUTRAL Y SE CERRO PUENTES ABIERTOS PARA SECCIONALIZAR | M23051300119 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 1280 | 2023-05-14 | 15360 | keep | 0 | May | 2023 | 0.010462 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-14 18:33 | 2023-05-15 09:30 | 22 | 14:57 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23051400169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 897 | 2023-05-14 | 19734 | keep | 0 | May | 2023 | 0.013441 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-05-14 18:37 | 2023-05-15 10:48 | 15 | 16:11 | P | ANIMAL | 1X 18 EN XMR SE RETIRO RATA | B23051400104 | New_Event | Animals | Include | Include | Wildlife | 971 | 2023-05-14 | 14565 | keep | 0 | May | 2023 | 0.0099202 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-05-14 18:48 | 2023-05-14 21:12 | 400 | 2:24 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | P23051400106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-05-14 | 57600 | keep | 0 | May | 2023 | 0.039231 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-05-14 19:06 | 2023-05-14 20:33 | 100 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTA CAUSA | M23051400139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-05-14 | 8700 | keep | 0 | May | 2023 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-14 19:13 | 2023-05-14 20:40 | 104 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | C23051400086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-05-14 | 9048 | keep | 0 | May | 2023 | 0.0061626 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
AGUADILLA | 2023-05-14 19:35 | 2023-05-15 09:50 | 1 | 14:15 | P | SOBRECARGA | 1 X 8 EN TRANSFORMADOR POR SOBRECARGA | M23051400149 | New_Event | Trip Due To Overload | Include | Include | Other | 855 | 2023-05-14 | 855 | keep | 0 | May | 2023 | 0.00058234 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-14 19:36 | 2023-05-15 09:40 | 8 | 14:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | M23051400150 | New_Event | Primary Wire Break | Include | Include | Equipment | 844 | 2023-05-14 | 6752 | keep | 0 | May | 2023 | 0.0045988 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-05-14 19:42 | 2023-05-15 04:54 | 1192 | 9:12 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA DEL ALIMENTADOR 7008-04 AL INTERRUPTOR 7008-05 POR INTERRUPTOR 7008-04 ESTAR AVERIADO POR HUMEDAD QUE ENTRO EN EL MISMO TAMBIEN SE AVERIARON LOS BUSHING DE SALIDA DE LAS FASES B Y C DEL #7 YA QUE SE ENCUENTRAN EN EL MISMO HOUSING | M23051400155 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 552 | 2023-05-14 | 657984 | keep | 0 | May | 2023 | 0.44815 | 0.00081187 | Sustained | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2023-05-14 19:42 | 2023-05-15 04:54 | 3041 | 9:12 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA DEL ALIMENTADOR 7008-04 AL INTERRUPTOR 7008-05 POR INTERRUPTOR 7008-04 ESTAR AVERIADO POR HUMEDAD QUE ENTRO EN EL MISMO TAMBIEN SE AVERIARON LOS BUSHING DE SALIDA DE LAS FASES B Y C DEL #7 YA QUE SE ENCUENTRAN EN EL MISMO HOUSING | M23051400155 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 552 | 2023-05-14 | 1678632 | keep | 0 | May | 2023 | 1.1433 | 0.0020712 | Sustained | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2023-05-14 19:42 | 2023-05-15 04:54 | 390 | 9:12 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA DEL ALIMENTADOR 7008-04 AL INTERRUPTOR 7008-05 POR INTERRUPTOR 7008-04 ESTAR AVERIADO POR HUMEDAD QUE ENTRO EN EL MISMO TAMBIEN SE AVERIARON LOS BUSHING DE SALIDA DE LAS FASES B Y C DEL #7 YA QUE SE ENCUENTRAN EN EL MISMO HOUSING | M23051400155 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 552 | 2023-05-14 | 215280 | keep | 0 | May | 2023 | 0.14663 | 0.00026563 | Sustained | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2023-05-14 19:42 | 2023-05-15 04:54 | 650 | 9:12 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE TRANSFIRIO LA CARGA DEL ALIMENTADOR 7008-04 AL INTERRUPTOR 7008-05 POR INTERRUPTOR 7008-04 ESTAR AVERIADO POR HUMEDAD QUE ENTRO EN EL MISMO TAMBIEN SE AVERIARON LOS BUSHING DE SALIDA DE LAS FASES B Y C DEL #7 YA QUE SE ENCUENTRAN EN EL MISMO HOUSING | M23051400155 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 552 | 2023-05-14 | 358800 | keep | 0 | May | 2023 | 0.24438 | 0.00044271 | Sustained | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2023-05-14 20:10 | 2023-05-15 09:15 | 60 | 13:05 | P | DESGANCHE | 1 X 30 EN SALIDA CONVERTIDOR DESGANCHE | A23051400070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 785 | 2023-05-14 | 47100 | keep | 0 | May | 2023 | 0.03208 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-14 20:59 | 2023-05-15 12:50 | 4 | 15:51 | P | DESGANCHE | SE REPARO BAJANTE EN CAJA PRIMARIA DESGANCHE | C23051400130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 951 | 2023-05-14 | 3804 | keep | 0 | May | 2023 | 0.0025909 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-14 21:23 | 2023-05-15 03:00 | 15 | 5:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23051400144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 337 | 2023-05-14 | 5055 | keep | 0 | May | 2023 | 0.0034429 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-14 21:27 | 2023-05-14 23:22 | 20 | 1:55 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23051400147 | New_Event | Animals | Include | Include | Wildlife | 115 | 2023-05-14 | 2300 | keep | 0 | May | 2023 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-14 21:32 | 2023-05-15 00:48 | 140 | 3:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA Y 1 X 100 EN C/L | B23051400149 | New_Event | Cutout Failure | Include | Include | Equipment | 196 | 2023-05-14 | 27440 | keep | 0 | May | 2023 | 0.018689 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
VEGA BAJA | 2023-05-14 22:00 | 2023-05-15 09:10 | 5 | 11:10 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | B23051400178 | New_Event | Primary Wire Break | Include | Include | Equipment | 670 | 2023-05-14 | 3350 | keep | 0 | May | 2023 | 0.0022817 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-14 22:03 | 2023-05-15 09:03 | 9 | 11:00 | P | ANIMAL | 1 X 10 EN XMR SE RETIRO AVE | B23051400180 | New_Event | Animals | Include | Include | Wildlife | 660 | 2023-05-14 | 5940 | keep | 0 | May | 2023 | 0.0040457 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-05-14 22:12 | 2023-05-15 11:40 | 70 | 13:28 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | M23051400271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 808 | 2023-05-14 | 56560 | keep | 0 | May | 2023 | 0.038523 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
PONCE | 2023-05-14 22:17 | 2023-05-15 07:00 | 10 | 8:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO BAJANTE PRIMARIO Y CAJA PRIMARIA DE TRANSFORMADOR | P23051400147 | New_Event | Cutout Failure | Include | Include | Equipment | 523 | 2023-05-14 | 5230 | keep | 0 | May | 2023 | 0.0035621 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-14 22:18 | 2023-05-14 23:54 | 150 | 1:36 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA Y SE REPARO CONDUCTOR PRIMARIO RADIAL | S23051400208 | New_Event | Primary Wire Break | Include | Include | Equipment | 96 | 2023-05-14 | 14400 | keep | 0 | May | 2023 | 0.0098078 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-05-14 23:56 | 2023-05-15 00:05 | 179 | 0:09 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23051400187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 9 | 2023-05-14 | 1611 | keep | 0 | May | 2023 | 0.0010972 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
CANOVANAS | 2023-05-15 00:08 | 2023-05-15 00:09 | 2708 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23051500001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 2708 | keep | 0 | May | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-05-15 00:14 | 2023-05-15 01:15 | 464 | 1:01 | P | AISLADOR ROTO, PARTIDO O SAFADO | 2 X 100 EN C/L SE REEMPLAZO AISLADOR | R23051500003 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 61 | 2023-05-15 | 28304 | keep | 0 | May | 2023 | 0.019278 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
AGUADILLA | 2023-05-15 00:48 | 2023-05-15 10:17 | 60 | 9:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23051500004 | New_Event | Primary Wire Break | Include | Include | Equipment | 569 | 2023-05-15 | 34140 | keep | 0 | May | 2023 | 0.023253 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-15 02:39 | 2023-05-15 15:01 | 16 | 12:22 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR PM AVERIADO (T-45) MEDIANTE G.O.I. SJ-230515-01 | S23051500003 | New_Event | Service Transformer Failure | Include | Include | Equipment | 742 | 2023-05-15 | 11872 | keep | 0 | May | 2023 | 0.008086 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
FAJARDO | 2023-05-15 04:12 | 2023-05-15 08:32 | 164 | 4:20 | P | ARBOL SOBRE LINEA | 1 X 80 EN C/L SE RETIRO ARBOL SOBRE LINEA | R23051500007 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 260 | 2023-05-15 | 42640 | keep | 0 | May | 2023 | 0.029042 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
PONCE | 2023-05-15 04:46 | 2023-05-15 04:58 | 5063 | 0:12 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL | P23051500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2023-05-15 | 60756 | keep | 0 | May | 2023 | 0.041381 | 0.0034484 | Sustained | FALSE | FALSE | Not_TMED_Event | 5063
CAGUAS | 2023-05-15 04:55 | 2023-05-15 04:56 | 1702 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051500002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 1702 | keep | 0 | May | 2023 | 0.0011592 | 0.0011592 | Momentary | FALSE | FALSE | Not_TMED_Event | 1702
CANOVANAS | 2023-05-15 05:03 | 2023-05-15 05:04 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23051500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
BAYAMON | 2023-05-15 05:18 | 2023-05-15 11:45 | 1 | 6:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X100 EN RISER SE REMPLAZO PORTAFUSIBLE | S23051500006 | New_Event | Cutout Failure | Include | Include | Equipment | 387 | 2023-05-15 | 387 | keep | 0 | May | 2023 | 0.00026358 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-15 05:48 | 2023-05-15 09:23 | 8 | 3:35 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23051500010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 215 | 2023-05-15 | 1720 | keep | 0 | May | 2023 | 0.0011715 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-05-15 06:00 | 2023-05-15 17:25 | 30 | 11:25 | P | CONDUCTOR ROTO O ABIERTO | 2 X 30 EN CONVERTIDOR SE REPARO BAJANTE ZAFADO DE CAJA A CONVERTIDOR | A23051500040 | New_Event | Primary Wire Break | Include | Include | Equipment | 685 | 2023-05-15 | 20550 | keep | 0 | May | 2023 | 0.013997 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-15 06:14 | 2023-05-15 14:42 | 2 | 8:28 | P | DESGANCHE | 2X50 EN C/L | S23051500007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 508 | 2023-05-15 | 1016 | keep | 0 | May | 2023 | 0.00069199 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-15 06:25 | 2023-05-15 14:19 | 150 | 7:54 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S23051500008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 474 | 2023-05-15 | 71100 | keep | 0 | May | 2023 | 0.048426 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-05-15 06:35 | 2023-05-15 10:30 | 19 | 3:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARARON BAJANTES Y LINEAS SECUNDARIAS | R23051500014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 235 | 2023-05-15 | 4465 | keep | 0 | May | 2023 | 0.0030411 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-05-15 06:40 | 2023-05-15 14:04 | 20 | 7:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR Y SUBIR SECUNDARIA AVERIADA/ARRIADA TRASPATIO | S23051500010 | New_Event | Secondary Wire Break | Include | Include | Equipment | 444 | 2023-05-15 | 8880 | keep | 0 | May | 2023 | 0.0060481 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-15 07:02 | 2023-05-15 15:59 | 1 | 8:57 | P | NO SE REPORTO CAUSA | 1X25 DE RISER @ SUBESTACION PRIVADA | S23051500012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 537 | 2023-05-15 | 537 | keep | 0 | May | 2023 | 0.00036575 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-15 07:02 | 2023-05-15 09:18 | 5 | 2:16 | P | PARARRAYOS DEFECTUOSO | 2 X 50 EN C/L Y 2 X 40 EN RISER SE ELIMINARON PARARRAYOS EN GABINETE PRIVADO | R23051500022 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 136 | 2023-05-15 | 680 | keep | 0 | May | 2023 | 0.00046314 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-05-15 07:08 | 2023-05-15 11:12 | 10 | 4:04 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGA ELECTRICA | A23051500006 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 244 | 2023-05-15 | 2440 | keep | 0 | May | 2023 | 0.0016619 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-15 07:09 | 2023-05-15 07:10 | 2891 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | R23051500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 2891 | keep | 0 | May | 2023 | 0.001969 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
CANOVANAS | 2023-05-15 07:14 | 2023-05-15 10:49 | 59 | 3:35 | P | ANIMAL | 2 X 25 EN RISER CRUCE X AVE | R23051500025 | New_Event | Animals | Include | Include | Wildlife | 215 | 2023-05-15 | 12685 | keep | 0 | May | 2023 | 0.0086397 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
CANOVANAS | 2023-05-15 07:17 | 2023-05-15 12:10 | 15 | 4:53 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | R23051500026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 293 | 2023-05-15 | 4395 | keep | 0 | May | 2023 | 0.0029934 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-15 07:22 | 2023-05-15 14:57 | 4 | 7:35 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23051500007 | New_Event | Animals | Include | Include | Wildlife | 455 | 2023-05-15 | 1820 | keep | 0 | May | 2023 | 0.0012396 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-05-15 07:28 | 2023-05-15 13:10 | 1 | 5:42 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23051500040 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 342 | 2023-05-15 | 342 | keep | 0 | May | 2023 | 0.00023293 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-15 07:29 | 2023-05-15 14:10 | 2450 | 6:41 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5300 SE TRANSFIRIO 20% DE LA CARGA AL 2603-09 AVERIA EN TRAMO SOTERRADO 12631B - PUENTES. | C23051500009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 401 | 2023-05-15 | 982450 | keep | 0 | May | 2023 | 0.66914 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-05-15 07:29 | 2023-05-15 21:54 | 640 | 14:25 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 12600 AVERIA EN TRAMO SOTERRADO 12631B - PUENTES. | C23051500009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 865 | 2023-05-15 | 553600 | keep | 0 | May | 2023 | 0.37705 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
BAYAMON | 2023-05-15 07:31 | 2023-05-15 12:46 | 1 | 5:15 | P | DESGANCHE | 1X50 EN RISER DESGANCHE | S23051500015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2023-05-15 | 315 | keep | 0 | May | 2023 | 0.00021455 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-15 07:41 | 2023-05-15 07:42 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECIIERE | B2305150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 3438 | keep | 0 | May | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
AGUADILLA | 2023-05-15 07:43 | 2023-05-15 07:44 | 4607 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23051500009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 4607 | keep | 0 | May | 2023 | 0.0031378 | 0.0031378 | Momentary | FALSE | FALSE | Not_TMED_Event | 4607
MAYAGÃœEZ | 2023-05-15 08:01 | 2023-05-15 11:50 | 60 | 3:49 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23051500048 | New_Event | Animals | Include | Include | Wildlife | 229 | 2023-05-15 | 13740 | keep | 0 | May | 2023 | 0.0093583 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-05-15 08:09 | 2023-05-15 16:56 | 1835 | 8:47 | T | CAUSAS EXTERNAS | SE SECCIONALIZO EL ALIMENTADOR | C23051500019 | New_Event | Damage From Public | Include | Include | Public | 527 | 2023-05-15 | 967045 | keep | 0 | May | 2023 | 0.65865 | 0.0012498 | Sustained | FALSE | FALSE | Not_TMED_Event | 1835
BAYAMON | 2023-05-15 08:12 | 2023-05-17 12:02 | 12 | 51:50 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 50KVA | B23051500015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3110 | 2023-05-15 | 37320 | keep | 0 | May | 2023 | 0.025418 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-15 08:14 | 2023-05-15 12:44 | 57 | 4:30 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23051500019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 270 | 2023-05-15 | 15390 | keep | 0 | May | 2023 | 0.010482 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
GUAYAMA | 2023-05-15 08:27 | 2023-05-15 12:55 | 1 | 4:28 | P | PARARRAYOS DEFECTUOSO | SE INSTALO PARARRAYO Y SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | P23051500019 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 268 | 2023-05-15 | 268 | keep | 0 | May | 2023 | 0.00018253 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-15 08:34 | 2023-05-15 08:35 | 67 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23051500018 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-15 | 67 | keep | 0 | May | 2023 | 4.5633e-05 | 4.5633e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 67
VEGA BAJA | 2023-05-15 08:35 | 2023-05-15 10:27 | 60 | 1:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23051500021 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 112 | 2023-05-15 | 6720 | keep | 0 | May | 2023 | 0.004577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-05-15 08:44 | 2023-05-15 15:27 | 81 | 6:43 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | C23051500034 | New_Event | Animals | Include | Include | Wildlife | 403 | 2023-05-15 | 32643 | keep | 0 | May | 2023 | 0.022233 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2023-05-15 08:48 | 2023-05-15 11:33 | 10 | 2:45 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23051500019 | New_Event | Animals | Include | Include | Wildlife | 165 | 2023-05-15 | 1650 | keep | 0 | May | 2023 | 0.0011238 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-15 09:01 | 2023-05-15 11:11 | 10 | 2:10 | P | NO SE REPORTO CAUSA | 1X80 DEL SU-3 @ SUBESTACION PRIVADA | S23051500032 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-05-15 | 1300 | keep | 0 | May | 2023 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-15 09:03 | 2023-05-15 14:14 | 3 | 5:11 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23051500025 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 311 | 2023-05-15 | 933 | keep | 0 | May | 2023 | 0.00063546 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-15 09:08 | 2023-05-15 21:19 | 43 | 12:11 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | B23051500029 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 731 | 2023-05-15 | 31433 | keep | 0 | May | 2023 | 0.021409 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
GUAYAMA | 2023-05-15 09:22 | 2023-05-15 13:33 | 1 | 4:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA DE CORTE DE LINEA QUEMADA DE 100A Y 1 X 65 EN CORTE DE LINEA | P23051500071 | New_Event | Cutout Failure | Include | Include | Equipment | 251 | 2023-05-15 | 251 | keep | 0 | May | 2023 | 0.00017095 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-15 09:31 | 2023-05-15 11:02 | 4 | 1:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | M23051500076 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2023-05-15 | 364 | keep | 0 | May | 2023 | 0.00024792 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-05-15 09:36 | 2023-05-15 16:45 | 75 | 7:09 | P | DESGANCHE | 2 X 30 EN C/L | C23051500054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 429 | 2023-05-15 | 32175 | keep | 0 | May | 2023 | 0.021914 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-05-15 09:53 | 2023-05-15 10:46 | 7 | 0:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | REMPLAZO EL BAJANTE SECUNDARIO Y REGULO EL XMR BAJO DEL TAP A @ B QUEDO EN 123/246V | C23051500056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 53 | 2023-05-15 | 371 | keep | 0 | May | 2023 | 0.00025269 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-05-15 10:01 | 2023-05-16 13:53 | 1 | 27:52 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23051600114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1672 | 2023-05-15 | 1672 | keep | 0 | May | 2023 | 0.0011388 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-15 10:04 | 2023-05-15 10:05 | 1342 | 0:01 | T | ANIMAL | RECIERRE | C2305150000X | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-15 | 1342 | keep | 0 | May | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
CAGUAS | 2023-05-15 10:05 | 2023-05-15 14:47 | 1 | 4:42 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | C23051500103 | 1st_after_momentary | Animals | Include | Include | Wildlife | 282 | 2023-05-15 | 282 | keep | 0 | May | 2023 | 0.00019207 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-15 10:10 | 2023-05-15 11:46 | 1 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 25 EN RISER | R23051500050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2023-05-15 | 96 | keep | 0 | May | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-15 10:12 | 2023-05-15 12:00 | 150 | 1:48 | P | ANIMAL | 1 X 80 SMU-20 CRUCE POR AVE EN AEREO PROVISIONAL | B23051500040 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-05-15 | 16200 | keep | 0 | May | 2023 | 0.011034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-05-15 10:13 | 2023-05-15 12:21 | 10 | 2:08 | P | CAUSAS EXTERNAS | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS ROTAS POR UN CAMION | M23051500091 | New_Event | Damage From Public | Include | Include | Public | 128 | 2023-05-15 | 1280 | keep | 0 | May | 2023 | 0.0008718 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-15 10:17 | 2023-05-15 10:18 | 271 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23051500044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 271 | keep | 0 | May | 2023 | 0.00018458 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2023-05-15 10:20 | 2023-05-15 17:38 | 97 | 7:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L | B23051500043 | New_Event | Cutout Failure | Include | Include | Equipment | 438 | 2023-05-15 | 42486 | keep | 0 | May | 2023 | 0.028937 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
FAJARDO | 2023-05-15 10:21 | 2023-05-15 11:38 | 3 | 1:17 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R23051500051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-05-15 | 231 | keep | 0 | May | 2023 | 0.00015733 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-05-15 10:28 | 2023-05-15 12:39 | 3 | 2:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | B23051500049 | New_Event | Cutout Failure | Include | Include | Equipment | 131 | 2023-05-15 | 393 | keep | 0 | May | 2023 | 0.00026767 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
YAUCO | 2023-05-15 10:36 | 2023-05-15 15:42 | 8 | 5:06 | P | TRANSFORMADOR AVERIADO | CAMBIO TRANSFORMADOR AVERIADO DE 25KVA A 2400 POR UNO MISMA CAPACIDAD | P23051500052 | New_Event | Service Transformer Failure | Include | Include | Equipment | 306 | 2023-05-15 | 2448 | keep | 0 | May | 2023 | 0.0016673 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-15 10:38 | 2023-05-15 14:05 | 3 | 3:27 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23051500098 | New_Event | Animals | Include | Include | Wildlife | 207 | 2023-05-15 | 621 | keep | 0 | May | 2023 | 0.00042296 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-05-15 10:47 | 2023-05-15 15:52 | 5 | 5:05 | P | NO SE REPORTO CAUSA | 1 XX10 EN XMR | C23051500070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 305 | 2023-05-15 | 1525 | keep | 0 | May | 2023 | 0.0010387 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-05-15 10:51 | 2023-05-15 14:15 | 100 | 3:24 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23051500109 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 204 | 2023-05-15 | 20400 | keep | 0 | May | 2023 | 0.013894 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-15 11:08 | 2023-05-15 15:46 | 4 | 4:38 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE RAPARO SECUNDARIA | S23051500052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 278 | 2023-05-15 | 1112 | keep | 0 | May | 2023 | 0.00075738 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-05-15 11:18 | 2023-05-15 13:07 | 66 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA QUEMADA, NO FUNDIO | C23051500079 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2023-05-15 | 7194 | keep | 0 | May | 2023 | 0.0048998 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
HUMACAO | 2023-05-15 11:28 | 2023-05-15 22:18 | 8 | 10:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZO DE BAJANTE SECUNDARIO | C23051500084 | New_Event | Secondary Wire Break | Include | Include | Equipment | 650 | 2023-05-15 | 5200 | keep | 0 | May | 2023 | 0.0035417 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-15 11:39 | 2023-05-16 10:53 | 8 | 23:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23051500079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1394 | 2023-05-15 | 11152 | keep | 0 | May | 2023 | 0.0075956 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-15 11:46 | 2023-05-15 13:25 | 10 | 1:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23051400126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 99 | 2023-05-15 | 990 | keep | 0 | May | 2023 | 0.00067428 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-15 11:51 | 2023-05-15 14:19 | 62 | 2:28 | P | ARBOL SOBRE LINEA | 1 X 65 EN RISER @ SU-4 ARBOL CAYO SOBRE SU-3 Y AL MOVER LA ESTRUCTURA CAUSO LA AVERIA. | R23051500062 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 148 | 2023-05-15 | 9176 | keep | 0 | May | 2023 | 0.0062497 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
GUAYAMA | 2023-05-15 12:09 | 2023-05-15 13:19 | 40 | 1:10 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | P23051500062 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-05-15 | 2800 | keep | 0 | May | 2023 | 0.0019071 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-15 12:28 | 2023-05-15 12:47 | 6 | 0:19 | P | DESGANCHE | 1 X 10 EN C/L DESGANCHE | C23051500106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 19 | 2023-05-15 | 114 | keep | 0 | May | 2023 | 7.7645e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-15 12:39 | 2023-05-15 12:42 | 2216 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | B23051500049 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-15 | 6648 | keep | 0 | May | 2023 | 0.0045279 | 0.0015093 | Momentary | FALSE | FALSE | Not_TMED_Event | 2216
SAN JUAN | 2023-05-15 12:55 | 2023-05-15 17:19 | 40 | 4:24 | P | DESGANCHE | 2X80 EN C/L 2X65 EN OTRO C/L DESGANCHE | S23051500105 | New_Event | Vegetation Contact | Include | Include | Vegetation | 264 | 2023-05-15 | 10560 | keep | 0 | May | 2023 | 0.0071924 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-05-15 13:00 | 2023-05-15 15:30 | 35 | 2:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA REQUIERE DESGANCHE | A23051500061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-05-15 | 5250 | keep | 0 | May | 2023 | 0.0035758 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-05-15 13:37 | 2023-05-15 19:51 | 40 | 6:14 | P | NO SE REPORTO CAUSA | 1X40 DE RISER @ TRANSCLOSURE | S23051500121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 374 | 2023-05-15 | 14960 | keep | 0 | May | 2023 | 0.010189 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-15 13:38 | 2023-05-15 13:39 | 713 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | A23051500068 | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-15 | 713 | keep | 0 | May | 2023 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
AGUADILLA | 2023-05-15 13:39 | 2023-05-15 14:40 | 7 | 1:01 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO MASETILLA QUEMADA | A23051500073 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 61 | 2023-05-15 | 427 | keep | 0 | May | 2023 | 0.00029083 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-05-15 13:44 | 2023-05-15 18:32 | 1 | 4:48 | P | NO SE REPORTO CAUSA | 2 X 15 EN BANCO DE XMR | C23051500138 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 288 | 2023-05-15 | 288 | keep | 0 | May | 2023 | 0.00019616 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-15 13:48 | 2023-05-15 17:45 | 6 | 3:57 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23051500159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 237 | 2023-05-15 | 1422 | keep | 0 | May | 2023 | 0.00096852 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-15 13:57 | 2023-05-15 17:50 | 30 | 3:53 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23051500072 | New_Event | Vegetation Contact | Include | Include | Vegetation | 233 | 2023-05-15 | 6990 | keep | 0 | May | 2023 | 0.0047609 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-05-15 14:00 | 2023-05-15 17:20 | 50 | 3:20 | P | PARARRAYOS DEFECTUOSO | 1 X 50 EN CORTE DE LINEA SE RETIRO PARARRAYO CRUZADO | A23051500078 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 200 | 2023-05-15 | 10000 | keep | 0 | May | 2023 | 0.006811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-15 14:10 | 2023-05-15 21:55 | 1960 | 7:45 | P | LINEA DE TRANSMISION 38KV | SE ENERGIZO LA SUBESTACION Y SE CERRO POR CONTROL 100% EN SERVICIO AVERIA EN TRAMO SOTERRADO 12631B - PUENTES. | C23051500009 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 465 | 2023-05-15 | 911400 | keep | 0 | May | 2023 | 0.62075 | 0.0013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 1960
SAN JUAN | 2023-05-15 14:58 | 2023-05-15 19:04 | 10 | 4:06 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO DE RISER @ T-3 PARA CERRAR PUENTE PRIMARIO (RADIAL) - EN LA SALIDA HACIA LA CARGA | S23051500144 | New_Event | Primary Wire Break | Include | Include | Equipment | 246 | 2023-05-15 | 2460 | keep | 0 | May | 2023 | 0.0016755 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-15 14:59 | 2023-05-15 15:01 | 726 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23051500146 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-15 | 1452 | keep | 0 | May | 2023 | 0.00098895 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
BAYAMON | 2023-05-15 15:05 | 2023-05-15 15:40 | 1497 | 0:35 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE LEVANTO CONDUCTOR PRIMARIO BY-230515-01 | S23051500149 | New_Event | Primary Wire Break | Include | Include | Equipment | 35 | 2023-05-15 | 52395 | keep | 0 | May | 2023 | 0.035686 | 0.0010196 | Sustained | FALSE | FALSE | Not_TMED_Event | 1497
CANOVANAS | 2023-05-15 15:12 | 2023-05-15 15:15 | 1615 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23051500154 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-15 | 4845 | keep | 0 | May | 2023 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-05-15 15:28 | 2023-05-15 20:13 | 25 | 4:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA SE DEJO FUERA 7 CLIENTES CON PUENTES ABIERTOS EN LA SECUNDARIA. | R23051300187 | New_Event | Secondary Wire Break | Include | Include | Equipment | 285 | 2023-05-15 | 7125 | keep | 0 | May | 2023 | 0.0048528 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-15 15:31 | 2023-05-16 00:19 | 15 | 8:48 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | B23051500154 | New_Event | Animals | Include | Include | Wildlife | 528 | 2023-05-15 | 7920 | keep | 0 | May | 2023 | 0.0053943 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-05-15 15:35 | 2023-05-15 16:38 | 35 | 1:03 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23051500085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-05-15 | 2205 | keep | 0 | May | 2023 | 0.0015018 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
CAGUAS | 2023-05-15 15:50 | 2023-05-16 08:20 | 1 | 16:30 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23051500187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 990 | 2023-05-15 | 990 | keep | 0 | May | 2023 | 0.00067428 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-15 16:03 | 2023-05-15 18:48 | 1 | 2:45 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | C23051500193 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 165 | 2023-05-15 | 165 | keep | 0 | May | 2023 | 0.00011238 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-15 16:09 | 2023-05-15 17:41 | 18 | 1:32 | P | ANIMAL | 1 X 20 EN RISER CRUCE X AVE | R23051500088 | New_Event | Animals | Include | Include | Wildlife | 92 | 2023-05-15 | 1656 | keep | 0 | May | 2023 | 0.0011279 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-05-15 16:11 | 2023-05-16 09:13 | 5 | 17:02 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23051500206 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1022 | 2023-05-15 | 5110 | keep | 0 | May | 2023 | 0.0034804 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-05-15 16:14 | 2023-05-15 16:58 | 25 | 0:44 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23051500094 | New_Event | Animals | Include | Include | Wildlife | 44 | 2023-05-15 | 1100 | keep | 0 | May | 2023 | 0.0007492 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-05-15 16:20 | 2023-05-15 18:38 | 40 | 2:18 | P | DESGANCHE | DESGANCHE 1 X 80 EN CORTE DE LINEA | P23051500096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-05-15 | 5520 | keep | 0 | May | 2023 | 0.0037596 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-05-15 16:22 | 2023-05-15 21:00 | 68 | 4:38 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN SU - 22 N/O DEL T - 60 @ T - 61 QUE ESTABA EN CALENTAMIENTO AVERIADO | C23051500204 | New_Event | UG Cable Fault | Include | Include | Equipment | 278 | 2023-05-15 | 18904 | keep | 0 | May | 2023 | 0.012875 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
BAYAMON | 2023-05-15 16:50 | 2023-05-15 16:55 | 959 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1904-07 | S23051500172 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-05-15 | 4795 | keep | 0 | May | 2023 | 0.0032659 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-05-15 16:50 | 2023-05-15 16:53 | 1297 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1904-06 SE CERRO POR SCADA LLEVA LA CARGA DEL 1901-02 Y 1901-03 | S23051500171 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-15 | 3891 | keep | 0 | May | 2023 | 0.0026501 | 0.00088338 | Momentary | FALSE | FALSE | Not_TMED_Event | 1297
BAYAMON | 2023-05-15 16:50 | 2023-05-15 16:53 | 451 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1904-06 SE CERRO POR SCADA LLEVA LA CARGA DEL 1901-02 Y 1901-03 | S23051500171 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-15 | 1353 | keep | 0 | May | 2023 | 0.00092152 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
BAYAMON | 2023-05-15 16:50 | 2023-05-15 16:55 | 1264 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1904-07 | S23051500172 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-05-15 | 6320 | keep | 0 | May | 2023 | 0.0043045 | 0.0008609 | Momentary | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-05-15 16:50 | 2023-05-15 20:32 | 2435 | 3:42 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DEL INTERRUPTOR 1909-08 SE SECCIONALIZO TRAMO Y SE REPARO PUENTE ABIERTO EN LA SALIDA DEL 1907-05 BY-230515-02 | S23051500288 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-05-15 | 540570 | keep | 0 | May | 2023 | 0.36818 | 0.0016585 | Sustained | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-15 16:50 | 2023-05-15 16:51 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR LLEVA LA CARGA DEL 1907-05 | S23051500181 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-15 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
HUMACAO | 2023-05-15 16:56 | 2023-05-15 18:33 | 183 | 1:37 | P | CAUSAS EXTERNAS | SE SECCIONALIZO EL ALIMENTADOR 90% EN SERVICIO\ CG-23051500205 | C23051500019 | New_Event | Damage From Public | Include | Include | Public | 97 | 2023-05-15 | 17751 | keep | 0 | May | 2023 | 0.01209 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
AGUADILLA | 2023-05-15 17:00 | 2023-05-15 17:43 | 3 | 0:43 | P | DESGANCHE | 2 X 30 Y 1 X 40 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051500188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 43 | 2023-05-15 | 129 | keep | 0 | May | 2023 | 8.7861e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-05-15 17:19 | 2023-05-15 19:35 | 20 | 2:16 | P | SECUNDARIA/DESGANCHE | ABRIO XMR PARA DESGANCHAR Y REPARAR BAJANTE SECUNDARIO | C23051500240 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 136 | 2023-05-15 | 2720 | keep | 0 | May | 2023 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-15 17:29 | 2023-05-15 17:30 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305150000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 2402 | keep | 0 | May | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
ARECIBO | 2023-05-15 17:41 | 2023-05-15 19:15 | 150 | 1:34 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23051500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 94 | 2023-05-15 | 14100 | keep | 0 | May | 2023 | 0.0096034 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-05-15 17:43 | 2023-05-15 18:20 | 65 | 0:37 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23051500094 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-05-15 | 2405 | keep | 0 | May | 2023 | 0.001638 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2023-05-15 17:51 | 2023-05-15 20:25 | 30 | 2:34 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE Y SE REEMPLAZO PORTAFUSIBLE | R23051500095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-05-15 | 4620 | keep | 0 | May | 2023 | 0.0031467 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-05-15 18:00 | 2023-05-15 20:20 | 300 | 2:20 | P | CAUSAS EXTERNAS | SE ABRIO CORTE DE LINEA PARA RETIRAR TENSOR SOBRE CAJA DE CORTE DE LINEA | A23051500092 | New_Event | Damage From Public | Include | Include | Public | 140 | 2023-05-15 | 42000 | keep | 0 | May | 2023 | 0.028606 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2023-05-15 18:33 | 2023-05-15 19:07 | 1835 | 0:34 | T | CAUSAS EXTERNAS | DISPARO SE VERIFICO PERSONAL, REALIZANDO OPERACIONES PARA RETIRAR TENZOR SOBRE LA LINEA 5400 | C23051500229 | Additional_clients | Damage From Public | Include | Include | Public | 34 | 2023-05-15 | 62390 | keep | 0 | May | 2023 | 0.042494 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-15 19:03 | 2023-05-15 20:10 | 10 | 1:07 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR FUSIBLE PODRIDO | A23051500120 | New_Event | Other Causes | Include | Include | Other | 67 | 2023-05-15 | 670 | keep | 0 | May | 2023 | 0.00045633 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-15 19:07 | 2023-05-15 19:39 | 183 | 0:32 | P | CAUSAS EXTERNAS | SE RETIRO TENSOR SOBRE LA LINEA 5400 CERCA HACIA LA DE DISTRIBUCION | C23051500230 | Partial_restoration | Damage From Public | Include | Include | Public | 32 | 2023-05-15 | 5856 | keep | 0 | May | 2023 | 0.0039885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-15 19:26 | 2023-05-16 09:50 | 50 | 14:24 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23051500130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 864 | 2023-05-15 | 43200 | keep | 0 | May | 2023 | 0.029423 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-15 19:39 | 2023-05-16 14:35 | 1 | 18:56 | P | CAUSAS EXTERNAS | SE CERRO PUENTE ABIERTO EN TRAMO MONOFASICO | C23051500231 | Partial_restoration | Damage From Public | Include | Include | Public | 1136 | 2023-05-15 | 1136 | keep | 0 | May | 2023 | 0.00077372 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-15 19:53 | 2023-05-15 23:00 | 75 | 3:07 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER NO SE ENCONTRO CAUSA | P23051500122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 187 | 2023-05-15 | 14025 | keep | 0 | May | 2023 | 0.0095524 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-05-15 20:20 | 2023-05-15 22:25 | 1200 | 2:05 | P | NO SE REPORTO CAUSA | 1 X 140 EN CONVERTIDOR NO SE REPORTO CAUSA | M23051500208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2023-05-15 | 150000 | keep | 0 | May | 2023 | 0.10216 | 0.00081731 | Sustained | FALSE | FALSE | Not_TMED_Event | 1200
CANOVANAS | 2023-05-15 20:25 | 2023-05-15 21:20 | 15 | 0:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO CAJA PRIMARIA | R23051500105 | New_Event | Cutout Failure | Include | Include | Equipment | 55 | 2023-05-15 | 825 | keep | 0 | May | 2023 | 0.0005619 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-05-15 21:00 | 2023-05-15 23:50 | 400 | 2:50 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23051500250 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 170 | 2023-05-15 | 68000 | keep | 0 | May | 2023 | 0.046314 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
MAYAGÃœEZ | 2023-05-15 21:20 | 2023-05-16 12:24 | 10 | 15:04 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | M23051500244 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 904 | 2023-05-15 | 9040 | keep | 0 | May | 2023 | 0.0061571 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-15 22:23 | 2023-05-16 17:15 | 4 | 18:52 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR Y DESGANCHE SECUNDARIO | B23051500223 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1132 | 2023-05-15 | 4528 | keep | 0 | May | 2023 | 0.003084 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-15 22:35 | 2023-05-16 12:24 | 16 | 13:49 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23051500345 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 829 | 2023-05-15 | 13264 | keep | 0 | May | 2023 | 0.0090341 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-05-15 23:29 | 2023-05-16 07:25 | 214 | 7:56 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23051500258 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 476 | 2023-05-15 | 101864 | keep | 0 | May | 2023 | 0.069379 | 0.00014575 | Sustained | FALSE | FALSE | Not_TMED_Event | 214
MAYAGÃœEZ | 2023-05-15 23:37 | 2023-05-15 23:38 | 1036 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051500281 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-15 | 1036 | keep | 0 | May | 2023 | 0.00070561 | 0.00070561 | Momentary | FALSE | FALSE | Not_TMED_Event | 1036
SAN JUAN | 2023-05-16 01:00 | 2023-05-16 13:44 | 69 | 12:44 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23051600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 764 | 2023-05-16 | 52716 | keep | 0 | May | 2023 | 0.035905 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
VEGA BAJA | 2023-05-16 01:06 | 2023-05-16 07:47 | 85 | 6:41 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23051600003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 401 | 2023-05-16 | 34085 | keep | 0 | May | 2023 | 0.023215 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-05-16 02:23 | 2023-05-16 07:56 | 37 | 5:33 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23051600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 333 | 2023-05-16 | 12321 | keep | 0 | May | 2023 | 0.0083918 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-05-16 02:33 | 2023-05-16 02:35 | 271 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKE CERRADO POR SCADA | S2305170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-16 | 542 | keep | 0 | May | 2023 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
CANOVANAS | 2023-05-16 04:20 | 2023-05-16 04:21 | 3464 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | R2305160000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-16 | 3464 | keep | 0 | May | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
CANOVANAS | 2023-05-16 04:21 | 2023-05-16 09:28 | 76 | 5:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN C/L REMPLAZO CAJA QUEMADA | R23051600004 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 307 | 2023-05-16 | 23332 | keep | 0 | May | 2023 | 0.015891 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
CAGUAS | 2023-05-16 04:28 | 2023-05-16 10:37 | 156 | 6:09 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23051600005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 369 | 2023-05-16 | 57564 | keep | 0 | May | 2023 | 0.039207 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
HUMACAO | 2023-05-16 05:58 | 2023-05-16 11:24 | 1 | 5:26 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23051500241 | New_Event | Vegetation Contact | Include | Include | Vegetation | 326 | 2023-05-16 | 326 | keep | 0 | May | 2023 | 0.00022204 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-16 06:04 | 2023-05-16 13:10 | 100 | 7:06 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M23051600004 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 426 | 2023-05-16 | 42600 | keep | 0 | May | 2023 | 0.029015 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-16 06:21 | 2023-05-16 06:23 | 1825 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO SU CARGA POR 1118-09 | S23051600011 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-16 | 3650 | keep | 0 | May | 2023 | 0.002486 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-05-16 06:21 | 2023-05-16 06:23 | 4398 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 1118-08 | S23051600011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-16 | 8796 | keep | 0 | May | 2023 | 0.0059909 | 0.0029955 | Momentary | FALSE | FALSE | Not_TMED_Event | 4398
BAYAMON | 2023-05-16 06:32 | 2023-05-16 09:57 | 20 | 3:25 | P | DESGANCHE | 1 X 50 C/L Y DESGANCHE | S23051600014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 205 | 2023-05-16 | 4100 | keep | 0 | May | 2023 | 0.0027925 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-05-16 06:35 | 2023-05-16 11:42 | 15 | 5:07 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23051600008 | New_Event | Animals | Include | Include | Wildlife | 307 | 2023-05-16 | 4605 | keep | 0 | May | 2023 | 0.0031364 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-16 06:36 | 2023-05-16 12:35 | 30 | 5:59 | P | ANIMAL | 1 X 25 EN CORTE DE LINEA AVE CRUZO LINEAS | A23051600009 | New_Event | Animals | Include | Include | Wildlife | 359 | 2023-05-16 | 10770 | keep | 0 | May | 2023 | 0.0073354 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-05-16 06:46 | 2023-05-16 11:28 | 20 | 4:42 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R23051600021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 282 | 2023-05-16 | 5640 | keep | 0 | May | 2023 | 0.0038414 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-16 06:52 | 2023-05-16 08:49 | 13 | 1:57 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23051600031 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-05-16 | 1521 | keep | 0 | May | 2023 | 0.0010359 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CAGUAS | 2023-05-16 06:59 | 2023-05-16 11:32 | 59 | 4:33 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23051600015 | New_Event | Animals | Include | Include | Wildlife | 273 | 2023-05-16 | 16107 | keep | 0 | May | 2023 | 0.01097 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
GUAYAMA | 2023-05-16 07:00 | 2023-05-16 07:01 | 1093 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P23051600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1093 | keep | 0 | May | 2023 | 0.00074444 | 0.00074444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1093
GUAYAMA | 2023-05-16 07:00 | 2023-05-16 07:01 | 1067 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P23051600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1067 | keep | 0 | May | 2023 | 0.00072673 | 0.00072673 | Momentary | FALSE | FALSE | Not_TMED_Event | 1067
GUAYAMA | 2023-05-16 07:00 | 2023-05-16 07:01 | 836 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P23051600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 836 | keep | 0 | May | 2023 | 0.0005694 | 0.0005694 | Momentary | FALSE | FALSE | Not_TMED_Event | 836
GUAYAMA | 2023-05-16 07:00 | 2023-05-16 07:01 | 1339 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P23051600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1339 | keep | 0 | May | 2023 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
GUAYAMA | 2023-05-16 07:00 | 2023-05-16 07:01 | 1295 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P23051600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1295 | keep | 0 | May | 2023 | 0.00088202 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
GUAYAMA | 2023-05-16 07:00 | 2023-05-16 07:01 | 978 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P23051600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 978 | keep | 0 | May | 2023 | 0.00066611 | 0.00066611 | Momentary | FALSE | FALSE | Not_TMED_Event | 978
GUAYAMA | 2023-05-16 07:00 | 2023-05-16 07:01 | 1730 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 200 | P23051600015 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1730 | keep | 0 | May | 2023 | 0.0011783 | 0.0011783 | Momentary | FALSE | FALSE | Not_TMED_Event | 1730
AGUADILLA | 2023-05-16 07:01 | 2023-05-16 07:03 | 1287 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CON RECIERRE EN ON SE CERRO POR CONTROL SCADA | M23051600007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-16 | 2574 | keep | 0 | May | 2023 | 0.0017531 | 0.00087657 | Momentary | FALSE | FALSE | Not_TMED_Event | 1287
SAN JUAN | 2023-05-16 07:15 | 2023-05-16 10:30 | 53 | 3:15 | P | NO SE REPORTO CAUSA | 1 X 50 EN PROVISIONAL NO CAUSA | S23051600018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 195 | 2023-05-16 | 10335 | keep | 0 | May | 2023 | 0.0070391 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
CAGUAS | 2023-05-16 07:50 | 2023-05-16 14:21 | 1 | 6:31 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | C23051600034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 391 | 2023-05-16 | 391 | keep | 0 | May | 2023 | 0.00026631 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-16 07:53 | 2023-05-16 08:54 | 69 | 1:01 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23051600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 61 | 2023-05-16 | 4209 | keep | 0 | May | 2023 | 0.0028667 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
VEGA BAJA | 2023-05-16 07:56 | 2023-05-16 10:00 | 11 | 2:04 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23051600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-05-16 | 1364 | keep | 0 | May | 2023 | 0.00092901 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-05-16 07:56 | 2023-05-16 10:00 | 11 | 2:04 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23051600045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-05-16 | 1364 | keep | 0 | May | 2023 | 0.00092901 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-05-16 07:59 | 2023-05-16 17:19 | 30 | 9:20 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23051600037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 560 | 2023-05-16 | 16800 | keep | 0 | May | 2023 | 0.011442 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-05-16 08:13 | 2023-05-16 08:14 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23051600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 179 | keep | 0 | May | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
YAUCO | 2023-05-16 08:20 | 2023-05-16 10:15 | 12 | 1:55 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE BUSHING SECUNDARIOS | P23051600021 | New_Event | Service Transformer Failure | Include | Include | Equipment | 115 | 2023-05-16 | 1380 | keep | 0 | May | 2023 | 0.00093991 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-16 08:23 | 2023-05-16 14:03 | 6 | 5:40 | P | NO SE REPORTO CAUSA | 1 X 20 EN XMR | S23051600043 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 340 | 2023-05-16 | 2040 | keep | 0 | May | 2023 | 0.0013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-05-16 08:29 | 2023-05-16 08:32 | 5668 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | R23061600036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-16 | 17004 | keep | 0 | May | 2023 | 0.011581 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
SAN JUAN | 2023-05-16 08:30 | 2023-05-16 14:48 | 1 | 6:18 | P | PROBLEMA DEL CLIENTE | 1 X 25 EN RISER SE ORIENTO CLIENTE MANTENIMIENTO A SUBEST. | S23051600044 | New_Event | Customer-Related Interruption | Include | Include | Public | 378 | 2023-05-16 | 378 | keep | 0 | May | 2023 | 0.00025745 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-16 08:35 | 2023-05-16 09:53 | 1 | 1:18 | P | NO SE REPORTO CAUSA | CERRO CAJA DE RISER QUE SE ABRIO SIN RAZON | R23051600037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 78 | 2023-05-16 | 78 | keep | 0 | May | 2023 | 5.3125e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-16 08:39 | 2023-05-16 09:50 | 1 | 1:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE AVERIADO | M23051600025 | New_Event | Cutout Failure | Include | Include | Equipment | 71 | 2023-05-16 | 71 | keep | 0 | May | 2023 | 4.8358e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-16 08:56 | 2023-05-16 19:40 | 10 | 10:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | S23051600047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 644 | 2023-05-16 | 6440 | keep | 0 | May | 2023 | 0.0043863 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-16 08:58 | 2023-05-16 10:46 | 1 | 1:48 | P | OTRAS CAUSAS | 1 NX DE 65 AMP. 1 SUM-25 MEDICION EN MAL ESTADO | S23051600048 | New_Event | Other Causes | Include | Include | Other | 108 | 2023-05-16 | 108 | keep | 0 | May | 2023 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-16 08:59 | 2023-05-16 10:00 | 2 | 1:01 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO Y SE CERRO C/L EVENTO TRANSFERIDO DE SAN JUAN | S23051600049 | New_Event | Primary Wire Break | Include | Include | Equipment | 61 | 2023-05-16 | 122 | keep | 0 | May | 2023 | 8.3094e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-05-16 09:00 | 2023-05-16 09:48 | 11 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA | C23051500228 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2023-05-16 | 528 | keep | 0 | May | 2023 | 0.00035962 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
UTUADO | 2023-05-16 09:04 | 2023-05-16 15:20 | 15 | 6:16 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL SOBRE LINEAS PRIMARIAS | A23051600024 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 376 | 2023-05-16 | 5640 | keep | 0 | May | 2023 | 0.0038414 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-16 09:13 | 2023-05-16 11:24 | 5 | 2:11 | P | DESGANCHE | 1 X 20 EN XMR Y DESGANCHE | S23051600051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 131 | 2023-05-16 | 655 | keep | 0 | May | 2023 | 0.00044612 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-05-16 09:16 | 2023-05-16 11:00 | 1 | 1:44 | P | OTRAS CAUSAS | 1 X 50 EN RISER CORROSION DEL FUSIBLE | A23051600028 | New_Event | Other Causes | Include | Include | Other | 104 | 2023-05-16 | 104 | keep | 0 | May | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-16 09:20 | 2023-05-16 09:35 | 6 | 0:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | A23051600029 | New_Event | Secondary Wire Break | Include | Include | Equipment | 15 | 2023-05-16 | 90 | keep | 0 | May | 2023 | 6.1299e-05 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-16 09:34 | 2023-05-16 10:00 | 5 | 0:26 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO XMR Y SE RETEZO LINEA SECUNDARIA | B23051600065 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 26 | 2023-05-16 | 130 | keep | 0 | May | 2023 | 8.8542e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-05-16 09:35 | 2023-05-16 16:50 | 5 | 7:15 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA PODER INCAR POSTE PRIMARIO | A23051600027 | New_Event | Primary Pole Failure | Include | Include | Equipment | 435 | 2023-05-16 | 2175 | keep | 0 | May | 2023 | 0.0014814 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-05-16 09:54 | 2023-05-16 13:07 | 34 | 3:13 | P | SECUNDARIA/DESGANCHE | 1 X 15 XMR DESGANCHE DE ENREDADERA | C23051600074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 193 | 2023-05-16 | 6562 | keep | 0 | May | 2023 | 0.0044693 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
CANOVANAS | 2023-05-16 10:12 | 2023-05-16 10:15 | 1745 | 0:03 | P | EXCAVACIONES | DISPARO DE INTERRUPTOR CERRADO X CONTROL 15% X 1646-03 | R23051600047 | New_Event | Excavation | Include | Include | Public | 3 | 2023-05-16 | 5235 | keep | 0 | May | 2023 | 0.0035655 | 0.0011885 | Momentary | FALSE | FALSE | Not_TMED_Event | 1745
CANOVANAS | 2023-05-16 10:15 | 2023-05-16 11:27 | 206 | 1:12 | P | EXCAVACIONES | SE SECCIONALIZO EL SU-6B CABLE AVERIADO POR EXCAVADORA Y SE CERRO N/O | R23051600049 | 1st_after_momentary | Excavation | Include | Include | Public | 72 | 2023-05-16 | 14832 | keep | 0 | May | 2023 | 0.010102 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
VEGA BAJA | 2023-05-16 10:20 | 2023-05-16 14:30 | 200 | 4:10 | P | DESGANCHE | 1 X 30 Y 2 X 80 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051600040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 250 | 2023-05-16 | 50000 | keep | 0 | May | 2023 | 0.034055 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-05-16 10:25 | 2023-05-16 10:31 | 362 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 90% POR 1620-01 | S23051600000 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-16 | 2172 | keep | 0 | May | 2023 | 0.0014793 | 0.00024656 | Sustained | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-05-16 10:25 | 2023-05-16 10:31 | 2230 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 60% POR 1620-01 | S23051600000 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-16 | 13380 | keep | 0 | May | 2023 | 0.0091131 | 0.0015188 | Sustained | FALSE | FALSE | Not_TMED_Event | 2230
SAN JUAN | 2023-05-16 10:28 | 2023-05-16 10:31 | 36 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 90% DEL 1336-10 Y LLEVA 60% DEL 1620-02 | S23051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-16 | 108 | keep | 0 | May | 2023 | 7.3558e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2023-05-16 10:32 | 2023-05-16 13:30 | 8 | 2:58 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23051600043 | New_Event | Cutout Failure | Include | Include | Equipment | 178 | 2023-05-16 | 1424 | keep | 0 | May | 2023 | 0.00096988 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-16 10:35 | 2023-05-16 11:30 | 10 | 0:55 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS (RELACIONADO A EVENTO M23051500117) | M23051600063 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 55 | 2023-05-16 | 550 | keep | 0 | May | 2023 | 0.0003746 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-16 10:39 | 2023-05-16 14:30 | 100 | 3:51 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE CERRO PUENTE ABIERTO BY-230516-01 | B23051600115 | New_Event | Primary Wire Break | Include | Include | Equipment | 231 | 2023-05-16 | 23100 | keep | 0 | May | 2023 | 0.015733 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-05-16 10:46 | 2023-05-16 10:47 | 1339 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1339 | keep | 0 | May | 2023 | 0.00091199 | 0.00091199 | Momentary | FALSE | FALSE | Not_TMED_Event | 1339
YAUCO | 2023-05-16 10:46 | 2023-05-16 10:47 | 470 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 470 | keep | 0 | May | 2023 | 0.00032011 | 0.00032011 | Momentary | FALSE | FALSE | Not_TMED_Event | 470
YAUCO | 2023-05-16 10:46 | 2023-05-16 10:47 | 2483 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 2483 | keep | 0 | May | 2023 | 0.0016912 | 0.0016912 | Momentary | FALSE | FALSE | Not_TMED_Event | 2483
YAUCO | 2023-05-16 10:46 | 2023-05-16 10:47 | 2190 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600087 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 2190 | keep | 0 | May | 2023 | 0.0014916 | 0.0014916 | Momentary | FALSE | FALSE | Not_TMED_Event | 2190
YAUCO | 2023-05-16 10:46 | 2023-05-16 10:47 | 3006 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 3006 | keep | 0 | May | 2023 | 0.0020474 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-05-16 10:46 | 2023-05-16 10:47 | 179 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600088 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 179 | keep | 0 | May | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
MAYAGÃœEZ | 2023-05-16 10:46 | 2023-05-16 10:47 | 107 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 107 | keep | 0 | May | 2023 | 7.2877e-05 | 7.2877e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 107
MAYAGÃœEZ | 2023-05-16 10:46 | 2023-05-16 10:47 | 1666 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1666 | keep | 0 | May | 2023 | 0.0011347 | 0.0011347 | Momentary | FALSE | FALSE | Not_TMED_Event | 1666
MAYAGÃœEZ | 2023-05-16 10:46 | 2023-05-16 10:47 | 4387 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600089 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 4387 | keep | 0 | May | 2023 | 0.002988 | 0.002988 | Momentary | FALSE | FALSE | Not_TMED_Event | 4387
MAYAGÃœEZ | 2023-05-16 10:46 | 2023-05-16 10:47 | 3147 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 3147 | keep | 0 | May | 2023 | 0.0021434 | 0.0021434 | Momentary | FALSE | FALSE | Not_TMED_Event | 3147
MAYAGÃœEZ | 2023-05-16 10:46 | 2023-05-16 10:47 | 4304 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 13400 | M23051600090 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 4304 | keep | 0 | May | 2023 | 0.0029314 | 0.0029314 | Momentary | FALSE | FALSE | Not_TMED_Event | 4304
CAGUAS | 2023-05-16 10:57 | 2023-05-16 13:38 | 39 | 2:41 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23051600095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-05-16 | 6279 | keep | 0 | May | 2023 | 0.0042766 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
AGUADILLA | 2023-05-16 10:57 | 2023-05-16 14:30 | 9 | 3:33 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA CRUZADA | M23051600070 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 213 | 2023-05-16 | 1917 | keep | 0 | May | 2023 | 0.0013057 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-05-16 10:59 | 2023-05-16 11:18 | 25 | 0:19 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR | B23051600216 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-05-16 | 475 | keep | 0 | May | 2023 | 0.00032352 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-05-16 11:01 | 2023-05-16 11:11 | 3973 | 0:10 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL | P23051600074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-05-16 | 39730 | keep | 0 | May | 2023 | 0.02706 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
CANOVANAS | 2023-05-16 11:18 | 2023-05-16 13:43 | 1 | 2:25 | P | CONDUCTOR ROTO O ABIERTO | REMPLAZO PUENTE DE CAJA A LINEA NO FUNDIO | R23051600057 | New_Event | Primary Wire Break | Include | Include | Equipment | 145 | 2023-05-16 | 145 | keep | 0 | May | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-16 11:21 | 2023-05-16 18:56 | 18 | 7:35 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23051600076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2023-05-16 | 8190 | keep | 0 | May | 2023 | 0.0055782 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
MAYAGÃœEZ | 2023-05-16 11:30 | 2023-05-16 15:20 | 4 | 3:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA ABIERTA | M23051600081 | New_Event | Secondary Wire Break | Include | Include | Equipment | 230 | 2023-05-16 | 920 | keep | 0 | May | 2023 | 0.00062661 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-05-16 11:34 | 2023-05-16 13:50 | 10 | 2:16 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23051600052 | New_Event | Animals | Include | Include | Wildlife | 136 | 2023-05-16 | 1360 | keep | 0 | May | 2023 | 0.00092629 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-05-16 11:35 | 2023-05-16 12:00 | 12 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZARON CONEXIONES EN BARRA DE PEDESTAL SECUNDARIO | P23051600086 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-16 | 300 | keep | 0 | May | 2023 | 0.00020433 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-16 11:41 | 2023-05-16 16:07 | 10 | 4:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIOXMR TOTAL SE REPARO SECUNDARIA ABIERTA Y SE REPUSO 1 X 40 EN C/L | S23051500074 | New_Event | Secondary Wire Break | Include | Include | Equipment | 266 | 2023-05-16 | 2660 | keep | 0 | May | 2023 | 0.0018117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-16 11:47 | 2023-05-16 13:33 | 145 | 1:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23051600102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-16 | 15370 | keep | 0 | May | 2023 | 0.010468 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
UTUADO | 2023-05-16 11:50 | 2023-05-16 12:45 | 6 | 0:55 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE TRANSFIRIO TRANSFORMADOR A POSTE CONTIGUO | A23051600051 | New_Event | Primary Pole Failure | Include | Include | Equipment | 55 | 2023-05-16 | 330 | keep | 0 | May | 2023 | 0.00022476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-05-16 11:55 | 2023-05-16 12:17 | 1 | 0:22 | P | DESGANCHE | 1 X 65 EN C/L Y 1 X 30 EN RISER DESGANCHE | C23051600104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-05-16 | 22 | keep | 0 | May | 2023 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-16 11:59 | 2023-05-16 13:52 | 8 | 1:53 | P | SECUNDARIA/OTROS | ABRIO XMR Y SE REPARO PEDESTAL SECUNDARIO | C23051600106 | New_Event |  |  |  |  | 113 | 2023-05-16 | 904 | keep | 0 | May | 2023 | 0.00061571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-16 12:03 | 2023-05-16 13:11 | 3 | 1:08 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50 @ 50KVA | B23051500086 | New_Event | Service Transformer Failure | Include | Include | Equipment | 68 | 2023-05-16 | 204 | keep | 0 | May | 2023 | 0.00013894 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-05-16 12:16 | 2023-05-16 18:17 | 10 | 6:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REPARAR SECUNDARIA Y TOMA | S23051600094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 361 | 2023-05-16 | 3610 | keep | 0 | May | 2023 | 0.0024588 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-16 12:28 | 2023-05-16 12:29 | 709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23051600098 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 709 | keep | 0 | May | 2023 | 0.0004829 | 0.0004829 | Momentary | FALSE | FALSE | Not_TMED_Event | 709
CANOVANAS | 2023-05-16 12:30 | 2023-05-16 12:37 | 21 | 0:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR NEUTRAL SECUNDARIO | R23051600058 | New_Event | Secondary Wire Break | Include | Include | Equipment | 7 | 2023-05-16 | 147 | keep | 0 | May | 2023 | 0.00010012 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
FAJARDO | 2023-05-16 12:32 | 2023-05-16 14:08 | 7 | 1:36 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO DE 37.5 KVA X 37.5 KVA | R23051600059 | New_Event | Service Transformer Failure | Include | Include | Equipment | 96 | 2023-05-16 | 672 | keep | 0 | May | 2023 | 0.0004577 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-16 12:47 | 2023-05-16 13:27 | 16 | 0:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | B23051600107 | New_Event | Secondary Wire Break | Include | Include | Equipment | 40 | 2023-05-16 | 640 | keep | 0 | May | 2023 | 0.0004359 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CANOVANAS | 2023-05-16 12:54 | 2023-05-16 14:01 | 1 | 1:07 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER | R23051600064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 67 | 2023-05-16 | 67 | keep | 0 | May | 2023 | 4.5633e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-16 13:04 | 2023-05-16 18:35 | 20 | 5:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA | B23051600113 | New_Event | Primary Wire Break | Include | Include | Equipment | 331 | 2023-05-16 | 6620 | keep | 0 | May | 2023 | 0.0045089 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-16 13:20 | 2023-05-16 14:25 | 6 | 1:05 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DE 50KVA CON DERRAME DE ACEITE | M23051600107 | New_Event | Service Transformer Failure | Include | Include | Equipment | 65 | 2023-05-16 | 390 | keep | 0 | May | 2023 | 0.00026563 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-05-16 13:21 | 2023-05-16 17:05 | 30 | 3:44 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEA | M23051600109 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-05-16 | 6720 | keep | 0 | May | 2023 | 0.004577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-16 13:29 | 2023-05-16 15:13 | 761 | 1:44 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE ABRIO N/O CONTRA 1421-02 QUE TENIA ALAMBRE EN EL PISO | S23051600225 | New_Event | Feeder Load Transferred | Include | Include | Other | 104 | 2023-05-16 | 79144 | keep | 0 | May | 2023 | 0.053905 | 0.00051831 | Sustained | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2023-05-16 13:29 | 2023-05-16 15:20 | 312 | 1:51 | T | CONDUCTOR ARRIADO O CRUZADO | DISPARO SE DESENREDO LINEA CON VARETA DE PISO Y SE CERRO INTERRUPTOR Y DESPUES SE CERRO MACHETE 100% EN SERVICIO | S23051600112 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 111 | 2023-05-16 | 34632 | keep | 0 | May | 2023 | 0.023588 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
SAN JUAN | 2023-05-16 13:29 | 2023-05-16 17:23 | 1498 | 3:54 | T | ALIMENTADOR AMARRADO | SE LEVANTO LINEA PRIMARIA 80% DE 1421-02 Y LLEVA 1421-01 SE NORMALIZO CARGA DEL 1421-02 | S23051600225 | New_Event | Feeder Load Transferred | Include | Include | Other | 234 | 2023-05-16 | 350532 | keep | 0 | May | 2023 | 0.23875 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2023-05-16 13:29 | 2023-05-16 17:23 | 131 | 3:54 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA 80% DE 1421-02 Y LLEVA 1421-01 SE NORMALIZO CARGA DEL 1421-02 | S23051600225 | New_Event | Primary Wire Break | Include | Include | Equipment | 234 | 2023-05-16 | 30654 | keep | 0 | May | 2023 | 0.020878 | 8.9224e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 131
PONCE | 2023-05-16 13:39 | 2023-05-16 16:23 | 150 | 2:44 | P | DESGANCHE | DESGANCHE Y COORDINACION DE FUSIBLES 1 X 80 EN CORTE DE LINEA | P23051600107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-05-16 | 24600 | keep | 0 | May | 2023 | 0.016755 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2023-05-16 13:42 | 2023-05-16 13:43 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051600111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 2113 | keep | 0 | May | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
CANOVANAS | 2023-05-16 13:43 | 2023-05-16 15:42 | 1 | 1:59 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23051600070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-05-16 | 119 | keep | 0 | May | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-16 13:51 | 2023-05-16 13:53 | 1310 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | S2305160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-16 | 2620 | keep | 0 | May | 2023 | 0.0017845 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
CANOVANAS | 2023-05-16 14:03 | 2023-05-16 14:05 | 5668 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR CERRADO X CONTROL | R23051600073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-16 | 11336 | keep | 0 | May | 2023 | 0.0077209 | 0.0038604 | Momentary | FALSE | FALSE | Not_TMED_Event | 5668
VEGA BAJA | 2023-05-16 14:03 | 2023-05-16 16:26 | 100 | 2:23 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051600066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-05-16 | 14300 | keep | 0 | May | 2023 | 0.0097397 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-05-16 14:06 | 2023-05-16 17:50 | 10 | 3:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE PM PARA ELIMINAR PROVISIONAL AEREO YA QUE SE CONSTRUYO TOMA SOTERRADA | P23051600113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 224 | 2023-05-16 | 2240 | keep | 0 | May | 2023 | 0.0015257 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-16 14:16 | 2023-05-16 14:46 | 2 | 0:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR REMPLAZO EL PORTAFUSIBLE | R23051600076 | New_Event | Cutout Failure | Include | Include | Equipment | 30 | 2023-05-16 | 60 | keep | 0 | May | 2023 | 4.0866e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-05-16 14:20 | 2023-05-16 14:43 | 9 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REMEPLAZAR BAJANTES SECUNDARIOS | C23051600100 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-05-16 | 207 | keep | 0 | May | 2023 | 0.00014099 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-05-16 14:31 | 2023-05-16 15:30 | 25 | 0:59 | P | ARBOL SOBRE LINEA | SE ABRE CORTE DE LINEA 2 FUNDIDO PARA RETIRAR ARBOL EN FUEGO CRUZANDO LINEA | S23051600163 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 59 | 2023-05-16 | 1475 | keep | 0 | May | 2023 | 0.0010046 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-05-16 14:51 | 2023-05-16 17:00 | 20 | 2:09 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A23051600072 | New_Event | Animals | Include | Include | Wildlife | 129 | 2023-05-16 | 2580 | keep | 0 | May | 2023 | 0.0017572 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-16 14:54 | 2023-05-16 14:55 | 1105 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 1105 | keep | 0 | May | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-05-16 14:54 | 2023-05-16 15:49 | 3295 | 0:55 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA Y SE CERRO POR SCADA BY-230516-02 | B23051600137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-05-16 | 181225 | keep | 0 | May | 2023 | 0.12343 | 0.0022442 | Sustained | FALSE | FALSE | Not_TMED_Event | 3295
CANOVANAS | 2023-05-16 14:56 | 2023-05-16 16:52 | 100 | 1:56 | P | DESGANCHE | 1 X 80 Y 1 X 40 SMU 20 DESGANCHO Y REPARO TERMINACION | R23051600082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-05-16 | 11600 | keep | 0 | May | 2023 | 0.0079007 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-16 15:13 | 2023-05-16 17:19 | 30 | 2:06 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23051600085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-05-16 | 3780 | keep | 0 | May | 2023 | 0.0025745 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-16 15:23 | 2023-05-16 15:24 | 2234 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | B2305160000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-16 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-05-16 15:24 | 2023-05-16 18:13 | 16 | 2:49 | P | DESGANCHE | 1 X 40 EN C/L SE REALIZO DESGANCHE | B23051600199 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-05-16 | 2704 | keep | 0 | May | 2023 | 0.0018417 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-05-16 15:30 | 2023-05-16 17:24 | 50 | 1:54 | P | ARBOL SOBRE LINEA | 2 X 80 EN CORTE DE LINEA SE RETIRA ARBOL EN FUEGO Y SE CERRO CORTE DE LINEA | S23051600163 | Additional_clients | Vegetation Uprooted Tree | Include | Include | Vegetation | 114 | 2023-05-16 | 5700 | keep | 0 | May | 2023 | 0.0038822 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-16 15:30 | 2023-05-16 16:00 | 8 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTORES SECUNDARIO | B23051600148 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-05-16 | 240 | keep | 0 | May | 2023 | 0.00016346 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-05-16 15:30 | 2023-05-16 18:52 | 30 | 3:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23051600078 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-05-16 | 6060 | keep | 0 | May | 2023 | 0.0041274 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-16 15:42 | 2023-05-16 21:56 | 117 | 6:14 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23051600222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2023-05-16 | 43758 | keep | 0 | May | 2023 | 0.029803 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2023-05-16 15:49 | 2023-05-16 17:00 | 2307 | 1:11 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA Y SE CERRO POR SCADA SE REALIZO DESGANCHE PRIMARIO EN VARIOS PUNTOS BY-230516-02 | B23051600137 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-05-16 | 163797 | keep | 0 | May | 2023 | 0.11156 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-16 15:52 | 2023-05-16 15:53 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2023-05-16 16:05 | 2023-05-17 09:40 | 6 | 17:35 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | C23051600154 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1055 | 2023-05-16 | 6330 | keep | 0 | May | 2023 | 0.0043113 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-05-16 16:11 | 2023-05-16 18:33 | 100 | 2:22 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23051600092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-05-16 | 14200 | keep | 0 | May | 2023 | 0.0096716 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-16 16:23 | 2023-05-16 18:51 | 141 | 2:28 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23051600168 | New_Event | Animals | Include | Include | Wildlife | 148 | 2023-05-16 | 20868 | keep | 0 | May | 2023 | 0.014213 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
BARRANQUITAS | 2023-05-16 16:23 | 2023-05-16 17:19 | 120 | 0:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIMEPO | C23051600163 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 56 | 2023-05-16 | 6720 | keep | 0 | May | 2023 | 0.004577 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-05-16 16:37 | 2023-05-17 16:32 | 5 | 23:55 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 50KVA X 50KVA | B23051600183 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1435 | 2023-05-16 | 7175 | keep | 0 | May | 2023 | 0.0048869 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-16 16:37 | 2023-05-16 18:56 | 14 | 2:19 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23051600184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-16 | 1946 | keep | 0 | May | 2023 | 0.0013254 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2023-05-16 16:44 | 2023-05-16 19:10 | 200 | 2:26 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051600088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-05-16 | 29200 | keep | 0 | May | 2023 | 0.019888 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
HUMACAO | 2023-05-16 16:57 | 2023-05-16 16:58 | 3701 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 VARIOS PUNTOS DE DESGANCHE SEGUN PATRULLAJE AEREO DEL 5/17/2023. | C23051600170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 3701 | keep | 0 | May | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2023-05-16 16:57 | 2023-05-16 16:58 | 989 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 VARIOS PUNTOS DE DESGANCHE SEGUN PATRULLAJE AEREO DEL 5/17/2023. | C23051600170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 989 | keep | 0 | May | 2023 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2023-05-16 16:57 | 2023-05-16 16:58 | 1467 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 5400 VARIOS PUNTOS DE DESGANCHE SEGUN PATRULLAJE AEREO DEL 5/17/2023. | C23051600170 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-16 | 1467 | keep | 0 | May | 2023 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BARRANQUITAS | 2023-05-16 16:57 | 2023-05-16 19:21 | 60 | 2:24 | P | DESGANCHE | 1 X 40 EN C/L DEAGANCHE | C23051600169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-05-16 | 8640 | keep | 0 | May | 2023 | 0.0058847 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-16 17:00 | 2023-05-16 17:09 | 1318 | 0:09 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO AVERIA Y SE CERRO POR SCADA SE REALIZO DESGANCHE PRIMARIO EN VARIOS PUNTOS BY-230516-02 | B23051600137 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 9 | 2023-05-16 | 11862 | keep | 0 | May | 2023 | 0.0080792 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-16 17:11 | 2023-05-16 17:49 | 1 | 0:38 | T | NO SE REPORTO CAUSA | SE VERIFICO EN EL CAMPO BKR. ABIERTO SE BORRARON BANDERAS Y SE CERRO TOTALMENTE QUEDO EN SERVICIO | S23051600000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 38 | 2023-05-16 | 38 | keep | 0 | May | 2023 | 2.5882e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-16 17:11 | 2023-05-16 17:12 | 2402 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 2402 | keep | 0 | May | 2023 | 0.001636 | 0.001636 | Momentary | FALSE | FALSE | Not_TMED_Event | 2402
MAYAGÃœEZ | 2023-05-16 17:17 | 2023-05-16 18:15 | 150 | 0:58 | P | DESGANCHE | 1 X 100 Y 2 X 80 EN DIFERENTES CORTES DE LINEA REQUIERE DESGANCHE | M23051600156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-05-16 | 8700 | keep | 0 | May | 2023 | 0.0059255 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-05-16 17:21 | 2023-05-16 17:22 | 1192 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA POR 7008-05 | M23051600157 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-16 | 1192 | keep | 0 | May | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2023-05-16 17:21 | 2023-05-16 17:22 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051600157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 3041 | keep | 0 | May | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2023-05-16 17:22 | 2023-05-16 18:55 | 20 | 1:33 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23051600167 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 93 | 2023-05-16 | 1860 | keep | 0 | May | 2023 | 0.0012668 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-16 17:27 | 2023-05-16 19:03 | 104 | 1:36 | P | CAUSAS EXTERNAS | SE ABRE MACHETE PARA SECCIONALIZAR TRAMO EN EL PISO CAUSADO POR PERSONAL DE CLARO | S23051600289 | New_Event | Damage From Public | Include | Include | Public | 96 | 2023-05-16 | 9984 | keep | 0 | May | 2023 | 0.0068001 | 7.0834e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 104
PONCE | 2023-05-16 17:30 | 2023-05-16 17:44 | 21 | 0:14 | P | TRANSFORMADOR AVERIADO | SE REPARO BUSHING SECUNDARIO | P23051600135 | New_Event | Service Transformer Failure | Include | Include | Equipment | 14 | 2023-05-16 | 294 | keep | 0 | May | 2023 | 0.00020024 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-05-16 18:12 | 2023-05-17 10:34 | 2 | 16:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S23051600302 | New_Event | Secondary Wire Break | Include | Include | Equipment | 982 | 2023-05-16 | 1964 | keep | 0 | May | 2023 | 0.0013377 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-05-16 18:26 | 2023-05-17 10:22 | 5 | 15:56 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | C23051600185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 956 | 2023-05-16 | 4780 | keep | 0 | May | 2023 | 0.0032556 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-16 18:32 | 2023-05-16 19:29 | 8 | 0:57 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER NO CAUSA | S23051600305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 57 | 2023-05-16 | 456 | keep | 0 | May | 2023 | 0.00031058 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-16 19:03 | 2023-05-16 20:45 | 312 | 1:42 | T | CAUSAS EXTERNAS | SE ABRE MACHETE DE RISER PARA ESTABLECER GOI Y LEVANTAR LINEA PRIMARIA CAUSADO POR PERSONAL DE CLARO | S23051600289 | Additional_clients | Damage From Public | Include | Include | Public | 102 | 2023-05-16 | 31824 | keep | 0 | May | 2023 | 0.021675 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-16 19:07 | 2023-05-16 20:35 | 80 | 1:28 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23051600103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-05-16 | 7040 | keep | 0 | May | 2023 | 0.0047949 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-16 19:16 | 2023-05-16 19:17 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051600192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 853 | keep | 0 | May | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
VEGA BAJA | 2023-05-16 19:18 | 2023-05-17 09:41 | 21 | 14:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO LLUVIAS | B23051600223 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 863 | 2023-05-16 | 18123 | keep | 0 | May | 2023 | 0.012343 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
BAYAMON | 2023-05-16 19:28 | 2023-05-16 22:18 | 8 | 2:50 | P | CABLE SOTERRADO AVERIADO | SE CONSTRUYO PROVISIONAL AEREO PARA ENERGIZARA T-8 | B23051500214 | New_Event | UG Cable Fault | Include | Include | Equipment | 170 | 2023-05-16 | 1360 | keep | 0 | May | 2023 | 0.00092629 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-05-16 19:49 | 2023-05-17 08:12 | 50 | 12:23 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23051600150 | New_Event | Animals | Include | Include | Wildlife | 743 | 2023-05-16 | 37150 | keep | 0 | May | 2023 | 0.025303 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-16 19:55 | 2023-05-16 19:56 | 1261 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305160000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 1261 | keep | 0 | May | 2023 | 0.00085886 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
VEGA BAJA | 2023-05-16 19:56 | 2023-05-17 09:09 | 7 | 13:13 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23051600227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 793 | 2023-05-16 | 5551 | keep | 0 | May | 2023 | 0.0037808 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-05-16 20:04 | 2023-05-17 11:28 | 20 | 15:24 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C23051600196 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 924 | 2023-05-16 | 18480 | keep | 0 | May | 2023 | 0.012587 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-16 20:21 | 2023-05-16 23:40 | 800 | 3:19 | P | PROTECCION DEFECTUOSA | 2 X 200 EN CORTE DE LINEA SE COORDINO FUSIBLES | M23051600193 | New_Event | Protection Miscoordination | Include | Include | Other | 199 | 2023-05-16 | 159200 | keep | 0 | May | 2023 | 0.10843 | 0.00054488 | Sustained | FALSE | FALSE | Not_TMED_Event | 800
AGUADILLA | 2023-05-16 20:48 | 2023-05-16 23:10 | 500 | 2:22 | P | NO SE REPORTO CAUSA | 1 X 140 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | A23051600109 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2023-05-16 | 71000 | keep | 0 | May | 2023 | 0.048358 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2023-05-16 21:04 | 2023-05-17 01:17 | 136 | 4:13 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L Y 1 X 50 RN RISER | C23051600204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2023-05-16 | 34408 | keep | 0 | May | 2023 | 0.023435 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
BARRANQUITAS | 2023-05-16 21:19 | 2023-05-17 09:55 | 8 | 12:36 | P | TRANSFORMADOR AVERIADO | 1 X 20 EN TRANSFORMADOR SE REPARO BUSHING PRIMARIO | C23051600207 | New_Event | Service Transformer Failure | Include | Include | Equipment | 756 | 2023-05-16 | 6048 | keep | 0 | May | 2023 | 0.0041193 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-16 21:22 | 2023-05-17 10:30 | 15 | 13:08 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23051600233 | New_Event | Animals | Include | Include | Wildlife | 788 | 2023-05-16 | 11820 | keep | 0 | May | 2023 | 0.0080505 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-05-16 21:28 | 2023-05-16 21:29 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051600166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-16 | 1746 | keep | 0 | May | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
MAYAGÃœEZ | 2023-05-16 21:31 | 2023-05-17 09:30 | 70 | 11:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23051600229 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 719 | 2023-05-16 | 50330 | keep | 0 | May | 2023 | 0.03428 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BARRANQUITAS | 2023-05-16 21:46 | 2023-05-17 08:30 | 87 | 10:44 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEAS SE RETIRO PENCA DE LA LINEA | C23051600209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2023-05-16 | 56028 | keep | 0 | May | 2023 | 0.03816 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
AGUADILLA | 2023-05-16 22:05 | 2023-05-17 06:09 | 80 | 8:04 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA | A23051600182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 484 | 2023-05-16 | 38720 | keep | 0 | May | 2023 | 0.026372 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-05-16 22:51 | 2023-05-17 11:20 | 267 | 12:29 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN CORTE DE LINEA SE FIJO CONDUCTOR AL CORNED BRAKET | C23051600211 | New_Event | Primary Wire Break | Include | Include | Equipment | 749 | 2023-05-16 | 199983 | keep | 0 | May | 2023 | 0.13621 | 0.00018185 | Sustained | FALSE | FALSE | Not_TMED_Event | 267
BAYAMON | 2023-05-16 23:04 | 2023-05-17 11:31 | 6 | 12:27 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23051600240 | New_Event | Animals | Include | Include | Wildlife | 747 | 2023-05-16 | 4482 | keep | 0 | May | 2023 | 0.0030527 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-05-16 23:12 | 2023-05-17 09:00 | 200 | 9:48 | P | DESGANCHE | SE RETIRO RAMA SE CERRO "TRIPSAVER" | A23051600192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 588 | 2023-05-16 | 117600 | keep | 0 | May | 2023 | 0.080097 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-05-17 00:45 | 2023-05-17 18:22 | 116 | 17:37 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C23051700004 | New_Event | Primary Wire Break | Include | Include | Equipment | 1057 | 2023-05-17 | 122612 | keep | 0 | May | 2023 | 0.08351 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
AGUADILLA | 2023-05-17 01:24 | 2023-05-17 11:43 | 30 | 10:19 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PUENTE PRIMARIO | A23051700001 | New_Event | Primary Wire Break | Include | Include | Equipment | 619 | 2023-05-17 | 18570 | keep | 0 | May | 2023 | 0.012648 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-17 01:39 | 2023-05-17 12:20 | 8 | 10:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C23051700007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 641 | 2023-05-17 | 5128 | keep | 0 | May | 2023 | 0.0034927 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-05-17 01:41 | 2023-05-17 10:20 | 14 | 8:39 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REMPLAZO AISLADOR | P23051700015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 519 | 2023-05-17 | 7266 | keep | 0 | May | 2023 | 0.0049488 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-05-17 02:00 | 2023-05-17 02:01 | 2094 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 50% DE SU CARGA | R23051700002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 2094 | keep | 0 | May | 2023 | 0.0014262 | 0.0014262 | Momentary | FALSE | FALSE | Not_TMED_Event | 2094
SAN JUAN | 2023-05-17 02:08 | 2023-05-17 12:00 | 150 | 9:52 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23051700001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 592 | 2023-05-17 | 88800 | keep | 0 | May | 2023 | 0.060481 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-05-17 03:01 | 2023-05-17 05:51 | 2126 | 2:50 | T | ANIMAL | DISPARO DE INTERRUPTOR SE PATRULLO LA LINEA NO SE ENCONTRO CAUSA SE RETIRO IGUANA SE CERRO POR CONTROL ABRIENDO EL N/O CONTRA EL 2605-01 ERA UN 20% DEL 2605-01 | C23051700008 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-05-17 | 361420 | keep | 0 | May | 2023 | 0.24616 | 0.001448 | Sustained | FALSE | FALSE | Not_TMED_Event | 2126
HUMACAO | 2023-05-17 03:01 | 2023-05-17 06:00 | 490 | 2:59 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 2603-09 SE SECCIONALIZO LA CARGA QUE ESTABA POR EL ALIMENTADOR Y SE NORMALIZO | C23051700008 | New_Event | Feeder Load Transferred | Include | Include | Other | 179 | 2023-05-17 | 87710 | keep | 0 | May | 2023 | 0.059739 | 0.00033374 | Sustained | FALSE | FALSE | Not_TMED_Event | 490
BAYAMON | 2023-05-17 05:24 | 2023-05-17 10:48 | 8 | 5:24 | P | ANIMAL | 1 X 20 EN XMR SE RETIRO CULEBRA | B23051700004 | New_Event | Animals | Include | Include | Wildlife | 324 | 2023-05-17 | 2592 | keep | 0 | May | 2023 | 0.0017654 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-05-17 05:37 | 2023-05-17 05:38 | 2100 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051700016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 2100 | keep | 0 | May | 2023 | 0.0014303 | 0.0014303 | Momentary | FALSE | FALSE | Not_TMED_Event | 2100
CAGUAS | 2023-05-17 05:38 | 2023-05-17 05:41 | 329 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | C23051700010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-17 | 987 | keep | 0 | May | 2023 | 0.00067224 | 0.00022408 | Momentary | FALSE | FALSE | Not_TMED_Event | 329
CAGUAS | 2023-05-17 05:38 | 2023-05-17 05:39 | 1342 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 1342 | keep | 0 | May | 2023 | 0.00091403 | 0.00091403 | Momentary | FALSE | FALSE | Not_TMED_Event | 1342
ARECIBO | 2023-05-17 05:44 | 2023-05-17 11:45 | 90 | 6:01 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23051700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 361 | 2023-05-17 | 32490 | keep | 0 | May | 2023 | 0.022129 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-05-17 06:14 | 2023-05-17 06:16 | 10211 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-17 | 20422 | keep | 0 | May | 2023 | 0.013909 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
GUAYAMA | 2023-05-17 06:24 | 2023-05-17 06:25 | 4132 | 0:01 | T | DESGANCHE | RECIERRE NO CAUSAS | P23051700016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-17 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2023-05-17 06:25 | 2023-05-17 08:55 | 80 | 2:30 | P | DESGANCHE | 1 X 65, 1 X 80 Y 1 140 EN C/LS DESGANCHE | P23051700019 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-05-17 | 12000 | keep | 0 | May | 2023 | 0.0081731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-17 06:27 | 2023-05-17 12:44 | 7 | 6:17 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A TRANSFORMADOR | C23051700014 | New_Event | Primary Wire Break | Include | Include | Equipment | 377 | 2023-05-17 | 2639 | keep | 0 | May | 2023 | 0.0017974 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-17 06:31 | 2023-05-17 06:33 | 3955 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 80% DE SU CARGA | S23051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-17 | 7910 | keep | 0 | May | 2023 | 0.0053875 | 0.0026937 | Momentary | FALSE | FALSE | Not_TMED_Event | 3955
BARRANQUITAS | 2023-05-17 06:32 | 2023-05-17 12:30 | 10 | 5:58 | P | CRUCETA DEFECTUOSA O AVERIADA | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO CRUCETA PARTIDO Y SE INSTALO AISLADOR RIGIDO | C23051700016 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 358 | 2023-05-17 | 3580 | keep | 0 | May | 2023 | 0.0024383 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-17 06:35 | 2023-05-17 12:50 | 2 | 6:15 | P | OTRAS CAUSAS | SE PASO AL MH-1 1303-02 AL 1401-08 TRANSFERENCIA DE CARGA ENTRE SUBESTACIONES QUE NO FASEAN | S23051700089 | New_Event | Other Causes | Include | Include | Other | 375 | 2023-05-17 | 750 | keep | 0 | May | 2023 | 0.00051082 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-05-17 06:38 | 2023-05-17 12:00 | 25 | 5:22 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA SE RETIRO IGUANA SOBRE LINEAS | A23051700017 | New_Event | Animals | Include | Include | Wildlife | 322 | 2023-05-17 | 8050 | keep | 0 | May | 2023 | 0.0054828 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-17 06:43 | 2023-05-17 12:26 | 566 | 5:43 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE ALIMENTADOR POR CONDUCTOR SUELO PARA SECCIONALIZAR ALAMBRE | S23051700017 | New_Event | Primary Wire Break | Include | Include | Equipment | 343 | 2023-05-17 | 194138 | keep | 0 | May | 2023 | 0.13223 | 0.0003855 | Sustained | FALSE | FALSE | Not_TMED_Event | 566
CAGUAS | 2023-05-17 06:58 | 2023-05-17 06:59 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23051700018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 1307 | keep | 0 | May | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
AGUADILLA | 2023-05-17 07:55 | 2023-05-17 12:50 | 30 | 4:55 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051700012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2023-05-17 | 8850 | keep | 0 | May | 2023 | 0.0060277 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-17 07:55 | 2023-05-17 13:04 | 15 | 5:09 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23051700017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2023-05-17 | 4635 | keep | 0 | May | 2023 | 0.0031569 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-05-17 08:00 | 2023-05-17 11:18 | 6 | 3:18 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23051700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2023-05-17 | 1188 | keep | 0 | May | 2023 | 0.00080914 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-17 08:05 | 2023-05-17 19:12 | 45 | 11:07 | P | DESGANCHE | SE ABRIO CORTE DE LINEA PARA RETIRAR PALMA Y SE CERRO CORTE DE LINEA | S23051700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 667 | 2023-05-17 | 30015 | keep | 0 | May | 2023 | 0.020443 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-05-17 08:10 | 2023-05-17 12:40 | 15 | 4:30 | P | ANIMAL | 1 X 65 EN RISER CRUCE POR AVE | B23051700021 | New_Event | Animals | Include | Include | Wildlife | 270 | 2023-05-17 | 4050 | keep | 0 | May | 2023 | 0.0027584 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-17 08:16 | 2023-05-17 09:50 | 30 | 1:34 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23051700007 | New_Event | Animals | Include | Include | Wildlife | 94 | 2023-05-17 | 2820 | keep | 0 | May | 2023 | 0.0019207 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-05-17 08:25 | 2023-05-17 10:00 | 60 | 1:35 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS REQUIERE DESGANCHE | A23051700040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-05-17 | 5700 | keep | 0 | May | 2023 | 0.0038822 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-05-17 08:26 | 2023-05-17 10:47 | 32 | 2:21 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23051700024 | New_Event | Animals | Include | Include | Wildlife | 141 | 2023-05-17 | 4512 | keep | 0 | May | 2023 | 0.0030731 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2023-05-17 08:39 | 2023-05-17 08:40 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 4133 | keep | 0 | May | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
BAYAMON | 2023-05-17 08:51 | 2023-05-17 11:43 | 100 | 2:52 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | B23051700032 | New_Event | Animals | Include | Include | Wildlife | 172 | 2023-05-17 | 17200 | keep | 0 | May | 2023 | 0.011715 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-05-17 08:51 | 2023-05-17 11:50 | 13 | 2:59 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO ENRREDADERA SOBRE LINEAS | A23051700055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-05-17 | 2327 | keep | 0 | May | 2023 | 0.0015849 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2023-05-17 09:04 | 2023-05-17 11:57 | 6 | 2:53 | P | DESGANCHE | 1 X 10 Y DESGANCHE | R23051700014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-05-17 | 1038 | keep | 0 | May | 2023 | 0.00070698 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-17 09:07 | 2023-05-17 13:25 | 14 | 4:18 | P | NO SE REPORTO CAUSA | SE REPUSO 1X30 EN AEREO PROVISIONAL | B23051700034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2023-05-17 | 3612 | keep | 0 | May | 2023 | 0.0024601 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-05-17 09:12 | 2023-05-17 14:48 | 8 | 5:36 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO BAJANTE PRIMARIO DE CAJA A TRANSFORMADOR QUEMADO | C23051700055 | New_Event | Primary Wire Break | Include | Include | Equipment | 336 | 2023-05-17 | 2688 | keep | 0 | May | 2023 | 0.0018308 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-17 09:30 | 2023-05-17 14:02 | 5 | 4:32 | P | ANIMAL | 1 X 20 EN XMR CRUCE POR AVE | B23051700040 | New_Event | Animals | Include | Include | Wildlife | 272 | 2023-05-17 | 1360 | keep | 0 | May | 2023 | 0.00092629 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-17 09:36 | 2023-05-17 09:38 | 1746 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23051700041 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-17 | 3492 | keep | 0 | May | 2023 | 0.0023784 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2023-05-17 09:38 | 2023-05-17 11:44 | 1 | 2:06 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE DE LINEA A CAJA | B23051700044 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 126 | 2023-05-17 | 126 | keep | 0 | May | 2023 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-17 09:42 | 2023-05-17 11:00 | 10 | 1:18 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN C/L Y SE ELIMINO BAJANTE DE LINEA A CAJA VACANTE | R23051700020 | New_Event | Primary Wire Break | Include | Include | Equipment | 78 | 2023-05-17 | 780 | keep | 0 | May | 2023 | 0.00053125 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-05-17 09:42 | 2023-05-17 15:30 | 75 | 5:48 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P23051700050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2023-05-17 | 26100 | keep | 0 | May | 2023 | 0.017777 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-05-17 09:54 | 2023-05-17 12:19 | 215 | 2:25 | T | CABLE SOTERRADO AVERIADO | DISPARO PROBO MALO CON RISER ABIERTO LLEVA 1107-04 Y 5 SE PASARON CARGAS AL 1100-01 CERRANDO N/O FTE. SUBESTACION | S23051700094 | New_Event | UG Cable Fault | Include | Include | Equipment | 145 | 2023-05-17 | 31175 | keep | 0 | May | 2023 | 0.021233 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-05-17 09:54 | 2023-05-17 12:19 | 76 | 2:25 | T | ALIMENTADOR AMARRADO | DISPARO PROBO MALO CON RISER ABIERTO LLEVA 1107-04 Y 5 SE PASARON CARGAS AL 1100-01 CERRAOD N/O FTE. SUBESTACION | S23051700094 | New_Event | Feeder Load Transferred | Include | Include | Other | 145 | 2023-05-17 | 11020 | keep | 0 | May | 2023 | 0.0075057 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
SAN JUAN | 2023-05-17 09:54 | 2023-05-17 12:19 | 1079 | 2:25 | T | ALIMENTADOR AMARRADO | DISPARO PROBO MALO CON RISER ABIERTO LLEVA 1107-04 Y 5 SE PASARON CARGAS AL 1100-01 CERRAOD N/O FTE. SUBESTACION | S23051700094 | New_Event | Feeder Load Transferred | Include | Include | Other | 145 | 2023-05-17 | 156455 | keep | 0 | May | 2023 | 0.10656 | 0.0007349 | Sustained | FALSE | FALSE | Not_TMED_Event | 1079
SAN JUAN | 2023-05-17 09:54 | 2023-05-17 09:55 | 2040 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 1115-01 (SPARE) LLEVA 1119-04 25% POR 1117-09 | S2305170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 2040 | keep | 0 | May | 2023 | 0.0013894 | 0.0013894 | Momentary | FALSE | FALSE | Not_TMED_Event | 2040
AGUADILLA | 2023-05-17 10:10 | 2023-05-17 10:55 | 6 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23051700059 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-05-17 | 270 | keep | 0 | May | 2023 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-17 10:19 | 2023-05-17 12:51 | 1570 | 2:32 | T | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO POR SCADA BY-230517-01 | B23051700053 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 152 | 2023-05-17 | 238640 | keep | 0 | May | 2023 | 0.16254 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
PONCE | 2023-05-17 10:21 | 2023-05-17 12:43 | 25 | 2:22 | P | ANIMAL | 1 X 25 EN C/L ANIMAL CRUZO | P23051700060 | New_Event | Animals | Include | Include | Wildlife | 142 | 2023-05-17 | 3550 | keep | 0 | May | 2023 | 0.0024179 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-17 10:32 | 2023-05-17 14:14 | 1 | 3:42 | P | DESGANCHE | 2 X 20 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051700064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-05-17 | 222 | keep | 0 | May | 2023 | 0.0001512 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-17 10:34 | 2023-05-17 11:53 | 15 | 1:19 | P | NO SE REPORTO CAUSA | 1 X 100 EN XMR | R23051700026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 79 | 2023-05-17 | 1185 | keep | 0 | May | 2023 | 0.0008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-17 10:34 | 2023-05-17 16:00 | 135 | 5:26 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | C23051700087 | New_Event | Animals | Include | Include | Wildlife | 326 | 2023-05-17 | 44010 | keep | 0 | May | 2023 | 0.029975 | 9.1948e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 135
CANOVANAS | 2023-05-17 10:47 | 2023-05-17 11:45 | 12 | 0:58 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | R23051700027 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 58 | 2023-05-17 | 696 | keep | 0 | May | 2023 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-05-17 10:55 | 2023-05-17 13:13 | 2 | 2:18 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23051700070 | New_Event | Animals | Include | Include | Wildlife | 138 | 2023-05-17 | 276 | keep | 0 | May | 2023 | 0.00018798 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-17 11:15 | 2023-05-17 13:03 | 5 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23051700133 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2023-05-17 | 540 | keep | 0 | May | 2023 | 0.00036779 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-05-17 11:15 | 2023-05-17 18:23 | 213 | 7:08 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | C23051700106 | New_Event | Primary Wire Break | Include | Include | Equipment | 428 | 2023-05-17 | 91164 | keep | 0 | May | 2023 | 0.062091 | 0.00014507 | Sustained | FALSE | FALSE | Not_TMED_Event | 213
CAGUAS | 2023-05-17 11:16 | 2023-05-17 14:40 | 177 | 3:24 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE CON AVE | C23051700107 | New_Event | Animals | Include | Include | Wildlife | 204 | 2023-05-17 | 36108 | keep | 0 | May | 2023 | 0.024593 | 0.00012055 | Sustained | FALSE | FALSE | Not_TMED_Event | 177
AGUADILLA | 2023-05-17 11:18 | 2023-05-17 19:00 | 8 | 7:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23051700082 | New_Event | Secondary Wire Break | Include | Include | Equipment | 462 | 2023-05-17 | 3696 | keep | 0 | May | 2023 | 0.0025173 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-05-17 11:24 | 2023-05-18 12:58 | 1 | 25:34 | P | ANIMAL | 2 X 30 EN RISER CRUCE X AVE | C23051700111 | New_Event | Animals | Include | Include | Wildlife | 1534 | 2023-05-17 | 1534 | keep | 0 | May | 2023 | 0.0010448 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-17 11:25 | 2023-05-17 12:55 | 8 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23051700079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-05-17 | 720 | keep | 0 | May | 2023 | 0.00049039 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-05-17 11:40 | 2023-05-17 14:18 | 161 | 2:38 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23051700033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 158 | 2023-05-17 | 25438 | keep | 0 | May | 2023 | 0.017326 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
HUMACAO | 2023-05-17 12:09 | 2023-05-17 13:45 | 1 | 1:36 | P | ANIMAL | 1 X 25 EN RISER CRUCE POR AVE | C23051700122 | New_Event | Animals | Include | Include | Wildlife | 96 | 2023-05-17 | 96 | keep | 0 | May | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-17 12:21 | 2023-05-17 14:05 | 35 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23051700116 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-05-17 | 3640 | keep | 0 | May | 2023 | 0.0024792 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-05-17 12:26 | 2023-05-17 12:34 | 1699 | 0:08 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE ALIMENTADOR POR CONDUCTOR SUELO PARA SECCIONALIZAR ALAMBRE | S23051700017 | New_Event | Primary Wire Break | Include | Include | Equipment | 8 | 2023-05-17 | 13592 | keep | 0 | May | 2023 | 0.0092574 | 0.0011572 | Sustained | FALSE | FALSE | Not_TMED_Event | 1699
YAUCO | 2023-05-17 12:30 | 2023-05-17 15:11 | 75 | 2:41 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | P23051700095 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 161 | 2023-05-17 | 12075 | keep | 0 | May | 2023 | 0.0082242 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-05-17 12:34 | 2023-05-17 14:26 | 1609 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA Y SE CERRO MACHETE 100% EN SERVICIO | S23051700017 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 112 | 2023-05-17 | 180208 | keep | 0 | May | 2023 | 0.12274 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-17 12:49 | 2023-05-17 13:26 | 6 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTOR SECUNDARIO | B23051700099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-05-17 | 222 | keep | 0 | May | 2023 | 0.0001512 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-17 12:50 | 2023-05-17 19:28 | 31 | 6:38 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L Y SE CERRO PUENTE DE LINE A CAJA | S23051700171 | New_Event | Primary Wire Break | Include | Include | Equipment | 398 | 2023-05-17 | 12338 | keep | 0 | May | 2023 | 0.0084034 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-05-17 12:51 | 2023-05-17 20:23 | 5 | 7:32 | P | CONDUCTOR ROTO O ABIERTO | SE INSTALO C/L NUEVO Y SE LEVANTO CONDUCTOR PRIMARIO | B23051700101 | New_Event | Primary Wire Break | Include | Include | Equipment | 452 | 2023-05-17 | 2260 | keep | 0 | May | 2023 | 0.0015393 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-05-17 12:57 | 2023-05-17 13:05 | 4 | 0:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23051700013 | New_Event | Secondary Wire Break | Include | Include | Equipment | 8 | 2023-05-17 | 32 | keep | 0 | May | 2023 | 2.1795e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-05-17 13:12 | 2023-05-17 18:34 | 52 | 5:22 | P | DESGANCHE | 3 X 65 EN CORTES DE LINEA DESGANCHE | C23051700140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 322 | 2023-05-17 | 16744 | keep | 0 | May | 2023 | 0.011404 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CAGUAS | 2023-05-17 13:20 | 2023-05-17 13:30 | 968 | 0:10 | P | CAUSAS EXTERNAS | POSTE IMPACTADO POR VEHICULO | C23051700152 | New_Event | Damage From Public | Include | Include | Public | 10 | 2023-05-17 | 9680 | keep | 0 | May | 2023 | 0.006593 | 0.0006593 | Sustained | FALSE | FALSE | Not_TMED_Event | 968
PONCE | 2023-05-17 13:24 | 2023-05-17 14:28 | 9 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23051700116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-05-17 | 576 | keep | 0 | May | 2023 | 0.00039231 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-05-17 13:26 | 2023-05-17 13:28 | 220 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO 98% POR 1303-05 | S23051700192 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-17 | 440 | keep | 0 | May | 2023 | 0.00029968 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-05-17 13:26 | 2023-05-17 13:28 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 98% DEL 1303-04 | S23051700192 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-17 | 1740 | keep | 0 | May | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
CAGUAS | 2023-05-17 13:30 | 2023-05-17 15:42 | 388 | 2:12 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PARTIDO IMPACTADO POR VEHICULO | C23051700152 | Partial_restoration | Damage From Public | Include | Include | Public | 132 | 2023-05-17 | 51216 | keep | 0 | May | 2023 | 0.034883 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-17 13:34 | 2023-05-17 16:14 | 10 | 2:40 | P | SECUNDARIA/DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE SECUNDARIO | S23051700198 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 160 | 2023-05-17 | 1600 | keep | 0 | May | 2023 | 0.0010898 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-17 13:42 | 2023-05-17 14:22 | 9 | 0:40 | P | ANIMAL | 1 X 20 EN TRANSFORMADOR AVE CRUZO FASES | A23051700132 | New_Event | Animals | Include | Include | Wildlife | 40 | 2023-05-17 | 360 | keep | 0 | May | 2023 | 0.00024519 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-05-17 13:46 | 2023-05-17 22:40 | 2 | 8:54 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051700104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 534 | 2023-05-17 | 1068 | keep | 0 | May | 2023 | 0.00072741 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-17 13:54 | 2023-05-17 14:47 | 1 | 0:53 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | B23051700111 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-05-17 | 53 | keep | 0 | May | 2023 | 3.6098e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-17 13:59 | 2023-05-17 14:02 | 271 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | S23051700225 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-17 | 813 | keep | 0 | May | 2023 | 0.00055373 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
VEGA BAJA | 2023-05-17 14:05 | 2023-05-17 15:35 | 22 | 1:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23051700113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 90 | 2023-05-17 | 1980 | keep | 0 | May | 2023 | 0.0013486 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
MAYAGÃœEZ | 2023-05-17 14:25 | 2023-05-17 17:40 | 60 | 3:15 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23051700113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-05-17 | 11700 | keep | 0 | May | 2023 | 0.0079688 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-17 14:27 | 2023-05-17 15:34 | 20 | 1:07 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZO BAJANTES SECUNDARIOS | R23051700056 | New_Event | Secondary Wire Break | Include | Include | Equipment | 67 | 2023-05-17 | 1340 | keep | 0 | May | 2023 | 0.00091267 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-17 14:31 | 2023-05-17 19:00 | 10 | 4:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M23051700118 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 269 | 2023-05-17 | 2690 | keep | 0 | May | 2023 | 0.0018321 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-17 14:31 | 2023-05-17 17:16 | 106 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | B23051700116 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-05-17 | 17490 | keep | 0 | May | 2023 | 0.011912 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
BARRANQUITAS | 2023-05-17 14:36 | 2023-05-17 16:13 | 100 | 1:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUVIAS | C23051700168 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 97 | 2023-05-17 | 9700 | keep | 0 | May | 2023 | 0.0066066 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-17 14:39 | 2023-05-17 15:09 | 1 | 0:30 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23051700119 | New_Event | Animals | Include | Include | Wildlife | 30 | 2023-05-17 | 30 | keep | 0 | May | 2023 | 2.0433e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-17 15:00 | 2023-05-17 16:45 | 10 | 1:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR REPARAR LINEA SECUNDARIA | M23051700123 | New_Event | Secondary Wire Break | Include | Include | Equipment | 105 | 2023-05-17 | 1050 | keep | 0 | May | 2023 | 0.00071515 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-17 15:00 | 2023-05-17 15:45 | 12 | 0:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 50KVA | M23051700137 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-05-17 | 540 | keep | 0 | May | 2023 | 0.00036779 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-17 15:13 | 2023-05-17 17:43 | 45 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L Y 100 EN C/L SE REPARO BAJANTE DE CAJA A LINEA, SE REPARO NEUTRAL PRIMARIO Y SECUNDARIO | R23051700058 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2023-05-17 | 6750 | keep | 0 | May | 2023 | 0.0045974 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-05-17 15:23 | 2023-05-17 19:50 | 70 | 4:27 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE CON AVE | C23051700189 | New_Event | Animals | Include | Include | Wildlife | 267 | 2023-05-17 | 18690 | keep | 0 | May | 2023 | 0.01273 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-05-17 15:23 | 2023-05-17 19:28 | 1310 | 4:05 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO Y SE REEMPLAZO ASILADOR PARTIDO BY-230517-02 | B23051700133 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 245 | 2023-05-17 | 320950 | keep | 0 | May | 2023 | 0.2186 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
BAYAMON | 2023-05-17 15:24 | 2023-05-17 18:27 | 117 | 3:03 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23051700132 | New_Event | Animals | Include | Include | Wildlife | 183 | 2023-05-17 | 21411 | keep | 0 | May | 2023 | 0.014583 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2023-05-17 15:31 | 2023-05-17 15:32 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 1859 | keep | 0 | May | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
ARECIBO | 2023-05-17 15:33 | 2023-05-17 18:50 | 1 | 3:17 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO FASES | A23051700148 | New_Event | Animals | Include | Include | Wildlife | 197 | 2023-05-17 | 197 | keep | 0 | May | 2023 | 0.00013418 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-17 15:34 | 2023-05-17 19:37 | 87 | 4:03 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23051700138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-05-17 | 21141 | keep | 0 | May | 2023 | 0.014399 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
BAYAMON | 2023-05-17 15:34 | 2023-05-17 15:35 | 652 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 652 | keep | 0 | May | 2023 | 0.00044407 | 0.00044407 | Momentary | FALSE | FALSE | Not_TMED_Event | 652
BAYAMON | 2023-05-17 15:34 | 2023-05-17 17:28 | 1859 | 1:54 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA Y SE CERRO POR TRAMOS SE REPORTA MAL TIEMPO EN LA ZONA | B23051700136 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 114 | 2023-05-17 | 211926 | keep | 0 | May | 2023 | 0.14434 | 0.0012662 | Sustained | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2023-05-17 15:40 | 2023-05-17 18:25 | 5 | 2:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR SECUNDARIA PARTIDA | A23051700111 | New_Event | Secondary Wire Break | Include | Include | Equipment | 165 | 2023-05-17 | 825 | keep | 0 | May | 2023 | 0.0005619 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-05-17 15:42 | 2023-05-17 15:46 | 968 | 0:04 | P | CAUSAS EXTERNAS | SE NORMALIZO ALIMENTADOR | C23051700152 | Additional_clients | Damage From Public | Include | Include | Public | 4 | 2023-05-17 | 3872 | keep | 0 | May | 2023 | 0.0026372 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-17 15:42 | 2023-05-17 20:45 | 60 | 5:03 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA | A23051700150 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 303 | 2023-05-17 | 18180 | keep | 0 | May | 2023 | 0.012382 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-17 15:43 | 2023-05-17 17:33 | 6 | 1:50 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C23051700194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 110 | 2023-05-17 | 660 | keep | 0 | May | 2023 | 0.00044952 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-05-17 15:45 | 2023-05-17 18:19 | 200 | 2:34 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051700146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 154 | 2023-05-17 | 30800 | keep | 0 | May | 2023 | 0.020978 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-05-17 15:51 | 2023-05-18 14:14 | 300 | 22:23 | P | CONDUCTOR ROTO O ABIERTO | 2 X 140 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23051700148 | New_Event | Primary Wire Break | Include | Include | Equipment | 1343 | 2023-05-17 | 402900 | keep | 0 | May | 2023 | 0.27441 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
VEGA BAJA | 2023-05-17 15:56 | 2023-05-18 07:52 | 12 | 15:56 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYO | A23051700158 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 956 | 2023-05-17 | 11472 | keep | 0 | May | 2023 | 0.0078135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-05-17 15:58 | 2023-05-17 19:07 | 169 | 3:09 | P | ANIMAL | 1 X 65, 1 X 80 Y 1 X 100 EN CORTES DE LINEA CRUCE CON AVES | C23051700197 | New_Event | Animals | Include | Include | Wildlife | 189 | 2023-05-17 | 31941 | keep | 0 | May | 2023 | 0.021755 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
BAYAMON | 2023-05-17 16:01 | 2023-05-17 18:25 | 245 | 2:24 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE LEVANTO CONDUCTOR PRIMARIO BY-230517-04 | B23051700163 | New_Event | Primary Wire Break | Include | Include | Equipment | 144 | 2023-05-17 | 35280 | keep | 0 | May | 2023 | 0.024029 | 0.00016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 245
UTUADO | 2023-05-17 16:04 | 2023-05-17 18:40 | 125 | 2:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEA | A23051700162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-05-17 | 19500 | keep | 0 | May | 2023 | 0.013281 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-05-17 16:06 | 2023-05-17 16:39 | 316 | 0:33 | S | NO SE REPORTO CAUSA | DISPARO AL CERRAR CCE- EL 0060 DE LA 1117-00 DISPARO TIE BKR POR DIFERENCIAL ABRIO 1117-11 Y 1117-09 LLEVA 25% DEL 1119-4 Y 25% DEL 1119-2 Y TIRO LOCKOUT | S23051700280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2023-05-17 | 10428 | keep | 0 | May | 2023 | 0.0071025 | 0.00021523 | Sustained | FALSE | FALSE | Not_TMED_Event | 316
SAN JUAN | 2023-05-17 16:06 | 2023-05-17 16:39 | 1356 | 0:33 | S | NO SE REPORTO CAUSA | DISPARO AL CERRAR CCE- EL 0060 DE LA 1117-00 DISPARO TIE BKR POR DIFERENCIAL ABRIO 1117-11 Y 1117-09 LLEVA 25% DEL 1119-4 Y 25% DEL 1119-2 Y TIRO LOCKOUT | S23051700280 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 33 | 2023-05-17 | 44748 | keep | 0 | May | 2023 | 0.030478 | 0.00092357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1356
SAN JUAN | 2023-05-17 16:06 | 2023-05-17 16:39 | 215 | 0:33 | P | ALIMENTADOR AMARRADO | DISPARO AL CERRAR CCE- EL 0060 DE LA 1117-00 DISPARO TIE BKR POR DIFERENCIAL ABRIO 1117-11 Y 1117-09 LLEVA 25% DEL 1119-4 Y 25% DEL 1119-2 Y TIRO LOCKOUT | S23051700280 | New_Event | Feeder Load Transferred | Include | Include | Other | 33 | 2023-05-17 | 7095 | keep | 0 | May | 2023 | 0.0048324 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
SAN JUAN | 2023-05-17 16:06 | 2023-05-17 16:39 | 680 | 0:33 | P | ALIMENTADOR AMARRADO | DISPARO AL CERRAR CCE- EL 0060 DE LA 1117-00 DISPARO TIE BKR POR DIFERENCIAL ABRIO 1117-11 Y 1117-09 LLEVA 25% DEL 1119-4 Y 25% DEL 1119-2 Y TIRO LOCKOUT | S23051700280 | New_Event | Feeder Load Transferred | Include | Include | Other | 33 | 2023-05-17 | 22440 | keep | 0 | May | 2023 | 0.015284 | 0.00046314 | Sustained | FALSE | FALSE | Not_TMED_Event | 680
FAJARDO | 2023-05-17 16:07 | 2023-05-17 17:47 | 40 | 1:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN C/L 1 X 20 EN XMR SE REEMPLAZO CAJA PRIMARIA | R23051700059 | New_Event | Cutout Failure | Include | Include | Equipment | 100 | 2023-05-17 | 4000 | keep | 0 | May | 2023 | 0.0027244 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-17 16:10 | 2023-05-17 20:21 | 130 | 4:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA LLUVIAS | C23051700206 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 251 | 2023-05-17 | 32630 | keep | 0 | May | 2023 | 0.022224 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
MAYAGÃœEZ | 2023-05-17 16:12 | 2023-05-17 18:05 | 60 | 1:53 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051700161 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-05-17 | 6780 | keep | 0 | May | 2023 | 0.0046178 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-05-17 16:20 | 2023-05-17 19:09 | 1923 | 2:49 | T | INTERRUPTOR DEFECTUOSO O NO OPERA | BOBINA DE CIERRE QUEMADA SE NORMALIZO CARGA DEL 8401-03 Y SE LE TRANSFIRIO CARGA DEL 8401-02 | A23051700163 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 169 | 2023-05-17 | 324987 | keep | 0 | May | 2023 | 0.22135 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-05-17 16:20 | 2023-05-17 19:09 | 1066 | 2:49 | T | ALIMENTADOR AMARRADO | CARGA POR 8401-02 | A23051700163 | New_Event | Feeder Load Transferred | Include | Include | Other | 169 | 2023-05-17 | 180154 | keep | 0 | May | 2023 | 0.1227 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
BAYAMON | 2023-05-17 16:23 | 2023-05-18 15:32 | 12 | 23:09 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | B23051700185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1389 | 2023-05-17 | 16668 | keep | 0 | May | 2023 | 0.011352 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-17 16:28 | 2023-05-17 18:35 | 70 | 2:07 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REEMPLAZO DISCOS ROTOS | C23051700215 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 127 | 2023-05-17 | 8890 | keep | 0 | May | 2023 | 0.0060549 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-05-17 16:29 | 2023-05-17 21:19 | 3 | 4:50 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE PARARRAYO | M23051700169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 290 | 2023-05-17 | 870 | keep | 0 | May | 2023 | 0.00059255 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-17 16:43 | 2023-05-18 15:05 | 180 | 22:22 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA BY-230518-01 | B23051700204 | New_Event | Primary Wire Break | Include | Include | Equipment | 1342 | 2023-05-17 | 241560 | keep | 0 | May | 2023 | 0.16453 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
PONCE | 2023-05-17 16:45 | 2023-05-17 18:37 | 50 | 1:52 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23051700162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-05-17 | 5600 | keep | 0 | May | 2023 | 0.0038141 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-17 16:45 | 2023-05-17 19:41 | 320 | 2:56 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REMOVIO RAMA SOBRE LINEA Y SE CERRO POR SCADA | B23051700209 | New_Event | Vegetation Contact | Include | Include | Vegetation | 176 | 2023-05-17 | 56320 | keep | 0 | May | 2023 | 0.038359 | 0.00021795 | Sustained | FALSE | FALSE | Not_TMED_Event | 320
VEGA BAJA | 2023-05-17 16:47 | 2023-05-18 11:05 | 50 | 18:18 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | A23051700173 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1098 | 2023-05-17 | 54900 | keep | 0 | May | 2023 | 0.037392 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-17 16:59 | 2023-05-17 17:02 | 1891 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | C23051700022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-17 | 5673 | keep | 0 | May | 2023 | 0.0038639 | 0.001288 | Momentary | FALSE | FALSE | Not_TMED_Event | 1891
HUMACAO | 2023-05-17 16:59 | 2023-05-17 17:02 | 1250 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | C23051700022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-17 | 3750 | keep | 0 | May | 2023 | 0.0025541 | 0.00085137 | Momentary | FALSE | FALSE | Not_TMED_Event | 1250
HUMACAO | 2023-05-17 16:59 | 2023-05-17 17:02 | 2141 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | C23051700022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-17 | 6423 | keep | 0 | May | 2023 | 0.0043747 | 0.0014582 | Momentary | FALSE | FALSE | Not_TMED_Event | 2141
HUMACAO | 2023-05-17 16:59 | 2023-05-17 17:02 | 1827 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3700 | C23051700022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-17 | 5481 | keep | 0 | May | 2023 | 0.0037331 | 0.0012444 | Momentary | FALSE | FALSE | Not_TMED_Event | 1827
ARECIBO | 2023-05-17 17:02 | 2023-05-17 17:04 | 2523 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A23051700184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-17 | 5046 | keep | 0 | May | 2023 | 0.0034368 | 0.0017184 | Momentary | FALSE | FALSE | Not_TMED_Event | 2523
ARECIBO | 2023-05-17 17:02 | 2023-05-17 17:04 | 1607 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A23051700184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-17 | 3214 | keep | 0 | May | 2023 | 0.002189 | 0.0010945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1607
ARECIBO | 2023-05-17 17:02 | 2023-05-17 17:04 | 1722 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A23051700184 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-17 | 3444 | keep | 0 | May | 2023 | 0.0023457 | 0.0011728 | Momentary | FALSE | FALSE | Not_TMED_Event | 1722
ARECIBO | 2023-05-17 17:02 | 2023-05-17 17:04 | 619 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A23051700186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-17 | 1238 | keep | 0 | May | 2023 | 0.0008432 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
ARECIBO | 2023-05-17 17:02 | 2023-05-17 17:04 | 243 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A23051700186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-17 | 486 | keep | 0 | May | 2023 | 0.00033101 | 0.00016551 | Momentary | FALSE | FALSE | Not_TMED_Event | 243
ARECIBO | 2023-05-17 17:02 | 2023-05-17 17:04 | 2703 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2200 | A23051700186 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-17 | 5406 | keep | 0 | May | 2023 | 0.003682 | 0.001841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2703
PONCE | 2023-05-17 17:24 | 2023-05-17 20:05 | 653 | 2:41 | T | DESGANCHE | SE REALIZO DESGANCHE | P23051700178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-05-17 | 105133 | keep | 0 | May | 2023 | 0.071606 | 0.00044476 | Sustained | FALSE | FALSE | Not_TMED_Event | 653
BAYAMON | 2023-05-17 17:28 | 2023-05-17 18:07 | 930 | 0:39 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA Y SE CERRO POR TRAMOS SE REPORTA MAL TIEMPO EN LA ZONA | B23051700136 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 39 | 2023-05-17 | 36270 | keep | 0 | May | 2023 | 0.024703 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-17 17:29 | 2023-05-17 21:42 | 100 | 4:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 100 EN C/L | B23051700247 | New_Event | Cutout Failure | Include | Include | Equipment | 253 | 2023-05-17 | 25300 | keep | 0 | May | 2023 | 0.017232 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-17 17:40 | 2023-05-17 18:50 | 7 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR SE REMPLAZO CONECTOR SECUNDARIO | S23051700177 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-05-17 | 490 | keep | 0 | May | 2023 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-17 17:45 | 2023-05-17 18:20 | 12 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO BAJANTE SECUNDARIO | S23051700253 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-05-17 | 420 | keep | 0 | May | 2023 | 0.00028606 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-17 17:59 | 2023-05-18 00:27 | 223 | 6:28 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23051700296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 388 | 2023-05-17 | 86524 | keep | 0 | May | 2023 | 0.058931 | 0.00015188 | Sustained | FALSE | FALSE | Not_TMED_Event | 223
BAYAMON | 2023-05-17 18:07 | 2023-05-17 18:30 | 93 | 0:23 | P | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA Y SE CERRO POR TRAMOS SE REPORTA MAL TIEMPO EN LA ZONA | B23051700136 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 23 | 2023-05-17 | 2139 | keep | 0 | May | 2023 | 0.0014569 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-17 18:20 | 2023-05-17 19:05 | 10 | 0:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REEMPLAZO PORTAFUSIBLE | R23051700068 | New_Event | Cutout Failure | Include | Include | Equipment | 45 | 2023-05-17 | 450 | keep | 0 | May | 2023 | 0.00030649 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-17 18:21 | 2023-05-17 18:22 | 1799 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051700000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 1799 | keep | 0 | May | 2023 | 0.0012253 | 0.0012253 | Momentary | FALSE | FALSE | Not_TMED_Event | 1799
VEGA BAJA | 2023-05-17 18:29 | 2023-05-18 12:45 | 12 | 18:16 | P | ARBOL SOBRE LINEA | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHEDE ARBOL SOBRE LINEA | A23051700220 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1096 | 2023-05-17 | 13152 | keep | 0 | May | 2023 | 0.0089578 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-17 18:35 | 2023-05-17 22:09 | 137 | 3:34 | P | ARBOL SOBRE LINEA | SJ-230517-03 SE SECCIONALIZO ALIMENTADOR Y 1 X 65 EN C/L SE RETIRO ARBOL SOBRE LA LINEA | S23051700306 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 214 | 2023-05-17 | 29318 | keep | 0 | May | 2023 | 0.019968 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
BAYAMON | 2023-05-17 18:46 | 2023-05-17 20:05 | 100 | 1:19 | P | CONDUCTOR ROTO O ABIERTO | CERRAR PUENTE DE LINEA A CAJA | B23051700335 | New_Event | Primary Wire Break | Include | Include | Equipment | 79 | 2023-05-17 | 7900 | keep | 0 | May | 2023 | 0.0053807 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-05-17 18:49 | 2023-05-17 21:55 | 100 | 3:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | A23051700226 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 186 | 2023-05-17 | 18600 | keep | 0 | May | 2023 | 0.012668 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-05-17 18:51 | 2023-05-18 07:00 | 20 | 12:09 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | P23051700238 | New_Event | Vegetation Contact | Include | Include | Vegetation | 729 | 2023-05-17 | 14580 | keep | 0 | May | 2023 | 0.0099304 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-17 18:53 | 2023-05-18 08:45 | 11 | 13:52 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | R23051700070 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 832 | 2023-05-17 | 9152 | keep | 0 | May | 2023 | 0.0062334 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-05-17 18:59 | 2023-05-17 19:32 | 70 | 0:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23051700249 | New_Event | Vegetation Contact | Include | Include | Vegetation | 33 | 2023-05-17 | 2310 | keep | 0 | May | 2023 | 0.0015733 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-05-17 19:05 | 2023-05-18 02:26 | 150 | 7:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y SE REEMPLAZO CAJA PRIMARIA | B23051700348 | New_Event | Cutout Failure | Include | Include | Equipment | 441 | 2023-05-17 | 66150 | keep | 0 | May | 2023 | 0.045054 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-05-17 19:05 | 2023-05-17 19:06 | 2094 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 50% DE SU CARGA | R23051700073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-17 | 2094 | keep | 0 | May | 2023 | 0.0014262 | 0.0014262 | Momentary | FALSE | FALSE | Not_TMED_Event | 2094
AGUADILLA | 2023-05-17 19:18 | 2023-05-18 09:28 | 10 | 14:10 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23051700213 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2023-05-17 | 8500 | keep | 0 | May | 2023 | 0.0057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-17 19:21 | 2023-05-18 08:03 | 140 | 12:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA 1 X 100 EN C/L Y 1 X 10 EN XMR | B23051700354 | New_Event | Cutout Failure | Include | Include | Equipment | 762 | 2023-05-17 | 106680 | keep | 0 | May | 2023 | 0.072659 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CANOVANAS | 2023-05-17 19:27 | 2023-05-17 20:40 | 12 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 50 RBA EN SU-3A | R23051700076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-05-17 | 876 | keep | 0 | May | 2023 | 0.00059664 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-17 19:28 | 2023-05-17 19:29 | 2435 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE CARGA POR EL 1909-08 | S2305170000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-17 | 2435 | keep | 0 | May | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-17 19:28 | 2023-05-17 19:29 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE LLEVA LA CARGA DEL 1907-05 | S2305170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-17 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-05-17 19:29 | 2023-05-17 22:16 | 812 | 2:47 | P | CONDUCTOR ROTO O ABIERTO | BY-230517-05 SE ENCONTRO PUENTE ABIERTO Y SE SECCIONALIZO | S23051700404 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 167 | 2023-05-17 | 135604 | keep | 0 | May | 2023 | 0.092359 | 0.00055305 | Sustained | FALSE | FALSE | Not_TMED_Event | 812
BAYAMON | 2023-05-17 19:29 | 2023-05-17 23:27 | 31 | 3:58 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L Y SE CERRO PUENTE DE LINE A CAJA | S23051700171 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 238 | 2023-05-17 | 7378 | keep | 0 | May | 2023 | 0.0050251 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-17 19:29 | 2023-05-17 20:10 | 7 | 0:41 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | B23051700359 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 41 | 2023-05-17 | 287 | keep | 0 | May | 2023 | 0.00019547 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-05-17 19:40 | 2023-05-18 09:30 | 30 | 13:50 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | M23051700219 | New_Event | Animals | Include | Include | Wildlife | 830 | 2023-05-17 | 24900 | keep | 0 | May | 2023 | 0.016959 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-17 19:53 | 2023-05-17 21:45 | 15 | 1:52 | P | ANIMAL | 2 X 50 EN C/L CRUCE POR POR IGUANA | B23051700373 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-05-17 | 1680 | keep | 0 | May | 2023 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-05-17 20:04 | 2023-05-17 21:23 | 50 | 1:19 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23051700263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 79 | 2023-05-17 | 3950 | keep | 0 | May | 2023 | 0.0026903 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-17 20:35 | 2023-05-18 19:30 | 30 | 22:55 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN CORTE DE LINEA POR BAJANTE PRIMARIO | M23051700228 | New_Event | Primary Wire Break | Include | Include | Equipment | 1375 | 2023-05-17 | 41250 | keep | 0 | May | 2023 | 0.028095 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-17 20:35 | 2023-05-18 13:15 | 11 | 16:40 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR NO SE ENCONTRO CAUSA | M23051700238 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1000 | 2023-05-17 | 11000 | keep | 0 | May | 2023 | 0.007492 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
MAYAGÃœEZ | 2023-05-17 20:57 | 2023-05-18 08:45 | 60 | 11:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M23051700231 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 708 | 2023-05-17 | 42480 | keep | 0 | May | 2023 | 0.028933 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
FAJARDO | 2023-05-17 21:01 | 2023-05-18 08:34 | 1 | 11:33 | P | PROBLEMA DEL CLIENTE | 2 X 50 EN RISER REQUIERE MANTENIMIENTO DEL TRANSCLOSURE DE CONDOMINIO | R23051700081 | New_Event | Customer-Related Interruption | Include | Include | Public | 693 | 2023-05-17 | 693 | keep | 0 | May | 2023 | 0.000472 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-17 21:42 | 2023-05-18 14:56 | 70 | 17:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN RISER SE REMPLAZO CAJA PRIMARIA | S23051700551 | New_Event | Cutout Failure | Include | Include | Equipment | 1034 | 2023-05-17 | 72380 | keep | 0 | May | 2023 | 0.049298 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-05-17 22:09 | 2023-05-18 13:16 | 17 | 15:07 | P | ARBOL SOBRE LINEA | POSTE PRIMARIO PARTIDO Y CONDUCTORES EN SUELO | S23051700306 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 907 | 2023-05-17 | 15419 | keep | 0 | May | 2023 | 0.010502 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-17 22:12 | 2023-05-18 08:50 | 2 | 10:38 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR POR DESGANCHE | A23051700252 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 638 | 2023-05-17 | 1276 | keep | 0 | May | 2023 | 0.00086908 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-17 22:16 | 2023-05-17 23:28 | 2435 | 1:12 | T | CONDUCTOR ROTO O ABIERTO | BY-230517-05 SE SECCIONALIZO ALIMENTADOR Y SE CERRO PUENTE | S23051700404 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 72 | 2023-05-17 | 175320 | keep | 0 | May | 2023 | 0.11941 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-17 23:01 | 2023-05-17 23:03 | 837 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR CERRADO POR SCADA LLEVA 1401-06 | S2305170000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-17 | 1674 | keep | 0 | May | 2023 | 0.0011402 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-05-17 23:01 | 2023-05-17 23:03 | 908 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA LLEVA 1401-06 | S2305170000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-17 | 1816 | keep | 0 | May | 2023 | 0.0012369 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BAYAMON | 2023-05-17 23:27 | 2023-05-17 23:28 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR A PETICION (WILFREDO VALLESCORBO) DE PERSONAL EN EL CAMPO PARA CERRAR MACHETES SIN CARGA | S2305170000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-17 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
CANOVANAS | 2023-05-17 23:28 | 2023-05-18 11:00 | 25 | 11:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | C23051700308 | New_Event | Cutout Failure | Include | Include | Equipment | 692 | 2023-05-17 | 17300 | keep | 0 | May | 2023 | 0.011783 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-17 23:28 | 2023-05-18 04:12 | 31 | 4:44 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L Y SE CERRO PUENTE DE LINE A CAJA | S23051700171 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 284 | 2023-05-17 | 8804 | keep | 0 | May | 2023 | 0.0059964 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-17 23:49 | 2023-05-18 13:15 | 51 | 13:26 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23051700683 | New_Event | Vegetation Contact | Include | Include | Vegetation | 806 | 2023-05-17 | 41106 | keep | 0 | May | 2023 | 0.027997 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
MAYAGÃœEZ | 2023-05-18 03:07 | 2023-05-18 14:30 | 20 | 11:23 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M23051800003 | New_Event | Primary Wire Break | Include | Include | Equipment | 683 | 2023-05-18 | 13660 | keep | 0 | May | 2023 | 0.0093038 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-18 03:49 | 2023-05-18 03:50 | 112 | 0:01 | T | NO SE REPORTO CAUSA | RECIIERE DE BKR | S2305180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 112 | keep | 0 | May | 2023 | 7.6283e-05 | 7.6283e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 112
PONCE | 2023-05-18 05:00 | 2023-05-18 05:01 | 2113 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051800017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 2113 | keep | 0 | May | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
AGUADILLA | 2023-05-18 05:22 | 2023-05-18 08:56 | 2000 | 3:34 | P | ANIMAL | SE CERRO POLE BREAKER A LAS 0856 | M23051800010 | New_Event | Animals | Include | Include | Wildlife | 214 | 2023-05-18 | 428000 | keep | 0 | May | 2023 | 0.29151 | 0.0013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 2000
BAYAMON | 2023-05-18 05:35 | 2023-05-18 10:36 | 20 | 5:01 | P | DESGANCHE | 1 X 30 EN RISER Y 1 X 40 EN RISER PRINCIPAL DESGANCHE | B23051800011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 301 | 2023-05-18 | 6020 | keep | 0 | May | 2023 | 0.0041002 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-18 06:11 | 2023-05-18 07:30 | 2608 | 1:19 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL 0010 BUS SUPPORT AVERIADO | C23051800027 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 79 | 2023-05-18 | 206032 | keep | 0 | May | 2023 | 0.14033 | 0.0017763 | Sustained | FALSE | FALSE | Not_TMED_Event | 2608
CAGUAS | 2023-05-18 06:11 | 2023-05-18 07:30 | 845 | 1:19 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DEL 0010 BUS SUPPORT AVERIADO | C23051800027 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 79 | 2023-05-18 | 66755 | keep | 0 | May | 2023 | 0.045467 | 0.00057553 | Sustained | FALSE | FALSE | Not_TMED_Event | 845
SAN JUAN | 2023-05-18 06:26 | 2023-05-18 15:02 | 8 | 8:36 | P | DESGANCHE | SE ABRIO EN XMR PARA DESGANCHE PRIMARIO Y REPARAR BAJANTE DE NEUTRAL EN XMR | S23051800013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 516 | 2023-05-18 | 4128 | keep | 0 | May | 2023 | 0.0028116 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-05-18 06:28 | 2023-05-18 11:00 | 25 | 4:32 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA ARBOL CAYO Y CAUSO CRUCE DE LINEAS | M23051800052 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 272 | 2023-05-18 | 6800 | keep | 0 | May | 2023 | 0.0046314 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-05-18 06:31 | 2023-05-18 09:00 | 50 | 2:29 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23051800020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-05-18 | 7450 | keep | 0 | May | 2023 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-05-18 06:44 | 2023-05-18 07:01 | 150 | 0:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | A23051800006 | New_Event | Cutout Failure | Include | Include | Equipment | 17 | 2023-05-18 | 2550 | keep | 0 | May | 2023 | 0.0017368 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 1222 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 1222 | keep | 0 | May | 2023 | 0.0008323 | 0.0008323 | Momentary | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 2756 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 2756 | keep | 0 | May | 2023 | 0.0018771 | 0.0018771 | Momentary | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 2833 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 2833 | keep | 0 | May | 2023 | 0.0019295 | 0.0019295 | Momentary | FALSE | FALSE | Not_TMED_Event | 2833
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 1218 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 1218 | keep | 0 | May | 2023 | 0.00082957 | 0.00082957 | Momentary | FALSE | FALSE | Not_TMED_Event | 1218
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 1345 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 1345 | keep | 0 | May | 2023 | 0.00091607 | 0.00091607 | Momentary | FALSE | FALSE | Not_TMED_Event | 1345
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 1265 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 1265 | keep | 0 | May | 2023 | 0.00086159 | 0.00086159 | Momentary | FALSE | FALSE | Not_TMED_Event | 1265
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 2071 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 2071 | keep | 0 | May | 2023 | 0.0014105 | 0.0014105 | Momentary | FALSE | FALSE | Not_TMED_Event | 2071
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 760 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800018 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 760 | keep | 0 | May | 2023 | 0.00051763 | 0.00051763 | Momentary | FALSE | FALSE | Not_TMED_Event | 760
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 509 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 509 | keep | 0 | May | 2023 | 0.00034668 | 0.00034668 | Momentary | FALSE | FALSE | Not_TMED_Event | 509
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 2620 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 2620 | keep | 0 | May | 2023 | 0.0017845 | 0.0017845 | Momentary | FALSE | FALSE | Not_TMED_Event | 2620
ARECIBO | 2023-05-18 07:01 | 2023-05-18 07:02 | 1916 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 2100 FUSIBLE FUNDIDO EN SUB 7601 CAMUY | A23051800020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 1916 | keep | 0 | May | 2023 | 0.001305 | 0.001305 | Momentary | FALSE | FALSE | Not_TMED_Event | 1916
ARECIBO | 2023-05-18 07:02 | 2023-05-18 08:45 | 150 | 1:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REEMPLAZO PORTAFUSIBLE | A23051800006 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 103 | 2023-05-18 | 15450 | keep | 0 | May | 2023 | 0.010523 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-18 07:06 | 2023-05-18 11:26 | 1 | 4:20 | P | NO SE REPORTO CAUSA | 1 SMU 20 DE 100A Y 1 X 50 EN C/L | C23051800039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 260 | 2023-05-18 | 260 | keep | 0 | May | 2023 | 0.00017708 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-18 07:06 | 2023-05-18 08:16 | 1 | 1:10 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23051800022 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-05-18 | 70 | keep | 0 | May | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-18 07:06 | 2023-05-18 12:31 | 120 | 5:25 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23051800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 325 | 2023-05-18 | 39000 | keep | 0 | May | 2023 | 0.026563 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CAGUAS | 2023-05-18 07:16 | 2023-05-18 14:38 | 28 | 7:22 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR 1 X 30 EN CORTE DE LINEA CRUCE CON AVE | C23051800045 | New_Event | Animals | Include | Include | Wildlife | 442 | 2023-05-18 | 12376 | keep | 0 | May | 2023 | 0.0084292 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2023-05-18 07:18 | 2023-05-18 13:07 | 1 | 5:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRAS EN PEDESTAL | B23051800023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 349 | 2023-05-18 | 349 | keep | 0 | May | 2023 | 0.0002377 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-18 07:20 | 2023-05-18 10:22 | 10 | 3:02 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23051800002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-05-18 | 1820 | keep | 0 | May | 2023 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-18 07:24 | 2023-05-18 07:25 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051800017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 338 | keep | 0 | May | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
VEGA BAJA | 2023-05-18 07:27 | 2023-05-18 12:22 | 9 | 4:55 | P | DESGANCHE | 1 X 50 EN C/L 1 X 25 SE REALIZO DESGANCHE | B23051800027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2023-05-18 | 2655 | keep | 0 | May | 2023 | 0.0018083 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-05-18 07:39 | 2023-05-18 14:22 | 7 | 6:43 | P | ANIMAL | 1 X 8 EN TRANSFORMADOR CRUCE CON AVE | C23051800057 | New_Event | Animals | Include | Include | Wildlife | 403 | 2023-05-18 | 2821 | keep | 0 | May | 2023 | 0.0019214 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-05-18 07:44 | 2023-05-18 11:41 | 60 | 3:57 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23051800040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2023-05-18 | 14220 | keep | 0 | May | 2023 | 0.0096852 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-05-18 07:47 | 2023-05-18 07:51 | 3 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO NO RECERRO CERRADO X CONTROL | C23051800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-18 | 12 | keep | 0 | May | 2023 | 8.1731e-06 | 2.0433e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 3
HUMACAO | 2023-05-18 07:49 | 2023-05-18 15:38 | 7 | 7:49 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | C23051800058 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 469 | 2023-05-18 | 3283 | keep | 0 | May | 2023 | 0.002236 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-05-18 07:52 | 2023-05-18 09:45 | 28 | 1:53 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R23051800003 | New_Event | Animals | Include | Include | Wildlife | 113 | 2023-05-18 | 3164 | keep | 0 | May | 2023 | 0.002155 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BARRANQUITAS | 2023-05-18 08:02 | 2023-05-18 11:00 | 40 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIAS | C23051800066 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-05-18 | 7120 | keep | 0 | May | 2023 | 0.0048494 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-18 08:03 | 2023-05-18 08:04 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051800021 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 338 | keep | 0 | May | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
SAN JUAN | 2023-05-18 08:08 | 2023-05-18 13:50 | 80 | 5:42 | P | DESGANCHE | 2X80 EN C/L DESGANCHE | S23051800023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 342 | 2023-05-18 | 27360 | keep | 0 | May | 2023 | 0.018635 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-18 08:15 | 2023-05-18 08:43 | 10 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE DEJO ABIERTA TOMA SOTERRADA AVERIADA SE VOLVIO A CERRAR TRANSFORMADOR | M23051700198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-05-18 | 280 | keep | 0 | May | 2023 | 0.00019071 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-18 08:32 | 2023-05-18 11:20 | 8 | 2:48 | P | PROBLEMA DEL CLIENTE | SE ABRIO XMR PARA RECONECTAR CLIENTE | B23051800048 | New_Event | Customer-Related Interruption | Include | Include | Public | 168 | 2023-05-18 | 1344 | keep | 0 | May | 2023 | 0.00091539 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-18 08:37 | 2023-05-18 08:38 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051800030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 733 | keep | 0 | May | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
MAYAGÃœEZ | 2023-05-18 08:45 | 2023-05-18 16:45 | 20 | 8:00 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | M23051800125 | New_Event | Primary Wire Break | Include | Include | Equipment | 480 | 2023-05-18 | 9600 | keep | 0 | May | 2023 | 0.0065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-05-18 08:47 | 2023-05-18 09:00 | 1 | 0:13 | P | NO SE REPORTO CAUSA | 2 X 40 EN RISER | C23051800073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2023-05-18 | 13 | keep | 0 | May | 2023 | 8.8542e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-18 08:49 | 2023-05-18 10:17 | 2 | 1:28 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN BANCO DE TRANSFORMADORES SE REEMPLAZO TRANSFORMADOR CON DERRAME DE 37.5 KVA X 37.5 KVA | R23051800015 | New_Event | Service Transformer Failure | Include | Include | Equipment | 88 | 2023-05-18 | 176 | keep | 0 | May | 2023 | 0.00011987 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-05-18 08:55 | 2023-05-18 10:59 | 30 | 2:04 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE | R23051800018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-05-18 | 3720 | keep | 0 | May | 2023 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-18 08:56 | 2023-05-18 13:16 | 16 | 4:20 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23051800077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 260 | 2023-05-18 | 4160 | keep | 0 | May | 2023 | 0.0028334 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-05-18 08:56 | 2023-05-18 11:00 | 350 | 2:04 | P | ANIMAL | SE CERRO TRIP SAVER A LAS 1100 SE RETIRO RANA QUE CAUSO CRUCE A TIERRA | M23051800010 | Partial_restoration | Animals | Include | Include | Wildlife | 124 | 2023-05-18 | 43400 | keep | 0 | May | 2023 | 0.02956 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-18 08:57 | 2023-05-18 16:55 | 8 | 7:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23051800035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 478 | 2023-05-18 | 3824 | keep | 0 | May | 2023 | 0.0026045 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-18 09:04 | 2023-05-18 11:43 | 1 | 2:39 | P | NO SE REPORTO CAUSA | 2 X 40 RN RISER HACIA SUB. OFICINAS DE PUEBLO | S23051800038 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 159 | 2023-05-18 | 159 | keep | 0 | May | 2023 | 0.00010829 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-18 09:11 | 2023-05-18 13:23 | 75 | 4:12 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P23051800064 | New_Event | Cutout Failure | Include | Include | Equipment | 252 | 2023-05-18 | 18900 | keep | 0 | May | 2023 | 0.012873 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-05-18 09:24 | 2023-05-18 12:37 | 12 | 3:13 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L REMPLAZO PORTAFUSIBLE PARTIDO | C23051800084 | New_Event | Cutout Failure | Include | Include | Equipment | 193 | 2023-05-18 | 2316 | keep | 0 | May | 2023 | 0.0015774 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-18 09:30 | 2023-05-18 11:07 | 53 | 1:37 | P | CONDUCTOR ROTO O ABIERTO | ABRIO C/L PARA LEVANTAR NEUTRAL PRIMARIO | C23051800079 | New_Event | Primary Wire Break | Include | Include | Equipment | 97 | 2023-05-18 | 5141 | keep | 0 | May | 2023 | 0.0035015 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
UTUADO | 2023-05-18 09:30 | 2023-05-18 16:32 | 300 | 7:02 | P | CONDUCTOR ROTO O ABIERTO | REPARAR LINEA PRIMARIA PARTIDA | A23051800121 | New_Event | Primary Wire Break | Include | Include | Equipment | 422 | 2023-05-18 | 126600 | keep | 0 | May | 2023 | 0.086227 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
GUAYAMA | 2023-05-18 09:58 | 2023-05-18 13:25 | 1 | 3:27 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | P23051800080 | New_Event | Vegetation Contact | Include | Include | Vegetation | 207 | 2023-05-18 | 207 | keep | 0 | May | 2023 | 0.00014099 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-18 09:59 | 2023-05-18 13:51 | 18 | 3:52 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23051800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-05-18 | 4176 | keep | 0 | May | 2023 | 0.0028443 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-05-18 10:06 | 2023-05-18 12:39 | 1222 | 2:33 | S | LINEA DE TRANSMISION 38KV | SE REPUSO 1 X 125 STANDAR EN LA ALTA | A23051800132 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 153 | 2023-05-18 | 186966 | keep | 0 | May | 2023 | 0.12734 | 0.0008323 | Sustained | FALSE | FALSE | Not_TMED_Event | 1222
ARECIBO | 2023-05-18 10:06 | 2023-05-18 12:39 | 2756 | 2:33 | S | LINEA DE TRANSMISION 38KV | SE REPUSO 1 X 125 STANDAR EN LA ALTA | A23051800133 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 153 | 2023-05-18 | 421668 | keep | 0 | May | 2023 | 0.2872 | 0.0018771 | Sustained | FALSE | FALSE | Not_TMED_Event | 2756
ARECIBO | 2023-05-18 10:06 | 2023-05-18 12:39 | 2833 | 2:33 | S | LINEA DE TRANSMISION 38KV | SE REPUSO 1 X 125 STANDAR EN LA ALTA | A23051800134 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 153 | 2023-05-18 | 433449 | keep | 0 | May | 2023 | 0.29522 | 0.0019295 | Sustained | FALSE | FALSE | Not_TMED_Event | 2833
YAUCO | 2023-05-18 10:15 | 2023-05-18 14:52 | 8 | 4:37 | P | DESGANCHE | SE HIZO DEZGANCHE MASIVO 1 X 10 EN TRANSFORMADOR Y SE LEVANTO SECUNDARIA Y | P23051800087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2023-05-18 | 2216 | keep | 0 | May | 2023 | 0.0015093 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-18 10:21 | 2023-05-18 14:35 | 45 | 4:14 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | M23051800182 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 254 | 2023-05-18 | 11430 | keep | 0 | May | 2023 | 0.0077849 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-05-18 10:21 | 2023-05-18 15:45 | 30 | 5:24 | P | DESGANCHE | 1 X 30 EN C/L | B23051800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 324 | 2023-05-18 | 9720 | keep | 0 | May | 2023 | 0.0066202 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-18 10:26 | 2023-05-18 11:56 | 7 | 1:30 | P | ANIMAL | 1 X 5 EN XMR CRUCE X AVE | C23051800103 | New_Event | Animals | Include | Include | Wildlife | 90 | 2023-05-18 | 630 | keep | 0 | May | 2023 | 0.00042909 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-18 10:41 | 2023-05-18 15:00 | 24 | 4:19 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR CON DERRAME 37.5 X 37.5 | B23051800078 | New_Event | Service Transformer Failure | Include | Include | Equipment | 259 | 2023-05-18 | 6216 | keep | 0 | May | 2023 | 0.0042337 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
VEGA BAJA | 2023-05-18 10:41 | 2023-05-18 17:41 | 250 | 7:00 | P | TERMINACION SOTERRADA AVERIADA | 1 X 50 EN CORTE DE LINEA POR STRESS CONE AVERIADOS EN SWITCH UNIT | A23051800149 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 420 | 2023-05-18 | 105000 | keep | 0 | May | 2023 | 0.071515 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
VEGA BAJA | 2023-05-18 10:43 | 2023-05-18 12:30 | 10 | 1:47 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA SE RETIRO IGUANA | A23051800150 | New_Event | Animals | Include | Include | Wildlife | 107 | 2023-05-18 | 1070 | keep | 0 | May | 2023 | 0.00072877 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-18 10:51 | 2023-05-18 12:40 | 180 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 50 Y 1 X 80 EN CORTE DE LINEA DISTINTOS NO SE ENCONTRO CAUSA | M23051800190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-05-18 | 19620 | keep | 0 | May | 2023 | 0.013363 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
VEGA BAJA | 2023-05-18 10:55 | 2023-05-18 19:10 | 3 | 8:15 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15KVA | A23051800153 | New_Event | Service Transformer Failure | Include | Include | Equipment | 495 | 2023-05-18 | 1485 | keep | 0 | May | 2023 | 0.0010114 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-05-18 10:59 | 2023-05-18 14:00 | 1 | 3:01 | P | TRANSFORMADOR AVERIADO | REEMPLAZO DE TRANSFORMADOR CON DERRAME DE ACEITE DE 50KVA X 50KVA | A23051800161 | New_Event | Service Transformer Failure | Include | Include | Equipment | 181 | 2023-05-18 | 181 | keep | 0 | May | 2023 | 0.00012328 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-18 11:04 | 2023-05-18 11:36 | 8 | 0:32 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REMPLAZO CAJA AVERIADA NO FUNDIO | C23051800098 | New_Event | Cutout Failure | Include | Include | Equipment | 32 | 2023-05-18 | 256 | keep | 0 | May | 2023 | 0.00017436 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-18 11:14 | 2023-05-18 13:24 | 8 | 2:10 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R23051800036 | New_Event | Animals | Include | Include | Wildlife | 130 | 2023-05-18 | 1040 | keep | 0 | May | 2023 | 0.00070834 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
UTUADO | 2023-05-18 11:17 | 2023-05-18 18:50 | 50 | 7:33 | P | DESGANCHE | 1 X 65 EN CORTE DE LINE A RETIRO PALMA SOBRE LINEA | A23051800162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 453 | 2023-05-18 | 22650 | keep | 0 | May | 2023 | 0.015427 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-18 11:25 | 2023-05-18 13:45 | 603 | 2:20 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | EN OPERACIONES PARA SECCIONALIZAR TRAMO SOTERRADO DE LA VIA LIBRE D2023-3841 EL OPERADOR DEL VS MH-2 NO OPERO CORRECTAMENTE LLEVA 9206-09 | B23051800086 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 140 | 2023-05-18 | 84420 | keep | 0 | May | 2023 | 0.057498 | 0.0004107 | Sustained | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-05-18 11:25 | 2023-05-18 13:45 | 6 | 2:20 | T | ALIMENTADOR AMARRADO | EN OPERACIONES PARA SECCIONALIZAR TRAMO SOTERRADO DE LA VIA LIBRE D2023-3841 EL OPERADOR DEL VS MH-2 NO OPERO CORRECTAMENTE CARGA X 9206-08 | B23051800086 | New_Event | Feeder Load Transferred | Include | Include | Other | 140 | 2023-05-18 | 840 | keep | 0 | May | 2023 | 0.00057212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-18 11:27 | 2023-05-18 13:38 | 598 | 2:11 | T | ALIMENTADOR AMARRADO | NO SE REPORTO CAUSA CARGAS X 3405-03 | C23051800113 | New_Event | Feeder Load Transferred | Include | Include | Other | 131 | 2023-05-18 | 78338 | keep | 0 | May | 2023 | 0.053356 | 0.0004073 | Sustained | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2023-05-18 11:27 | 2023-05-18 13:03 | 1001 | 1:36 | T | NO SE REPORTO CAUSA | DISPARO LLEVA LA CARGA DEL 3403-01 50% DEL 3405-03 EN SERVICIO, 3403-01 SIGUE FUERA | C23051800113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2023-05-18 | 96096 | keep | 0 | May | 2023 | 0.065451 | 0.00068178 | Sustained | FALSE | FALSE | Not_TMED_Event | 1001
AGUADILLA | 2023-05-18 11:29 | 2023-05-18 14:39 | 80 | 3:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 140 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | M23051800200 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2023-05-18 | 15200 | keep | 0 | May | 2023 | 0.010353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-05-18 11:30 | 2023-05-18 15:10 | 50 | 3:40 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBU SOBRE LINEA | M23051800201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-05-18 | 11000 | keep | 0 | May | 2023 | 0.007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-05-18 11:33 | 2023-05-18 17:22 | 2 | 5:49 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE | P23051800099 | New_Event | Animals | Include | Include | Wildlife | 349 | 2023-05-18 | 698 | keep | 0 | May | 2023 | 0.0004754 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-18 11:34 | 2023-05-18 12:14 | 1 | 0:40 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23051800008 | New_Event | Animals | Include | Include | Wildlife | 40 | 2023-05-18 | 40 | keep | 0 | May | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-18 11:35 | 2023-05-18 12:45 | 15 | 1:10 | P | SECUNDARIA/DESGANCHE | SE ABRIO TRANSFORMADOR PARA REALIZAR DESGANCHE Y SE REMPLAZO LINEA SECUNDARIA Y BAJANTES SECUNDARIOS AVERIADOS | M23051800001 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 70 | 2023-05-18 | 1050 | keep | 0 | May | 2023 | 0.00071515 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-18 11:36 | 2023-05-18 12:48 | 1 | 1:12 | P | MAL TIEMPO/RAYOS | 1 X 8 EN TRANSFORMADOR POR RAYO (VAQUERIA) | A23051800167 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 72 | 2023-05-18 | 72 | keep | 0 | May | 2023 | 4.9039e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-18 11:50 | 2023-05-18 16:50 | 40 | 5:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M23051800206 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 300 | 2023-05-18 | 12000 | keep | 0 | May | 2023 | 0.0081731 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-18 11:51 | 2023-05-19 10:40 | 25 | 22:49 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR SE RETIRO CULEBRA | A23051800171 | New_Event | Animals | Include | Include | Wildlife | 1369 | 2023-05-18 | 34225 | keep | 0 | May | 2023 | 0.02331 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-05-18 12:25 | 2023-05-18 17:32 | 250 | 5:07 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | A23051800183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-05-18 | 76750 | keep | 0 | May | 2023 | 0.052274 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
CANOVANAS | 2023-05-18 12:51 | 2023-05-18 14:29 | 5 | 1:38 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | R23051800042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 98 | 2023-05-18 | 490 | keep | 0 | May | 2023 | 0.00033374 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-05-18 13:03 | 2023-05-18 13:38 | 500 | 0:35 | P | NO SE REPORTO CAUSA | EN SERVICIO NO SE REPORTO CAUSA | C23051800113 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 35 | 2023-05-18 | 17500 | keep | 0 | May | 2023 | 0.011919 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-18 13:16 | 2023-05-18 16:00 | 137 | 2:44 | P | ARBOL SOBRE LINEA | SE ABRIO EN C/L PARA REMPLAZO POSTE PRIMARIO PARTIDO Y LEVANTAR CONDUCTORES | S23051700306 | Additional_clients | Vegetation Uprooted Tree | Include | Include | Vegetation | 164 | 2023-05-18 | 22468 | keep | 0 | May | 2023 | 0.015303 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-18 13:21 | 2023-05-18 16:20 | 6 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23051800227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-05-18 | 1074 | keep | 0 | May | 2023 | 0.0007315 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-05-18 13:30 | 2023-05-18 13:50 | 1 | 0:20 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA POR LINEA ARRIADA | A23051800203 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 20 | 2023-05-18 | 20 | keep | 0 | May | 2023 | 1.3622e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-18 13:56 | 2023-05-18 17:18 | 12 | 3:22 | P | SOBRECARGA | 1 X 40 EN TRANSFORMADOR POR CARGAS | A23051800211 | New_Event | Trip Due To Overload | Include | Include | Other | 202 | 2023-05-18 | 2424 | keep | 0 | May | 2023 | 0.001651 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-18 13:57 | 2023-05-18 14:20 | 72 | 0:23 | P | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 1404-07 LLEVA 5% DEL 1112-04 SE REALIZARON GESTIONES HASTA CONFIRMAR PERSONAL FUERA Y SE CERRO POR CONTROL | S23051800082 | New_Event | Feeder Load Transferred | Include | Include | Other | 23 | 2023-05-18 | 1656 | keep | 0 | May | 2023 | 0.0011279 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-05-18 13:57 | 2023-05-18 14:20 | 1357 | 0:23 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR 1404-07 LLEVA 5% DEL 1112-04 SE REALIZARON GESTIONES HASTA CONFIRMAR PERSONAL FUERA Y SE CERRO POR CONTROL | S23051800082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 23 | 2023-05-18 | 31211 | keep | 0 | May | 2023 | 0.021258 | 0.00092425 | Sustained | FALSE | FALSE | Not_TMED_Event | 1357
BAYAMON | 2023-05-18 13:59 | 2023-05-18 15:36 | 1498 | 1:37 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE SECCIONALIZO POSTE PARTIDO ENTRO 50% DE SU CARGA | B23051800118 | New_Event | Primary Pole Failure | Include | Include | Equipment | 97 | 2023-05-18 | 145306 | keep | 0 | May | 2023 | 0.098967 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
FAJARDO | 2023-05-18 14:10 | 2023-05-18 17:24 | 161 | 3:14 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESPEJE DE LINEA | R23051800052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-05-18 | 31234 | keep | 0 | May | 2023 | 0.021273 | 0.00010966 | Sustained | FALSE | FALSE | Not_TMED_Event | 161
BAYAMON | 2023-05-18 14:28 | 2023-05-18 17:10 | 12 | 2:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | B23051800126 | New_Event | Secondary Wire Break | Include | Include | Equipment | 162 | 2023-05-18 | 1944 | keep | 0 | May | 2023 | 0.001324 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-05-18 14:35 | 2023-05-18 20:20 | 5 | 5:45 | P | CAUSAS EXTERNAS | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA PARTIDA POR CAMION | M23051800242 | New_Event | Damage From Public | Include | Include | Public | 345 | 2023-05-18 | 1725 | keep | 0 | May | 2023 | 0.0011749 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-05-18 14:55 | 2023-05-18 17:08 | 70 | 2:13 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA DESGANCHE | C23051800143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 133 | 2023-05-18 | 9310 | keep | 0 | May | 2023 | 0.006341 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-05-18 14:56 | 2023-05-18 15:47 | 25 | 0:51 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23051800139 | New_Event | Animals | Include | Include | Wildlife | 51 | 2023-05-18 | 1275 | keep | 0 | May | 2023 | 0.0008684 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-05-18 15:00 | 2023-05-18 15:44 | 17 | 0:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23051800140 | New_Event | Cutout Failure | Include | Include | Equipment | 44 | 2023-05-18 | 748 | keep | 0 | May | 2023 | 0.00050946 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2023-05-18 15:02 | 2023-05-18 15:03 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2305180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
BAYAMON | 2023-05-18 15:09 | 2023-05-19 05:34 | 24 | 14:25 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | B23051800149 | New_Event | Animals | Include | Include | Wildlife | 865 | 2023-05-18 | 20760 | keep | 0 | May | 2023 | 0.01414 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
SAN JUAN | 2023-05-18 15:15 | 2023-05-18 17:30 | 8 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X10 EN T-6 Y SE AJUSTARON BARRAS EN T-6 | S23051800113 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2023-05-18 | 1080 | keep | 0 | May | 2023 | 0.00073558 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-18 15:16 | 2023-05-18 18:35 | 60 | 3:19 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE DESPEGO LINEA DE BRAZO DE ALUMBRADO | M23051800247 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 199 | 2023-05-18 | 11940 | keep | 0 | May | 2023 | 0.0081323 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-18 15:17 | 2023-05-18 18:31 | 50 | 3:14 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO DE LINEA @ CAJA NO FUNDIO | S23051800114 | New_Event | Primary Wire Break | Include | Include | Equipment | 194 | 2023-05-18 | 9700 | keep | 0 | May | 2023 | 0.0066066 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-05-18 15:20 | 2023-05-18 17:47 | 150 | 2:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REPARO CAJA PRIMARIA DE 100A CON 1 X 50 EN CORTE DE LINEA | P23051800120 | New_Event | Cutout Failure | Include | Include | Equipment | 147 | 2023-05-18 | 22050 | keep | 0 | May | 2023 | 0.015018 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-05-18 15:20 | 2023-05-18 17:25 | 100 | 2:05 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PARTIDA | A23051800261 | New_Event | Primary Wire Break | Include | Include | Equipment | 125 | 2023-05-18 | 12500 | keep | 0 | May | 2023 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-18 15:21 | 2023-05-18 17:10 | 80 | 1:49 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23051800156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 109 | 2023-05-18 | 8720 | keep | 0 | May | 2023 | 0.0059392 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-05-18 15:28 | 2023-05-18 18:00 | 12 | 2:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR POR LLUVIAS | A23051800264 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 152 | 2023-05-18 | 1824 | keep | 0 | May | 2023 | 0.0012423 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-18 15:36 | 2023-05-18 22:04 | 649 | 6:28 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO POSTE PRIMARIO Y SE CERRARON MACHETES | B23051800118 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 388 | 2023-05-18 | 251812 | keep | 0 | May | 2023 | 0.17151 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-18 15:42 | 2023-05-18 18:30 | 80 | 2:48 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA CAMION CRUZO FASES | M23051800257 | New_Event | Damage From Public | Include | Include | Public | 168 | 2023-05-18 | 13440 | keep | 0 | May | 2023 | 0.0091539 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-18 15:54 | 2023-05-18 19:34 | 12 | 3:40 | P | CABLE SOTERRADO AVERIADO | 1 X 20 EN PROVISIONAL AEREO SE SECCIONALIZO TRAMO SOTERRADO AVERIADO AVERIA VIEJA T-33 @ T-32 AVERIA NUEVA T-31 @ T-32 | B23051800173 | New_Event | UG Cable Fault | Include | Include | Equipment | 220 | 2023-05-18 | 2640 | keep | 0 | May | 2023 | 0.0017981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-05-18 16:04 | 2023-05-18 18:15 | 50 | 2:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIAS | A23051800287 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 131 | 2023-05-18 | 6550 | keep | 0 | May | 2023 | 0.0044612 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-05-18 16:10 | 2023-05-18 18:34 | 85 | 2:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA POR LLUVIAS | A23051800289 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 144 | 2023-05-18 | 12240 | keep | 0 | May | 2023 | 0.0083366 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CAGUAS | 2023-05-18 16:30 | 2023-05-18 18:13 | 70 | 1:43 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE CON AVE | C23051800164 | New_Event | Animals | Include | Include | Wildlife | 103 | 2023-05-18 | 7210 | keep | 0 | May | 2023 | 0.0049107 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-05-18 16:30 | 2023-05-18 21:50 | 25 | 5:20 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A23051800303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 320 | 2023-05-18 | 8000 | keep | 0 | May | 2023 | 0.0054488 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-05-18 16:31 | 2023-05-18 16:32 | 4811 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE PARTE DE LA CARGA POR EL 3205-07 | C2305180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 4811 | keep | 0 | May | 2023 | 0.0032768 | 0.0032768 | Momentary | FALSE | FALSE | Not_TMED_Event | 4811
YAUCO | 2023-05-18 16:33 | 2023-05-19 08:50 | 125 | 16:17 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23051800133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 977 | 2023-05-18 | 122125 | keep | 0 | May | 2023 | 0.083179 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2023-05-18 16:34 | 2023-05-18 18:26 | 60 | 1:52 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA Y 1 X 100 EN DIFERENTE CORTE DE LINEA AVE | P23051800134 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-05-18 | 6720 | keep | 0 | May | 2023 | 0.004577 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-05-18 16:34 | 2023-05-18 18:36 | 30 | 2:02 | P | MAL TIEMPO/RAYOS | 2 X 10 EN TRANSFORMADOR Y 2 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS Y DESGANCHE | M23051800285 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 122 | 2023-05-18 | 3660 | keep | 0 | May | 2023 | 0.0024928 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-18 16:38 | 2023-05-18 19:43 | 80 | 3:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN C/L Y SE REMPLAZO CAJA PRIMARIA | S23051800137 | New_Event | Cutout Failure | Include | Include | Equipment | 185 | 2023-05-18 | 14800 | keep | 0 | May | 2023 | 0.01008 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-05-18 16:40 | 2023-05-18 16:41 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051800289 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 1352 | keep | 0 | May | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
CAGUAS | 2023-05-18 16:50 | 2023-05-18 19:29 | 250 | 2:39 | P | ANIMAL | 1 X 100 Y 1 X 80 EN CORTES DE LINEA CRUCE CON AVE | C23051800172 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-05-18 | 39750 | keep | 0 | May | 2023 | 0.027074 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2023-05-18 16:58 | 2023-05-18 16:59 | 312 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051800000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 312 | keep | 0 | May | 2023 | 0.0002125 | 0.0002125 | Momentary | FALSE | FALSE | Not_TMED_Event | 312
CANOVANAS | 2023-05-18 17:09 | 2023-05-18 21:51 | 7 | 4:42 | P | CAUSAS EXTERNAS | SE REEMPLAZO SECUNDARIA Y 2 X 10 EN XMR CAMION SE ENREDO EN SECUNDARIA | R23051800086 | New_Event | Damage From Public | Include | Include | Public | 282 | 2023-05-18 | 1974 | keep | 0 | May | 2023 | 0.0013445 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-05-18 17:13 | 2023-05-19 16:05 | 500 | 22:52 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA | M23051800300 | New_Event | Primary Wire Break | Include | Include | Equipment | 1372 | 2023-05-18 | 686000 | keep | 0 | May | 2023 | 0.46723 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2023-05-18 17:56 | 2023-05-18 20:55 | 50 | 2:59 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS | M23051800332 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-05-18 | 8950 | keep | 0 | May | 2023 | 0.0060958 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-18 18:21 | 2023-05-18 18:22 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2305180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 1746 | keep | 0 | May | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BAYAMON | 2023-05-18 18:22 | 2023-05-18 20:28 | 183 | 2:06 | P | SOBRECARGA | 2 X 150 EN SU-13A POR CARGA | B23051800212 | New_Event | Trip Due To Overload | Include | Include | Other | 126 | 2023-05-18 | 23058 | keep | 0 | May | 2023 | 0.015705 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
AGUADILLA | 2023-05-18 18:42 | 2023-05-18 19:20 | 8 | 0:38 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M23051800357 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 38 | 2023-05-18 | 304 | keep | 0 | May | 2023 | 0.00020705 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-18 18:48 | 2023-05-18 18:49 | 2435 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO 1909-08 | S2305180000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-18 | 2435 | keep | 0 | May | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-18 18:48 | 2023-05-18 18:49 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO LLEVA 1907-05 | S2305180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-18 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-05-18 18:49 | 2023-05-18 22:26 | 812 | 3:37 | P | CONDUCTOR ROTO O ABIERTO | SE ENCONTRO PUENTE ABIERTO EN EL AMARRE CONTRA EL 1909-08 | S23051800158 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 217 | 2023-05-18 | 176204 | keep | 0 | May | 2023 | 0.12001 | 0.00055305 | Sustained | FALSE | FALSE | Not_TMED_Event | 812
BAYAMON | 2023-05-18 18:49 | 2023-05-18 18:50 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO 9206-10 | B2305180000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-18 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-18 18:49 | 2023-05-18 18:50 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 9206-07 | B2305180000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-05-18 18:56 | 2023-05-18 20:14 | 172 | 1:18 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23051800217 | New_Event | Animals | Include | Include | Wildlife | 78 | 2023-05-18 | 13416 | keep | 0 | May | 2023 | 0.0091376 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
MAYAGÃœEZ | 2023-05-18 18:59 | 2023-05-19 09:05 | 40 | 14:06 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | M23051800362 | New_Event | Vegetation Contact | Include | Include | Vegetation | 846 | 2023-05-18 | 33840 | keep | 0 | May | 2023 | 0.023048 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-05-18 19:04 | 2023-05-19 08:50 | 10 | 13:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REEMPLAZO SECUNDARIA | C23051800198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 826 | 2023-05-18 | 8260 | keep | 0 | May | 2023 | 0.0056258 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-18 19:08 | 2023-05-19 09:49 | 4 | 14:41 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR POR RAYO | A23051800364 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 881 | 2023-05-18 | 3524 | keep | 0 | May | 2023 | 0.0024002 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-18 19:09 | 2023-05-18 19:10 | 5809 | 0:01 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECERRO | B2305180000X | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-05-18 | 5809 | keep | 0 | May | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
ARECIBO | 2023-05-18 19:15 | 2023-05-18 21:56 | 70 | 2:41 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A23051800319 | New_Event | Vegetation Contact | Include | Include | Vegetation | 161 | 2023-05-18 | 11270 | keep | 0 | May | 2023 | 0.0076759 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-05-18 19:21 | 2023-05-18 20:01 | 8 | 0:40 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23051800371 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 40 | 2023-05-18 | 320 | keep | 0 | May | 2023 | 0.00021795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-18 19:21 | 2023-05-18 19:22 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23051800224 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-18 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-18 19:21 | 2023-05-18 19:22 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23051800224 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CANOVANAS | 2023-05-18 19:29 | 2023-05-18 22:13 | 10 | 2:44 | P | CAUSAS EXTERNAS | SE REPARO SECUNDARIA AVERIADA POR CAMION Y 2 X 8 EN XMR | R23051800095 | New_Event | Damage From Public | Include | Include | Public | 164 | 2023-05-18 | 1640 | keep | 0 | May | 2023 | 0.001117 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-18 19:30 | 2023-05-18 23:05 | 10 | 3:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23051800322 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 215 | 2023-05-18 | 2150 | keep | 0 | May | 2023 | 0.0014644 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-18 19:30 | 2023-05-18 19:31 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | 9206-10 RECERRO | B2305180000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-18 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-18 19:30 | 2023-05-18 19:31 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 9206-07 | B2305180000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-05-18 19:34 | 2023-05-19 12:50 | 12 | 17:16 | P | CABLE SOTERRADO AVERIADO | SE REPARO SOTERRADO AVERIADO (RADIAL) DEL T-31 @ T-32 | B23051800173 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 1036 | 2023-05-18 | 12432 | keep | 0 | May | 2023 | 0.0084674 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-18 19:40 | 2023-05-18 19:41 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | 9206-10 RECERRO | B2305180000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-18 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-18 19:40 | 2023-05-18 19:41 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO LLEVA 9206-07 | B2305180000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-18 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-05-18 19:46 | 2023-05-19 02:45 | 27 | 6:59 | T | ALIMENTADOR AMARRADO | DISPARO INTERRUPTOR 9206-10 LLEVA EL 9206-07. SE REALIZARON OPERACIONES 100% EN SERVICIO | B23051800232 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 419 | 2023-05-18 | 11313 | keep | 0 | May | 2023 | 0.0077052 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-18 19:46 | 2023-05-19 01:10 | 325 | 5:24 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR LLEVA EL 9206-07. SE ABRIO EL N/O CONTRA 9206-07 Y SE CERO POR CONTROL. 100% EN SERVICIO | B23051800232 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 324 | 2023-05-18 | 105300 | keep | 0 | May | 2023 | 0.071719 | 0.00022136 | Sustained | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-05-18 20:09 | 2023-05-19 16:15 | 15 | 20:06 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR SE LEVANTO LINEA SECUNDARIA Y DESGANCHE SECUNDARIO | S23051800301 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1206 | 2023-05-18 | 18090 | keep | 0 | May | 2023 | 0.012321 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-05-18 20:14 | 2023-05-19 00:21 | 218 | 4:07 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23051800230 | New_Event | Cutout Failure | Include | Include | Equipment | 247 | 2023-05-18 | 53846 | keep | 0 | May | 2023 | 0.036674 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
BAYAMON | 2023-05-18 20:23 | 2023-05-19 15:27 | 30 | 19:04 | P | CONDUCTOR ROTO O ABIERTO | 2X50 EN C/L Y SE LEVANTO/REPARO CONDUCTOR PRIMARIO DEL SUELO (RADIAL) | B23051800240 | New_Event | Primary Wire Break | Include | Include | Equipment | 1144 | 2023-05-18 | 34320 | keep | 0 | May | 2023 | 0.023375 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-18 20:41 | 2023-05-19 10:19 | 25 | 13:38 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR POR CAJA PRIMARIA QUEMADA | M23051800396 | New_Event | Cutout Failure | Include | Include | Equipment | 818 | 2023-05-18 | 20450 | keep | 0 | May | 2023 | 0.013928 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-05-18 20:48 | 2023-05-18 22:20 | 526 | 1:32 | P | NO SE REPORTO CAUSA | 1 X 140 C/L NO CAUSA | C23051800244 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 92 | 2023-05-18 | 48392 | keep | 0 | May | 2023 | 0.03296 | 0.00035826 | Sustained | FALSE | FALSE | Not_TMED_Event | 526
MAYAGÃœEZ | 2023-05-18 21:11 | 2023-05-19 13:36 | 11 | 16:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA AVERIADA | M23051800405 | New_Event | Secondary Wire Break | Include | Include | Equipment | 985 | 2023-05-18 | 10835 | keep | 0 | May | 2023 | 0.0073797 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
ARECIBO | 2023-05-18 21:17 | 2023-05-18 22:55 | 120 | 1:38 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA AVERIADA EN TRONCAL ALIMENTADOR | A23051800343 | New_Event | Primary Wire Break | Include | Include | Equipment | 98 | 2023-05-18 | 11760 | keep | 0 | May | 2023 | 0.0080097 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
AGUADILLA | 2023-05-18 21:20 | 2023-05-19 10:45 | 20 | 13:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIA | M23051800408 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 805 | 2023-05-18 | 16100 | keep | 0 | May | 2023 | 0.010966 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-18 21:24 | 2023-05-19 01:05 | 230 | 3:41 | P | DESGANCHE | SE REPARO PUENTE PRIMARIO Y SE REALIZO DESGANCHE | A23051800355 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2023-05-18 | 50830 | keep | 0 | May | 2023 | 0.03462 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
AGUADILLA | 2023-05-18 21:32 | 2023-05-18 21:33 | 693 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M23051800411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 693 | keep | 0 | May | 2023 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2023-05-18 21:32 | 2023-05-18 21:33 | 47 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M23051800411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 47 | keep | 0 | May | 2023 | 3.2011e-05 | 3.2011e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 47
AGUADILLA | 2023-05-18 21:32 | 2023-05-18 21:33 | 1256 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M23051800411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 1256 | keep | 0 | May | 2023 | 0.00085546 | 0.00085546 | Momentary | FALSE | FALSE | Not_TMED_Event | 1256
AGUADILLA | 2023-05-18 21:32 | 2023-05-18 21:33 | 558 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2800 | M23051800411 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-18 | 558 | keep | 0 | May | 2023 | 0.00038005 | 0.00038005 | Momentary | FALSE | FALSE | Not_TMED_Event | 558
BAYAMON | 2023-05-18 22:26 | 2023-05-19 00:14 | 2435 | 1:48 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR 1909-08 PARA ESTABLECER ZONA DE GOI Y CERRAR PUENTE ABIERTO EN EL AMARRE CONTRA EL 1909-08. | S23051800158 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 108 | 2023-05-18 | 262980 | keep | 0 | May | 2023 | 0.17911 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-18 22:26 | 2023-05-19 00:14 | 2956 | 1:48 | T | ALIMENTADOR AMARRADO | SE ABRIO BKR 1909-08 PARA ESTABLECER ZONA DE GOI Y CERRAR PUENTE ABIERTO EN EL AMARRE CONTRA EL 1907-05 | S23051800158 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 108 | 2023-05-18 | 319248 | keep | 0 | May | 2023 | 0.21744 | 0.0020133 | Sustained | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-05-18 22:35 | 2023-05-19 11:56 | 8 | 13:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X15 EN XMR POR LLUVIA | B23051800277 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 801 | 2023-05-18 | 6408 | keep | 0 | May | 2023 | 0.0043645 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-05-18 22:55 | 2023-05-19 00:01 | 1720 | 1:06 | T | CONDUCTOR ROTO O ABIERTO | AR-230518-01A REPARAR LINEA PRIMARIA AVERIADA EN TRONCAL ALIMENTADOR | A23051800411 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 66 | 2023-05-18 | 113520 | keep | 0 | May | 2023 | 0.077318 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-18 23:23 | 2023-05-19 00:55 | 80 | 1:32 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23051800303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-05-18 | 7360 | keep | 0 | May | 2023 | 0.0050129 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-05-18 23:50 | 2023-05-19 07:52 | 44 | 8:02 | P | ANIMAL | 1X100 EN C/L CRUCE POR AVE | B23051800282 | New_Event | Animals | Include | Include | Wildlife | 482 | 2023-05-18 | 21208 | keep | 0 | May | 2023 | 0.014445 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
FAJARDO | 2023-05-19 00:05 | 2023-05-19 08:18 | 1 | 8:13 | P | ANIMAL | 2 X 25 EN C/L CRUCE X AVE | R23051900001 | New_Event | Animals | Include | Include | Wildlife | 493 | 2023-05-19 | 493 | keep | 0 | May | 2023 | 0.00033578 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-19 00:50 | 2023-05-19 00:51 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051900011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
AGUADILLA | 2023-05-19 01:40 | 2023-05-19 09:30 | 20 | 7:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN RISER SE REMPLAZO CAJA PRIMARIA | A23051900005 | New_Event | Cutout Failure | Include | Include | Equipment | 470 | 2023-05-19 | 9400 | keep | 0 | May | 2023 | 0.0064023 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-19 01:59 | 2023-05-19 05:26 | 118 | 3:27 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | S23051900013 | New_Event | Animals | Include | Include | Wildlife | 207 | 2023-05-19 | 24426 | keep | 0 | May | 2023 | 0.016636 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
HUMACAO | 2023-05-19 02:14 | 2023-05-19 05:43 | 1467 | 3:29 | T | CONDUCTOR ROTO O ABIERTO | CG-230519-01 SE SECCIONALIZO ALIMENTADOR Y SE LEVANTO CONDUCTOR Y SE CERRO POR SCADA | C23051900003 | New_Event | Primary Wire Break | Include | Include | Equipment | 209 | 2023-05-19 | 306603 | keep | 0 | May | 2023 | 0.20883 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
GUAYAMA | 2023-05-19 02:40 | 2023-05-19 02:41 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051900024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 449 | keep | 0 | May | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
CAGUAS | 2023-05-19 02:43 | 2023-05-19 15:00 | 22 | 12:17 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23051900008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 737 | 2023-05-19 | 16214 | keep | 0 | May | 2023 | 0.011043 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
HUMACAO | 2023-05-19 03:07 | 2023-05-19 08:41 | 8 | 5:34 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | C23051900010 | New_Event | Animals | Include | Include | Wildlife | 334 | 2023-05-19 | 2672 | keep | 0 | May | 2023 | 0.0018199 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-19 03:10 | 2023-05-19 19:20 | 20 | 16:10 | P | CABLE SOTERRADO AVERIADO | 1 X 40 EN RISER SE CONSTRUYO PROVISIONAL AEREO | M23051900005 | New_Event | UG Cable Fault | Include | Include | Equipment | 970 | 2023-05-19 | 19400 | keep | 0 | May | 2023 | 0.013213 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-05-19 03:47 | 2023-05-19 03:49 | 377 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23051900025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-19 | 754 | keep | 0 | May | 2023 | 0.00051355 | 0.00025677 | Momentary | FALSE | FALSE | Not_TMED_Event | 377
YAUCO | 2023-05-19 05:21 | 2023-05-19 05:23 | 1475 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23051900031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-19 | 2950 | keep | 0 | May | 2023 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
HUMACAO | 2023-05-19 05:36 | 2023-05-19 05:37 | 2354 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C23051900015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 2354 | keep | 0 | May | 2023 | 0.0016033 | 0.0016033 | Momentary | FALSE | FALSE | Not_TMED_Event | 2354
BAYAMON | 2023-05-19 05:58 | 2023-05-19 09:34 | 178 | 3:36 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | B23051900036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 216 | 2023-05-19 | 38448 | keep | 0 | May | 2023 | 0.026187 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
SAN JUAN | 2023-05-19 06:09 | 2023-05-19 06:12 | 1061 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | S23051900022 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-19 | 3183 | keep | 0 | May | 2023 | 0.0021679 | 0.00072264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1061
CAGUAS | 2023-05-19 06:23 | 2023-05-19 12:00 | 12 | 5:37 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23051900019 | New_Event | Animals | Include | Include | Wildlife | 337 | 2023-05-19 | 4044 | keep | 0 | May | 2023 | 0.0027543 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-19 06:24 | 2023-05-19 06:25 | 2708 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | R23051900003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-19 | 2708 | keep | 0 | May | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
CANOVANAS | 2023-05-19 06:25 | 2023-05-19 07:01 | 500 | 0:36 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | R23051900004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 36 | 2023-05-19 | 18000 | keep | 0 | May | 2023 | 0.01226 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
BARRANQUITAS | 2023-05-19 06:26 | 2023-05-19 08:40 | 48 | 2:14 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23051900020 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-05-19 | 6432 | keep | 0 | May | 2023 | 0.0043808 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
MAYAGÃœEZ | 2023-05-19 06:40 | 2023-05-19 13:45 | 20 | 7:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR Y 1 X 40 EN CORTE DE LINEA POR LLUVIA | A23051900015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 425 | 2023-05-19 | 8500 | keep | 0 | May | 2023 | 0.0057893 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-19 06:41 | 2023-05-19 12:05 | 60 | 5:24 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | M23051900017 | New_Event | Animals | Include | Include | Wildlife | 324 | 2023-05-19 | 19440 | keep | 0 | May | 2023 | 0.01324 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-19 06:51 | 2023-05-19 12:00 | 1 | 5:09 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23051900023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 309 | 2023-05-19 | 309 | keep | 0 | May | 2023 | 0.00021046 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-19 06:57 | 2023-05-19 06:59 | 362 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO 90% POR 1620-01 | S23051900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-19 | 724 | keep | 0 | May | 2023 | 0.00049311 | 0.00024656 | Momentary | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-05-19 06:57 | 2023-05-19 06:59 | 36 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO LLEVA 90% 1336-10 Y LLEVA 60% 1620-02 | S23051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-19 | 72 | keep | 0 | May | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-19 06:57 | 2023-05-19 06:59 | 2230 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR SE PROBO POR CONTROL QUEDO EN SERVICIO 60% POR 1620-01 | S23051900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-19 | 4460 | keep | 0 | May | 2023 | 0.0030377 | 0.0015188 | Momentary | FALSE | FALSE | Not_TMED_Event | 2230
CANOVANAS | 2023-05-19 07:01 | 2023-05-19 07:02 | 2708 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | R23051900008 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-19 | 2708 | keep | 0 | May | 2023 | 0.0018444 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-19 07:02 | 2023-05-19 09:12 | 500 | 2:10 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | R23051900004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-05-19 | 65000 | keep | 0 | May | 2023 | 0.044271 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
PONCE | 2023-05-19 07:02 | 2023-05-19 08:38 | 5 | 1:36 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | P23051900045 | New_Event | Animals | Include | Include | Wildlife | 96 | 2023-05-19 | 480 | keep | 0 | May | 2023 | 0.00032693 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-05-19 07:05 | 2023-05-19 10:16 | 1 | 3:11 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23051900025 | New_Event | Animals | Include | Include | Wildlife | 191 | 2023-05-19 | 191 | keep | 0 | May | 2023 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-19 07:09 | 2023-05-19 10:10 | 69 | 3:01 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C23051900026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-05-19 | 12489 | keep | 0 | May | 2023 | 0.0085062 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
MAYAGÃœEZ | 2023-05-19 07:16 | 2023-05-19 15:30 | 65 | 8:14 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASES | M23051900025 | New_Event | Animals | Include | Include | Wildlife | 494 | 2023-05-19 | 32110 | keep | 0 | May | 2023 | 0.02187 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
CANOVANAS | 2023-05-19 07:17 | 2023-05-19 09:32 | 50 | 2:15 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | R23051900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-05-19 | 6750 | keep | 0 | May | 2023 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-19 07:44 | 2023-05-19 17:37 | 80 | 9:53 | P | ANIMAL | 1 X 100 EN C/L CRUCE POR AVE | S23051900032 | New_Event | Animals | Include | Include | Wildlife | 593 | 2023-05-19 | 47440 | keep | 0 | May | 2023 | 0.032311 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-19 07:50 | 2023-05-21 13:48 | 5 | 53:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR QUEMADO DE 15 X 25KVA | S23051900033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 3238 | 2023-05-19 | 16190 | keep | 0 | May | 2023 | 0.011027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
GUAYAMA | 2023-05-19 07:51 | 2023-05-19 09:39 | 10 | 1:48 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23051900056 | New_Event | Animals | Include | Include | Wildlife | 108 | 2023-05-19 | 1080 | keep | 0 | May | 2023 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-05-19 07:52 | 2023-05-19 10:35 | 50 | 2:43 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051900015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-05-19 | 8150 | keep | 0 | May | 2023 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-05-19 08:01 | 2023-05-19 09:48 | 3 | 1:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE FIJO CAJA A CRUCETA SE REEMPLAZO PORTAFUSIBLE | C23051900036 | New_Event | Cutout Failure | Include | Include | Equipment | 107 | 2023-05-19 | 321 | keep | 0 | May | 2023 | 0.00021863 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-05-19 08:23 | 2023-05-19 19:15 | 7 | 10:52 | P | ARBOL SOBRE LINEA | 1 X 20 EN TRANSFORMADOR SE RETIRO ARBOL | M23051900040 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 652 | 2023-05-19 | 4564 | keep | 0 | May | 2023 | 0.0031085 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
AGUADILLA | 2023-05-19 08:52 | 2023-05-19 14:00 | 25 | 5:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBU | M23051900069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 308 | 2023-05-19 | 7700 | keep | 0 | May | 2023 | 0.0052444 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-19 09:07 | 2023-05-19 09:26 | 1825 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 34675 | keep | 0 | May | 2023 | 0.023617 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-05-19 09:07 | 2023-05-19 09:26 | 47 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 893 | keep | 0 | May | 2023 | 0.00060822 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-05-19 09:07 | 2023-05-19 09:26 | 315 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 5985 | keep | 0 | May | 2023 | 0.0040764 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-05-19 09:07 | 2023-05-19 09:26 | 2 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 38 | keep | 0 | May | 2023 | 2.5882e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-19 09:07 | 2023-05-19 09:26 | 2391 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900059 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 45429 | keep | 0 | May | 2023 | 0.030941 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2023-05-19 09:07 | 2023-05-19 09:26 | 2276 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 43244 | keep | 0 | May | 2023 | 0.029453 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-05-19 09:07 | 2023-05-19 09:26 | 777 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 14763 | keep | 0 | May | 2023 | 0.010055 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-05-19 09:07 | 2023-05-19 09:26 | 12 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 228 | keep | 0 | May | 2023 | 0.00015529 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-19 09:07 | 2023-05-19 09:26 | 1290 | 0:19 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 19 | 2023-05-19 | 24510 | keep | 0 | May | 2023 | 0.016694 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
BAYAMON | 2023-05-19 09:09 | 2023-05-19 12:22 | 70 | 3:13 | P | CAUSAS EXTERNAS | 2X65 EN C/L PERSONAL DEL MUNICIPIO REALIZANDO DESGANCHE | B23051900072 | New_Event | Damage From Public | Include | Include | Public | 193 | 2023-05-19 | 13510 | keep | 0 | May | 2023 | 0.0092016 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-05-19 09:12 | 2023-05-19 14:23 | 2 | 5:11 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23051900075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2023-05-19 | 622 | keep | 0 | May | 2023 | 0.00042364 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-05-19 09:32 | 2023-05-19 10:47 | 1648 | 1:15 | T | CAUSAS EXTERNAS | SE CERRO INTERRUPTOR EN SUBESTACION Y SE RETIRO CHRINGA CON VARETA DESDE EL PISO. 100% EN SERVICIO | R23051900028 | New_Event | Damage From Public | Include | Include | Public | 75 | 2023-05-19 | 123600 | keep | 0 | May | 2023 | 0.084183 | 0.0011224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1648
CAGUAS | 2023-05-19 09:38 | 2023-05-19 12:30 | 5 | 2:52 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 37.5KVA X 50KVA | C23051900062 | New_Event | Service Transformer Failure | Include | Include | Equipment | 172 | 2023-05-19 | 860 | keep | 0 | May | 2023 | 0.00058574 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-05-19 09:42 | 2023-05-19 12:12 | 30 | 2:30 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051900035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-05-19 | 4500 | keep | 0 | May | 2023 | 0.0030649 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-19 09:58 | 2023-05-19 13:00 | 30 | 3:02 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23051900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-05-19 | 5460 | keep | 0 | May | 2023 | 0.0037188 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-19 10:08 | 2023-05-19 11:14 | 2524 | 1:06 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIEMTADOR POR AISLADOR PARTIDO ENTRO 75% EN SERVICIO | R23051900049 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 66 | 2023-05-19 | 166584 | keep | 0 | May | 2023 | 0.11346 | 0.0017191 | Sustained | FALSE | FALSE | Not_TMED_Event | 2524
SAN JUAN | 2023-05-19 10:10 | 2023-05-19 10:12 | 73 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO 1404-07 SE PROBO QUEDO EN SERVICIO LLEVA 5% DEL 1112-04 | S23051900085 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-19 | 146 | keep | 0 | May | 2023 | 9.944e-05 | 4.972e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2023-05-19 10:10 | 2023-05-19 10:12 | 1357 | 0:02 | T | DESGANCHE | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 5% DEL 1112-04 | S23051900085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-05-19 | 2714 | keep | 0 | May | 2023 | 0.0018485 | 0.00092425 | Momentary | FALSE | FALSE | Not_TMED_Event | 1357
MAYAGÃœEZ | 2023-05-19 10:13 | 2023-05-19 11:46 | 1352 | 1:33 | T | CONDUCTOR ROTO O ABIERTO | GOI-MY-230519-01 CERRAR PUENTE EN TRONCAL | M23051900099 | New_Event | Primary Wire Break | Include | Include | Equipment | 93 | 2023-05-19 | 125736 | keep | 0 | May | 2023 | 0.085638 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-05-19 10:13 | 2023-05-19 11:46 | 871 | 1:33 | T | CONDUCTOR ROTO O ABIERTO | GOI-MY-230519-01 CERRAR PUENTE EN TRONCAL | M23051900099 | New_Event | Primary Wire Break | Include | Include | Equipment | 93 | 2023-05-19 | 81003 | keep | 0 | May | 2023 | 0.055171 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
SAN JUAN | 2023-05-19 10:14 | 2023-05-19 12:06 | 73 | 1:52 | P | ALIMENTADOR AMARRADO | DISPARO 1404-07 SE PROBO QUEDO EN SERVICIO LLEVA 5% DEL 1112-04 | S23051900085 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 112 | 2023-05-19 | 8176 | keep | 0 | May | 2023 | 0.0055686 | 4.972e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 73
SAN JUAN | 2023-05-19 10:14 | 2023-05-19 12:06 | 1357 | 1:52 | T | DESGANCHE | DISPARO SE ABRIO MACHETE PARA SECCIONALIZAR DESGANCHE PRIMARIO Y AISLADOR PARTIDO. SE CERRO INTERRUPTOR 10% EN SERVICIO, LLEVA 5% DEL 1112-04 | S23051900087 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-05-19 | 151984 | keep | 0 | May | 2023 | 0.10352 | 0.00092425 | Sustained | FALSE | FALSE | Not_TMED_Event | 1357
GUAYAMA | 2023-05-19 10:14 | 2023-05-19 12:06 | 75 | 1:52 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L SE REPARO BAJANTE PRIMARIO EN C/L | P23051900089 | New_Event | Primary Wire Break | Include | Include | Equipment | 112 | 2023-05-19 | 8400 | keep | 0 | May | 2023 | 0.0057212 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
HUMACAO | 2023-05-19 10:16 | 2023-05-19 10:20 | 2126 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL SE VERIFICO PERSONAL FUERA | C23051900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-19 | 8504 | keep | 0 | May | 2023 | 0.005792 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
SAN JUAN | 2023-05-19 10:26 | 2023-05-19 10:28 | 1681 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE PROBO POR CONTROL QUEDO EN SERVICIO | S23051900099 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-19 | 3362 | keep | 0 | May | 2023 | 0.0022898 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
BAYAMON | 2023-05-19 10:36 | 2023-05-19 14:59 | 894 | 4:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X140 EN C/L POR LLUVIA | S23051600107 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 263 | 2023-05-19 | 235122 | keep | 0 | May | 2023 | 0.16014 | 0.0006089 | Sustained | FALSE | FALSE | Not_TMED_Event | 894
MAYAGÃœEZ | 2023-05-19 10:38 | 2023-05-19 16:01 | 50 | 5:23 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051900080 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 323 | 2023-05-19 | 16150 | keep | 0 | May | 2023 | 0.011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-19 10:44 | 2023-05-19 14:57 | 30 | 4:13 | P | MAL TIEMPO/RAYOS | 1 X 140 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23051900046 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 253 | 2023-05-19 | 7590 | keep | 0 | May | 2023 | 0.0051695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-19 10:47 | 2023-05-19 19:14 | 43 | 8:27 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | S23051900115 | New_Event | Primary Wire Break | Include | Include | Equipment | 507 | 2023-05-19 | 21801 | keep | 0 | May | 2023 | 0.014849 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2023-05-19 10:47 | 2023-05-19 12:17 | 50 | 1:30 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | R23051900009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-05-19 | 4500 | keep | 0 | May | 2023 | 0.0030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-19 10:51 | 2023-05-19 10:52 | 1320 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23051900083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 1320 | keep | 0 | May | 2023 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
SAN JUAN | 2023-05-19 10:55 | 2023-05-19 12:14 | 9 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23051900120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2023-05-19 | 711 | keep | 0 | May | 2023 | 0.00048426 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-05-19 10:56 | 2023-05-19 14:22 | 200 | 3:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO LLUVIAS FUERTES | C23051900084 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 206 | 2023-05-19 | 41200 | keep | 0 | May | 2023 | 0.028061 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-05-19 11:00 | 2023-05-19 11:58 | 65 | 0:58 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23051900136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 58 | 2023-05-19 | 3770 | keep | 0 | May | 2023 | 0.0025677 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
GUAYAMA | 2023-05-19 11:00 | 2023-05-19 13:00 | 75 | 2:00 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR | P23051900106 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 120 | 2023-05-19 | 9000 | keep | 0 | May | 2023 | 0.0061299 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-05-19 11:14 | 2023-05-19 11:35 | 631 | 0:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIEMTADOR POR AISLADOR PARTIDO ENTRO 75% EN SERVICIO | R23051900049 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 21 | 2023-05-19 | 13251 | keep | 0 | May | 2023 | 0.0090252 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-19 11:22 | 2023-05-19 14:30 | 1 | 3:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR SE REPORTA FUERTES LLUVIAS | R23051900068 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 188 | 2023-05-19 | 188 | keep | 0 | May | 2023 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-19 11:27 | 2023-05-19 12:24 | 25 | 0:57 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | R23051900071 | New_Event | Animals | Include | Include | Wildlife | 57 | 2023-05-19 | 1425 | keep | 0 | May | 2023 | 0.00097056 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-19 11:37 | 2023-05-19 11:41 | 844 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO LLEVA 35% DEL 1345-05 | S23051900142 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-19 | 3376 | keep | 0 | May | 2023 | 0.0022994 | 0.00057484 | Momentary | FALSE | FALSE | Not_TMED_Event | 844
SAN JUAN | 2023-05-19 11:37 | 2023-05-19 11:41 | 619 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO SE PROBO QUEDO EN SERVICIO 35% POR 1330-04 | S23051900142 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-19 | 2476 | keep | 0 | May | 2023 | 0.0016864 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
PONCE | 2023-05-19 11:43 | 2023-05-19 12:40 | 10 | 0:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23051900118 | New_Event | Primary Wire Break | Include | Include | Equipment | 57 | 2023-05-19 | 570 | keep | 0 | May | 2023 | 0.00038822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-19 11:46 | 2023-05-20 10:48 | 6 | 23:02 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR AVERIADO SE ABRIO INTERRUPTOR PARA ABRIR CORTE DE LINEA Y SECCIONALIZAR PARA PODER SER REMPLAZADO | A23051900063 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1382 | 2023-05-19 | 8292 | keep | 0 | May | 2023 | 0.0056476 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-05-19 11:55 | 2023-05-19 14:03 | 1 | 2:08 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051900102 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 128 | 2023-05-19 | 128 | keep | 0 | May | 2023 | 8.718e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-19 12:00 | 2023-05-19 13:48 | 8 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23051900115 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2023-05-19 | 864 | keep | 0 | May | 2023 | 0.00058847 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-19 12:02 | 2023-05-20 00:29 | 236 | 12:27 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | S23051900159 | New_Event | Vegetation Contact | Include | Include | Vegetation | 747 | 2023-05-19 | 176292 | keep | 0 | May | 2023 | 0.12007 | 0.00016074 | Sustained | FALSE | FALSE | Not_TMED_Event | 236
SAN JUAN | 2023-05-19 12:06 | 2023-05-19 14:05 | 1221 | 1:59 | P | DESGANCHE | REALIZANDO OPERACIONES PARA SECCIONALIZAR ALIMENTADOR HUBO DISPARO | S23051900087 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-05-19 | 145299 | keep | 0 | May | 2023 | 0.098962 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-19 12:06 | 2023-05-19 14:11 | 6 | 2:05 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR Y 1 X 20 EN RISER SE NECESITA DESGANCHE | M23051900104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-05-19 | 750 | keep | 0 | May | 2023 | 0.00051082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-19 12:10 | 2023-05-19 16:53 | 1950 | 4:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PRIMARIO PARTIDO MEDIANTE G.O.I. BY-230519-01 | B23051900094 | New_Event | Primary Pole Failure | Include | Include | Equipment | 283 | 2023-05-19 | 551850 | keep | 0 | May | 2023 | 0.37586 | 0.0013281 | Sustained | FALSE | FALSE | Not_TMED_Event | 1950
HUMACAO | 2023-05-19 12:12 | 2023-05-19 15:06 | 2354 | 2:54 | T | TERMINACION SOTERRADA AVERIADA | CG-230519-03 DISPARO | C23051900122 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 174 | 2023-05-19 | 409596 | keep | 0 | May | 2023 | 0.27897 | 0.0016033 | Sustained | FALSE | FALSE | Not_TMED_Event | 2354
PONCE | 2023-05-19 12:12 | 2023-05-19 16:20 | 50 | 4:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 50 EN C/L SE REMPLAZO 2 CAJAS EN C/L | P23051900124 | New_Event | Cutout Failure | Include | Include | Equipment | 248 | 2023-05-19 | 12400 | keep | 0 | May | 2023 | 0.0084456 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-19 12:20 | 2023-05-19 12:53 | 1 | 0:33 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE | C23051900123 | New_Event | Animals | Include | Include | Wildlife | 33 | 2023-05-19 | 33 | keep | 0 | May | 2023 | 2.2476e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-19 12:25 | 2023-05-19 14:46 | 40 | 2:21 | P | DESGANCHE | 1X40 EN C/L DESGANCHE | B23051900118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-05-19 | 5640 | keep | 0 | May | 2023 | 0.0038414 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-19 12:26 | 2023-05-19 18:50 | 50 | 6:24 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23051900077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2023-05-19 | 19200 | keep | 0 | May | 2023 | 0.013077 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-19 12:30 | 2023-05-19 13:28 | 1 | 0:58 | P | ANIMAL | 1 X 20 EN BANCO DE XMR CRUCE X AVE | C23051900127 | New_Event | Animals | Include | Include | Wildlife | 58 | 2023-05-19 | 58 | keep | 0 | May | 2023 | 3.9504e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-19 12:34 | 2023-05-20 13:04 | 6 | 24:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23051900228 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1470 | 2023-05-19 | 8820 | keep | 0 | May | 2023 | 0.0060073 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-19 12:48 | 2023-05-19 18:15 | 100 | 5:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ABIERTO HACIA MACHETE LLEVA 90% 1401-08 | S23051900175 | New_Event | Primary Wire Break | Include | Include | Equipment | 327 | 2023-05-19 | 32700 | keep | 0 | May | 2023 | 0.022272 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-19 12:48 | 2023-05-19 18:15 | 122 | 5:27 | P | ALIMENTADOR AMARRADO | SE REPARO BAJJANTE ABIERTO HACIA MACHETE LLEVA 90% 1401-08 | S23051900175 | New_Event | Feeder Load Transferred | Include | Include | Other | 327 | 2023-05-19 | 39894 | keep | 0 | May | 2023 | 0.027172 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
GUAYAMA | 2023-05-19 12:52 | 2023-05-19 14:00 | 15 | 1:08 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23051900133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-05-19 | 1020 | keep | 0 | May | 2023 | 0.00069472 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-19 12:55 | 2023-05-20 11:04 | 1 | 22:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN RISER SE REMPLAZO PORTAFUSIBLE | S23051900181 | New_Event | Cutout Failure | Include | Include | Equipment | 1329 | 2023-05-19 | 1329 | keep | 0 | May | 2023 | 0.00090518 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-19 13:00 | 2023-05-19 16:30 | 51 | 3:30 | P | CAUSAS EXTERNAS | SE ABRIO C/L Y SE RETIRARON SECUNDARIAS Y SE RELOCAIZO XMR TRASPATIO. CASO JUDICIAL POR INVACION SERVIDUMBRE 21-1-048 | S23051900118 | New_Event | Damage From Public | Include | Include | Public | 210 | 2023-05-19 | 10710 | keep | 0 | May | 2023 | 0.0072945 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
ARECIBO | 2023-05-19 13:00 | 2023-05-19 15:14 | 75 | 2:14 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23051900086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 134 | 2023-05-19 | 10050 | keep | 0 | May | 2023 | 0.006845 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-05-19 13:01 | 2023-05-19 13:02 | 1533 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23051900190 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 1533 | keep | 0 | May | 2023 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
HUMACAO | 2023-05-19 13:02 | 2023-05-19 15:41 | 34 | 2:39 | P | DESGANCHE | 1 X 30 1 X 20 EN C/L | C23051900134 | New_Event | Vegetation Contact | Include | Include | Vegetation | 159 | 2023-05-19 | 5406 | keep | 0 | May | 2023 | 0.003682 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2023-05-19 13:03 | 2023-05-19 13:05 | 250 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO INTERUPTOR SE PROBO QUEDO EN SERVICIO LLEVA 20% DEL 1348-06 Y LLEVA 1348-08 | S23051900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-19 | 500 | keep | 0 | May | 2023 | 0.00034055 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-05-19 13:03 | 2023-05-19 13:05 | 1290 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO INTERUPTOR SE PROBO QUEDO EN SERVICIO LLEVA 20% DEL 1348-06 Y LLEVA 1348-08 | S23051900000 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-19 | 2580 | keep | 0 | May | 2023 | 0.0017572 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-05-19 13:03 | 2023-05-19 13:05 | 13 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO INTERUPTOR SE PROBO QUEDO EN SERVICIO LLEVA 20% DEL 1348-06 Y LLEVA 1348-08 90% DE SU CARGA POR 1303-02 | S23051900000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-19 | 26 | keep | 0 | May | 2023 | 1.7708e-05 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-05-19 13:06 | 2023-05-20 06:36 | 60 | 17:30 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | B23051900125 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1050 | 2023-05-19 | 63000 | keep | 0 | May | 2023 | 0.042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-19 13:07 | 2023-05-19 15:30 | 140 | 2:23 | P | DESGANCHE | DESGANCHE 2 X 50 EN C/L | C23051900136 | New_Event | Vegetation Contact | Include | Include | Vegetation | 143 | 2023-05-19 | 20020 | keep | 0 | May | 2023 | 0.013636 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
BAYAMON | 2023-05-19 13:08 | 2023-05-20 06:52 | 200 | 17:44 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE TRASPATIO | B23051900128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1064 | 2023-05-19 | 212800 | keep | 0 | May | 2023 | 0.14494 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-05-19 13:09 | 2023-05-19 15:10 | 15 | 2:01 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051900120 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 121 | 2023-05-19 | 1815 | keep | 0 | May | 2023 | 0.0012362 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-19 13:11 | 2023-05-19 14:12 | 3957 | 1:01 | T | CRUCETA DEFECTUOSA O AVERIADA | SJ-230519-02 SE SECCIONALIZO CRUCETA VIRADA Y NEUTRAL PRIMARIO PARTIDO Y SE CERRO POR CONTROL. 40% EN SERVICIO | S23051900203 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 61 | 2023-05-19 | 241377 | keep | 0 | May | 2023 | 0.1644 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2023-05-19 13:15 | 2023-05-19 13:26 | 1825 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23051900209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 20075 | keep | 0 | May | 2023 | 0.013673 | 0.001243 | Sustained | FALSE | FALSE | Not_TMED_Event | 1825
SAN JUAN | 2023-05-19 13:15 | 2023-05-19 13:26 | 47 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23051900209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 517 | keep | 0 | May | 2023 | 0.00035213 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
SAN JUAN | 2023-05-19 13:15 | 2023-05-19 13:26 | 315 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23051900209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 3465 | keep | 0 | May | 2023 | 0.00236 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
SAN JUAN | 2023-05-19 13:15 | 2023-05-19 13:26 | 2 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23051900209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 22 | keep | 0 | May | 2023 | 1.4984e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-19 13:15 | 2023-05-19 13:26 | 2391 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | S23051900209 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 26301 | keep | 0 | May | 2023 | 0.017913 | 0.0016285 | Sustained | FALSE | FALSE | Not_TMED_Event | 2391
CAGUAS | 2023-05-19 13:15 | 2023-05-19 13:26 | 2276 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 25036 | keep | 0 | May | 2023 | 0.017052 | 0.0015502 | Sustained | FALSE | FALSE | Not_TMED_Event | 2276
CAGUAS | 2023-05-19 13:15 | 2023-05-19 13:26 | 777 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 8547 | keep | 0 | May | 2023 | 0.0058213 | 0.00052921 | Sustained | FALSE | FALSE | Not_TMED_Event | 777
CAGUAS | 2023-05-19 13:15 | 2023-05-19 13:26 | 12 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 132 | keep | 0 | May | 2023 | 8.9905e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-19 13:15 | 2023-05-19 13:26 | 1290 | 0:11 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23051900138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 11 | 2023-05-19 | 14190 | keep | 0 | May | 2023 | 0.0096647 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
GUAYAMA | 2023-05-19 13:22 | 2023-05-19 15:00 | 100 | 1:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 65 EN C/L SE REMPLAZO AISLADOR | P23051900119 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 98 | 2023-05-19 | 9800 | keep | 0 | May | 2023 | 0.0066747 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-19 13:22 | 2023-05-19 16:55 | 50 | 3:33 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051900125 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 213 | 2023-05-19 | 10650 | keep | 0 | May | 2023 | 0.0072537 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-19 13:23 | 2023-05-19 18:26 | 75 | 5:03 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | B23051900140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-05-19 | 22725 | keep | 0 | May | 2023 | 0.015478 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-05-19 13:25 | 2023-05-19 18:10 | 10 | 4:45 | P | DESGANCHE | 1 X 20 EN AEREO PROVISIONAL DESGANCHE | S23051900222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2023-05-19 | 2850 | keep | 0 | May | 2023 | 0.0019411 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-05-19 13:30 | 2023-05-19 14:00 | 6 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23051900141 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-05-19 | 180 | keep | 0 | May | 2023 | 0.0001226 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-19 13:38 | 2023-05-19 16:30 | 14 | 2:52 | P | DESGANCHE | 1 X 15 EN XMR Y 1 X 20 EN C/L SE REALIZO DESGANCHE | S23051900237 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-05-19 | 2408 | keep | 0 | May | 2023 | 0.0016401 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-05-19 13:45 | 2023-05-19 18:48 | 230 | 5:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN CORTE DE LINEA SE REEMPLAZARON DISCOS EXPLOTADOS | C23051900152 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 303 | 2023-05-19 | 69690 | keep | 0 | May | 2023 | 0.047466 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
BAYAMON | 2023-05-19 13:48 | 2023-05-20 08:04 | 20 | 18:16 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23051900164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1096 | 2023-05-19 | 21920 | keep | 0 | May | 2023 | 0.01493 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-19 13:55 | 2023-05-20 21:08 | 12 | 31:13 | P | TRANSFORMADOR AVERIADO | 2X25 EN XMR SE REMPLAZO XMR 50KVA X 50KVA | S23051900262 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1873 | 2023-05-19 | 22476 | keep | 0 | May | 2023 | 0.015308 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-19 13:57 | 2023-05-20 10:53 | 70 | 20:56 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | S23051900265 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1256 | 2023-05-19 | 87920 | keep | 0 | May | 2023 | 0.059882 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-05-19 13:59 | 2023-05-19 16:09 | 23 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO BAJANTE | C23051900161 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-05-19 | 2990 | keep | 0 | May | 2023 | 0.0020365 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-05-19 14:03 | 2023-05-19 16:57 | 867 | 2:54 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR CONTROL 10% EN SERVICIO | S23051900279 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2023-05-19 | 150858 | keep | 0 | May | 2023 | 0.10275 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2023-05-19 14:03 | 2023-05-19 14:04 | 1192 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA POR 7008-05 | M23051900141 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-19 | 1192 | keep | 0 | May | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2023-05-19 14:03 | 2023-05-19 14:04 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051900141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 3041 | keep | 0 | May | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
FAJARDO | 2023-05-19 14:04 | 2023-05-19 16:54 | 1 | 2:50 | P | DESGANCHE | 1 X 50 Y 2 X 40 EN C/L | R23051900095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 170 | 2023-05-19 | 170 | keep | 0 | May | 2023 | 0.00011579 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-19 14:04 | 2023-05-19 14:30 | 1 | 0:26 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051900102 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 26 | 2023-05-19 | 26 | keep | 0 | May | 2023 | 1.7708e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-19 14:04 | 2023-05-19 18:35 | 20 | 4:31 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M23051900192 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 271 | 2023-05-19 | 5420 | keep | 0 | May | 2023 | 0.0036915 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-19 14:05 | 2023-05-19 14:06 | 73 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO 1404-07 SE PROBO QUEDO EN SERVICIO LLEVA 5% DEL 1112-04 | S23051900085 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-19 | 73 | keep | 0 | May | 2023 | 4.972e-05 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 14:05 | 2023-05-19 14:06 | 1357 | 0:01 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE CERRO POR CONTROL . EN SERVICIO 10% 1404-07 Y 5% 1112-04 | S23051900087 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-19 | 1357 | keep | 0 | May | 2023 | 0.00092425 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 14:06 | 2023-05-19 14:46 | 1221 | 0:40 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO Y SE REEMPLAZO AISLADOR SJ-230519-01 | S23051900087 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 40 | 2023-05-19 | 48840 | keep | 0 | May | 2023 | 0.033265 | 0.00083162 | Sustained | FALSE | FALSE | Not_TMED_Event | 1221
GUAYAMA | 2023-05-19 14:11 | 2023-05-19 16:30 | 8 | 2:19 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE | P23051900152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-19 | 1112 | keep | 0 | May | 2023 | 0.00075738 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-19 14:12 | 2023-05-19 14:21 | 2374 | 0:09 | P | CRUCETA DEFECTUOSA O AVERIADA | SE SECCIONALIZO CRUCETA VIRADA Y NEUTRAL PRIMARIO PARTIDO Y SE PASO 40% DE LA CARGA AL 1346-03 | S23051900203 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 9 | 2023-05-19 | 21366 | keep | 0 | May | 2023 | 0.014552 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-19 14:15 | 2023-05-19 14:30 | 3438 | 0:15 | T | DESGANCHE | SE SECCIONALIZO TRAMO PRIMARIO PARA DESGANCHE A VARETA (DESDE EL SUELO) MEDIANTE SWITCHING-FORM BY-230519-02 - 15% EN SERVICIO | B23051900126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 15 | 2023-05-19 | 51570 | keep | 0 | May | 2023 | 0.035124 | 0.0023416 | Sustained | FALSE | FALSE | Not_TMED_Event | 3438
HUMACAO | 2023-05-19 14:15 | 2023-05-19 18:02 | 100 | 3:47 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA | C23051900167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-05-19 | 22700 | keep | 0 | May | 2023 | 0.015461 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-19 14:21 | 2023-05-19 14:23 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-19 | 3230 | keep | 0 | May | 2023 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
SAN JUAN | 2023-05-19 14:21 | 2023-05-19 15:59 | 791 | 1:38 | P | CRUCETA DEFECTUOSA O AVERIADA | SE REPARO CRUCETA VIRADA Y SE REPARO NEUTRAL PRIMARIO | S23051900203 | Partial_restoration | Primary Crossarm Failure | Include | Include | Equipment | 98 | 2023-05-19 | 77518 | keep | 0 | May | 2023 | 0.052797 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:26 | 959 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-19 | 2877 | keep | 0 | May | 2023 | 0.0019595 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:26 | 1382 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-19 | 4146 | keep | 0 | May | 2023 | 0.0028238 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:26 | 663 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900196 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-19 | 1989 | keep | 0 | May | 2023 | 0.0013547 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 1715 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 3430 | keep | 0 | May | 2023 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 1498 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 2996 | keep | 0 | May | 2023 | 0.0020406 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 1221 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 2442 | keep | 0 | May | 2023 | 0.0016632 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 1100 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900215 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 2200 | keep | 0 | May | 2023 | 0.0014984 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 1514 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900252 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 3028 | keep | 0 | May | 2023 | 0.0020624 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 1105 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900252 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 2210 | keep | 0 | May | 2023 | 0.0015052 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 4176 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900253 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 8352 | keep | 0 | May | 2023 | 0.0056885 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 252 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900253 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 504 | keep | 0 | May | 2023 | 0.00034327 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 2147 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900253 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 4294 | keep | 0 | May | 2023 | 0.0029246 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-05-19 14:23 | 2023-05-19 14:25 | 2858 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23051900254 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-19 | 5716 | keep | 0 | May | 2023 | 0.0038931 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
GUAYAMA | 2023-05-19 14:25 | 2023-05-19 16:35 | 40 | 2:10 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23051900154 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-05-19 | 5200 | keep | 0 | May | 2023 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-19 14:25 | 2023-05-19 18:10 | 80 | 3:45 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23051900145 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 225 | 2023-05-19 | 18000 | keep | 0 | May | 2023 | 0.01226 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-19 14:27 | 2023-05-20 10:05 | 1 | 19:38 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 25 KVA X 10 KVA | M23051900147 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1178 | 2023-05-19 | 1178 | keep | 0 | May | 2023 | 0.00080233 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-19 14:30 | 2023-05-19 15:33 | 2922 | 1:03 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO A VARETA (DESDE EL SUELO) MEDIANTE SWITCHING-FORM BY-230519-02 - 100% EN SERVICIO | B23051900126 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-05-19 | 184086 | keep | 0 | May | 2023 | 0.12538 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-05-19 14:31 | 2023-05-19 16:40 | 60 | 2:09 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23051900114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 129 | 2023-05-19 | 7740 | keep | 0 | May | 2023 | 0.0052717 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-19 14:33 | 2023-05-19 14:34 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S230519000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 4291 | keep | 0 | May | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
BARRANQUITAS | 2023-05-19 14:42 | 2023-05-19 18:40 | 200 | 3:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN CORTE DE LINEA LLUVIA VIENTO | C23051900176 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 238 | 2023-05-19 | 47600 | keep | 0 | May | 2023 | 0.03242 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CAGUAS | 2023-05-19 14:46 | 2023-05-19 17:56 | 100 | 3:10 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C23051900180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-05-19 | 19000 | keep | 0 | May | 2023 | 0.012941 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-05-19 14:48 | 2023-05-20 09:51 | 1 | 19:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A23051900126 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1143 | 2023-05-19 | 1143 | keep | 0 | May | 2023 | 0.00077849 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-19 14:49 | 2023-05-19 16:42 | 100 | 1:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23051900127 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-05-19 | 11300 | keep | 0 | May | 2023 | 0.0076964 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-19 14:50 | 2023-05-19 14:51 | 2435 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1909-08 LLEVA LA CARGA DEL 1907-05 | S23051900324 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-19 | 2435 | keep | 0 | May | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-19 14:50 | 2023-05-19 14:51 | 2956 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR 1909-08 LLEVA LA CARGA DEL 1907-05 | S23051900324 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-19 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
FAJARDO | 2023-05-19 14:56 | 2023-05-19 18:22 | 40 | 3:26 | P | DESGANCHE | 1 X 40 EN C/L SE DESGANCHO | R23051900102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-05-19 | 8240 | keep | 0 | May | 2023 | 0.0056122 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-19 14:56 | 2023-05-20 08:20 | 1 | 17:24 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE DE BAMBUA | A23051900128 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1044 | 2023-05-19 | 1044 | keep | 0 | May | 2023 | 0.00071106 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-19 14:57 | 2023-05-19 18:43 | 100 | 3:46 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE X AVE | C23051900187 | New_Event | Animals | Include | Include | Wildlife | 226 | 2023-05-19 | 22600 | keep | 0 | May | 2023 | 0.015393 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-19 15:02 | 2023-05-19 16:52 | 47 | 1:50 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C23051900192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-05-19 | 5170 | keep | 0 | May | 2023 | 0.0035213 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2023-05-19 15:06 | 2023-05-19 15:07 | 1533 | 0:01 | T | ANIMAL | RECERRO | S23051900249 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-19 | 1533 | keep | 0 | May | 2023 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
HUMACAO | 2023-05-19 15:06 | 2023-05-19 15:11 | 120 | 0:05 | P | TERMINACION SOTERRADA AVERIADA | CG-230519-03 SE CERRO PUENTE ABRIETO EN DISCONECTIVO HACIA PB-2 | C23051900122 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 5 | 2023-05-19 | 600 | keep | 0 | May | 2023 | 0.00040866 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-19 15:07 | 2023-05-20 05:00 | 78 | 13:53 | P | ANIMAL | 1 X 65 EN C/L CRCE X AVE | S23051900407 | 1st_after_momentary | Animals | Include | Include | Wildlife | 833 | 2023-05-19 | 64974 | keep | 0 | May | 2023 | 0.044253 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
SAN JUAN | 2023-05-19 15:08 | 2023-05-19 17:23 | 28 | 2:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L LLUVIA FUERTE | S23051900377 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 135 | 2023-05-19 | 3780 | keep | 0 | May | 2023 | 0.0025745 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
BAYAMON | 2023-05-19 15:10 | 2023-05-19 18:12 | 593 | 3:02 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO EN TRONCAL DE ALIMENTADOR MEDIANTE G.O.I. BY-230519-04 | S23051900381 | New_Event | Primary Wire Break | Include | Include | Equipment | 182 | 2023-05-19 | 107926 | keep | 0 | May | 2023 | 0.073508 | 0.00040389 | Sustained | FALSE | FALSE | Not_TMED_Event | 593
HUMACAO | 2023-05-19 15:11 | 2023-05-19 15:21 | 2354 | 0:10 | T | TERMINACION SOTERRADA AVERIADA | CG-230519-03 DISPARO PERSONAL REALIZANDO OPERACIONES CERRANDO PB-2 | C23051900122 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 10 | 2023-05-19 | 23540 | keep | 0 | May | 2023 | 0.016033 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-19 15:12 | 2023-05-19 18:07 | 15 | 2:55 | P | DESGANCHE | 1 X 30 EN C/L SE DESGANCHO | R23051900108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-05-19 | 2625 | keep | 0 | May | 2023 | 0.0017879 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-05-19 15:14 | 2023-05-19 17:10 | 40 | 1:56 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23051900164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 116 | 2023-05-19 | 4640 | keep | 0 | May | 2023 | 0.0031603 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-19 15:16 | 2023-05-19 17:43 | 260 | 2:27 | P | DESGANCHE | 2 X 50 EN CORTES DE LINEA | C23051900197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-05-19 | 38220 | keep | 0 | May | 2023 | 0.026031 | 0.00017708 | Sustained | FALSE | FALSE | Not_TMED_Event | 260
CAGUAS | 2023-05-19 15:19 | 2023-05-19 18:58 | 170 | 3:39 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA | C23051900198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2023-05-19 | 37230 | keep | 0 | May | 2023 | 0.025357 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
HUMACAO | 2023-05-19 15:21 | 2023-05-19 15:40 | 120 | 0:19 | P | TERMINACION SOTERRADA AVERIADA | CG-230519-03 SECCIONALIZADO PB-1, 2 Y 3 LOCALIZANDO AVERIA | C23051900122 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 19 | 2023-05-19 | 2280 | keep | 0 | May | 2023 | 0.0015529 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-19 15:40 | 2023-05-19 16:10 | 111 | 0:30 | P | TERMINACION SOTERRADA AVERIADA | CG-230519-03 SE CERRO PB-3 LOCALIZANDO AVERIA | C23051900122 | Partial_restoration | UG Cable Termination Failure | Include | Include | Equipment | 30 | 2023-05-19 | 3330 | keep | 0 | May | 2023 | 0.002268 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-19 16:00 | 2023-05-19 18:00 | 100 | 2:00 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23051900178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-05-19 | 12000 | keep | 0 | May | 2023 | 0.0081731 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-05-19 16:10 | 2023-05-19 16:19 | 1349 | 0:09 | P | TERMINACION SOTERRADA AVERIADA | CG-230519-03 SE CERRO PB-1 LOCALIZANDO AVERIA | C23051900122 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 9 | 2023-05-19 | 12141 | keep | 0 | May | 2023 | 0.0082692 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 16:12 | 2023-05-19 20:02 | 1500 | 3:50 | P | NO SE REPORTO CAUSA | SE CERRO BKR EN SUBESTACION CON PARTE DE SU CARGA POR 1346-02 Y LLEVANDO 1346-04 | S23051900483 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 230 | 2023-05-19 | 345000 | keep | 0 | May | 2023 | 0.23498 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
SAN JUAN | 2023-05-19 16:12 | 2023-05-19 20:02 | 3932 | 3:50 | T | ALIMENTADOR AMARRADO | SE CERRO BKR EN SUBESTACION CON PARTE DE SU CARGA POR 1346-02 Y LLEVANDO 1346-04 | S23051900483 | New_Event | Feeder Load Transferred | Include | Include | Other | 230 | 2023-05-19 | 904360 | keep | 0 | May | 2023 | 0.61596 | 0.0026781 | Sustained | FALSE | FALSE | Not_TMED_Event | 3932
PONCE | 2023-05-19 16:17 | 2023-05-19 17:12 | 3114 | 0:55 | T | DESGANCHE | SE DESGANCHO | P23051900184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-05-19 | 171270 | keep | 0 | May | 2023 | 0.11665 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
ARECIBO | 2023-05-19 16:18 | 2023-05-19 17:12 | 8 | 0:54 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23051900144 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 54 | 2023-05-19 | 432 | keep | 0 | May | 2023 | 0.00029423 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-19 16:19 | 2023-05-19 16:23 | 2354 | 0:04 | T | TERMINACION SOTERRADA AVERIADA | CG-230519-03 DISPARO TRAMO AVERIADO DEL SG13 HACIA PB-2 | C23051900122 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 4 | 2023-05-19 | 9416 | keep | 0 | May | 2023 | 0.0064132 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-19 16:23 | 2023-05-19 17:01 | 774 | 0:38 | P | TERMINACION SOTERRADA AVERIADA | CG-230519-03 DISPARO SE SECCIONALIZO TRAMO SG-13 HACIA PB-2 SE CERRO N/O EN EL PB-F | C23051900122 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 38 | 2023-05-19 | 29412 | keep | 0 | May | 2023 | 0.020032 | 0.00052717 | Sustained | FALSE | FALSE | Not_TMED_Event | 774
MAYAGÃœEZ | 2023-05-19 16:31 | 2023-05-19 22:17 | 25 | 5:46 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051900177 | New_Event | Vegetation Contact | Include | Include | Vegetation | 346 | 2023-05-19 | 8650 | keep | 0 | May | 2023 | 0.0058915 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-19 16:33 | 2023-05-19 18:00 | 1 | 1:27 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO SE REPORTO CAUSA | M23051900178 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 87 | 2023-05-19 | 87 | keep | 0 | May | 2023 | 5.9255e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-19 16:34 | 2023-05-19 18:33 | 1 | 1:59 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE CON AVE | C23051900241 | New_Event | Animals | Include | Include | Wildlife | 119 | 2023-05-19 | 119 | keep | 0 | May | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-05-19 16:35 | 2023-05-19 18:45 | 10 | 2:10 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | A23051900146 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 130 | 2023-05-19 | 1300 | keep | 0 | May | 2023 | 0.00088542 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-19 16:45 | 2023-05-19 16:54 | 1825 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900676 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-19 | 16425 | keep | 0 | May | 2023 | 0.011187 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 16:45 | 2023-05-19 16:54 | 47 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900676 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-19 | 423 | keep | 0 | May | 2023 | 0.0002881 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 16:45 | 2023-05-19 16:54 | 315 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900676 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-19 | 2835 | keep | 0 | May | 2023 | 0.0019309 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 16:45 | 2023-05-19 16:54 | 2 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900676 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-19 | 18 | keep | 0 | May | 2023 | 1.226e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 16:45 | 2023-05-19 16:54 | 2391 | 0:09 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3000 | S23051900676 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 9 | 2023-05-19 | 21519 | keep | 0 | May | 2023 | 0.014656 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 16:45 | 2023-05-19 16:51 | 3957 | 0:06 | T | NO SE REPORTO CAUSA | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | S23051900610 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 6 | 2023-05-19 | 23742 | keep | 0 | May | 2023 | 0.016171 | 0.0026951 | Sustained | FALSE | FALSE | Not_TMED_Event | 3957
SAN JUAN | 2023-05-19 16:57 | 2023-05-19 17:22 | 780 | 0:25 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR AL REALIZAR OPERACIONES PARA SECCIONALIZAR | S23051900279 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 25 | 2023-05-19 | 19500 | keep | 0 | May | 2023 | 0.013281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-19 17:11 | 2023-05-20 08:21 | 15 | 15:10 | P | DESGANCHE | 1 X 25 EN C/L | B23051900305 | New_Event | Vegetation Contact | Include | Include | Vegetation | 910 | 2023-05-19 | 13650 | keep | 0 | May | 2023 | 0.009297 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-19 17:13 | 2023-05-19 17:14 | 3597 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23051900308 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 3597 | keep | 0 | May | 2023 | 0.0024499 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
CANOVANAS | 2023-05-19 17:16 | 2023-05-20 13:13 | 230 | 19:57 | P | TERMINACION SOTERRADA AVERIADA | SJ-230520-01 TERMINACION QUEMADA DEL MH 10 HACIA TORRE DEL ESTE | R23051900126 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 1197 | 2023-05-19 | 275310 | keep | 0 | May | 2023 | 0.18751 | 0.00015665 | Sustained | FALSE | FALSE | Not_TMED_Event | 230
PONCE | 2023-05-19 17:20 | 2023-05-19 20:13 | 60 | 2:53 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23051900206 | New_Event | Vegetation Contact | Include | Include | Vegetation | 173 | 2023-05-19 | 10380 | keep | 0 | May | 2023 | 0.0070698 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-05-19 17:21 | 2023-05-19 20:00 | 200 | 2:39 | P | ANIMAL | 1 X 200 EN C/L AVE CRUZO LINEAS | P23051900210 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-05-19 | 31800 | keep | 0 | May | 2023 | 0.021659 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
SAN JUAN | 2023-05-19 17:22 | 2023-05-19 17:52 | 867 | 0:30 | T | NO SE REPORTO CAUSA | SE SECCIONALIZO INTERRUPTOR Y SE CERRO POR SCADA 30% EN SERVICIO | S23051900279 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 30 | 2023-05-19 | 26010 | keep | 0 | May | 2023 | 0.017715 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-19 17:36 | 2023-05-19 17:37 | 841 | 0:01 | P | ANIMAL | RECIERRE | C23051900261 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-19 | 841 | keep | 0 | May | 2023 | 0.0005728 | 0.0005728 | Momentary | FALSE | FALSE | Not_TMED_Event | 841
CAGUAS | 2023-05-19 17:37 | 2023-05-19 19:04 | 100 | 1:27 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C23051900262 | 1st_after_momentary | Animals | Include | Include | Wildlife | 87 | 2023-05-19 | 8700 | keep | 0 | May | 2023 | 0.0059255 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-19 17:41 | 2023-05-19 23:55 | 80 | 6:14 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051900187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 374 | 2023-05-19 | 29920 | keep | 0 | May | 2023 | 0.020378 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-19 17:42 | 2023-05-19 19:43 | 5 | 2:01 | P | SECUNDARIA/DESGANCHE | 1X15 EN XMR DESGANCHE SECUNDARIO | S23051900806 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 121 | 2023-05-19 | 605 | keep | 0 | May | 2023 | 0.00041206 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-19 17:52 | 2023-05-19 17:53 | 607 | 0:01 | P | NO SE REPORTO CAUSA | SE CERRO EN MH 4 HACIA MH 2 100% EN SERVICIO SE DEJO TRAMO SIN CARGA SECCIONALIZADO SJ-230519-03 | S23051900279 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 607 | keep | 0 | May | 2023 | 0.00041342 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-19 17:58 | 2023-05-19 21:00 | 40 | 3:02 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23051900223 | New_Event | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-05-19 | 7280 | keep | 0 | May | 2023 | 0.0049584 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-05-19 17:59 | 2023-05-19 20:08 | 8 | 2:09 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23051900158 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 129 | 2023-05-19 | 1032 | keep | 0 | May | 2023 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-05-19 18:19 | 2023-05-19 18:47 | 15 | 0:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23051900128 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 28 | 2023-05-19 | 420 | keep | 0 | May | 2023 | 0.00028606 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-19 18:20 | 2023-05-19 18:21 | 3766 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | R23051900129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 3766 | keep | 0 | May | 2023 | 0.002565 | 0.002565 | Momentary | FALSE | FALSE | Not_TMED_Event | 3766
ARECIBO | 2023-05-19 18:39 | 2023-05-19 20:23 | 60 | 1:44 | P | DESGANCHE | 1 X 65 Y 1 X 40 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23051900163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 104 | 2023-05-19 | 6240 | keep | 0 | May | 2023 | 0.00425 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-19 19:04 | 2023-05-20 11:55 | 45 | 16:51 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA | R23051900131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1011 | 2023-05-19 | 45495 | keep | 0 | May | 2023 | 0.030986 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-05-19 19:07 | 2023-05-20 12:54 | 120 | 17:47 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | S23051900989 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1067 | 2023-05-19 | 128040 | keep | 0 | May | 2023 | 0.087207 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-05-19 19:09 | 2023-05-19 19:10 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
SAN JUAN | 2023-05-19 19:09 | 2023-05-19 20:12 | 5307 | 1:03 | P | DESGANCHE | SE SECCIONALIZO ALIMENTADOR PARA REALIZAR DESGANCHE Y SE CERRO POR CONTROL. 10% EN SERVICIO 15% DE SU CARGA TRANSFERIDA AL 1336-08 | S23051901057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 63 | 2023-05-19 | 334341 | keep | 0 | May | 2023 | 0.22772 | 0.0036146 | Sustained | FALSE | FALSE | Not_TMED_Event | 5307
MAYAGÃœEZ | 2023-05-19 19:09 | 2023-05-20 02:10 | 40 | 7:01 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23051900195 | New_Event | Vegetation Contact | Include | Include | Vegetation | 421 | 2023-05-19 | 16840 | keep | 0 | May | 2023 | 0.01147 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-19 19:12 | 2023-05-19 19:13 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305190000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
BAYAMON | 2023-05-19 19:19 | 2023-05-19 19:20 | 723 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1912-08 LLEVA LA CARGA DEL 1711-02 LLEVA LA CARGA DEL 1711-05 | S2305190000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-19 | 723 | keep | 0 | May | 2023 | 0.00049243 | 0.00049243 | Momentary | FALSE | FALSE | Not_TMED_Event | 723
BAYAMON | 2023-05-19 19:19 | 2023-05-19 19:20 | 1976 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1912-08 LLEVA LA CARGA DEL 1711-02 LLEVA LA CARGA DEL 1711-05 | S2305190000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-19 | 1976 | keep | 0 | May | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
BAYAMON | 2023-05-19 19:19 | 2023-05-19 19:20 | 577 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1912-08 LLEVA LA CARGA DEL 1711-02 LLEVA LA CARGA DEL 1711-05 | S2305190000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 577 | keep | 0 | May | 2023 | 0.00039299 | 0.00039299 | Momentary | FALSE | FALSE | Not_TMED_Event | 577
BAYAMON | 2023-05-19 19:21 | 2023-05-20 10:36 | 80 | 15:15 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | B23051900351 | New_Event | Animals | Include | Include | Wildlife | 915 | 2023-05-19 | 73200 | keep | 0 | May | 2023 | 0.049856 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-05-19 19:28 | 2023-05-19 21:28 | 60 | 2:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | P23051900264 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 120 | 2023-05-19 | 7200 | keep | 0 | May | 2023 | 0.0049039 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-19 19:29 | 2023-05-20 09:12 | 19 | 13:43 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR DEL SUELO 1 X 40 EN CORTE DE LINEA | C23051900302 | New_Event | Primary Wire Break | Include | Include | Equipment | 823 | 2023-05-19 | 15637 | keep | 0 | May | 2023 | 0.01065 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2023-05-19 19:34 | 2023-05-19 21:38 | 25 | 2:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | C23051900304 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 124 | 2023-05-19 | 3100 | keep | 0 | May | 2023 | 0.0021114 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-19 19:50 | 2023-05-19 19:51 | 3458 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23051900208 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 3458 | keep | 0 | May | 2023 | 0.0023552 | 0.0023552 | Momentary | FALSE | FALSE | Not_TMED_Event | 3458
YAUCO | 2023-05-19 19:55 | 2023-05-19 23:37 | 500 | 3:42 | P | CONDUCTOR ROTO O ABIERTO | TIERRA ZAFADA EN MONTURA TRIFASICA HIZO CONTACTO CON ESTRUCTURA 3 X 100 EN CORTE DE LINEA Y 2 X 10 EN MONTURA TRIFASICA | P23051900282 | New_Event | Primary Wire Break | Include | Include | Equipment | 222 | 2023-05-19 | 111000 | keep | 0 | May | 2023 | 0.075602 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
MAYAGÃœEZ | 2023-05-19 20:01 | 2023-05-20 11:05 | 12 | 15:04 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR AVE CRUZO BUSHING | M23051900209 | New_Event | Animals | Include | Include | Wildlife | 904 | 2023-05-19 | 10848 | keep | 0 | May | 2023 | 0.0073885 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-19 20:12 | 2023-05-19 20:52 | 4683 | 0:40 | P | DESGANCHE | SE REALIZO DESGANCHE PRIMARIO Y SE CERRO MACHETES | S23051901057 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 40 | 2023-05-19 | 187320 | keep | 0 | May | 2023 | 0.12758 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-19 20:25 | 2023-05-20 00:11 | 204 | 3:46 | P | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR A PETICION DE PERSONAL EN EL CAMPO PARA ABRIR MACHETES EN MALAS CONDICIONES | S23051901273 | New_Event | Switch Failure | Include | Include | Equipment | 226 | 2023-05-19 | 46104 | keep | 0 | May | 2023 | 0.031401 | 0.00013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 204
ARECIBO | 2023-05-19 20:34 | 2023-05-19 21:36 | 100 | 1:02 | P | DESGANCHE | 1 X 140 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23051900178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-05-19 | 6200 | keep | 0 | May | 2023 | 0.0042228 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-05-19 20:38 | 2023-05-20 02:05 | 1475 | 5:27 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO CONDUCTOR DE PARARRAYO HACIA CAJA PEGANDO A ESTRUCTURA SE ELININO LOS 3 PARARRAYOS | P23051900297 | New_Event | Primary Wire Break | Include | Include | Equipment | 327 | 2023-05-19 | 482325 | keep | 0 | May | 2023 | 0.32851 | 0.0010046 | Sustained | FALSE | FALSE | Not_TMED_Event | 1475
CAGUAS | 2023-05-19 20:58 | 2023-05-20 17:57 | 25 | 20:59 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L | C23051900329 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1259 | 2023-05-19 | 31475 | keep | 0 | May | 2023 | 0.021437 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-19 21:00 | 2023-05-19 22:25 | 25 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23051900174 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2023-05-19 | 2125 | keep | 0 | May | 2023 | 0.0014473 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-19 21:08 | 2023-05-20 10:40 | 6 | 13:32 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y SE REALIZO DESGANCHE MASIVO | B23051900399 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 812 | 2023-05-19 | 4872 | keep | 0 | May | 2023 | 0.0033183 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-19 21:12 | 2023-05-19 21:31 | 5 | 0:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO SECUNDARIA | S23051901228 | New_Event | Secondary Wire Break | Include | Include | Equipment | 19 | 2023-05-19 | 95 | keep | 0 | May | 2023 | 6.4704e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-19 21:29 | 2023-05-20 03:36 | 71 | 6:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | B23051900405 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 367 | 2023-05-19 | 26057 | keep | 0 | May | 2023 | 0.017747 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
PONCE | 2023-05-19 21:52 | 2023-05-20 13:58 | 400 | 16:06 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | SE REMPLAZO SWITCH UNIT TERMINACIONES Y PARARRAYOS | P23051900321 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 966 | 2023-05-19 | 386400 | keep | 0 | May | 2023 | 0.26318 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
SAN JUAN | 2023-05-19 21:59 | 2023-05-19 23:47 | 129 | 1:48 | P | CONDUCTOR ROTO O ABIERTO | 3 X 40 EN RISER Y SE CERRO PUENTES DE LINEA A CAJA. | S23051901260 | New_Event | Primary Wire Break | Include | Include | Equipment | 108 | 2023-05-19 | 13932 | keep | 0 | May | 2023 | 0.009489 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
AGUADILLA | 2023-05-19 22:00 | 2023-05-20 09:25 | 8 | 11:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REEMPLAZO PORTA FUSIBLE | A23051900186 | New_Event | Cutout Failure | Include | Include | Equipment | 685 | 2023-05-19 | 5480 | keep | 0 | May | 2023 | 0.0037324 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-19 22:01 | 2023-05-20 12:00 | 5 | 13:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 37.5 KVA X 37.5 KVA RELACIONAD A WR 6320107 CERRDAO EL DIA ANTERIOR CON CLIENTES SIN SERVCIO | M23052000070 | New_Event | Service Transformer Failure | Include | Include | Equipment | 839 | 2023-05-19 | 4195 | keep | 0 | May | 2023 | 0.0028572 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-05-19 22:17 | 2023-05-20 11:55 | 30 | 13:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | P23051900324 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 818 | 2023-05-19 | 24540 | keep | 0 | May | 2023 | 0.016714 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-05-19 22:20 | 2023-05-19 22:21 | 1457 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23051900325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-19 | 1457 | keep | 0 | May | 2023 | 0.00099236 | 0.00099236 | Momentary | FALSE | FALSE | Not_TMED_Event | 1457
BAYAMON | 2023-05-19 23:08 | 2023-05-20 01:30 | 470 | 2:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN RISER MAL TIEMPO LLUVIA | S23051901284 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 142 | 2023-05-19 | 66740 | keep | 0 | May | 2023 | 0.045456 | 0.00032011 | Sustained | FALSE | FALSE | Not_TMED_Event | 470
MAYAGÃœEZ | 2023-05-19 23:13 | 2023-05-20 10:07 | 40 | 10:54 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M23051900235 | New_Event | Animals | Include | Include | Wildlife | 654 | 2023-05-19 | 26160 | keep | 0 | May | 2023 | 0.017817 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-19 23:58 | 2023-05-20 16:29 | 30 | 16:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/SUBIO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. SJ-230520-04 | S23051901293 | New_Event | Primary Wire Break | Include | Include | Equipment | 991 | 2023-05-19 | 29730 | keep | 0 | May | 2023 | 0.020249 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-05-20 00:05 | 2023-05-20 13:15 | 15 | 13:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO CAJA EN XMR | P23052000001 | New_Event | Cutout Failure | Include | Include | Equipment | 790 | 2023-05-20 | 11850 | keep | 0 | May | 2023 | 0.008071 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-20 00:10 | 2023-05-20 09:03 | 10 | 8:53 | P | DESGANCHE | 1 X 15 EN CORTE DE LINEA | R23052000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 533 | 2023-05-20 | 5330 | keep | 0 | May | 2023 | 0.0036302 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-20 00:11 | 2023-05-20 00:12 | 3957 | 0:01 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO BKR A PETICION DE PERSONAL EN EL CAMPO PARA ABRIR MACHETES EN MALAS CONDICIONES | S2305200000X | Additional_clients | Switch Failure | Include | Include | Equipment | 1 | 2023-05-20 | 3957 | keep | 0 | May | 2023 | 0.0026951 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-20 00:12 | 2023-05-20 10:35 | 2388 | 10:23 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO TRAMO MACHETE QUEMADO Y SE CERRO PB-3A | S23051901273 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 623 | 2023-05-20 | 1487724 | keep | 0 | May | 2023 | 1.0133 | 0.0016265 | Sustained | FALSE | FALSE | Not_TMED_Event | 2388
YAUCO | 2023-05-20 00:34 | 2023-05-20 09:46 | 50 | 9:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X 80 EN C/L MAL TIEMPO LLUVIAS | P23052000005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 552 | 2023-05-20 | 27600 | keep | 0 | May | 2023 | 0.018798 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-20 01:17 | 2023-05-20 01:18 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052000028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 449 | keep | 0 | May | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
YAUCO | 2023-05-20 01:19 | 2023-05-20 10:30 | 40 | 9:11 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052000005 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 551 | 2023-05-20 | 22040 | keep | 0 | May | 2023 | 0.015011 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-05-20 02:11 | 2023-05-20 02:32 | 575 | 0:21 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRE MACHETES EN FID 7316596 NO SE REPORTO CAUSA | P23052000034 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 21 | 2023-05-20 | 12075 | keep | 0 | May | 2023 | 0.0082242 | 0.00039163 | Sustained | FALSE | FALSE | Not_TMED_Event | 575
SAN JUAN | 2023-05-20 02:14 | 2023-05-20 07:57 | 4944 | 5:43 | T | DESCONECTIVO DEFECTUOSO | MACHETE QUEMADO SE SECCIONALIZO Y SE PASO 80% POR 1204-05 | S23052000045 | New_Event | Switch Failure | Include | Include | Equipment | 343 | 2023-05-20 | 1695792 | keep | 0 | May | 2023 | 1.155 | 0.0033673 | Sustained | FALSE | FALSE | Not_TMED_Event | 4944
YAUCO | 2023-05-20 02:32 | 2023-05-20 13:20 | 900 | 10:48 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADOR EN VARIOS PUNTOS | P23052000036 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 648 | 2023-05-20 | 583200 | keep | 0 | May | 2023 | 0.39721 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-20 02:56 | 2023-05-20 02:57 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23052000005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 1234 | keep | 0 | May | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
ARECIBO | 2023-05-20 03:20 | 2023-05-20 09:28 | 30 | 6:08 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23052000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 368 | 2023-05-20 | 11040 | keep | 0 | May | 2023 | 0.0075193 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-20 03:43 | 2023-05-20 03:46 | 1725 | 0:03 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO Y SE CERRO POR SCADA | C2305200000X | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 3 | 2023-05-20 | 5175 | keep | 0 | May | 2023 | 0.0035247 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CAGUAS | 2023-05-20 03:46 | 2023-05-20 07:58 | 197 | 4:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | C23052000004 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 252 | 2023-05-20 | 49644 | keep | 0 | May | 2023 | 0.033812 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
SAN JUAN | 2023-05-20 04:02 | 2023-05-20 13:07 | 300 | 9:05 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE X AVE | S23052000168 | New_Event | Animals | Include | Include | Wildlife | 545 | 2023-05-20 | 163500 | keep | 0 | May | 2023 | 0.11136 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
HUMACAO | 2023-05-20 04:31 | 2023-05-20 07:17 | 2 | 2:46 | P | TERMINACION SOTERRADA AVERIADA | CG-230520-01 REMPLAZO DE TERMINACION AVERIADA | C23052000005 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 166 | 2023-05-20 | 332 | keep | 0 | May | 2023 | 0.00022612 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-20 04:57 | 2023-05-20 09:43 | 51 | 4:46 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23052000178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2023-05-20 | 14586 | keep | 0 | May | 2023 | 0.0099345 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
VEGA BAJA | 2023-05-20 05:05 | 2023-05-20 08:48 | 80 | 3:43 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR AVE | A23052000003 | New_Event | Animals | Include | Include | Wildlife | 223 | 2023-05-20 | 17840 | keep | 0 | May | 2023 | 0.012151 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-05-20 05:18 | 2023-05-20 05:19 | 327 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | C23052000007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 327 | keep | 0 | May | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BARRANQUITAS | 2023-05-20 05:20 | 2023-05-20 10:26 | 1843 | 5:06 | T | DESGANCHE | SE DESGANCHO BAMBUAS A VARETA Y SE CERRO POR SCADA | C23052000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 306 | 2023-05-20 | 563958 | keep | 0 | May | 2023 | 0.38411 | 0.0012553 | Sustained | FALSE | FALSE | Not_TMED_Event | 1843
HUMACAO | 2023-05-20 06:11 | 2023-05-20 15:00 | 16 | 8:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23052000017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 529 | 2023-05-20 | 8464 | keep | 0 | May | 2023 | 0.0057648 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-05-20 06:34 | 2023-05-20 06:36 | 1879 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23052000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-20 | 3758 | keep | 0 | May | 2023 | 0.0025596 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
CAGUAS | 2023-05-20 06:49 | 2023-05-20 06:51 | 1089 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE 3015-07 QUE LLEVA 50% DEL 3103-05 | C2305200000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-20 | 2178 | keep | 0 | May | 2023 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
FAJARDO | 2023-05-20 06:50 | 2023-05-20 06:51 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R2305200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 2722 | keep | 0 | May | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
PONCE | 2023-05-20 06:52 | 2023-05-20 13:00 | 10 | 6:08 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE CRUZO LINEAS | P23052000074 | New_Event | Animals | Include | Include | Wildlife | 368 | 2023-05-20 | 3680 | keep | 0 | May | 2023 | 0.0025064 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-20 07:03 | 2023-05-20 11:22 | 40 | 4:19 | P | DESGANCHE | 1 X 80 EN C/L DESGANCH | B23052000023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-05-20 | 10360 | keep | 0 | May | 2023 | 0.0070561 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-20 07:05 | 2023-05-20 07:06 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23052000008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
HUMACAO | 2023-05-20 07:17 | 2023-05-20 07:18 | 2354 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE DE 2604-01 SOLO LLEVA 68% DE SU CARGA | C23052000029 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-05-20 | 2354 | keep | 0 | May | 2023 | 0.0016033 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-20 07:18 | 2023-05-20 07:34 | 2 | 0:16 | P | TERMINACION SOTERRADA AVERIADA | CG-230520-01 REMPLAZO DE TERMINACION AVERIADA | C23052000005 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 16 | 2023-05-20 | 32 | keep | 0 | May | 2023 | 2.1795e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 1192 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 5960 | keep | 0 | May | 2023 | 0.0040593 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 3041 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 15205 | keep | 0 | May | 2023 | 0.010356 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 390 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 1950 | keep | 0 | May | 2023 | 0.0013281 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 650 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000024 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 3250 | keep | 0 | May | 2023 | 0.0022136 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 154 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000025 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 770 | keep | 0 | May | 2023 | 0.00052444 | 0.00010489 | Momentary | FALSE | FALSE | Not_TMED_Event | 154
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 1261 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000025 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 6305 | keep | 0 | May | 2023 | 0.0042943 | 0.00085886 | Momentary | FALSE | FALSE | Not_TMED_Event | 1261
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 3894 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000025 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 19470 | keep | 0 | May | 2023 | 0.013261 | 0.0026522 | Momentary | FALSE | FALSE | Not_TMED_Event | 3894
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 997 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000025 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 4985 | keep | 0 | May | 2023 | 0.0033953 | 0.00067905 | Momentary | FALSE | FALSE | Not_TMED_Event | 997
AGUADILLA | 2023-05-20 07:18 | 2023-05-20 07:23 | 1497 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO BARRA VICTORIA 38 KV BUS SUPPORT PENDIENTE DE REEMPLAZO | M23052000025 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-20 | 7485 | keep | 0 | May | 2023 | 0.005098 | 0.0010196 | Momentary | FALSE | FALSE | Not_TMED_Event | 1497
CANOVANAS | 2023-05-20 07:26 | 2023-05-20 09:51 | 100 | 2:25 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R23052000012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 145 | 2023-05-20 | 14500 | keep | 0 | May | 2023 | 0.0098759 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-20 07:34 | 2023-05-20 10:52 | 54 | 3:18 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | R23052000014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 198 | 2023-05-20 | 10692 | keep | 0 | May | 2023 | 0.0072823 | 3.6779e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 54
HUMACAO | 2023-05-20 07:34 | 2023-05-20 07:35 | 2354 | 0:01 | T | TERMINACION SOTERRADA AVERIADA | RECIERRE DE 2604-01 SOLO LLEVA 68% DE SU CARGA | C2305200000X | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 1 | 2023-05-20 | 2354 | keep | 0 | May | 2023 | 0.0016033 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-20 07:35 | 2023-05-20 13:11 | 36 | 5:36 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 C/L SE REMPLAZO AISLADOR | R23052000015 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 336 | 2023-05-20 | 12096 | keep | 0 | May | 2023 | 0.0082385 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
HUMACAO | 2023-05-20 07:35 | 2023-05-20 09:28 | 2 | 1:53 | P | TERMINACION SOTERRADA AVERIADA | CG-230520-01 REMPLAZO DE TERMINACION AVERIADA | C23052000005 | 1st_after_momentary | UG Cable Termination Failure | Include | Include | Equipment | 113 | 2023-05-20 | 226 | keep | 0 | May | 2023 | 0.00015393 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-05-20 07:35 | 2023-05-20 10:42 | 40 | 3:07 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23052000026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-05-20 | 7480 | keep | 0 | May | 2023 | 0.0050946 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-20 07:39 | 2023-05-20 09:13 | 25 | 1:34 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23052000027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 94 | 2023-05-20 | 2350 | keep | 0 | May | 2023 | 0.0016006 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-05-20 07:46 | 2023-05-20 11:09 | 30 | 3:23 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE XMR | R23052000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 203 | 2023-05-20 | 6090 | keep | 0 | May | 2023 | 0.0041479 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-20 07:57 | 2023-05-20 08:16 | 988 | 0:19 | P | DESCONECTIVO DEFECTUOSO | DISPARO MACHETE QUEMADO SE SECCIONALIZO | S23052000337 | Partial_restoration | Switch Failure | Include | Include | Equipment | 19 | 2023-05-20 | 18772 | keep | 0 | May | 2023 | 0.012786 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-20 08:13 | 2023-05-20 12:26 | 450 | 4:13 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23052000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 253 | 2023-05-20 | 113850 | keep | 0 | May | 2023 | 0.077543 | 0.00030649 | Sustained | FALSE | FALSE | Not_TMED_Event | 450
MAYAGÃœEZ | 2023-05-20 08:13 | 2023-05-20 11:40 | 80 | 3:27 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23052000041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 207 | 2023-05-20 | 16560 | keep | 0 | May | 2023 | 0.011279 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-20 08:16 | 2023-05-20 10:29 | 4944 | 2:13 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR 1204-05 LLEVANDO 1204-04 SE ABRIO N/O Y CARGA PERMANECIO FUERA HASTA QUE SE REMPLAZO 3 MACHETES QUEMADOS Y SE ELIMINO PARARRAYO | S23052000045 | Additional_clients | Switch Failure | Include | Include | Equipment | 133 | 2023-05-20 | 657552 | keep | 0 | May | 2023 | 0.44786 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-20 08:16 | 2023-05-20 08:25 | 10211 | 0:09 | T | CONDUCTOR ROTO O ABIERTO | DISPARO ALIMENTADOR LLEVANDO 80% DEL 1204-04 Y SE ABRIO N/O Y SE CERRO INTERRUPTOR QUEDO EN SERVICIO SE DEJA FUERA 80% DEL 1204-04 | S23052000337 | New_Event | Primary Wire Break | Include | Include | Equipment | 9 | 2023-05-20 | 91899 | keep | 0 | May | 2023 | 0.062592 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2023-05-20 08:25 | 2023-05-20 12:56 | 3403 | 4:31 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZA TRAMO PARA CERRAR PUENTE PRIMARIO | S23052000586 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 271 | 2023-05-20 | 922213 | keep | 0 | May | 2023 | 0.62812 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-20 08:25 | 2023-05-20 11:07 | 20 | 2:42 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23052000035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-05-20 | 3240 | keep | 0 | May | 2023 | 0.0022067 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-05-20 08:37 | 2023-05-20 11:38 | 132 | 3:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO LLUVIAS | C23052000044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 181 | 2023-05-20 | 23892 | keep | 0 | May | 2023 | 0.016273 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
YAUCO | 2023-05-20 08:40 | 2023-05-20 12:27 | 50 | 3:47 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | P23052000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-05-20 | 11350 | keep | 0 | May | 2023 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-20 08:43 | 2023-05-20 09:12 | 19 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23052000048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-05-20 | 551 | keep | 0 | May | 2023 | 0.00037528 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-05-20 08:56 | 2023-05-20 09:02 | 34 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO L-5900 LLEVA PARTE DE 1910-01 Y 1519-3 | S23052000398 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-20 | 204 | keep | 0 | May | 2023 | 0.00013894 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2023-05-20 08:56 | 2023-05-20 09:02 | 19 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO L-5900 | S23052000398 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-20 | 114 | keep | 0 | May | 2023 | 7.7645e-05 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-05-20 08:56 | 2023-05-20 09:02 | 154 | 0:06 | P | LINEA DE TRANSMISION 38KV | DISPARO SUB. 1512-04 POR L-5900 QUE LLEVA PARTE DE 1910-01 Y 80% DEL 1519-3 | S23052000398 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-20 | 924 | keep | 0 | May | 2023 | 0.00062933 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
BAYAMON | 2023-05-20 08:56 | 2023-05-20 09:02 | 10 | 0:06 | P | LINEA DE TRANSMISION 38KV | DISPARO SUB. 1512-04 POR L-5900 QUE LLEVA PARTE DE 1910-01 Y 80% DEL 1519-3 | S23052000398 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-20 | 60 | keep | 0 | May | 2023 | 4.0866e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-20 09:00 | 2023-05-20 16:48 | 30 | 7:48 | P | DESGANCHE | 1X65 EN C/L Y 1X40 EN C/L DESGANCHE | S23052000402 | New_Event | Vegetation Contact | Include | Include | Vegetation | 468 | 2023-05-20 | 14040 | keep | 0 | May | 2023 | 0.0095626 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-20 09:08 | 2023-05-20 10:39 | 34 | 1:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN CORTES DE LINEA 2 X 8 EN TRANSFORMADOR SE REEMPLAZARON CAJAS PRIMARIAS | R23052000025 | New_Event | Cutout Failure | Include | Include | Equipment | 91 | 2023-05-20 | 3094 | keep | 0 | May | 2023 | 0.0021073 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BARRANQUITAS | 2023-05-20 09:08 | 2023-05-20 09:09 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | C23052000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2725 | keep | 0 | May | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-05-20 09:08 | 2023-05-20 09:09 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | C23052000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-05-20 09:08 | 2023-05-20 09:09 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | C23052000063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 1437 | keep | 0 | May | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-05-20 09:08 | 2023-05-20 09:09 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | C23052000064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2565 | keep | 0 | May | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-05-20 09:08 | 2023-05-20 09:09 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 4800 | C23052000064 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 3565 | keep | 0 | May | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
SAN JUAN | 2023-05-20 09:24 | 2023-05-20 12:00 | 92 | 2:36 | P | NO SE REPORTO CAUSA | DISPARO NO HAY RTU SE VERIFICO SE PROBO LOCALMENTE LLEVA 5% DE SU CARGA, LLEVA 1346-06 Y LLEVA 80% DEL 1346-05, LLEVA 40% DEL 1346-03 | S23052000443 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2023-05-20 | 14352 | keep | 0 | May | 2023 | 0.0097751 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
SAN JUAN | 2023-05-20 09:24 | 2023-05-20 12:00 | 996 | 2:36 | P | NO SE REPORTO CAUSA | DISPARO 1346-02 NO HAY RTU SE VERIFICO SE PROBO LOCALMENTE LLEVA 5% DE SU CARGA, LLEVA 1346-06 Y LLEVA 80% DEL 1346-05, LLEVA 40% DEL 1346-03 | S23052000443 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 156 | 2023-05-20 | 155376 | keep | 0 | May | 2023 | 0.10583 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
SAN JUAN | 2023-05-20 09:24 | 2023-05-20 12:00 | 737 | 2:36 | P | ALIMENTADOR AMARRADO | DISPARO 1346-02 NO HAY RTU SE VERIFICO SE PROBO LOCALMENTE LLEVA 5% DE SU CARGA, LLEVA 1346-06 Y LLEVA 80% DEL 1346-05 | S23052000443 | New_Event | Feeder Load Transferred | Include | Include | Other | 156 | 2023-05-20 | 114972 | keep | 0 | May | 2023 | 0.078307 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2023-05-20 09:24 | 2023-05-20 12:00 | 1598 | 2:36 | T | ALIMENTADOR AMARRADO | DISPARO NO HAY RTU SE VERIFICO SE PROBO LOCALMENTE SU CARGA POR 1346-02 | S23052000443 | New_Event | Feeder Load Transferred | Include | Include | Other | 156 | 2023-05-20 | 249288 | keep | 0 | May | 2023 | 0.16979 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
BAYAMON | 2023-05-20 09:25 | 2023-05-20 10:49 | 80 | 1:24 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIA | B23052000044 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 84 | 2023-05-20 | 6720 | keep | 0 | May | 2023 | 0.004577 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-05-20 09:28 | 2023-05-20 12:25 | 159 | 2:57 | P | TERMINACION SOTERRADA AVERIADA | CG-230520-01 REMPLAZO DE TERMINACION AVERIADA Y SE NORMALIZO CARGAS | C23052000005 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 177 | 2023-05-20 | 28143 | keep | 0 | May | 2023 | 0.019168 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-20 09:39 | 2023-05-20 10:47 | 58 | 1:08 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | R23052000028 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-05-20 | 3944 | keep | 0 | May | 2023 | 0.0026862 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
CAGUAS | 2023-05-20 09:42 | 2023-05-20 15:08 | 34 | 5:26 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23052000073 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 326 | 2023-05-20 | 11084 | keep | 0 | May | 2023 | 0.0075493 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BAYAMON | 2023-05-20 09:56 | 2023-05-20 10:57 | 25 | 1:01 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2023-05-20 | 1525 | keep | 0 | May | 2023 | 0.0010387 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-20 10:12 | 2023-05-20 14:50 | 15 | 4:38 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052000074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2023-05-20 | 4170 | keep | 0 | May | 2023 | 0.0028402 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
UTUADO | 2023-05-20 10:17 | 2023-05-20 16:05 | 100 | 5:48 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA POR BAMBUAS SOBRE LINEAS | P23052000116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 348 | 2023-05-20 | 34800 | keep | 0 | May | 2023 | 0.023702 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-05-20 10:24 | 2023-05-20 12:21 | 134 | 1:57 | P | TERMINACION SOTERRADA AVERIADA | 1 X 25 EN RISER POR TERMINACION AVERIADA EN PROVISIONAL | C23052000090 | New_Event | UG Cable Termination Failure | Include | Include | Equipment | 117 | 2023-05-20 | 15678 | keep | 0 | May | 2023 | 0.010678 | 9.1267e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 134
BARRANQUITAS | 2023-05-20 10:26 | 2023-05-20 10:40 | 67 | 0:14 | P | DESGANCHE | 2 X 80 EN C/L SE DESGANCHO BAMBUAS | C23052000008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 14 | 2023-05-20 | 938 | keep | 0 | May | 2023 | 0.00063887 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
BAYAMON | 2023-05-20 10:30 | 2023-05-20 11:59 | 8 | 1:29 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | B23052000054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-05-20 | 712 | keep | 0 | May | 2023 | 0.00048494 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-20 10:35 | 2023-05-20 13:47 | 150 | 3:12 | P | DESCONECTIVO DEFECTUOSO | SE ESTABLECE GOI PARA REMPLAZAR 3 MACHETES | S23052000607 | Partial_restoration | Switch Failure | Include | Include | Equipment | 192 | 2023-05-20 | 28800 | keep | 0 | May | 2023 | 0.019616 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-20 10:42 | 2023-05-20 16:43 | 185 | 6:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L DESGANCHE | S23052000606 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 361 | 2023-05-20 | 66785 | keep | 0 | May | 2023 | 0.045487 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
VEGA BAJA | 2023-05-20 10:48 | 2023-05-20 10:52 | 2132 | 0:04 | T | TRANSFORMADOR AVERIADO | SE ABRE INTERRUPTOR PARA ABRIR CORTE DE LINEA EN AREA DIFICIL DE MANIOBRAR PARA REEMPLAZO DE TRANSFORMADOR QUEMADO Y SE CIERRA | A23052000075 | Additional_clients | Service Transformer Failure | Include | Include | Equipment | 4 | 2023-05-20 | 8528 | keep | 0 | May | 2023 | 0.0058084 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-20 10:52 | 2023-05-20 18:03 | 400 | 7:11 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR SE CERRO CORTE DE LINEA | A23051900063 | 1st_after_momentary | Service Transformer Failure | Include | Include | Equipment | 431 | 2023-05-20 | 172400 | keep | 0 | May | 2023 | 0.11742 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
CANOVANAS | 2023-05-20 10:56 | 2023-05-20 12:16 | 40 | 1:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | R23052000034 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 80 | 2023-05-20 | 3200 | keep | 0 | May | 2023 | 0.0021795 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-05-20 11:00 | 2023-05-20 12:00 | 30 | 1:00 | P | ANIMAL | 1 X 40 EN C/L AVE CRUZO LINEAS | P23052000117 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-05-20 | 1800 | keep | 0 | May | 2023 | 0.001226 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-20 11:07 | 2023-05-20 12:30 | 5 | 1:23 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052000088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 83 | 2023-05-20 | 415 | keep | 0 | May | 2023 | 0.00028265 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-05-20 11:16 | 2023-05-20 14:23 | 90 | 3:07 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C23052000102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-05-20 | 16830 | keep | 0 | May | 2023 | 0.011463 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
VEGA BAJA | 2023-05-20 11:19 | 2023-05-20 14:45 | 112 | 3:26 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | B23052000063 | New_Event | Animals | Include | Include | Wildlife | 206 | 2023-05-20 | 23072 | keep | 0 | May | 2023 | 0.015714 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
MAYAGÃœEZ | 2023-05-20 11:24 | 2023-05-20 14:30 | 35 | 3:06 | P | DESGANCHE | 1 X 65 Y 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052000091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-05-20 | 6510 | keep | 0 | May | 2023 | 0.0044339 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-05-20 11:24 | 2023-05-20 15:25 | 50 | 4:01 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052000098 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 241 | 2023-05-20 | 12050 | keep | 0 | May | 2023 | 0.0082072 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-20 11:31 | 2023-05-20 14:50 | 112 | 3:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 50 EN AEREO PROVISIONAL | B23052000064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 199 | 2023-05-20 | 22288 | keep | 0 | May | 2023 | 0.01518 | 7.6283e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 112
FAJARDO | 2023-05-20 11:34 | 2023-05-20 11:56 | 15 | 0:22 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE X AVE | R23052000036 | New_Event | Animals | Include | Include | Wildlife | 22 | 2023-05-20 | 330 | keep | 0 | May | 2023 | 0.00022476 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-20 11:35 | 2023-05-20 13:50 | 50 | 2:15 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M23052000093 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-05-20 | 6750 | keep | 0 | May | 2023 | 0.0045974 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-20 11:38 | 2023-05-20 13:15 | 65 | 1:37 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23052000104 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-05-20 | 6305 | keep | 0 | May | 2023 | 0.0042943 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
PONCE | 2023-05-20 11:38 | 2023-05-20 13:39 | 1 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN TRANSFORMADOR MAL TIEMPO LLUVIAS | P23052000130 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-05-20 | 121 | keep | 0 | May | 2023 | 8.2413e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-20 11:40 | 2023-05-20 17:08 | 75 | 5:28 | P | DESGANCHE | 1 X 80 Y 1 X 50 EN C/L DESGANCHE | C23052000107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 328 | 2023-05-20 | 24600 | keep | 0 | May | 2023 | 0.016755 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
UTUADO | 2023-05-20 11:42 | 2023-05-20 13:50 | 50 | 2:08 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A23052000049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 128 | 2023-05-20 | 6400 | keep | 0 | May | 2023 | 0.004359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-05-20 11:43 | 2023-05-20 15:05 | 36 | 3:22 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R23052000039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 202 | 2023-05-20 | 7272 | keep | 0 | May | 2023 | 0.0049529 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
VEGA BAJA | 2023-05-20 11:49 | 2023-05-20 17:15 | 1 | 5:26 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052000054 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 326 | 2023-05-20 | 326 | keep | 0 | May | 2023 | 0.00022204 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-20 11:58 | 2023-05-20 11:59 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23052000079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 3511 | keep | 0 | May | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
UTUADO | 2023-05-20 12:00 | 2023-05-20 16:30 | 30 | 4:30 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052000088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 270 | 2023-05-20 | 8100 | keep | 0 | May | 2023 | 0.0055169 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-05-20 12:03 | 2023-05-20 15:35 | 30 | 3:32 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052000070 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 212 | 2023-05-20 | 6360 | keep | 0 | May | 2023 | 0.0043318 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-20 12:08 | 2023-05-20 18:15 | 100 | 6:07 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 50 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA CRUZADA | M23052000099 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 367 | 2023-05-20 | 36700 | keep | 0 | May | 2023 | 0.024996 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-20 12:11 | 2023-05-20 13:04 | 15 | 0:53 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23052000754 | New_Event | Vegetation Contact | Include | Include | Vegetation | 53 | 2023-05-20 | 795 | keep | 0 | May | 2023 | 0.00054147 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-20 12:12 | 2023-05-20 16:15 | 35 | 4:03 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23052000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 243 | 2023-05-20 | 8505 | keep | 0 | May | 2023 | 0.0057927 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2023-05-20 12:14 | 2023-05-20 15:34 | 8 | 3:20 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE X AVE | R23052000045 | New_Event | Animals | Include | Include | Wildlife | 200 | 2023-05-20 | 1600 | keep | 0 | May | 2023 | 0.0010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-20 12:21 | 2023-05-20 14:47 | 2 | 2:26 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE CERRO SECUNDARIA ABIERTA | R23052000049 | New_Event | Secondary Wire Break | Include | Include | Equipment | 146 | 2023-05-20 | 292 | keep | 0 | May | 2023 | 0.00019888 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-20 12:21 | 2023-05-21 15:00 | 4 | 26:39 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23052000088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1599 | 2023-05-20 | 6396 | keep | 0 | May | 2023 | 0.0043563 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-05-20 12:23 | 2023-05-20 14:54 | 29 | 2:31 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23052000123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 151 | 2023-05-20 | 4379 | keep | 0 | May | 2023 | 0.0029825 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-05-20 12:25 | 2023-05-21 01:25 | 364 | 13:00 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | S23052000767 | New_Event | Vegetation Contact | Include | Include | Vegetation | 780 | 2023-05-20 | 283920 | keep | 0 | May | 2023 | 0.19338 | 0.00024792 | Sustained | FALSE | FALSE | Not_TMED_Event | 364
BAYAMON | 2023-05-20 12:31 | 2023-05-20 16:37 | 1 | 4:06 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN BANCO DE TRANSFORMADORES SE DESGANCHO SECUNDARIA | B23052000091 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 246 | 2023-05-20 | 246 | keep | 0 | May | 2023 | 0.00016755 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-20 12:47 | 2023-05-20 19:24 | 6 | 6:37 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | S23052000129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 397 | 2023-05-20 | 2382 | keep | 0 | May | 2023 | 0.0016224 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-20 12:54 | 2023-05-20 13:08 | 1381 | 0:14 | T | DESGANCHE | DISPARO ALIMENTADOR SE VERIFICO CON PERSONAL INDICAN QUE INSTALANDO POSTE CERCA LINEA VIENTO EN EL AREA SE PEGO GANCHO A LINEA Y CRUZO FASE DISPARO ALIMENTADO SE RETIRO GANCHO Y SE CERRO INTERRUPTOR | S23052000000 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 14 | 2023-05-20 | 19334 | keep | 0 | May | 2023 | 0.013168 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-20 12:54 | 2023-05-20 14:49 | 51 | 1:55 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23052000132 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 115 | 2023-05-20 | 5865 | keep | 0 | May | 2023 | 0.0039946 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
SAN JUAN | 2023-05-20 12:56 | 2023-05-20 13:37 | 10211 | 0:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETE CAMINO PABLO ORTIZ PARA CERRAR PUENTE POR GOI ENTRE FID-16397661 Y FID-30353161 SALIENDO DE SUBESTACION | S23052000586 | New_Event | Primary Wire Break | Include | Include | Equipment | 41 | 2023-05-20 | 418651 | keep | 0 | May | 2023 | 0.28514 | 0.0069547 | Sustained | FALSE | FALSE | Not_TMED_Event | 10211
SAN JUAN | 2023-05-20 13:02 | 2023-05-20 17:14 | 7 | 4:12 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X10 EN XMR SE REPARO SECUNDARIA | S23052000810 | New_Event | Secondary Wire Break | Include | Include | Equipment | 252 | 2023-05-20 | 1764 | keep | 0 | May | 2023 | 0.0012015 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BARRANQUITAS | 2023-05-20 13:02 | 2023-05-20 14:01 | 26 | 0:59 | P | DESGANCHE | 1 X 30 EN C/L SE RETIRO RAMA | C23052000137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 59 | 2023-05-20 | 1534 | keep | 0 | May | 2023 | 0.0010448 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2023-05-20 13:03 | 2023-05-20 13:04 | 906 | 0:01 | T | DESGANCHE | RECIERRE | C2305200000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-20 | 906 | keep | 0 | May | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CAGUAS | 2023-05-20 13:04 | 2023-05-20 16:30 | 174 | 3:26 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO PENCA | C23052000139 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 206 | 2023-05-20 | 35844 | keep | 0 | May | 2023 | 0.024413 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
YAUCO | 2023-05-20 13:04 | 2023-05-20 16:35 | 15 | 3:31 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052000116 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 211 | 2023-05-20 | 3165 | keep | 0 | May | 2023 | 0.0021557 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-20 13:05 | 2023-05-20 13:58 | 42 | 0:53 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | B23052000096 | New_Event | Animals | Include | Include | Wildlife | 53 | 2023-05-20 | 2226 | keep | 0 | May | 2023 | 0.0015161 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
SAN JUAN | 2023-05-20 13:08 | 2023-05-20 14:17 | 120 | 1:09 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23051900989 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 69 | 2023-05-20 | 8280 | keep | 0 | May | 2023 | 0.0056395 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-20 13:13 | 2023-05-20 17:01 | 332 | 3:48 | P | TERMINACION SOTERRADA AVERIADA | SJ-230520-01 SE REEMPLAZARON TERMINACIONES QUEMADAS DEL MH-10 HACIA CONDOMINIO MARIBELLA TORRE DEL ESTE | R23051900126 | Additional_clients | UG Cable Termination Failure | Include | Include | Equipment | 228 | 2023-05-20 | 75696 | keep | 0 | May | 2023 | 0.051556 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-20 13:19 | 2023-05-20 13:20 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23052000099 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 3511 | keep | 0 | May | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
MAYAGÃœEZ | 2023-05-20 13:25 | 2023-05-20 21:00 | 60 | 7:35 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA Y 1 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052000149 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 455 | 2023-05-20 | 27300 | keep | 0 | May | 2023 | 0.018594 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-05-20 13:25 | 2023-05-20 18:50 | 40 | 5:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052000128 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 325 | 2023-05-20 | 13000 | keep | 0 | May | 2023 | 0.0088542 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-05-20 13:38 | 2023-05-20 15:39 | 100 | 2:01 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR | R23052000052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 121 | 2023-05-20 | 12100 | keep | 0 | May | 2023 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-05-20 13:38 | 2023-05-20 15:42 | 300 | 2:04 | P | MAL TIEMPO/RAYOS | 2 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052000131 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 124 | 2023-05-20 | 37200 | keep | 0 | May | 2023 | 0.025337 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-05-20 13:46 | 2023-05-20 13:47 | 4431 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B2305200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 4431 | keep | 0 | May | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
CANOVANAS | 2023-05-20 13:47 | 2023-05-20 15:13 | 6 | 1:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | R23052000054 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 86 | 2023-05-20 | 516 | keep | 0 | May | 2023 | 0.00035145 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-05-20 13:52 | 2023-05-20 17:54 | 15 | 4:02 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052000227 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 242 | 2023-05-20 | 3630 | keep | 0 | May | 2023 | 0.0024724 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-20 13:58 | 2023-05-20 13:59 | 2132 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | A23052000065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2132 | keep | 0 | May | 2023 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2023-05-20 13:58 | 2023-05-20 13:59 | 2366 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | A23052000065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2366 | keep | 0 | May | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2023-05-20 13:58 | 2023-05-20 13:59 | 1976 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | A23052000065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 1976 | keep | 0 | May | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2023-05-20 13:58 | 2023-05-20 13:59 | 3688 | 0:01 | T | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | A23052000065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 3688 | keep | 0 | May | 2023 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 3070 | keep | 0 | May | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2735 | keep | 0 | May | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000113 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 1070 | keep | 0 | May | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000114 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 1647 | keep | 0 | May | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000114 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 3295 | keep | 0 | May | 2023 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000114 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 1180 | keep | 0 | May | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000115 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 320 | keep | 0 | May | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-05-20 13:58 | 2023-05-20 13:59 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | RECIERRE DE LA LINEA 36100 DE PIÃ‘AS A CIALES TIENE DESGANCHES PENDIENTES DE REALIZAR REPORTADOS EN PATRULLAJE AEREO DEL 4/29/2023. | B23052000115 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-05-20 13:59 | 2023-05-20 14:13 | 42 | 0:14 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | B23052000096 | Partial_restoration | Animals | Include | Include | Wildlife | 14 | 2023-05-20 | 588 | keep | 0 | May | 2023 | 0.00040048 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-20 14:01 | 2023-05-20 16:28 | 86 | 2:27 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23052000167 | New_Event | Animals | Include | Include | Wildlife | 147 | 2023-05-20 | 12642 | keep | 0 | May | 2023 | 0.0086104 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
PONCE | 2023-05-20 14:01 | 2023-05-20 15:42 | 12 | 1:41 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23052000152 | New_Event | Animals | Include | Include | Wildlife | 101 | 2023-05-20 | 1212 | keep | 0 | May | 2023 | 0.00082549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
MAYAGÃœEZ | 2023-05-20 14:04 | 2023-05-20 16:40 | 100 | 2:36 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052000160 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 156 | 2023-05-20 | 15600 | keep | 0 | May | 2023 | 0.010625 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-20 14:07 | 2023-05-20 15:27 | 92 | 1:20 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1346-02 NO TIENE RTU 95% DE SU CARGA POR EL 1907-04 LLEVA LA CARGA DEL 1346-06 LLEVA 80% DEL 1346-05,LLEVA 40% DEL 1346-03 SE CERRO LOCALMENTE EN LA SUBESTACION | S23052000938 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-05-20 | 7360 | keep | 0 | May | 2023 | 0.0050129 | 6.2661e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 92
SAN JUAN | 2023-05-20 14:07 | 2023-05-20 15:27 | 996 | 1:20 | P | NO SE REPORTO CAUSA | DISPARO 1346-02 NO HAY RTU SE VERIFICO SE PROBO LOCALMENTE LLEVA 5% DE SU CARGA, LLEVA 1346-06 Y LLEVA 80% DEL 1346-05, LLEVA 40% DEL 1346-03 | S23052000938 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 80 | 2023-05-20 | 79680 | keep | 0 | May | 2023 | 0.05427 | 0.00067837 | Sustained | FALSE | FALSE | Not_TMED_Event | 996
SAN JUAN | 2023-05-20 14:07 | 2023-05-20 15:27 | 737 | 1:20 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1346-02 NO TIENE RTU 95% DE SU CARGA POR EL 1907-04 LLEVA LA CARGA DEL 1346-06 LLEVA 80% DEL 1346-05 SE CERRO LOCALMENTE EN LA SUBESTACION | S23052000938 | New_Event | Feeder Load Transferred | Include | Include | Other | 80 | 2023-05-20 | 58960 | keep | 0 | May | 2023 | 0.040157 | 0.00050197 | Sustained | FALSE | FALSE | Not_TMED_Event | 737
SAN JUAN | 2023-05-20 14:07 | 2023-05-20 15:27 | 1598 | 1:20 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1346-02 NO TIENE RTU 95% DE SU CARGA POR EL 1907-04 LLEVA LA CARGA DEL 1346-06 LLEVA 80% DEL 1346-05 SE CERRO LOCALMENTE EN LA SUBESTACION | S23052000938 | New_Event | Feeder Load Transferred | Include | Include | Other | 80 | 2023-05-20 | 127840 | keep | 0 | May | 2023 | 0.087071 | 0.0010884 | Sustained | FALSE | FALSE | Not_TMED_Event | 1598
CANOVANAS | 2023-05-20 14:07 | 2023-05-20 19:45 | 36 | 5:38 | P | CAUSAS EXTERNAS | SJ-230520-02 SE SECCIONALIZO T8 IMPACTADO POR VEHICULO SE CERRO N/O EN PROVISIONAL AEREO HACIA T3 | R23052000055 | New_Event | Damage From Public | Include | Include | Public | 338 | 2023-05-20 | 12168 | keep | 0 | May | 2023 | 0.0082876 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-20 14:17 | 2023-05-21 14:40 | 43 | 24:23 | P | DESGANCHE | 1X65 EN C/L Y 1X40 EN C/L DESGANCHE | S23052000944 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1463 | 2023-05-20 | 62909 | keep | 0 | May | 2023 | 0.042847 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2023-05-20 14:18 | 2023-05-20 16:01 | 8 | 1:43 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | R23052000057 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 103 | 2023-05-20 | 824 | keep | 0 | May | 2023 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-20 14:24 | 2023-05-21 13:47 | 6 | 23:23 | P | DESGANCHE | 1 X 20 EN TRANSFORMADOR | S23052000953 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1403 | 2023-05-20 | 8418 | keep | 0 | May | 2023 | 0.0057335 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-05-20 14:30 | 2023-05-20 17:05 | 500 | 2:35 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23052000163 | New_Event | Primary Wire Break | Include | Include | Equipment | 155 | 2023-05-20 | 77500 | keep | 0 | May | 2023 | 0.052785 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
ARECIBO | 2023-05-20 14:34 | 2023-05-20 16:25 | 6 | 1:51 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | A23052000099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 111 | 2023-05-20 | 666 | keep | 0 | May | 2023 | 0.00045361 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-20 14:35 | 2023-05-20 19:30 | 196 | 4:55 | P | DESGANCHE | 2X80 EN C/L DESGANCHE | S23052000959 | New_Event | Vegetation Contact | Include | Include | Vegetation | 295 | 2023-05-20 | 57820 | keep | 0 | May | 2023 | 0.039381 | 0.00013349 | Sustained | FALSE | FALSE | Not_TMED_Event | 196
ARECIBO | 2023-05-20 14:45 | 2023-05-20 16:45 | 50 | 2:00 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052000102 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-05-20 | 6000 | keep | 0 | May | 2023 | 0.0040866 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-05-20 14:45 | 2023-05-20 14:46 | 3387 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CERRADO POR CONTROL | B23052000121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 3387 | keep | 0 | May | 2023 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
VEGA BAJA | 2023-05-20 14:46 | 2023-05-20 15:48 | 112 | 1:02 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | B23052000063 | Partial_restoration | Animals | Include | Include | Wildlife | 62 | 2023-05-20 | 6944 | keep | 0 | May | 2023 | 0.0047295 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-20 14:52 | 2023-05-20 16:02 | 1 | 1:10 | P | ANIMAL | 1X30 EN C/L Y 2X25 EN BANCO DE XMR DEL CLIENTE CRUCE POR AVE | S23052000971 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-05-20 | 70 | keep | 0 | May | 2023 | 4.7677e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-20 14:56 | 2023-05-20 18:40 | 200 | 3:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23052000176 | New_Event | Vegetation Contact | Include | Include | Vegetation | 224 | 2023-05-20 | 44800 | keep | 0 | May | 2023 | 0.030513 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-05-20 15:07 | 2023-05-20 17:25 | 35 | 2:18 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052000112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-05-20 | 4830 | keep | 0 | May | 2023 | 0.0032897 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
PONCE | 2023-05-20 15:08 | 2023-05-20 16:30 | 18 | 1:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR 1 X 15 EN TRANSFORMADOR | P23052000164 | New_Event | Primary Wire Break | Include | Include | Equipment | 82 | 2023-05-20 | 1476 | keep | 0 | May | 2023 | 0.0010053 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
BARRANQUITAS | 2023-05-20 15:09 | 2023-05-20 15:29 | 25 | 0:20 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23052000185 | New_Event | Vegetation Contact | Include | Include | Vegetation | 20 | 2023-05-20 | 500 | keep | 0 | May | 2023 | 0.00034055 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-20 15:20 | 2023-05-20 17:40 | 70 | 2:20 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | M23052000183 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 140 | 2023-05-20 | 9800 | keep | 0 | May | 2023 | 0.0066747 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2023-05-20 15:21 | 2023-05-20 16:13 | 10 | 0:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR POR MAL TIEMPO | P23052000166 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 52 | 2023-05-20 | 520 | keep | 0 | May | 2023 | 0.00035417 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-20 15:26 | 2023-05-21 01:18 | 155 | 9:52 | P | CAUSAS EXTERNAS | 2 X 50 EN CORTE DE LINEA VECINO CORTANDO ARBOL SE FUE SOBRE LA LINEA | B23052000129 | New_Event | Damage From Public | Include | Include | Public | 592 | 2023-05-20 | 91760 | keep | 0 | May | 2023 | 0.062497 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
AGUADILLA | 2023-05-20 15:26 | 2023-05-20 16:00 | 50 | 0:34 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052000187 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 34 | 2023-05-20 | 1700 | keep | 0 | May | 2023 | 0.0011579 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-20 15:27 | 2023-05-20 15:28 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23052000131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 3438 | keep | 0 | May | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
CAGUAS | 2023-05-20 15:28 | 2023-05-20 15:29 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23052000194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BARRANQUITAS | 2023-05-20 15:28 | 2023-05-20 17:38 | 40 | 2:10 | P | NO SE REPORTO CAUSA | 1 X 30 C/L | C23052000193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 130 | 2023-05-20 | 5200 | keep | 0 | May | 2023 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-20 15:34 | 2023-05-21 04:23 | 242 | 12:49 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO | B23052000134 | New_Event | Switch Failure | Include | Include | Equipment | 769 | 2023-05-20 | 186098 | keep | 0 | May | 2023 | 0.12675 | 0.00016483 | Sustained | FALSE | FALSE | Not_TMED_Event | 242
UTUADO | 2023-05-20 15:41 | 2023-05-20 16:29 | 50 | 0:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052000117 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-05-20 | 2400 | keep | 0 | May | 2023 | 0.0016346 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-20 15:42 | 2023-05-21 13:27 | 30 | 21:45 | P | TRANSFORMADOR AVERIADO | 1 X 50 EN RISER TRANSFORMADOR QUEMADO SE TRANSFIRIO SECUNDARIA A OTRO TRANSFORMADOR | S23052001001 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1305 | 2023-05-20 | 39150 | keep | 0 | May | 2023 | 0.026665 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-20 15:45 | 2023-05-21 09:32 | 30 | 17:47 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA TOTAL Y SE REPARO PUENTE ABIERTO DE LINEA A CAJA | B23052000140 | New_Event | Primary Wire Break | Include | Include | Equipment | 1067 | 2023-05-20 | 32010 | keep | 0 | May | 2023 | 0.021802 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-20 15:45 | 2023-05-20 15:46 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23052000143 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 3438 | keep | 0 | May | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
AGUADILLA | 2023-05-20 15:46 | 2023-05-21 | 1 | 8:14 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | A23052000120 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 494 | 2023-05-20 | 494 | keep | 0 | May | 2023 | 0.00033646 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-20 15:47 | 2023-05-21 19:34 | 12 | 27:47 | P | DESGANCHE | 1X20 EN XMR DESGANCHE PRIMARIO | S23052001006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1667 | 2023-05-20 | 20004 | keep | 0 | May | 2023 | 0.013625 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-20 15:49 | 2023-05-21 06:06 | 100 | 14:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA LLUVIAS | B23052000146 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 857 | 2023-05-20 | 85700 | keep | 0 | May | 2023 | 0.05837 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-20 15:49 | 2023-05-20 17:40 | 80 | 1:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23052000204 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 111 | 2023-05-20 | 8880 | keep | 0 | May | 2023 | 0.0060481 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-20 15:52 | 2023-05-20 15:53 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23052000151 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 3438 | keep | 0 | May | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-05-20 15:56 | 2023-05-20 23:38 | 138 | 7:42 | P | ANIMAL | 1 X 65 Y 1 X 80 EN CORTES DE LINEA CRUCE POR PALOMA | B23052000153 | New_Event | Animals | Include | Include | Wildlife | 462 | 2023-05-20 | 63756 | keep | 0 | May | 2023 | 0.043424 | 9.3991e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 138
PONCE | 2023-05-20 16:06 | 2023-05-20 16:07 | 485 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052000173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 485 | keep | 0 | May | 2023 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
BAYAMON | 2023-05-20 16:12 | 2023-05-21 17:38 | 5 | 25:26 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO CMR 50KVA X 50KVA | B23052000167 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1526 | 2023-05-20 | 7630 | keep | 0 | May | 2023 | 0.0051968 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-20 16:26 | 2023-05-20 16:27 | 1452 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2305200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 1452 | keep | 0 | May | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
VEGA BAJA | 2023-05-20 16:26 | 2023-05-20 18:19 | 45 | 1:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA INTERRUPCION EVENTO EXPORTADO DE ARECIBO | A23052000134 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 113 | 2023-05-20 | 5085 | keep | 0 | May | 2023 | 0.0034634 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-05-20 16:27 | 2023-05-20 17:57 | 150 | 1:30 | P | NO SE REPORTO CAUSA | 1X80 EN C/L | S23052001012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-05-20 | 13500 | keep | 0 | May | 2023 | 0.0091948 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
ARECIBO | 2023-05-20 16:31 | 2023-05-20 22:25 | 6 | 5:54 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052000136 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 354 | 2023-05-20 | 2124 | keep | 0 | May | 2023 | 0.0014466 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-05-20 16:32 | 2023-05-20 18:00 | 12 | 1:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO PORTAFUSIBLES Y 1 X 10 EN XMR | C23052000231 | New_Event | Cutout Failure | Include | Include | Equipment | 88 | 2023-05-20 | 1056 | keep | 0 | May | 2023 | 0.00071924 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-20 16:37 | 2023-05-21 11:34 | 25 | 18:57 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO CORTE DE LINEA Y REPARO BAJANTE DE LINEA A CAJA | B23052000172 | New_Event | Cutout Failure | Include | Include | Equipment | 1137 | 2023-05-20 | 28425 | keep | 0 | May | 2023 | 0.01936 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CAGUAS | 2023-05-20 16:37 | 2023-05-20 21:39 | 200 | 5:02 | P | DESGANCHE | 2 X 100 EN C/L BAMBUAS | C23052000233 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2023-05-20 | 60400 | keep | 0 | May | 2023 | 0.041138 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-20 16:39 | 2023-05-20 16:40 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 9206-10 EN SERVICIO | B23052000176 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-20 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-20 16:39 | 2023-05-20 16:40 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 9206-07 EN SERVICIO | B23052000176 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CAGUAS | 2023-05-20 16:41 | 2023-05-20 18:33 | 86 | 1:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | C23052000234 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 112 | 2023-05-20 | 9632 | keep | 0 | May | 2023 | 0.0065603 | 5.8574e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 86
CAGUAS | 2023-05-20 16:41 | 2023-05-20 18:35 | 20 | 1:54 | P | NO SE REPORTO CAUSA | 1 X 15 XMR | C23052000088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 114 | 2023-05-20 | 2280 | keep | 0 | May | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-05-20 16:44 | 2023-05-20 17:00 | 7 | 0:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23052000071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 16 | 2023-05-20 | 112 | keep | 0 | May | 2023 | 7.6283e-05 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-05-20 16:45 | 2023-05-20 18:34 | 169 | 1:49 | P | DESGANCHE | SE SACO ARBOL SOBRE PRIMARIA Y SE LEVANTO SECUNDARIA | P23052000180 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-05-20 | 18421 | keep | 0 | May | 2023 | 0.012546 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
VEGA BAJA | 2023-05-20 17:02 | 2023-05-20 18:56 | 2231 | 1:54 | S | OTRAS CAUSAS | ENERGIZAR SUB PORTATIL # 7 Y SACAR DE SERVICIO SUB 8401 PARA CORREGIR PROBLEMA DE FASEO. GOI # AR-230520-01A | A23052000139 | New_Event | Other Causes | Include | Include | Other | 114 | 2023-05-20 | 254334 | keep | 0 | May | 2023 | 0.17323 | 0.0015195 | Sustained | FALSE | FALSE | Not_TMED_Event | 2231
VEGA BAJA | 2023-05-20 17:02 | 2023-05-20 18:56 | 1923 | 1:54 | S | OTRAS CAUSAS | ENERGIZAR SUB PORTATIL # 7 Y SACAR DE SERVICIO SUB 8401 PARA CORREGIR PROBLEMA DE FASEO. GOI # AR-230520-01A | A23052000139 | New_Event | Other Causes | Include | Include | Other | 114 | 2023-05-20 | 219222 | keep | 0 | May | 2023 | 0.14931 | 0.0013097 | Sustained | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-05-20 17:02 | 2023-05-20 18:56 | 1066 | 1:54 | S | OTRAS CAUSAS | ENERGIZAR SUB PORTATIL # 7 Y SACAR DE SERVICIO SUB 8401 PARA CORREGIR PROBLEMA DE FASEO. GOI # AR-230520-01A | A23052000139 | New_Event | Other Causes | Include | Include | Other | 114 | 2023-05-20 | 121524 | keep | 0 | May | 2023 | 0.082769 | 0.00072605 | Sustained | FALSE | FALSE | Not_TMED_Event | 1066
VEGA BAJA | 2023-05-20 17:02 | 2023-05-20 18:56 | 141 | 1:54 | S | OTRAS CAUSAS | ENERGIZAR SUB PORTATIL # 7 Y SACAR DE SERVICIO SUB 8401 PARA CORREGIR PROBLEMA DE FASEO. GOI # AR-230520-01A | A23052000139 | New_Event | Other Causes | Include | Include | Other | 114 | 2023-05-20 | 16074 | keep | 0 | May | 2023 | 0.010948 | 9.6034e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 141
BAYAMON | 2023-05-20 17:06 | 2023-05-20 17:07 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 9206-10 EN SERVICIO | B23052000183 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-20 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-20 17:06 | 2023-05-20 17:07 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 9206-07 EN SERVICIO | B23052000183 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CANOVANAS | 2023-05-20 17:14 | 2023-05-21 08:40 | 40 | 15:26 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN SU-2 LLUVIAS | R23052000071 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 926 | 2023-05-20 | 37040 | keep | 0 | May | 2023 | 0.025228 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
FAJARDO | 2023-05-20 17:15 | 2023-05-20 18:00 | 80 | 0:45 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR | R23052000072 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 45 | 2023-05-20 | 3600 | keep | 0 | May | 2023 | 0.0024519 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-05-20 17:41 | 2023-05-21 18:33 | 38 | 24:52 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C23052000257 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1492 | 2023-05-20 | 56696 | keep | 0 | May | 2023 | 0.038615 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
CANOVANAS | 2023-05-20 18:01 | 2023-05-21 10:30 | 20 | 16:29 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE X AVE | R23052000083 | New_Event | Animals | Include | Include | Wildlife | 989 | 2023-05-20 | 19780 | keep | 0 | May | 2023 | 0.013472 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
GUAYAMA | 2023-05-20 18:02 | 2023-05-20 19:22 | 50 | 1:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA 1 X 65 EN CORTE DE LINEA | P23052000187 | New_Event | Cutout Failure | Include | Include | Equipment | 80 | 2023-05-20 | 4000 | keep | 0 | May | 2023 | 0.0027244 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
FAJARDO | 2023-05-20 18:04 | 2023-05-20 19:06 | 139 | 1:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 180 EN CORTES DE LINEA LLUVIAS | R23052000085 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 62 | 2023-05-20 | 8618 | keep | 0 | May | 2023 | 0.0058697 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
FAJARDO | 2023-05-20 18:17 | 2023-05-20 19:42 | 70 | 1:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | R23052000088 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 85 | 2023-05-20 | 5950 | keep | 0 | May | 2023 | 0.0040525 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-05-20 18:22 | 2023-05-22 14:40 | 11 | 44:18 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR PAD-MOUNTED (PM) MEDIANTE G.O.I. SJ-230522-01 | S23052001047 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2658 | 2023-05-20 | 29238 | keep | 0 | May | 2023 | 0.019914 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-05-20 18:33 | 2023-05-20 21:00 | 41 | 2:27 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA DE EMERGENCIA PARA LEVANTAR CONDUCTOR PRIMARIO DEL SUELO | B23052000214 | New_Event | Primary Wire Break | Include | Include | Equipment | 147 | 2023-05-20 | 6027 | keep | 0 | May | 2023 | 0.004105 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2023-05-20 18:39 | 2023-05-21 00:46 | 128 | 6:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | B23052000215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 367 | 2023-05-20 | 46976 | keep | 0 | May | 2023 | 0.031995 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
FAJARDO | 2023-05-20 18:44 | 2023-05-20 22:27 | 25 | 3:43 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23052000093 | New_Event | Vegetation Contact | Include | Include | Vegetation | 223 | 2023-05-20 | 5575 | keep | 0 | May | 2023 | 0.0037971 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-05-20 19:02 | 2023-05-20 21:13 | 1 | 2:11 | P | SECUNDARIA/DESGANCHE | 2 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | R23052000103 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 131 | 2023-05-20 | 131 | keep | 0 | May | 2023 | 8.9224e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-20 19:12 | 2023-05-21 09:05 | 35 | 13:53 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052000166 | New_Event | Vegetation Contact | Include | Include | Vegetation | 833 | 2023-05-20 | 29155 | keep | 0 | May | 2023 | 0.019857 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-20 19:14 | 2023-05-20 20:00 | 226 | 0:46 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | B23052000225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 46 | 2023-05-20 | 10396 | keep | 0 | May | 2023 | 0.0070807 | 0.00015393 | Sustained | FALSE | FALSE | Not_TMED_Event | 226
CAGUAS | 2023-05-20 19:21 | 2023-05-20 22:44 | 384 | 3:23 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | C23052000300 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 203 | 2023-05-20 | 77952 | keep | 0 | May | 2023 | 0.053093 | 0.00026154 | Sustained | FALSE | FALSE | Not_TMED_Event | 384
CANOVANAS | 2023-05-20 19:28 | 2023-05-21 11:09 | 100 | 15:41 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE CON AVE | R23052000110 | New_Event | Animals | Include | Include | Wildlife | 941 | 2023-05-20 | 94100 | keep | 0 | May | 2023 | 0.064091 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-05-20 19:38 | 2023-05-20 20:07 | 35 | 0:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X40 EN C/L POR LLUVIAS | R23052000113 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 29 | 2023-05-20 | 1015 | keep | 0 | May | 2023 | 0.00069131 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-05-20 19:41 | 2023-05-20 21:20 | 60 | 1:39 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052000245 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 99 | 2023-05-20 | 5940 | keep | 0 | May | 2023 | 0.0040457 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-20 19:45 | 2023-05-20 22:00 | 10 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 25 EN TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | S23052001064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2023-05-20 | 1350 | keep | 0 | May | 2023 | 0.00091948 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-20 19:45 | 2023-05-21 07:01 | 14 | 11:16 | P | CAUSAS EXTERNAS | SE REEMPLAZO TRANSFORMADOR IMPACTADO POR VEHICULO DE 75 X 75KVA SJ-230520-51 | R23052000055 | Partial_restoration | Damage From Public | Include | Include | Public | 676 | 2023-05-20 | 9464 | keep | 0 | May | 2023 | 0.0064459 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-20 19:55 | 2023-05-20 19:56 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 9206-10 EN SERVICIO | B23052000237 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-20 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-20 19:55 | 2023-05-20 19:56 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 9206-07 EN SERVICIO | B23052000237 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-05-20 20:07 | 2023-05-20 20:08 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23052000242 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-20 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-20 20:07 | 2023-05-20 20:08 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23052000242 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
ARECIBO | 2023-05-20 20:22 | 2023-05-20 23:30 | 3 | 3:08 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE EN TRANSFORMADOR | A23052000175 | New_Event | Primary Wire Break | Include | Include | Equipment | 188 | 2023-05-20 | 564 | keep | 0 | May | 2023 | 0.00038414 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BARRANQUITAS | 2023-05-20 20:34 | 2023-05-22 12:30 | 17 | 39:56 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR 25KVA X 37.5 KVA | C23052000319 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2396 | 2023-05-20 | 40732 | keep | 0 | May | 2023 | 0.027742 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-05-20 20:39 | 2023-05-20 20:40 | 1284 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | B23052000249 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 1284 | keep | 0 | May | 2023 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
BAYAMON | 2023-05-20 21:08 | 2023-05-20 21:09 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO INTERRUPTOR CARGA POR EL 9206-10 EN SERVICIO | B23052000255 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-20 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-20 21:08 | 2023-05-20 21:09 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR LLEVA LA CARGA DEL 9206-07 EN SERVICIO | B23052000255 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-05-20 21:15 | 2023-05-20 21:20 | 800 | 0:05 | P | OTRAS CAUSAS | SE NORMALIZO CARGA ENTRE 1346-02 Y 1907-04 CON SJ-230503-03 PARA EVITAR INTERRUPCION PROLONGADO POR VL D2023-3348 A REALIZARSE MAÃ‘ANA (05/23/2023) - SUBESTACIONES NO FASEAN | S23052001070 | New_Event | Other Causes | Include | Include | Other | 5 | 2023-05-20 | 4000 | keep | 0 | May | 2023 | 0.0027244 | 0.00054488 | Momentary | FALSE | FALSE | Not_TMED_Event | 800
BARRANQUITAS | 2023-05-20 22:01 | 2023-05-20 23:55 | 20 | 1:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 50 EN C/L | C23052000348 | New_Event | Cutout Failure | Include | Include | Equipment | 114 | 2023-05-20 | 2280 | keep | 0 | May | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-20 22:28 | 2023-05-20 22:29 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | S2305200000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
PONCE | 2023-05-20 22:28 | 2023-05-20 22:29 | 2696 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23052000222 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 2696 | keep | 0 | May | 2023 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
ARECIBO | 2023-05-20 22:33 | 2023-05-21 11:50 | 10 | 13:17 | P | TRANSFORMADOR AVERIADO | REMPLAZO TRANSFORMADOR AVERIADO DE 75KVA POR 50 KVA | A23052000182 | New_Event | Service Transformer Failure | Include | Include | Equipment | 797 | 2023-05-20 | 7970 | keep | 0 | May | 2023 | 0.0054283 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-05-20 22:35 | 2023-05-21 09:47 | 80 | 11:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIA | M23052000258 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 672 | 2023-05-20 | 53760 | keep | 0 | May | 2023 | 0.036616 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
ARECIBO | 2023-05-20 22:48 | 2023-05-21 09:50 | 1 | 11:02 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052000183 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 662 | 2023-05-20 | 662 | keep | 0 | May | 2023 | 0.00045089 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-20 23:09 | 2023-05-21 12:50 | 14 | 13:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | A23052000184 | New_Event | Cutout Failure | Include | Include | Equipment | 821 | 2023-05-20 | 11494 | keep | 0 | May | 2023 | 0.0078285 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-05-20 23:33 | 2023-05-20 23:34 | 1320 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23052000357 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-20 | 1320 | keep | 0 | May | 2023 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
CAGUAS | 2023-05-20 23:34 | 2023-05-21 01:35 | 198 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO LLUVIA | C23052000360 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-05-20 | 23958 | keep | 0 | May | 2023 | 0.016318 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
BARRANQUITAS | 2023-05-20 23:55 | 2023-05-20 23:56 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 DE CONSAT A CIDRA | C23052000365 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 1565 | keep | 0 | May | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-20 23:55 | 2023-05-20 23:56 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 DE CONSAT A CIDRA | C23052000365 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 976 | keep | 0 | May | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-20 23:55 | 2023-05-20 23:56 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 DE CONSAT A CIDRA | C23052000365 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 548 | keep | 0 | May | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-20 23:55 | 2023-05-20 23:56 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 DE CONSAT A CIDRA | C23052000366 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 315 | keep | 0 | May | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-20 23:55 | 2023-05-20 23:56 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 DE CONSAT A CIDRA | C23052000366 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 870 | keep | 0 | May | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-20 23:55 | 2023-05-20 23:56 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 DE CONSAT A CIDRA | C23052000367 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2906 | keep | 0 | May | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-20 23:55 | 2023-05-20 23:56 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 DE CONSAT A CIDRA | C23052000367 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-20 | 2343 | keep | 0 | May | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
BARRANQUITAS | 2023-05-20 23:56 | 2023-05-21 10:15 | 20 | 10:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 50 EN C/L | C23052000348 | Partial_restoration | Cutout Failure | Include | Include | Equipment | 619 | 2023-05-20 | 12380 | keep | 0 | May | 2023 | 0.008432 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-21 00:01 | 2023-05-21 09:06 | 55 | 9:05 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA DESCARGA ELECTRICA | P23052100001 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 545 | 2023-05-21 | 29975 | keep | 0 | May | 2023 | 0.020416 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
GUAYAMA | 2023-05-21 00:29 | 2023-05-21 13:49 | 65 | 13:20 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA 1 X 65 EN CORTE DE LINEA | P23052100002 | New_Event | Primary Wire Break | Include | Include | Equipment | 800 | 2023-05-21 | 52000 | keep | 0 | May | 2023 | 0.035417 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2023-05-21 02:08 | 2023-05-21 10:18 | 20 | 8:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | M23052100001 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 490 | 2023-05-21 | 9800 | keep | 0 | May | 2023 | 0.0066747 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
VEGA BAJA | 2023-05-21 03:30 | 2023-05-21 08:16 | 30 | 4:46 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23052100005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 286 | 2023-05-21 | 8580 | keep | 0 | May | 2023 | 0.0058438 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-21 03:37 | 2023-05-21 11:21 | 1058 | 7:44 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR 1424-08 LLEVA LA CARGA DEL 1348-07 LLEVA LA CARGA DEL 1401-10 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO PUENTE PRIMARIO ABIERTO DEL 1348-07 - 100% EN SERVICIO | S23052100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 464 | 2023-05-21 | 490912 | keep | 0 | May | 2023 | 0.33436 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-05-21 03:37 | 2023-05-21 11:21 | 1000 | 7:44 | P | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR 1424-08 LLEVA LA CARGA DEL 1348-07 LLEVA LA CARGA DEL 1401-10 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO PUENTE PRIMARIO ABIERTO DEL 1348-07 - 100% EN SERVICIO | S23052100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 464 | 2023-05-21 | 464000 | keep | 0 | May | 2023 | 0.31603 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-05-21 03:37 | 2023-05-21 11:21 | 278 | 7:44 | T | CONDUCTOR ROTO O ABIERTO | DISPARO ALIMENTADOR 1424-08 LLEVA LA CARGA DEL 1348-07 LLEVA LA CARGA DEL 1401-10 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO PUENTE PRIMARIO ABIERTO DEL 1348-07 - 100% EN SERVICIO | S23052100003 | New_Event | Primary Wire Break | Include | Include | Equipment | 464 | 2023-05-21 | 128992 | keep | 0 | May | 2023 | 0.087856 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-21 03:37 | 2023-05-21 07:06 | 1295 | 3:29 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR 1424-08 LLEVA LA CARGA DEL 1348-07 LLEVA LA CARGA DEL 1401-10 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE SECCIONALIZO PUENTE PRIMARIO DEL 1348-07 ABIERTO 100% EN SERVICIO 1424-08 Y 1401-10 | S23052100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 209 | 2023-05-21 | 270655 | keep | 0 | May | 2023 | 0.18434 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-05-21 03:37 | 2023-05-21 07:06 | 9 | 3:29 | T | ALIMENTADOR AMARRADO | DISPARO ALIMENTADOR 1424-08 LLEVA LA CARGA DEL 1401-10 LLEVA LA CARGA DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE SECCIONALIZO PUENTE PRIMARIO ABIERTO DEL 1348-07 100% EN SERVICIO 1424-08 Y 1401-10 | S23052100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 209 | 2023-05-21 | 1881 | keep | 0 | May | 2023 | 0.0012811 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-05-21 04:32 | 2023-05-21 07:17 | 228 | 2:45 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23052100011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-05-21 | 37620 | keep | 0 | May | 2023 | 0.025623 | 0.00015529 | Sustained | FALSE | FALSE | Not_TMED_Event | 228
CAGUAS | 2023-05-21 05:37 | 2023-05-21 05:38 | 1709 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | C23052100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 1709 | keep | 0 | May | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
AGUADILLA | 2023-05-21 05:38 | 2023-05-21 09:30 | 80 | 3:52 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 232 | 2023-05-21 | 18560 | keep | 0 | May | 2023 | 0.012641 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-21 05:41 | 2023-05-21 05:42 | 1709 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | C23052100023 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 1709 | keep | 0 | May | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
CAGUAS | 2023-05-21 05:42 | 2023-05-21 17:52 | 517 | 12:10 | P | DESGANCHE | 2 X 200 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23052100024 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 730 | 2023-05-21 | 377410 | keep | 0 | May | 2023 | 0.25705 | 0.00035213 | Sustained | FALSE | FALSE | Not_TMED_Event | 517
CAGUAS | 2023-05-21 06:02 | 2023-05-21 17:46 | 264 | 11:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23052100026 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 704 | 2023-05-21 | 185856 | keep | 0 | May | 2023 | 0.12659 | 0.00017981 | Sustained | FALSE | FALSE | Not_TMED_Event | 264
MAYAGÃœEZ | 2023-05-21 06:04 | 2023-05-21 10:33 | 40 | 4:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR MAL TIEMPO | M23052100005 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 269 | 2023-05-21 | 10760 | keep | 0 | May | 2023 | 0.0073286 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-21 06:09 | 2023-05-21 06:10 | 7 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO ALIMENTADOR | S2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 7 | keep | 0 | May | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-21 06:09 | 2023-05-21 06:10 | 15 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO ALIMENTADOR | S2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 15 | keep | 0 | May | 2023 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-05-21 06:11 | 2023-05-21 09:18 | 55 | 3:07 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | C23052100028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 187 | 2023-05-21 | 10285 | keep | 0 | May | 2023 | 0.0070051 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
MAYAGÃœEZ | 2023-05-21 06:26 | 2023-05-21 08:55 | 50 | 2:29 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | M23052100006 | New_Event | Animals | Include | Include | Wildlife | 149 | 2023-05-21 | 7450 | keep | 0 | May | 2023 | 0.0050742 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-21 06:31 | 2023-05-21 06:32 | 2900 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 2900 | keep | 0 | May | 2023 | 0.0019752 | 0.0019752 | Momentary | FALSE | FALSE | Not_TMED_Event | 2900
BARRANQUITAS | 2023-05-21 06:31 | 2023-05-21 10:49 | 69 | 4:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23052100034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 258 | 2023-05-21 | 17802 | keep | 0 | May | 2023 | 0.012125 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
VEGA BAJA | 2023-05-21 06:35 | 2023-05-21 06:36 | 3387 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23052100013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 3387 | keep | 0 | May | 2023 | 0.0023069 | 0.0023069 | Momentary | FALSE | FALSE | Not_TMED_Event | 3387
PONCE | 2023-05-21 06:36 | 2023-05-21 09:38 | 10 | 3:02 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REEMPLAZAERON PUENTES SECUNDARIOS EN TRANSFORMADOR | P23052100020 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 182 | 2023-05-21 | 1820 | keep | 0 | May | 2023 | 0.0012396 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-21 06:37 | 2023-05-21 08:47 | 39 | 2:10 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R23052100008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-05-21 | 5070 | keep | 0 | May | 2023 | 0.0034532 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2023-05-21 06:38 | 2023-05-21 08:53 | 279 | 2:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | B23052100015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 135 | 2023-05-21 | 37665 | keep | 0 | May | 2023 | 0.025653 | 0.00019003 | Sustained | FALSE | FALSE | Not_TMED_Event | 279
UTUADO | 2023-05-21 06:40 | 2023-05-21 09:20 | 15 | 2:40 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052100007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-05-21 | 2400 | keep | 0 | May | 2023 | 0.0016346 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-21 06:46 | 2023-05-21 08:05 | 2448 | 1:19 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE SECCIONALIZO TRAMO Y SE REEMPLAZO FUSIBLE FUNDIDO EN LA ALTA DEL MAIN XMR SE ENCONTRO PUENTE ABIERTO EN 3009-03. CAPITOR TRIP NO OPERO A TIEMPO Y FUNDIO FUSIBLES. SE TRANSFIRIO AL 3004-04 | C23052100045 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 79 | 2023-05-21 | 193392 | keep | 0 | May | 2023 | 0.13172 | 0.0016673 | Sustained | FALSE | FALSE | Not_TMED_Event | 2448
CAGUAS | 2023-05-21 06:46 | 2023-05-21 13:52 | 128 | 7:06 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE SECCIONALIZO TRAMO Y SE REEMPLAZO FUSIBLE FUNDIDO EN LA ALTA DEL MAIN XMR SE ENCONTRO PUENTE ABIERTO EN 3009-03 CAPITOR TRIP NO OPERO A TIEMPO Y FUNDIO FUSIBLES. | C23052100045 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 426 | 2023-05-21 | 54528 | keep | 0 | May | 2023 | 0.037139 | 8.718e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 128
CAGUAS | 2023-05-21 06:46 | 2023-05-21 15:49 | 273 | 9:03 | S | CONDUCTOR ROTO O ABIERTO | CG-230521-01 SE CERRO PUENTE DE TRONCAL AL RISER DE CENTRO COMERCIAL SE DEJO LA CARGA TRANSFERIDA AL 3009-04 | C23052100045 | New_Event | Primary Wire Break | Include | Include | Equipment | 543 | 2023-05-21 | 148239 | keep | 0 | May | 2023 | 0.10096 | 0.00018594 | Sustained | FALSE | FALSE | Not_TMED_Event | 273
CAGUAS | 2023-05-21 06:46 | 2023-05-21 08:26 | 1772 | 1:40 | S | INTERRUPTOR DEFECTUOSO O NO OPERA | SE SECCIONALIZO TRAMO Y SE REEMPLAZO FUSIBLE FUNDIDO EN LA ALTA DEL MAIN XMR SE ENCONTRO PUENTE ABIERTO EN 3009-03 CAPITOR TRIP NO OPERO A TIEMPO Y FUNDIO FUSIBLES. SE TRANSFIRIO AL 3009-01 | C23052100045 | New_Event | Feeder Breaker Failure | Include | Include | Equipment | 100 | 2023-05-21 | 177200 | keep | 0 | May | 2023 | 0.12069 | 0.0012069 | Sustained | FALSE | FALSE | Not_TMED_Event | 1772
VEGA BAJA | 2023-05-21 06:47 | 2023-05-21 10:15 | 75 | 3:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | A23052100008 | New_Event | Cutout Failure | Include | Include | Equipment | 208 | 2023-05-21 | 15600 | keep | 0 | May | 2023 | 0.010625 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-05-21 07:01 | 2023-05-21 07:04 | 1615 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL | S2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-21 | 4845 | keep | 0 | May | 2023 | 0.0032999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
CANOVANAS | 2023-05-21 07:04 | 2023-05-21 08:23 | 14 | 1:19 | P | CAUSAS EXTERNAS | SE REEMPLAZO TRANSFORMADOR IMPACTADO POR VEHICULO DE 75 X 75KVA SJ-230520-51 | R23052000055 | Partial_restoration | Damage From Public | Include | Include | Public | 79 | 2023-05-21 | 1106 | keep | 0 | May | 2023 | 0.00075329 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-21 07:05 | 2023-05-21 14:58 | 41 | 7:53 | P | DESGANCHE | 1 X 100 1X 80 C/L 1X 80 CL/L 1 X 15 EN XMR DESGANCHE | B23052100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 473 | 2023-05-21 | 19393 | keep | 0 | May | 2023 | 0.013208 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
FAJARDO | 2023-05-21 07:16 | 2023-05-21 12:09 | 70 | 4:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REEMPLAZO DISCO PARTIDO | R23052100011 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 293 | 2023-05-21 | 20510 | keep | 0 | May | 2023 | 0.013969 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2023-05-21 07:18 | 2023-05-21 16:29 | 3 | 9:11 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REEMPLAZO CAJA QUEMADA | R23052100051 | New_Event | Cutout Failure | Include | Include | Equipment | 551 | 2023-05-21 | 1653 | keep | 0 | May | 2023 | 0.0011259 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-05-21 07:54 | 2023-05-22 08:00 | 23 | 24:06 | P | ANIMAL | 1 X 30 EN XMR CRUCE POR AVE | C23052100069 | New_Event | Animals | Include | Include | Wildlife | 1446 | 2023-05-21 | 33258 | keep | 0 | May | 2023 | 0.022652 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
ARECIBO | 2023-05-21 08:01 | 2023-05-21 15:25 | 30 | 7:24 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | A23052100010 | New_Event | Primary Wire Break | Include | Include | Equipment | 444 | 2023-05-21 | 13320 | keep | 0 | May | 2023 | 0.0090722 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-05-21 08:11 | 2023-05-21 12:01 | 11 | 3:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR LLUVIAS | C23052100074 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 230 | 2023-05-21 | 2530 | keep | 0 | May | 2023 | 0.0017232 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-05-21 08:23 | 2023-05-21 08:25 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S2305210000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-21 | 3230 | keep | 0 | May | 2023 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
BARRANQUITAS | 2023-05-21 08:23 | 2023-05-21 11:14 | 500 | 2:51 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23052100076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-05-21 | 85500 | keep | 0 | May | 2023 | 0.058234 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CANOVANAS | 2023-05-21 08:25 | 2023-05-21 11:54 | 14 | 3:29 | P | CAUSAS EXTERNAS | SE REEMPLAZO TRANSFORMADOR IMPACTADO POR VEHICULO DE 75 X 75KVA SJ-230520-51 | R23052000055 | Partial_restoration | Damage From Public | Include | Include | Public | 209 | 2023-05-21 | 2926 | keep | 0 | May | 2023 | 0.0019929 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-05-21 08:28 | 2023-05-21 13:00 | 75 | 4:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | P23052100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2023-05-21 | 20400 | keep | 0 | May | 2023 | 0.013894 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-05-21 08:43 | 2023-05-21 08:44 | 7621 | 0:01 | T | DESGANCHE | RECIERRE | R23052100027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 7621 | keep | 0 | May | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-05-21 08:44 | 2023-05-21 09:32 | 100 | 0:48 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | R23052100091 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 48 | 2023-05-21 | 4800 | keep | 0 | May | 2023 | 0.0032693 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-05-21 08:48 | 2023-05-21 14:35 | 50 | 5:47 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052100016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 347 | 2023-05-21 | 17350 | keep | 0 | May | 2023 | 0.011817 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-05-21 08:48 | 2023-05-21 16:25 | 5 | 7:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23052100015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 457 | 2023-05-21 | 2285 | keep | 0 | May | 2023 | 0.0015563 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-05-21 08:49 | 2023-05-21 09:56 | 200 | 1:07 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA 1 X 50 EN RISER LLUVIAS | R23052100028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 67 | 2023-05-21 | 13400 | keep | 0 | May | 2023 | 0.0091267 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-05-21 08:50 | 2023-05-21 12:27 | 2 | 3:37 | P | ANIMAL | 2 X 8 EN TRANSFORMADOR AVE CRUZO FASE | R23052100030 | New_Event | Animals | Include | Include | Wildlife | 217 | 2023-05-21 | 434 | keep | 0 | May | 2023 | 0.0002956 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-05-21 08:52 | 2023-05-21 12:55 | 6 | 4:03 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | A23052100017 | New_Event | Cutout Failure | Include | Include | Equipment | 243 | 2023-05-21 | 1458 | keep | 0 | May | 2023 | 0.00099304 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-05-21 09:09 | 2023-05-21 11:57 | 60 | 2:48 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | R23052100033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 168 | 2023-05-21 | 10080 | keep | 0 | May | 2023 | 0.0068654 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-21 09:12 | 2023-05-21 15:57 | 40 | 6:45 | P | DESGANCHE | 1X30 EN C/L DESGANCHE | S23052100190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 405 | 2023-05-21 | 16200 | keep | 0 | May | 2023 | 0.011034 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
GUAYAMA | 2023-05-21 09:20 | 2023-05-21 10:40 | 25 | 1:20 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA PALOMA CRUZO FASE | P23052100042 | New_Event | Animals | Include | Include | Wildlife | 80 | 2023-05-21 | 2000 | keep | 0 | May | 2023 | 0.0013622 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-05-21 09:22 | 2023-05-21 11:36 | 12 | 2:14 | P | ANIMAL | 2 X 80 EN SU CRUCE POR RANA | C23052100104 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-05-21 | 1608 | keep | 0 | May | 2023 | 0.0010952 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-21 09:26 | 2023-05-21 09:27 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-05-21 09:28 | 2023-05-21 17:14 | 959 | 7:46 | T | OTRAS CAUSAS | BY-230521-01 REMPLAZO DE VS-4A SE ABRIO ESTA CARGA PARA PODER SECCIONALIZARLO | B23052100209 | New_Event | Other Causes | Include | Include | Other | 466 | 2023-05-21 | 446894 | keep | 0 | May | 2023 | 0.30438 | 0.00065317 | Sustained | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-05-21 09:28 | 2023-05-21 17:14 | 1264 | 7:46 | T | OTRAS CAUSAS | BY-230521-01 REMPLAZO DE VS-4A SE ABRIO ESTA CARGA PARA PODER SECCIONALIZARLO | S23052100209 | New_Event | Other Causes | Include | Include | Other | 466 | 2023-05-21 | 589024 | keep | 0 | May | 2023 | 0.40118 | 0.0008609 | Sustained | FALSE | FALSE | Not_TMED_Event | 1264
BAYAMON | 2023-05-21 09:29 | 2023-05-21 09:30 | 57 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 57 | keep | 0 | May | 2023 | 3.8822e-05 | 3.8822e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 57
GUAYAMA | 2023-05-21 09:33 | 2023-05-21 13:40 | 35 | 4:07 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA LINEAS CRUZADAS | P23052100047 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 247 | 2023-05-21 | 8645 | keep | 0 | May | 2023 | 0.0058881 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-05-21 09:55 | 2023-05-21 12:11 | 6 | 2:16 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR | C23052100115 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 136 | 2023-05-21 | 816 | keep | 0 | May | 2023 | 0.00055577 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-21 10:12 | 2023-05-21 10:13 | 2280 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE FUERTES LLUVIAS | C2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 2280 | keep | 0 | May | 2023 | 0.0015529 | 0.0015529 | Momentary | FALSE | FALSE | Not_TMED_Event | 2280
CAGUAS | 2023-05-21 10:30 | 2023-05-21 17:09 | 10 | 6:39 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23052100137 | New_Event | Vegetation Contact | Include | Include | Vegetation | 399 | 2023-05-21 | 3990 | keep | 0 | May | 2023 | 0.0027176 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-21 10:33 | 2023-05-21 16:46 | 50 | 6:13 | P | DESGANCHE | 1 X 65 C/L DESGANCHE | B23052100282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 373 | 2023-05-21 | 18650 | keep | 0 | May | 2023 | 0.012702 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-05-21 10:39 | 2023-05-21 15:20 | 1 | 4:41 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE RISER | A23052100029 | New_Event | Primary Wire Break | Include | Include | Equipment | 281 | 2023-05-21 | 281 | keep | 0 | May | 2023 | 0.00019139 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-21 10:51 | 2023-05-21 13:22 | 5 | 2:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 3X20 EN MONTURA DE XMRS SE REMPLAZO CAJA PRIMARIA | S23052100295 | New_Event | Cutout Failure | Include | Include | Equipment | 151 | 2023-05-21 | 755 | keep | 0 | May | 2023 | 0.00051423 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-21 10:58 | 2023-05-21 10:59 | 4028 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23052100075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 4028 | keep | 0 | May | 2023 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
BARRANQUITAS | 2023-05-21 11:04 | 2023-05-21 13:58 | 3296 | 2:54 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE A VERETA CG-230521-02 LLEVA 20% DEL 9602-03 LLEVA LA CARGA DEL 9602-04 | C23052100168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2023-05-21 | 573504 | keep | 0 | May | 2023 | 0.39061 | 0.0022449 | Sustained | FALSE | FALSE | Not_TMED_Event | 3296
BARRANQUITAS | 2023-05-21 11:04 | 2023-05-21 13:58 | 273 | 2:54 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE A VERETA CG-230521-02 20% DE SU CARGA POR EL 9602-02 | C23052100168 | New_Event | Feeder Load Transferred | Include | Include | Other | 174 | 2023-05-21 | 47502 | keep | 0 | May | 2023 | 0.032353 | 0.00018594 | Sustained | FALSE | FALSE | Not_TMED_Event | 273
BARRANQUITAS | 2023-05-21 11:04 | 2023-05-21 13:58 | 2937 | 2:54 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE REALIZO DESGANCHE A VERETA CG-230521-02 100% DE SU CARGA POR EL 9601-02 | C23052100168 | New_Event | Feeder Load Transferred | Include | Include | Other | 174 | 2023-05-21 | 511038 | keep | 0 | May | 2023 | 0.34807 | 0.0020004 | Sustained | FALSE | FALSE | Not_TMED_Event | 2937
VEGA BAJA | 2023-05-21 11:09 | 2023-05-21 13:30 | 150 | 2:21 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052100031 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-05-21 | 21150 | keep | 0 | May | 2023 | 0.014405 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-21 11:29 | 2023-05-21 15:38 | 97 | 4:09 | P | DESGANCHE | 1X65 EN C/L Y 1X50 EN RISER DESGANCHE | S23052100336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 249 | 2023-05-21 | 24153 | keep | 0 | May | 2023 | 0.01645 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
CANOVANAS | 2023-05-21 11:36 | 2023-05-21 11:39 | 172 | 0:03 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23052100340 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-21 | 516 | keep | 0 | May | 2023 | 0.00035145 | 0.00011715 | Momentary | FALSE | FALSE | Not_TMED_Event | 172
GUAYAMA | 2023-05-21 11:42 | 2023-05-21 17:40 | 10 | 5:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN RISER FUERTE LLUVIA | P23052100084 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 358 | 2023-05-21 | 3580 | keep | 0 | May | 2023 | 0.0024383 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-21 11:46 | 2023-05-21 16:12 | 75 | 4:26 | P | DESGANCHE | 2X100 EN C/L DESGANCHE | S23052100345 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-05-21 | 19950 | keep | 0 | May | 2023 | 0.013588 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CAGUAS | 2023-05-21 11:49 | 2023-05-21 18:48 | 187 | 6:59 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA | C23052100197 | New_Event | Vegetation Contact | Include | Include | Vegetation | 419 | 2023-05-21 | 78353 | keep | 0 | May | 2023 | 0.053366 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
PONCE | 2023-05-21 12:00 | 2023-05-21 13:50 | 22 | 1:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE HIZO DESGANCHE | P23052100092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 110 | 2023-05-21 | 2420 | keep | 0 | May | 2023 | 0.0016483 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
UTUADO | 2023-05-21 12:00 | 2023-05-21 14:47 | 4 | 2:47 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE IDENTIFICO CAUSA | A23052100054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 167 | 2023-05-21 | 668 | keep | 0 | May | 2023 | 0.00045497 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-05-21 12:05 | 2023-05-21 14:47 | 1058 | 2:42 | P | DESGANCHE | DISPARO DE INTERRUPTOR 1424-08 LLEVA LA CARGA DEL 1401-10 LLEVA LA CARGA DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 100% EN SERVICIO - SE REALIZO DESGANCHE EN EL AREA TRANSFERIDA DEL 1336-08 | S23052100354 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-05-21 | 171396 | keep | 0 | May | 2023 | 0.11674 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-05-21 12:05 | 2023-05-21 13:39 | 1000 | 1:34 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA LA CARGA DEL 1401-10 LLEVA LA CARGA DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 100% EN SERVICIO - SE SECCIONALIZO PARA DESGANCHE EN EL 1336-08 | S23052100354 | New_Event | Feeder Load Transferred | Include | Include | Other | 94 | 2023-05-21 | 94000 | keep | 0 | May | 2023 | 0.064023 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-05-21 12:05 | 2023-05-21 13:39 | 278 | 1:34 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA LA CARGA DEL 1401-10 LLEVA LA CARGA DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 100% EN SERVICIO - SE SECCIONALIZO PARA DESGANCHE EN EL 1336-08 | S23052100354 | New_Event | Feeder Load Transferred | Include | Include | Other | 94 | 2023-05-21 | 26132 | keep | 0 | May | 2023 | 0.017798 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-21 12:05 | 2023-05-21 13:39 | 1295 | 1:34 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA LA CARGA DEL 1401-10 LLEVA LA CARGA DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 100% EN SERVICIO - SE SECCIONALIZO PARA DESGANCHE EN EL 1336-08 | S23052100354 | New_Event | Feeder Load Transferred | Include | Include | Other | 94 | 2023-05-21 | 121730 | keep | 0 | May | 2023 | 0.08291 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-05-21 12:05 | 2023-05-21 13:39 | 9 | 1:34 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA LA CARGA DEL 1401-10 LLEVA LA CARGA DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 100% EN SERVICIO - SE SECCIONALIZO PARA DESGANCHE EN EL 1336-08 | S23052100354 | New_Event | Feeder Load Transferred | Include | Include | Other | 94 | 2023-05-21 | 846 | keep | 0 | May | 2023 | 0.00057621 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
YAUCO | 2023-05-21 12:21 | 2023-05-21 15:42 | 10 | 3:21 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR DESCARGA ELECTRICA | P23052100088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 201 | 2023-05-21 | 2010 | keep | 0 | May | 2023 | 0.001369 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-21 12:30 | 2023-05-21 13:43 | 60 | 1:13 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | M23052100035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-05-21 | 4380 | keep | 0 | May | 2023 | 0.0029832 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-05-21 12:40 | 2023-05-21 16:00 | 70 | 3:20 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23052100039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-05-21 | 14000 | keep | 0 | May | 2023 | 0.0095353 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-05-21 12:52 | 2023-05-21 16:00 | 30 | 3:08 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052100040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-05-21 | 5640 | keep | 0 | May | 2023 | 0.0038414 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-21 13:01 | 2023-05-21 18:04 | 50 | 5:03 | P | NO SE REPORTO CAUSA | 1X65 EN C/L | S23052100390 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 303 | 2023-05-21 | 15150 | keep | 0 | May | 2023 | 0.010319 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-05-21 13:16 | 2023-05-22 08:54 | 2 | 19:38 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | B23052100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1178 | 2023-05-21 | 2356 | keep | 0 | May | 2023 | 0.0016047 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-05-21 13:19 | 2023-05-21 17:42 | 206 | 4:23 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | C23052100259 | New_Event | Cutout Failure | Include | Include | Equipment | 263 | 2023-05-21 | 54178 | keep | 0 | May | 2023 | 0.0369 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
BAYAMON | 2023-05-21 13:21 | 2023-05-21 16:45 | 50 | 3:24 | P | DESGANCHE | 1X50 EN C/L DESGANCHE | B23052100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 204 | 2023-05-21 | 10200 | keep | 0 | May | 2023 | 0.0069472 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-05-21 13:30 | 2023-05-22 06:52 | 12 | 17:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X15 EN XMR SE REMPLAZO PORTAFUSIBLE | B23052100406 | New_Event | Cutout Failure | Include | Include | Equipment | 1042 | 2023-05-21 | 12504 | keep | 0 | May | 2023 | 0.0085164 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CAGUAS | 2023-05-21 13:41 | 2023-05-22 11:38 | 25 | 21:57 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23052100274 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1317 | 2023-05-21 | 32925 | keep | 0 | May | 2023 | 0.022425 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-05-21 13:43 | 2023-05-21 14:28 | 8 | 0:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23052100276 | New_Event | Secondary Wire Break | Include | Include | Equipment | 45 | 2023-05-21 | 360 | keep | 0 | May | 2023 | 0.00024519 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 1212 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1212 | keep | 0 | May | 2023 | 0.00082549 | 0.00082549 | Momentary | FALSE | FALSE | Not_TMED_Event | 1212
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 200 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 200 | keep | 0 | May | 2023 | 0.00013622 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 520 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 520 | keep | 0 | May | 2023 | 0.00035417 | 0.00035417 | Momentary | FALSE | FALSE | Not_TMED_Event | 520
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 948 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 948 | keep | 0 | May | 2023 | 0.00064568 | 0.00064568 | Momentary | FALSE | FALSE | Not_TMED_Event | 948
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 114 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 114 | keep | 0 | May | 2023 | 7.7645e-05 | 7.7645e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 114
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 2113 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 2113 | keep | 0 | May | 2023 | 0.0014392 | 0.0014392 | Momentary | FALSE | FALSE | Not_TMED_Event | 2113
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 1478 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1478 | keep | 0 | May | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
PONCE | 2023-05-21 13:43 | 2023-05-21 13:44 | 396 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 1800 | P23052100102 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 396 | keep | 0 | May | 2023 | 0.00026971 | 0.00026971 | Momentary | FALSE | FALSE | Not_TMED_Event | 396
UTUADO | 2023-05-21 14:07 | 2023-05-21 16:30 | 30 | 2:23 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA EN CONVERTIDOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052100049 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 143 | 2023-05-21 | 4290 | keep | 0 | May | 2023 | 0.0029219 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-21 14:13 | 2023-05-21 16:03 | 7 | 1:50 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C23052100293 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-05-21 | 770 | keep | 0 | May | 2023 | 0.00052444 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-05-21 14:22 | 2023-05-21 17:00 | 120 | 2:38 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | P23052100108 | New_Event | Primary Wire Break | Include | Include | Equipment | 158 | 2023-05-21 | 18960 | keep | 0 | May | 2023 | 0.012914 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
VEGA BAJA | 2023-05-21 14:25 | 2023-05-21 18:30 | 50 | 4:05 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A23052100053 | New_Event | Animals | Include | Include | Wildlife | 245 | 2023-05-21 | 12250 | keep | 0 | May | 2023 | 0.0083434 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-21 14:42 | 2023-05-21 14:44 | 3046 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE VERIFICO PERSONA, TODO EN ORDEN LLEVANDO LA CARGA DEL 1647-10 (61 CLIENTES) LLEVANDO PARTE DE LA CARGA DEL 1647-09 (15%) (308 CLIENTES) | R2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-21 | 6092 | keep | 0 | May | 2023 | 0.0041492 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-05-21 14:42 | 2023-05-21 14:44 | 308 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO CARGA POR EL 1646-03 | R2305210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-21 | 616 | keep | 0 | May | 2023 | 0.00041955 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-05-21 14:42 | 2023-05-21 14:44 | 61 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO CARGA POR EL 1646-03 | R2305210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-21 | 122 | keep | 0 | May | 2023 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2023-05-21 15:00 | 2023-05-21 18:18 | 113 | 3:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA NO FUNDIO | S23052100448 | New_Event | Cutout Failure | Include | Include | Equipment | 198 | 2023-05-21 | 22374 | keep | 0 | May | 2023 | 0.015239 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
SAN JUAN | 2023-05-21 15:19 | 2023-05-22 12:05 | 20 | 20:46 | P | DESGANCHE | SE CERRO PUENTE PRIMARIO Y SE REALIZO DESGANCHE PRIMARIO MASIVO - TRASPATIO - MEDIANTE G.O.I. SJ-230522-02 | S23052100456 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1246 | 2023-05-21 | 24920 | keep | 0 | May | 2023 | 0.016973 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-21 15:20 | 2023-05-21 15:48 | 7 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23052100051 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-05-21 | 196 | keep | 0 | May | 2023 | 0.00013349 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-05-21 15:24 | 2023-05-21 15:25 | 508 | 0:01 | T | DESGANCHE | RECIERRE | P23052100118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 508 | keep | 0 | May | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-05-21 15:24 | 2023-05-21 15:25 | 64 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23052100118 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-21 | 64 | keep | 0 | May | 2023 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
SAN JUAN | 2023-05-21 15:30 | 2023-05-21 18:14 | 40 | 2:44 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | S23052100458 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-05-21 | 6560 | keep | 0 | May | 2023 | 0.004468 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-21 15:35 | 2023-05-21 18:20 | 81 | 2:45 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA DESGANCHE | P23052100119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-05-21 | 13365 | keep | 0 | May | 2023 | 0.0091028 | 5.5169e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 81
BAYAMON | 2023-05-21 15:36 | 2023-05-21 18:20 | 69 | 2:44 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | B23052100009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 164 | 2023-05-21 | 11316 | keep | 0 | May | 2023 | 0.0077073 | 4.6996e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 69
AGUADILLA | 2023-05-21 15:46 | 2023-05-21 19:15 | 200 | 3:29 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ROTA | M23052100059 | New_Event | Primary Wire Break | Include | Include | Equipment | 209 | 2023-05-21 | 41800 | keep | 0 | May | 2023 | 0.02847 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-05-21 16:02 | 2023-05-21 17:14 | 50 | 1:12 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23052100061 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-05-21 | 3600 | keep | 0 | May | 2023 | 0.0024519 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-21 16:07 | 2023-05-21 16:08 | 281 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 281 | keep | 0 | May | 2023 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2023-05-21 16:07 | 2023-05-21 16:08 | 1252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100063 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1252 | keep | 0 | May | 2023 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2023-05-21 16:07 | 2023-05-21 16:08 | 595 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 595 | keep | 0 | May | 2023 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2023-05-21 16:07 | 2023-05-21 16:08 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 51 | keep | 0 | May | 2023 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2023-05-21 16:07 | 2023-05-21 16:08 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100062 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 721 | keep | 0 | May | 2023 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2023-05-21 16:07 | 2023-05-21 16:08 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 3502 | keep | 0 | May | 2023 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2023-05-21 16:07 | 2023-05-21 16:08 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1241 | keep | 0 | May | 2023 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2023-05-21 16:07 | 2023-05-21 16:08 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100060 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 650 | keep | 0 | May | 2023 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2023-05-21 16:07 | 2023-05-21 16:08 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1382 | keep | 0 | May | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2023-05-21 16:07 | 2023-05-21 16:08 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100061 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 654 | keep | 0 | May | 2023 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
MAYAGÃœEZ | 2023-05-21 16:13 | 2023-05-21 16:14 | 281 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100066 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 281 | keep | 0 | May | 2023 | 0.00019139 | 0.00019139 | Momentary | FALSE | FALSE | Not_TMED_Event | 281
MAYAGÃœEZ | 2023-05-21 16:13 | 2023-05-21 16:14 | 1252 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100066 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1252 | keep | 0 | May | 2023 | 0.00085273 | 0.00085273 | Momentary | FALSE | FALSE | Not_TMED_Event | 1252
AGUADILLA | 2023-05-21 16:13 | 2023-05-21 16:14 | 595 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100065 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 595 | keep | 0 | May | 2023 | 0.00040525 | 0.00040525 | Momentary | FALSE | FALSE | Not_TMED_Event | 595
AGUADILLA | 2023-05-21 16:13 | 2023-05-21 16:14 | 51 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100065 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 51 | keep | 0 | May | 2023 | 3.4736e-05 | 3.4736e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 51
AGUADILLA | 2023-05-21 16:13 | 2023-05-21 16:14 | 721 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | M23052100065 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 721 | keep | 0 | May | 2023 | 0.00049107 | 0.00049107 | Momentary | FALSE | FALSE | Not_TMED_Event | 721
UTUADO | 2023-05-21 16:13 | 2023-05-21 16:14 | 3502 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100062 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 3502 | keep | 0 | May | 2023 | 0.0023852 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2023-05-21 16:13 | 2023-05-21 16:14 | 1241 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100062 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1241 | keep | 0 | May | 2023 | 0.00084524 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2023-05-21 16:13 | 2023-05-21 16:14 | 650 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100062 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 650 | keep | 0 | May | 2023 | 0.00044271 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
UTUADO | 2023-05-21 16:13 | 2023-05-21 16:14 | 1382 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100063 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 1382 | keep | 0 | May | 2023 | 0.00094127 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
UTUADO | 2023-05-21 16:13 | 2023-05-21 16:14 | 654 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 8100 TIENE DESGANCHES PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. HABÃA MAL TIEMPO EN EL ÃREA. | A23052100063 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-21 | 654 | keep | 0 | May | 2023 | 0.00044544 | 0.00044544 | Momentary | FALSE | FALSE | Not_TMED_Event | 654
BAYAMON | 2023-05-21 16:13 | 2023-05-21 16:14 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 1859 | keep | 0 | May | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
VEGA BAJA | 2023-05-21 16:22 | 2023-05-22 14:39 | 1 | 22:17 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE DESGANCHO EN LINEAS SECUNDARIAS | A23052100065 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1337 | 2023-05-21 | 1337 | keep | 0 | May | 2023 | 0.00091062 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-21 16:30 | 2023-05-21 16:31 | 1533 | 0:01 | T | DESGANCHE | RECIERRE | B23052100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 1533 | keep | 0 | May | 2023 | 0.0010441 | 0.0010441 | Momentary | FALSE | FALSE | Not_TMED_Event | 1533
BAYAMON | 2023-05-21 16:31 | 2023-05-21 19:30 | 100 | 2:59 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23052100483 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-05-21 | 17900 | keep | 0 | May | 2023 | 0.012192 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-21 16:33 | 2023-05-22 12:50 | 12 | 20:17 | P | NO SE REPORTO CAUSA | 1 X 40 Y 1 X 65 EN CORTES DE LINEA | C23052100342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1217 | 2023-05-21 | 14604 | keep | 0 | May | 2023 | 0.0099467 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-21 16:34 | 2023-05-21 16:35 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305210000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 1859 | keep | 0 | May | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
AGUADILLA | 2023-05-21 16:44 | 2023-05-21 19:20 | 1798 | 2:36 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 13700 SOBRE ALIMENTADOR 7502-03 Y SE ENERGIZO LA SUBESTACION CONDUCTOR AVERIADO ENTRE 13701B-13707 | A23052100081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 156 | 2023-05-21 | 280488 | keep | 0 | May | 2023 | 0.19104 | 0.0012246 | Sustained | FALSE | FALSE | Not_TMED_Event | 1798
AGUADILLA | 2023-05-21 16:44 | 2023-05-21 19:20 | 3309 | 2:36 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 13700 SOBRE ALIMENTADOR 7502-03 Y SE ENERGIZO LA SUBESTACION CONDUCTOR AVERIADO ENTRE 13701B-13707 | A23052100081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 156 | 2023-05-21 | 516204 | keep | 0 | May | 2023 | 0.35158 | 0.0022537 | Sustained | FALSE | FALSE | Not_TMED_Event | 3309
AGUADILLA | 2023-05-21 16:44 | 2023-05-21 19:20 | 713 | 2:36 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 13700 SOBRE ALIMENTADOR 7502-03 Y SE ENERGIZO LA SUBESTACION CONDUCTOR AVERIADO ENTRE 13701B-13707 | A23052100081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 156 | 2023-05-21 | 111228 | keep | 0 | May | 2023 | 0.075757 | 0.00048562 | Sustained | FALSE | FALSE | Not_TMED_Event | 713
AGUADILLA | 2023-05-21 16:44 | 2023-05-21 19:20 | 1628 | 2:36 | S | LINEA DE TRANSMISION 38KV | SE SECCIONALIZO LINEA 13700 SOBRE ALIMENTADOR 7502-03 Y SE ENERGIZO LA SUBESTACION CONDUCTOR AVERIADO ENTRE 13701B-13707 | A23052100081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 156 | 2023-05-21 | 253968 | keep | 0 | May | 2023 | 0.17298 | 0.0011088 | Sustained | FALSE | FALSE | Not_TMED_Event | 1628
AGUADILLA | 2023-05-21 16:44 | 2023-05-21 19:45 | 1483 | 3:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION A TRAVES DE LINEA 2700 CONDUCTOR AVERIADO ENTRE 13701B-13707 | A23052100082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 181 | 2023-05-21 | 268423 | keep | 0 | May | 2023 | 0.18282 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
AGUADILLA | 2023-05-21 16:44 | 2023-05-21 19:45 | 89 | 3:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 13700 SE SECCIONALIZO LA LINEA Y SE ENERGIZO LA SUBESTACION A TRAVES DE LINEA 2700 CONDUCTOR AVERIADO ENTRE 13701B-13707 | A23052100082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 181 | 2023-05-21 | 16109 | keep | 0 | May | 2023 | 0.010972 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
PONCE | 2023-05-21 16:50 | 2023-05-21 19:40 | 30 | 2:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P23052100131 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 170 | 2023-05-21 | 5100 | keep | 0 | May | 2023 | 0.0034736 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-21 17:04 | 2023-05-21 22:28 | 7 | 5:24 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 25KVA AVERIADO | B23052100109 | New_Event | Service Transformer Failure | Include | Include | Equipment | 324 | 2023-05-21 | 2268 | keep | 0 | May | 2023 | 0.0015447 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-05-21 17:22 | 2023-05-21 17:23 | 508 | 0:01 | T | DESGANCHE | RECIERRE | P23052100136 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 508 | keep | 0 | May | 2023 | 0.000346 | 0.000346 | Momentary | FALSE | FALSE | Not_TMED_Event | 508
YAUCO | 2023-05-21 17:22 | 2023-05-21 17:23 | 64 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23052100136 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-21 | 64 | keep | 0 | May | 2023 | 4.359e-05 | 4.359e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 64
YAUCO | 2023-05-21 17:23 | 2023-05-21 19:35 | 106 | 2:12 | P | PARARRAYOS DEFECTUOSO | SE ELIMINO PARARRAYO CRUZADO SE RETIRO RAMA 1 X 80 EN CORTE DE LINEA | P23052100139 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 132 | 2023-05-21 | 13992 | keep | 0 | May | 2023 | 0.0095299 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
CAGUAS | 2023-05-21 17:43 | 2023-05-21 18:59 | 56 | 1:16 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO DE LINEA A CAJA DE CORTE DE LINEA | C23052100366 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2023-05-21 | 4256 | keep | 0 | May | 2023 | 0.0028987 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2023-05-21 17:48 | 2023-05-21 17:49 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B2305210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-21 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-21 17:48 | 2023-05-21 17:49 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B2305210000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
VEGA BAJA | 2023-05-21 18:00 | 2023-05-21 18:34 | 6 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23052100103 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-05-21 | 204 | keep | 0 | May | 2023 | 0.00013894 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-21 18:18 | 2023-05-22 04:32 | 358 | 10:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 Y 1 X 65 EN C/L SE REMPLAZO CAJA | B23052100119 | New_Event | Cutout Failure | Include | Include | Equipment | 614 | 2023-05-21 | 219812 | keep | 0 | May | 2023 | 0.14971 | 0.00024383 | Sustained | FALSE | FALSE | Not_TMED_Event | 358
GUAYAMA | 2023-05-21 18:26 | 2023-05-22 14:30 | 15 | 20:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTE LLUVIA | P23052100205 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1204 | 2023-05-21 | 18060 | keep | 0 | May | 2023 | 0.012301 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-21 18:27 | 2023-05-21 23:58 | 123 | 5:31 | P | DESGANCHE | 1 X 65 EN C/L SE DESGANCHO | B23052100118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 331 | 2023-05-21 | 40713 | keep | 0 | May | 2023 | 0.027729 | 8.3775e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 123
MAYAGÃœEZ | 2023-05-21 18:35 | 2023-05-22 09:50 | 40 | 15:15 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052100094 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 915 | 2023-05-21 | 36600 | keep | 0 | May | 2023 | 0.024928 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-21 18:36 | 2023-05-21 18:39 | 220 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S23052100527 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-21 | 660 | keep | 0 | May | 2023 | 0.00044952 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-05-21 18:36 | 2023-05-21 18:39 | 870 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S23052100527 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-21 | 2610 | keep | 0 | May | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 1924 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 7696 | keep | 0 | May | 2023 | 0.0052417 | 0.0013104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1924
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 968 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 3872 | keep | 0 | May | 2023 | 0.0026372 | 0.0006593 | Momentary | FALSE | FALSE | Not_TMED_Event | 968
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 680 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 2720 | keep | 0 | May | 2023 | 0.0018526 | 0.00046314 | Momentary | FALSE | FALSE | Not_TMED_Event | 680
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 2246 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 8984 | keep | 0 | May | 2023 | 0.006119 | 0.0015297 | Momentary | FALSE | FALSE | Not_TMED_Event | 2246
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 1569 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 6276 | keep | 0 | May | 2023 | 0.0042746 | 0.0010686 | Momentary | FALSE | FALSE | Not_TMED_Event | 1569
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 2309 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 9236 | keep | 0 | May | 2023 | 0.0062906 | 0.0015726 | Momentary | FALSE | FALSE | Not_TMED_Event | 2309
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 2179 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 8716 | keep | 0 | May | 2023 | 0.0059364 | 0.0014841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2179
YAUCO | 2023-05-21 18:44 | 2023-05-21 18:48 | 2440 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 700 HABÃA MAL TIEMPO EN EL ÃREA. | P23052100160 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-21 | 9760 | keep | 0 | May | 2023 | 0.0066475 | 0.0016619 | Momentary | FALSE | FALSE | Not_TMED_Event | 2440
MAYAGÃœEZ | 2023-05-21 19:01 | 2023-05-22 09:50 | 30 | 14:49 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS REQUIERE DESGANCHE | M23052100099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 889 | 2023-05-21 | 26670 | keep | 0 | May | 2023 | 0.018165 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-21 19:07 | 2023-05-21 19:08 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23052100135 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-21 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-21 19:07 | 2023-05-21 19:08 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23052100135 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
CAGUAS | 2023-05-21 19:16 | 2023-05-21 19:17 | 918 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | C2305210000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-21 19:17 | 2023-05-21 20:35 | 163 | 1:18 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23052100385 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-05-21 | 12714 | keep | 0 | May | 2023 | 0.0086594 | 0.00011102 | Sustained | FALSE | FALSE | Not_TMED_Event | 163
ARECIBO | 2023-05-21 19:19 | 2023-05-21 20:05 | 100 | 0:46 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052100131 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 46 | 2023-05-21 | 4600 | keep | 0 | May | 2023 | 0.003133 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-05-21 19:20 | 2023-05-21 19:21 | 1615 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE FUERTE LLUVIA | P23052100170 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-21 | 1615 | keep | 0 | May | 2023 | 0.0011 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
AGUADILLA | 2023-05-21 19:20 | 2023-05-21 22:35 | 713 | 3:15 | T | LINEA DE TRANSMISION 38KV | SE ABRIO ALIMENTADOR REPARAR CONDICION CON LINEA 13700 | A23052100081 | Partial_restoration | 38 kV Transmission Line Source | Include | Include | Power supply | 195 | 2023-05-21 | 139035 | keep | 0 | May | 2023 | 0.094696 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-21 19:23 | 2023-05-22 11:47 | 125 | 16:24 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23052100546 | New_Event | Vegetation Contact | Include | Include | Vegetation | 984 | 2023-05-21 | 123000 | keep | 0 | May | 2023 | 0.083775 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
SAN JUAN | 2023-05-21 19:26 | 2023-05-21 19:29 | 936 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 20% DE SU CARGA POR 1424-08 LLEVA 15% DEL 1336-07 SE CERRO POR CONTROL | S23052100547 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-21 | 2808 | keep | 0 | May | 2023 | 0.0019125 | 0.00063751 | Momentary | FALSE | FALSE | Not_TMED_Event | 936
SAN JUAN | 2023-05-21 19:26 | 2023-05-21 19:29 | 4232 | 0:03 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1336-08 20% DE SU CARGA POR 1424-08 LLEVA 15% DEL 1336-07 SE CERRO POR CONTROL | S23052100547 | New_Event | Primary Wire Break | Include | Include | Equipment | 3 | 2023-05-21 | 12696 | keep | 0 | May | 2023 | 0.0086472 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
SAN JUAN | 2023-05-21 19:29 | 2023-05-21 21:37 | 1763 | 2:08 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO | S23052100547 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 128 | 2023-05-21 | 225664 | keep | 0 | May | 2023 | 0.1537 | 0.0012008 | Sustained | FALSE | FALSE | Not_TMED_Event | 1763
HUMACAO | 2023-05-21 19:34 | 2023-05-22 07:59 | 94 | 12:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 30 EN C/L MAL TIEMPO LLUVIAS | C23052100389 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 745 | 2023-05-21 | 70030 | keep | 0 | May | 2023 | 0.047697 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
UTUADO | 2023-05-21 19:34 | 2023-05-21 19:36 | 3502 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 HABÃA MAL TIEMPO EN EL ÃREA. TENIA DESGANCHE PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. | A23052100151 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 7004 | keep | 0 | May | 2023 | 0.0047704 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
UTUADO | 2023-05-21 19:34 | 2023-05-21 19:36 | 1241 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 HABÃA MAL TIEMPO EN EL ÃREA. TENIA DESGANCHE PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. | A23052100151 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 2482 | keep | 0 | May | 2023 | 0.0016905 | 0.00084524 | Momentary | FALSE | FALSE | Not_TMED_Event | 1241
UTUADO | 2023-05-21 19:34 | 2023-05-21 19:36 | 650 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 4700 HABÃA MAL TIEMPO EN EL ÃREA. TENIA DESGANCHE PENDIENTE DE REALIZAR SEGÃšN PATRULLAJE DEL 5/15/2023. | A23052100151 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 1300 | keep | 0 | May | 2023 | 0.00088542 | 0.00044271 | Momentary | FALSE | FALSE | Not_TMED_Event | 650
BAYAMON | 2023-05-21 19:36 | 2023-05-21 19:37 | 1859 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23052100145 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 1859 | keep | 0 | May | 2023 | 0.0012662 | 0.0012662 | Momentary | FALSE | FALSE | Not_TMED_Event | 1859
CANOVANAS | 2023-05-21 19:38 | 2023-05-22 09:46 | 26 | 14:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN PROVISIONAL MAL TIEMPO LLUVIAS | R23052100072 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 848 | 2023-05-21 | 22048 | keep | 0 | May | 2023 | 0.015017 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CANOVANAS | 2023-05-21 19:47 | 2023-05-21 19:48 | 4085 | 0:01 | T | DESGANCHE | RECERRO INTERRUPTOR EN SERVICIO | R23052100074 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-21 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
CANOVANAS | 2023-05-21 19:48 | 2023-05-21 23:22 | 62 | 3:34 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | R23052100075 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-05-21 | 13268 | keep | 0 | May | 2023 | 0.0090368 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
UTUADO | 2023-05-21 19:51 | 2023-05-21 22:55 | 150 | 3:04 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23052100159 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 184 | 2023-05-21 | 27600 | keep | 0 | May | 2023 | 0.018798 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-05-21 20:00 | 2023-05-22 01:18 | 669 | 5:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R23052100076 | New_Event | Cutout Failure | Include | Include | Equipment | 318 | 2023-05-21 | 212742 | keep | 0 | May | 2023 | 0.1449 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
PONCE | 2023-05-21 20:03 | 2023-05-22 11:35 | 20 | 15:32 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA FUERTE LLUVIA | P23052100180 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 932 | 2023-05-21 | 18640 | keep | 0 | May | 2023 | 0.012696 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-21 20:14 | 2023-05-22 02:20 | 120 | 6:06 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | B23052100166 | New_Event | Primary Wire Break | Include | Include | Equipment | 366 | 2023-05-21 | 43920 | keep | 0 | May | 2023 | 0.029914 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
ARECIBO | 2023-05-21 20:22 | 2023-05-22 08:47 | 17 | 12:25 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052100180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 745 | 2023-05-21 | 12665 | keep | 0 | May | 2023 | 0.0086261 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-05-21 20:32 | 2023-05-21 20:33 | 2435 | 0:01 | T | OTRAS CAUSAS | BY-220503-03 AL CERRAR N/O ENTRE 1909-08 Y 1907-05 ALIMENTADORES DISPARARON NO DIERON FASEO LLEVA EL 1909-08 | B2305210000X | New_Event | Other Causes | Include | Include | Other | 1 | 2023-05-21 | 2435 | keep | 0 | May | 2023 | 0.0016585 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-21 20:32 | 2023-05-21 20:33 | 2956 | 0:01 | T | ALIMENTADOR AMARRADO | BY-220503-03 AL CERRAR N/O ENTRE 1909-08 Y 1907-05 ALIMENTADORES DISPARARON NO DIERON FASEO CARGA X 1907-05 | B2305210000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-21 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
AGUADILLA | 2023-05-21 20:37 | 2023-05-22 00:30 | 200 | 3:53 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE REPARO NEUTRAL | A23052100147 | New_Event | Primary Wire Break | Include | Include | Equipment | 233 | 2023-05-21 | 46600 | keep | 0 | May | 2023 | 0.031739 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-05-21 20:37 | 2023-05-21 23:26 | 150 | 2:49 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052100189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 169 | 2023-05-21 | 25350 | keep | 0 | May | 2023 | 0.017266 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-21 21:15 | 2023-05-22 12:30 | 15 | 15:15 | P | DESGANCHE | 2X65 EN C/L DESGANCHE | S23052100686 | New_Event | Vegetation Contact | Include | Include | Vegetation | 915 | 2023-05-21 | 13725 | keep | 0 | May | 2023 | 0.009348 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-21 21:20 | 2023-05-21 21:23 | 2435 | 0:03 | T | OTRAS CAUSAS | BY-220503-03 SE DISPARO EL BKR 1907-05 PARA TRANSFERIR LAS CARGAS AL 1909-08 LLEVA 1909-08 | B2305210000X | 1st_after_momentary | Other Causes | Include | Include | Other | 3 | 2023-05-21 | 7305 | keep | 0 | May | 2023 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-21 21:20 | 2023-05-21 21:23 | 2956 | 0:03 | T | ALIMENTADOR AMARRADO | BY-220503-03 SE DISPARO EL BKR 1907-05 PARA TRANSFERIR LAS CARGA AL 1909-08 CARGA X 1907-05 | B2305210000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-21 | 8868 | keep | 0 | May | 2023 | 0.00604 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-05-21 21:21 | 2023-05-21 21:22 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23052100135 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-21 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-21 21:21 | 2023-05-21 21:22 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-10 LLEVA LA CARGA DEL 9206-07 | B23052100135 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-21 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
SAN JUAN | 2023-05-21 21:37 | 2023-05-21 22:35 | 936 | 0:58 | P | ALIMENTADOR AMARRADO | CON GOI SJ-230521-03 SE CERRO PUENTE ABIERTO EN TRONCAL 15% DEL 1336-07 TRANSFERIDO AL 1336-08 | S23052100547 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 58 | 2023-05-21 | 54288 | keep | 0 | May | 2023 | 0.036975 | 0.00063751 | Sustained | FALSE | FALSE | Not_TMED_Event | 936
SAN JUAN | 2023-05-21 21:37 | 2023-05-21 21:52 | 4232 | 0:15 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA CERRAR PUENTE PRIMARIO EN TRONCAL DE ALIMENTADOR CERCA SUBESTACION LLEVA 80% DE SU CARGA, LLEVA 15% DE LA CARGA DEL 1336-07 - EN SERVICIO 5% DEL 80% DE SU CARGA QUE AUN LLEVA, (211 CTES.) | S23052100547 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 15 | 2023-05-21 | 63480 | keep | 0 | May | 2023 | 0.043236 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-21 21:39 | 2023-05-22 12:30 | 19 | 14:51 | P | MAL TIEMPO/RAYOS | 1 X 25 EN TRANSFORMADOR DESCARGA ELECTRICA | P23052100189 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 891 | 2023-05-21 | 16929 | keep | 0 | May | 2023 | 0.01153 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
CANOVANAS | 2023-05-21 21:46 | 2023-05-22 02:32 | 218 | 4:46 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REEMPLAZO CAJA PRIMARIA | R23052100138 | New_Event | Cutout Failure | Include | Include | Equipment | 286 | 2023-05-21 | 62348 | keep | 0 | May | 2023 | 0.042465 | 0.00014848 | Sustained | FALSE | FALSE | Not_TMED_Event | 218
SAN JUAN | 2023-05-21 21:52 | 2023-05-21 22:35 | 4021 | 0:43 | P | CONDUCTOR ROTO O ABIERTO | CON GOI SJ-230521-03 SE CERRO PUENTE ABIERTO EN TRONCAL | S23052100547 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 43 | 2023-05-21 | 172903 | keep | 0 | May | 2023 | 0.11776 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-21 21:55 | 2023-05-21 21:57 | 1717 | 0:02 | S | LINEA DE TRANSMISION 38KV | LLUVIA INTENSA CON DESCARGAS ELECTRICAS PUENTE ABIERTO ENTRE 0335A - 0381B | P23052100194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 3434 | keep | 0 | May | 2023 | 0.0023389 | 0.0011694 | Momentary | FALSE | FALSE | Not_TMED_Event | 1717
PONCE | 2023-05-21 21:55 | 2023-05-21 21:57 | 974 | 0:02 | S | LINEA DE TRANSMISION 38KV | LLUVIA INTENSA CON DESCARGAS ELECTRICAS PUENTE ABIERTO ENTRE 0335A - 0381B | P23052100194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 1948 | keep | 0 | May | 2023 | 0.0013268 | 0.00066339 | Momentary | FALSE | FALSE | Not_TMED_Event | 974
PONCE | 2023-05-21 21:55 | 2023-05-21 21:57 | 1905 | 0:02 | S | LINEA DE TRANSMISION 38KV | LLUVIA INTENSA CON DESCARGAS ELECTRICAS PUENTE ABIERTO ENTRE 0335A - 0381B | P23052100194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 3810 | keep | 0 | May | 2023 | 0.002595 | 0.0012975 | Momentary | FALSE | FALSE | Not_TMED_Event | 1905
PONCE | 2023-05-21 21:55 | 2023-05-21 21:57 | 1262 | 0:02 | S | LINEA DE TRANSMISION 38KV | LLUVIA INTENSA CON DESCARGAS ELECTRICAS PUENTE ABIERTO ENTRE 0335A - 0381B | P23052100194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 2524 | keep | 0 | May | 2023 | 0.0017191 | 0.00085954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1262
PONCE | 2023-05-21 21:55 | 2023-05-21 21:57 | 200 | 0:02 | S | LINEA DE TRANSMISION 38KV | LLUVIA INTENSA CON DESCARGAS ELECTRICAS PUENTE ABIERTO ENTRE 0335A - 0381B | P23052100194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 400 | keep | 0 | May | 2023 | 0.00027244 | 0.00013622 | Momentary | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-05-21 21:55 | 2023-05-21 21:57 | 222 | 0:02 | S | LINEA DE TRANSMISION 38KV | INTENSA LLUVIA CON DESCARGAS ELECTRICAS PUENTE ABIERTO ENTRE 0335A - 0381B | P23052100194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 444 | keep | 0 | May | 2023 | 0.00030241 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
PONCE | 2023-05-21 21:55 | 2023-05-21 21:57 | 537 | 0:02 | S | LINEA DE TRANSMISION 38KV | INTENSA LLUVIA CON DESCARGAS ELECTRICAS PUENTE ABIERTO ENTRE 0335A - 0381B | P23052100194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-21 | 1074 | keep | 0 | May | 2023 | 0.0007315 | 0.00036575 | Momentary | FALSE | FALSE | Not_TMED_Event | 537
HUMACAO | 2023-05-21 22:11 | 2023-05-22 02:01 | 120 | 3:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 100 Y 1X 80 Y 2 X 65 EN CORTES DE LINEA | C23052100407 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2023-05-21 | 27600 | keep | 0 | May | 2023 | 0.018798 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
PONCE | 2023-05-21 22:16 | 2023-05-21 22:17 | 113 | 0:01 | T | MAL TIEMPO/RAYOS | LLUVIA INTENSA CON DESCARGAS ELECTRICAS | P23052100196 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-05-21 | 113 | keep | 0 | May | 2023 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
SAN JUAN | 2023-05-21 22:35 | 2023-05-21 22:37 | 936 | 0:02 | P | ALIMENTADOR AMARRADO | CON GOI SJ-230521-03 SE ABRIO PARA CERRAR MACHETE SE CERRO PUENTE ABIERTO EN TRONCAL 15% TRANSFERIDO AL 1336-08 | S23052100547 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-21 | 1872 | keep | 0 | May | 2023 | 0.001275 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-21 22:35 | 2023-05-21 22:37 | 4232 | 0:02 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR. PARA CERRAR MACHETE A PETICION JUAN C. RAMOS | S23052100547 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-21 | 8464 | keep | 0 | May | 2023 | 0.0057648 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-21 22:35 | 2023-05-22 13:28 | 10 | 14:53 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE PRIMARIO A CAJA | A23052100229 | New_Event | Primary Wire Break | Include | Include | Equipment | 893 | 2023-05-21 | 8930 | keep | 0 | May | 2023 | 0.0060822 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-05-21 22:46 | 2023-05-21 22:47 | 113 | 0:01 | T | MAL TIEMPO/RAYOS | INTENSA LLUVIA Y DESCARGAS ELECTRICAS | P23052100201 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-05-21 | 113 | keep | 0 | May | 2023 | 7.6964e-05 | 7.6964e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 113
GUAYAMA | 2023-05-21 23:06 | 2023-05-22 13:40 | 20 | 14:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 65 EN CORTE DE LINEA | P23052100204 | New_Event | Cutout Failure | Include | Include | Equipment | 874 | 2023-05-21 | 17480 | keep | 0 | May | 2023 | 0.011906 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-05-21 23:30 | 2023-05-22 03:27 | 3114 | 3:57 | T | MAL TIEMPO/LLUVIA O VIENTO | SE SACO ARBOL SOBRE LINEA SE ABRIO FID 1000419291 PARA SECCIONALIZAR AVERIA Y SE CERRO INTERRUPTOR | P23052100210 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 237 | 2023-05-21 | 738018 | keep | 0 | May | 2023 | 0.50266 | 0.0021209 | Sustained | FALSE | FALSE | Not_TMED_Event | 3114
HUMACAO | 2023-05-21 23:53 | 2023-05-22 04:09 | 1089 | 4:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO. SE SECCIONALIZO LINEA | C23052100418 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 256 | 2023-05-21 | 278784 | keep | 0 | May | 2023 | 0.18988 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2023-05-21 23:53 | 2023-05-22 04:09 | 3896 | 4:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO. SE SECCIONALIZO LINEA | C23052100418 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 256 | 2023-05-21 | 997376 | keep | 0 | May | 2023 | 0.67931 | 0.0026535 | Sustained | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2023-05-21 23:53 | 2023-05-22 04:09 | 1467 | 4:16 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 DE JUNCOS A RIO BLANCO. SE SECCIONALIZO LINEA | C23052100418 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 256 | 2023-05-21 | 375552 | keep | 0 | May | 2023 | 0.25579 | 0.00099917 | Sustained | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2023-05-22 00:05 | 2023-05-22 00:06 | 327 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23052200001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 327 | keep | 0 | May | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
PONCE | 2023-05-22 00:06 | 2023-05-22 01:49 | 113 | 1:43 | T | MAL TIEMPO/RAYOS | LUEGO DE CESAR LAS LLUVIAS Y DESCARGAS SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23052200002 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 103 | 2023-05-22 | 11639 | keep | 0 | May | 2023 | 0.0079273 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
PONCE | 2023-05-22 00:14 | 2023-05-22 00:15 | 171 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE INTENSA LLUVIA Y DESCARGAS ELECTRICAS | P23052200003 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-05-22 | 171 | keep | 0 | May | 2023 | 0.00011647 | 0.00011647 | Momentary | FALSE | FALSE | Not_TMED_Event | 171
PONCE | 2023-05-22 00:14 | 2023-05-22 00:15 | 2446 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE INTENSA LLUVIA Y DESCARGAS ELECTRICAS | P23052200004 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-05-22 | 2446 | keep | 0 | May | 2023 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2023-05-22 00:30 | 2023-05-22 00:31 | 1746 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE INTENSA LLUVIA Y DESCARGAS ELECTRICAS | P23052200008 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-05-22 | 1746 | keep | 0 | May | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
PONCE | 2023-05-22 00:40 | 2023-05-22 00:41 | 1746 | 0:01 | T | MAL TIEMPO/RAYOS | RECIERRE INTENSA LLUVIA Y DESCARGAS ELECTRICAS | P23052200014 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-05-22 | 1746 | keep | 0 | May | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
HUMACAO | 2023-05-22 02:01 | 2023-05-22 02:02 | 1891 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE BK | C23052200009 | Additional_clients | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-22 | 1891 | keep | 0 | May | 2023 | 0.001288 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-22 02:02 | 2023-05-22 12:52 | 120 | 10:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA 1 X 100 Y 1X 80 Y 2 X 65 EN CORTES DE LINEA | C23052100407 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 650 | 2023-05-22 | 78000 | keep | 0 | May | 2023 | 0.053125 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
HUMACAO | 2023-05-22 02:21 | 2023-05-22 02:22 | 327 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | C23052200012 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 327 | keep | 0 | May | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
AGUADILLA | 2023-05-22 03:20 | 2023-05-22 05:30 | 200 | 2:10 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052200009 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 130 | 2023-05-22 | 26000 | keep | 0 | May | 2023 | 0.017708 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-05-22 03:24 | 2023-05-22 07:58 | 90 | 4:34 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23052200023 | New_Event | Vegetation Contact | Include | Include | Vegetation | 274 | 2023-05-22 | 24660 | keep | 0 | May | 2023 | 0.016796 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
PONCE | 2023-05-22 03:27 | 2023-05-22 06:09 | 2174 | 2:42 | P | MAL TIEMPO/LLUVIA O VIENTO | SE HIZO DESGANCHE Y SE REEMPLAZO AISLADOR ROTO | P23052200036 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 162 | 2023-05-22 | 352188 | keep | 0 | May | 2023 | 0.23987 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-22 03:32 | 2023-05-22 19:30 | 50 | 15:58 | P | ARBOL SOBRE LINEA | SE REEMPLAZO CRUCETA PARTIDA SE SACO ARBOL DE LINEA PRIMARIA 2 X 50 EN CORTE DE LINEA | P23052200037 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 958 | 2023-05-22 | 47900 | keep | 0 | May | 2023 | 0.032624 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-22 03:32 | 2023-05-22 12:15 | 50 | 8:43 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052200011 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 523 | 2023-05-22 | 26150 | keep | 0 | May | 2023 | 0.017811 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-22 03:36 | 2023-05-22 12:45 | 9 | 9:09 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23052200025 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 549 | 2023-05-22 | 4941 | keep | 0 | May | 2023 | 0.0033653 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-05-22 04:05 | 2023-05-22 05:53 | 1310 | 1:48 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO ALIMENTADOR POR PUENTE ABIERTO Y ENTRO 60% EN SERVICIO BY-230522-01 | B23052200007 | New_Event | Primary Wire Break | Include | Include | Equipment | 108 | 2023-05-22 | 141480 | keep | 0 | May | 2023 | 0.096361 | 0.00089224 | Sustained | FALSE | FALSE | Not_TMED_Event | 1310
FAJARDO | 2023-05-22 04:33 | 2023-05-22 09:45 | 30 | 5:12 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23052200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-05-22 | 9360 | keep | 0 | May | 2023 | 0.0063751 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-05-22 04:42 | 2023-05-22 10:16 | 5 | 5:34 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23052200031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 334 | 2023-05-22 | 1670 | keep | 0 | May | 2023 | 0.0011374 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-22 04:43 | 2023-05-22 09:34 | 187 | 4:51 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23052200009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2023-05-22 | 54417 | keep | 0 | May | 2023 | 0.037063 | 0.00012736 | Sustained | FALSE | FALSE | Not_TMED_Event | 187
HUMACAO | 2023-05-22 04:55 | 2023-05-22 12:17 | 11 | 7:22 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYO | C23052200033 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 442 | 2023-05-22 | 4862 | keep | 0 | May | 2023 | 0.0033115 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
FAJARDO | 2023-05-22 05:38 | 2023-05-22 05:39 | 1394 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | R23052200011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 1394 | keep | 0 | May | 2023 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
HUMACAO | 2023-05-22 05:40 | 2023-05-22 16:18 | 97 | 10:38 | P | CONDUCTOR ROTO O ABIERTO | 3 X 80 EN C/L Y 1 X 10 EN XMR SE LEVANTO CONDUCTOR PRIMARIO | C23052200036 | New_Event | Primary Wire Break | Include | Include | Equipment | 638 | 2023-05-22 | 61886 | keep | 0 | May | 2023 | 0.04215 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
CAGUAS | 2023-05-22 05:40 | 2023-05-22 09:18 | 113 | 3:38 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23052200035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 218 | 2023-05-22 | 24634 | keep | 0 | May | 2023 | 0.016778 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
AGUADILLA | 2023-05-22 05:49 | 2023-05-22 09:15 | 80 | 3:26 | P | TRANSFORMADOR AVERIADO | 1 X 30 EN CORTE DE LINEA POR PM QUEMADO | A23052200016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 206 | 2023-05-22 | 16480 | keep | 0 | May | 2023 | 0.011224 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-05-22 05:53 | 2023-05-22 09:31 | 524 | 3:38 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE BKR PARA SECCIONALIZAR ALIMENTADOR POR PUENTE ABIERTO BY-230522-01 | B23052200007 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 218 | 2023-05-22 | 114232 | keep | 0 | May | 2023 | 0.077803 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-22 05:57 | 2023-05-22 10:00 | 122 | 4:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L LLUVIAS | C23052200038 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 243 | 2023-05-22 | 29646 | keep | 0 | May | 2023 | 0.020192 | 8.3094e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 122
BAYAMON | 2023-05-22 06:00 | 2023-05-22 16:58 | 152 | 10:58 | P | DESGANCHE | 1 X 65 EN C/L Y 2 X 50 EN C/L DESGANCHE | B23052200017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 658 | 2023-05-22 | 100016 | keep | 0 | May | 2023 | 0.06812 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
YAUCO | 2023-05-22 06:11 | 2023-05-22 08:24 | 194 | 2:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P23052200055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 133 | 2023-05-22 | 25802 | keep | 0 | May | 2023 | 0.017574 | 0.00013213 | Sustained | FALSE | FALSE | Not_TMED_Event | 194
PONCE | 2023-05-22 06:11 | 2023-05-22 14:05 | 149 | 7:54 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA EN EL PISO 1 X 50 EN CORTE DE LINEA | P23052200054 | New_Event | Primary Wire Break | Include | Include | Equipment | 474 | 2023-05-22 | 70626 | keep | 0 | May | 2023 | 0.048103 | 0.00010148 | Sustained | FALSE | FALSE | Not_TMED_Event | 149
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 06:36 | 386 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 100 CABLERIA DE CT'S AVERIADA POR RATONES BKR 0050 SUB 4006 GUAYAMA PDS | P23052200079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 386 | keep | 0 | May | 2023 | 0.0002629 | 0.0002629 | Momentary | FALSE | FALSE | Not_TMED_Event | 386
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 06:36 | 610 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 100 CABLERIA DE CT'S AVERIADA POR RATONES BKR 0050 SUB 4006 GUAYAMA PDS | P23052200079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 610 | keep | 0 | May | 2023 | 0.00041547 | 0.00041547 | Momentary | FALSE | FALSE | Not_TMED_Event | 610
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 06:36 | 1785 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 100 CABLERIA DE CT'S AVERIADA POR RATONES BKR 0050 SUB 4006 GUAYAMA PDS | P23052200079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 1785 | keep | 0 | May | 2023 | 0.0012158 | 0.0012158 | Momentary | FALSE | FALSE | Not_TMED_Event | 1785
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 06:36 | 1233 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 100 CABLERIA DE CT'S AVERIADA POR RATONES BKR 0050 SUB 4006 GUAYAMA PDS | P23052200079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 1233 | keep | 0 | May | 2023 | 0.00083979 | 0.00083979 | Momentary | FALSE | FALSE | Not_TMED_Event | 1233
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 06:36 | 584 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 100 CABLERIA DE CT'S AVERIADA POR RATONES BKR 0050 SUB 4006 GUAYAMA PDS | P23052200079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 584 | keep | 0 | May | 2023 | 0.00039776 | 0.00039776 | Momentary | FALSE | FALSE | Not_TMED_Event | 584
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 06:36 | 1658 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 100 CABLERIA DE CT'S AVERIADA POR RATONES BKR 0050 SUB 4006 GUAYAMA PDS | P23052200079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 1658 | keep | 0 | May | 2023 | 0.0011293 | 0.0011293 | Momentary | FALSE | FALSE | Not_TMED_Event | 1658
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 06:36 | 630 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 100 CABLERIA DE CT'S AVERIADA POR RATONES BKR 0050 SUB 4006 GUAYAMA PDS | P23052200079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 630 | keep | 0 | May | 2023 | 0.00042909 | 0.00042909 | Momentary | FALSE | FALSE | Not_TMED_Event | 630
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 10:07 | 1173 | 3:32 | S | LINEA DE TRANSMISION 38KV | BREAKER 0050 AVERIADO SE TRANSFIERE CARGA A 4003-00 CABLERIA DE CT'S AVERIADA POR RATONES | P23052200081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2023-05-22 | 248676 | keep | 0 | May | 2023 | 0.16937 | 0.00079892 | Sustained | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 10:07 | 215 | 3:32 | S | LINEA DE TRANSMISION 38KV | BREAKER 0050 AVERIADO SE TRANSFIERE CARGA A 4003-00 CABLERIA DE CT'S AVERIADA POR RATONES | P23052200081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 212 | 2023-05-22 | 45580 | keep | 0 | May | 2023 | 0.031044 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2023-05-22 06:35 | 2023-05-22 09:45 | 464 | 3:10 | S | LINEA DE TRANSMISION 38KV | BREAKER 0050 AVERIADO SE TRANSFIERE CARGA A 4003-02 CABLERIA DE CT'S AVERIADA POR RATONES | P23052200081 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 190 | 2023-05-22 | 88160 | keep | 0 | May | 2023 | 0.060045 | 0.00031603 | Sustained | FALSE | FALSE | Not_TMED_Event | 464
PONCE | 2023-05-22 06:41 | 2023-05-22 06:42 | 485 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052200067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 485 | keep | 0 | May | 2023 | 0.00033033 | 0.00033033 | Momentary | FALSE | FALSE | Not_TMED_Event | 485
MAYAGÃœEZ | 2023-05-22 06:49 | 2023-05-22 12:15 | 30 | 5:26 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23052200029 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 326 | 2023-05-22 | 9780 | keep | 0 | May | 2023 | 0.0066611 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-22 06:51 | 2023-05-22 11:17 | 1078 | 4:26 | T | MAL TIEMPO/LLUVIA O VIENTO | ALIMENTADOR FUERA DE SERVICIO FUERTE LLUVIA | P23052200076 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 266 | 2023-05-22 | 286748 | keep | 0 | May | 2023 | 0.1953 | 0.00073422 | Sustained | FALSE | FALSE | Not_TMED_Event | 1078
AGUADILLA | 2023-05-22 06:51 | 2023-05-22 10:27 | 1 | 3:36 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA POR RAYO | A23052200030 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 216 | 2023-05-22 | 216 | keep | 0 | May | 2023 | 0.00014712 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-22 07:30 | 2023-05-22 07:31 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | R23052200016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 2722 | keep | 0 | May | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
CAGUAS | 2023-05-22 07:30 | 2023-05-23 07:31 | 16 | 24:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADO MAL TIEMPO LLUVIA | C23052200319 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1441 | 2023-05-22 | 23056 | keep | 0 | May | 2023 | 0.015703 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
PONCE | 2023-05-22 07:31 | 2023-05-22 21:14 | 67 | 13:43 | P | DESGANCHE | 1 X 50 EN CORTRE DE LINEA SE RETIRO RAMA DE LINEA | P23052200098 | New_Event | Vegetation Contact | Include | Include | Vegetation | 823 | 2023-05-22 | 55141 | keep | 0 | May | 2023 | 0.037556 | 4.5633e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 67
SAN JUAN | 2023-05-22 07:43 | 2023-05-22 09:00 | 6 | 1:17 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23052200026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-05-22 | 462 | keep | 0 | May | 2023 | 0.00031467 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
UTUADO | 2023-05-22 07:52 | 2023-05-22 12:05 | 30 | 4:13 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052200043 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 253 | 2023-05-22 | 7590 | keep | 0 | May | 2023 | 0.0051695 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-22 07:53 | 2023-05-22 14:39 | 1 | 6:46 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23052200027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 406 | 2023-05-22 | 406 | keep | 0 | May | 2023 | 0.00027652 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-22 07:54 | 2023-05-22 09:40 | 10 | 1:46 | P | DESGANCHE | 1 X 20AMP EN CORTE DE LINEA | P23052200110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-22 | 1060 | keep | 0 | May | 2023 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-22 08:13 | 2023-05-22 11:14 | 100 | 3:01 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23052200047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-05-22 | 18100 | keep | 0 | May | 2023 | 0.012328 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-05-22 08:16 | 2023-05-22 17:40 | 113 | 9:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZARON DOS CAJAS PRIMARIAS DE 100AMP EN CORTE DE LINEA | P23052200133 | New_Event | Cutout Failure | Include | Include | Equipment | 564 | 2023-05-22 | 63732 | keep | 0 | May | 2023 | 0.043408 | 7.6964e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 113
BAYAMON | 2023-05-22 08:25 | 2023-05-22 10:41 | 20 | 2:16 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052200060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-05-22 | 2720 | keep | 0 | May | 2023 | 0.0018526 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-05-22 08:26 | 2023-05-22 19:20 | 35 | 10:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTE LLUVIA | P23052200144 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 654 | 2023-05-22 | 22890 | keep | 0 | May | 2023 | 0.01559 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-05-22 08:27 | 2023-05-22 17:30 | 2 | 9:03 | P | DESGANCHE | SE ABRIO EN C/L PARA REALIZAR DESGANCHE PRIMARIO MASIVO NO FUNDIO | S23052200034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 543 | 2023-05-22 | 1086 | keep | 0 | May | 2023 | 0.00073967 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-05-22 08:29 | 2023-05-22 11:09 | 2 | 2:40 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR POR RAYOS | M23052200048 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 160 | 2023-05-22 | 320 | keep | 0 | May | 2023 | 0.00021795 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-05-22 08:44 | 2023-05-22 15:50 | 36 | 7:06 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN TRANSFORMADOR FUETE LLUVIA | P23052200156 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 426 | 2023-05-22 | 15336 | keep | 0 | May | 2023 | 0.010445 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
FAJARDO | 2023-05-22 08:50 | 2023-05-22 09:11 | 2 | 0:21 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23052200021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 21 | 2023-05-22 | 42 | keep | 0 | May | 2023 | 2.8606e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-05-22 08:51 | 2023-05-22 12:34 | 10 | 3:43 | P | MAL TIEMPO/RAYOS | 1 X 5 EN TRANSFORMADOR Y 1 X 15 EN CORTE DE LINEA POR RAYOS | A23052200060 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 223 | 2023-05-22 | 2230 | keep | 0 | May | 2023 | 0.0015188 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-05-22 09:06 | 2023-05-22 13:12 | 5 | 4:06 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P23052200164 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 246 | 2023-05-22 | 1230 | keep | 0 | May | 2023 | 0.00083775 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-05-22 09:08 | 2023-05-22 10:32 | 5 | 1:24 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZA BAJANTE PRIMARIO Y SE CIERRA CORTE DE LINEA | A23052200068 | New_Event | Primary Wire Break | Include | Include | Equipment | 84 | 2023-05-22 | 420 | keep | 0 | May | 2023 | 0.00028606 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-05-22 09:15 | 2023-05-22 14:56 | 11 | 5:41 | P | NO SE REPORTO CAUSA | 2 X 25 EN RISER Y 2 X 30 EN C/L | C23052200111 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 341 | 2023-05-22 | 3751 | keep | 0 | May | 2023 | 0.0025548 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-05-22 09:26 | 2023-05-22 19:00 | 85 | 9:34 | P | CABLE SOTERRADO AVERIADO | 1 X 50 EN RISER SE ENCONTRO AVERIA NUEVA T-11 @ T-10 Y AVERIA VIEJA DE T-9 @ T10 | B23052200094 | New_Event | UG Cable Fault | Include | Include | Equipment | 574 | 2023-05-22 | 48790 | keep | 0 | May | 2023 | 0.033231 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
AGUADILLA | 2023-05-22 09:27 | 2023-05-22 16:30 | 7 | 7:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 75 KVA | A23052200076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 423 | 2023-05-22 | 2961 | keep | 0 | May | 2023 | 0.0020167 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-05-22 09:31 | 2023-05-22 11:03 | 1310 | 1:32 | T | CONDUCTOR ROTO O ABIERTO | SE ABRE BKR PARA SECCIONALIZAR ALIMENTADOR POR PUENTE ABIERTO ENTRO 80% EN SERVICIO BY-230522-01 | B23052200007 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 92 | 2023-05-22 | 120520 | keep | 0 | May | 2023 | 0.082086 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-05-22 09:32 | 2023-05-22 10:35 | 45 | 1:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P23052200181 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 63 | 2023-05-22 | 2835 | keep | 0 | May | 2023 | 0.0019309 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
VEGA BAJA | 2023-05-22 09:40 | 2023-05-22 11:55 | 75 | 2:15 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23052200079 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-05-22 | 10125 | keep | 0 | May | 2023 | 0.0068961 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
MAYAGÃœEZ | 2023-05-22 10:15 | 2023-05-22 15:34 | 1 | 5:19 | P | MAL TIEMPO/RAYOS | 1 X 30 EN RISER DESCARGA ELECTRICA | M23052200073 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 319 | 2023-05-22 | 319 | keep | 0 | May | 2023 | 0.00021727 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-22 10:16 | 2023-05-22 14:21 | 101 | 4:05 | P | NO SE REPORTO CAUSA | 1X50 DE SU-3 @ RISER | S23052200066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 245 | 2023-05-22 | 24745 | keep | 0 | May | 2023 | 0.016854 | 6.8791e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 101
HUMACAO | 2023-05-22 10:21 | 2023-05-22 10:39 | 1 | 0:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO | C23052200149 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 18 | 2023-05-22 | 18 | keep | 0 | May | 2023 | 1.226e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-22 10:27 | 2023-05-22 17:03 | 180 | 6:36 | P | ANIMAL | 1 X 15 Y 1 X 25 EN C/L CRUCE X AVE | B23052200130 | New_Event | Animals | Include | Include | Wildlife | 396 | 2023-05-22 | 71280 | keep | 0 | May | 2023 | 0.048548 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
VEGA BAJA | 2023-05-22 10:28 | 2023-05-22 18:42 | 1 | 8:14 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 494 | 2023-05-22 | 494 | keep | 0 | May | 2023 | 0.00033646 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-22 10:31 | 2023-05-22 10:34 | 3157 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23052200098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-22 | 9471 | keep | 0 | May | 2023 | 0.0064507 | 0.0021502 | Momentary | FALSE | FALSE | Not_TMED_Event | 3157
VEGA BAJA | 2023-05-22 10:31 | 2023-05-22 10:34 | 35 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23052200098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-22 | 105 | keep | 0 | May | 2023 | 7.1515e-05 | 2.3838e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 35
VEGA BAJA | 2023-05-22 10:31 | 2023-05-22 10:34 | 2916 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 11400 | A23052200098 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-22 | 8748 | keep | 0 | May | 2023 | 0.0059582 | 0.0019861 | Momentary | FALSE | FALSE | Not_TMED_Event | 2916
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:46 | 959 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-05-22 | 4795 | keep | 0 | May | 2023 | 0.0032659 | 0.00065317 | Momentary | FALSE | FALSE | Not_TMED_Event | 959
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:46 | 1382 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-05-22 | 6910 | keep | 0 | May | 2023 | 0.0047064 | 0.00094127 | Momentary | FALSE | FALSE | Not_TMED_Event | 1382
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:46 | 663 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200157 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-05-22 | 3315 | keep | 0 | May | 2023 | 0.0022578 | 0.00045157 | Momentary | FALSE | FALSE | Not_TMED_Event | 663
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:45 | 1715 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-22 | 6860 | keep | 0 | May | 2023 | 0.0046723 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:45 | 1498 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-22 | 5992 | keep | 0 | May | 2023 | 0.0040811 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:45 | 1221 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-22 | 4884 | keep | 0 | May | 2023 | 0.0033265 | 0.00083162 | Momentary | FALSE | FALSE | Not_TMED_Event | 1221
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:45 | 1100 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200153 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-22 | 4400 | keep | 0 | May | 2023 | 0.0029968 | 0.0007492 | Momentary | FALSE | FALSE | Not_TMED_Event | 1100
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:45 | 1514 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-22 | 6056 | keep | 0 | May | 2023 | 0.0041247 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:45 | 1105 | 0:04 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200158 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 4 | 2023-05-22 | 4420 | keep | 0 | May | 2023 | 0.0030104 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
AGUADILLA | 2023-05-22 10:41 | 2023-05-22 12:00 | 150 | 1:19 | P | CAUSAS EXTERNAS | 1 X 80 EN CORTE DE LINEA CAMION CRUZO LINEAS | M23052200081 | New_Event | Damage From Public | Include | Include | Public | 79 | 2023-05-22 | 11850 | keep | 0 | May | 2023 | 0.008071 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:46 | 4176 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-05-22 | 20880 | keep | 0 | May | 2023 | 0.014221 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:46 | 252 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-05-22 | 1260 | keep | 0 | May | 2023 | 0.00085818 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:46 | 2147 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200148 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-05-22 | 10735 | keep | 0 | May | 2023 | 0.0073116 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-05-22 10:41 | 2023-05-22 10:46 | 2858 | 0:05 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 10000 | B23052200149 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 5 | 2023-05-22 | 14290 | keep | 0 | May | 2023 | 0.0097329 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
UTUADO | 2023-05-22 10:43 | 2023-05-22 14:33 | 7 | 3:50 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052200096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 230 | 2023-05-22 | 1610 | keep | 0 | May | 2023 | 0.0010966 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-05-22 10:44 | 2023-05-22 16:30 | 7 | 5:46 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRES TRANSFORMADORES DIFERENTES DESCARGAS ELECTRICAS | M23052200084 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 346 | 2023-05-22 | 2422 | keep | 0 | May | 2023 | 0.0016496 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-22 10:45 | 2023-05-22 13:05 | 20 | 2:20 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052200060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-05-22 | 2800 | keep | 0 | May | 2023 | 0.0019071 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-22 10:46 | 2023-05-22 11:00 | 5 | 0:14 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052200086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 14 | 2023-05-22 | 70 | keep | 0 | May | 2023 | 4.7677e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-22 10:55 | 2023-05-22 10:56 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23052200159 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 3511 | keep | 0 | May | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-05-22 10:57 | 2023-05-22 10:58 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23052200162 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 3511 | keep | 0 | May | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
MAYAGÃœEZ | 2023-05-22 11:01 | 2023-05-22 13:54 | 6 | 2:53 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | M23052200096 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 173 | 2023-05-22 | 1038 | keep | 0 | May | 2023 | 0.00070698 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-22 11:03 | 2023-05-22 11:27 | 262 | 0:24 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO ENTRO 20% EN SERVICIO BY-230522-01 | B23052200007 | New_Event | Primary Wire Break | Include | Include | Equipment | 24 | 2023-05-22 | 6288 | keep | 0 | May | 2023 | 0.0042827 | 0.00017845 | Sustained | FALSE | FALSE | Not_TMED_Event | 262
ARECIBO | 2023-05-22 11:07 | 2023-05-22 13:20 | 30 | 2:13 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23052200115 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2023-05-22 | 3990 | keep | 0 | May | 2023 | 0.0027176 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-05-22 11:10 | 2023-05-22 11:50 | 20 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE CONVERTIDOR PARA ABRIR PUENTES Y SECCIONALIZAR AVERIA DE NEUTRAL PARTIDO | A23052200114 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2023-05-22 | 800 | keep | 0 | May | 2023 | 0.00054488 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-22 11:14 | 2023-05-22 11:15 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S23052200078 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 2203 | keep | 0 | May | 2023 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
PONCE | 2023-05-22 11:17 | 2023-05-22 11:45 | 600 | 0:28 | P | DESGANCHE | SE ABREN MACHETES PARA SECCIONALIZAR AVERIA | P23052200076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 28 | 2023-05-22 | 16800 | keep | 0 | May | 2023 | 0.011442 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
PONCE | 2023-05-22 11:26 | 2023-05-22 12:11 | 55 | 0:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA FUERTE LLUVIA | P23052200228 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 45 | 2023-05-22 | 2475 | keep | 0 | May | 2023 | 0.0016857 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
PONCE | 2023-05-22 11:26 | 2023-05-22 14:26 | 250 | 3:00 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P23052200227 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 180 | 2023-05-22 | 45000 | keep | 0 | May | 2023 | 0.030649 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-05-22 11:33 | 2023-05-22 15:44 | 1 | 4:11 | P | DESGANCHE | 1X30 C/L 1X10 BANCO DE XMRS DESGANCHE | S23052200085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2023-05-22 | 251 | keep | 0 | May | 2023 | 0.00017095 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-22 11:39 | 2023-05-22 14:33 | 1 | 2:54 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | R23052200050 | New_Event | Vegetation Contact | Include | Include | Vegetation | 174 | 2023-05-22 | 174 | keep | 0 | May | 2023 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-22 11:41 | 2023-05-22 15:10 | 150 | 3:29 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P23052200242 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 209 | 2023-05-22 | 31350 | keep | 0 | May | 2023 | 0.021352 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
PONCE | 2023-05-22 11:45 | 2023-05-22 13:22 | 278 | 1:37 | P | DESGANCHE | SE HIZO DESGANCHE Y SE CIERRA CORTE DE LINEA | P23052200258 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-05-22 | 26966 | keep | 0 | May | 2023 | 0.018366 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-22 11:46 | 2023-05-22 14:04 | 24 | 2:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO VIENTO | R23052200052 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 138 | 2023-05-22 | 3312 | keep | 0 | May | 2023 | 0.0022558 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BAYAMON | 2023-05-22 11:48 | 2023-05-22 23:49 | 150 | 12:01 | P | DESGANCHE | 1 X 50 Y 1 X 65 EN C/L DESGANCHE | B23052200190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 721 | 2023-05-22 | 108150 | keep | 0 | May | 2023 | 0.07366 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-22 11:49 | 2023-05-23 10:50 | 1 | 23:01 | P | DESGANCHE | 2 X 25 EN C/L DESGANCHE | S23052200090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1381 | 2023-05-22 | 1381 | keep | 0 | May | 2023 | 0.00094059 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-22 11:49 | 2023-05-22 12:14 | 10 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZO BARRA EN PEDESTAL | R23052200053 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-22 | 250 | keep | 0 | May | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-22 11:49 | 2023-05-23 01:50 | 330 | 14:01 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO | B23052200191 | New_Event | Primary Wire Break | Include | Include | Equipment | 841 | 2023-05-22 | 277530 | keep | 0 | May | 2023 | 0.18902 | 0.00022476 | Sustained | FALSE | FALSE | Not_TMED_Event | 330
UTUADO | 2023-05-22 11:50 | 2023-05-22 18:00 | 7 | 6:10 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA NEUTRAL ROTA HAY PUENTES ABIERTOS | A23052200123 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 370 | 2023-05-22 | 2590 | keep | 0 | May | 2023 | 0.001764 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-22 11:51 | 2023-05-23 12:10 | 10 | 24:19 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR DESGANCHE | P23052200252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1459 | 2023-05-22 | 14590 | keep | 0 | May | 2023 | 0.0099372 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-05-22 11:53 | 2023-05-22 13:44 | 50 | 1:51 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | A23052200141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-05-22 | 5550 | keep | 0 | May | 2023 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-05-22 11:54 | 2023-05-22 17:20 | 15 | 5:26 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | REEMPLAZO DE POSTE CON PROVICIONAL AEREO | P23052200253 | New_Event | Primary Pole Failure | Include | Include | Equipment | 326 | 2023-05-22 | 4890 | keep | 0 | May | 2023 | 0.0033306 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-22 12:00 | 2023-05-22 12:01 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23052200194 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 3511 | keep | 0 | May | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
PONCE | 2023-05-22 12:01 | 2023-05-23 13:49 | 80 | 25:48 | P | DESGANCHE | SE INSTALO TENSOR DESGANCHE Y SE LEVANTO ALAMBRE PRIMARIO | P23052200258 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1548 | 2023-05-22 | 123840 | keep | 0 | May | 2023 | 0.084347 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-22 12:05 | 2023-05-22 14:41 | 427 | 2:36 | T | DESGANCHE | SE ABRIO INTERRUPTOR A PETICION DEL PERSONAL DE CAMPO PARA REPARAR PUENTE PRIMARIO Y REALIZAR DESGANCHE PRIMARIO MASIVO TRASPATIO | S23052200092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-05-22 | 66612 | keep | 0 | May | 2023 | 0.045369 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
HUMACAO | 2023-05-22 12:14 | 2023-05-22 16:17 | 10 | 4:03 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYO | C23052200187 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 243 | 2023-05-22 | 2430 | keep | 0 | May | 2023 | 0.0016551 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-05-22 12:15 | 2023-05-22 15:00 | 12 | 2:45 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGA ELECTRICA | P23052200268 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 165 | 2023-05-22 | 1980 | keep | 0 | May | 2023 | 0.0013486 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-22 12:17 | 2023-05-22 13:19 | 10 | 1:02 | P | NO SE REPORTO CAUSA | 1X15 EN XMR | S23052200096 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 62 | 2023-05-22 | 620 | keep | 0 | May | 2023 | 0.00042228 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-22 12:25 | 2023-05-22 12:54 | 5 | 0:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO CONECTOR DE BAJANTE SECUNDARIO | S23052100542 | New_Event | Secondary Wire Break | Include | Include | Equipment | 29 | 2023-05-22 | 145 | keep | 0 | May | 2023 | 9.8759e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
HUMACAO | 2023-05-22 12:27 | 2023-05-22 20:48 | 191 | 8:21 | P | MAL TIEMPO/LLUVIA O VIENTO | MAL TIEMPO LLUVIAS 1 X 50 EN C/L | C23052200190 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 501 | 2023-05-22 | 95691 | keep | 0 | May | 2023 | 0.065175 | 0.00013009 | Sustained | FALSE | FALSE | Not_TMED_Event | 191
ARECIBO | 2023-05-22 12:40 | 2023-05-22 14:57 | 70 | 2:17 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23052200160 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 137 | 2023-05-22 | 9590 | keep | 0 | May | 2023 | 0.0065317 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CAGUAS | 2023-05-22 12:42 | 2023-05-22 13:25 | 6197 | 0:43 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR A PETICION VICTOR SANTIAGO POR CONDUCTOR EL SUELO CG-230522-01 SE SECCIONALIZO TRAMO PARA LEVANTAR CONDUCTOR | C23052200234 | New_Event | Primary Wire Break | Include | Include | Equipment | 43 | 2023-05-22 | 266471 | keep | 0 | May | 2023 | 0.18149 | 0.0042207 | Sustained | FALSE | FALSE | Not_TMED_Event | 6197
UTUADO | 2023-05-22 12:47 | 2023-05-22 19:20 | 7 | 6:33 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052200294 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 393 | 2023-05-22 | 2751 | keep | 0 | May | 2023 | 0.0018737 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-22 12:58 | 2023-05-22 13:01 | 1368 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CORROBORO PERSONAL FUERA Y SE CERRO POR CONTROL | S23052200106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-22 | 4104 | keep | 0 | May | 2023 | 0.0027952 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
FAJARDO | 2023-05-22 13:09 | 2023-05-22 16:28 | 64 | 3:19 | P | MAL TIEMPO/RAYOS | 2 X 40 C/L 1 X 15 EN XMR MAL TIEMPO RAYO | R23052200073 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 199 | 2023-05-22 | 12736 | keep | 0 | May | 2023 | 0.0086744 | 4.359e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 64
GUAYAMA | 2023-05-22 13:21 | 2023-05-22 15:42 | 20 | 2:21 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | SE REPARO LINEA SECUNDARIA 1 X 10 EN TRANSFORMADOR | P23052200053 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 141 | 2023-05-22 | 2820 | keep | 0 | May | 2023 | 0.0019207 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-22 13:22 | 2023-05-22 14:53 | 1 | 1:31 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO ABIERTO | R23052200079 | New_Event | Primary Wire Break | Include | Include | Equipment | 91 | 2023-05-22 | 91 | keep | 0 | May | 2023 | 6.198e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-22 13:23 | 2023-05-22 16:15 | 50 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGA ELECTRICA | P23052200315 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2023-05-22 | 8600 | keep | 0 | May | 2023 | 0.0058574 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-22 13:25 | 2023-05-22 19:00 | 21 | 5:35 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO CG-230522-01 | C23052200303 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 335 | 2023-05-22 | 7035 | keep | 0 | May | 2023 | 0.0047915 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-22 13:26 | 2023-05-23 16:31 | 1 | 27:05 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS UTILIZARON EVENTO A23052400094 | A23052200185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1625 | 2023-05-22 | 1625 | keep | 0 | May | 2023 | 0.0011068 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-22 13:33 | 2023-05-22 16:20 | 15 | 2:47 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052200129 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-05-22 | 2505 | keep | 0 | May | 2023 | 0.0017061 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-22 13:36 | 2023-05-22 13:37 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
HUMACAO | 2023-05-22 13:44 | 2023-05-22 13:47 | 3701 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 TIENE DESGANCHES PENDIENTES A REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 5/17/2023. | C23052200284 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-22 | 11103 | keep | 0 | May | 2023 | 0.0075622 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2023-05-22 13:44 | 2023-05-22 13:47 | 989 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 TIENE DESGANCHES PENDIENTES A REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 5/17/2023. | C23052200284 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-22 | 2967 | keep | 0 | May | 2023 | 0.0020208 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2023-05-22 13:44 | 2023-05-22 13:47 | 1467 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 TIENE DESGANCHES PENDIENTES A REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 5/17/2023. | C23052200284 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-22 | 4401 | keep | 0 | May | 2023 | 0.0029975 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
HUMACAO | 2023-05-22 13:58 | 2023-05-22 15:20 | 78 | 1:22 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23052200302 | New_Event | Vegetation Contact | Include | Include | Vegetation | 82 | 2023-05-22 | 6396 | keep | 0 | May | 2023 | 0.0043563 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
FAJARDO | 2023-05-22 14:05 | 2023-05-22 16:12 | 14 | 2:07 | P | DESGANCHE | 1 X 100 EN C/L Y DESGANCHE | R23052200088 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-05-22 | 1778 | keep | 0 | May | 2023 | 0.001211 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-05-22 14:09 | 2023-05-22 16:10 | 40 | 2:01 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052200140 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 121 | 2023-05-22 | 4840 | keep | 0 | May | 2023 | 0.0032965 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-22 14:12 | 2023-05-22 14:13 | 4009 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052200361 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 4009 | keep | 0 | May | 2023 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
PONCE | 2023-05-22 14:15 | 2023-05-22 18:50 | 45 | 4:35 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE SACO RAMA DE ARBOL DE LINEA PRIMARIA | P23052200347 | New_Event | Vegetation Contact | Include | Include | Vegetation | 275 | 2023-05-22 | 12375 | keep | 0 | May | 2023 | 0.0084286 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
HUMACAO | 2023-05-22 14:16 | 2023-05-22 14:17 | 1883 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 80% DE SU CARGA | C2305220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 1883 | keep | 0 | May | 2023 | 0.0012825 | 0.0012825 | Momentary | FALSE | FALSE | Not_TMED_Event | 1883
YAUCO | 2023-05-22 14:19 | 2023-05-23 10:22 | 10 | 20:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR MAL TIEMPO | P23052200350 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1203 | 2023-05-22 | 12030 | keep | 0 | May | 2023 | 0.0081936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-22 14:23 | 2023-05-23 09:45 | 14 | 19:22 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA PRIMARIA DE TRANSFORMADOR | C23052200317 | New_Event | Primary Wire Break | Include | Include | Equipment | 1162 | 2023-05-22 | 16268 | keep | 0 | May | 2023 | 0.01108 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-05-22 14:36 | 2023-05-22 16:25 | 12 | 1:49 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 40 EN C/L MAL TIEMPO LLUVIAS | C23052200300 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 109 | 2023-05-22 | 1308 | keep | 0 | May | 2023 | 0.00089087 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-22 14:41 | 2023-05-22 14:49 | 20 | 0:08 | P | DESGANCHE | SE CERRO PUENTE PRIMARIO Y SE REALIZO DESGANCHE PRIMARIO MASIVO - TRASPATIO - MEDIANTE G.O.I. SJ-230522-02 | S23052100456 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 8 | 2023-05-22 | 160 | keep | 0 | May | 2023 | 0.00010898 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-22 14:45 | 2023-05-22 18:55 | 90 | 4:10 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P23052200379 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 250 | 2023-05-22 | 22500 | keep | 0 | May | 2023 | 0.015325 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
YAUCO | 2023-05-22 14:45 | 2023-05-22 15:12 | 5 | 0:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA EN TRANSFORMADOR | P23052200312 | New_Event | Cutout Failure | Include | Include | Equipment | 27 | 2023-05-22 | 135 | keep | 0 | May | 2023 | 9.1948e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-05-22 14:47 | 2023-05-23 15:05 | 41 | 24:18 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DE SU-19 @ T-43A Y SE ENERGIZO | C23052200328 | New_Event | UG Cable Fault | Include | Include | Equipment | 1458 | 2023-05-22 | 59778 | keep | 0 | May | 2023 | 0.040715 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BARRANQUITAS | 2023-05-22 14:52 | 2023-05-22 18:09 | 20 | 3:17 | P | DESGANCHE | 1 X 15 Y 1 X 30 EN XMR DESGANCHE | C23052200331 | New_Event | Vegetation Contact | Include | Include | Vegetation | 197 | 2023-05-22 | 3940 | keep | 0 | May | 2023 | 0.0026835 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-05-22 14:52 | 2023-05-22 17:30 | 381 | 2:38 | P | MAL TIEMPO/RAYOS | 2 X 100 EN C/L MAL TIEMPO RAYO | C23052200337 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 158 | 2023-05-22 | 60198 | keep | 0 | May | 2023 | 0.041001 | 0.0002595 | Sustained | FALSE | FALSE | Not_TMED_Event | 381
BARRANQUITAS | 2023-05-22 14:53 | 2023-05-22 15:21 | 34 | 0:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | C23052100320 | New_Event | Secondary Wire Break | Include | Include | Equipment | 28 | 2023-05-22 | 952 | keep | 0 | May | 2023 | 0.0006484 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
BARRANQUITAS | 2023-05-22 14:57 | 2023-05-22 17:50 | 136 | 2:53 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | C23052200334 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 173 | 2023-05-22 | 23528 | keep | 0 | May | 2023 | 0.016025 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
HUMACAO | 2023-05-22 15:00 | 2023-05-22 17:00 | 75 | 2:00 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | C23052200335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 120 | 2023-05-22 | 9000 | keep | 0 | May | 2023 | 0.0061299 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-05-22 15:01 | 2023-05-22 16:22 | 100 | 1:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23052200216 | New_Event | Cutout Failure | Include | Include | Equipment | 81 | 2023-05-22 | 8100 | keep | 0 | May | 2023 | 0.0055169 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
FAJARDO | 2023-05-22 15:14 | 2023-05-22 15:30 | 1 | 0:16 | P | DESGANCHE | 1 X 40 C/L Y DESGANCHE | R23052200068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 16 | 2023-05-22 | 16 | keep | 0 | May | 2023 | 1.0898e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-22 15:17 | 2023-05-22 15:19 | 315 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C23052200343 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-22 | 630 | keep | 0 | May | 2023 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-22 15:18 | 2023-05-22 18:19 | 15 | 3:01 | P | ALIMENTADOR AMARRADO | 1 X 65 EN C/L | C23052200341 | New_Event | Feeder Load Transferred | Include | Include | Other | 181 | 2023-05-22 | 2715 | keep | 0 | May | 2023 | 0.0018492 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-22 15:24 | 2023-05-22 18:33 | 100 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CL FUERTES VIENTOS | M23052200152 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2023-05-22 | 18900 | keep | 0 | May | 2023 | 0.012873 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-05-22 15:30 | 2023-05-22 16:24 | 12 | 0:54 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | C23052200349 | New_Event | Animals | Include | Include | Wildlife | 54 | 2023-05-22 | 648 | keep | 0 | May | 2023 | 0.00044135 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-05-22 15:41 | 2023-05-22 17:30 | 60 | 1:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMA DE ARBOL | P23052200444 | New_Event | Vegetation Contact | Include | Include | Vegetation | 109 | 2023-05-22 | 6540 | keep | 0 | May | 2023 | 0.0044544 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-05-22 15:50 | 2023-05-22 16:04 | 6285 | 0:14 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | DISPARO INTERRUPTOR SE VERIFICO PERSONAL FUERA DE LAS LINEAS SE CERRO INTERRUPTOR | M23052200158 | New_Event | Primary Pole Failure | Include | Include | Equipment | 14 | 2023-05-22 | 87990 | keep | 0 | May | 2023 | 0.05993 | 0.0042807 | Sustained | FALSE | FALSE | Not_TMED_Event | 6285
MAYAGÃœEZ | 2023-05-22 16:00 | 2023-05-23 01:05 | 150 | 9:05 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA QUEMADA | M23052200235 | New_Event | Cutout Failure | Include | Include | Equipment | 545 | 2023-05-22 | 81750 | keep | 0 | May | 2023 | 0.05568 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-05-22 16:04 | 2023-05-23 01:35 | 1277 | 9:31 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO Y SE CERRO MACHETES | M23052200182 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 571 | 2023-05-22 | 729167 | keep | 0 | May | 2023 | 0.49663 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-22 16:05 | 2023-05-22 19:37 | 25 | 3:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE SACO RAMA DE PALMA DE LINEA PRIMARIA | P23052200450 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2023-05-22 | 5300 | keep | 0 | May | 2023 | 0.0036098 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-22 16:19 | 2023-05-23 06:36 | 12 | 14:17 | P | TRANSFORMADOR AVERIADO | SE ABRIO XMR Y SE REEMPLAZO BUSHING SECUNDARIO PARTIDO | B23052200299 | New_Event | Service Transformer Failure | Include | Include | Equipment | 857 | 2023-05-22 | 10284 | keep | 0 | May | 2023 | 0.0070044 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-22 16:25 | 2023-05-22 19:31 | 12 | 3:06 | P | DESGANCHE | SE ABRIO EN XMR Y SE REALIZO DESGANCHE PRIMARIO (ROMPIENDO CLEARANCE) | S23052200150 | New_Event | Vegetation Contact | Include | Include | Vegetation | 186 | 2023-05-22 | 2232 | keep | 0 | May | 2023 | 0.0015202 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
YAUCO | 2023-05-22 16:25 | 2023-05-22 18:11 | 12 | 1:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN TRANSFORMADOR FUERTE LLUVIA | P23052200475 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 106 | 2023-05-22 | 1272 | keep | 0 | May | 2023 | 0.00086635 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-22 16:28 | 2023-05-22 20:12 | 1 | 3:44 | P | NO SE REPORTO CAUSA | 1 X 100 EN BANCO DE XMR | B23052200305 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 224 | 2023-05-22 | 224 | keep | 0 | May | 2023 | 0.00015257 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-22 16:29 | 2023-05-22 18:15 | 80 | 1:46 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052200247 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 106 | 2023-05-22 | 8480 | keep | 0 | May | 2023 | 0.0057757 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-05-22 16:30 | 2023-05-22 19:09 | 8 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | C23052200369 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2023-05-22 | 1272 | keep | 0 | May | 2023 | 0.00086635 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-22 16:31 | 2023-05-22 18:11 | 6 | 1:40 | P | NO SE REPORTO CAUSA | 1 X 8 EN XMR | C23052200370 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 100 | 2023-05-22 | 600 | keep | 0 | May | 2023 | 0.00040866 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-05-22 16:42 | 2023-05-22 21:21 | 4 | 4:39 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | C23052200372 | New_Event | Animals | Include | Include | Wildlife | 279 | 2023-05-22 | 1116 | keep | 0 | May | 2023 | 0.0007601 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-22 16:47 | 2023-05-22 16:54 | 3798 | 0:07 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR, SE VERIFICO PERSONAL FUERA, SE CERRO POR CONTROL. SE QUEDO FUERA EL PB 1806-01A Y 1806-01B LLEVA 1214 CLIENTES DEL 1806-02 | B23052200565 | New_Event | Primary Wire Break | Include | Include | Equipment | 7 | 2023-05-22 | 26586 | keep | 0 | May | 2023 | 0.018108 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
PONCE | 2023-05-22 16:48 | 2023-05-22 21:05 | 53 | 4:17 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA FUERTE LLUVIA | P23052200490 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 257 | 2023-05-22 | 13621 | keep | 0 | May | 2023 | 0.0092772 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
BARRANQUITAS | 2023-05-22 16:49 | 2023-05-22 17:38 | 12 | 0:49 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE | C23052200378 | New_Event | Vegetation Contact | Include | Include | Vegetation | 49 | 2023-05-22 | 588 | keep | 0 | May | 2023 | 0.00040048 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-22 16:54 | 2023-05-22 19:40 | 2377 | 2:46 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZO PRUEBA EN EL PB 1806-01A EN SERVICIO SIGUE FUERA EL PB 1806-01B LLEVA 1214 CLIENTES DEL 1806-02 | B23052200565 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 166 | 2023-05-22 | 394582 | keep | 0 | May | 2023 | 0.26875 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-22 16:54 | 2023-05-22 20:40 | 1214 | 3:46 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1806-01, SE CERRO POR CONTROL SE QUEDO FUERA EL PB 1806-01A Y 1806-01B LLEVA 1214 CLIENTES DEL 1806-02. LOS 1214 CLIENTES SE NORMALIZARON. EN SERVICIO | B23052200314 | New_Event | Feeder Load Transferred | Include | Include | Other | 226 | 2023-05-22 | 274364 | keep | 0 | May | 2023 | 0.18687 | 0.00082685 | Sustained | FALSE | FALSE | Not_TMED_Event | 1214
CANOVANAS | 2023-05-22 16:57 | 2023-05-22 18:00 | 35 | 1:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 C/L MAL TIEMPO VIENTO | R23052200109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 63 | 2023-05-22 | 2205 | keep | 0 | May | 2023 | 0.0015018 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-22 16:59 | 2023-05-23 08:25 | 30 | 15:26 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052200320 | New_Event | Vegetation Contact | Include | Include | Vegetation | 926 | 2023-05-22 | 27780 | keep | 0 | May | 2023 | 0.018921 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-22 16:59 | 2023-05-23 07:59 | 30 | 15:00 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23052200043 | New_Event | Animals | Include | Include | Wildlife | 900 | 2023-05-22 | 27000 | keep | 0 | May | 2023 | 0.01839 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-22 17:00 | 2023-05-22 17:45 | 15 | 0:45 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE DE 75 KVA X 75 KVA | M23052200199 | New_Event | Service Transformer Failure | Include | Include | Equipment | 45 | 2023-05-22 | 675 | keep | 0 | May | 2023 | 0.00045974 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-22 17:03 | 2023-05-22 17:04 | 3438 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B23052200325 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 3438 | keep | 0 | May | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-05-22 17:04 | 2023-05-23 04:24 | 180 | 11:20 | P | ANIMAL | 1 X 15 Y 1 X 25 EN C/L CRUCE X AVE | B23052200130 | Partial_restoration | Animals | Include | Include | Wildlife | 680 | 2023-05-22 | 122400 | keep | 0 | May | 2023 | 0.083366 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-22 17:08 | 2023-05-22 18:37 | 20 | 1:29 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23052200386 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-05-22 | 1780 | keep | 0 | May | 2023 | 0.0012123 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-05-22 17:24 | 2023-05-22 17:50 | 1 | 0:26 | P | MAL TIEMPO/RAYOS | 1 X 50 EN C/L MAL TIEMPO VIENTO | R23052200112 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 26 | 2023-05-22 | 26 | keep | 0 | May | 2023 | 1.7708e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-22 17:30 | 2023-05-22 19:25 | 105 | 1:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTE LLUVIA | P23052200515 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 115 | 2023-05-22 | 12075 | keep | 0 | May | 2023 | 0.0082242 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
BAYAMON | 2023-05-22 17:37 | 2023-05-23 05:20 | 10 | 11:43 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | B23052200374 | New_Event | Animals | Include | Include | Wildlife | 703 | 2023-05-22 | 7030 | keep | 0 | May | 2023 | 0.0047881 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-22 17:42 | 2023-05-22 17:43 | 693 | 0:01 | T | NO SE REPORTO CAUSA | RECIEERE | R2305220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 693 | keep | 0 | May | 2023 | 0.000472 | 0.000472 | Momentary | FALSE | FALSE | Not_TMED_Event | 693
AGUADILLA | 2023-05-22 17:42 | 2023-05-22 19:00 | 40 | 1:18 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR Y 3 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052200267 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 78 | 2023-05-22 | 3120 | keep | 0 | May | 2023 | 0.002125 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-22 17:59 | 2023-05-22 19:34 | 1883 | 1:35 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA SE CERRO POR SCADA 20% DE SU CARGA POR EL 2604-03 CG-230522-02 | C23052200407 | New_Event | UG Cable Fault | Include | Include | Equipment | 95 | 2023-05-22 | 178885 | keep | 0 | May | 2023 | 0.12184 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
HUMACAO | 2023-05-22 18:00 | 2023-05-22 18:01 | 640 | 0:01 | T | MAL TIEMPO/RAYOS | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C2305220000X | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1 | 2023-05-22 | 640 | keep | 0 | May | 2023 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
HUMACAO | 2023-05-22 18:00 | 2023-05-22 19:47 | 5 | 1:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR MAL TIEMPO VIENTO | C23052200408 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 107 | 2023-05-22 | 535 | keep | 0 | May | 2023 | 0.00036439 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
UTUADO | 2023-05-22 18:00 | 2023-05-22 18:30 | 20 | 0:30 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CONVERTIDOR PARA CERRAR PUENTES | A23052200139 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 30 | 2023-05-22 | 600 | keep | 0 | May | 2023 | 0.00040866 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-22 18:01 | 2023-05-22 20:42 | 21 | 2:41 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYOS | C23052200420 | 1st_after_momentary | Bad Weather (Lightning) | Include | Include | Lightning | 161 | 2023-05-22 | 3381 | keep | 0 | May | 2023 | 0.0023028 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
SAN JUAN | 2023-05-22 18:04 | 2023-05-22 18:05 | 4291 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2305220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 4291 | keep | 0 | May | 2023 | 0.0029226 | 0.0029226 | Momentary | FALSE | FALSE | Not_TMED_Event | 4291
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 569 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 569 | keep | 0 | May | 2023 | 0.00038754 | 0.00038754 | Momentary | FALSE | FALSE | Not_TMED_Event | 569
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 1245 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 1245 | keep | 0 | May | 2023 | 0.00084796 | 0.00084796 | Momentary | FALSE | FALSE | Not_TMED_Event | 1245
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 1155 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200218 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 1155 | keep | 0 | May | 2023 | 0.00078667 | 0.00078667 | Momentary | FALSE | FALSE | Not_TMED_Event | 1155
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 867 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 867 | keep | 0 | May | 2023 | 0.00059051 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 257 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 257 | keep | 0 | May | 2023 | 0.00017504 | 0.00017504 | Momentary | FALSE | FALSE | Not_TMED_Event | 257
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 1336 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200219 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 1336 | keep | 0 | May | 2023 | 0.00090994 | 0.00090994 | Momentary | FALSE | FALSE | Not_TMED_Event | 1336
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 3315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 3315 | keep | 0 | May | 2023 | 0.0022578 | 0.0022578 | Momentary | FALSE | FALSE | Not_TMED_Event | 3315
AGUADILLA | 2023-05-22 18:11 | 2023-05-22 18:12 | 1718 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2500 | M23052200220 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-22 | 1718 | keep | 0 | May | 2023 | 0.0011701 | 0.0011701 | Momentary | FALSE | FALSE | Not_TMED_Event | 1718
GUAYAMA | 2023-05-22 18:15 | 2023-05-22 18:16 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052200545 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
SAN JUAN | 2023-05-22 18:17 | 2023-05-23 11:02 | 20 | 16:45 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23052200156 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1005 | 2023-05-22 | 20100 | keep | 0 | May | 2023 | 0.01369 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-22 18:19 | 2023-05-23 08:39 | 22 | 14:20 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C23052200427 | New_Event | Animals | Include | Include | Wildlife | 860 | 2023-05-22 | 18920 | keep | 0 | May | 2023 | 0.012886 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-05-22 18:23 | 2023-05-23 09:40 | 14 | 15:17 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23052200157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 917 | 2023-05-22 | 12838 | keep | 0 | May | 2023 | 0.0087439 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2023-05-22 18:27 | 2023-05-22 20:25 | 60 | 1:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052200270 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 118 | 2023-05-22 | 7080 | keep | 0 | May | 2023 | 0.0048222 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
PONCE | 2023-05-22 18:28 | 2023-05-22 19:30 | 10 | 1:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN TRANSFORMADOR FUERTE LLUVIA | P23052200550 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 62 | 2023-05-22 | 620 | keep | 0 | May | 2023 | 0.00042228 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-22 18:31 | 2023-05-23 14:40 | 10 | 20:09 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052200271 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1209 | 2023-05-22 | 12090 | keep | 0 | May | 2023 | 0.0082344 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-05-22 18:42 | 2023-05-22 20:00 | 137 | 1:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 140 EN CORTE DE LINEA FUERTE LLUVIA | P23052200560 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 78 | 2023-05-22 | 10686 | keep | 0 | May | 2023 | 0.0072782 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
ARECIBO | 2023-05-22 18:47 | 2023-05-22 20:29 | 12 | 1:42 | P | OTRAS CAUSAS | 1 X 10 EN TRANSFORMADOR FUSIBLE CORROIDO | A23052200272 | New_Event | Other Causes | Include | Include | Other | 102 | 2023-05-22 | 1224 | keep | 0 | May | 2023 | 0.00083366 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
HUMACAO | 2023-05-22 18:48 | 2023-05-23 11:35 | 9 | 16:47 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA | C23052200418 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1007 | 2023-05-22 | 9063 | keep | 0 | May | 2023 | 0.0061728 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-05-22 18:55 | 2023-05-23 12:15 | 4 | 17:20 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23052200160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1040 | 2023-05-22 | 4160 | keep | 0 | May | 2023 | 0.0028334 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
MAYAGÃœEZ | 2023-05-22 18:56 | 2023-05-23 10:10 | 12 | 15:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23052200227 | New_Event | Vegetation Contact | Include | Include | Vegetation | 914 | 2023-05-22 | 10968 | keep | 0 | May | 2023 | 0.0074703 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-22 19:00 | 2023-05-23 17:43 | 10 | 22:43 | P | CABLE SOTERRADO AVERIADO | SE REPARO CABLE SOTERRADO DE T9 A T10 | B23052300094 | New_Event | UG Cable Fault | Include | Include | Equipment | 1363 | 2023-05-22 | 13630 | keep | 0 | May | 2023 | 0.0092833 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-22 19:02 | 2023-05-22 21:54 | 29 | 2:52 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23052200419 | New_Event | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-05-22 | 4988 | keep | 0 | May | 2023 | 0.0033973 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
PONCE | 2023-05-22 19:08 | 2023-05-22 19:09 | 5063 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052200580 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 5063 | keep | 0 | May | 2023 | 0.0034484 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
CANOVANAS | 2023-05-22 19:09 | 2023-05-22 19:10 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1602-05 | R2305220000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-05-22 19:09 | 2023-05-22 19:10 | 188 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE CARGA POR 1602-02 | R2305220000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-22 | 188 | keep | 0 | May | 2023 | 0.00012805 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
GUAYAMA | 2023-05-22 19:10 | 2023-05-22 19:11 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052200586 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 1945 | keep | 0 | May | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
SAN JUAN | 2023-05-22 19:16 | 2023-05-22 21:28 | 115 | 2:12 | P | DESGANCHE | 1X80 EN C/L DESGANCHE | S23052200164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-05-22 | 15180 | keep | 0 | May | 2023 | 0.010339 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
CANOVANAS | 2023-05-22 19:24 | 2023-05-22 20:47 | 11 | 1:23 | P | DESGANCHE | 1 X 50EN C/L Y DESGANCHE | R23052200118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 83 | 2023-05-22 | 913 | keep | 0 | May | 2023 | 0.00062184 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
HUMACAO | 2023-05-22 19:34 | 2023-05-22 19:38 | 706 | 0:04 | P | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES BUSCANDO AVERIA CG-230522-02 | C23052200407 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 4 | 2023-05-22 | 2824 | keep | 0 | May | 2023 | 0.0019234 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-22 19:38 | 2023-05-22 19:56 | 1883 | 0:18 | P | CABLE SOTERRADO AVERIADO | DISPARO DE INTERRUPTOR SE REALIZARON OPERACIONES BUSCANDO AVERIA SOLO LLEVA EL 80% DE SU CARGA CG-230522-02 | C23052200407 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 18 | 2023-05-22 | 33894 | keep | 0 | May | 2023 | 0.023085 | 0.0012825 | Sustained | FALSE | FALSE | Not_TMED_Event | 1883
BAYAMON | 2023-05-22 19:40 | 2023-05-22 22:02 | 440 | 2:22 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE EN MACHETE CERCA DEL PB 1806-01A | B23052200565 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 142 | 2023-05-22 | 62480 | keep | 0 | May | 2023 | 0.042555 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-22 19:40 | 2023-05-22 22:13 | 1059 | 2:33 | P | CONDUCTOR ROTO O ABIERTO | SE REALIZO PRUEBA EN EL PB 1806-01B EN SERVICIO LA CAUSA FUE EL PUENTE ABIERTO EN MACHETE CERCA DEL PB 1806-01A | B23052200565 | New_Event | Primary Wire Break | Include | Include | Equipment | 153 | 2023-05-22 | 162027 | keep | 0 | May | 2023 | 0.11036 | 0.00072128 | Sustained | FALSE | FALSE | Not_TMED_Event | 1059
BARRANQUITAS | 2023-05-22 19:46 | 2023-05-23 09:15 | 36 | 13:29 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23052200432 | New_Event | Vegetation Contact | Include | Include | Vegetation | 809 | 2023-05-22 | 29124 | keep | 0 | May | 2023 | 0.019836 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
BAYAMON | 2023-05-22 19:50 | 2023-05-22 19:51 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVA EL 9206-07 | B23052200587 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-22 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-22 19:50 | 2023-05-22 19:51 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA EL 9206-07 | B23052200587 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
PONCE | 2023-05-22 19:53 | 2023-05-22 19:57 | 5063 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL | P23052200602 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-22 | 20252 | keep | 0 | May | 2023 | 0.013794 | 0.0034484 | Momentary | FALSE | FALSE | Not_TMED_Event | 5063
HUMACAO | 2023-05-22 19:56 | 2023-05-22 20:30 | 471 | 0:34 | P | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES BUSCANDO AVERIA SE CERRO N/O CONTRA EL MISMO EN SERVICIO 100% Y 20% DE SU CARGA POR EL 2604-03. AVERIA SOTERRADA DE PB-1 @ SU-PDR1 CG-230522-02 | C23052200407 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 34 | 2023-05-22 | 16014 | keep | 0 | May | 2023 | 0.010907 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-22 20:00 | 2023-05-23 11:05 | 6 | 15:05 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO RAYOS | C23052200439 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 905 | 2023-05-22 | 5430 | keep | 0 | May | 2023 | 0.0036983 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-05-22 20:03 | 2023-05-23 10:29 | 95 | 14:26 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA | C23052200440 | New_Event | Vegetation Contact | Include | Include | Vegetation | 866 | 2023-05-22 | 82270 | keep | 0 | May | 2023 | 0.056034 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
UTUADO | 2023-05-22 20:09 | 2023-05-23 12:30 | 50 | 16:21 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23052200280 | New_Event | Vegetation Contact | Include | Include | Vegetation | 981 | 2023-05-22 | 49050 | keep | 0 | May | 2023 | 0.033408 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-22 20:16 | 2023-05-22 22:38 | 9 | 2:22 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA POR DESCARGA ELECTRICA | P23052200609 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 142 | 2023-05-22 | 1278 | keep | 0 | May | 2023 | 0.00087044 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-05-22 20:36 | 2023-05-22 20:38 | 4381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE REALIZA PRUEBA Y QUEDA EN SERVICIO | M23052200243 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-22 | 8762 | keep | 0 | May | 2023 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
YAUCO | 2023-05-22 21:19 | 2023-05-23 10:56 | 582 | 13:37 | P | MAL TIEMPO/LLUVIA O VIENTO | SE SECCIONALIZO AVERIA ALAMBRE PRIMARIO EN EL PISO 1 X 80 EN CORTE DE LINEA | P23052200632 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 817 | 2023-05-22 | 475494 | keep | 0 | May | 2023 | 0.32386 | 0.0003964 | Sustained | FALSE | FALSE | Not_TMED_Event | 582
BAYAMON | 2023-05-22 21:19 | 2023-05-22 21:20 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVA 9206-07 | B23052200734 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-22 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-22 21:19 | 2023-05-22 21:20 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 9206-07 | B23052200734 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
BAYAMON | 2023-05-22 21:32 | 2023-05-23 02:48 | 234 | 5:16 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23052200752 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-05-22 | 73944 | keep | 0 | May | 2023 | 0.050363 | 0.00015938 | Sustained | FALSE | FALSE | Not_TMED_Event | 234
GUAYAMA | 2023-05-22 21:37 | 2023-05-22 22:53 | 9 | 1:16 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR POR DESGANCHE | P23052200633 | New_Event | Vegetation Contact | Include | Include | Vegetation | 76 | 2023-05-22 | 684 | keep | 0 | May | 2023 | 0.00046587 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
PONCE | 2023-05-22 21:38 | 2023-05-23 05:34 | 25 | 7:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR MAL TIEMPO | P23052200634 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 476 | 2023-05-22 | 11900 | keep | 0 | May | 2023 | 0.008105 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-22 21:52 | 2023-05-23 12:05 | 1 | 14:13 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052200249 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 853 | 2023-05-22 | 853 | keep | 0 | May | 2023 | 0.00058097 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-22 22:19 | 2023-05-23 07:42 | 30 | 9:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA | C23052200457 | New_Event | Vegetation Contact | Include | Include | Vegetation | 563 | 2023-05-22 | 16890 | keep | 0 | May | 2023 | 0.011504 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-05-22 22:21 | 2023-05-23 09:09 | 23 | 10:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN XMR SE REEMPLAZO PORTA FUSIBLE | R23052200128 | New_Event | Cutout Failure | Include | Include | Equipment | 648 | 2023-05-22 | 14904 | keep | 0 | May | 2023 | 0.010151 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
AGUADILLA | 2023-05-22 23:11 | 2023-05-23 09:10 | 8 | 9:59 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR CONEXIONES SECUNDARIAS | M23052200254 | New_Event | Secondary Wire Break | Include | Include | Equipment | 599 | 2023-05-22 | 4792 | keep | 0 | May | 2023 | 0.0032638 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-05-22 23:30 | 2023-05-22 23:32 | 215 | 0:02 | T | MAL TIEMPO/LLUVIA O VIENTO | DISPARO DE BKR SE CERRO POR CONTROL | B23052200804 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 2 | 2023-05-22 | 430 | keep | 0 | May | 2023 | 0.00029287 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
BARRANQUITAS | 2023-05-22 23:31 | 2023-05-23 11:43 | 154 | 12:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23052200462 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 732 | 2023-05-22 | 112728 | keep | 0 | May | 2023 | 0.076779 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
VEGA BAJA | 2023-05-22 23:32 | 2023-05-23 07:57 | 48 | 8:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO | B23052200806 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 505 | 2023-05-22 | 24240 | keep | 0 | May | 2023 | 0.01651 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
ARECIBO | 2023-05-22 23:49 | 2023-05-22 23:50 | 2703 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23052200287 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-22 | 2703 | keep | 0 | May | 2023 | 0.001841 | 0.001841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2703
CAGUAS | 2023-05-22 23:51 | 2023-05-23 09:10 | 53 | 9:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23052200463 | New_Event | Vegetation Contact | Include | Include | Vegetation | 559 | 2023-05-22 | 29627 | keep | 0 | May | 2023 | 0.020179 | 3.6098e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 53
YAUCO | 2023-05-22 23:51 | 2023-05-23 12:12 | 50 | 12:21 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO ESE FUE EL EVENTO QUE DIERON | P23052200650 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 741 | 2023-05-22 | 37050 | keep | 0 | May | 2023 | 0.025235 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-23 | 2023-05-23 10:47 | 1 | 10:47 | P | PROBLEMA DEL CLIENTE | 2 X 20 EN RISER FALTA DE MANTENIMIENTO EN SUBESTACION PRIVADA | B23052300001 | New_Event | Customer-Related Interruption | Include | Include | Public | 647 | 2023-05-23 | 647 | keep | 0 | May | 2023 | 0.00044067 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-05-23 00:05 | 2023-05-23 10:30 | 100 | 10:25 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23052300001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 625 | 2023-05-23 | 62500 | keep | 0 | May | 2023 | 0.042568 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-05-23 00:10 | 2023-05-23 12:45 | 20 | 12:35 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052300087 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 755 | 2023-05-23 | 15100 | keep | 0 | May | 2023 | 0.010285 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-23 00:23 | 2023-05-23 00:24 | 841 | 0:01 | P | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR 50% DE LA CARGA POR EL 3103-02 EN SERVICIO | C23052300003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 841 | keep | 0 | May | 2023 | 0.0005728 | 0.0005728 | Momentary | FALSE | FALSE | Not_TMED_Event | 841
BARRANQUITAS | 2023-05-23 00:38 | 2023-05-23 00:39 | 2486 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 2486 | keep | 0 | May | 2023 | 0.0016932 | 0.0016932 | Momentary | FALSE | FALSE | Not_TMED_Event | 2486
BARRANQUITAS | 2023-05-23 00:44 | 2023-05-23 13:00 | 25 | 12:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C23052300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 736 | 2023-05-23 | 18400 | keep | 0 | May | 2023 | 0.012532 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
AGUADILLA | 2023-05-23 01:16 | 2023-05-23 08:50 | 20 | 7:34 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052300009 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 454 | 2023-05-23 | 9080 | keep | 0 | May | 2023 | 0.0061843 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-23 01:30 | 2023-05-23 01:31 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23052300011 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 199 | keep | 0 | May | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
AGUADILLA | 2023-05-23 01:35 | 2023-05-23 13:30 | 15 | 11:55 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE PASO E INSTALO TRANSFORMADOR A POSTE NUEVO | M23052200182 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 715 | 2023-05-23 | 10725 | keep | 0 | May | 2023 | 0.0073047 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-23 01:45 | 2023-05-23 15:14 | 89 | 13:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA | C23052300012 | New_Event | Cutout Failure | Include | Include | Equipment | 809 | 2023-05-23 | 72001 | keep | 0 | May | 2023 | 0.04904 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
BAYAMON | 2023-05-23 01:56 | 2023-05-23 01:57 | 2861 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9400 | B23052300006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 2861 | keep | 0 | May | 2023 | 0.0019486 | 0.0019486 | Momentary | FALSE | FALSE | Not_TMED_Event | 2861
BAYAMON | 2023-05-23 01:56 | 2023-05-23 01:57 | 2096 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9400 | B23052300006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 2096 | keep | 0 | May | 2023 | 0.0014276 | 0.0014276 | Momentary | FALSE | FALSE | Not_TMED_Event | 2096
BAYAMON | 2023-05-23 01:56 | 2023-05-23 01:57 | 493 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 9400 | B23052300006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 493 | keep | 0 | May | 2023 | 0.00033578 | 0.00033578 | Momentary | FALSE | FALSE | Not_TMED_Event | 493
PONCE | 2023-05-23 02:13 | 2023-05-23 02:14 | 4009 | 0:01 | S | NO SE REPORTO CAUSA | RECIERRE PORTATIL 14 | P23052300044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 4009 | keep | 0 | May | 2023 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
HUMACAO | 2023-05-23 02:41 | 2023-05-23 14:00 | 60 | 11:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO DESCARGAS ELECTRICAS | C23052300015 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 679 | 2023-05-23 | 40740 | keep | 0 | May | 2023 | 0.027748 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-05-23 04:00 | 2023-05-23 12:00 | 45 | 8:00 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052300004 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 480 | 2023-05-23 | 21600 | keep | 0 | May | 2023 | 0.014712 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2023-05-23 04:27 | 2023-05-23 09:40 | 78 | 5:13 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23052300018 | New_Event | Vegetation Contact | Include | Include | Vegetation | 313 | 2023-05-23 | 24414 | keep | 0 | May | 2023 | 0.016628 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
CAGUAS | 2023-05-23 04:59 | 2023-05-24 18:50 | 70 | 37:51 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN C/L SE REEMPLAZO POSTE PRIMARIO | C23052300295 | New_Event | Primary Pole Failure | Include | Include | Equipment | 2271 | 2023-05-23 | 158970 | keep | 0 | May | 2023 | 0.10827 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2023-05-23 05:10 | 2023-05-23 10:21 | 94 | 5:11 | P | DESGANCHE | DESGANCHE 1 X 50 EN C/L | R2305230000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2023-05-23 | 29234 | keep | 0 | May | 2023 | 0.019911 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
SAN JUAN | 2023-05-23 05:12 | 2023-05-23 05:14 | 10211 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL | S2305230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-23 | 20422 | keep | 0 | May | 2023 | 0.013909 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
HUMACAO | 2023-05-23 05:15 | 2023-05-23 08:32 | 29 | 3:17 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO RAYOS | C23052300023 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 197 | 2023-05-23 | 5713 | keep | 0 | May | 2023 | 0.0038911 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2023-05-23 05:15 | 2023-05-23 10:22 | 50 | 5:07 | P | DESGANCHE | 1 X 80 C/L DESGANCHE | B23052300008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 307 | 2023-05-23 | 15350 | keep | 0 | May | 2023 | 0.010455 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-23 05:47 | 2023-05-23 11:35 | 25 | 5:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CORTE DE LINEA Y 1 X 40 Y 1 X 65 EN DIFERENTES CORTES DE LINEA | P23052300048 | New_Event | Cutout Failure | Include | Include | Equipment | 348 | 2023-05-23 | 8700 | keep | 0 | May | 2023 | 0.0059255 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-05-23 05:50 | 2023-05-23 11:51 | 50 | 6:01 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23052300049 | New_Event | Animals | Include | Include | Wildlife | 361 | 2023-05-23 | 18050 | keep | 0 | May | 2023 | 0.012294 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-05-23 06:09 | 2023-05-23 09:07 | 30 | 2:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR MAL TIEMPO | P23052300054 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 178 | 2023-05-23 | 5340 | keep | 0 | May | 2023 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-23 06:28 | 2023-05-23 10:50 | 7 | 4:22 | P | DESGANCHE | 1 X 80 EN C/L DEGANCHE | S23052300007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 262 | 2023-05-23 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-23 06:36 | 2023-05-23 06:37 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 4133 | keep | 0 | May | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
VEGA BAJA | 2023-05-23 06:52 | 2023-05-23 13:45 | 50 | 6:53 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | A23052300022 | New_Event | Animals | Include | Include | Wildlife | 413 | 2023-05-23 | 20650 | keep | 0 | May | 2023 | 0.014065 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-05-23 07:11 | 2023-05-23 15:20 | 50 | 8:09 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23052300068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 489 | 2023-05-23 | 24450 | keep | 0 | May | 2023 | 0.016653 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-23 07:12 | 2023-05-23 15:02 | 10 | 7:50 | P | MAL TIEMPO/RAYOS | 2 X 50 EN C/L MAL TIEMPO RAYOS | P23052300069 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 470 | 2023-05-23 | 4700 | keep | 0 | May | 2023 | 0.0032011 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-23 07:15 | 2023-05-23 10:35 | 2 | 3:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23052300006 | New_Event | Secondary Wire Break | Include | Include | Equipment | 200 | 2023-05-23 | 400 | keep | 0 | May | 2023 | 0.00027244 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BARRANQUITAS | 2023-05-23 07:21 | 2023-05-23 07:26 | 327 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV AISLADOR CON FOGONAZO DEBIDO A CONTAMINACIÃ“N. | C23052300038 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-23 | 1635 | keep | 0 | May | 2023 | 0.0011136 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
BARRANQUITAS | 2023-05-23 07:21 | 2023-05-23 07:26 | 1843 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV AISLADOR CON FOGONAZO DEBIDO A CONTAMINACIÃ“N. | C23052300038 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-23 | 9215 | keep | 0 | May | 2023 | 0.0062763 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BARRANQUITAS | 2023-05-23 07:21 | 2023-05-23 07:26 | 2203 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV AISLADOR CON FOGONAZO DEBIDO A CONTAMINACIÃ“N. | C23052300038 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-23 | 11015 | keep | 0 | May | 2023 | 0.0075023 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
BARRANQUITAS | 2023-05-23 07:21 | 2023-05-23 07:26 | 2457 | 0:05 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE BARRA DE 38KV AISLADOR CON FOGONAZO DEBIDO A CONTAMINACIÃ“N. | C23052300038 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 5 | 2023-05-23 | 12285 | keep | 0 | May | 2023 | 0.0083673 | 0.0016735 | Momentary | FALSE | FALSE | Not_TMED_Event | 2457
AGUADILLA | 2023-05-23 07:33 | 2023-05-23 07:34 | 390 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR NO SE REPORTO CAUSA | M23052300002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 390 | keep | 0 | May | 2023 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
BARRANQUITAS | 2023-05-23 07:33 | 2023-05-23 10:34 | 28 | 3:01 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | C23052300040 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 181 | 2023-05-23 | 5068 | keep | 0 | May | 2023 | 0.0034518 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2023-05-23 07:55 | 2023-05-23 14:30 | 2 | 6:35 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS SECUNDARIAS CRUZADAS | A23052300040 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 395 | 2023-05-23 | 790 | keep | 0 | May | 2023 | 0.00053807 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-05-23 07:57 | 2023-05-24 15:20 | 1 | 31:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | A23052300023 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1883 | 2023-05-23 | 1883 | keep | 0 | May | 2023 | 0.0012825 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-23 08:19 | 2023-05-23 09:16 | 15 | 0:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23052300055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 57 | 2023-05-23 | 855 | keep | 0 | May | 2023 | 0.00058234 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-05-23 08:20 | 2023-05-23 10:25 | 100 | 2:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER DESCARGAS ELECTRICAS | P23052300091 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 125 | 2023-05-23 | 12500 | keep | 0 | May | 2023 | 0.0085137 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-23 08:31 | 2023-05-23 09:26 | 2 | 0:55 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | S23052300038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 55 | 2023-05-23 | 110 | keep | 0 | May | 2023 | 7.492e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CANOVANAS | 2023-05-23 08:34 | 2023-05-23 12:05 | 78 | 3:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y 1 X 10 EN XMR Y 1 40 EN C/L | R23052300013 | New_Event | Cutout Failure | Include | Include | Equipment | 211 | 2023-05-23 | 16458 | keep | 0 | May | 2023 | 0.011209 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
ARECIBO | 2023-05-23 08:43 | 2023-05-23 12:15 | 1 | 3:32 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A23052300057 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 212 | 2023-05-23 | 212 | keep | 0 | May | 2023 | 0.00014439 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-23 08:47 | 2023-05-23 13:42 | 2450 | 4:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 12600 DE HUMACAO TC A VERDEMAR | C23052300065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 295 | 2023-05-23 | 722750 | keep | 0 | May | 2023 | 0.49226 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-05-23 08:47 | 2023-05-23 13:42 | 640 | 4:55 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 12600 DE HUMACAO TC A VERDEMAR | C23052300065 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 295 | 2023-05-23 | 188800 | keep | 0 | May | 2023 | 0.12859 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
VEGA BAJA | 2023-05-23 08:49 | 2023-05-23 21:20 | 35 | 12:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO C/L PARA REPARAR SECUNDARIA Y NEUTRAL SECUNDARIO USADO COMO NEUTRAL PRIMARIO | B23052300494 | New_Event | Secondary Wire Break | Include | Include | Equipment | 751 | 2023-05-23 | 26285 | keep | 0 | May | 2023 | 0.017903 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
AGUADILLA | 2023-05-23 08:51 | 2023-05-23 12:00 | 150 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052300012 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2023-05-23 | 28350 | keep | 0 | May | 2023 | 0.019309 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-05-23 08:59 | 2023-05-23 09:29 | 7 | 0:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X10 EN XMR MAL TIEMPO | C23052300075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 30 | 2023-05-23 | 210 | keep | 0 | May | 2023 | 0.00014303 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-05-23 09:03 | 2023-05-23 11:13 | 15 | 2:10 | P | DESGANCHE | 1 X 25 EN C/L Y 1 X30 EN C.L DESGANCHE | R23052300017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 130 | 2023-05-23 | 1950 | keep | 0 | May | 2023 | 0.0013281 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-23 09:12 | 2023-05-23 15:53 | 80 | 6:41 | P | DESGANCHE | 1 X 65 C/L DESGANCHE Y SE REMPLAZO AISLADOR | S23052300055 | New_Event | Vegetation Contact | Include | Include | Vegetation | 401 | 2023-05-23 | 32080 | keep | 0 | May | 2023 | 0.02185 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-05-23 09:12 | 2023-05-23 16:38 | 10 | 7:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR Y SE REEMPLAZO CAJA PRIMARIA | B23052300065 | New_Event | Cutout Failure | Include | Include | Equipment | 446 | 2023-05-23 | 4460 | keep | 0 | May | 2023 | 0.0030377 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-23 09:14 | 2023-05-23 14:05 | 7 | 4:51 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE PRIMARIO Y SECUNDARIO | C23052300085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 291 | 2023-05-23 | 2037 | keep | 0 | May | 2023 | 0.0013874 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-05-23 09:17 | 2023-05-23 17:27 | 6 | 8:10 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 37.5 POR 37.5 KVA | R23052300019 | New_Event | Service Transformer Failure | Include | Include | Equipment | 490 | 2023-05-23 | 2940 | keep | 0 | May | 2023 | 0.0020024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-05-23 09:26 | 2023-05-23 15:50 | 15 | 6:24 | P | MAL TIEMPO/RAYOS | 1 X 40 EN C/L MAL TIEMPO RAYOS | P23052300124 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 384 | 2023-05-23 | 5760 | keep | 0 | May | 2023 | 0.0039231 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-23 09:29 | 2023-05-23 10:00 | 8 | 0:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZO DE BARRA EN PEDESTAL | C23052300098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 31 | 2023-05-23 | 248 | keep | 0 | May | 2023 | 0.00016891 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-23 09:33 | 2023-05-23 19:41 | 10 | 10:08 | P | CAUSAS EXTERNAS | SE REEMPLAZARON 2 POSTES SECUNDARIOS Y SE REEMPLAZO XMR 50 KVA. CAMION PRIVADO SE ENREDO EN LINEAS DE COMUNICACIONES Y TUMBO POSTES | B23052300469 | New_Event | Damage From Public | Include | Include | Public | 608 | 2023-05-23 | 6080 | keep | 0 | May | 2023 | 0.0041411 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-23 09:35 | 2023-05-23 13:15 | 82 | 3:40 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | B23052300092 | New_Event | Animals | Include | Include | Wildlife | 220 | 2023-05-23 | 18040 | keep | 0 | May | 2023 | 0.012287 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
MAYAGÃœEZ | 2023-05-23 09:35 | 2023-05-23 11:55 | 11 | 2:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23052300021 | New_Event | Secondary Wire Break | Include | Include | Equipment | 140 | 2023-05-23 | 1540 | keep | 0 | May | 2023 | 0.0010489 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CAGUAS | 2023-05-23 09:40 | 2023-05-23 10:00 | 35 | 0:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23052300062 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 20 | 2023-05-23 | 700 | keep | 0 | May | 2023 | 0.00047677 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BARRANQUITAS | 2023-05-23 10:01 | 2023-05-23 12:40 | 37 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO LLUVIAS | C23052300109 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2023-05-23 | 5883 | keep | 0 | May | 2023 | 0.0040069 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
AGUADILLA | 2023-05-23 10:01 | 2023-05-24 09:59 | 60 | 23:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052300258 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1438 | 2023-05-23 | 86280 | keep | 0 | May | 2023 | 0.058765 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-23 10:11 | 2023-05-23 11:43 | 9 | 1:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA AVERIADA | S23052200140 | New_Event | Secondary Wire Break | Include | Include | Equipment | 92 | 2023-05-23 | 828 | keep | 0 | May | 2023 | 0.00056395 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-05-23 10:14 | 2023-05-23 10:15 | 1307 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | B2305230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 1307 | keep | 0 | May | 2023 | 0.00089019 | 0.00089019 | Momentary | FALSE | FALSE | Not_TMED_Event | 1307
BAYAMON | 2023-05-23 10:22 | 2023-05-23 15:04 | 5 | 4:42 | P | CAUSAS EXTERNAS | 2 X 50 EN RISER HACIA COLEGIO Y 2 X 50 EN RISER HACIA RESIDENCIAS. PERSONAL AJENO A LUMA REALIZANDO DESGANCHE | S23052300089 | New_Event | Damage From Public | Include | Include | Public | 282 | 2023-05-23 | 1410 | keep | 0 | May | 2023 | 0.00096034 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-23 10:30 | 2023-05-23 14:54 | 20 | 4:24 | P | ANIMAL | 1 X 50 1 X 100 CRUCE POR AVE | S23052300093 | New_Event | Animals | Include | Include | Wildlife | 264 | 2023-05-23 | 5280 | keep | 0 | May | 2023 | 0.0035962 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-23 10:32 | 2023-05-23 15:17 | 8 | 4:45 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23052300094 | New_Event | Secondary Wire Break | Include | Include | Equipment | 285 | 2023-05-23 | 2280 | keep | 0 | May | 2023 | 0.0015529 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-05-23 10:42 | 2023-05-23 12:32 | 25 | 1:50 | P | CONDUCTOR ROTO O ABIERTO | 1 X 80 Y 1 X 100 EN DIFERENTES CORTES DE LINEAS ALAMBRE HACIENDO CONTACTO CON CAJA | P23052300166 | New_Event | Primary Wire Break | Include | Include | Equipment | 110 | 2023-05-23 | 2750 | keep | 0 | May | 2023 | 0.001873 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-23 10:43 | 2023-05-23 12:24 | 4 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23052300098 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2023-05-23 | 404 | keep | 0 | May | 2023 | 0.00027516 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
UTUADO | 2023-05-23 10:44 | 2023-05-23 13:30 | 15 | 2:46 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052300086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 166 | 2023-05-23 | 2490 | keep | 0 | May | 2023 | 0.0016959 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
YAUCO | 2023-05-23 10:49 | 2023-05-23 10:51 | 661 | 0:02 | T | DESGANCHE | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23052300170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-05-23 | 1322 | keep | 0 | May | 2023 | 0.00090041 | 0.0004502 | Momentary | FALSE | FALSE | Not_TMED_Event | 661
CANOVANAS | 2023-05-23 10:51 | 2023-05-23 10:53 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2305230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-23 | 3230 | keep | 0 | May | 2023 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
YAUCO | 2023-05-23 10:51 | 2023-05-23 14:50 | 50 | 3:59 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23052300178 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 239 | 2023-05-23 | 11950 | keep | 0 | May | 2023 | 0.0081391 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-05-23 10:56 | 2023-05-23 12:06 | 15 | 1:10 | P | MAL TIEMPO/LLUVIA O VIENTO | SE LEVANTO ALAMBRE PRIMARIO Y SE HIZO DESGANCHE Y SE CERRO CORTE DE LINEA | P23052300173 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 70 | 2023-05-23 | 1050 | keep | 0 | May | 2023 | 0.00071515 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-23 11:05 | 2023-05-23 11:30 | 6 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23052300017 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-23 | 150 | keep | 0 | May | 2023 | 0.00010216 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-05-23 11:21 | 2023-05-23 11:23 | 3005 | 0:02 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR QUEDO FUERA CON SOLO 2 OPERACIONES, SE REALIZO PRUEBA Y PROBO BUENO | C23052300141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-23 | 6010 | keep | 0 | May | 2023 | 0.0040934 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
ARECIBO | 2023-05-23 11:24 | 2023-05-23 14:00 | 50 | 2:36 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23052300092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 156 | 2023-05-23 | 7800 | keep | 0 | May | 2023 | 0.0053125 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-05-23 11:34 | 2023-05-23 14:04 | 80 | 2:30 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C/L SE ELIMINO PARARRAYO AVERIADO | C23052300148 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 150 | 2023-05-23 | 12000 | keep | 0 | May | 2023 | 0.0081731 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BARRANQUITAS | 2023-05-23 11:36 | 2023-05-23 14:32 | 2 | 2:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN XMR MAL TIEMPO LLUVIAS | C23052300149 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 176 | 2023-05-23 | 352 | keep | 0 | May | 2023 | 0.00023975 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-05-23 11:44 | 2023-05-23 14:39 | 50 | 2:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L LLUVIA FUERTE | B23052300136 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 175 | 2023-05-23 | 8750 | keep | 0 | May | 2023 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-23 11:52 | 2023-05-23 13:40 | 1 | 1:48 | P | MAL TIEMPO/RAYOS | 2 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052300053 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 108 | 2023-05-23 | 108 | keep | 0 | May | 2023 | 7.3558e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-23 11:53 | 2023-05-23 11:55 | 1902 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-23 | 3804 | keep | 0 | May | 2023 | 0.0025909 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-05-23 11:53 | 2023-05-23 11:55 | 970 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-23 | 1940 | keep | 0 | May | 2023 | 0.0013213 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-05-23 11:53 | 2023-05-23 11:55 | 3003 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052300034 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-23 | 6006 | keep | 0 | May | 2023 | 0.0040907 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-05-23 11:53 | 2023-05-23 11:55 | 2343 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052300033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-23 | 4686 | keep | 0 | May | 2023 | 0.0031916 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-05-23 11:53 | 2023-05-23 11:55 | 1830 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 CARGA POR EL 2201-04 | R23052300033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-23 | 3660 | keep | 0 | May | 2023 | 0.0024928 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-05-23 11:53 | 2023-05-23 11:55 | 710 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052300033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-23 | 1420 | keep | 0 | May | 2023 | 0.00096716 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-05-23 11:53 | 2023-05-23 11:55 | 1197 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 LLEVA LA CARGA DEL 2201-02 | R23052300033 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-23 | 2394 | keep | 0 | May | 2023 | 0.0016305 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
CAGUAS | 2023-05-23 11:55 | 2023-05-23 13:15 | 65 | 1:20 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO RAYOS | C23052300157 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 80 | 2023-05-23 | 5200 | keep | 0 | May | 2023 | 0.0035417 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
BAYAMON | 2023-05-23 12:13 | 2023-05-23 14:41 | 71 | 2:28 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23052300146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-05-23 | 10508 | keep | 0 | May | 2023 | 0.007157 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
YAUCO | 2023-05-23 12:22 | 2023-05-23 14:40 | 30 | 2:18 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23052300201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 138 | 2023-05-23 | 4140 | keep | 0 | May | 2023 | 0.0028197 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-23 12:40 | 2023-05-23 16:26 | 1 | 3:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN RISER MAL TIEMPO LLUVIAS | C23052300165 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 226 | 2023-05-23 | 226 | keep | 0 | May | 2023 | 0.00015393 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-05-23 12:44 | 2023-05-23 14:35 | 40 | 1:51 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23052300107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-05-23 | 4440 | keep | 0 | May | 2023 | 0.0030241 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-23 13:03 | 2023-05-23 14:40 | 10 | 1:37 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | R23052300047 | New_Event | Animals | Include | Include | Wildlife | 97 | 2023-05-23 | 970 | keep | 0 | May | 2023 | 0.00066066 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-23 13:04 | 2023-05-23 14:48 | 17 | 1:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO SECUNDARIA | S23052300128 | New_Event | Secondary Wire Break | Include | Include | Equipment | 104 | 2023-05-23 | 1768 | keep | 0 | May | 2023 | 0.0012042 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-05-23 13:06 | 2023-05-23 13:09 | 320 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | B2305230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-23 | 960 | keep | 0 | May | 2023 | 0.00065385 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
GUAYAMA | 2023-05-23 13:10 | 2023-05-23 13:11 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052300223 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 1945 | keep | 0 | May | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
HUMACAO | 2023-05-23 13:16 | 2023-05-23 19:33 | 10 | 6:17 | P | TRANSFORMADOR AVERIADO | 1 X 10 EN XMR, SE REEMPLAZO DE XMR 37.5 X 25KVA | C23052300175 | New_Event | Service Transformer Failure | Include | Include | Equipment | 377 | 2023-05-23 | 3770 | keep | 0 | May | 2023 | 0.0025677 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-23 13:30 | 2023-05-23 13:40 | 1 | 0:10 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO SE REPORTO CAUSA | A23052300114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 10 | 2023-05-23 | 10 | keep | 0 | May | 2023 | 6.811e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-23 13:35 | 2023-05-23 15:00 | 4 | 1:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052300065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 85 | 2023-05-23 | 340 | keep | 0 | May | 2023 | 0.00023157 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-05-23 13:38 | 2023-05-23 15:15 | 15 | 1:37 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | P23052300238 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 97 | 2023-05-23 | 1455 | keep | 0 | May | 2023 | 0.00099099 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-05-23 13:39 | 2023-05-23 13:40 | 1192 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23052300066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 1192 | keep | 0 | May | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
CAGUAS | 2023-05-23 13:45 | 2023-05-23 18:34 | 46 | 4:49 | P | ARBOL SOBRE LINEA | SE ABRIO CORTE DE LINEA PARA RETIRAR ARBOL DE LA LINEA | C23052300182 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 289 | 2023-05-23 | 13294 | keep | 0 | May | 2023 | 0.0090545 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
AGUADILLA | 2023-05-23 13:50 | 2023-05-23 18:15 | 150 | 4:25 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA Y 2 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052300067 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 265 | 2023-05-23 | 39750 | keep | 0 | May | 2023 | 0.027074 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-05-23 13:51 | 2023-05-24 10:34 | 2 | 20:43 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 15 KVA POR UNO DE 25 KVA | C23052300188 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1243 | 2023-05-23 | 2486 | keep | 0 | May | 2023 | 0.0016932 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-05-23 13:57 | 2023-05-23 16:16 | 3 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO VIENTOS | P23052300247 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-05-23 | 417 | keep | 0 | May | 2023 | 0.00028402 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
FAJARDO | 2023-05-23 14:09 | 2023-05-23 15:42 | 527 | 1:33 | P | PARARRAYOS DEFECTUOSO | 2 X 80 Y 2 X 100 EN C/L SE REMOVIO PARARRAYO AVERIADO | R23052300058 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 93 | 2023-05-23 | 49011 | keep | 0 | May | 2023 | 0.033381 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
ARECIBO | 2023-05-23 14:12 | 2023-05-23 15:59 | 1 | 1:47 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052300123 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 107 | 2023-05-23 | 107 | keep | 0 | May | 2023 | 7.2877e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-23 14:16 | 2023-05-23 15:13 | 75 | 0:57 | P | ANIMAL | 1 X 40 EN C/L CRUCE POR AVE | R23052300062 | New_Event | Animals | Include | Include | Wildlife | 57 | 2023-05-23 | 4275 | keep | 0 | May | 2023 | 0.0029117 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-05-23 14:26 | 2023-05-23 16:55 | 80 | 2:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 Y 1 X 30 EN CORTES DE LINEA DISTINTOS SE REMPLAZO PORTAFUSIBLE QUEMADO | M23052300075 | New_Event | Cutout Failure | Include | Include | Equipment | 149 | 2023-05-23 | 11920 | keep | 0 | May | 2023 | 0.0081187 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
VEGA BAJA | 2023-05-23 14:34 | 2023-05-23 16:35 | 100 | 2:01 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052300130 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 121 | 2023-05-23 | 12100 | keep | 0 | May | 2023 | 0.0082413 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-23 14:35 | 2023-05-23 15:31 | 2 | 0:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REMPLAZARON CONECTORES SECUNDARIOS SE BAJO TAP DE 4 A 1 SE BAJO A 123 POR FASE | B23052300185 | New_Event | Secondary Wire Break | Include | Include | Equipment | 56 | 2023-05-23 | 112 | keep | 0 | May | 2023 | 7.6283e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-05-23 14:36 | 2023-05-23 16:35 | 50 | 1:59 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052300132 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 119 | 2023-05-23 | 5950 | keep | 0 | May | 2023 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-05-23 14:42 | 2023-05-23 16:00 | 60 | 1:18 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO ENREDADERA SOBRE LAS LINEAS | A23052300133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 78 | 2023-05-23 | 4680 | keep | 0 | May | 2023 | 0.0031875 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-23 14:45 | 2023-05-23 18:57 | 1 | 4:12 | P | PROBLEMA DEL CLIENTE | 3 X 80 EN BOVEDA DEL CLIENTE | S23052300154 | New_Event | Customer-Related Interruption | Include | Include | Public | 252 | 2023-05-23 | 252 | keep | 0 | May | 2023 | 0.00017164 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-23 15:05 | 2023-05-23 15:06 | 2020 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 90% DE SU CARGA POR EL 1658-14 | R2305230000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 2020 | keep | 0 | May | 2023 | 0.0013758 | 0.0013758 | Momentary | FALSE | FALSE | Not_TMED_Event | 2020
CANOVANAS | 2023-05-23 15:05 | 2023-05-23 15:06 | 1 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA 90% DE LA CARGA DEL 1658-13 | R2305230000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-23 | 1 | keep | 0 | May | 2023 | 6.811e-07 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-23 15:12 | 2023-05-23 17:17 | 50 | 2:05 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L | B23052300193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 125 | 2023-05-23 | 6250 | keep | 0 | May | 2023 | 0.0042568 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-23 15:15 | 2023-05-23 16:11 | 10 | 0:56 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | S23052300163 | New_Event | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-05-23 | 560 | keep | 0 | May | 2023 | 0.00038141 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-05-23 15:18 | 2023-05-23 18:10 | 60 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052300083 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2023-05-23 | 10320 | keep | 0 | May | 2023 | 0.0070289 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
ARECIBO | 2023-05-23 15:19 | 2023-05-23 18:45 | 60 | 3:26 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052300139 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 206 | 2023-05-23 | 12360 | keep | 0 | May | 2023 | 0.0084183 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-23 15:21 | 2023-05-23 18:50 | 6 | 3:29 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23052300164 | New_Event | Secondary Wire Break | Include | Include | Equipment | 209 | 2023-05-23 | 1254 | keep | 0 | May | 2023 | 0.00085409 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-05-23 15:21 | 2023-05-23 17:38 | 4 | 2:17 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE MONTURA DE TRANSFORMADORES | A23052300140 | New_Event | Primary Wire Break | Include | Include | Equipment | 137 | 2023-05-23 | 548 | keep | 0 | May | 2023 | 0.00037324 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CAGUAS | 2023-05-23 15:28 | 2023-05-23 17:28 | 8 | 2:00 | P | CAUSAS EXTERNAS | SE ABRIO XMR PARA REPARAR SECUNDARIA A CAUSA DE IMPACTO DE CAMION SE QUEDA PENDIENTE PARA CONTINUAR MANANA. SE CERRO EL XMR. | C23052300197 | New_Event | Damage From Public | Include | Include | Public | 120 | 2023-05-23 | 960 | keep | 0 | May | 2023 | 0.00065385 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
GUAYAMA | 2023-05-23 15:30 | 2023-05-23 16:31 | 100 | 1:01 | P | DESCONECTIVO DEFECTUOSO | SE REMPLAZO MACHETE QUEMADO | P23052300298 | New_Event | Switch Failure | Include | Include | Equipment | 61 | 2023-05-23 | 6100 | keep | 0 | May | 2023 | 0.0041547 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-23 15:34 | 2023-05-23 15:53 | 85 | 0:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REMEPLAZO PORTAFUSIBLE | C23052300223 | New_Event | Cutout Failure | Include | Include | Equipment | 19 | 2023-05-23 | 1615 | keep | 0 | May | 2023 | 0.0011 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
VEGA BAJA | 2023-05-23 15:36 | 2023-05-23 16:16 | 4702 | 0:40 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR Y SE CERRO POR SCADA 30% EN SERVICIO | B23052300201 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 40 | 2023-05-23 | 188080 | keep | 0 | May | 2023 | 0.1281 | 0.0032025 | Sustained | FALSE | FALSE | Not_TMED_Event | 4702
BARRANQUITAS | 2023-05-23 15:49 | 2023-05-23 17:37 | 1246 | 1:48 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO CIERRA POR CONTROL. SE CERRO EN EL CAMPO. | C23052300227 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 108 | 2023-05-23 | 134568 | keep | 0 | May | 2023 | 0.091654 | 0.00084864 | Sustained | FALSE | FALSE | Not_TMED_Event | 1246
ARECIBO | 2023-05-23 15:53 | 2023-05-23 18:40 | 20 | 2:47 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052300141 | New_Event | Vegetation Contact | Include | Include | Vegetation | 167 | 2023-05-23 | 3340 | keep | 0 | May | 2023 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-23 15:54 | 2023-05-23 17:00 | 30 | 1:06 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23052300303 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-05-23 | 1980 | keep | 0 | May | 2023 | 0.0013486 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-23 15:57 | 2023-05-23 16:29 | 2450 | 0:32 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE LA 2605-00 A PETICION DE PERSONAL DE CAMPO Y CCE PARA REALIZAR OPERACIONES A NIVEL DE TRANSMISION EN LA LINEA 12600. VIA LIBRE PARA REPARAR PUENTES ABIERTOS. | C23052300229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 32 | 2023-05-23 | 78400 | keep | 0 | May | 2023 | 0.053398 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-05-23 15:57 | 2023-05-23 16:29 | 640 | 0:32 | T | LINEA DE TRANSMISION 38KV | SE RETIRO CARGA DE LA 2605-00 A PETICION DE PERSONAL DE CAMPO Y CCE PARA REALIZAR OPERACIONES A NIVEL DE TRANSMISION EN LA LINEA 12600. VIA LIBRE PARA REPARAR PUENTES ABIERTOS. | C23052300230 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 32 | 2023-05-23 | 20480 | keep | 0 | May | 2023 | 0.013949 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
PONCE | 2023-05-23 16:01 | 2023-05-23 17:00 | 10 | 0:59 | P | MAL TIEMPO/RAYOS | 1 X 15 EN XMR MAL TIEMPO RAYOS | P23052300305 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 59 | 2023-05-23 | 590 | keep | 0 | May | 2023 | 0.00040185 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-23 16:03 | 2023-05-24 09:37 | 40 | 17:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO | C23052300235 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1054 | 2023-05-23 | 42160 | keep | 0 | May | 2023 | 0.028715 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-05-23 16:11 | 2023-05-23 17:04 | 527 | 0:53 | T | MAL TIEMPO/RAYOS | SE CERRO INTERRUPTOR MANUAL ELECTRICO (RTU FUERA DE SERVICIO) MAL TIEMPO DESCARGAS ELECTRICAS EN EL AREA | M23052300099 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 53 | 2023-05-23 | 27931 | keep | 0 | May | 2023 | 0.019024 | 0.00035894 | Sustained | FALSE | FALSE | Not_TMED_Event | 527
MAYAGÃœEZ | 2023-05-23 16:16 | 2023-05-23 17:45 | 60 | 1:29 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052300104 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 89 | 2023-05-23 | 5340 | keep | 0 | May | 2023 | 0.003637 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-05-23 16:16 | 2023-05-23 17:48 | 3291 | 1:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZO AISLADOR PARTIDO Y SE CERRO MACHETES 99% EN SERVICIO | B23052300201 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 92 | 2023-05-23 | 302772 | keep | 0 | May | 2023 | 0.20622 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-23 16:28 | 2023-05-23 19:29 | 200 | 3:01 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | B23052300244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 181 | 2023-05-23 | 36200 | keep | 0 | May | 2023 | 0.024656 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 2231 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 2231 | keep | 0 | May | 2023 | 0.0015195 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 1923 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 1923 | keep | 0 | May | 2023 | 0.0013097 | 0.0013097 | Momentary | FALSE | FALSE | Not_TMED_Event | 1923
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 1066 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 1066 | keep | 0 | May | 2023 | 0.00072605 | 0.00072605 | Momentary | FALSE | FALSE | Not_TMED_Event | 1066
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 141 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300143 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 141 | keep | 0 | May | 2023 | 9.6034e-05 | 9.6034e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 141
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 1879 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 1879 | keep | 0 | May | 2023 | 0.0012798 | 0.0012798 | Momentary | FALSE | FALSE | Not_TMED_Event | 1879
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 2777 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 2777 | keep | 0 | May | 2023 | 0.0018914 | 0.0018914 | Momentary | FALSE | FALSE | Not_TMED_Event | 2777
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 2 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300144 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 2 | keep | 0 | May | 2023 | 1.3622e-06 | 1.3622e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 2
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 2839 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300145 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 2839 | keep | 0 | May | 2023 | 0.0019336 | 0.0019336 | Momentary | FALSE | FALSE | Not_TMED_Event | 2839
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 1160 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300145 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 1160 | keep | 0 | May | 2023 | 0.00079007 | 0.00079007 | Momentary | FALSE | FALSE | Not_TMED_Event | 1160
VEGA BAJA | 2023-05-23 16:31 | 2023-05-23 16:32 | 1860 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 2200 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | A23052300145 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-23 | 1860 | keep | 0 | May | 2023 | 0.0012668 | 0.0012668 | Momentary | FALSE | FALSE | Not_TMED_Event | 1860
VEGA BAJA | 2023-05-23 16:32 | 2023-05-24 16:35 | 1 | 24:03 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS RELACIONADO A EVENTO A23052200185 | A23052200185 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 1443 | 2023-05-23 | 1443 | keep | 0 | May | 2023 | 0.00098282 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-23 16:35 | 2023-05-23 18:11 | 31 | 1:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L LLUVIA FUERTE | B23052300256 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 96 | 2023-05-23 | 2976 | keep | 0 | May | 2023 | 0.0020269 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
CAGUAS | 2023-05-23 16:45 | 2023-05-23 16:54 | 10 | 0:09 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO SECUNDARIA | C23052300215 | New_Event | Secondary Wire Break | Include | Include | Equipment | 9 | 2023-05-23 | 90 | keep | 0 | May | 2023 | 6.1299e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-23 16:47 | 2023-05-23 18:02 | 2366 | 1:15 | T | MAL TIEMPO/RAYOS | SE CERRO INTERRUPTOR MANUAL ELECTRICO DESCARGAS ELECTRICAS EN EL AREA | M23052300133 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2023-05-23 | 177450 | keep | 0 | May | 2023 | 0.12086 | 0.0016115 | Sustained | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2023-05-23 16:49 | 2023-05-23 18:45 | 25 | 1:56 | P | MAL TIEMPO/RAYOS | 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052300138 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 116 | 2023-05-23 | 2900 | keep | 0 | May | 2023 | 0.0019752 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
FAJARDO | 2023-05-23 16:52 | 2023-05-23 18:08 | 6 | 1:16 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23052300076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 76 | 2023-05-23 | 456 | keep | 0 | May | 2023 | 0.00031058 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-23 17:01 | 2023-05-24 18:16 | 72 | 25:15 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23052300322 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1515 | 2023-05-23 | 109080 | keep | 0 | May | 2023 | 0.074294 | 4.9039e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 72
BAYAMON | 2023-05-23 17:02 | 2023-05-23 18:37 | 40 | 1:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L LLUVIA FUERTE | B23052300323 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 95 | 2023-05-23 | 3800 | keep | 0 | May | 2023 | 0.0025882 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-23 17:12 | 2023-05-23 21:47 | 14 | 4:35 | P | EMPALME SOTERRADO AVERIADO | SE REMPLAZARON PISTOLAS EN CAJAS SECAS | S23052300133 | New_Event | UG Cable Splice Failure | Include | Include | Equipment | 275 | 2023-05-23 | 3850 | keep | 0 | May | 2023 | 0.0026222 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-05-23 17:25 | 2023-05-23 18:49 | 45 | 1:24 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23052300263 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-05-23 | 3780 | keep | 0 | May | 2023 | 0.0025745 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-05-23 17:33 | 2023-05-23 20:30 | 14 | 2:57 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052300203 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 177 | 2023-05-23 | 2478 | keep | 0 | May | 2023 | 0.0016878 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-05-23 17:41 | 2023-05-23 20:00 | 50 | 2:19 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052300157 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-23 | 6950 | keep | 0 | May | 2023 | 0.0047336 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
UTUADO | 2023-05-23 17:42 | 2023-05-23 20:15 | 40 | 2:33 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23052300158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-05-23 | 6120 | keep | 0 | May | 2023 | 0.0041683 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-23 17:48 | 2023-05-23 18:20 | 47 | 0:32 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 Y 2 X 65 EN C/L | B23052300201 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 32 | 2023-05-23 | 1504 | keep | 0 | May | 2023 | 0.0010244 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-23 17:51 | 2023-05-24 13:11 | 1 | 19:20 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE RETIRO PARARRAYO | B23052300416 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1160 | 2023-05-23 | 1160 | keep | 0 | May | 2023 | 0.00079007 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-23 18:05 | 2023-05-24 10:45 | 43 | 16:40 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | S23052300193 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1000 | 2023-05-23 | 43000 | keep | 0 | May | 2023 | 0.029287 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
HUMACAO | 2023-05-23 18:16 | 2023-05-23 18:50 | 10 | 0:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZO BAJANTE SECUNDARIO | C23052300264 | New_Event | Secondary Wire Break | Include | Include | Equipment | 34 | 2023-05-23 | 340 | keep | 0 | May | 2023 | 0.00023157 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-23 18:20 | 2023-05-23 21:36 | 50 | 3:16 | P | PARARRAYOS DEFECTUOSO | 1 X 100 2 X 40 EN C/L SE ELIMINO PARARRAYO | B23052300464 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 196 | 2023-05-23 | 9800 | keep | 0 | May | 2023 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-23 19:02 | 2023-05-23 20:14 | 6 | 1:12 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | R23052300082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 72 | 2023-05-23 | 432 | keep | 0 | May | 2023 | 0.00029423 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-23 19:40 | 2023-05-24 11:28 | 1 | 15:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | C23052300276 | New_Event | Secondary Wire Break | Include | Include | Equipment | 948 | 2023-05-23 | 948 | keep | 0 | May | 2023 | 0.00064568 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-23 19:42 | 2023-05-23 20:30 | 75 | 0:48 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23052300168 | New_Event | Cutout Failure | Include | Include | Equipment | 48 | 2023-05-23 | 3600 | keep | 0 | May | 2023 | 0.0024519 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-05-23 19:52 | 2023-05-23 20:35 | 25 | 0:43 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052300249 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 43 | 2023-05-23 | 1075 | keep | 0 | May | 2023 | 0.00073218 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-05-23 19:59 | 2023-05-24 11:35 | 20 | 15:36 | P | NO SE REPORTO CAUSA | 1SMU-20 X 40 EN SU-51 @ SU-5B1 | C23052300278 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 936 | 2023-05-23 | 18720 | keep | 0 | May | 2023 | 0.01275 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-23 20:02 | 2023-05-23 22:01 | 150 | 1:59 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 80 EN C/L SE REEMPLAZO AISLADOR | C23052300280 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 119 | 2023-05-23 | 17850 | keep | 0 | May | 2023 | 0.012158 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-23 20:30 | 2023-05-24 12:39 | 47 | 16:09 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYO | B23052300515 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 969 | 2023-05-23 | 45543 | keep | 0 | May | 2023 | 0.031019 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
BAYAMON | 2023-05-23 20:50 | 2023-05-23 20:51 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVANDO 9206-07 | B23052300524 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-23 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-23 20:50 | 2023-05-23 20:51 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-10 LLEVANDO 9206-07 | B23052300524 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
MAYAGÃœEZ | 2023-05-23 21:02 | 2023-05-24 12:22 | 10 | 15:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA ROTA | M23052300254 | New_Event | Secondary Wire Break | Include | Include | Equipment | 920 | 2023-05-23 | 9200 | keep | 0 | May | 2023 | 0.0062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-23 21:20 | 2023-05-23 23:00 | 8 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REEMPLAZAR 300' PIES DE 3/2 SECUNDARIO | B23052300494 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2023-05-23 | 800 | keep | 0 | May | 2023 | 0.00054488 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-23 21:54 | 2023-05-23 21:56 | 1058 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1424-08 LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 100% 1401-10 SE CERRO X CONTROL | S23052300212 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-23 | 2116 | keep | 0 | May | 2023 | 0.0014412 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-05-23 21:54 | 2023-05-23 21:56 | 1001 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1424-08 LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 100% 1401-10 SE CERRO X CONTROL | S23052300212 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-23 | 2002 | keep | 0 | May | 2023 | 0.0013636 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2023-05-23 21:54 | 2023-05-23 21:56 | 278 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1424-08 LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 100% 1401-10 SE CERRO X CONTROL | S23052300212 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-23 | 556 | keep | 0 | May | 2023 | 0.00037869 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-23 21:54 | 2023-05-23 21:56 | 1295 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1424-08 LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 100% 1401-10 SE CERRO X CONTROL | S23052300212 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-23 | 2590 | keep | 0 | May | 2023 | 0.001764 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-05-23 21:54 | 2023-05-23 21:56 | 9 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 LLEVA 100% 1401-10 SE CERRO X CONTROL | S23052300212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-23 | 18 | keep | 0 | May | 2023 | 1.226e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-05-23 21:56 | 2023-05-23 21:57 | 27 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 9206-10 LLEVANDO 9206-07 | B2305230000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-23 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
BAYAMON | 2023-05-23 21:56 | 2023-05-23 21:57 | 325 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 9206-10 LLEVANDO 9206-07 | B2305230000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-23 | 325 | keep | 0 | May | 2023 | 0.00022136 | 0.00022136 | Momentary | FALSE | FALSE | Not_TMED_Event | 325
UTUADO | 2023-05-23 22:02 | 2023-05-24 10:00 | 6 | 11:58 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052300181 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 718 | 2023-05-23 | 4308 | keep | 0 | May | 2023 | 0.0029342 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-23 22:03 | 2023-05-24 08:48 | 80 | 10:45 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | B23052300534 | New_Event | Vegetation Contact | Include | Include | Vegetation | 645 | 2023-05-23 | 51600 | keep | 0 | May | 2023 | 0.035145 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-23 22:03 | 2023-05-24 07:17 | 258 | 9:14 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23052300293 | New_Event | Vegetation Contact | Include | Include | Vegetation | 554 | 2023-05-23 | 142932 | keep | 0 | May | 2023 | 0.09735 | 0.00017572 | Sustained | FALSE | FALSE | Not_TMED_Event | 258
AGUADILLA | 2023-05-23 22:21 | 2023-05-24 10:57 | 4 | 12:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M23052300263 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 756 | 2023-05-23 | 3024 | keep | 0 | May | 2023 | 0.0020596 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
GUAYAMA | 2023-05-23 22:31 | 2023-05-24 15:20 | 6 | 16:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARARON CONEXIONES SECUNDARIAS | P23052400370 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1009 | 2023-05-23 | 6054 | keep | 0 | May | 2023 | 0.0041234 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-05-23 22:48 | 2023-05-24 09:30 | 1 | 10:42 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052300182 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 642 | 2023-05-23 | 642 | keep | 0 | May | 2023 | 0.00043726 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-23 22:54 | 2023-05-24 04:59 | 95 | 6:05 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTE SECCIONALIZANDO POSTE PRIMARIO EN EL SUELO. | C23052300295 | New_Event | Primary Pole Failure | Include | Include | Equipment | 365 | 2023-05-23 | 34675 | keep | 0 | May | 2023 | 0.023617 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
ARECIBO | 2023-05-24 01:52 | 2023-05-24 09:00 | 12 | 7:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN RISER SE REMPLAZO PORTAFUSIBLE AVERIADO | A23052400001 | New_Event | Cutout Failure | Include | Include | Equipment | 428 | 2023-05-24 | 5136 | keep | 0 | May | 2023 | 0.0034981 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-24 03:22 | 2023-05-24 07:00 | 12 | 3:38 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23052400001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 218 | 2023-05-24 | 2616 | keep | 0 | May | 2023 | 0.0017817 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-05-24 03:46 | 2023-05-24 10:05 | 70 | 6:19 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA REQUIERE DESGANCHE | A23052400005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2023-05-24 | 26530 | keep | 0 | May | 2023 | 0.018069 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-05-24 05:04 | 2023-05-24 11:55 | 17 | 6:51 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23052400002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2023-05-24 | 6987 | keep | 0 | May | 2023 | 0.0047588 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
VEGA BAJA | 2023-05-24 05:06 | 2023-05-24 05:07 | 1494 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | A23052400000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1494 | keep | 0 | May | 2023 | 0.0010176 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
HUMACAO | 2023-05-24 05:23 | 2023-05-24 14:05 | 30 | 8:42 | P | DESGANCHE | 1 X 40 Y 1 X50 EN C/L DESGANCHE | C23052400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 522 | 2023-05-24 | 15660 | keep | 0 | May | 2023 | 0.010666 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-05-24 06:00 | 2023-05-24 10:15 | 170 | 4:15 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | C23052400008 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2023-05-24 | 43350 | keep | 0 | May | 2023 | 0.029525 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
CAGUAS | 2023-05-24 06:05 | 2023-05-24 20:10 | 40 | 14:05 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23052400009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 845 | 2023-05-24 | 33800 | keep | 0 | May | 2023 | 0.023021 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-05-24 06:06 | 2023-05-24 06:07 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052400015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1352 | keep | 0 | May | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
UTUADO | 2023-05-24 06:29 | 2023-05-24 11:00 | 25 | 4:31 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052400007 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 271 | 2023-05-24 | 6775 | keep | 0 | May | 2023 | 0.0046144 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-24 06:31 | 2023-05-24 13:25 | 10 | 6:54 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052400004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 414 | 2023-05-24 | 4140 | keep | 0 | May | 2023 | 0.0028197 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
PONCE | 2023-05-24 06:33 | 2023-05-24 06:34 | 2379 | 0:01 | T | ANIMAL | RECIERRE | P23052400010 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-24 | 2379 | keep | 0 | May | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2023-05-24 06:34 | 2023-05-24 12:40 | 66 | 6:06 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P23052400012 | 1st_after_momentary | Animals | Include | Include | Wildlife | 366 | 2023-05-24 | 24156 | keep | 0 | May | 2023 | 0.016453 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
VEGA BAJA | 2023-05-24 06:44 | 2023-05-24 14:20 | 45 | 7:36 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23052400008 | New_Event | Animals | Include | Include | Wildlife | 456 | 2023-05-24 | 20520 | keep | 0 | May | 2023 | 0.013976 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
FAJARDO | 2023-05-24 06:55 | 2023-05-24 06:56 | 1234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052400004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1234 | keep | 0 | May | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
MAYAGÃœEZ | 2023-05-24 07:00 | 2023-05-24 11:40 | 11 | 4:40 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | M23052400006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 280 | 2023-05-24 | 3080 | keep | 0 | May | 2023 | 0.0020978 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BARRANQUITAS | 2023-05-24 07:08 | 2023-05-24 16:19 | 20 | 9:11 | P | DESGANCHE | SE ABRIO C/L PARA REALIZAR DESGANCHE | C23052400014 | New_Event | Vegetation Contact | Include | Include | Vegetation | 551 | 2023-05-24 | 11020 | keep | 0 | May | 2023 | 0.0075057 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-24 07:13 | 2023-05-24 10:28 | 1 | 3:15 | P | DESGANCHE | 1 X 20 EN CORTE DE LINEA SE HIZO DESGANCHE | P23052400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-05-24 | 195 | keep | 0 | May | 2023 | 0.00013281 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-24 07:17 | 2023-05-24 07:18 | 327 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA | C23052400016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 327 | keep | 0 | May | 2023 | 0.00022272 | 0.00022272 | Momentary | FALSE | FALSE | Not_TMED_Event | 327
SAN JUAN | 2023-05-24 07:22 | 2023-05-24 07:23 | 4944 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 4944 | keep | 0 | May | 2023 | 0.0033673 | 0.0033673 | Momentary | FALSE | FALSE | Not_TMED_Event | 4944
CAGUAS | 2023-05-24 07:39 | 2023-05-24 07:40 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-24 07:46 | 2023-05-24 11:51 | 226 | 4:05 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23052400019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-05-24 | 55370 | keep | 0 | May | 2023 | 0.037712 | 0.00015393 | Sustained | FALSE | FALSE | Not_TMED_Event | 226
HUMACAO | 2023-05-24 07:49 | 2023-05-24 12:40 | 1 | 4:51 | P | MAL TIEMPO/RAYOS | 1 X50 EN RISER RAYOS | C23052400071 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 291 | 2023-05-24 | 291 | keep | 0 | May | 2023 | 0.0001982 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-24 08:03 | 2023-05-24 10:53 | 42 | 2:50 | P | ANIMAL | 1 X 140 EN C/L CRUCE POR AVE | B23052400013 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-05-24 | 7140 | keep | 0 | May | 2023 | 0.004863 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
CAGUAS | 2023-05-24 08:06 | 2023-05-24 08:07 | 851 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 3103-02 LLEVANDO 50% 3102-01 | C2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 851 | keep | 0 | May | 2023 | 0.00057961 | 0.00057961 | Momentary | FALSE | FALSE | Not_TMED_Event | 851
CAGUAS | 2023-05-24 08:06 | 2023-05-24 08:07 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1922 | keep | 0 | May | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
CANOVANAS | 2023-05-24 08:09 | 2023-05-24 10:06 | 7 | 1:57 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | R23052400007 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-05-24 | 819 | keep | 0 | May | 2023 | 0.00055782 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-05-24 08:22 | 2023-05-24 12:45 | 200 | 4:23 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052400017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 263 | 2023-05-24 | 52600 | keep | 0 | May | 2023 | 0.035826 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-05-24 08:33 | 2023-05-24 11:10 | 4 | 2:37 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052400016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 157 | 2023-05-24 | 628 | keep | 0 | May | 2023 | 0.00042773 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-05-24 08:44 | 2023-05-24 10:53 | 8 | 2:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN TRANSFORMADOR MAL TIEMPO VIENTOS FUERTES | M23052400017 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 129 | 2023-05-24 | 1032 | keep | 0 | May | 2023 | 0.00070289 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-24 08:45 | 2023-05-24 14:16 | 80 | 5:31 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052400019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 331 | 2023-05-24 | 26480 | keep | 0 | May | 2023 | 0.018035 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-05-24 08:47 | 2023-05-24 08:48 | 4098 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052400012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 4098 | keep | 0 | May | 2023 | 0.0027911 | 0.0027911 | Momentary | FALSE | FALSE | Not_TMED_Event | 4098
GUAYAMA | 2023-05-24 08:49 | 2023-05-24 08:50 | 3718 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052400082 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 3718 | keep | 0 | May | 2023 | 0.0025323 | 0.0025323 | Momentary | FALSE | FALSE | Not_TMED_Event | 3718
PONCE | 2023-05-24 08:50 | 2023-05-24 14:10 | 97 | 5:20 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA PALOMA CRUZO FASE | P23052400052 | New_Event | Animals | Include | Include | Wildlife | 320 | 2023-05-24 | 31040 | keep | 0 | May | 2023 | 0.021141 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
CANOVANAS | 2023-05-24 08:54 | 2023-05-24 08:57 | 2891 | 0:03 | T | DESGANCHE | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | R23052400016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-05-24 | 8673 | keep | 0 | May | 2023 | 0.0059071 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
CANOVANAS | 2023-05-24 08:57 | 2023-05-24 09:53 | 50 | 0:56 | P | DESGANCHE | 2 X 25 EN CORTE DE LINEA DESGANCHE | R23052400017 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 56 | 2023-05-24 | 2800 | keep | 0 | May | 2023 | 0.0019071 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-24 09:10 | 2023-05-24 13:12 | 29 | 4:02 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23052400034 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 242 | 2023-05-24 | 7018 | keep | 0 | May | 2023 | 0.0047799 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
CANOVANAS | 2023-05-24 09:22 | 2023-05-24 11:30 | 50 | 2:08 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | R23052400022 | New_Event | Animals | Include | Include | Wildlife | 128 | 2023-05-24 | 6400 | keep | 0 | May | 2023 | 0.004359 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-24 09:25 | 2023-05-24 10:42 | 179 | 1:17 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | R23052400024 | New_Event | Animals | Include | Include | Wildlife | 77 | 2023-05-24 | 13783 | keep | 0 | May | 2023 | 0.0093875 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
BAYAMON | 2023-05-24 09:26 | 2023-05-24 11:05 | 3 | 1:39 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23052400024 | New_Event | Animals | Include | Include | Wildlife | 99 | 2023-05-24 | 297 | keep | 0 | May | 2023 | 0.00020229 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
GUAYAMA | 2023-05-24 09:32 | 2023-05-24 09:37 | 1945 | 0:05 | T | NO SE REPORTO CAUSA | DISPARO DE ALIMENTADOR SE CERRO POR CONTROL | P23052400075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 5 | 2023-05-24 | 9725 | keep | 0 | May | 2023 | 0.0066237 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
PONCE | 2023-05-24 09:34 | 2023-05-24 14:27 | 12 | 4:53 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | LINEA SECUNDARIA AVERIADA 1 X 5 EN TRANSFORMADOR | P23052400076 | New_Event | Secondary Wire Break | Include | Include | Equipment | 293 | 2023-05-24 | 3516 | keep | 0 | May | 2023 | 0.0023947 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
FAJARDO | 2023-05-24 09:39 | 2023-05-24 14:00 | 50 | 4:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA DESGANCHE | R23052400027 | New_Event | Vegetation Contact | Include | Include | Vegetation | 261 | 2023-05-24 | 13050 | keep | 0 | May | 2023 | 0.0088883 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-05-24 09:40 | 2023-05-24 11:01 | 3 | 1:21 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25KVA X 25KVA | B23052400033 | New_Event | Service Transformer Failure | Include | Include | Equipment | 81 | 2023-05-24 | 243 | keep | 0 | May | 2023 | 0.00016551 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-05-24 09:42 | 2023-05-24 13:56 | 1 | 4:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 C/L SE REMPLAZO CAJA PRIMARIA | S23052400029 | New_Event | Cutout Failure | Include | Include | Equipment | 254 | 2023-05-24 | 254 | keep | 0 | May | 2023 | 0.000173 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-24 09:45 | 2023-05-24 10:58 | 8 | 1:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR LINEAS SECUNDARIAS | M23052400014 | New_Event | Secondary Wire Break | Include | Include | Equipment | 73 | 2023-05-24 | 584 | keep | 0 | May | 2023 | 0.00039776 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-05-24 09:58 | 2023-05-24 11:00 | 2 | 1:02 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON DERRAME DE ACEITE 25 KVA X 25 KVA | A23052400046 | New_Event | Service Transformer Failure | Include | Include | Equipment | 62 | 2023-05-24 | 124 | keep | 0 | May | 2023 | 8.4456e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
GUAYAMA | 2023-05-24 09:59 | 2023-05-24 13:23 | 62 | 3:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | REEMPLAZO DE CAJA PRIMARIA EN TRANSFORMADOR 1 X 80 EN CORTE DE LINEA | P23052400089 | New_Event | Cutout Failure | Include | Include | Equipment | 204 | 2023-05-24 | 12648 | keep | 0 | May | 2023 | 0.0086145 | 4.2228e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-05-24 10:03 | 2023-05-24 13:38 | 28 | 3:35 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN C.L SE REEMPLAZO PARARRAYO | B23052400036 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 215 | 2023-05-24 | 6020 | keep | 0 | May | 2023 | 0.0041002 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
VEGA BAJA | 2023-05-24 10:18 | 2023-05-24 13:50 | 1 | 3:32 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052400027 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 212 | 2023-05-24 | 212 | keep | 0 | May | 2023 | 0.00014439 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-24 10:39 | 2023-05-24 14:10 | 6 | 3:31 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | S23052400039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 211 | 2023-05-24 | 1266 | keep | 0 | May | 2023 | 0.00086227 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-05-24 10:47 | 2023-05-24 17:05 | 15 | 6:18 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGA ELECTRICA | P23052400108 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 378 | 2023-05-24 | 5670 | keep | 0 | May | 2023 | 0.0038618 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-24 11:00 | 2023-05-24 16:30 | 4 | 5:30 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS EVENTO TRANSFERIDO | P23052400115 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 330 | 2023-05-24 | 1320 | keep | 0 | May | 2023 | 0.00089905 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
VEGA BAJA | 2023-05-24 11:04 | 2023-05-24 14:15 | 1 | 3:11 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR CULEBRA CRUZO BUSHING | A23052400042 | New_Event | Animals | Include | Include | Wildlife | 191 | 2023-05-24 | 191 | keep | 0 | May | 2023 | 0.00013009 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-24 11:07 | 2023-05-24 12:17 | 5 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO CONECTORES SECUNDARIO | B23052400048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-05-24 | 350 | keep | 0 | May | 2023 | 0.00023838 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-24 11:27 | 2023-05-24 11:30 | 72 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO 1404-07 LLEVA 5% POR 1404-07 CERRADO POR CONTROL | S23052400055 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-24 | 216 | keep | 0 | May | 2023 | 0.00014712 | 4.9039e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 72
SAN JUAN | 2023-05-24 11:27 | 2023-05-24 11:30 | 1357 | 0:03 | T | OTRAS CAUSAS | DISPARO 1404-07 LLEVA 5% DEL 1112-04 CERRADO POR SCADA | S23052400055 | New_Event | Other Causes | Include | Include | Other | 3 | 2023-05-24 | 4071 | keep | 0 | May | 2023 | 0.0027727 | 0.00092425 | Momentary | FALSE | FALSE | Not_TMED_Event | 1357
SAN JUAN | 2023-05-24 11:30 | 2023-05-24 15:47 | 1 | 4:17 | P | OTRAS CAUSAS | 2 X 50 2 X 40 SMU SE REMPLAZO PT DE MEDICION | S23052400068 | 1st_after_momentary | Other Causes | Include | Include | Other | 257 | 2023-05-24 | 257 | keep | 0 | May | 2023 | 0.00017504 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-24 11:30 | 2023-05-24 12:55 | 490 | 1:25 | P | DESGANCHE | SE ABRE MACHETE PARA ABRIR PUENTE Y CERRAR MACHETE SECCIONALIZAR TRAMO CON PUENTE ABIERTO Y HACER DESGANCHE | R23052400026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 85 | 2023-05-24 | 41650 | keep | 0 | May | 2023 | 0.028368 | 0.00033374 | Sustained | FALSE | FALSE | Not_TMED_Event | 490
AGUADILLA | 2023-05-24 11:35 | 2023-05-24 15:30 | 150 | 3:55 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA Y 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052400049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 235 | 2023-05-24 | 35250 | keep | 0 | May | 2023 | 0.024009 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-05-24 11:38 | 2023-05-24 15:25 | 50 | 3:47 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23052400006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-05-24 | 11350 | keep | 0 | May | 2023 | 0.0077304 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-24 11:40 | 2023-05-24 18:17 | 4 | 6:37 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | P23052400135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 397 | 2023-05-24 | 1588 | keep | 0 | May | 2023 | 0.0010816 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-24 11:43 | 2023-05-24 13:11 | 10 | 1:28 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L Y 1X 15 EN XMR | B23052400053 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 88 | 2023-05-24 | 880 | keep | 0 | May | 2023 | 0.00059936 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-24 11:45 | 2023-05-24 17:18 | 5 | 5:33 | P | DESGANCHE | 1 X 15 EN XMR Y DESGANCHE | S23052400085 | New_Event | Vegetation Contact | Include | Include | Vegetation | 333 | 2023-05-24 | 1665 | keep | 0 | May | 2023 | 0.001134 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-05-24 11:47 | 2023-05-24 13:00 | 1 | 1:13 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 25 KVA X 25 KVA | M23052400051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 73 | 2023-05-24 | 73 | keep | 0 | May | 2023 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-24 11:48 | 2023-05-24 18:09 | 5 | 6:21 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO CAJAS SECAS Y PISTOLA | S23052400059 | New_Event | UG Cable Fault | Include | Include | Equipment | 381 | 2023-05-24 | 1905 | keep | 0 | May | 2023 | 0.0012975 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-05-24 11:50 | 2023-05-24 16:16 | 49 | 4:26 | P | DESGANCHE | 1 X 40 Y 1 X 80 EN C/L | B23052400054 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-05-24 | 13034 | keep | 0 | May | 2023 | 0.0088774 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
VEGA BAJA | 2023-05-24 11:59 | 2023-05-24 14:00 | 90 | 2:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | B23052400056 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 121 | 2023-05-24 | 10890 | keep | 0 | May | 2023 | 0.0074171 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
BAYAMON | 2023-05-24 11:59 | 2023-05-24 14:15 | 58 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | B23052400057 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-05-24 | 7888 | keep | 0 | May | 2023 | 0.0053725 | 3.9504e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 58
VEGA BAJA | 2023-05-24 12:03 | 2023-05-24 19:20 | 28 | 7:17 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23052400058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 437 | 2023-05-24 | 12236 | keep | 0 | May | 2023 | 0.0083339 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
GUAYAMA | 2023-05-24 12:05 | 2023-05-24 12:06 | 4279 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052400149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 4279 | keep | 0 | May | 2023 | 0.0029144 | 0.0029144 | Momentary | FALSE | FALSE | Not_TMED_Event | 4279
GUAYAMA | 2023-05-24 12:05 | 2023-05-24 12:06 | 1173 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23052400149 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-24 | 1173 | keep | 0 | May | 2023 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2023-05-24 12:05 | 2023-05-24 12:06 | 215 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23052400149 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-24 | 215 | keep | 0 | May | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2023-05-24 12:05 | 2023-05-24 12:06 | 464 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE | P23052400149 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-24 | 464 | keep | 0 | May | 2023 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
SAN JUAN | 2023-05-24 12:17 | 2023-05-24 15:00 | 50 | 2:43 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | S23052400069 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 163 | 2023-05-24 | 8150 | keep | 0 | May | 2023 | 0.0055509 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-24 12:20 | 2023-05-24 12:22 | 1501 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 3002 | keep | 0 | May | 2023 | 0.0020446 | 0.0010223 | Momentary | FALSE | FALSE | Not_TMED_Event | 1501
BAYAMON | 2023-05-24 12:26 | 2023-05-24 17:04 | 8 | 4:38 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23052400063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2023-05-24 | 2224 | keep | 0 | May | 2023 | 0.0015148 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-24 12:27 | 2023-05-24 12:28 | 5809 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE DE INTERRUPTOR | B2305240000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-05-24 | 5809 | keep | 0 | May | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2023-05-24 12:30 | 2023-05-24 12:31 | 4079 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 10% DE SU CARGA POR EL 1801-02 | B2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 4079 | keep | 0 | May | 2023 | 0.0027782 | 0.0027782 | Momentary | FALSE | FALSE | Not_TMED_Event | 4079
BAYAMON | 2023-05-24 12:33 | 2023-05-24 17:26 | 5809 | 4:53 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE SECCIONALIZO Y SE REEMPLAZO MACHETE QUEMADO EN LA SALIDA Y SE CERRO POR SCADA BY-230524-02 | B23052400067 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 293 | 2023-05-24 | 1702037 | keep | 0 | May | 2023 | 1.1592 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
BAYAMON | 2023-05-24 12:39 | 2023-05-24 12:41 | 1514 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23052400068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 3028 | keep | 0 | May | 2023 | 0.0020624 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-05-24 12:41 | 2023-05-24 14:15 | 47 | 1:34 | P | MAL TIEMPO/RAYOS | 1 X 65 EN C/L MAL TIEMPO RAYO | B23052300515 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 94 | 2023-05-24 | 4418 | keep | 0 | May | 2023 | 0.0030091 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-24 12:42 | 2023-05-24 19:52 | 20 | 7:10 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | B23052400071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 430 | 2023-05-24 | 8600 | keep | 0 | May | 2023 | 0.0058574 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-24 12:53 | 2023-05-24 19:32 | 1 | 6:39 | P | ARBOL SOBRE LINEA | 2 X 100 EN C/L SE RETIRO ARBOL | S23052400076 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 399 | 2023-05-24 | 399 | keep | 0 | May | 2023 | 0.00027176 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-24 12:53 | 2023-05-24 16:13 | 30 | 3:20 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23052400081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 200 | 2023-05-24 | 6000 | keep | 0 | May | 2023 | 0.0040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-05-24 12:55 | 2023-05-24 16:52 | 123 | 3:57 | P | DESGANCHE | SE CERRO PUENTE PRIMARIO Y SE HIZO DESGANCHE | R23052400026 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 237 | 2023-05-24 | 29151 | keep | 0 | May | 2023 | 0.019855 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-24 12:59 | 2023-05-24 13:00 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 2466 | keep | 0 | May | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
SAN JUAN | 2023-05-24 13:01 | 2023-05-24 13:23 | 1 | 0:22 | P | NO SE REPORTO CAUSA | 1 X 40 EN BOVEDA Y 1 X 50 EN RISER | S23052400080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 22 | 2023-05-24 | 22 | keep | 0 | May | 2023 | 1.4984e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-24 13:01 | 2023-05-24 13:02 | 427 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23052400081 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 427 | keep | 0 | May | 2023 | 0.00029083 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
BAYAMON | 2023-05-24 13:01 | 2023-05-24 13:03 | 2466 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305240000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 4932 | keep | 0 | May | 2023 | 0.0033592 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
SAN JUAN | 2023-05-24 13:04 | 2023-05-24 13:05 | 761 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 761 | keep | 0 | May | 2023 | 0.00051831 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
BAYAMON | 2023-05-24 13:08 | 2023-05-24 21:08 | 20 | 8:00 | P | DESGANCHE | SE REALIZO DESGANCHE Y 2 X 100 EN C/L | S23052400089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 480 | 2023-05-24 | 9600 | keep | 0 | May | 2023 | 0.0065385 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-24 13:08 | 2023-05-24 13:09 | 2466 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305240000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 2466 | keep | 0 | May | 2023 | 0.0016796 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-05-24 13:10 | 2023-05-24 13:12 | 2735 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 5470 | keep | 0 | May | 2023 | 0.0037256 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
SAN JUAN | 2023-05-24 13:11 | 2023-05-24 14:30 | 1 | 1:19 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | S23052400090 | New_Event | Primary Wire Break | Include | Include | Equipment | 79 | 2023-05-24 | 79 | keep | 0 | May | 2023 | 5.3807e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-24 13:11 | 2023-05-24 13:15 | 3597 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | B23052400094 | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-24 | 14388 | keep | 0 | May | 2023 | 0.0097996 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-24 13:13 | 2023-05-24 14:26 | 2735 | 1:13 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTORSE CERRO POR SCADA SE CERRO ALIMENTADOR POR PARTES QUEDO EN SERVICIO BY-230524-03 | B23052400093 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-05-24 | 199655 | keep | 0 | May | 2023 | 0.13598 | 0.0018628 | Sustained | FALSE | FALSE | Not_TMED_Event | 2735
SAN JUAN | 2023-05-24 13:14 | 2023-05-24 13:15 | 427 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23052400097 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 427 | keep | 0 | May | 2023 | 0.00029083 | 0.00029083 | Momentary | FALSE | FALSE | Not_TMED_Event | 427
BAYAMON | 2023-05-24 13:15 | 2023-05-24 17:40 | 10 | 4:25 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L Y 1X 15 EN XMR | B23052400053 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 265 | 2023-05-24 | 2650 | keep | 0 | May | 2023 | 0.0018049 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-24 13:15 | 2023-05-24 13:50 | 1 | 0:35 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN C/L SE RETIRO PARARRAYO | B23052300416 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 35 | 2023-05-24 | 35 | keep | 0 | May | 2023 | 2.3838e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-24 13:17 | 2023-05-24 14:52 | 948 | 1:35 | T | DESGANCHE | SE RETIRO RAMAS Y SE CERRO POR SCADA | S23052500120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-05-24 | 90060 | keep | 0 | May | 2023 | 0.061339 | 0.00064568 | Sustained | FALSE | FALSE | Not_TMED_Event | 948
SAN JUAN | 2023-05-24 13:24 | 2023-05-24 13:26 | 867 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO 1115-05 CERRADO POR SCADA | S2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 1734 | keep | 0 | May | 2023 | 0.001181 | 0.00059051 | Momentary | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2023-05-24 13:39 | 2023-05-24 13:40 | 1984 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23052400113 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1984 | keep | 0 | May | 2023 | 0.0013513 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
YAUCO | 2023-05-24 13:39 | 2023-05-24 15:59 | 50 | 2:20 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | P23052400215 | New_Event | Animals | Include | Include | Wildlife | 140 | 2023-05-24 | 7000 | keep | 0 | May | 2023 | 0.0047677 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-24 13:46 | 2023-05-24 13:47 | 1210 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1210 | keep | 0 | May | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
CANOVANAS | 2023-05-24 13:49 | 2023-05-24 14:47 | 80 | 0:58 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23052400058 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 58 | 2023-05-24 | 4640 | keep | 0 | May | 2023 | 0.0031603 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-05-24 13:53 | 2023-05-24 14:15 | 1464 | 0:22 | T | DESGANCHE | ALIMENTADOR FUERA DE SERVICIO POR BAMBUA SOBRE LINEA | P23052400307 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-05-24 | 32208 | keep | 0 | May | 2023 | 0.021937 | 0.00099712 | Sustained | FALSE | FALSE | Not_TMED_Event | 1464
BAYAMON | 2023-05-24 13:53 | 2023-05-24 18:00 | 18 | 4:07 | P | DESGANCHE | 3 X 30 EN C/L DESGANCHE | B23052400120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 247 | 2023-05-24 | 4446 | keep | 0 | May | 2023 | 0.0030282 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-05-24 13:55 | 2023-05-24 21:15 | 6 | 7:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 20 EN XMR SE REPARO SECUNDARIA | S23052400122 | New_Event | Secondary Wire Break | Include | Include | Equipment | 440 | 2023-05-24 | 2640 | keep | 0 | May | 2023 | 0.0017981 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-24 13:56 | 2023-05-24 15:06 | 40 | 1:10 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | B23052400121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 70 | 2023-05-24 | 2800 | keep | 0 | May | 2023 | 0.0019071 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-24 14:04 | 2023-05-24 15:06 | 120 | 1:02 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052400126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-05-24 | 7440 | keep | 0 | May | 2023 | 0.0050674 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
CANOVANAS | 2023-05-24 14:11 | 2023-05-24 14:13 | 4188 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO CON PERSONAL EN EL AREA REALIZANDO V.L. INDICAN QUE SE PUEDE CERRAR INTERRUPTOR QUEDO EN SERVICIO | R23052400063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 8376 | keep | 0 | May | 2023 | 0.0057049 | 0.0028524 | Momentary | FALSE | FALSE | Not_TMED_Event | 4188
BAYAMON | 2023-05-24 14:26 | 2023-05-24 15:06 | 2050 | 0:40 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTORSE CERRO POR SCADA SE CERRO ALIMENTADOR POR PARTES QUEDO EN SERVICIO BY-230524-03 | B23052400093 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 40 | 2023-05-24 | 82000 | keep | 0 | May | 2023 | 0.05585 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-24 14:27 | 2023-05-24 17:47 | 7 | 3:20 | P | TRANSFORMADOR AVERIADO | TRANSFORMAFDOR 37.5 KVA A 7620 VOLTS QUEMADO | P23052400076 | New_Event | Service Transformer Failure | Include | Include | Equipment | 200 | 2023-05-24 | 1400 | keep | 0 | May | 2023 | 0.00095353 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2023-05-24 14:29 | 2023-05-24 19:40 | 30 | 5:11 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23052400076 | New_Event | Vegetation Contact | Include | Include | Vegetation | 311 | 2023-05-24 | 9330 | keep | 0 | May | 2023 | 0.0063546 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-24 14:30 | 2023-05-24 15:16 | 50 | 0:46 | P | CONDUCTOR ROTO O ABIERTO | SE EMPLAZO Y SE REPARO ALAMBRE Y SE CERRO PROVISIONAL | R23052400071 | New_Event | Primary Wire Break | Include | Include | Equipment | 46 | 2023-05-24 | 2300 | keep | 0 | May | 2023 | 0.0015665 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-05-24 14:39 | 2023-05-24 17:23 | 3 | 2:44 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052400086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 164 | 2023-05-24 | 492 | keep | 0 | May | 2023 | 0.0003351 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-24 15:00 | 2023-05-24 17:40 | 16 | 2:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23052400158 | New_Event | Secondary Wire Break | Include | Include | Equipment | 160 | 2023-05-24 | 2560 | keep | 0 | May | 2023 | 0.0017436 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
VEGA BAJA | 2023-05-24 15:06 | 2023-05-24 15:07 | 2132 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | A23052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 2132 | keep | 0 | May | 2023 | 0.0014521 | 0.0014521 | Momentary | FALSE | FALSE | Not_TMED_Event | 2132
VEGA BAJA | 2023-05-24 15:06 | 2023-05-24 15:07 | 2366 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | A23052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 2366 | keep | 0 | May | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
VEGA BAJA | 2023-05-24 15:06 | 2023-05-24 15:07 | 1976 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | A23052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 1976 | keep | 0 | May | 2023 | 0.0013458 | 0.0013458 | Momentary | FALSE | FALSE | Not_TMED_Event | 1976
VEGA BAJA | 2023-05-24 15:06 | 2023-05-24 15:07 | 3688 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | A23052300000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 3688 | keep | 0 | May | 2023 | 0.0025119 | 0.0025119 | Momentary | FALSE | FALSE | Not_TMED_Event | 3688
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 3070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 3070 | keep | 0 | May | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 2735 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 2735 | keep | 0 | May | 2023 | 0.0018628 | 0.0018628 | Momentary | FALSE | FALSE | Not_TMED_Event | 2735
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 1070 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400162 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 1070 | keep | 0 | May | 2023 | 0.00072877 | 0.00072877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1070
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 1647 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400159 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 1647 | keep | 0 | May | 2023 | 0.0011218 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 3295 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400159 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 3295 | keep | 0 | May | 2023 | 0.0022442 | 0.0022442 | Momentary | FALSE | FALSE | Not_TMED_Event | 3295
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 1180 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400159 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 1180 | keep | 0 | May | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 320 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400160 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 320 | keep | 0 | May | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
BAYAMON | 2023-05-24 15:06 | 2023-05-24 15:07 | 2234 | 0:01 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36100 TIENE DESGANCHES PENDIENTES DE REALIZAR SEGÃšN PATRULLAJE AÃ‰REO DEL 4/29/2023 Y 5/26/2023. | B23052400160 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-05-24 15:07 | 2023-05-25 12:19 | 24 | 21:12 | P | NO SE REPORTO CAUSA | 1 X 30 EN PROVISIONAL AEREO | B23052400161 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1272 | 2023-05-24 | 30528 | keep | 0 | May | 2023 | 0.020792 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2023-05-24 15:07 | 2023-05-24 15:36 | 20 | 0:29 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REGULAR VOLTAJE Y DESGANCHE SECUNDARIO | C23052400022 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 29 | 2023-05-24 | 580 | keep | 0 | May | 2023 | 0.00039504 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-24 15:07 | 2023-05-24 16:44 | 120 | 1:37 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052400126 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-05-24 | 11640 | keep | 0 | May | 2023 | 0.007928 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-24 15:07 | 2023-05-24 15:29 | 2050 | 0:22 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTORSE CERRO POR SCADA SE CERRO ALIMENTADOR POR PARTES QUEDO EN SERVICIO BY-230524-03 | B23052400093 | Partial_restoration | No Probable Cause Reported | Include | Include | Unknown | 22 | 2023-05-24 | 45100 | keep | 0 | May | 2023 | 0.030717 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-24 15:17 | 2023-05-25 06:43 | 80 | 15:26 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23052400143 | New_Event | Vegetation Contact | Include | Include | Vegetation | 926 | 2023-05-24 | 74080 | keep | 0 | May | 2023 | 0.050456 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-24 15:26 | 2023-05-24 18:05 | 10 | 2:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO POSTE Y LINEA SECUNDARIA | S23052400145 | New_Event | Secondary Wire Break | Include | Include | Equipment | 159 | 2023-05-24 | 1590 | keep | 0 | May | 2023 | 0.0010829 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
GUAYAMA | 2023-05-24 15:43 | 2023-05-24 18:20 | 627 | 2:37 | P | CONDUCTOR ROTO O ABIERTO | SE ABREN MACHETES PARA CERRAR PUENTE PRIMARIO Y REEMPLAZO DE AISLADOR | P23042400294 | New_Event | Primary Wire Break | Include | Include | Equipment | 157 | 2023-05-24 | 98439 | keep | 0 | May | 2023 | 0.067046 | 0.00042705 | Sustained | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2023-05-24 15:47 | 2023-05-24 16:36 | 411 | 0:49 | T | CONDUCTOR ROTO O ABIERTO | 100% EN SERVICIO SE CERRO PUENTE ABIERTO Y SE CERRO POR SCADA MEDIANTE SJ-230524-02. 1530-10 LLEVA 1924-03 | S23052400150 | New_Event | Primary Wire Break | Include | Include | Equipment | 49 | 2023-05-24 | 20139 | keep | 0 | May | 2023 | 0.013717 | 0.00027993 | Sustained | FALSE | FALSE | Not_TMED_Event | 411
BAYAMON | 2023-05-24 15:47 | 2023-05-24 16:36 | 5 | 0:49 | T | ALIMENTADOR AMARRADO | 1530-10 100% EN SERVICIO SE CERRO PUENTE ABIERTO Y SE CERRO POR SCADA MEDIANTE SJ-230524-02. 1530-10 LLEVA 1924-03 | S23052400150 | New_Event | Feeder Load Transferred | Include | Include | Other | 49 | 2023-05-24 | 245 | keep | 0 | May | 2023 | 0.00016687 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-24 15:48 | 2023-05-24 15:50 | 271 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | S23052400151 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 542 | keep | 0 | May | 2023 | 0.00036915 | 0.00018458 | Momentary | FALSE | FALSE | Not_TMED_Event | 271
BAYAMON | 2023-05-24 15:51 | 2023-05-24 15:52 | 4028 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 4028 | keep | 0 | May | 2023 | 0.0027435 | 0.0027435 | Momentary | FALSE | FALSE | Not_TMED_Event | 4028
MAYAGÃœEZ | 2023-05-24 15:51 | 2023-05-24 20:42 | 42 | 4:51 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REPARO LINEAS SECUNDARIAS CRUZADAS | M23052400108 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 291 | 2023-05-24 | 12222 | keep | 0 | May | 2023 | 0.0083243 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
VEGA BAJA | 2023-05-24 15:54 | 2023-05-24 16:02 | 2777 | 0:08 | T | AISLADOR ROTO, PARTIDO O SAFADO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR LINEA ZAFADA DE AISLADOR SOBRE CRUCETA DE METAL EN POSTE DE MADERA SE SECCIONALIZO LINEA SE CERRO INTERRUPTOR | A23052400051 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 8 | 2023-05-24 | 22216 | keep | 0 | May | 2023 | 0.015131 | 0.0018914 | Sustained | FALSE | FALSE | Not_TMED_Event | 2777
AGUADILLA | 2023-05-24 16:00 | 2023-05-24 22:55 | 3 | 6:55 | P | MAL TIEMPO/RAYOS | 1 X 20 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23052400278 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 415 | 2023-05-24 | 1245 | keep | 0 | May | 2023 | 0.00084796 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-05-24 16:02 | 2023-05-24 16:40 | 607 | 0:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REMPLAZO AISLADORES PARTIDOS SE CERRO CORTE DE LINEA | A23052400097 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 38 | 2023-05-24 | 23066 | keep | 0 | May | 2023 | 0.01571 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-24 16:03 | 2023-05-24 16:04 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S23052400153 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 733 | keep | 0 | May | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
YAUCO | 2023-05-24 16:10 | 2023-05-24 19:30 | 20 | 3:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052400308 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 200 | 2023-05-24 | 4000 | keep | 0 | May | 2023 | 0.0027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-24 16:17 | 2023-05-24 18:06 | 19 | 1:49 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23052400197 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-05-24 | 2071 | keep | 0 | May | 2023 | 0.0014105 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
UTUADO | 2023-05-24 16:30 | 2023-05-24 17:50 | 7 | 1:20 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO 25 KVA X 37.5 KVA | A23052400098 | New_Event | Service Transformer Failure | Include | Include | Equipment | 80 | 2023-05-24 | 560 | keep | 0 | May | 2023 | 0.00038141 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-24 16:33 | 2023-05-25 18:04 | 20 | 25:31 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | B23052400158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1531 | 2023-05-24 | 30620 | keep | 0 | May | 2023 | 0.020855 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-24 16:37 | 2023-05-24 20:00 | 8 | 3:23 | P | MAL TIEMPO/RAYOS | 2 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052400102 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 203 | 2023-05-24 | 1624 | keep | 0 | May | 2023 | 0.0011061 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-24 16:41 | 2023-05-24 16:45 | 7621 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE VERIFICO CON PERSONAL REALIZANDO VIA LIBRE Y CULMINARON Y SE PROCEDE A CERRAR INTERRUPTOR | R23052400083 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-24 | 30484 | keep | 0 | May | 2023 | 0.020763 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
HUMACAO | 2023-05-24 16:48 | 2023-05-24 17:28 | 40 | 0:40 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23052400140 | New_Event | Animals | Include | Include | Wildlife | 40 | 2023-05-24 | 1600 | keep | 0 | May | 2023 | 0.0010898 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BARRANQUITAS | 2023-05-24 17:11 | 2023-05-24 18:03 | 5 | 0:52 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23052400144 | New_Event | Secondary Wire Break | Include | Include | Equipment | 52 | 2023-05-24 | 260 | keep | 0 | May | 2023 | 0.00017708 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
ARECIBO | 2023-05-24 17:15 | 2023-05-24 18:40 | 10 | 1:25 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A23052400107 | New_Event | Animals | Include | Include | Wildlife | 85 | 2023-05-24 | 850 | keep | 0 | May | 2023 | 0.00057893 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-24 17:17 | 2023-05-24 18:53 | 1352 | 1:36 | T | ALIMENTADOR AMARRADO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA EN ALIMENTADOR 6014-03 SE CERRO INTERRUPTOR 6012-05 | M23052400121 | New_Event | Feeder Load Transferred | Include | Include | Other | 96 | 2023-05-24 | 129792 | keep | 0 | May | 2023 | 0.088401 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-05-24 17:17 | 2023-05-24 18:53 | 871 | 1:36 | T | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO LINEA PRIMARIA PARTIDA EN ALIMENTADOR 6014-03 SE CERRO INTERRUPTOR 6012-05 | M23052400121 | New_Event | Primary Wire Break | Include | Include | Equipment | 96 | 2023-05-24 | 83616 | keep | 0 | May | 2023 | 0.05695 | 0.00059323 | Sustained | FALSE | FALSE | Not_TMED_Event | 871
PONCE | 2023-05-24 17:30 | 2023-05-24 17:31 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052400XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 2379 | keep | 0 | May | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
UTUADO | 2023-05-24 17:30 | 2023-05-24 17:55 | 4 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23052400106 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-24 | 100 | keep | 0 | May | 2023 | 6.811e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BARRANQUITAS | 2023-05-24 17:34 | 2023-05-24 19:00 | 1 | 1:26 | P | DESGANCHE | 2 X 30 EN C/L DESGANCHE | C23052400147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-05-24 | 86 | keep | 0 | May | 2023 | 5.8574e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-24 17:43 | 2023-05-24 17:44 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052400XX | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
VEGA BAJA | 2023-05-24 17:52 | 2023-05-24 21:00 | 100 | 3:08 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | B23052400261 | New_Event | Vegetation Contact | Include | Include | Vegetation | 188 | 2023-05-24 | 18800 | keep | 0 | May | 2023 | 0.012805 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-24 18:09 | 2023-05-24 18:13 | 1058 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL REALIZANDO OPERACIONES DISPARO EL ALIMENTADO 1424-08 20% POR 1424-08 | S2305240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-24 | 4232 | keep | 0 | May | 2023 | 0.0028824 | 0.0007206 | Momentary | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-05-24 18:09 | 2023-05-24 18:13 | 1000 | 0:04 | P | CABLE SOTERRADO AVERIADO | DISPARO DEL 1424-08 CERRADO POR CONTROL REALIZANDO OPERACIONES DISPARO EL ALIMENTADO 1424-08 80 % POR 1424-08 | S2305240000X | Additional_clients | UG Cable Fault | Include | Include | Equipment | 4 | 2023-05-24 | 4000 | keep | 0 | May | 2023 | 0.0027244 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-24 18:09 | 2023-05-24 18:13 | 278 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL REALIZANDO OPERACIONES DISPARO EL ALIMENTADO 1424-08 100% POR 1424-08 | S2305240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-24 | 1112 | keep | 0 | May | 2023 | 0.00075738 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-24 18:09 | 2023-05-24 18:13 | 1295 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1424-08 CERRADO POR CONTROL REALIZANDO OPERACIONES DISPARO EL ALIMENTADO 1424-08 100% POR 1424-08 | S2305240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-24 | 5180 | keep | 0 | May | 2023 | 0.0035281 | 0.00088202 | Momentary | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-05-24 18:09 | 2023-05-24 18:13 | 9 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL LLEVA 100% 1348-07 LLEVA 80% 1348-06 LLEVA 20% 1336-08 | S2305240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-24 | 36 | keep | 0 | May | 2023 | 2.4519e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-05-24 18:13 | 2023-05-24 20:32 | 5 | 2:19 | P | CABLE SOTERRADO AVERIADO | SE REMPLAZO CAJAS SECAS Y PISTOLA | S23052400059 | 1st_after_momentary | UG Cable Fault | Include | Include | Equipment | 139 | 2023-05-24 | 695 | keep | 0 | May | 2023 | 0.00047336 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CANOVANAS | 2023-05-24 18:15 | 2023-05-24 18:16 | 1894 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052400094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1894 | keep | 0 | May | 2023 | 0.00129 | 0.00129 | Momentary | FALSE | FALSE | Not_TMED_Event | 1894
CANOVANAS | 2023-05-24 18:15 | 2023-05-24 18:16 | 4154 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052400093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 4154 | keep | 0 | May | 2023 | 0.0028293 | 0.0028293 | Momentary | FALSE | FALSE | Not_TMED_Event | 4154
VEGA BAJA | 2023-05-24 18:21 | 2023-05-24 20:20 | 30 | 1:59 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052400114 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 119 | 2023-05-24 | 3570 | keep | 0 | May | 2023 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-24 18:27 | 2023-05-25 17:28 | 30 | 23:01 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 DE RISER @ SU-6 MAL TIEMPO LLUVIAS | B23052400282 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1381 | 2023-05-24 | 41430 | keep | 0 | May | 2023 | 0.028218 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-24 18:28 | 2023-05-24 18:29 | 1514 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23052400291 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 1514 | keep | 0 | May | 2023 | 0.0010312 | 0.0010312 | Momentary | FALSE | FALSE | Not_TMED_Event | 1514
BAYAMON | 2023-05-24 18:28 | 2023-05-24 18:29 | 1105 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23052400291 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 1105 | keep | 0 | May | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
BAYAMON | 2023-05-24 18:28 | 2023-05-24 18:29 | 4176 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23052400292 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 4176 | keep | 0 | May | 2023 | 0.0028443 | 0.0028443 | Momentary | FALSE | FALSE | Not_TMED_Event | 4176
BAYAMON | 2023-05-24 18:28 | 2023-05-24 18:29 | 252 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23052400292 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 252 | keep | 0 | May | 2023 | 0.00017164 | 0.00017164 | Momentary | FALSE | FALSE | Not_TMED_Event | 252
BAYAMON | 2023-05-24 18:28 | 2023-05-24 18:29 | 2147 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23052400292 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 2147 | keep | 0 | May | 2023 | 0.0014623 | 0.0014623 | Momentary | FALSE | FALSE | Not_TMED_Event | 2147
BAYAMON | 2023-05-24 18:28 | 2023-05-24 18:29 | 2858 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 10000 | B23052400294 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 2858 | keep | 0 | May | 2023 | 0.0019466 | 0.0019466 | Momentary | FALSE | FALSE | Not_TMED_Event | 2858
UTUADO | 2023-05-24 18:30 | 2023-05-24 19:20 | 1 | 0:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA | A23052400116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 50 | 2023-05-24 | 50 | keep | 0 | May | 2023 | 3.4055e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-24 18:33 | 2023-05-25 09:58 | 10 | 15:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25, 1 X 20 BANCO 1 X 40 C/L MAL TIEMPO LLUVIAS | S23052400185 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 925 | 2023-05-24 | 9250 | keep | 0 | May | 2023 | 0.0063001 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-24 18:36 | 2023-05-24 18:37 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305240000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
HUMACAO | 2023-05-24 18:46 | 2023-05-25 11:06 | 16 | 16:20 | P | TRANSFORMADOR AVERIADO | CG-230525-01 SE REEMPLAZO XMR AVERIADO | C23052400156 | New_Event | Service Transformer Failure | Include | Include | Equipment | 980 | 2023-05-24 | 15680 | keep | 0 | May | 2023 | 0.01068 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
SAN JUAN | 2023-05-24 18:50 | 2023-05-25 09:47 | 100 | 14:57 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23052400187 | New_Event | Vegetation Contact | Include | Include | Vegetation | 897 | 2023-05-24 | 89700 | keep | 0 | May | 2023 | 0.061094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-24 18:51 | 2023-05-25 11:36 | 7 | 16:45 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25 KVA POR UNO DE 50 KVA | C23052400157 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1005 | 2023-05-24 | 7035 | keep | 0 | May | 2023 | 0.0047915 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
MAYAGÃœEZ | 2023-05-24 18:53 | 2023-05-24 21:50 | 150 | 2:57 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PARTIDO | M23052400215 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 177 | 2023-05-24 | 26550 | keep | 0 | May | 2023 | 0.018083 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-24 18:56 | 2023-05-25 11:26 | 65 | 16:30 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23052400191 | New_Event | Vegetation Contact | Include | Include | Vegetation | 990 | 2023-05-24 | 64350 | keep | 0 | May | 2023 | 0.043828 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
SAN JUAN | 2023-05-24 18:57 | 2023-05-25 12:42 | 35 | 17:45 | P | CAUSAS EXTERNAS | CAMION IMPACTA POSTE Y LINEAS SE CRUZAN SE RETEZO PRIMARIA Y SE REPUSO 1X80 EN C/L. | S23052400192 | New_Event | Damage From Public | Include | Include | Public | 1065 | 2023-05-24 | 37275 | keep | 0 | May | 2023 | 0.025388 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-24 19:00 | 2023-05-24 20:16 | 5809 | 1:16 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO SE CERRO INTERRUPTOR BY-230524-04 | B23052400317 | New_Event | Primary Wire Break | Include | Include | Equipment | 76 | 2023-05-24 | 441484 | keep | 0 | May | 2023 | 0.30069 | 0.0039565 | Sustained | FALSE | FALSE | Not_TMED_Event | 5809
GUAYAMA | 2023-05-24 19:00 | 2023-05-24 20:05 | 55 | 1:05 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA DESCARGA ELECTRICA TRABAJO CON WR 6320981 | P23052400000 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 65 | 2023-05-24 | 3575 | keep | 0 | May | 2023 | 0.0024349 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
AGUADILLA | 2023-05-24 19:07 | 2023-05-24 19:08 | 2225 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23052400139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 2225 | keep | 0 | May | 2023 | 0.0015154 | 0.0015154 | Momentary | FALSE | FALSE | Not_TMED_Event | 2225
VEGA BAJA | 2023-05-24 19:13 | 2023-05-24 21:10 | 60 | 1:57 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 1 X 25 EN CORTES DE LINEA DISTINTOS MAL TIEMPO DESCARGAS ELECTRICAS | A23052400126 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 117 | 2023-05-24 | 7020 | keep | 0 | May | 2023 | 0.0047813 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-05-24 19:15 | 2023-05-24 19:16 | 990 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23052400147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 990 | keep | 0 | May | 2023 | 0.00067428 | 0.00067428 | Momentary | FALSE | FALSE | Not_TMED_Event | 990
UTUADO | 2023-05-24 19:18 | 2023-05-25 15:26 | 25 | 20:08 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO LINEA PRIMARIA PARTIDA | A23052400128 | New_Event | Primary Wire Break | Include | Include | Equipment | 1208 | 2023-05-24 | 30200 | keep | 0 | May | 2023 | 0.020569 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
MAYAGÃœEZ | 2023-05-24 19:19 | 2023-05-24 23:55 | 150 | 4:36 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA QUEMADA EN RISER | M23052400143 | New_Event | Cutout Failure | Include | Include | Equipment | 276 | 2023-05-24 | 41400 | keep | 0 | May | 2023 | 0.028197 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-24 19:24 | 2023-05-25 11:15 | 7 | 15:51 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23052400199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 951 | 2023-05-24 | 6657 | keep | 0 | May | 2023 | 0.0045341 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
VEGA BAJA | 2023-05-24 19:35 | 2023-05-25 08:05 | 50 | 12:30 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A23052400136 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 750 | 2023-05-24 | 37500 | keep | 0 | May | 2023 | 0.025541 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-24 19:36 | 2023-05-24 19:37 | 1588 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1716-03 LLEVA 1711-01, 1711-03 | B23052400352 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-24 | 1588 | keep | 0 | May | 2023 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-05-24 19:36 | 2023-05-24 19:37 | 13 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1716-03 LLEVA 1711-01, 1711-03 | B23052400352 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-24 | 13 | keep | 0 | May | 2023 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-05-24 19:36 | 2023-05-24 19:37 | 1812 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 1716-03 LLEVA 1711-01, 1711-03 | B23052400352 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-24 | 1812 | keep | 0 | May | 2023 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
SAN JUAN | 2023-05-24 19:45 | 2023-05-25 09:44 | 80 | 13:59 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23052400203 | New_Event | Primary Wire Break | Include | Include | Equipment | 839 | 2023-05-24 | 67120 | keep | 0 | May | 2023 | 0.045715 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-24 19:51 | 2023-05-24 21:45 | 1943 | 1:54 | T | DESCONECTIVO DEFECTUOSO | SE TRANSFIRIO CARGA AL 7006-03 POR MACHETE QUEMADO EN TRONCAL DEL 7006-01 | M23052400180 | New_Event | Switch Failure | Include | Include | Equipment | 114 | 2023-05-24 | 221502 | keep | 0 | May | 2023 | 0.15086 | 0.0013234 | Sustained | FALSE | FALSE | Not_TMED_Event | 1943
UTUADO | 2023-05-24 20:02 | 2023-05-24 20:05 | 3502 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR CON RECIERRE EN ON NO RECERRO SE CERRO POR CONTROL SCADA | A23052400145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-24 | 10506 | keep | 0 | May | 2023 | 0.0071556 | 0.0023852 | Momentary | FALSE | FALSE | Not_TMED_Event | 3502
BAYAMON | 2023-05-24 20:03 | 2023-05-25 11:23 | 10 | 15:20 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | B23052400365 | New_Event | Primary Wire Break | Include | Include | Equipment | 920 | 2023-05-24 | 9200 | keep | 0 | May | 2023 | 0.0062661 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-24 20:12 | 2023-05-25 02:45 | 120 | 6:33 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO BAMBU | M23052400210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 393 | 2023-05-24 | 47160 | keep | 0 | May | 2023 | 0.03212 | 8.1731e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 120
BAYAMON | 2023-05-24 20:16 | 2023-05-24 21:04 | 871 | 0:48 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y ENTRO 85% EN SERVICIO BY-230524-04 | B23052400317 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 48 | 2023-05-24 | 41808 | keep | 0 | May | 2023 | 0.028475 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-24 20:23 | 2023-05-24 22:18 | 350 | 1:55 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 2 X 65 EN CORTES DE LINEA MAL TIEMPO RAYOS | B23052400384 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 115 | 2023-05-24 | 40250 | keep | 0 | May | 2023 | 0.027414 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
BAYAMON | 2023-05-24 20:26 | 2023-05-25 05:56 | 65 | 9:30 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA | B23052400392 | New_Event | Vegetation Contact | Include | Include | Vegetation | 570 | 2023-05-24 | 37050 | keep | 0 | May | 2023 | 0.025235 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
MAYAGÃœEZ | 2023-05-24 20:30 | 2023-05-24 20:32 | 4381 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DEL INTERRUPTOR NO RECERRO NO SE REPORTO CAUSA SE CERRO POR SCADA | M23052400232 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-24 | 8762 | keep | 0 | May | 2023 | 0.0059678 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
MAYAGÃœEZ | 2023-05-24 20:32 | 2023-05-25 09:26 | 30 | 12:54 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23052400222 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 774 | 2023-05-24 | 23220 | keep | 0 | May | 2023 | 0.015815 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-24 21:04 | 2023-05-24 21:06 | 5809 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR HACIENDO OPERACIONES BUSCANDO AVERIA BY-230524-04 PUENTE ABIERTO | B23052400317 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-24 | 11618 | keep | 0 | May | 2023 | 0.007913 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-24 21:06 | 2023-05-24 23:39 | 855 | 2:33 | P | CONDUCTOR ROTO O ABIERTO | BY230524-04 SE CERRO PUENTE DE LINEA A LINEA | B23052400317 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 153 | 2023-05-24 | 130815 | keep | 0 | May | 2023 | 0.089098 | 0.00058234 | Sustained | FALSE | FALSE | Not_TMED_Event | 855
PONCE | 2023-05-24 21:13 | 2023-05-24 22:30 | 25 | 1:17 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA QUEMADA EN C/L | P23052400333 | New_Event | Cutout Failure | Include | Include | Equipment | 77 | 2023-05-24 | 1925 | keep | 0 | May | 2023 | 0.0013111 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-05-24 21:55 | 2023-05-25 12:45 | 47 | 14:50 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA PAJARO CRUZO FASE | P23052400359 | New_Event | Animals | Include | Include | Wildlife | 890 | 2023-05-24 | 41830 | keep | 0 | May | 2023 | 0.02849 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
CANOVANAS | 2023-05-24 22:43 | 2023-05-24 23:00 | 165 | 0:17 | S | NO SE REPORTO CAUSA | DISPARO DE BKR 1 Y 4 PROVOCARON DISPARO DE ALTA BKR 0010, SE PROBO Y QUEDO EN SERVICIO. NO CAUSA | R23052400131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 17 | 2023-05-24 | 2805 | keep | 0 | May | 2023 | 0.0019105 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
CANOVANAS | 2023-05-24 22:43 | 2023-05-24 22:59 | 1937 | 0:16 | S | NO SE REPORTO CAUSA | DISPARO DE BKR 1 Y 4 PROVOCARON DISPARO DE ALTA BKR 0010, SE PROBO Y QUEDO EN SERVICIO. NO CAUSA | R23052400131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 16 | 2023-05-24 | 30992 | keep | 0 | May | 2023 | 0.021109 | 0.0013193 | Sustained | FALSE | FALSE | Not_TMED_Event | 1937
CANOVANAS | 2023-05-24 22:43 | 2023-05-24 23:02 | 363 | 0:19 | S | NO SE REPORTO CAUSA | DISPARO DE BKR 1 Y 4 PROVOCARON DISPARO DE ALTA BKR 0010, SE PROBO Y QUEDO EN SERVICIO. NO CAUSA. CARGA X 1657-04 | R23052400131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-05-24 | 6897 | keep | 0 | May | 2023 | 0.0046975 | 0.00024724 | Sustained | FALSE | FALSE | Not_TMED_Event | 363
CANOVANAS | 2023-05-24 22:43 | 2023-05-24 23:02 | 14 | 0:19 | S | NO SE REPORTO CAUSA | DISPARO DE BKR 1 Y 4 PROVOCARON DISPARO DE ALTA BKR 0010, SE PROBO Y QUEDO EN SERVICIO. NO CAUSA. LLEVA EL 1657-03 | R23052400131 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 19 | 2023-05-24 | 266 | keep | 0 | May | 2023 | 0.00018117 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-05-24 22:52 | 2023-05-24 22:53 | 2368 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 2200 DE DORADO TC A VEGA ALTA SUB 9171 MR SPECIAL FUNDIÃ“ FUSIBLE. | B23052400486 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 2368 | keep | 0 | May | 2023 | 0.0016128 | 0.0016128 | Momentary | FALSE | FALSE | Not_TMED_Event | 2368
VEGA BAJA | 2023-05-24 22:52 | 2023-05-24 22:53 | 538 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 2200 DE DORADO TC A VEGA ALTA SUB 9171 MR SPECIAL FUNDIÃ“ FUSIBLE. | B23052400486 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 538 | keep | 0 | May | 2023 | 0.00036643 | 0.00036643 | Momentary | FALSE | FALSE | Not_TMED_Event | 538
VEGA BAJA | 2023-05-24 22:52 | 2023-05-24 22:53 | 1284 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LA LINEA 2200 DE DORADO TC A VEGA ALTA SUB 9171 MR SPECIAL FUNDIÃ“ FUSIBLE. | B23052400486 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-24 | 1284 | keep | 0 | May | 2023 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
VEGA BAJA | 2023-05-24 23:02 | 2023-05-25 00:50 | 611 | 1:48 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN CORTE DE LINEA SE LEVANTO CONDUCTOR PRIMARIO | B23052400474 | New_Event | Primary Wire Break | Include | Include | Equipment | 108 | 2023-05-24 | 65988 | keep | 0 | May | 2023 | 0.044944 | 0.00041615 | Sustained | FALSE | FALSE | Not_TMED_Event | 611
BAYAMON | 2023-05-24 23:13 | 2023-05-25 23:40 | 261 | 24:27 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | B23052400488 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1467 | 2023-05-24 | 382887 | keep | 0 | May | 2023 | 0.26078 | 0.00017777 | Sustained | FALSE | FALSE | Not_TMED_Event | 261
BAYAMON | 2023-05-24 23:18 | 2023-05-25 04:30 | 232 | 5:12 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CRUCE POR AVE | B23052400489 | New_Event | Animals | Include | Include | Wildlife | 312 | 2023-05-24 | 72384 | keep | 0 | May | 2023 | 0.0493 | 0.00015801 | Sustained | FALSE | FALSE | Not_TMED_Event | 232
PONCE | 2023-05-24 23:26 | 2023-05-25 06:46 | 45 | 7:20 | P | NO SE REPORTO CAUSA | 1 X 30 EN SU B NO CAUSA | P23052400386 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 440 | 2023-05-24 | 19800 | keep | 0 | May | 2023 | 0.013486 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
GUAYAMA | 2023-05-25 00:34 | 2023-05-25 10:08 | 10 | 9:34 | P | CONDUCTOR ROTO O ABIERTO | PUENTE SAFADO EN RISER | P23052500005 | New_Event | Primary Wire Break | Include | Include | Equipment | 574 | 2023-05-25 | 5740 | keep | 0 | May | 2023 | 0.0039095 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-25 01:41 | 2023-05-25 07:41 | 65 | 6:00 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | C23052500002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2023-05-25 | 23400 | keep | 0 | May | 2023 | 0.015938 | 4.4271e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 65
UTUADO | 2023-05-25 02:09 | 2023-05-25 14:50 | 18 | 12:41 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REPARA BAJANTE PRIMARIO | A23052500002 | New_Event | Primary Wire Break | Include | Include | Equipment | 761 | 2023-05-25 | 13698 | keep | 0 | May | 2023 | 0.0093296 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
PONCE | 2023-05-25 02:49 | 2023-05-25 07:34 | 32 | 4:45 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | P23052500017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 285 | 2023-05-25 | 9120 | keep | 0 | May | 2023 | 0.0062116 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
HUMACAO | 2023-05-25 02:51 | 2023-05-25 08:51 | 40 | 6:00 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | C23052500004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 360 | 2023-05-25 | 14400 | keep | 0 | May | 2023 | 0.0098078 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-25 03:11 | 2023-05-26 12:08 | 8 | 32:57 | P | TRANSFORMADOR AVERIADO | REMPLAZO XMR 37.5KVA | B23052500010 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1977 | 2023-05-25 | 15816 | keep | 0 | May | 2023 | 0.010772 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-25 03:42 | 2023-05-25 03:43 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23052500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-05-25 04:00 | 2023-05-25 10:16 | 284 | 6:16 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23052500005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 376 | 2023-05-25 | 106784 | keep | 0 | May | 2023 | 0.07273 | 0.00019343 | Sustained | FALSE | FALSE | Not_TMED_Event | 284
YAUCO | 2023-05-25 04:18 | 2023-05-25 10:00 | 40 | 5:42 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA | M23052500004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 342 | 2023-05-25 | 13680 | keep | 0 | May | 2023 | 0.0093174 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
YAUCO | 2023-05-25 05:06 | 2023-05-25 05:07 | 179 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23052500005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 179 | keep | 0 | May | 2023 | 0.00012192 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
CAGUAS | 2023-05-25 05:11 | 2023-05-25 08:45 | 40 | 3:34 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AVE | C23052500005 | New_Event | Animals | Include | Include | Wildlife | 214 | 2023-05-25 | 8560 | keep | 0 | May | 2023 | 0.0058302 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-25 05:44 | 2023-05-25 08:06 | 166 | 2:22 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23052500006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-05-25 | 23572 | keep | 0 | May | 2023 | 0.016055 | 0.00011306 | Sustained | FALSE | FALSE | Not_TMED_Event | 166
SAN JUAN | 2023-05-25 06:01 | 2023-05-25 06:25 | 178 | 0:24 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO MANUAL EN CAMPO | S23052500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 24 | 2023-05-25 | 4272 | keep | 0 | May | 2023 | 0.0029096 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
GUAYAMA | 2023-05-25 06:29 | 2023-05-25 06:30 | 4132 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23052500060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
BAYAMON | 2023-05-25 06:40 | 2023-05-25 11:52 | 100 | 5:12 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23052500021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 312 | 2023-05-25 | 31200 | keep | 0 | May | 2023 | 0.02125 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-25 07:13 | 2023-05-25 14:04 | 17 | 6:51 | P | CONDUCTOR ROTO O ABIERTO | 1 X 30 EN C/L SE LEVANTO Y REPARO CONDUCTOR PRIMARIO | C23052500011 | New_Event | Primary Wire Break | Include | Include | Equipment | 411 | 2023-05-25 | 6987 | keep | 0 | May | 2023 | 0.0047588 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BAYAMON | 2023-05-25 07:15 | 2023-05-25 09:40 | 1 | 2:25 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN RISER MAL TIEMPO LLUVIA | B23052500029 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 145 | 2023-05-25 | 145 | keep | 0 | May | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-25 07:17 | 2023-05-25 07:18 | 851 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 3103-02 LLEVANDO 50% 3102-01 | C2305240000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-25 | 851 | keep | 0 | May | 2023 | 0.00057961 | 0.00057961 | Momentary | FALSE | FALSE | Not_TMED_Event | 851
CAGUAS | 2023-05-25 07:17 | 2023-05-25 07:18 | 1922 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 1922 | keep | 0 | May | 2023 | 0.0013091 | 0.0013091 | Momentary | FALSE | FALSE | Not_TMED_Event | 1922
VEGA BAJA | 2023-05-25 07:17 | 2023-05-25 13:42 | 6 | 6:25 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23052500031 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 385 | 2023-05-25 | 2310 | keep | 0 | May | 2023 | 0.0015733 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-05-25 07:27 | 2023-05-25 13:00 | 30 | 5:33 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO | P23052500069 | New_Event | Primary Wire Break | Include | Include | Equipment | 333 | 2023-05-25 | 9990 | keep | 0 | May | 2023 | 0.0068041 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-25 07:30 | 2023-05-25 07:32 | 1647 | 0:02 | T | CONDUCTOR ROTO O ABIERTO | DISPARO Y SE CERRO POR CONTROL | B23052500036 | New_Event | Primary Wire Break | Include | Include | Equipment | 2 | 2023-05-25 | 3294 | keep | 0 | May | 2023 | 0.0022435 | 0.0011218 | Momentary | FALSE | FALSE | Not_TMED_Event | 1647
BAYAMON | 2023-05-25 07:32 | 2023-05-25 16:34 | 143 | 9:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L Y 1 X 65 SE REPARO PUENTE | B23052500269 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 542 | 2023-05-25 | 77506 | keep | 0 | May | 2023 | 0.052789 | 9.7397e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 143
YAUCO | 2023-05-25 07:34 | 2023-05-25 17:20 | 10 | 9:46 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR AVERIADO 37 .5 KVA A 2400 VOLT | P23052500072 | New_Event | Service Transformer Failure | Include | Include | Equipment | 586 | 2023-05-25 | 5860 | keep | 0 | May | 2023 | 0.0039912 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-25 07:41 | 2023-05-25 10:00 | 23 | 2:19 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | B23052500039 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-25 | 3197 | keep | 0 | May | 2023 | 0.0021775 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
HUMACAO | 2023-05-25 07:42 | 2023-05-25 09:02 | 63 | 1:20 | P | ANIMAL | 1 X 80 EN RISER Y 1 X 65 EN RISER CRUCE POR AVE | C23052500014 | New_Event | Animals | Include | Include | Wildlife | 80 | 2023-05-25 | 5040 | keep | 0 | May | 2023 | 0.0034327 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
CAGUAS | 2023-05-25 07:42 | 2023-05-25 09:46 | 154 | 2:04 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | C23052500013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 124 | 2023-05-25 | 19096 | keep | 0 | May | 2023 | 0.013006 | 0.00010489 | Sustained | FALSE | FALSE | Not_TMED_Event | 154
HUMACAO | 2023-05-25 07:56 | 2023-05-25 10:20 | 70 | 2:24 | P | ANIMAL | 1 X 30 EN C/L CRUCE POR AV | C23052500017 | New_Event | Animals | Include | Include | Wildlife | 144 | 2023-05-25 | 10080 | keep | 0 | May | 2023 | 0.0068654 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
BAYAMON | 2023-05-25 08:00 | 2023-05-25 13:52 | 1 | 5:52 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | B23052500045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 352 | 2023-05-25 | 352 | keep | 0 | May | 2023 | 0.00023975 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-25 08:15 | 2023-05-25 08:18 | 2126 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRRADO POR SCADA | C23052500019 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-25 | 6378 | keep | 0 | May | 2023 | 0.004344 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
VEGA BAJA | 2023-05-25 08:17 | 2023-05-25 08:18 | 1284 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 1284 | keep | 0 | May | 2023 | 0.00087453 | 0.00087453 | Momentary | FALSE | FALSE | Not_TMED_Event | 1284
FAJARDO | 2023-05-25 08:23 | 2023-05-25 09:16 | 59 | 0:53 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | R23052500010 | New_Event | Cutout Failure | Include | Include | Equipment | 53 | 2023-05-25 | 3127 | keep | 0 | May | 2023 | 0.0021298 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
VEGA BAJA | 2023-05-25 08:41 | 2023-05-25 16:55 | 40 | 8:14 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23052500075 | New_Event | Animals | Include | Include | Wildlife | 494 | 2023-05-25 | 19760 | keep | 0 | May | 2023 | 0.013458 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-25 08:45 | 2023-05-25 13:00 | 10 | 4:15 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRIO XMR PARA REMPLAZO POSTE SECUNDARIO | B23052500077 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 255 | 2023-05-25 | 2550 | keep | 0 | May | 2023 | 0.0017368 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-25 08:49 | 2023-05-25 10:55 | 1 | 2:06 | P | ANIMAL | 1 X 20 EN C/L CRUCE POR AVE EVENTO TRANSFERIDO DE PONCE | P23052500168 | New_Event | Animals | Include | Include | Wildlife | 126 | 2023-05-25 | 126 | keep | 0 | May | 2023 | 8.5818e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-25 08:59 | 2023-05-25 10:00 | 106 | 1:01 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO FASE | R23052500013 | New_Event | Animals | Include | Include | Wildlife | 61 | 2023-05-25 | 6466 | keep | 0 | May | 2023 | 0.004404 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
SAN JUAN | 2023-05-25 09:02 | 2023-05-25 09:03 | 1225 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR LLEVA 75% DEL 1203-03 | S2305250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-25 | 1225 | keep | 0 | May | 2023 | 0.00083434 | 0.00083434 | Momentary | FALSE | FALSE | Not_TMED_Event | 1225
SAN JUAN | 2023-05-25 09:02 | 2023-05-25 09:03 | 462 | 0:01 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | RECIERRE DE INTERRUPTOR 75% DE SU CARGA POR EL 1203-01 | S2305250000X | New_Event | Primary Pole Failure | Include | Include | Equipment | 1 | 2023-05-25 | 462 | keep | 0 | May | 2023 | 0.00031467 | 0.00031467 | Momentary | FALSE | FALSE | Not_TMED_Event | 462
SAN JUAN | 2023-05-25 09:03 | 2023-05-25 13:33 | 63 | 4:30 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REPUSO 2 X 100 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | S23052500041 | 1st_after_momentary | Primary Pole Failure | Include | Include | Equipment | 270 | 2023-05-25 | 17010 | keep | 0 | May | 2023 | 0.011585 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
FAJARDO | 2023-05-25 09:06 | 2023-05-25 10:21 | 324 | 1:15 | P | CAUSAS EXTERNAS | 1 X 100 EN CORTE DE LINEA MAQUINA TOCO FASE | R23052500014 | New_Event | Damage From Public | Include | Include | Public | 75 | 2023-05-25 | 24300 | keep | 0 | May | 2023 | 0.016551 | 0.00022067 | Sustained | FALSE | FALSE | Not_TMED_Event | 324
BARRANQUITAS | 2023-05-25 09:08 | 2023-05-25 10:07 | 1 | 0:59 | P | ANIMAL | 1 X 20 EN RISER CRUCE POR CULEBRA | C23052500028 | New_Event | Animals | Include | Include | Wildlife | 59 | 2023-05-25 | 59 | keep | 0 | May | 2023 | 4.0185e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-25 09:10 | 2023-05-25 13:30 | 8 | 4:20 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR AVE | M23052500026 | New_Event | Animals | Include | Include | Wildlife | 260 | 2023-05-25 | 2080 | keep | 0 | May | 2023 | 0.0014167 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-25 09:17 | 2023-05-25 10:47 | 2617 | 1:30 | T | DESGANCHE | BY-230525-02 SE RETIRO BAMBUA Y SE CERRO BKR POR CONTROL | B23052500089 | New_Event | Vegetation Contact | Include | Include | Vegetation | 90 | 2023-05-25 | 235530 | keep | 0 | May | 2023 | 0.16042 | 0.0017824 | Sustained | FALSE | FALSE | Not_TMED_Event | 2617
CAGUAS | 2023-05-25 09:23 | 2023-05-25 12:35 | 60 | 3:12 | P | CONDUCTOR ROTO O ABIERTO | 1 X 50 EN C/L SE LEVANTO ALAMBRE EN EL SUELO | C23052500031 | New_Event | Primary Wire Break | Include | Include | Equipment | 192 | 2023-05-25 | 11520 | keep | 0 | May | 2023 | 0.0078462 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-25 09:26 | 2023-05-25 16:27 | 7 | 7:01 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMADOR PARA REMPLAZO SECUNDARIA BAJANTES Y 2 TOMAS | R23052500019 | New_Event | Secondary Wire Break | Include | Include | Equipment | 421 | 2023-05-25 | 2947 | keep | 0 | May | 2023 | 0.0020072 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-25 09:27 | 2023-05-25 17:01 | 7 | 7:34 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE PRIMARIO | S23052500045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 454 | 2023-05-25 | 3178 | keep | 0 | May | 2023 | 0.0021645 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
FAJARDO | 2023-05-25 09:27 | 2023-05-25 10:35 | 204 | 1:08 | P | CAUSAS EXTERNAS | TRACTOR PASO POR ENCIMA Y CAYO TAPA DENTRO POOL BOX SE RETIRO TAPA | R23052500011 | New_Event | Damage From Public | Include | Include | Public | 68 | 2023-05-25 | 13872 | keep | 0 | May | 2023 | 0.0094482 | 0.00013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 204
CANOVANAS | 2023-05-25 09:30 | 2023-05-25 10:54 | 1 | 1:24 | P | ANIMAL | 1 X 20 EN MEDICION SE RETIRO AVE CRUZO PARARRAYO EVENTO TRANSFERIDO | P23052500128 | New_Event | Animals | Include | Include | Wildlife | 84 | 2023-05-25 | 84 | keep | 0 | May | 2023 | 5.7212e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-25 09:30 | 2023-05-25 18:00 | 6 | 8:30 | P | POSTE SECUNDARIO PARTIDO O DEFECTUOSO | SE ABRE MONTURA DE TRANSFORMADOR Y SE REEMPLAZA POSTE | A23052500000 | New_Event | Secondary Pole Failure | Include | Include | Equipment | 510 | 2023-05-25 | 3060 | keep | 0 | May | 2023 | 0.0020842 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-05-25 09:32 | 2023-05-25 13:51 | 1 | 4:19 | P | NO SE REPORTO CAUSA | 2 X 30 EN RISER Y 1 X 40 EN C/L | C23052500066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2023-05-25 | 259 | keep | 0 | May | 2023 | 0.0001764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-25 09:38 | 2023-05-25 18:00 | 173 | 8:22 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO ALIMENTADOR Y SE LEVANTO CONDUCTOR PRIMARIO DEL SUELO | S23052500049 | New_Event | Primary Wire Break | Include | Include | Equipment | 502 | 2023-05-25 | 86846 | keep | 0 | May | 2023 | 0.05915 | 0.00011783 | Sustained | FALSE | FALSE | Not_TMED_Event | 173
SAN JUAN | 2023-05-25 09:42 | 2023-05-25 13:01 | 63 | 3:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA Y 1 X 100 EN C/L | S23052500051 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2023-05-25 | 12537 | keep | 0 | May | 2023 | 0.0085389 | 4.2909e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 63
PONCE | 2023-05-25 09:43 | 2023-05-25 21:42 | 6 | 11:59 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR SUMERGIBLE 300 KVA 13200 VOLT | P23052500140 | New_Event | Service Transformer Failure | Include | Include | Equipment | 719 | 2023-05-25 | 4314 | keep | 0 | May | 2023 | 0.0029382 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-05-25 09:57 | 2023-05-25 13:32 | 1 | 3:35 | P | NO SE REPORTO CAUSA | 2 X 20 EN C/L NO CAUSA | C23052500041 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2023-05-25 | 215 | keep | 0 | May | 2023 | 0.00014644 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-25 10:26 | 2023-05-25 15:22 | 1 | 4:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 40 EN C/L SE REEMPLAZO CAJA PRIMARIA PARTIDA | S23052500063 | New_Event | Cutout Failure | Include | Include | Equipment | 296 | 2023-05-25 | 296 | keep | 0 | May | 2023 | 0.0002016 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-25 10:37 | 2023-05-25 15:30 | 30 | 4:53 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | B23052500209 | New_Event | Animals | Include | Include | Wildlife | 293 | 2023-05-25 | 8790 | keep | 0 | May | 2023 | 0.0059868 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-05-25 10:41 | 2023-05-25 17:00 | 11 | 6:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN XMR SE REMPLAZO CAJA EN XMR | P23052500177 | New_Event | Cutout Failure | Include | Include | Equipment | 379 | 2023-05-25 | 4169 | keep | 0 | May | 2023 | 0.0028395 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-05-25 10:47 | 2023-05-25 14:44 | 45 | 3:57 | P | DESGANCHE | 1 X 40 EN RISER PROVISIONAL Y 1 X 50 EN SU-3 SE RETIRO ENREDADERA DENTRO DEL SU-3 | B23052500160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 237 | 2023-05-25 | 10665 | keep | 0 | May | 2023 | 0.0072639 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-05-25 10:50 | 2023-05-25 21:30 | 10 | 10:40 | P | CONDUCTOR ROTO O ABIERTO | 1 X 25 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | A23052500021 | New_Event | Primary Wire Break | Include | Include | Equipment | 640 | 2023-05-25 | 6400 | keep | 0 | May | 2023 | 0.004359 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
ARECIBO | 2023-05-25 10:52 | 2023-05-25 14:04 | 10 | 3:12 | P | ANIMAL | 1 X 25 EN RISER POR AVE | A23052500022 | New_Event | Animals | Include | Include | Wildlife | 192 | 2023-05-25 | 1920 | keep | 0 | May | 2023 | 0.0013077 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-25 10:53 | 2023-05-25 12:10 | 6 | 1:17 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50KVA X 50KVA | M23052500042 | New_Event | Service Transformer Failure | Include | Include | Equipment | 77 | 2023-05-25 | 462 | keep | 0 | May | 2023 | 0.00031467 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
YAUCO | 2023-05-25 11:06 | 2023-05-25 19:51 | 33 | 8:45 | P | TRANSFORMADOR AVERIADO | 2 X 30 EN CORTE DE LINES TRANSFORMADOR 37.5 KVA QUEMADO RELACIONADO A WR 6321149 | P23052500229 | New_Event | Service Transformer Failure | Include | Include | Equipment | 525 | 2023-05-25 | 17325 | keep | 0 | May | 2023 | 0.0118 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
FAJARDO | 2023-05-25 11:30 | 2023-05-25 12:40 | 22 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR T-3 PARA ENCABEZAR TOMA A T-3 | R23052500032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-05-25 | 1540 | keep | 0 | May | 2023 | 0.0010489 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
CAGUAS | 2023-05-25 11:48 | 2023-05-25 11:49 | 476 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 476 | keep | 0 | May | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
SAN JUAN | 2023-05-25 11:53 | 2023-05-25 13:06 | 4 | 1:13 | P | DESGANCHE | 1 X 30 EN MONTURA | S23052500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-05-25 | 292 | keep | 0 | May | 2023 | 0.00019888 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-05-25 12:00 | 2023-05-25 13:20 | 20 | 1:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTORES SECUNDARIO Y BAJANTE | R23052500031 | New_Event | Secondary Wire Break | Include | Include | Equipment | 80 | 2023-05-25 | 1600 | keep | 0 | May | 2023 | 0.0010898 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-05-25 12:12 | 2023-05-25 12:20 | 2 | 0:08 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONECTOR Y BAJANTE SECUNDARIO | R23052500035 | New_Event | Secondary Wire Break | Include | Include | Equipment | 8 | 2023-05-25 | 16 | keep | 0 | May | 2023 | 1.0898e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-05-25 12:21 | 2023-05-25 13:03 | 6 | 0:42 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA DE NEUTRAL EN PEDESTAL | C23052500065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 42 | 2023-05-25 | 252 | keep | 0 | May | 2023 | 0.00017164 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-05-25 12:31 | 2023-05-25 15:50 | 40 | 3:19 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052500065 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 199 | 2023-05-25 | 7960 | keep | 0 | May | 2023 | 0.0054215 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-25 12:32 | 2023-05-25 20:45 | 200 | 8:13 | P | CONDUCTOR ROTO O ABIERTO | 1 X 200 EN CORTE DE LINEA SE CERRO PUENTE | A23052500033 | New_Event | Primary Wire Break | Include | Include | Equipment | 493 | 2023-05-25 | 98600 | keep | 0 | May | 2023 | 0.067156 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-25 12:40 | 2023-05-25 14:55 | 169 | 2:15 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23052500198 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-05-25 | 22815 | keep | 0 | May | 2023 | 0.015539 | 0.00011511 | Sustained | FALSE | FALSE | Not_TMED_Event | 169
VEGA BAJA | 2023-05-25 12:41 | 2023-05-25 16:03 | 80 | 3:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | B23052500199 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 202 | 2023-05-25 | 16160 | keep | 0 | May | 2023 | 0.011007 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
MAYAGÃœEZ | 2023-05-25 12:46 | 2023-05-25 15:40 | 50 | 2:54 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23052500068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 174 | 2023-05-25 | 8700 | keep | 0 | May | 2023 | 0.0059255 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-25 12:48 | 2023-05-25 13:27 | 1 | 0:39 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C23052500067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2023-05-25 | 39 | keep | 0 | May | 2023 | 2.6563e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-25 13:00 | 2023-05-25 14:45 | 70 | 1:45 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23052500038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-05-25 | 7350 | keep | 0 | May | 2023 | 0.0050061 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
FAJARDO | 2023-05-25 13:05 | 2023-05-25 14:05 | 41 | 1:00 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR AVE CRUZO FASE | R23052500041 | New_Event | Animals | Include | Include | Wildlife | 60 | 2023-05-25 | 2460 | keep | 0 | May | 2023 | 0.0016755 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
CAGUAS | 2023-05-25 13:11 | 2023-05-25 15:39 | 14 | 2:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA TRASPATIO | C23052500071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 148 | 2023-05-25 | 2072 | keep | 0 | May | 2023 | 0.0014112 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CAGUAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 874 | 0:02 | T | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 3604-06 LLEVA 20% DEL 3010-01 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 1748 | keep | 0 | May | 2023 | 0.0011906 | 0.00059528 | Momentary | FALSE | FALSE | Not_TMED_Event | 874
BARRANQUITAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 1565 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 3130 | keep | 0 | May | 2023 | 0.0021318 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 976 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 1952 | keep | 0 | May | 2023 | 0.0013295 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 548 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 1096 | keep | 0 | May | 2023 | 0.00074648 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 315 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 630 | keep | 0 | May | 2023 | 0.00042909 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 870 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 1740 | keep | 0 | May | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 2906 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 5812 | keep | 0 | May | 2023 | 0.0039585 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-25 13:15 | 2023-05-25 13:17 | 2343 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052500075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-25 | 4686 | keep | 0 | May | 2023 | 0.0031916 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
CANOVANAS | 2023-05-25 13:20 | 2023-05-25 13:40 | 20 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO BARRA PEDESTAL | R23052500039 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-05-25 | 400 | keep | 0 | May | 2023 | 0.00027244 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-25 13:33 | 2023-05-25 18:42 | 45 | 5:09 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REEMPLAZO 2 POSTE PARTIDO PRIMARIO RELACIONADO A EVENTO S23052500041 | S23052500094 | New_Event | Primary Pole Failure | Include | Include | Equipment | 309 | 2023-05-25 | 13905 | keep | 0 | May | 2023 | 0.0094706 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-05-25 13:35 | 2023-05-25 14:48 | 1 | 1:13 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | S23052500093 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 73 | 2023-05-25 | 73 | keep | 0 | May | 2023 | 4.972e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-25 13:35 | 2023-05-25 16:10 | 9 | 2:35 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR BUSHING PRIMARIO AVERIADO DE 25KVA X 37.5KVA | M23052500075 | New_Event | Service Transformer Failure | Include | Include | Equipment | 155 | 2023-05-25 | 1395 | keep | 0 | May | 2023 | 0.00095013 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-05-25 14:03 | 2023-05-25 15:26 | 25 | 1:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA Y BAJANTE SECUNDARIO | C23052500079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 83 | 2023-05-25 | 2075 | keep | 0 | May | 2023 | 0.0014133 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-05-25 14:09 | 2023-05-25 21:17 | 100 | 7:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR FUERTES VIENTOS | A23052500049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 428 | 2023-05-25 | 42800 | keep | 0 | May | 2023 | 0.029151 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-25 14:15 | 2023-05-25 14:16 | 189 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR Y SE CERRO POR CONTROL 95% DE LOS CLIENTES TRANFERIDOS POR VIA LIBRE D2023-4068 SE VERIFICO PERSONAL FUERA CON HOLD OFF 7014 | B23052500024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 189 | keep | 0 | May | 2023 | 0.00012873 | 0.00012873 | Momentary | FALSE | FALSE | Not_TMED_Event | 189
FAJARDO | 2023-05-25 14:25 | 2023-05-25 18:07 | 1 | 3:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA | R23052500053 | New_Event | Cutout Failure | Include | Include | Equipment | 222 | 2023-05-25 | 222 | keep | 0 | May | 2023 | 0.0001512 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-25 14:28 | 2023-05-25 15:49 | 140 | 1:21 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23052500082 | New_Event | Vegetation Contact | Include | Include | Vegetation | 81 | 2023-05-25 | 11340 | keep | 0 | May | 2023 | 0.0077236 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
CAGUAS | 2023-05-25 14:30 | 2023-05-25 18:48 | 15 | 4:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REPARO BAJANTE SECUNDARIO Y SE REEMPLAZARON CONECTORES | C23052500032 | New_Event | Secondary Wire Break | Include | Include | Equipment | 258 | 2023-05-25 | 3870 | keep | 0 | May | 2023 | 0.0026358 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-25 14:32 | 2023-05-25 18:13 | 25 | 3:41 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIAS | A23052500054 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 221 | 2023-05-25 | 5525 | keep | 0 | May | 2023 | 0.0037631 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-25 14:33 | 2023-05-25 18:20 | 10 | 3:47 | P | SECUNDARIA/DESGANCHE | SE ABRIR XMR PARA REPARAR BAJANTE SECUDNARIO Y DESGANCHE SECUDNARIO SE DEJO VOLTAJE 122V/FASE | S23052500102 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 227 | 2023-05-25 | 2270 | keep | 0 | May | 2023 | 0.0015461 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-25 14:36 | 2023-05-25 16:50 | 619 | 2:14 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | C23052500087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-05-25 | 82946 | keep | 0 | May | 2023 | 0.056494 | 0.0004216 | Sustained | FALSE | FALSE | Not_TMED_Event | 619
SAN JUAN | 2023-05-25 14:45 | 2023-05-25 15:05 | 8 | 0:20 | P | SECUNDARIA/OTROS | SE ABRIO XMR PARA HACER CONEXION EN LADO SECUNDARIO | S23052500100 | New_Event |  |  |  |  | 20 | 2023-05-25 | 160 | keep | 0 | May | 2023 | 0.00010898 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-05-25 15:07 | 2023-05-25 16:44 | 12 | 1:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR TRANSFORMADOR RETIRAR PROVISIONAL Y CONECTAR AL SISTEMA SOTERRADO | M230525000XX | New_Event | Secondary Wire Break | Include | Include | Equipment | 97 | 2023-05-25 | 1164 | keep | 0 | May | 2023 | 0.0007928 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-25 15:16 | 2023-05-25 20:46 | 5 | 5:30 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN C/L CONDUCTOR CRUZADO | B23052500278 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 330 | 2023-05-25 | 1650 | keep | 0 | May | 2023 | 0.0011238 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-05-25 15:19 | 2023-05-26 09:00 | 2 | 17:41 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR SE RETIRO CULEBRA | A23052500064 | New_Event | Animals | Include | Include | Wildlife | 1061 | 2023-05-25 | 2122 | keep | 0 | May | 2023 | 0.0014453 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-05-25 15:21 | 2023-05-25 15:58 | 1227 | 0:37 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR Y SE SECCIONALIZA AVERIA DE AISLADORES PARTIDOS | A23052500065 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 37 | 2023-05-25 | 45399 | keep | 0 | May | 2023 | 0.030921 | 0.0008357 | Sustained | FALSE | FALSE | Not_TMED_Event | 1227
AGUADILLA | 2023-05-25 15:26 | 2023-05-25 18:20 | 100 | 2:54 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 15 EN CORTE DE LINEA LINEAS CRUZADAS | M23052500095 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 174 | 2023-05-25 | 17400 | keep | 0 | May | 2023 | 0.011851 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-25 15:30 | 2023-05-25 19:35 | 5 | 4:05 | P | DESGANCHE | SE CERRO PUENTE AERIO RADIAL Y REALIZO DESGANCHE | B23052500283 | New_Event | Vegetation Contact | Include | Include | Vegetation | 245 | 2023-05-25 | 1225 | keep | 0 | May | 2023 | 0.00083434 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-25 15:49 | 2023-05-25 17:14 | 2234 | 1:25 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE INTERRUPTOR SE SECIONALIZO ALIEMTADOR POR AISLADOR PARTIDO ENTRO 30% EN SERVICIO | B23052500298 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 85 | 2023-05-25 | 189890 | keep | 0 | May | 2023 | 0.12933 | 0.0015216 | Sustained | FALSE | FALSE | Not_TMED_Event | 2234
ARECIBO | 2023-05-25 15:58 | 2023-05-25 18:07 | 200 | 2:09 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE REEMPLAZAN AISLADORES PARTIDOS Y SE CIERRA MACHETES | A23052500074 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 129 | 2023-05-25 | 25800 | keep | 0 | May | 2023 | 0.017572 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-25 15:59 | 2023-05-25 18:49 | 158 | 2:50 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | S23052500117 | New_Event | Animals | Include | Include | Wildlife | 170 | 2023-05-25 | 26860 | keep | 0 | May | 2023 | 0.018294 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
FAJARDO | 2023-05-25 16:00 | 2023-05-25 16:40 | 1 | 0:40 | P | ANIMAL | 1 X 20 EN CORTE DE LINEA AVE CRUZO FASE | R23052500060 | New_Event | Animals | Include | Include | Wildlife | 40 | 2023-05-25 | 40 | keep | 0 | May | 2023 | 2.7244e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-25 16:07 | 2023-05-26 16:30 | 30 | 24:23 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23052500099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1463 | 2023-05-25 | 43890 | keep | 0 | May | 2023 | 0.029893 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-25 16:25 | 2023-05-25 17:40 | 1417 | 1:15 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE CERRO MANUAL | M23052500101 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 75 | 2023-05-25 | 106275 | keep | 0 | May | 2023 | 0.072383 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
VEGA BAJA | 2023-05-25 16:26 | 2023-05-26 11:45 | 6 | 19:19 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052500097 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1159 | 2023-05-25 | 6954 | keep | 0 | May | 2023 | 0.0047363 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-05-25 16:46 | 2023-05-25 19:38 | 50 | 2:52 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA POR LLUVIAS | A23052500105 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 172 | 2023-05-25 | 8600 | keep | 0 | May | 2023 | 0.0058574 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-05-25 16:46 | 2023-05-25 17:38 | 1 | 0:52 | P | OTRAS CAUSAS | SE ABRIO RISER Y SE REALIZO BYPASS EQUIPO DE MEDICION | C23052500118 | New_Event | Other Causes | Include | Include | Other | 52 | 2023-05-25 | 52 | keep | 0 | May | 2023 | 3.5417e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-25 16:50 | 2023-05-25 16:51 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C23052500120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-25 | 2725 | keep | 0 | May | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-05-25 16:50 | 2023-05-25 16:51 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C23052500120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-25 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-05-25 16:50 | 2023-05-25 16:51 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C23052500120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-25 | 1437 | keep | 0 | May | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-05-25 16:50 | 2023-05-25 16:51 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C23052500121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-25 | 2565 | keep | 0 | May | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-05-25 16:50 | 2023-05-25 16:51 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8500 | C23052500121 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-25 | 3565 | keep | 0 | May | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
UTUADO | 2023-05-25 16:50 | 2023-05-25 20:02 | 150 | 3:12 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LINEA | A23052500107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 192 | 2023-05-25 | 28800 | keep | 0 | May | 2023 | 0.019616 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-05-25 16:51 | 2023-05-25 19:17 | 619 | 2:26 | P | DESGANCHE | 2 X 100 EN C/L SE REALIZO DESGANCHE | C23052500087 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 146 | 2023-05-25 | 90374 | keep | 0 | May | 2023 | 0.061553 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-25 16:53 | 2023-05-25 21:30 | 50 | 4:37 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA POR RAYOS | A23052500109 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 277 | 2023-05-25 | 13850 | keep | 0 | May | 2023 | 0.0094332 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-25 17:00 | 2023-05-25 17:43 | 2 | 0:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B2305250000X | New_Event | Cutout Failure | Include | Include | Equipment | 43 | 2023-05-25 | 86 | keep | 0 | May | 2023 | 5.8574e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-25 17:01 | 2023-05-25 17:04 | 766 | 0:03 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37500 PROBLEMAS CON OMS CARGA X 1909-07 OHGW PARTIDO TRAMO MONACILLOS-GRANA. | B2305250000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-25 | 2298 | keep | 0 | May | 2023 | 0.0015652 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
BAYAMON | 2023-05-25 17:01 | 2023-05-25 17:04 | 222 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37500 PROBLEMAS CON OMS OHGW PARTIDO TRAMO MONACILLOS-GRANA. | B2305250000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-25 | 666 | keep | 0 | May | 2023 | 0.00045361 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
BAYAMON | 2023-05-25 17:01 | 2023-05-25 17:04 | 2466 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37500 PROBLEMAS CON OMS OHGW PARTIDO TRAMO MONACILLOS-GRANA. | B2305250000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-25 | 7398 | keep | 0 | May | 2023 | 0.0050387 | 0.0016796 | Momentary | FALSE | FALSE | Not_TMED_Event | 2466
BAYAMON | 2023-05-25 17:01 | 2023-05-25 17:04 | 2435 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37500 PROBLEMAS CON OMS OHGW PARTIDO TRAMO MONACILLOS-GRANA. | B2305250000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-25 | 7305 | keep | 0 | May | 2023 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
BAYAMON | 2023-05-25 17:01 | 2023-05-25 17:04 | 1139 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37500 PROBLEMAS CON OMS LLEVA 50% DEL 1709-03 OHGW PARTIDO TRAMO MONACILLOS-GRANA. | B2305250000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-25 | 3417 | keep | 0 | May | 2023 | 0.0023273 | 0.00077577 | Momentary | FALSE | FALSE | Not_TMED_Event | 1139
BAYAMON | 2023-05-25 17:01 | 2023-05-25 17:04 | 2956 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37500 PROBLEMAS CON OMS OHGW PARTIDO TRAMO MONACILLOS-GRANA. | B2305250000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-25 | 8868 | keep | 0 | May | 2023 | 0.00604 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
BAYAMON | 2023-05-25 17:01 | 2023-05-25 17:04 | 4456 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 37500 PROBLEMAS CON OMS OHGW PARTIDO TRAMO MONACILLOS-GRANA. | B2305250000X | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-25 | 13368 | keep | 0 | May | 2023 | 0.0091049 | 0.003035 | Momentary | FALSE | FALSE | Not_TMED_Event | 4456
BAYAMON | 2023-05-25 17:04 | 2023-05-26 11:00 | 7 | 17:56 | P | DESGANCHE | 1 X 20 EN XMR DESGANCHE PRIMARIO | S23052500045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1076 | 2023-05-25 | 7532 | keep | 0 | May | 2023 | 0.00513 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
PONCE | 2023-05-25 17:06 | 2023-05-25 18:33 | 50 | 1:27 | P | ANIMAL | 1 X 100 EN C/L AVE CRUZO LINEAS | P23052500197 | New_Event | Animals | Include | Include | Wildlife | 87 | 2023-05-25 | 4350 | keep | 0 | May | 2023 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
YAUCO | 2023-05-25 17:10 | 2023-05-25 17:40 | 10 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23052500198 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-05-25 | 300 | keep | 0 | May | 2023 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-25 17:14 | 2023-05-25 18:06 | 1563 | 0:52 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE SECCIONALIZO ALIMENTADOR POR AISLADOR PARTIDO | B23052500298 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 52 | 2023-05-25 | 81276 | keep | 0 | May | 2023 | 0.055357 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-25 17:23 | 2023-05-25 19:33 | 40 | 2:10 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L CAMION IMPACTO POSTE Y CRUZO LINEAS | P23052500205 | New_Event | Damage From Public | Include | Include | Public | 130 | 2023-05-25 | 5200 | keep | 0 | May | 2023 | 0.0035417 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-25 17:23 | 2023-05-25 19:37 | 40 | 2:14 | P | ANIMAL | 1 X 40 EN S/U ANIMAL CRUZO LINEAS | P23052500206 | New_Event | Animals | Include | Include | Wildlife | 134 | 2023-05-25 | 5360 | keep | 0 | May | 2023 | 0.0036507 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-25 17:31 | 2023-05-25 22:15 | 60 | 4:44 | P | MAL TIEMPO/RAYOS | 1 X 25 , 1 X 40 Y 1 X 65 EN DIFERENTES CORTES DE LINEA DESCARGAS ELECTRICAS | A23052500122 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 284 | 2023-05-25 | 17040 | keep | 0 | May | 2023 | 0.011606 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
MAYAGÃœEZ | 2023-05-25 17:32 | 2023-05-26 08:35 | 15 | 15:03 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO | M23052500109 | New_Event | Primary Wire Break | Include | Include | Equipment | 903 | 2023-05-25 | 13545 | keep | 0 | May | 2023 | 0.0092254 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-25 17:38 | 2023-05-26 09:55 | 2 | 16:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M23052500110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 977 | 2023-05-25 | 1954 | keep | 0 | May | 2023 | 0.0013309 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
AGUADILLA | 2023-05-25 17:50 | 2023-05-26 10:04 | 2 | 16:14 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA POR DESGANCHE | A23052500112 | New_Event | Vegetation Contact | Include | Include | Vegetation | 974 | 2023-05-25 | 1948 | keep | 0 | May | 2023 | 0.0013268 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
ARECIBO | 2023-05-25 17:57 | 2023-05-25 19:55 | 70 | 1:58 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052500137 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 118 | 2023-05-25 | 8260 | keep | 0 | May | 2023 | 0.0056258 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-05-25 17:58 | 2023-05-25 20:00 | 100 | 2:02 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO | M23052500116 | New_Event | Primary Wire Break | Include | Include | Equipment | 122 | 2023-05-25 | 12200 | keep | 0 | May | 2023 | 0.0083094 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-25 18:06 | 2023-05-25 18:24 | 2234 | 0:18 | T | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO DE ALIMENTADOR SE SECCIONALIZO ALIEMTADOR POR AISLADOR PARTIDO Y SE REMPLAZO 100% EN SERVICIO | B23052500298 | Additional_clients | Insulator/ Pin Failure | Include | Include | Equipment | 18 | 2023-05-25 | 40212 | keep | 0 | May | 2023 | 0.027388 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-25 18:07 | 2023-05-25 19:42 | 1 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L EVENTO TRANSFERIDO DE ARECIBO | A23052500143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-05-25 | 95 | keep | 0 | May | 2023 | 6.4704e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-25 18:07 | 2023-05-25 19:50 | 8 | 1:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 37.5 KVA 13200 VOLT AVERIADO | P23052500229 | New_Event | Service Transformer Failure | Include | Include | Equipment | 103 | 2023-05-25 | 824 | keep | 0 | May | 2023 | 0.00056122 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-05-25 18:12 | 2023-05-26 11:05 | 200 | 16:53 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23052500119 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1013 | 2023-05-25 | 202600 | keep | 0 | May | 2023 | 0.13799 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
VEGA BAJA | 2023-05-25 18:15 | 2023-05-25 20:17 | 5 | 2:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23052500287 | New_Event | Secondary Wire Break | Include | Include | Equipment | 122 | 2023-05-25 | 610 | keep | 0 | May | 2023 | 0.00041547 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-25 18:17 | 2023-05-26 08:45 | 6 | 14:28 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA Y SE CERRO XMR | B23052500288 | New_Event | Secondary Wire Break | Include | Include | Equipment | 868 | 2023-05-25 | 5208 | keep | 0 | May | 2023 | 0.0035471 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-05-25 18:38 | 2023-05-25 19:00 | 50 | 0:22 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO VIENTOS | P23052500251 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 22 | 2023-05-25 | 1100 | keep | 0 | May | 2023 | 0.0007492 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-05-25 18:40 | 2023-05-25 19:23 | 150 | 0:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN C/L SE REEMPLAZO CAJA PRINMARIA EVENTO TRANSFERIDO | P23052500253 | New_Event | Cutout Failure | Include | Include | Equipment | 43 | 2023-05-25 | 6450 | keep | 0 | May | 2023 | 0.0043931 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-25 18:41 | 2023-05-25 19:29 | 35 | 0:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | S23052500167 | New_Event | Secondary Wire Break | Include | Include | Equipment | 48 | 2023-05-25 | 1680 | keep | 0 | May | 2023 | 0.0011442 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-05-25 19:24 | 2023-05-26 11:39 | 40 | 16:15 | P | NO SE REPORTO CAUSA | 1 X 100 EN RISER | S23052500016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 975 | 2023-05-25 | 39000 | keep | 0 | May | 2023 | 0.026563 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-25 19:25 | 2023-05-25 21:00 | 50 | 1:35 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23052500273 | New_Event | Vegetation Contact | Include | Include | Vegetation | 95 | 2023-05-25 | 4750 | keep | 0 | May | 2023 | 0.0032352 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-25 19:29 | 2023-05-26 13:09 | 3 | 17:40 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 5 EN TRANSFORMADOR CAJA PORTA FUSIBLE DE TRANSFORMADOR BAJANTES SECUNDARIO DE TRANSFORMADOR Y SE REPARO SECUNDARIA | P23052500275 | New_Event | Cutout Failure | Include | Include | Equipment | 1060 | 2023-05-25 | 3180 | keep | 0 | May | 2023 | 0.0021659 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-05-25 19:35 | 2023-05-25 20:00 | 13 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE TRANSFORMAODR PARA REMPLAZAR BARRA DE NUTRAL SECUNDARIO R23050200032 | R23052500067 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-25 | 325 | keep | 0 | May | 2023 | 0.00022136 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-05-25 19:45 | 2023-05-26 09:00 | 25 | 13:15 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23052500320 | New_Event | Vegetation Contact | Include | Include | Vegetation | 795 | 2023-05-25 | 19875 | keep | 0 | May | 2023 | 0.013537 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-05-25 19:46 | 2023-05-26 08:30 | 30 | 12:44 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23052500322 | New_Event | Vegetation Contact | Include | Include | Vegetation | 764 | 2023-05-25 | 22920 | keep | 0 | May | 2023 | 0.015611 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-25 20:14 | 2023-05-25 20:15 | 3420 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C2305250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 3420 | keep | 0 | May | 2023 | 0.0023293 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
BAYAMON | 2023-05-25 20:36 | 2023-05-25 22:02 | 26 | 1:26 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L Y SE REMPLAZO CAJA PRIMARIA | B23052500506 | New_Event | Cutout Failure | Include | Include | Equipment | 86 | 2023-05-25 | 2236 | keep | 0 | May | 2023 | 0.0015229 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
CAGUAS | 2023-05-25 20:49 | 2023-05-25 20:50 | 3005 | 0:01 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C23052500504 | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-05-25 | 3005 | keep | 0 | May | 2023 | 0.0020467 | 0.0020467 | Momentary | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2023-05-25 20:50 | 2023-05-25 21:38 | 3005 | 0:48 | T | DESCONECTIVO DEFECTUOSO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | C23052500504 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 48 | 2023-05-25 | 144240 | keep | 0 | May | 2023 | 0.098241 | 0.0020467 | Sustained | FALSE | FALSE | Not_TMED_Event | 3005
CAGUAS | 2023-05-25 20:58 | 2023-05-26 09:50 | 8 | 12:52 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | C23052500516 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 772 | 2023-05-25 | 6176 | keep | 0 | May | 2023 | 0.0042064 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-25 21:23 | 2023-05-26 07:17 | 144 | 9:54 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO | S23052500514 | New_Event | Primary Wire Break | Include | Include | Equipment | 594 | 2023-05-25 | 85536 | keep | 0 | May | 2023 | 0.058258 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
BAYAMON | 2023-05-25 21:34 | 2023-05-25 21:35 | 3438 | 0:01 | T | DESCONECTIVO DEFECTUOSO | RECIERRE | B2305250000X | New_Event | Switch Failure | Include | Include | Equipment | 1 | 2023-05-25 | 3438 | keep | 0 | May | 2023 | 0.0023416 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-05-25 21:35 | 2023-05-26 02:13 | 2036 | 4:38 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO MACHETE QUEMADO Y 2 PUENTES QUEMADOS DE DOS FASES DISTINTAS | B23052500522 | 1st_after_momentary | Switch Failure | Include | Include | Equipment | 278 | 2023-05-25 | 566008 | keep | 0 | May | 2023 | 0.38551 | 0.0013867 | Sustained | FALSE | FALSE | Not_TMED_Event | 2036
CAGUAS | 2023-05-25 21:38 | 2023-05-25 23:02 | 3005 | 1:24 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR MACHETE QUEMADO G.O.I. CG-230525-02 - 66% EN SERVICIO | C23052500551 | Partial_restoration | Switch Failure | Include | Include | Equipment | 84 | 2023-05-25 | 252420 | keep | 0 | May | 2023 | 0.17192 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-25 21:45 | 2023-05-25 21:46 | 603 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 9206-09 | B2305250000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 603 | keep | 0 | May | 2023 | 0.0004107 | 0.0004107 | Momentary | FALSE | FALSE | Not_TMED_Event | 603
BAYAMON | 2023-05-25 21:45 | 2023-05-25 21:46 | 6 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR LLEVA 9206-09 | B2305250000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-25 | 6 | keep | 0 | May | 2023 | 4.0866e-06 | 4.0866e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 6
PONCE | 2023-05-25 21:49 | 2023-05-26 07:09 | 20 | 9:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO Y SE LEVANTO SECUNDARIA Y SE CERRO TRANSFORMADOR NO FUSIBLE | P23052500527 | New_Event | Secondary Wire Break | Include | Include | Equipment | 560 | 2023-05-25 | 11200 | keep | 0 | May | 2023 | 0.0076283 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-25 21:55 | 2023-05-26 09:50 | 8 | 11:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REMPLAZO PORTA FUSIBLE | A23052500507 | New_Event | Cutout Failure | Include | Include | Equipment | 715 | 2023-05-25 | 5720 | keep | 0 | May | 2023 | 0.0038959 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-25 22:28 | 2023-05-26 06:57 | 29 | 8:29 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23052500520 | New_Event | Vegetation Contact | Include | Include | Vegetation | 509 | 2023-05-25 | 14761 | keep | 0 | May | 2023 | 0.010054 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
AGUADILLA | 2023-05-25 22:48 | 2023-05-26 01:00 | 150 | 2:12 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23052500520 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 132 | 2023-05-25 | 19800 | keep | 0 | May | 2023 | 0.013486 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-05-25 22:51 | 2023-05-26 08:37 | 45 | 9:46 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO PENCA DE LA LINEA | C23052500560 | New_Event | Vegetation Contact | Include | Include | Vegetation | 586 | 2023-05-25 | 26370 | keep | 0 | May | 2023 | 0.01796 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-05-25 23:00 | 2023-05-25 23:01 | 3871 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23052500576 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 3871 | keep | 0 | May | 2023 | 0.0026365 | 0.0026365 | Momentary | FALSE | FALSE | Not_TMED_Event | 3871
CAGUAS | 2023-05-25 23:02 | 2023-05-25 23:31 | 1001 | 0:29 | P | DESCONECTIVO DEFECTUOSO | SE CERRO AMARRE CONTRA 3006-04 PARA REMPLAZO DE MACHETE QUEMADO G.O.I. CG-230525-02 - 100% EN SERVICIO | C23052500551 | Partial_restoration | Switch Failure | Include | Include | Equipment | 29 | 2023-05-25 | 29029 | keep | 0 | May | 2023 | 0.019772 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-25 23:04 | 2023-05-26 10:40 | 6 | 11:36 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE SECUNDARIO | A23052500512 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 696 | 2023-05-25 | 4176 | keep | 0 | May | 2023 | 0.0028443 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-25 23:44 | 2023-05-25 23:45 | 1843 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23052500579 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-25 | 1843 | keep | 0 | May | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BAYAMON | 2023-05-26 00:06 | 2023-05-26 16:01 | 140 | 15:55 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23052600001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 955 | 2023-05-26 | 133700 | keep | 0 | May | 2023 | 0.091062 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
VEGA BAJA | 2023-05-26 00:14 | 2023-05-26 00:16 | 4702 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23052600006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-26 | 9404 | keep | 0 | May | 2023 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
CAGUAS | 2023-05-26 00:29 | 2023-05-26 06:53 | 137 | 6:24 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA | C23052600004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 384 | 2023-05-26 | 52608 | keep | 0 | May | 2023 | 0.035831 | 9.331e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 137
MAYAGÃœEZ | 2023-05-26 01:21 | 2023-05-26 10:50 | 50 | 9:29 | P | CAUSAS EXTERNAS | 1 X 100 EN CORTE DE LINEA VEHICULO IMPACTO POSTE Y CRUZO LINEAS | M23052600001 | New_Event | Damage From Public | Include | Include | Public | 569 | 2023-05-26 | 28450 | keep | 0 | May | 2023 | 0.019377 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-26 01:40 | 2023-05-26 09:13 | 20 | 7:33 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA Y CAJA DE 100A | P23052600009 | New_Event | Cutout Failure | Include | Include | Equipment | 453 | 2023-05-26 | 9060 | keep | 0 | May | 2023 | 0.0061707 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-26 01:42 | 2023-05-26 13:37 | 80 | 11:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN PROVISIONAL AEREO SE REPORTA MAL TIEMPO EN ZONA | B23052600027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 715 | 2023-05-26 | 57200 | keep | 0 | May | 2023 | 0.038959 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-05-26 01:45 | 2023-05-26 01:46 | 733 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23052600522 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 733 | keep | 0 | May | 2023 | 0.00049924 | 0.00049924 | Momentary | FALSE | FALSE | Not_TMED_Event | 733
HUMACAO | 2023-05-26 02:01 | 2023-05-26 10:34 | 7 | 8:33 | P | ARBOL SOBRE LINEA | 1 X 30 EN CORTE DE LINEA SE RETIRO ARBOL DE LA LINEA | C23052600010 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 513 | 2023-05-26 | 3591 | keep | 0 | May | 2023 | 0.0024458 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-26 02:13 | 2023-05-26 04:24 | 3055 | 2:11 | P | DESCONECTIVO DEFECTUOSO | SE REEMPLAZO MACHETE QUEMADO Y 2 PUENTES QUEMADOS | B23052500522 | Additional_clients | Switch Failure | Include | Include | Equipment | 131 | 2023-05-26 | 400205 | keep | 0 | May | 2023 | 0.27258 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-26 02:13 | 2023-05-26 05:48 | 658 | 3:35 | T | CAUSAS EXTERNAS | DISPARO INTERRUPTOR ACCIDENTE CON VEHICULO MOTOR PARTE POSTE PRIMARIO SE SECCIONALIZA Y SE COLOCA INTERRUPTOR EN SERVICIO | P23052600014 | New_Event | Damage From Public | Include | Include | Public | 215 | 2023-05-26 | 141470 | keep | 0 | May | 2023 | 0.096355 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
MAYAGÃœEZ | 2023-05-26 02:13 | 2023-05-26 08:15 | 250 | 6:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA PARTIDA | M23052600008 | New_Event | Primary Wire Break | Include | Include | Equipment | 362 | 2023-05-26 | 90500 | keep | 0 | May | 2023 | 0.061639 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-05-26 02:33 | 2023-05-26 02:34 | 1210 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 1210 | keep | 0 | May | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
CANOVANAS | 2023-05-26 02:55 | 2023-05-27 09:50 | 30 | 30:55 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | R23052600158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1855 | 2023-05-26 | 55650 | keep | 0 | May | 2023 | 0.037903 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-26 02:58 | 2023-05-26 02:59 | 2379 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23052600020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 2379 | keep | 0 | May | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
BAYAMON | 2023-05-26 03:13 | 2023-05-26 14:40 | 191 | 11:27 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23052600009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 687 | 2023-05-26 | 131217 | keep | 0 | May | 2023 | 0.089371 | 0.00013009 | Sustained | FALSE | FALSE | Not_TMED_Event | 191
VEGA BAJA | 2023-05-26 04:21 | 2023-05-26 04:23 | 4702 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23052600075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-26 | 9404 | keep | 0 | May | 2023 | 0.006405 | 0.0032025 | Momentary | FALSE | FALSE | Not_TMED_Event | 4702
PONCE | 2023-05-26 04:39 | 2023-05-26 04:40 | 1007 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR NO RECERRO SE COLOCA RR EN OFF Y SE REALIZA PRUEBA Y QUEDA EN SERVICIO | P23052600024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 1007 | keep | 0 | May | 2023 | 0.00068586 | 0.00068586 | Momentary | FALSE | FALSE | Not_TMED_Event | 1007
CAGUAS | 2023-05-26 05:29 | 2023-05-26 05:30 | 1271 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23052600016 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 1271 | keep | 0 | May | 2023 | 0.00086567 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
VEGA BAJA | 2023-05-26 05:36 | 2023-05-26 12:30 | 15 | 6:54 | P | ANIMAL | 1 X 30 EN C/L SE RETIRO RANA | B23052600080 | New_Event | Animals | Include | Include | Wildlife | 414 | 2023-05-26 | 6210 | keep | 0 | May | 2023 | 0.0042296 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-05-26 05:48 | 2023-05-26 06:30 | 430 | 0:42 | P | CAUSAS EXTERNAS | SE CIERRA N/O CONTRA 5817-01 Y SE SECCIONALIZA AVERIA | P23052600014 | Partial_restoration | Damage From Public | Include | Include | Public | 42 | 2023-05-26 | 18060 | keep | 0 | May | 2023 | 0.012301 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-26 06:29 | 2023-05-26 06:30 | 3046 | 0:01 | T | ANIMAL | RECERRO LLEVA 1647-10 Y 15% DEL 1647-09 | R23052600003 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-26 | 3046 | keep | 0 | May | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-05-26 06:29 | 2023-05-26 06:30 | 307 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 15% POR 1646-03 | R23052600003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-26 | 307 | keep | 0 | May | 2023 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
CANOVANAS | 2023-05-26 06:29 | 2023-05-26 06:30 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO SU CARGA POR 1646-03 | R23052600003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-26 | 61 | keep | 0 | May | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-05-26 06:30 | 2023-05-26 10:14 | 109 | 3:44 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | R23052600005 | 1st_after_momentary | Animals | Include | Include | Wildlife | 224 | 2023-05-26 | 24416 | keep | 0 | May | 2023 | 0.01663 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
PONCE | 2023-05-26 06:30 | 2023-05-26 13:28 | 80 | 6:58 | P | CAUSAS EXTERNAS | TRABAJAR AVERIA DE POSTE PARTIDO POR IMPACTO DE AUTO BO GALICIA CAR 1 GOI-PC-230526-01A | P23052600034 | Partial_restoration | Damage From Public | Include | Include | Public | 418 | 2023-05-26 | 33440 | keep | 0 | May | 2023 | 0.022776 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-26 06:40 | 2023-05-26 06:42 | 1474 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO POR CONTROL QUEDO EN SERVICIO | R23052600004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-26 | 2948 | keep | 0 | May | 2023 | 0.0020079 | 0.0010039 | Momentary | FALSE | FALSE | Not_TMED_Event | 1474
GUAYAMA | 2023-05-26 07:16 | 2023-05-26 12:07 | 5 | 4:51 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR POR ANIMAL | P23052600047 | New_Event | Animals | Include | Include | Wildlife | 291 | 2023-05-26 | 1455 | keep | 0 | May | 2023 | 0.00099099 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-05-26 07:19 | 2023-05-26 11:05 | 30 | 3:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23052600022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 226 | 2023-05-26 | 6780 | keep | 0 | May | 2023 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-05-26 07:22 | 2023-05-26 10:40 | 4 | 3:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | P23052600049 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 198 | 2023-05-26 | 792 | keep | 0 | May | 2023 | 0.00053943 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-05-26 07:24 | 2023-05-26 10:34 | 1 | 3:10 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUCE FASE EVENTO TRANSFERIDO | P23052600053 | New_Event | Animals | Include | Include | Wildlife | 190 | 2023-05-26 | 190 | keep | 0 | May | 2023 | 0.00012941 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-26 07:34 | 2023-05-26 09:49 | 61 | 2:15 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR PALOMA | C23052600027 | New_Event | Animals | Include | Include | Wildlife | 135 | 2023-05-26 | 8235 | keep | 0 | May | 2023 | 0.0056088 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
MAYAGÃœEZ | 2023-05-26 07:41 | 2023-05-26 13:35 | 30 | 5:54 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23052600028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 354 | 2023-05-26 | 10620 | keep | 0 | May | 2023 | 0.0072332 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-26 07:44 | 2023-05-26 07:45 | 207 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO | S2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 207 | keep | 0 | May | 2023 | 0.00014099 | 0.00014099 | Momentary | FALSE | FALSE | Not_TMED_Event | 207
SAN JUAN | 2023-05-26 07:45 | 2023-05-26 15:12 | 40 | 7:27 | P | NO SE REPORTO CAUSA | 1X140 EN RISER 1X80 EN SU-1 | S23052600041 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 447 | 2023-05-26 | 17880 | keep | 0 | May | 2023 | 0.012178 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-26 07:48 | 2023-05-26 14:25 | 1 | 6:37 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | M23052600035 | New_Event | Vegetation Contact | Include | Include | Vegetation | 397 | 2023-05-26 | 397 | keep | 0 | May | 2023 | 0.00027039 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-26 07:56 | 2023-05-26 15:48 | 645 | 7:52 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO TRASPATIO | B23052600096 | New_Event | Primary Wire Break | Include | Include | Equipment | 472 | 2023-05-26 | 304440 | keep | 0 | May | 2023 | 0.20735 | 0.00043931 | Sustained | FALSE | FALSE | Not_TMED_Event | 645
CANOVANAS | 2023-05-26 08:03 | 2023-05-26 10:58 | 13 | 2:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN TRANSFORMADOR SE REMPLAZO PORTAFUSIBLE | R23052600009 | New_Event | Cutout Failure | Include | Include | Equipment | 175 | 2023-05-26 | 2275 | keep | 0 | May | 2023 | 0.0015495 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
VEGA BAJA | 2023-05-26 08:09 | 2023-05-26 09:44 | 60 | 1:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L NO CAUSA | B23052600100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 95 | 2023-05-26 | 5700 | keep | 0 | May | 2023 | 0.0038822 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-26 08:10 | 2023-05-26 08:21 | 12 | 0:11 | P | NO SE REPORTO CAUSA | 1 X 8 EN TRANSFORMADOR NO CAUSA | R23052600013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 11 | 2023-05-26 | 132 | keep | 0 | May | 2023 | 8.9905e-05 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
AGUADILLA | 2023-05-26 08:16 | 2023-05-26 14:20 | 8 | 6:04 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZO CONEXIONES EN BAJANTE PRIMARIO | P23052600082 | New_Event | Primary Wire Break | Include | Include | Equipment | 364 | 2023-05-26 | 2912 | keep | 0 | May | 2023 | 0.0019833 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
ARECIBO | 2023-05-26 08:28 | 2023-05-26 11:40 | 8 | 3:12 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052600007 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 192 | 2023-05-26 | 1536 | keep | 0 | May | 2023 | 0.0010462 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
FAJARDO | 2023-05-26 08:30 | 2023-05-26 10:52 | 208 | 2:22 | P | DESGANCHE | DESPEJE DE LINEA 1 X 100 EN CORTE DE LINEA | R23052600015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-05-26 | 29536 | keep | 0 | May | 2023 | 0.020117 | 0.00014167 | Sustained | FALSE | FALSE | Not_TMED_Event | 208
PONCE | 2023-05-26 08:31 | 2023-05-26 13:25 | 6 | 4:54 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 8 EN TRANSFORMADOR MAL TIEMPO | P23052600093 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 294 | 2023-05-26 | 1764 | keep | 0 | May | 2023 | 0.0012015 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-26 08:35 | 2023-05-26 10:33 | 40 | 1:58 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23052600103 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 118 | 2023-05-26 | 4720 | keep | 0 | May | 2023 | 0.0032148 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
PONCE | 2023-05-26 08:40 | 2023-05-26 15:08 | 75 | 6:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO VIENTOS | P23052600104 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 388 | 2023-05-26 | 29100 | keep | 0 | May | 2023 | 0.01982 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-05-26 08:42 | 2023-05-27 06:52 | 60 | 22:10 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052600106 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1330 | 2023-05-26 | 79800 | keep | 0 | May | 2023 | 0.054351 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-26 08:45 | 2023-05-26 10:04 | 23 | 1:19 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REMPLAZO SECUNDARIA QUEMADA | R23052600025 | New_Event | Secondary Wire Break | Include | Include | Equipment | 79 | 2023-05-26 | 1817 | keep | 0 | May | 2023 | 0.0012376 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BARRANQUITAS | 2023-05-26 08:46 | 2023-05-26 09:00 | 1 | 0:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN BANCO DE TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE | C23052600036 | New_Event | Cutout Failure | Include | Include | Equipment | 14 | 2023-05-26 | 14 | keep | 0 | May | 2023 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-26 08:48 | 2023-05-26 10:15 | 50 | 1:27 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA DESGANCHE | C23052600037 | New_Event | Vegetation Contact | Include | Include | Vegetation | 87 | 2023-05-26 | 4350 | keep | 0 | May | 2023 | 0.0029628 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-26 08:55 | 2023-05-26 14:50 | 1 | 5:55 | P | DESGANCHE | SE REALIZO DESGANCHE Y SE CERRO PUENTE PRIMARIO | A23052600010 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2023-05-26 | 355 | keep | 0 | May | 2023 | 0.00024179 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-26 09:06 | 2023-05-26 16:57 | 1 | 7:51 | P | CRUCETA DEFECTUOSA O AVERIADA | 3 X 25 C/L Y 1 X 15 EN XMR SE REPARO CRUCETA SAFADA SE REEMPLAZARON AISLADORES | C23052600040 | New_Event | Primary Crossarm Failure | Include | Include | Equipment | 471 | 2023-05-26 | 471 | keep | 0 | May | 2023 | 0.0003208 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-26 09:30 | 2023-05-26 10:45 | 10 | 1:15 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE | B23052600118 | New_Event | Primary Wire Break | Include | Include | Equipment | 75 | 2023-05-26 | 750 | keep | 0 | May | 2023 | 0.00051082 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-26 09:30 | 2023-05-26 09:41 | 1 | 0:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN BANCO DE TRANSFORMADORES SE REEMPLAZO PORTAFUSIBLE MAL TIEMPO | C23052600058 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 11 | 2023-05-26 | 11 | keep | 0 | May | 2023 | 7.492e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-26 09:38 | 2023-05-26 09:39 | 4634 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 4634 | keep | 0 | May | 2023 | 0.0031562 | 0.0031562 | Momentary | FALSE | FALSE | Not_TMED_Event | 4634
BAYAMON | 2023-05-26 09:40 | 2023-05-26 10:54 | 12 | 1:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO CAJA | B23052600122 | New_Event | Cutout Failure | Include | Include | Equipment | 74 | 2023-05-26 | 888 | keep | 0 | May | 2023 | 0.00060481 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-05-26 09:47 | 2023-05-26 13:43 | 11 | 3:56 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA PARA REEMPLAZAR 150 PIES DE SECUNDARIA | C23052600057 | New_Event | Secondary Wire Break | Include | Include | Equipment | 236 | 2023-05-26 | 2596 | keep | 0 | May | 2023 | 0.0017681 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-05-26 09:50 | 2023-05-26 11:30 | 48 | 1:40 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA EN VARIOS PUNTOS CLIENTES CONFIRMADOS CON EL PERSONAL DE CAMPO | B23052600125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 100 | 2023-05-26 | 4800 | keep | 0 | May | 2023 | 0.0032693 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
HUMACAO | 2023-05-26 09:53 | 2023-05-26 10:29 | 1593 | 0:36 | T | CAUSAS EXTERNAS | SE RETIRO TENSOR DE LA LINEA CON VARETA, CERRADO POR CONTROL | C23052600060 | New_Event | Damage From Public | Include | Include | Public | 36 | 2023-05-26 | 57348 | keep | 0 | May | 2023 | 0.039059 | 0.001085 | Sustained | FALSE | FALSE | Not_TMED_Event | 1593
CANOVANAS | 2023-05-26 09:56 | 2023-05-26 11:24 | 1 | 1:28 | P | ANIMAL | 1 X 40 EN RISER 1 X 25 EN BANCO TRANSFORMADOR CRUCE POR IGUANA EVENTO TRANSFERIDO | P23052600151 | New_Event | Animals | Include | Include | Wildlife | 88 | 2023-05-26 | 88 | keep | 0 | May | 2023 | 5.9936e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-26 09:59 | 2023-05-26 12:53 | 1 | 2:54 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA CRUCE POR AVE EVENTO TRANSFERIDO | P23052600154 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-05-26 | 174 | keep | 0 | May | 2023 | 0.00011851 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-26 10:16 | 2023-05-26 12:00 | 1 | 1:44 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 8 EN TRANSFORMADOR CORROCION EN CAJA | R23052600035 | New_Event | Cutout Failure | Include | Include | Equipment | 104 | 2023-05-26 | 104 | keep | 0 | May | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-26 10:17 | 2023-05-26 14:05 | 2 | 3:48 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE EVENTO TRANSFERIDO | P23052600165 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-05-26 | 456 | keep | 0 | May | 2023 | 0.00031058 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
PONCE | 2023-05-26 10:19 | 2023-05-26 10:20 | 2379 | 0:01 | T | ANIMAL | RECIERRE | P23052600166 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-26 | 2379 | keep | 0 | May | 2023 | 0.0016203 | 0.0016203 | Momentary | FALSE | FALSE | Not_TMED_Event | 2379
PONCE | 2023-05-26 10:20 | 2023-05-26 10:34 | 70 | 0:14 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23052600010 | 1st_after_momentary | Animals | Include | Include | Wildlife | 14 | 2023-05-26 | 980 | keep | 0 | May | 2023 | 0.00066747 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-05-26 10:25 | 2023-05-27 09:57 | 7 | 23:32 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR CAMION IMPACTO SECUNDARIA. | S23052600065 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1412 | 2023-05-26 | 9884 | keep | 0 | May | 2023 | 0.0067319 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-26 10:27 | 2023-05-26 14:55 | 15 | 4:28 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 18 EN TRANSFORMADOR MAL TIEMPO LLUVIAS EVENTO TRANSFERIDO DE PONCE | P23052600170 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 268 | 2023-05-26 | 4020 | keep | 0 | May | 2023 | 0.002738 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-05-26 10:30 | 2023-05-26 10:55 | 1 | 0:25 | P | PARARRAYOS DEFECTUOSO | 1 X 30 EN TRANSCLOSURE SE REEMPLAZO PARARRAYO | C23052600085 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 25 | 2023-05-26 | 25 | keep | 0 | May | 2023 | 1.7027e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-26 10:31 | 2023-05-26 10:36 | 790 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1342-03 | S23052600068 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-05-26 | 3950 | keep | 0 | May | 2023 | 0.0026903 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2023-05-26 10:31 | 2023-05-26 10:36 | 29 | 0:05 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE BKR LLEVA 1345-03 1345-01 Y 1342-02 | S23052600068 | New_Event | Primary Wire Break | Include | Include | Equipment | 5 | 2023-05-26 | 145 | keep | 0 | May | 2023 | 9.8759e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-05-26 10:31 | 2023-05-26 10:36 | 660 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1342-03 | S23052600068 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-05-26 | 3300 | keep | 0 | May | 2023 | 0.0022476 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-05-26 10:31 | 2023-05-26 10:36 | 259 | 0:05 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1342-03 | S23052600068 | New_Event | Feeder Load Transferred | Include | Include | Other | 5 | 2023-05-26 | 1295 | keep | 0 | May | 2023 | 0.00088202 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
PONCE | 2023-05-26 10:34 | 2023-05-26 11:16 | 10 | 0:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR MAL TIEMPO | P23052600086 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 42 | 2023-05-26 | 420 | keep | 0 | May | 2023 | 0.00028606 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-26 10:35 | 2023-05-26 14:08 | 6 | 3:33 | P | SECUNDARIA/DESGANCHE | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA DESGANCHAR Y REPARAR SECUNDARIA PROYECTO FIONA. | C23052600069 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 213 | 2023-05-26 | 1278 | keep | 0 | May | 2023 | 0.00087044 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-26 10:36 | 2023-05-26 10:56 | 263 | 0:20 | P | ALIMENTADOR AMARRADO | SE CERRO PUENTE EN TRONCAL | S23052600089 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 20 | 2023-05-26 | 5260 | keep | 0 | May | 2023 | 0.0035826 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 10:36 | 2023-05-26 10:56 | 9 | 0:20 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE ABIERTO EN TRONCAL 1342-03 LLEVA 1342-02 | S23052600089 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 20 | 2023-05-26 | 180 | keep | 0 | May | 2023 | 0.0001226 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 10:36 | 2023-05-26 10:56 | 220 | 0:20 | P | ALIMENTADOR AMARRADO | SE CERRO PUENTE EN EL TRONCAL | S23052600089 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 20 | 2023-05-26 | 4400 | keep | 0 | May | 2023 | 0.0029968 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-26 10:37 | 2023-05-26 12:58 | 119 | 2:21 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C23052600092 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 141 | 2023-05-26 | 16779 | keep | 0 | May | 2023 | 0.011428 | 8.105e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 119
BARRANQUITAS | 2023-05-26 10:37 | 2023-05-26 13:36 | 109 | 2:59 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23052600091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 179 | 2023-05-26 | 19511 | keep | 0 | May | 2023 | 0.013289 | 7.4239e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 109
MAYAGÃœEZ | 2023-05-26 10:42 | 2023-05-26 13:40 | 80 | 2:58 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE NECESITA DESGANCHE | M23052600086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-05-26 | 14240 | keep | 0 | May | 2023 | 0.0096988 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-26 10:45 | 2023-05-26 11:20 | 60 | 0:35 | P | MAL TIEMPO/RAYOS | 2 X 65 Y 2 X 50 EN C/L SE REPORTA FUERTES LLUVIAS | B23052600145 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 35 | 2023-05-26 | 2100 | keep | 0 | May | 2023 | 0.0014303 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-05-26 10:50 | 2023-05-26 13:07 | 10 | 2:17 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | C23052600100 | New_Event | Animals | Include | Include | Wildlife | 137 | 2023-05-26 | 1370 | keep | 0 | May | 2023 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-26 10:58 | 2023-05-27 09:43 | 6 | 22:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 65 EN C/L MAL TIEMPO LLUVIA | B23052600150 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1365 | 2023-05-26 | 8190 | keep | 0 | May | 2023 | 0.0055782 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-26 11:07 | 2023-05-27 11:55 | 39 | 24:48 | P | ANIMAL | 1 X 25 EN SU-3C CRUCE X RATON EN EL T-7 | B23052600153 | New_Event | Animals | Include | Include | Wildlife | 1488 | 2023-05-26 | 58032 | keep | 0 | May | 2023 | 0.039525 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CANOVANAS | 2023-05-26 11:13 | 2023-05-26 11:50 | 6 | 0:37 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRA EN PEDESTAL T-321 | R23052600041 | New_Event | Secondary Wire Break | Include | Include | Equipment | 37 | 2023-05-26 | 222 | keep | 0 | May | 2023 | 0.0001512 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-26 11:18 | 2023-05-26 14:00 | 1 | 2:42 | P | DESGANCHE | 1 X 10 EN XMR DESGANCHE | C23052600110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 162 | 2023-05-26 | 162 | keep | 0 | May | 2023 | 0.00011034 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-26 11:20 | 2023-05-26 11:21 | 3070 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 3070 | keep | 0 | May | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BARRANQUITAS | 2023-05-26 11:40 | 2023-05-26 16:24 | 70 | 4:44 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23052600118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 284 | 2023-05-26 | 19880 | keep | 0 | May | 2023 | 0.01354 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-05-26 11:42 | 2023-05-26 15:25 | 6 | 3:43 | P | MAL TIEMPO/RAYOS | 1 X X 10 EN TRANSFORMADOR POR RAYOS | P23052600209 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 223 | 2023-05-26 | 1338 | keep | 0 | May | 2023 | 0.00091131 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-26 11:46 | 2023-05-26 11:47 | 215 | 0:01 | T | DESGANCHE | DISPARO Y SE CERRO POR CONTROL | B23052600170 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-26 | 215 | keep | 0 | May | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-05-26 11:47 | 2023-05-26 16:07 | 48 | 4:20 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23052600170 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 260 | 2023-05-26 | 12480 | keep | 0 | May | 2023 | 0.0085001 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
HUMACAO | 2023-05-26 11:54 | 2023-05-26 15:33 | 1 | 3:39 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE EVENTO TRANSFERIDO | P23052600214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 219 | 2023-05-26 | 219 | keep | 0 | May | 2023 | 0.00014916 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-26 11:58 | 2023-05-26 15:45 | 1 | 3:47 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN CORTE DE LINEA CAJA PRIMARIA EVENTO TRANSFERIDO DE PONCE | P23052600050 | New_Event | Cutout Failure | Include | Include | Equipment | 227 | 2023-05-26 | 227 | keep | 0 | May | 2023 | 0.00015461 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-26 12:00 | 2023-05-26 13:08 | 40 | 1:08 | P | ANIMAL | 1 X 65 EN C/L CRUCE POR AVE | B23052600175 | New_Event | Animals | Include | Include | Wildlife | 68 | 2023-05-26 | 2720 | keep | 0 | May | 2023 | 0.0018526 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-26 12:06 | 2023-05-26 14:34 | 75 | 2:28 | P | NO SE REPORTO CAUSA | 1 X 40 EN CORTE DE LINEA NO CAUSA | R23052600050 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 148 | 2023-05-26 | 11100 | keep | 0 | May | 2023 | 0.0075602 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
VEGA BAJA | 2023-05-26 12:13 | 2023-05-26 19:41 | 45 | 7:28 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A23052600034 | New_Event | Vegetation Contact | Include | Include | Vegetation | 448 | 2023-05-26 | 20160 | keep | 0 | May | 2023 | 0.013731 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-05-26 12:13 | 2023-05-26 15:59 | 30 | 3:46 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23052600181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 226 | 2023-05-26 | 6780 | keep | 0 | May | 2023 | 0.0046178 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
FAJARDO | 2023-05-26 12:16 | 2023-05-26 15:12 | 206 | 2:56 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | R23052600053 | New_Event | Cutout Failure | Include | Include | Equipment | 176 | 2023-05-26 | 36256 | keep | 0 | May | 2023 | 0.024694 | 0.00014031 | Sustained | FALSE | FALSE | Not_TMED_Event | 206
SAN JUAN | 2023-05-26 12:18 | 2023-05-26 13:36 | 9 | 1:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTES SECUNDARIOS | S23052600110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 78 | 2023-05-26 | 702 | keep | 0 | May | 2023 | 0.00047813 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
HUMACAO | 2023-05-26 12:29 | 2023-05-26 14:04 | 25 | 1:35 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23052600129 | New_Event | Animals | Include | Include | Wildlife | 95 | 2023-05-26 | 2375 | keep | 0 | May | 2023 | 0.0016176 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-26 12:42 | 2023-05-26 14:27 | 11 | 1:45 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA DESGANCHE SECUNDARIO | S23052600117 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 105 | 2023-05-26 | 1155 | keep | 0 | May | 2023 | 0.00078667 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
BAYAMON | 2023-05-26 12:54 | 2023-05-26 12:57 | 2617 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B23052600199 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-26 | 7851 | keep | 0 | May | 2023 | 0.0053473 | 0.0017824 | Momentary | FALSE | FALSE | Not_TMED_Event | 2617
BAYAMON | 2023-05-26 12:55 | 2023-05-26 12:57 | 1368 | 0:02 | T | NO SE REPORTO CAUSA | CERRADO EN SCADA EN SERVICIO | S23052600119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-26 | 2736 | keep | 0 | May | 2023 | 0.0018635 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2023-05-26 13:00 | 2023-05-26 13:12 | 427 | 0:12 | T | NO SE REPORTO CAUSA | CERRADO POR SCADA SUBESTACION TIENE RETRAZO EN REFLEJAR OPERACION | S23052600121 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 12 | 2023-05-26 | 5124 | keep | 0 | May | 2023 | 0.0034899 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
AGUADILLA | 2023-05-26 13:07 | 2023-05-26 14:40 | 300 | 1:33 | P | CAUSAS EXTERNAS | 1 X 65 EN CORTE DE LINEA POR IMPACTO DE CAMION | M23052600115 | New_Event | Damage From Public | Include | Include | Public | 93 | 2023-05-26 | 27900 | keep | 0 | May | 2023 | 0.019003 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
BAYAMON | 2023-05-26 13:09 | 2023-05-26 14:45 | 3798 | 1:36 | S | MAL TIEMPO/RAYOS | MAL TIEMPO REPORTAN QUE CAYO RAYO EN SUBESTACION | B23052600213 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 96 | 2023-05-26 | 364608 | keep | 0 | May | 2023 | 0.24833 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2023-05-26 13:09 | 2023-05-26 14:44 | 4622 | 1:35 | S | MAL TIEMPO/RAYOS | MAL TIEMPO REPORTAN QUE CAYO RAYO EN SUBESTACION | B23052600213 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 95 | 2023-05-26 | 439090 | keep | 0 | May | 2023 | 0.29906 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2023-05-26 13:09 | 2023-05-26 14:44 | 4089 | 1:35 | S | MAL TIEMPO/RAYOS | MAL TIEMPO REPORTAN QUE CAYO RAYO EN SUBESTACION | B23052600213 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 95 | 2023-05-26 | 388455 | keep | 0 | May | 2023 | 0.26457 | 0.002785 | Sustained | FALSE | FALSE | Not_TMED_Event | 4089
SAN JUAN | 2023-05-26 13:13 | 2023-05-26 13:20 | 34 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5900 EN SERVCIO LLEVA 50% 1910-01 LLEVA 50% 1519-03 | S23052600128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-26 | 238 | keep | 0 | May | 2023 | 0.0001621 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
SAN JUAN | 2023-05-26 13:13 | 2023-05-26 13:20 | 19 | 0:07 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5900 EN SERVCIO LLEVA 50% 1910-01 LLEVA 50% 1519-03 | S23052600128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-26 | 133 | keep | 0 | May | 2023 | 9.0586e-05 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
SAN JUAN | 2023-05-26 13:13 | 2023-05-26 13:20 | 97 | 0:07 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5900 EN SERVCIO | S23052600128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-26 | 679 | keep | 0 | May | 2023 | 0.00046246 | 6.6066e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 97
BAYAMON | 2023-05-26 13:13 | 2023-05-26 13:20 | 19 | 0:07 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5900 EN SERVCIO | S23052600128 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 7 | 2023-05-26 | 133 | keep | 0 | May | 2023 | 9.0586e-05 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
ARECIBO | 2023-05-26 13:21 | 2023-05-26 16:10 | 30 | 2:49 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA CRUCE DE FASE PRIMARIA POR BAMBU | A23052600049 | New_Event | Vegetation Contact | Include | Include | Vegetation | 169 | 2023-05-26 | 5070 | keep | 0 | May | 2023 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-26 13:28 | 2023-05-26 13:50 | 658 | 0:22 | T | CAUSAS EXTERNAS | SE ABRE INTERRUPTOR PARA CERRAR PUENTES PRIMARIOS Y NORMALIZAR CARGA DEBIDO A AVERIA CAUSADA POR VEHICULO DE MOTOR EL CUAL PARTE POSTE PRIMARIO GOI PC-230526-01A | P23052600258 | New_Event | Damage From Public | Include | Include | Public | 22 | 2023-05-26 | 14476 | keep | 0 | May | 2023 | 0.0098595 | 0.00044816 | Sustained | FALSE | FALSE | Not_TMED_Event | 658
BAYAMON | 2023-05-26 13:29 | 2023-05-27 08:49 | 15 | 19:20 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | S23052600135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1160 | 2023-05-26 | 17400 | keep | 0 | May | 2023 | 0.011851 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-05-26 13:31 | 2023-05-26 15:40 | 80 | 2:09 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | C23052600147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 129 | 2023-05-26 | 10320 | keep | 0 | May | 2023 | 0.0070289 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-26 13:32 | 2023-05-26 16:02 | 100 | 2:30 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | M23052600120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 150 | 2023-05-26 | 15000 | keep | 0 | May | 2023 | 0.010216 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-05-26 13:35 | 2023-05-26 13:36 | 234 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 QUEDO EN SERVICIO CERRAR ACB 11221C POR PUENTE ABIERTO EN LINEA 11200 | P23052600261 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-26 | 234 | keep | 0 | May | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-05-26 13:35 | 2023-05-26 13:36 | 2468 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE LINEA 200 QUEDO EN SERVICIO CERRAR ACB 11221C POR PUENTE ABIERTO EN LINEA 11200 | P23052600261 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-26 | 2468 | keep | 0 | May | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
CAGUAS | 2023-05-26 13:36 | 2023-05-26 14:13 | 499 | 0:37 | P | DESGANCHE | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA QUEMADA DESGANCHE | C23052600148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 37 | 2023-05-26 | 18463 | keep | 0 | May | 2023 | 0.012575 | 0.00033987 | Sustained | FALSE | FALSE | Not_TMED_Event | 499
BARRANQUITAS | 2023-05-26 13:43 | 2023-05-26 14:52 | 12 | 1:09 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA, DESGANCHE SECUNDARIO Y SE REGULO VOLTAJE DEL TAP 3 AL 1 SE DEJO EN 124/FASE | C23052600150 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 69 | 2023-05-26 | 828 | keep | 0 | May | 2023 | 0.00056395 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-26 13:49 | 2023-05-26 17:10 | 1 | 3:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR Y SE REPARO SECUNDARIA | S23052600140 | New_Event | Secondary Wire Break | Include | Include | Equipment | 201 | 2023-05-26 | 201 | keep | 0 | May | 2023 | 0.0001369 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-26 14:01 | 2023-05-26 14:02 | 1588 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1716-03 LLEVA 1711-01 Y LLEVA 1711-03 | B23052600233 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-26 | 1588 | keep | 0 | May | 2023 | 0.0010816 | 0.0010816 | Momentary | FALSE | FALSE | Not_TMED_Event | 1588
BAYAMON | 2023-05-26 14:01 | 2023-05-26 14:02 | 13 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 1716-03 LLEVA 1711-01 Y LLEVA 1711-03 | B23052600233 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-26 | 13 | keep | 0 | May | 2023 | 8.8542e-06 | 8.8542e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 13
BAYAMON | 2023-05-26 14:01 | 2023-05-26 14:02 | 1812 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR 1716-03 LLEVA 1711-01 Y LLEVA 1711-03 | B23052600233 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-26 | 1812 | keep | 0 | May | 2023 | 0.0012341 | 0.0012341 | Momentary | FALSE | FALSE | Not_TMED_Event | 1812
BAYAMON | 2023-05-26 14:02 | 2023-05-27 13:31 | 50 | 23:29 | P | ANIMAL | 1 X 40 EN CN PROVISIONAL CRUCE X AVE | B23052600234 | New_Event | Animals | Include | Include | Wildlife | 1409 | 2023-05-26 | 70450 | keep | 0 | May | 2023 | 0.047983 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-26 14:02 | 2023-05-26 20:37 | 40 | 6:35 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO | B23052600236 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 395 | 2023-05-26 | 15800 | keep | 0 | May | 2023 | 0.010761 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-26 14:02 | 2023-05-26 17:10 | 1 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 20 NX EN SWITCH UNIT NO SE REPORTO CAUSA | A23052600054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-05-26 | 188 | keep | 0 | May | 2023 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-26 14:06 | 2023-05-26 14:07 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
BAYAMON | 2023-05-26 14:07 | 2023-05-27 11:11 | 39 | 21:04 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE XMR AVERIADO DE 50KVA X 50KVA | B23052600238 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1264 | 2023-05-26 | 49296 | keep | 0 | May | 2023 | 0.033575 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2023-05-26 14:13 | 2023-05-26 14:14 | 1307 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C23052600160 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-26 | 1307 | keep | 0 | May | 2023 | 0.00089019 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-26 14:14 | 2023-05-26 14:31 | 499 | 0:17 | P | DESGANCHE | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA QUEMADA DESGANCHE | C23052600148 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 17 | 2023-05-26 | 8483 | keep | 0 | May | 2023 | 0.0057777 | 0.00033987 | Sustained | FALSE | FALSE | Not_TMED_Event | 499
AGUADILLA | 2023-05-26 14:22 | 2023-05-26 14:52 | 80 | 0:30 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR IGUANA | M23052600132 | New_Event | Animals | Include | Include | Wildlife | 30 | 2023-05-26 | 2400 | keep | 0 | May | 2023 | 0.0016346 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
PONCE | 2023-05-26 14:30 | 2023-05-26 16:56 | 116 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | P23052600283 | New_Event | Primary Wire Break | Include | Include | Equipment | 146 | 2023-05-26 | 16936 | keep | 0 | May | 2023 | 0.011535 | 7.9007e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 116
CAGUAS | 2023-05-26 14:31 | 2023-05-26 14:32 | 1307 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | C23052600166 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-26 | 1307 | keep | 0 | May | 2023 | 0.00089019 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-26 14:32 | 2023-05-26 17:32 | 499 | 3:00 | P | DESGANCHE | 1 X 100 EN C/L SE REEMPLAZO CAJA PRIMARIA QUEMADA DESGANCHE | C23052600148 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 180 | 2023-05-26 | 89820 | keep | 0 | May | 2023 | 0.061176 | 0.00033987 | Sustained | FALSE | FALSE | Not_TMED_Event | 499
AGUADILLA | 2023-05-26 14:38 | 2023-05-26 15:23 | 6 | 0:45 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR POR RAYO | P23052600293 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 45 | 2023-05-26 | 270 | keep | 0 | May | 2023 | 0.0001839 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-26 14:42 | 2023-05-26 18:08 | 40 | 3:26 | P | ANIMAL | 1X80 EN C/L CRUCE POR AVE | S23052600145 | New_Event | Animals | Include | Include | Wildlife | 206 | 2023-05-26 | 8240 | keep | 0 | May | 2023 | 0.0056122 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-26 14:42 | 2023-05-26 14:48 | 1058 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23052600147 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-26 | 6348 | keep | 0 | May | 2023 | 0.0043236 | 0.0007206 | Sustained | FALSE | FALSE | Not_TMED_Event | 1058
SAN JUAN | 2023-05-26 14:42 | 2023-05-26 14:48 | 1000 | 0:06 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23052600147 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-26 | 6000 | keep | 0 | May | 2023 | 0.0040866 | 0.0006811 | Sustained | FALSE | FALSE | Not_TMED_Event | 1000
SAN JUAN | 2023-05-26 14:42 | 2023-05-26 14:48 | 278 | 0:06 | T | DESGANCHE | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23052600147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 6 | 2023-05-26 | 1668 | keep | 0 | May | 2023 | 0.0011361 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-26 14:42 | 2023-05-26 14:48 | 1295 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23052600147 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-26 | 7770 | keep | 0 | May | 2023 | 0.0052921 | 0.00088202 | Sustained | FALSE | FALSE | Not_TMED_Event | 1295
SAN JUAN | 2023-05-26 14:42 | 2023-05-26 14:48 | 9 | 0:06 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CONFIRMO PERSONAL FUERA Y SE CERRO POR CONTROL | S23052600147 | New_Event | Feeder Load Transferred | Include | Include | Other | 6 | 2023-05-26 | 54 | keep | 0 | May | 2023 | 3.6779e-05 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
VEGA BAJA | 2023-05-26 14:52 | 2023-05-26 20:15 | 45 | 5:23 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | A23052600059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-05-26 | 14535 | keep | 0 | May | 2023 | 0.0098997 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-05-26 14:56 | 2023-05-26 17:02 | 1058 | 2:06 | P | ALIMENTADOR AMARRADO | 20% DE SU CARGA POR 1424-08 SE REALIZO DESGANCHE DE PISO (A VARETA) EN TRAMO DEL 1348-07 MEDIANTE SWITCHING FORM SJ-230526-01 - 100% EN SERVICIO | S23052600157 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 126 | 2023-05-26 | 133308 | keep | 0 | May | 2023 | 0.090795 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 14:56 | 2023-05-26 15:58 | 1000 | 1:02 | P | ALIMENTADOR AMARRADO | LLEVA 1401-10 - 100% EN SERVICIO LLEVA 1348-07 - 90% EN SERVICIO LLEVA 80% DEL 1348-06 - EN SERVICIO TOTAL LLEVA 20% DEL 1336-08 - AUN FUERA DE SERVICIO SE SECCIONALIZO PARA DESGANCHE PRIMARIO EN TRAMO DEL 1348-07 SWITCHING FORM SJ-230526-01 | S23052600157 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 62 | 2023-05-26 | 62000 | keep | 0 | May | 2023 | 0.042228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 14:56 | 2023-05-26 15:58 | 278 | 1:02 | T | DESGANCHE | LLEVA 1401-10 - 100% EN SERVICIO LLEVA 1348-07 - 90% EN SERVICIO LLEVA 80% DEL 1348-06 - EN SERVICIO TOTAL LLEVA 20% DEL 1336-08 - AUN FUERA DE SERVICIO SE SECCIONALIZO PARA DESGANCHE PRIMARIO EN TRAMO DEL 1348-07 SWITCHING FORM SJ-230526-01 | S23052600157 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 62 | 2023-05-26 | 17236 | keep | 0 | May | 2023 | 0.011739 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 14:56 | 2023-05-26 15:58 | 1295 | 1:02 | T | ALIMENTADOR AMARRADO | LLEVA 1401-10 - 100% EN SERVICIO LLEVA 1348-07 - 90% EN SERVICIO LLEVA 80% DEL 1348-06 - EN SERVICIO TOTAL LLEVA 20% DEL 1336-08 - AUN FUERA DE SERVICIO SE SECCIONALIZO PARA DESGANCHE PRIMARIO EN TRAMO DEL 1348-07 SWITCHING FORM SJ-230526-01 | S23052600157 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 62 | 2023-05-26 | 80290 | keep | 0 | May | 2023 | 0.054685 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 14:56 | 2023-05-26 15:58 | 9 | 1:02 | T | ALIMENTADOR AMARRADO | LLEVA 1401-10 - 100% EN SERVICIO LLEVA 1348-07 - 90% EN SERVICIO LLEVA 80% DEL 1348-06 - EN SERVICIO TOTAL LLEVA 20% DEL 1336-08 - AUN FUERA DE SERVICIO SE SECCIONALIZO PARA DESGANCHE PRIMARIO EN TRAMO DEL 1348-07 SWITCHING FORM SJ-230526-01 | S23052600157 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 62 | 2023-05-26 | 558 | keep | 0 | May | 2023 | 0.00038005 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-26 14:57 | 2023-05-26 19:45 | 106 | 4:48 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23052600177 | New_Event | Animals | Include | Include | Wildlife | 288 | 2023-05-26 | 30528 | keep | 0 | May | 2023 | 0.020792 | 7.2196e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 106
SAN JUAN | 2023-05-26 15:00 | 2023-05-26 19:45 | 15 | 4:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO EN C/L PARA REMPLAZAR (2) POSTES PRIMARIOS PARTIDOS | S23052600075 | New_Event | Primary Pole Failure | Include | Include | Equipment | 285 | 2023-05-26 | 4275 | keep | 0 | May | 2023 | 0.0029117 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-05-26 15:01 | 2023-05-26 15:02 | 956 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052600077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 956 | keep | 0 | May | 2023 | 0.00065113 | 0.00065113 | Momentary | FALSE | FALSE | Not_TMED_Event | 956
CAGUAS | 2023-05-26 15:01 | 2023-05-26 15:02 | 638 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 638 | keep | 0 | May | 2023 | 0.00043454 | 0.00043454 | Momentary | FALSE | FALSE | Not_TMED_Event | 638
SAN JUAN | 2023-05-26 15:09 | 2023-05-27 11:59 | 6 | 20:50 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23052600164 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1250 | 2023-05-26 | 7500 | keep | 0 | May | 2023 | 0.0051082 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-05-26 15:17 | 2023-05-26 17:01 | 100 | 1:44 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23052600185 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-05-26 | 10400 | keep | 0 | May | 2023 | 0.0070834 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-26 15:27 | 2023-05-26 18:12 | 250 | 2:45 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO EN MACHETE | C23052600196 | New_Event | Primary Wire Break | Include | Include | Equipment | 165 | 2023-05-26 | 41250 | keep | 0 | May | 2023 | 0.028095 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
PONCE | 2023-05-26 15:46 | 2023-05-26 16:55 | 150 | 1:09 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | P23052600355 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2023-05-26 | 10350 | keep | 0 | May | 2023 | 0.0070493 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-26 15:48 | 2023-05-26 17:59 | 1355 | 2:11 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO BKR A PETICION DE JOSE GONZALEZ PARA SECCIONALIZAR CONDUCTOR TRASPATIO 30% X 1708-02 | B23052600096 | New_Event | Primary Wire Break | Include | Include | Equipment | 131 | 2023-05-26 | 177505 | keep | 0 | May | 2023 | 0.1209 | 0.00092288 | Sustained | FALSE | FALSE | Not_TMED_Event | 1355
BAYAMON | 2023-05-26 15:50 | 2023-05-27 14:22 | 9 | 22:32 | P | DESGANCHE | 2 X 15 EN XMR SE DESGANCHO PRIMARIO | B23052600291 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1352 | 2023-05-26 | 12168 | keep | 0 | May | 2023 | 0.0082876 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
SAN JUAN | 2023-05-26 15:58 | 2023-05-26 17:02 | 27 | 1:04 | P | DESGANCHE | CARGA TRANSFERIDA AL 1424-08 SE REALIZO DESGANCHE DE PISO (A VARETA) EN TRAMO DEL 1348-07 MEDIANTE SWITCHING FORM SJ-230526-01 - 100% EN SERVICIO | S23052600157 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 64 | 2023-05-26 | 1728 | keep | 0 | May | 2023 | 0.0011769 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-26 16:02 | 2023-05-27 00:28 | 1250 | 8:26 | P | DESCONECTIVO DEFECTUOSO | SE PUENTEO MACHETE DEBIDO A QUE HAY FASE AVERIADA EN EL MACHETE DE BARRA SF BY-230526-05 | B23052600303 | New_Event | Switch Failure | Include | Include | Equipment | 506 | 2023-05-26 | 632500 | keep | 0 | May | 2023 | 0.43079 | 0.00085137 | Sustained | FALSE | FALSE | Not_TMED_Event | 1250
VEGA BAJA | 2023-05-26 16:07 | 2023-05-26 16:14 | 215 | 0:07 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA | B23052600310 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 7 | 2023-05-26 | 1505 | keep | 0 | May | 2023 | 0.001025 | 0.00014644 | Sustained | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-05-26 16:14 | 2023-05-26 17:22 | 48 | 1:08 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23052600170 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 68 | 2023-05-26 | 3264 | keep | 0 | May | 2023 | 0.0022231 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 16:20 | 2023-05-26 16:24 | 2052 | 0:04 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR EL 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-26 | 8208 | keep | 0 | May | 2023 | 0.0055904 | 0.0013976 | Momentary | FALSE | FALSE | Not_TMED_Event | 2052
SAN JUAN | 2023-05-26 16:20 | 2023-05-26 16:24 | 134 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1111-01 20% DE SU CARGA POR EL 1118-10 LLEVA LA CARGA DEL 1115-03 SE CERRO POR CONTROL | S2305260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-26 | 536 | keep | 0 | May | 2023 | 0.00036507 | 9.1267e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 134
HUMACAO | 2023-05-26 16:33 | 2023-05-26 17:31 | 12 | 0:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23052600254 | New_Event | Secondary Wire Break | Include | Include | Equipment | 58 | 2023-05-26 | 696 | keep | 0 | May | 2023 | 0.00047404 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-05-26 16:37 | 2023-05-26 18:54 | 15 | 2:17 | P | ANIMAL | 1 X 30 EN XMR AVE CRUZO LINEAS | P23052600388 | New_Event | Animals | Include | Include | Wildlife | 137 | 2023-05-26 | 2055 | keep | 0 | May | 2023 | 0.0013997 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BARRANQUITAS | 2023-05-26 16:47 | 2023-05-26 18:55 | 29 | 2:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 40 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | C23052600175 | New_Event | Primary Wire Break | Include | Include | Equipment | 128 | 2023-05-26 | 3712 | keep | 0 | May | 2023 | 0.0025282 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
HUMACAO | 2023-05-26 16:50 | 2023-05-26 18:23 | 100 | 1:33 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23052600271 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-05-26 | 9300 | keep | 0 | May | 2023 | 0.0063342 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-05-26 16:53 | 2023-05-26 17:55 | 1 | 1:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 15 EN MONTURA EN XMR MAL TIEMPO LLUVIAS | B23052600332 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 62 | 2023-05-26 | 62 | keep | 0 | May | 2023 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-26 17:06 | 2023-05-26 19:20 | 100 | 2:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA | R23052600087 | New_Event | Cutout Failure | Include | Include | Equipment | 134 | 2023-05-26 | 13400 | keep | 0 | May | 2023 | 0.0091267 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-26 17:15 | 2023-05-26 17:17 | 220 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S2305260000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-26 | 440 | keep | 0 | May | 2023 | 0.00029968 | 0.00014984 | Momentary | FALSE | FALSE | Not_TMED_Event | 220
SAN JUAN | 2023-05-26 17:15 | 2023-05-26 17:17 | 870 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1303-05 LLEVA 98% DEL 1303-04 SE CERRO POR CONTROL | S2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-26 | 1740 | keep | 0 | May | 2023 | 0.0011851 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-05-26 17:24 | 2023-05-26 17:25 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | S2305260000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
FAJARDO | 2023-05-26 17:24 | 2023-05-26 17:25 | 1394 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052600090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-26 | 1394 | keep | 0 | May | 2023 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
PONCE | 2023-05-26 17:26 | 2023-05-26 19:38 | 15 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN C/L MAL TIEMPO VIENTOS | P23052600430 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-05-26 | 1980 | keep | 0 | May | 2023 | 0.0013486 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-26 17:29 | 2023-05-27 10:26 | 7 | 16:57 | P | MAL TIEMPO/RAYOS | 1 X 10 EN XMR MAL TIEMPO RAYOS | C23052600307 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1017 | 2023-05-26 | 7119 | keep | 0 | May | 2023 | 0.0048487 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-26 17:45 | 2023-05-26 17:58 | 61 | 0:13 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL | B2305260000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2023-05-26 | 793 | keep | 0 | May | 2023 | 0.00054011 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
SAN JUAN | 2023-05-26 17:49 | 2023-05-26 20:00 | 1420 | 2:11 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1526-02 LLEVA LA CARGA DEL 1530-06 SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO G.O.I. SJ-230526-02 - 10% EN SERVICIO | S23052600229 | New_Event | Primary Wire Break | Include | Include | Equipment | 131 | 2023-05-26 | 186020 | keep | 0 | May | 2023 | 0.1267 | 0.00096716 | Sustained | FALSE | FALSE | Not_TMED_Event | 1420
SAN JUAN | 2023-05-26 17:49 | 2023-05-26 22:26 | 437 | 4:37 | T | ALIMENTADOR AMARRADO | CARGA POR EL 1526-02 SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO MEDIANTE G.O.I. SJ-230526-02 | S23052600229 | New_Event | Feeder Load Transferred | Include | Include | Other | 277 | 2023-05-26 | 121049 | keep | 0 | May | 2023 | 0.082446 | 0.00029764 | Sustained | FALSE | FALSE | Not_TMED_Event | 437
BAYAMON | 2023-05-26 17:53 | 2023-05-26 19:37 | 1 | 1:44 | P | NO SE REPORTO CAUSA | 1 X 15 EN MONTURA EN XMR | B23052600384 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 104 | 2023-05-26 | 104 | keep | 0 | May | 2023 | 7.0834e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-26 17:55 | 2023-05-26 17:56 | 4027 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | B23052600387 | Additional_clients | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-26 | 4027 | keep | 0 | May | 2023 | 0.0027428 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
VEGA BAJA | 2023-05-26 17:56 | 2023-05-26 18:11 | 1 | 0:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 15 EN MONTURA EN XMR MAL TIEMPO LLUVIAS | B23052600332 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 15 | 2023-05-26 | 15 | keep | 0 | May | 2023 | 1.0216e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-26 18:04 | 2023-05-26 18:44 | 50 | 0:40 | P | NO SE REPORTO CAUSA | 1 X 30 EN C/L | C23052600330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 40 | 2023-05-26 | 2000 | keep | 0 | May | 2023 | 0.0013622 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
GUAYAMA | 2023-05-26 18:06 | 2023-05-26 18:12 | 15 | 0:06 | P | MAL TIEMPO/RAYOS | 1 X 20 EN XMR MAL TIEMPO RAYOS | P23052600452 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 6 | 2023-05-26 | 90 | keep | 0 | May | 2023 | 6.1299e-05 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-26 18:13 | 2023-05-26 18:17 | 1058 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO POR CONTROL | S23052600233 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-26 | 4232 | keep | 0 | May | 2023 | 0.0028824 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 18:13 | 2023-05-26 18:17 | 1000 | 0:04 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO POR CONTROL | S23052600233 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-26 | 4000 | keep | 0 | May | 2023 | 0.0027244 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 18:13 | 2023-05-26 18:17 | 278 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO POR CONTROL | S23052600233 | New_Event | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-26 | 1112 | keep | 0 | May | 2023 | 0.00075738 | 0.00018934 | Momentary | FALSE | FALSE | Not_TMED_Event | 278
SAN JUAN | 2023-05-26 18:13 | 2023-05-26 18:17 | 1295 | 0:04 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO POR CONTROL | S23052600233 | Partial_restoration | Feeder Load Transferred | Include | Include | Other | 4 | 2023-05-26 | 5180 | keep | 0 | May | 2023 | 0.0035281 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-26 18:13 | 2023-05-26 18:17 | 9 | 0:04 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1424-08 LLEVA 100% DEL 1401-10 LLEVA 100% DEL 1348-07 LLEVA 80% DEL 1348-06 LLEVA 20% DEL 1336-08 SE CERRO POR CONTROL | S23052600233 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 4 | 2023-05-26 | 36 | keep | 0 | May | 2023 | 2.4519e-05 | 6.1299e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 9
MAYAGÃœEZ | 2023-05-26 18:14 | 2023-05-27 13:25 | 50 | 19:11 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR DESGANCHE | M23052600183 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1151 | 2023-05-26 | 57550 | keep | 0 | May | 2023 | 0.039197 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-26 18:19 | 2023-05-27 00:40 | 100 | 6:21 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | M23052600184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 381 | 2023-05-26 | 38100 | keep | 0 | May | 2023 | 0.02595 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-26 18:28 | 2023-05-26 19:39 | 145 | 1:11 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | C23052600341 | New_Event | Vegetation Contact | Include | Include | Vegetation | 71 | 2023-05-26 | 10295 | keep | 0 | May | 2023 | 0.0070119 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
BAYAMON | 2023-05-26 18:30 | 2023-05-27 07:12 | 6 | 12:42 | P | ANIMAL | 1 X 15 EN XMR CRUCE X AVE | B23052600406 | New_Event | Animals | Include | Include | Wildlife | 762 | 2023-05-26 | 4572 | keep | 0 | May | 2023 | 0.003114 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-05-26 18:32 | 2023-05-26 22:03 | 150 | 3:31 | P | ANIMAL | 3 X 100 1 X 80 Y 2 X 65 EN C/LS CRUCE X REPTIL | R23052600101 | New_Event | Animals | Include | Include | Wildlife | 211 | 2023-05-26 | 31650 | keep | 0 | May | 2023 | 0.021557 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-26 19:07 | 2023-05-26 19:09 | 3798 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | B23052600431 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-26 | 7596 | keep | 0 | May | 2023 | 0.0051736 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
SAN JUAN | 2023-05-26 19:16 | 2023-05-26 21:31 | 153 | 2:15 | P | DESGANCHE | SE ABRIO EN C/L PARA REALIZAR DESGANCHE PRIMARIO Y SE REMPLAZARON APROX. 20' DE ALAMBRE PRIMARIO | S23052600264 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-05-26 | 20655 | keep | 0 | May | 2023 | 0.014068 | 0.00010421 | Sustained | FALSE | FALSE | Not_TMED_Event | 153
VEGA BAJA | 2023-05-26 19:19 | 2023-05-26 23:30 | 40 | 4:11 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA | A23052600075 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 251 | 2023-05-26 | 10040 | keep | 0 | May | 2023 | 0.0068382 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-26 19:24 | 2023-05-27 12:26 | 10 | 17:02 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO PORTA FUSIBLE | M23052600192 | New_Event | Cutout Failure | Include | Include | Equipment | 1022 | 2023-05-26 | 10220 | keep | 0 | May | 2023 | 0.0069608 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
MAYAGÃœEZ | 2023-05-26 19:25 | 2023-05-26 20:15 | 150 | 0:50 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23052600193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 50 | 2023-05-26 | 7500 | keep | 0 | May | 2023 | 0.0051082 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-05-26 19:26 | 2023-05-27 10:00 | 20 | 14:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE IDENTIFICO CAUSA | M23052600194 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 874 | 2023-05-26 | 17480 | keep | 0 | May | 2023 | 0.011906 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-26 19:30 | 2023-05-26 19:33 | 291 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1342-05 LLEVA CARGA DEL 1345-02 LLEVA 65% DEL 1345-05 SE CERRO POR CONTROL | S23052600269 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-26 | 873 | keep | 0 | May | 2023 | 0.0005946 | 0.0001982 | Momentary | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2023-05-26 19:30 | 2023-05-26 19:33 | 435 | 0:03 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1342-05 LLEVA CARGA DEL 1345-02 LLEVA 65% DEL 1345-05 SE CERRO POR CONTROL | S23052600269 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-26 | 1305 | keep | 0 | May | 2023 | 0.00088883 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-05-26 19:30 | 2023-05-26 19:33 | 619 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1342-05 LLEVA CARGA DEL 1345-02 LLEVA 65% DEL 1345-05 SE CERRO POR CONTROL | S23052600269 | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-26 | 1857 | keep | 0 | May | 2023 | 0.0012648 | 0.0004216 | Momentary | FALSE | FALSE | Not_TMED_Event | 619
VEGA BAJA | 2023-05-26 19:52 | 2023-05-27 02:00 | 75 | 6:08 | P | ARBOL SOBRE LINEA | 1X65 EN C/L SE RETIRO ARBOL DEL TENDIDO ELECTRICO | B23052600471 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 368 | 2023-05-26 | 27600 | keep | 0 | May | 2023 | 0.018798 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
PONCE | 2023-05-26 19:53 | 2023-05-27 10:00 | 15 | 14:07 | P | ANIMAL | 1 X 20 EN XMR AVE CRUZO LINEAS | P23052600513 | New_Event | Animals | Include | Include | Wildlife | 847 | 2023-05-26 | 12705 | keep | 0 | May | 2023 | 0.0086533 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-26 19:53 | 2023-05-27 07:53 | 40 | 12:00 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23052600472 | New_Event | Animals | Include | Include | Wildlife | 720 | 2023-05-26 | 28800 | keep | 0 | May | 2023 | 0.019616 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-26 20:00 | 2023-05-26 21:09 | 291 | 1:09 | T | NO SE REPORTO CAUSA | SE ABRIO AMARRE CONTRA 1345-02 Y 1345-05 Y SE CERRO POR CONTROL 100% EN SERVICIO - SJ-230526-03 | S22052600311 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 69 | 2023-05-26 | 20079 | keep | 0 | May | 2023 | 0.013676 | 0.0001982 | Sustained | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2023-05-26 20:00 | 2023-05-26 22:01 | 435 | 2:01 | T | ALIMENTADOR AMARRADO | CARGA POR 1342-05 NO SE ENCONTRO LA AVERIA SE REALIZARON OPERACIONES DE CAMPO Y SE DEJO EN SERVICIO - SJ-230526-03 | S23052600311 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 121 | 2023-05-26 | 52635 | keep | 0 | May | 2023 | 0.035849 | 0.00029628 | Sustained | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-05-26 20:00 | 2023-05-26 22:27 | 619 | 2:27 | P | ALIMENTADOR AMARRADO | 65% DE SU CARGA POR 1342-05 NO SE ENCONTRO LA AVERIA SE REALIZARON OPERACIONES DE CAMPO Y SE DEJO EN SERVICIO - SJ-230526-03 | S23052600311 | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 147 | 2023-05-26 | 90993 | keep | 0 | May | 2023 | 0.061975 | 0.0004216 | Sustained | FALSE | FALSE | Not_TMED_Event | 619
SAN JUAN | 2023-05-26 20:00 | 2023-05-26 22:26 | 1278 | 2:26 | P | CONDUCTOR ROTO O ABIERTO | DISPARO DE INTERRUPTOR 1526-02 LLEVA LA CARGA DEL 1530-06 SE SECCIONALIZO CONDUCTOR PRIMARIO EN EL SUELO G.O.I. SJ-230526-02 - 100% EN SERVICIO | S23052600229 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 146 | 2023-05-26 | 186588 | keep | 0 | May | 2023 | 0.12708 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-26 20:05 | 2023-05-26 20:28 | 40 | 0:23 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23052600519 | New_Event | Vegetation Contact | Include | Include | Vegetation | 23 | 2023-05-26 | 920 | keep | 0 | May | 2023 | 0.00062661 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-26 20:05 | 2023-05-27 08:59 | 250 | 12:54 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA POR LINEA CRUZADA | M23052600198 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 774 | 2023-05-26 | 193500 | keep | 0 | May | 2023 | 0.13179 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
AGUADILLA | 2023-05-26 20:11 | 2023-05-26 22:05 | 100 | 1:54 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23052600201 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 114 | 2023-05-26 | 11400 | keep | 0 | May | 2023 | 0.0077645 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
YAUCO | 2023-05-26 20:30 | 2023-05-27 09:40 | 60 | 13:10 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | P23052600539 | New_Event | Vegetation Contact | Include | Include | Vegetation | 790 | 2023-05-26 | 47400 | keep | 0 | May | 2023 | 0.032284 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-26 20:38 | 2023-05-27 09:01 | 25 | 12:23 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | B23052600516 | New_Event | Vegetation Contact | Include | Include | Vegetation | 743 | 2023-05-26 | 18575 | keep | 0 | May | 2023 | 0.012651 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
VEGA BAJA | 2023-05-26 20:43 | 2023-05-27 01:05 | 200 | 4:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 200 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLE | A23052600083 | New_Event | Cutout Failure | Include | Include | Equipment | 262 | 2023-05-26 | 52400 | keep | 0 | May | 2023 | 0.035689 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
PONCE | 2023-05-26 20:44 | 2023-05-27 13:20 | 10 | 16:36 | P | ANIMAL | 1 X 10 EN XMR AVE CRUZO LINEAS | P23052600545 | New_Event | Animals | Include | Include | Wildlife | 996 | 2023-05-26 | 9960 | keep | 0 | May | 2023 | 0.0067837 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-05-26 20:46 | 2023-05-26 23:25 | 100 | 2:39 | P | ANIMAL | 1 X 50 EN CL EN CRUCE DE FASE PRIMARIA POR AVE | P23052600546 | New_Event | Animals | Include | Include | Wildlife | 159 | 2023-05-26 | 15900 | keep | 0 | May | 2023 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-26 20:53 | 2023-05-27 05:31 | 337 | 8:38 | P | DESGANCHE | 1X200 EN C/L DESGANCHE | B23052600525 | New_Event | Vegetation Contact | Include | Include | Vegetation | 518 | 2023-05-26 | 174566 | keep | 0 | May | 2023 | 0.1189 | 0.00022953 | Sustained | FALSE | FALSE | Not_TMED_Event | 337
BAYAMON | 2023-05-26 21:14 | 2023-05-27 18:48 | 4 | 21:34 | P | DESGANCHE | 2 X 65 EN C/L 2 X 50 EN RISER | S23052600350 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1294 | 2023-05-26 | 5176 | keep | 0 | May | 2023 | 0.0035254 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-05-26 21:20 | 2023-05-27 13:25 | 3 | 16:05 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO EN EL SUELO. NO HABIA ACCESO EN HOSPITAL DE VETERANOS. SE ABRIO INTERRUPTOR PARA SECCIONALIZAR SJ-230527-01 | S23052600358 | New_Event | Primary Wire Break | Include | Include | Equipment | 965 | 2023-05-26 | 2895 | keep | 0 | May | 2023 | 0.0019718 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
ARECIBO | 2023-05-26 21:21 | 2023-05-27 09:40 | 60 | 12:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23052600114 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 739 | 2023-05-26 | 44340 | keep | 0 | May | 2023 | 0.0302 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-26 21:52 | 2023-05-27 11:30 | 8 | 13:38 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 25 KVA X 50 KVA | C23052600368 | New_Event | Service Transformer Failure | Include | Include | Equipment | 818 | 2023-05-26 | 6544 | keep | 0 | May | 2023 | 0.0044571 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-26 22:03 | 2023-05-27 09:29 | 110 | 11:26 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23052600377 | New_Event | Vegetation Contact | Include | Include | Vegetation | 686 | 2023-05-26 | 75460 | keep | 0 | May | 2023 | 0.051395 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BAYAMON | 2023-05-26 22:06 | 2023-05-27 02:53 | 80 | 4:47 | P | MAL TIEMPO/LLUVIA O VIENTO | 1X100 EN C/L POR LLUVIA | S23052600381 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 287 | 2023-05-26 | 22960 | keep | 0 | May | 2023 | 0.015638 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-26 22:43 | 2023-05-27 01:14 | 100 | 2:31 | P | OTRAS CAUSAS | 1 X 100 EN CORTE DE LINEA FUSIBLE PODRIDO | A23052600150 | New_Event | Other Causes | Include | Include | Other | 151 | 2023-05-26 | 15100 | keep | 0 | May | 2023 | 0.010285 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-05-26 22:55 | 2023-05-27 02:10 | 100 | 3:15 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23052600219 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 195 | 2023-05-26 | 19500 | keep | 0 | May | 2023 | 0.013281 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-26 23:04 | 2023-05-27 02:18 | 250 | 3:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN CL | P23052600588 | New_Event | Cutout Failure | Include | Include | Equipment | 194 | 2023-05-26 | 48500 | keep | 0 | May | 2023 | 0.033033 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2023-05-26 23:09 | 2023-05-27 14:00 | 80 | 14:51 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052600225 | New_Event | Vegetation Contact | Include | Include | Vegetation | 891 | 2023-05-26 | 71280 | keep | 0 | May | 2023 | 0.048548 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-26 23:20 | 2023-05-27 11:07 | 60 | 11:47 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | B23052600640 | New_Event | Animals | Include | Include | Wildlife | 707 | 2023-05-26 | 42420 | keep | 0 | May | 2023 | 0.028892 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
SAN JUAN | 2023-05-26 23:53 | 2023-05-27 08:10 | 1 | 8:17 | P | NO SE REPORTO CAUSA | 1 X 25 EN XMR | S23052600391 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 497 | 2023-05-26 | 497 | keep | 0 | May | 2023 | 0.0003385 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-27 00:28 | 2023-05-27 00:58 | 4622 | 0:30 | T | DESCONECTIVO DEFECTUOSO | SE ABRIO INTERRUPTOR POR FASE AVERIADA EN MACHETE DE BARRA SF BY-230526-05 | B23052700008 | Additional_clients | Switch Failure | Include | Include | Equipment | 30 | 2023-05-27 | 138660 | keep | 0 | May | 2023 | 0.094441 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-27 00:33 | 2023-05-27 08:40 | 35 | 8:07 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA SOBRE LINEA | M23052700004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 487 | 2023-05-27 | 17045 | keep | 0 | May | 2023 | 0.011609 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
FAJARDO | 2023-05-27 00:44 | 2023-05-27 00:45 | 2722 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23052700006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 2722 | keep | 0 | May | 2023 | 0.0018539 | 0.0018539 | Momentary | FALSE | FALSE | Not_TMED_Event | 2722
BAYAMON | 2023-05-27 00:58 | 2023-05-27 01:02 | 1250 | 0:04 | P | DESCONECTIVO DEFECTUOSO | SE PUENTEO INTERRUPTOR DEBIDO A QUE HAY FASE AVERIADA EN EL MACHETE DE BARRA SF BY-230526-05 | B23052600303 | Partial_restoration | Switch Failure | Include | Include | Equipment | 4 | 2023-05-27 | 5000 | keep | 0 | May | 2023 | 0.0034055 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-27 01:04 | 2023-05-27 01:05 | 3114 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE COLOCO RR EN OFF Y SE REALIZO PRUEBA QUEDANDONDO EN SERVICIO | P23052700012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 3114 | keep | 0 | May | 2023 | 0.0021209 | 0.0021209 | Momentary | FALSE | FALSE | Not_TMED_Event | 3114
BAYAMON | 2023-05-27 01:35 | 2023-05-27 08:25 | 15 | 6:50 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | B23052700030 | New_Event | Animals | Include | Include | Wildlife | 410 | 2023-05-27 | 6150 | keep | 0 | May | 2023 | 0.0041887 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-27 01:44 | 2023-05-27 14:24 | 13 | 12:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA EN XMR | S23052700002 | New_Event | Primary Wire Break | Include | Include | Equipment | 760 | 2023-05-27 | 9880 | keep | 0 | May | 2023 | 0.0067292 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-05-27 02:06 | 2023-05-27 02:09 | 2126 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL | C23052700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-27 | 6378 | keep | 0 | May | 2023 | 0.004344 | 0.001448 | Momentary | FALSE | FALSE | Not_TMED_Event | 2126
FAJARDO | 2023-05-27 02:09 | 2023-05-27 17:30 | 12 | 15:21 | P | CABLE SOTERRADO AVERIADO | AVERIA RISER A T-16 SE CONTRUYO PROVISIONAL DE EXISTENTE A T-16 | R23052700004 | New_Event | UG Cable Fault | Include | Include | Equipment | 921 | 2023-05-27 | 11052 | keep | 0 | May | 2023 | 0.0075275 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
CANOVANAS | 2023-05-27 03:36 | 2023-05-27 10:52 | 20 | 7:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | R23052700005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 436 | 2023-05-27 | 8720 | keep | 0 | May | 2023 | 0.0059392 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-27 03:47 | 2023-05-27 03:48 | 4641 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23052700007 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 4641 | keep | 0 | May | 2023 | 0.003161 | 0.003161 | Momentary | FALSE | FALSE | Not_TMED_Event | 4641
CAGUAS | 2023-05-27 04:21 | 2023-05-27 07:18 | 1261 | 2:57 | T | ANIMAL | CG-230527-01 DISPARO DE MAIN BKR SE TRANSFIRIO LA CARGA AL 3006-03 PARARRAYO EN LA MEDICION REMOTA AVERIADO DEBIDO A CRUCE CON AVE | C23052700178 | New_Event | Animals | Include | Include | Wildlife | 177 | 2023-05-27 | 223197 | keep | 0 | May | 2023 | 0.15202 | 0.00085886 | Sustained | FALSE | FALSE | Not_TMED_Event | 1261
CAGUAS | 2023-05-27 04:21 | 2023-05-27 07:18 | 1922 | 2:57 | T | ANIMAL | CG-230527-01 DISPARO DE MAIN BKR SE TRANSFIRIO LA CARGA AL 3006-03 PARARRAYO EN LA MEDICION REMOTA AVERIADO DEBIDO A CRUCE CON AVE | C23052700179 | New_Event | Animals | Include | Include | Wildlife | 177 | 2023-05-27 | 340194 | keep | 0 | May | 2023 | 0.2317 | 0.0013091 | Sustained | FALSE | FALSE | Not_TMED_Event | 1922
CAGUAS | 2023-05-27 04:21 | 2023-05-27 07:18 | 853 | 2:57 | T | ANIMAL | CG-230527-01 DISPARO DE MAIN BKR SE TRANSFIRIO LA CARGA AL 3006-03 PARARRAYO EN LA MEDICION REMOTA AVERIADO DEBIDO A CRUCE CON AVE | C23052700180 | New_Event | Animals | Include | Include | Wildlife | 177 | 2023-05-27 | 150981 | keep | 0 | May | 2023 | 0.10283 | 0.00058097 | Sustained | FALSE | FALSE | Not_TMED_Event | 853
CAGUAS | 2023-05-27 04:21 | 2023-05-27 08:28 | 2900 | 4:07 | T | ANIMAL | CG-230527-01 DISPARO DE MAIN BKR SE TRANSFIRIO LA CARGA AL 3006-03 PARARRAYO EN LA MEDICION REMOTA AVERIADO DEBIDO A CRUCE CON AVE | C23052700181 | New_Event | Animals | Include | Include | Wildlife | 247 | 2023-05-27 | 716300 | keep | 0 | May | 2023 | 0.48787 | 0.0019752 | Sustained | FALSE | FALSE | Not_TMED_Event | 2900
CAGUAS | 2023-05-27 04:21 | 2023-05-27 07:31 | 1089 | 3:10 | P | ANIMAL | CG-230527-01 DISPARO DE MAIN BKR 3103-05 SOLO LLEVA EL 50% DE SU CARGA Y FUE TRANSERIDA AL 3015-07. PARARRAYO EN LA MEDICION REMOTA DEBIDO A CRUCE CON AVE | C23052700009 | New_Event | Animals | Include | Include | Wildlife | 190 | 2023-05-27 | 206910 | keep | 0 | May | 2023 | 0.14093 | 0.00074171 | Sustained | FALSE | FALSE | Not_TMED_Event | 1089
YAUCO | 2023-05-27 05:05 | 2023-05-27 10:15 | 50 | 5:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052700009 | New_Event | Vegetation Contact | Include | Include | Vegetation | 310 | 2023-05-27 | 15500 | keep | 0 | May | 2023 | 0.010557 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-27 05:38 | 2023-05-27 05:44 | 2450 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DEL 5350 ARBOLES Y ENREDADERAS. | C23052700166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-27 | 14700 | keep | 0 | May | 2023 | 0.010012 | 0.0016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-05-27 05:38 | 2023-05-27 05:44 | 640 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DEL 5350 ARBOLES Y ENREDADERAS. | C23052700166 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-27 | 3840 | keep | 0 | May | 2023 | 0.0026154 | 0.0004359 | Sustained | FALSE | FALSE | Not_TMED_Event | 640
GUAYAMA | 2023-05-27 06:00 | 2023-05-27 08:30 | 60 | 2:30 | P | MAL TIEMPO/RAYOS | 1 X 100 EN C/L MAL TIEMPO RAYOS | P23052700030 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 150 | 2023-05-27 | 9000 | keep | 0 | May | 2023 | 0.0061299 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-27 06:21 | 2023-05-27 10:55 | 100 | 4:34 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 65 EN C/L Y SE REMPLAZO CAJA PRIMARIA | B23052700047 | New_Event | Cutout Failure | Include | Include | Equipment | 274 | 2023-05-27 | 27400 | keep | 0 | May | 2023 | 0.018662 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-27 06:28 | 2023-05-27 12:33 | 79 | 6:05 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO FASE | R23052700007 | New_Event | Animals | Include | Include | Wildlife | 365 | 2023-05-27 | 28835 | keep | 0 | May | 2023 | 0.019639 | 5.3807e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 79
BAYAMON | 2023-05-27 06:34 | 2023-05-27 06:35 | 1368 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S23052700004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 1368 | keep | 0 | May | 2023 | 0.00093174 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2023-05-27 07:10 | 2023-05-27 13:12 | 23 | 6:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA 1 X 25 EN XMR | S23052700009 | New_Event | Secondary Wire Break | Include | Include | Equipment | 362 | 2023-05-27 | 8326 | keep | 0 | May | 2023 | 0.0056708 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
VEGA BAJA | 2023-05-27 07:22 | 2023-05-27 14:40 | 10 | 7:18 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR NIDO DE AVE | B23052700052 | New_Event | Animals | Include | Include | Wildlife | 438 | 2023-05-27 | 4380 | keep | 0 | May | 2023 | 0.0029832 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-27 07:24 | 2023-05-27 09:39 | 183 | 2:15 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | R23052700011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 135 | 2023-05-27 | 24705 | keep | 0 | May | 2023 | 0.016826 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
SAN JUAN | 2023-05-27 07:25 | 2023-05-27 07:27 | 363 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1620-01 CERRADO POR SCADA LLEVA 90% 1336-10 | S2305270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-27 | 726 | keep | 0 | May | 2023 | 0.00049448 | 0.00024724 | Momentary | FALSE | FALSE | Not_TMED_Event | 363
SAN JUAN | 2023-05-27 07:25 | 2023-05-27 07:27 | 36 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA LLEVA 90% 1336-10 LLEVA 60% 1620-02 | S2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-27 | 72 | keep | 0 | May | 2023 | 4.9039e-05 | 2.4519e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 36
SAN JUAN | 2023-05-27 07:25 | 2023-05-27 07:27 | 2231 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1620-01 CERRADO POR SCADA | S2305270000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-27 | 4462 | keep | 0 | May | 2023 | 0.003039 | 0.0015195 | Momentary | FALSE | FALSE | Not_TMED_Event | 2231
AGUADILLA | 2023-05-27 07:26 | 2023-05-27 10:16 | 80 | 2:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23052700010 | New_Event | Cutout Failure | Include | Include | Equipment | 170 | 2023-05-27 | 13600 | keep | 0 | May | 2023 | 0.0092629 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-05-27 07:44 | 2023-05-27 07:45 | 1527 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23052700014 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 1527 | keep | 0 | May | 2023 | 0.00104 | 0.00104 | Momentary | FALSE | FALSE | Not_TMED_Event | 1527
AGUADILLA | 2023-05-27 08:01 | 2023-05-27 13:19 | 30 | 5:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN CORTE DE LINEA POR LLUVIAS | M23052700013 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 318 | 2023-05-27 | 9540 | keep | 0 | May | 2023 | 0.0064977 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-27 08:08 | 2023-05-27 12:01 | 43 | 3:53 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23052700013 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 233 | 2023-05-27 | 10019 | keep | 0 | May | 2023 | 0.0068239 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
CANOVANAS | 2023-05-27 08:13 | 2023-05-27 12:35 | 12 | 4:22 | P | TRANSFORMADOR AVERIADO | TRANSFORMADOR 37.5KVA AVERIADO SE PASO CARGA A TRANSFORMADOR MAS CERCANO DE 50KVA FID-23521587 | R23052700016 | New_Event | Service Transformer Failure | Include | Include | Equipment | 262 | 2023-05-27 | 3144 | keep | 0 | May | 2023 | 0.0021414 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-27 08:20 | 2023-05-27 12:32 | 30 | 4:12 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23052700052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 252 | 2023-05-27 | 7560 | keep | 0 | May | 2023 | 0.0051491 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-27 08:23 | 2023-05-27 08:24 | 5662 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1717-02 LLEVA 95% 1713-05 SE CERRO POR CONTROL | B23052700059 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-27 | 5662 | keep | 0 | May | 2023 | 0.0038564 | 0.0038564 | Momentary | FALSE | FALSE | Not_TMED_Event | 5662
BAYAMON | 2023-05-27 08:23 | 2023-05-27 08:24 | 911 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1717-02 LLEVA 95% 1713-05 SE CERRO POR CONTROL | B23052700059 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 911 | keep | 0 | May | 2023 | 0.00062048 | 0.00062048 | Momentary | FALSE | FALSE | Not_TMED_Event | 911
BAYAMON | 2023-05-27 08:29 | 2023-05-27 08:51 | 4 | 0:22 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23052700059 | New_Event | Vegetation Contact | Include | Include | Vegetation | 22 | 2023-05-27 | 88 | keep | 0 | May | 2023 | 5.9936e-05 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
AGUADILLA | 2023-05-27 08:42 | 2023-05-27 11:31 | 30 | 2:49 | P | SOBRECARGA | 1 X 65 EN CORTE DE LINEA POR SOBRE CARGA | M23052700019 | New_Event | Trip Due To Overload | Include | Include | Other | 169 | 2023-05-27 | 5070 | keep | 0 | May | 2023 | 0.0034532 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-27 08:50 | 2023-05-27 08:51 | 4381 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTO | M23052700020 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 4381 | keep | 0 | May | 2023 | 0.0029839 | 0.0029839 | Momentary | FALSE | FALSE | Not_TMED_Event | 4381
SAN JUAN | 2023-05-27 09:16 | 2023-05-27 09:18 | 1984 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR SCADA | S23052700023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-27 | 3968 | keep | 0 | May | 2023 | 0.0027026 | 0.0013513 | Momentary | FALSE | FALSE | Not_TMED_Event | 1984
GUAYAMA | 2023-05-27 09:21 | 2023-05-27 11:20 | 50 | 1:59 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 80 EN C/L MAL TIEMPO VIENTOS | P23052700077 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 119 | 2023-05-27 | 5950 | keep | 0 | May | 2023 | 0.0040525 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-27 09:24 | 2023-05-27 12:01 | 20 | 2:37 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE | C23052700238 | New_Event | Animals | Include | Include | Wildlife | 157 | 2023-05-27 | 3140 | keep | 0 | May | 2023 | 0.0021386 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-05-27 10:00 | 2023-05-27 14:57 | 20 | 4:57 | P | ANIMAL | 1 X 65 EN C//L AVE CRUZO LINEAS | P23052700090 | New_Event | Animals | Include | Include | Wildlife | 297 | 2023-05-27 | 5940 | keep | 0 | May | 2023 | 0.0040457 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-05-27 10:01 | 2023-05-27 13:55 | 30 | 3:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO LINEA SECUNDARIA | C23052700248 | New_Event | Secondary Wire Break | Include | Include | Equipment | 234 | 2023-05-27 | 7020 | keep | 0 | May | 2023 | 0.0047813 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-05-27 10:04 | 2023-05-27 13:23 | 30 | 3:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23052700039 | New_Event | Cutout Failure | Include | Include | Equipment | 199 | 2023-05-27 | 5970 | keep | 0 | May | 2023 | 0.0040661 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-27 10:08 | 2023-05-27 12:43 | 48 | 2:35 | P | ANIMAL | 1 X 40 Y 1 X 50 EN CORTES DE LINEA CRUCE X AVE | C23052700250 | New_Event | Animals | Include | Include | Wildlife | 155 | 2023-05-27 | 7440 | keep | 0 | May | 2023 | 0.0050674 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
SAN JUAN | 2023-05-27 10:33 | 2023-05-27 10:34 | 1837 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 1837 | keep | 0 | May | 2023 | 0.0012512 | 0.0012512 | Momentary | FALSE | FALSE | Not_TMED_Event | 1837
GUAYAMA | 2023-05-27 10:41 | 2023-05-27 11:10 | 610 | 0:29 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO ALAMBRE PRIMARIO PARTIDO | P23052700100 | New_Event | Primary Wire Break | Include | Include | Equipment | 29 | 2023-05-27 | 17690 | keep | 0 | May | 2023 | 0.012049 | 0.00041547 | Sustained | FALSE | FALSE | Not_TMED_Event | 610
AGUADILLA | 2023-05-27 10:51 | 2023-05-27 13:08 | 60 | 2:17 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA POR DESGANCHE | M23052700038 | New_Event | Vegetation Contact | Include | Include | Vegetation | 137 | 2023-05-27 | 8220 | keep | 0 | May | 2023 | 0.0055986 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-27 11:00 | 2023-05-27 13:51 | 51 | 2:51 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE | C23052700266 | New_Event | Vegetation Contact | Include | Include | Vegetation | 171 | 2023-05-27 | 8721 | keep | 0 | May | 2023 | 0.0059398 | 3.4736e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 51
FAJARDO | 2023-05-27 11:06 | 2023-05-27 12:50 | 34 | 1:44 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN CORTE DE LINEA SE REMPLAZO PIN | R23052700036 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 104 | 2023-05-27 | 3536 | keep | 0 | May | 2023 | 0.0024084 | 2.3157e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 34
YAUCO | 2023-05-27 11:10 | 2023-05-27 14:00 | 40 | 2:50 | P | CAUSAS EXTERNAS | 1 X 65 EN C/L MAQUINA IMPACTO POSTE | P23052700110 | New_Event | Damage From Public | Include | Include | Public | 170 | 2023-05-27 | 6800 | keep | 0 | May | 2023 | 0.0046314 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-27 11:11 | 2023-05-27 11:13 | 3597 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-27 | 7194 | keep | 0 | May | 2023 | 0.0048998 | 0.0024499 | Momentary | FALSE | FALSE | Not_TMED_Event | 3597
BAYAMON | 2023-05-27 11:13 | 2023-05-27 13:25 | 39 | 2:12 | P | TRANSFORMADOR AVERIADO | REMPLAZO DE XMR AVERIADO DE 50KVA X 50KVA | B23052600238 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 132 | 2023-05-27 | 5148 | keep | 0 | May | 2023 | 0.0035063 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-27 11:16 | 2023-05-27 12:38 | 13 | 1:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C23052700277 | New_Event | Secondary Wire Break | Include | Include | Equipment | 82 | 2023-05-27 | 1066 | keep | 0 | May | 2023 | 0.00072605 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
PONCE | 2023-05-27 11:16 | 2023-05-27 13:48 | 1 | 2:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN RISER NO SE REPORTO CAUSA | P23052700114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 152 | 2023-05-27 | 152 | keep | 0 | May | 2023 | 0.00010353 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-27 11:17 | 2023-05-27 19:30 | 33 | 8:13 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA SECCIONALIZAR TRAMO SECUNDARIO SOTERRADO QUE NO SE LOGRO REPARAR | B23052700089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 493 | 2023-05-27 | 16269 | keep | 0 | May | 2023 | 0.011081 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-05-27 11:30 | 2023-05-27 21:35 | 4 | 10:05 | P | NO SE REPORTO CAUSA | 1X20 EN XMR | S23052700040 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 605 | 2023-05-27 | 2420 | keep | 0 | May | 2023 | 0.0016483 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
YAUCO | 2023-05-27 11:34 | 2023-05-27 13:13 | 3 | 1:39 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | P23052700122 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 99 | 2023-05-27 | 297 | keep | 0 | May | 2023 | 0.00020229 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-05-27 11:44 | 2023-05-27 12:10 | 100 | 0:26 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CHANGO CRUZO FASE | R23052700038 | New_Event | Animals | Include | Include | Wildlife | 26 | 2023-05-27 | 2600 | keep | 0 | May | 2023 | 0.0017708 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
GUAYAMA | 2023-05-27 11:45 | 2023-05-27 13:33 | 10 | 1:48 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | P23052700126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 108 | 2023-05-27 | 1080 | keep | 0 | May | 2023 | 0.00073558 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-27 11:54 | 2023-05-27 11:55 | 4981 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 4981 | keep | 0 | May | 2023 | 0.0033925 | 0.0033925 | Momentary | FALSE | FALSE | Not_TMED_Event | 4981
SAN JUAN | 2023-05-27 12:09 | 2023-05-27 12:10 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
UTUADO | 2023-05-27 12:16 | 2023-05-27 14:35 | 125 | 2:19 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | A23052700048 | New_Event | Cutout Failure | Include | Include | Equipment | 139 | 2023-05-27 | 17375 | keep | 0 | May | 2023 | 0.011834 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
BAYAMON | 2023-05-27 12:18 | 2023-05-27 12:19 | 1210 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305270000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 1210 | keep | 0 | May | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
FAJARDO | 2023-05-27 12:37 | 2023-05-27 13:24 | 60 | 0:47 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE EVENTO TRANSFERIDO | P23052700140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 47 | 2023-05-27 | 2820 | keep | 0 | May | 2023 | 0.0019207 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BARRANQUITAS | 2023-05-27 12:40 | 2023-05-27 15:36 | 42 | 2:56 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | C23052700300 | New_Event | Primary Wire Break | Include | Include | Equipment | 176 | 2023-05-27 | 7392 | keep | 0 | May | 2023 | 0.0050347 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
BAYAMON | 2023-05-27 12:55 | 2023-05-27 12:58 | 1410 | 0:03 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | EN TRANSFERENCIA PARA ESTABLECER GOI Y EL VS MH-8 NO HIZO LA OPERACION DE CERRAR SE CANCELARON TRABAJOS Y SE NORMALIZO CARGA | S2305270000X | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 3 | 2023-05-27 | 4230 | keep | 0 | May | 2023 | 0.002881 | 0.00096034 | Momentary | FALSE | FALSE | Not_TMED_Event | 1410
GUAYAMA | 2023-05-27 13:00 | 2023-05-27 13:16 | 40 | 0:16 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23052700148 | New_Event | Animals | Include | Include | Wildlife | 16 | 2023-05-27 | 640 | keep | 0 | May | 2023 | 0.0004359 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-27 13:07 | 2023-05-27 13:30 | 8 | 0:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA EVENTO TRANSFERIDO | P23052600518 | New_Event | Secondary Wire Break | Include | Include | Equipment | 23 | 2023-05-27 | 184 | keep | 0 | May | 2023 | 0.00012532 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-27 13:09 | 2023-05-27 16:27 | 3798 | 3:18 | S | CAUSAS EXTERNAS | LOCKOUT TRIP SE ENCONTRO TENSOR CRUZADO CON PUENTE PRIMARIA CERCA DE LA SUBESTACION EN EL FEEDER 1806-02 SE TRANSFIRIO EL 50% AL 1718-02 | B23052700188 | New_Event | Damage From Public | Include | Include | Public | 198 | 2023-05-27 | 752004 | keep | 0 | May | 2023 | 0.51219 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2023-05-27 13:09 | 2023-05-27 18:32 | 4622 | 5:23 | S | CAUSAS EXTERNAS | LOCKOUT TRIP SE ENCONTRO TENSOR CRUZADO CON PUENTE PRIMARIA CERCA DE LA SUBESTACION EN EL FEEDER 1806-02 CERRO POR SCADA. ESTE INTERRUPTOR ESTABA BY-PASS AL MOMENTO DEL LOCKOUT | B23052700188 | New_Event | Damage From Public | Include | Include | Public | 323 | 2023-05-27 | 1492906 | keep | 0 | May | 2023 | 1.0168 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2023-05-27 13:09 | 2023-05-27 15:47 | 4089 | 2:38 | S | CAUSAS EXTERNAS | LOCKOUT TRIP SE ENCONTRO TENSOR CRUZADO CON PUENTE PRIMARIA CERCA DE LA SUBESTACION EN EL FEEDER 1806-02 SE TRANSFIRIO LA CARGA AL 1801-05 | B23052700188 | New_Event | Damage From Public | Include | Include | Public | 158 | 2023-05-27 | 646062 | keep | 0 | May | 2023 | 0.44003 | 0.002785 | Sustained | FALSE | FALSE | Not_TMED_Event | 4089
MAYAGÃœEZ | 2023-05-27 13:09 | 2023-05-27 14:45 | 10 | 1:36 | P | ANIMAL | 1 X 65 EN RISER AVE | M23052700049 | New_Event | Animals | Include | Include | Wildlife | 96 | 2023-05-27 | 960 | keep | 0 | May | 2023 | 0.00065385 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-27 13:10 | 2023-05-27 13:26 | 8 | 0:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE ABRIO XMR Y SE REEMPLAZO PORTA FUISBLE 1 X 25 EN XMR | S23052700055 | New_Event | Cutout Failure | Include | Include | Equipment | 16 | 2023-05-27 | 128 | keep | 0 | May | 2023 | 8.718e-05 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-05-27 13:21 | 2023-05-27 13:22 | 1862 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R23052700041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 1862 | keep | 0 | May | 2023 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-05-27 13:21 | 2023-05-27 13:22 | 1613 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R23052700041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 1613 | keep | 0 | May | 2023 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-05-27 13:21 | 2023-05-27 13:22 | 1448 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 | R23052700041 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 1448 | keep | 0 | May | 2023 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
CANOVANAS | 2023-05-27 13:21 | 2023-05-27 13:22 | 4085 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052700042 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 4085 | keep | 0 | May | 2023 | 0.0027823 | 0.0027823 | Momentary | FALSE | FALSE | Not_TMED_Event | 4085
SAN JUAN | 2023-05-27 13:25 | 2023-05-27 13:32 | 7 | 0:07 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR PARA SECCIONALIZAR CONDUCTOR EN EL SUELO Y SE PASO 95% DE LA CARGA AL 1525-01 SJ-230527-01 | S23052600358 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 7 | 2023-05-27 | 49 | keep | 0 | May | 2023 | 3.3374e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-27 13:32 | 2023-05-27 16:36 | 1 | 3:04 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO/LEVANTO CONDUCTOR Y SE CERRO INTERRUPTOR | S23052600358 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 184 | 2023-05-27 | 184 | keep | 0 | May | 2023 | 0.00012532 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-27 13:36 | 2023-05-27 14:48 | 297 | 1:12 | P | DESGANCHE | 2 X 80 EN C/L SE DESGANCHO | B23052700172 | New_Event | Vegetation Contact | Include | Include | Vegetation | 72 | 2023-05-27 | 21384 | keep | 0 | May | 2023 | 0.014565 | 0.00020229 | Sustained | FALSE | FALSE | Not_TMED_Event | 297
SAN JUAN | 2023-05-27 13:57 | 2023-05-27 13:58 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23052700000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-05-27 13:58 | 2023-05-27 16:36 | 27 | 2:38 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO FASE | R23052700044 | New_Event | Animals | Include | Include | Wildlife | 158 | 2023-05-27 | 4266 | keep | 0 | May | 2023 | 0.0029056 | 1.839e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 27
PONCE | 2023-05-27 14:18 | 2023-05-27 15:28 | 25 | 1:10 | P | ANIMAL | 2 X 50 EN C/L AVE CRUZO LINEAS | P23052700169 | New_Event | Animals | Include | Include | Wildlife | 70 | 2023-05-27 | 1750 | keep | 0 | May | 2023 | 0.0011919 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-05-27 14:23 | 2023-05-27 16:40 | 43 | 2:17 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA CRUCE POR AVE | C23052700312 | New_Event | Animals | Include | Include | Wildlife | 137 | 2023-05-27 | 5891 | keep | 0 | May | 2023 | 0.0040123 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
UTUADO | 2023-05-27 14:32 | 2023-05-27 18:18 | 100 | 3:46 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052700073 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 226 | 2023-05-27 | 22600 | keep | 0 | May | 2023 | 0.015393 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-27 14:34 | 2023-05-27 15:30 | 70 | 0:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA MAL TIEMPO LLUVIA | R23052700047 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 56 | 2023-05-27 | 3920 | keep | 0 | May | 2023 | 0.0026699 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-05-27 14:44 | 2023-05-27 17:15 | 1 | 2:31 | P | MAL TIEMPO/RAYOS | 1 X 10 Y 1 X 20 EN MONTURA DE TRANSFORMADORES POR DESCARGAS ELECTRICAS | A23052700077 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 151 | 2023-05-27 | 151 | keep | 0 | May | 2023 | 0.00010285 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-27 14:50 | 2023-05-27 14:51 | 314 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23052700064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 314 | keep | 0 | May | 2023 | 0.00021386 | 0.00021386 | Momentary | FALSE | FALSE | Not_TMED_Event | 314
PONCE | 2023-05-27 15:00 | 2023-05-27 16:00 | 16 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR TOMA SOTERRADA AVERIADA | P23052700116 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-05-27 | 960 | keep | 0 | May | 2023 | 0.00065385 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-05-27 15:05 | 2023-05-27 16:25 | 4 | 1:20 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | P23052700180 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 80 | 2023-05-27 | 320 | keep | 0 | May | 2023 | 0.00021795 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
ARECIBO | 2023-05-27 15:07 | 2023-05-27 15:08 | 1105 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | A23052700083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-27 | 1105 | keep | 0 | May | 2023 | 0.00075261 | 0.00075261 | Momentary | FALSE | FALSE | Not_TMED_Event | 1105
ARECIBO | 2023-05-27 15:08 | 2023-05-27 18:00 | 80 | 2:52 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | A23052700084 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 172 | 2023-05-27 | 13760 | keep | 0 | May | 2023 | 0.0093719 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
GUAYAMA | 2023-05-27 15:09 | 2023-05-27 15:45 | 70 | 0:36 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO LLUVIA | C23052700319 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 36 | 2023-05-27 | 2520 | keep | 0 | May | 2023 | 0.0017164 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-05-27 15:09 | 2023-05-27 22:20 | 150 | 7:11 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052700082 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 431 | 2023-05-27 | 64650 | keep | 0 | May | 2023 | 0.044033 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-05-27 15:11 | 2023-05-27 19:20 | 5 | 4:09 | P | CONDUCTOR ROTO O ABIERTO | 1 X 10 EN TRANSFORMADOR SE REPARO BAJANTE | M23052700057 | New_Event | Primary Wire Break | Include | Include | Equipment | 249 | 2023-05-27 | 1245 | keep | 0 | May | 2023 | 0.00084796 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
VEGA BAJA | 2023-05-27 15:15 | 2023-05-28 07:26 | 1 | 16:11 | P | ANIMAL | 1 X 15 CRUCE POR ANIMAL EVENTO TRANSFERIDO DE PONCE. | P23052700190 | New_Event | Animals | Include | Include | Wildlife | 971 | 2023-05-27 | 971 | keep | 0 | May | 2023 | 0.00066134 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-05-27 15:26 | 2023-05-27 21:10 | 30 | 5:44 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A23052700088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 344 | 2023-05-27 | 10320 | keep | 0 | May | 2023 | 0.0070289 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-27 15:32 | 2023-05-27 19:40 | 100 | 4:08 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700060 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 248 | 2023-05-27 | 24800 | keep | 0 | May | 2023 | 0.016891 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
UTUADO | 2023-05-27 15:33 | 2023-05-27 20:12 | 100 | 4:39 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052700095 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 279 | 2023-05-27 | 27900 | keep | 0 | May | 2023 | 0.019003 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-27 15:44 | 2023-05-27 17:18 | 129 | 1:34 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 Y 1 X 80 EN CORTES DE LINEA MAL TIEMPO VIENTOS | C23052700324 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 94 | 2023-05-27 | 12126 | keep | 0 | May | 2023 | 0.008259 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
VEGA BAJA | 2023-05-27 15:51 | 2023-05-27 21:06 | 7 | 5:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN XMR SE REPARO LINEA SECUNDARIA | B23052700203 | New_Event | Secondary Wire Break | Include | Include | Equipment | 315 | 2023-05-27 | 2205 | keep | 0 | May | 2023 | 0.0015018 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
UTUADO | 2023-05-27 15:54 | 2023-05-27 21:30 | 100 | 5:36 | P | MAL TIEMPO/RAYOS | 2 X 40 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052700103 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 336 | 2023-05-27 | 33600 | keep | 0 | May | 2023 | 0.022885 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-27 15:55 | 2023-05-27 17:50 | 100 | 1:55 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA POR RAYO | M23052700065 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 115 | 2023-05-27 | 11500 | keep | 0 | May | 2023 | 0.0078326 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:05 | 627 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 627 | keep | 0 | May | 2023 | 0.00042705 | 0.00042705 | Momentary | FALSE | FALSE | Not_TMED_Event | 627
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:05 | 293 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 293 | keep | 0 | May | 2023 | 0.00019956 | 0.00019956 | Momentary | FALSE | FALSE | Not_TMED_Event | 293
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:05 | 761 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 761 | keep | 0 | May | 2023 | 0.00051831 | 0.00051831 | Momentary | FALSE | FALSE | Not_TMED_Event | 761
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:05 | 451 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700000 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 451 | keep | 0 | May | 2023 | 0.00030717 | 0.00030717 | Momentary | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:50 | 250 | 0:46 | P | LINEA DE TRANSMISION 38KV | SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA. TIENE 45% DE SU CARGA TRANSFERIDA Y LLEVA 20% 1348-06 Y 100% 1348-06. NO SE ENCONTRÃ“ CAUSA. DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MTC. | S23052700078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2023-05-27 | 11500 | keep | 0 | May | 2023 | 0.0078326 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:50 | 1290 | 0:46 | T | LINEA DE TRANSMISION 38KV | SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA. TIENE 45% DE SU CARGA TRANSFERIDA Y LLEVA 20% 1348-06 Y 100% 1348-06. NO SE ENCONTRÃ“ CAUSA. DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MTC. | S23052700078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2023-05-27 | 59340 | keep | 0 | May | 2023 | 0.040416 | 0.00087861 | Sustained | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:45 | 837 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA. DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MTC. | S23052700078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2023-05-27 | 34317 | keep | 0 | May | 2023 | 0.023373 | 0.00057008 | Sustained | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:45 | 908 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA. DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MTC. | S23052700078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2023-05-27 | 37228 | keep | 0 | May | 2023 | 0.025356 | 0.00061843 | Sustained | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:50 | 74 | 0:46 | P | LINEA DE TRANSMISION 38KV | SE VERIFICO PERSONAL FUERA Y SE CERRO POR SCADA. TIENE 45% DE SU CARGA TRANSFERIDA Y LLEVA 20% 1348-06 Y 100% 1348-06. NO SE ENCONTRÃ“ CAUSA. DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MTC. | S23052700078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 46 | 2023-05-27 | 3404 | keep | 0 | May | 2023 | 0.0023184 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:45 | 1 | 0:41 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA. DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MTC. | S23052700078 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 41 | 2023-05-27 | 41 | keep | 0 | May | 2023 | 2.7925e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:44 | 1498 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-05-27 | 59920 | keep | 0 | May | 2023 | 0.040811 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:44 | 164 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-05-27 | 6560 | keep | 0 | May | 2023 | 0.004468 | 0.0001117 | Sustained | FALSE | FALSE | Not_TMED_Event | 164
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:44 | 533 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-05-27 | 21320 | keep | 0 | May | 2023 | 0.014521 | 0.00036302 | Sustained | FALSE | FALSE | Not_TMED_Event | 533
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:44 | 451 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-05-27 | 18040 | keep | 0 | May | 2023 | 0.012287 | 0.00030717 | Sustained | FALSE | FALSE | Not_TMED_Event | 451
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 16:44 | 766 | 0:40 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700077 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 40 | 2023-05-27 | 30640 | keep | 0 | May | 2023 | 0.020869 | 0.00052172 | Sustained | FALSE | FALSE | Not_TMED_Event | 766
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 17:19 | 427 | 1:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2023-05-27 | 32025 | keep | 0 | May | 2023 | 0.021812 | 0.00029083 | Sustained | FALSE | FALSE | Not_TMED_Event | 427
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 17:19 | 716 | 1:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2023-05-27 | 53700 | keep | 0 | May | 2023 | 0.036575 | 0.00048766 | Sustained | FALSE | FALSE | Not_TMED_Event | 716
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 17:19 | 867 | 1:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2023-05-27 | 65025 | keep | 0 | May | 2023 | 0.044288 | 0.00059051 | Sustained | FALSE | FALSE | Not_TMED_Event | 867
SAN JUAN | 2023-05-27 16:04 | 2023-05-27 17:19 | 353 | 1:15 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 8900 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE, DISPARO JUNTO CON LINEA 3200 MONACILLO-VENEZUELA, ESTA TIENE 2 FASES CON DESPEJE INADECUADO SALIENDO DE MONACILLOS. | S23052700079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 75 | 2023-05-27 | 26475 | keep | 0 | May | 2023 | 0.018032 | 0.00024043 | Sustained | FALSE | FALSE | Not_TMED_Event | 353
PONCE | 2023-05-27 16:18 | 2023-05-28 09:30 | 50 | 17:12 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23052700208 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1032 | 2023-05-27 | 51600 | keep | 0 | May | 2023 | 0.035145 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-27 16:19 | 2023-05-28 11:18 | 29 | 18:59 | P | ANIMAL | 1 X 50 EN C/L 1 X 10 EN XMR CRUCE POR AVE | B23052700206 | New_Event | Animals | Include | Include | Wildlife | 1139 | 2023-05-27 | 33031 | keep | 0 | May | 2023 | 0.022497 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
UTUADO | 2023-05-27 16:22 | 2023-05-27 20:02 | 60 | 3:40 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO BAMBUS DE LAS LINEAS | A23052700108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-05-27 | 13200 | keep | 0 | May | 2023 | 0.0089905 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-27 16:27 | 2023-05-27 18:32 | 1899 | 2:05 | P | CAUSAS EXTERNAS | SE ENCONTRO TENSOR CRUZADO CON PUENTE PRIMARIA CERCA DE LA SUBESTACION EN EL FEEDER 1806-02 SE ENERGIZO POWER XMR Y SE CERRO BKR Y ENTRO EL OTRO 50% | B23052700188 | Partial_restoration | Damage From Public | Include | Include | Public | 125 | 2023-05-27 | 237375 | keep | 0 | May | 2023 | 0.16168 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-27 16:27 | 2023-05-28 12:32 | 40 | 20:05 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052700070 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1205 | 2023-05-27 | 48200 | keep | 0 | May | 2023 | 0.032829 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-27 16:29 | 2023-05-27 18:06 | 28 | 1:37 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA EVENTO TRANSFERIDO DE PONCE A HUMACAO | P23052700219 | New_Event | Vegetation Contact | Include | Include | Vegetation | 97 | 2023-05-27 | 2716 | keep | 0 | May | 2023 | 0.0018499 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
MAYAGÃœEZ | 2023-05-27 16:33 | 2023-05-27 22:15 | 150 | 5:42 | P | MAL TIEMPO/RAYOS | 1 X 100 Y 2 X 30 EN CORTE DE LINEA Y 2 X 8 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052700072 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 342 | 2023-05-27 | 51300 | keep | 0 | May | 2023 | 0.03494 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-05-27 16:47 | 2023-05-27 21:33 | 250 | 4:46 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | M23052700079 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 286 | 2023-05-27 | 71500 | keep | 0 | May | 2023 | 0.048698 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
MAYAGÃœEZ | 2023-05-27 16:48 | 2023-05-28 10:10 | 20 | 17:22 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700082 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1042 | 2023-05-27 | 20840 | keep | 0 | May | 2023 | 0.014194 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-27 16:49 | 2023-05-27 19:00 | 75 | 2:11 | P | MAL TIEMPO/RAYOS | 2 X 80 EN C/L MAL TIEMPO RAYOS | P23052700237 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 131 | 2023-05-27 | 9825 | keep | 0 | May | 2023 | 0.0066918 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-05-27 16:52 | 2023-05-27 16:53 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S23052700193 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 2203 | keep | 0 | May | 2023 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
MAYAGÃœEZ | 2023-05-27 16:54 | 2023-05-28 09:50 | 40 | 16:56 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700085 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1016 | 2023-05-27 | 40640 | keep | 0 | May | 2023 | 0.02768 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
SAN JUAN | 2023-05-27 16:56 | 2023-05-27 16:57 | 1384 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | S23052700203 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 1384 | keep | 0 | May | 2023 | 0.00094264 | 0.00094264 | Momentary | FALSE | FALSE | Not_TMED_Event | 1384
SAN JUAN | 2023-05-27 16:56 | 2023-05-27 16:57 | 869 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | S23052700203 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 869 | keep | 0 | May | 2023 | 0.00059187 | 0.00059187 | Momentary | FALSE | FALSE | Not_TMED_Event | 869
VEGA BAJA | 2023-05-27 17:00 | 2023-05-28 16:22 | 15 | 23:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN C/L SE REMPLAZO CAJA PRIMARIA | B23052700217 | New_Event | Cutout Failure | Include | Include | Equipment | 1402 | 2023-05-27 | 21030 | keep | 0 | May | 2023 | 0.014323 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
ARECIBO | 2023-05-27 17:03 | 2023-05-27 19:55 | 40 | 2:52 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052700121 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 172 | 2023-05-27 | 6880 | keep | 0 | May | 2023 | 0.0046859 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-27 17:11 | 2023-05-27 17:12 | 3070 | 0:01 | T | DESGANCHE | RECERRO | B2305270000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-27 | 3070 | keep | 0 | May | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-05-27 17:12 | 2023-05-27 19:34 | 75 | 2:22 | P | DESGANCHE | 3 X 50 EN C/L SE DESGANCHO | B23052700218 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 142 | 2023-05-27 | 10650 | keep | 0 | May | 2023 | 0.0072537 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
SAN JUAN | 2023-05-27 17:14 | 2023-05-28 10:55 | 28 | 17:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEEPLAZO CAJA PRIMARIA Y 1 X 80 EN C/L | S23052700226 | New_Event | Cutout Failure | Include | Include | Equipment | 1061 | 2023-05-27 | 29708 | keep | 0 | May | 2023 | 0.020234 | 1.9071e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 28
ARECIBO | 2023-05-27 17:19 | 2023-05-27 18:28 | 8 | 1:09 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | A23052700125 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 69 | 2023-05-27 | 552 | keep | 0 | May | 2023 | 0.00037596 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-05-27 17:41 | 2023-05-28 15:43 | 6 | 22:02 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEA DE RISER A PEDESTAL | C23052700332 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1322 | 2023-05-27 | 7932 | keep | 0 | May | 2023 | 0.0054024 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-05-27 17:41 | 2023-05-28 11:40 | 60 | 17:59 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23052700113 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1079 | 2023-05-27 | 64740 | keep | 0 | May | 2023 | 0.044094 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-27 17:51 | 2023-05-27 17:52 | 966 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 966 | keep | 0 | May | 2023 | 0.00065794 | 0.00065794 | Momentary | FALSE | FALSE | Not_TMED_Event | 966
MAYAGÃœEZ | 2023-05-27 17:55 | 2023-05-28 10:10 | 17 | 16:15 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | M23052700120 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 975 | 2023-05-27 | 16575 | keep | 0 | May | 2023 | 0.011289 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
CANOVANAS | 2023-05-27 18:00 | 2023-05-27 18:20 | 12 | 0:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE T-46 PARA REMPLAZO BARRA PEDESTAL COJIENDO FUEGO REF. R23052700051 | R23052700052 | New_Event | Secondary Wire Break | Include | Include | Equipment | 20 | 2023-05-27 | 240 | keep | 0 | May | 2023 | 0.00016346 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-05-27 18:04 | 2023-05-28 00:42 | 44 | 6:38 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23052700244 | New_Event | Vegetation Contact | Include | Include | Vegetation | 398 | 2023-05-27 | 17512 | keep | 0 | May | 2023 | 0.011927 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2023-05-27 18:15 | 2023-05-28 14:45 | 10 | 20:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 2 X 10 EN XMR SE REPARO SECUNDARIA | B23052700235 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1230 | 2023-05-27 | 12300 | keep | 0 | May | 2023 | 0.0083775 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
UTUADO | 2023-05-27 18:16 | 2023-05-28 13:15 | 1 | 18:59 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052700143 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1139 | 2023-05-27 | 1139 | keep | 0 | May | 2023 | 0.00077577 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-27 18:17 | 2023-05-27 22:32 | 30 | 4:15 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHO Y LEVANTO CONDUCTOR | C23052700335 | New_Event | Vegetation Contact | Include | Include | Vegetation | 255 | 2023-05-27 | 7650 | keep | 0 | May | 2023 | 0.0052104 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-05-27 18:19 | 2023-05-27 19:25 | 40 | 1:06 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | A23052700146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-05-27 | 2640 | keep | 0 | May | 2023 | 0.0017981 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-27 18:40 | 2023-05-28 07:56 | 239 | 13:16 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | B23052700243 | New_Event | Vegetation Contact | Include | Include | Vegetation | 796 | 2023-05-27 | 190244 | keep | 0 | May | 2023 | 0.12957 | 0.00016278 | Sustained | FALSE | FALSE | Not_TMED_Event | 239
ARECIBO | 2023-05-27 18:41 | 2023-05-27 20:30 | 10 | 1:49 | P | MAL TIEMPO/RAYOS | 1 X 30 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052700155 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 109 | 2023-05-27 | 1090 | keep | 0 | May | 2023 | 0.00074239 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-27 18:45 | 2023-05-27 18:46 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 5252 | keep | 0 | May | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
CAGUAS | 2023-05-27 18:46 | 2023-05-27 18:47 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 2178 | keep | 0 | May | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
CANOVANAS | 2023-05-27 18:47 | 2023-05-27 18:48 | 1648 | 0:01 | T | ANIMAL | RECERRO LLEVA 50% DEL 2402-02 | R23052700055 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-27 | 1648 | keep | 0 | May | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-05-27 18:47 | 2023-05-27 18:48 | 2094 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 50% POR 2302-03 | R23052700055 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-27 | 2094 | keep | 0 | May | 2023 | 0.0014262 | 0.0014262 | Momentary | FALSE | FALSE | Not_TMED_Event | 2094
CANOVANAS | 2023-05-27 18:48 | 2023-05-27 21:39 | 178 | 2:51 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | R23052700056 | 1st_after_momentary | Animals | Include | Include | Wildlife | 171 | 2023-05-27 | 30438 | keep | 0 | May | 2023 | 0.020731 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
VEGA BAJA | 2023-05-27 18:51 | 2023-05-28 09:30 | 3 | 14:39 | P | MAL TIEMPO/RAYOS | 1 X 15 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052700159 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 879 | 2023-05-27 | 2637 | keep | 0 | May | 2023 | 0.001796 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-05-27 19:00 | 2023-05-28 11:12 | 30 | 16:12 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700148 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 972 | 2023-05-27 | 29160 | keep | 0 | May | 2023 | 0.019861 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-27 19:13 | 2023-05-27 19:14 | 2234 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B2305270000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-27 | 2234 | keep | 0 | May | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
MAYAGÃœEZ | 2023-05-27 19:15 | 2023-05-27 22:40 | 50 | 3:25 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700154 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 205 | 2023-05-27 | 10250 | keep | 0 | May | 2023 | 0.0069812 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-27 19:19 | 2023-05-27 21:53 | 100 | 2:34 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 65 EN AEREO PROVISIONAL | S23052700251 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 154 | 2023-05-27 | 15400 | keep | 0 | May | 2023 | 0.010489 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-27 19:25 | 2023-05-28 02:46 | 40 | 7:21 | P | CONDUCTOR ROTO O ABIERTO | 3X50 EN C/L Y SE REPARO/LEVANTO CONDUCTOR PRIMARIO DEL SUELO | B23052700251 | New_Event | Primary Wire Break | Include | Include | Equipment | 441 | 2023-05-27 | 17640 | keep | 0 | May | 2023 | 0.012015 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
BAYAMON | 2023-05-27 19:30 | 2023-05-30 09:30 | 3 | 61:60 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SECUNDARIA SOTERRADA AVERIADA | B23052700089 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 3720 | 2023-05-27 | 11160 | keep | 0 | May | 2023 | 0.007601 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-27 19:40 | 2023-05-28 09:28 | 14 | 13:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | M23052700060 | New_Event | Primary Wire Break | Include | Include | Equipment | 828 | 2023-05-27 | 11592 | keep | 0 | May | 2023 | 0.0078953 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
VEGA BAJA | 2023-05-27 19:40 | 2023-05-28 10:50 | 20 | 15:10 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA LINEAS CRUZADAS | A23052700175 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 910 | 2023-05-27 | 18200 | keep | 0 | May | 2023 | 0.012396 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-27 19:47 | 2023-05-27 21:22 | 3 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR SE REPARO BAJANTE SECUNDARIO | C23052700340 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-05-27 | 285 | keep | 0 | May | 2023 | 0.00019411 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-27 19:49 | 2023-05-28 10:52 | 15 | 15:03 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN C/L MAL TIEMPO VIENTO EVENTO TRANSFERIDO DE PONCE | P23052700315 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 903 | 2023-05-27 | 13545 | keep | 0 | May | 2023 | 0.0092254 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
FAJARDO | 2023-05-27 20:00 | 2023-05-28 09:22 | 6 | 13:22 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE | R23052700066 | New_Event | Vegetation Contact | Include | Include | Vegetation | 802 | 2023-05-27 | 4812 | keep | 0 | May | 2023 | 0.0032774 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
AGUADILLA | 2023-05-27 20:00 | 2023-05-27 21:15 | 100 | 1:15 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA DESCARGAS ELECTRICAS | A23052700182 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2023-05-27 | 7500 | keep | 0 | May | 2023 | 0.0051082 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-05-27 20:25 | 2023-05-27 21:40 | 70 | 1:15 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052700195 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 75 | 2023-05-27 | 5250 | keep | 0 | May | 2023 | 0.0035758 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-05-27 20:32 | 2023-05-28 14:06 | 14 | 17:34 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN DESGANCHE | R23052700070 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 1054 | 2023-05-27 | 14756 | keep | 0 | May | 2023 | 0.01005 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
CANOVANAS | 2023-05-27 20:42 | 2023-05-28 08:53 | 23 | 12:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23052700071 | New_Event | Secondary Wire Break | Include | Include | Equipment | 731 | 2023-05-27 | 16813 | keep | 0 | May | 2023 | 0.011451 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BARRANQUITAS | 2023-05-27 20:58 | 2023-05-27 20:59 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700349 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 1565 | keep | 0 | May | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-27 20:58 | 2023-05-27 20:59 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700349 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 976 | keep | 0 | May | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-27 20:58 | 2023-05-27 20:59 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700349 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 548 | keep | 0 | May | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-27 20:58 | 2023-05-27 20:59 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700350 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 315 | keep | 0 | May | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-27 20:58 | 2023-05-27 20:59 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700350 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 870 | keep | 0 | May | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-27 20:58 | 2023-05-27 20:59 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700351 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 2906 | keep | 0 | May | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-27 20:58 | 2023-05-27 20:59 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700351 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 2343 | keep | 0 | May | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
AGUADILLA | 2023-05-27 21:02 | 2023-05-28 11:05 | 60 | 14:03 | P | OTRAS CAUSAS | 1 X 65 EN CORTE DE LINEA SE DESCONECTO EQUIPO DE MEDICION AVERIADO Y SE REPORTO PARA SU REMPLAZO | M23052700184 | New_Event | Other Causes | Include | Include | Other | 843 | 2023-05-27 | 50580 | keep | 0 | May | 2023 | 0.03445 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
AGUADILLA | 2023-05-27 21:03 | 2023-05-28 01:50 | 100 | 4:47 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700185 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 287 | 2023-05-27 | 28700 | keep | 0 | May | 2023 | 0.019547 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-27 21:08 | 2023-05-27 21:09 | 873 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 DE COMSAT A CIDRA 20% DEL 3010-01 POR EL 3604-06 VARIOS PUNTOS DE DESGANCHE CRITICO EN CARR.#1 Y CARR. 787 BARRIO BEATRIZ. | C23052700351 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-27 | 873 | keep | 0 | May | 2023 | 0.0005946 | 0.0005946 | Momentary | FALSE | FALSE | Not_TMED_Event | 873
AGUADILLA | 2023-05-27 21:09 | 2023-05-28 13:05 | 25 | 15:56 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA DE LAS LINEAS | M23052700188 | New_Event | Vegetation Contact | Include | Include | Vegetation | 956 | 2023-05-27 | 23900 | keep | 0 | May | 2023 | 0.016278 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
UTUADO | 2023-05-27 21:13 | 2023-05-27 23:20 | 70 | 2:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23052700214 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-05-27 | 8890 | keep | 0 | May | 2023 | 0.0060549 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-05-27 21:22 | 2023-05-28 14:50 | 280 | 17:28 | P | CONDUCTOR ROTO O ABIERTO | 3 X 100 EN CL NEUTRAL PRIMARIO PARTIDO | M23052700193 | New_Event | Primary Wire Break | Include | Include | Equipment | 1048 | 2023-05-27 | 293440 | keep | 0 | May | 2023 | 0.19986 | 0.00019071 | Sustained | FALSE | FALSE | Not_TMED_Event | 280
ARECIBO | 2023-05-27 21:26 | 2023-05-27 23:20 | 15 | 1:54 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052700217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-05-27 | 1710 | keep | 0 | May | 2023 | 0.0011647 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-27 21:27 | 2023-05-28 21:30 | 30 | 24:03 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE REPARO LINEA PARTIDA BITACORA ABRIR E INSTALAR TAGS POSTES PARTIDOS SE DEJO TIERRAS Y TAGS INSTALADOS (02:55) | A23052700218 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1443 | 2023-05-27 | 43290 | keep | 0 | May | 2023 | 0.029485 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-27 21:33 | 2023-05-28 07:56 | 1 | 10:23 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C23052700353 | New_Event | Animals | Include | Include | Wildlife | 623 | 2023-05-27 | 623 | keep | 0 | May | 2023 | 0.00042432 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-27 21:35 | 2023-05-27 22:26 | 80 | 0:51 | P | DESGANCHE | 1 X 65 EN C/L | R23052700077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 51 | 2023-05-27 | 4080 | keep | 0 | May | 2023 | 0.0027789 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
YAUCO | 2023-05-27 22:10 | 2023-05-28 12:30 | 10 | 14:20 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO LINEAS SECUNDARIAS ROTAS | M23052700205 | New_Event | Secondary Wire Break | Include | Include | Equipment | 860 | 2023-05-27 | 8600 | keep | 0 | May | 2023 | 0.0058574 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-27 22:17 | 2023-05-28 15:24 | 9 | 17:07 | P | OTRAS CAUSAS | 1 X 8 EN XMR FUSIBLE PODRIDO | R23052700080 | New_Event | Other Causes | Include | Include | Other | 1027 | 2023-05-27 | 9243 | keep | 0 | May | 2023 | 0.0062954 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-05-27 22:24 | 2023-05-28 08:45 | 80 | 10:21 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052700227 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 621 | 2023-05-27 | 49680 | keep | 0 | May | 2023 | 0.033837 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-05-27 22:29 | 2023-05-28 09:10 | 3 | 10:41 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23052700228 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 641 | 2023-05-27 | 1923 | keep | 0 | May | 2023 | 0.0013097 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-05-27 22:43 | 2023-05-28 08:40 | 15 | 9:57 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR RATON CRUZO FASE A TIERRA | M23052700208 | New_Event | Animals | Include | Include | Wildlife | 597 | 2023-05-27 | 8955 | keep | 0 | May | 2023 | 0.0060992 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-05-27 22:43 | 2023-05-28 03:40 | 75 | 4:57 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700207 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 297 | 2023-05-27 | 22275 | keep | 0 | May | 2023 | 0.015171 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
AGUADILLA | 2023-05-27 22:43 | 2023-05-28 03:00 | 150 | 4:17 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052700196 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 257 | 2023-05-27 | 38550 | keep | 0 | May | 2023 | 0.026256 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
UTUADO | 2023-05-27 22:48 | 2023-05-29 16:19 | 1 | 41:31 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR DESCARGAS ELECTRICAS VERIFCADO CON BITACORA | A23052700231 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 2491 | 2023-05-27 | 2491 | keep | 0 | May | 2023 | 0.0016966 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
HUMACAO | 2023-05-27 23:06 | 2023-05-27 23:08 | 1089 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23052700360 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-27 | 2178 | keep | 0 | May | 2023 | 0.0014834 | 0.00074171 | Momentary | FALSE | FALSE | Not_TMED_Event | 1089
HUMACAO | 2023-05-27 23:06 | 2023-05-27 23:08 | 3896 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23052700360 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-27 | 7792 | keep | 0 | May | 2023 | 0.0053071 | 0.0026535 | Momentary | FALSE | FALSE | Not_TMED_Event | 3896
HUMACAO | 2023-05-27 23:06 | 2023-05-27 23:08 | 1467 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 | C23052700360 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-05-27 | 2934 | keep | 0 | May | 2023 | 0.0019983 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
BAYAMON | 2023-05-27 23:11 | 2023-05-28 09:26 | 42 | 10:15 | P | DESGANCHE | 1 X 30 EN C/L Y DESGANCHE | B23052700278 | New_Event | Vegetation Contact | Include | Include | Vegetation | 615 | 2023-05-27 | 25830 | keep | 0 | May | 2023 | 0.017593 | 2.8606e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 42
HUMACAO | 2023-05-28 00:18 | 2023-05-28 08:59 | 159 | 8:41 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23052800004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 521 | 2023-05-28 | 82839 | keep | 0 | May | 2023 | 0.056421 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
ARECIBO | 2023-05-28 00:18 | 2023-05-28 10:25 | 40 | 10:07 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052800001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 607 | 2023-05-28 | 24280 | keep | 0 | May | 2023 | 0.016537 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-05-28 00:34 | 2023-05-28 09:44 | 37 | 9:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 EN C/L SE REMPLAZO CAJA PRIMARIA | R2305280000 | New_Event | Cutout Failure | Include | Include | Equipment | 550 | 2023-05-28 | 20350 | keep | 0 | May | 2023 | 0.01386 | 2.5201e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 37
SAN JUAN | 2023-05-28 00:42 | 2023-05-28 00:44 | 1066 | 0:02 | T | DESGANCHE | SE CERRO POR CONTROL | S23052800001 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 2 | 2023-05-28 | 2132 | keep | 0 | May | 2023 | 0.0014521 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-28 00:44 | 2023-05-28 13:11 | 44 | 12:27 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23052700244 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 747 | 2023-05-28 | 32868 | keep | 0 | May | 2023 | 0.022386 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
FAJARDO | 2023-05-28 00:45 | 2023-05-28 02:27 | 277 | 1:42 | P | NO SE REPORTO CAUSA | 1 X 140 EN C/L | R23052800008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 102 | 2023-05-28 | 28254 | keep | 0 | May | 2023 | 0.019244 | 0.00018866 | Sustained | FALSE | FALSE | Not_TMED_Event | 277
GUAYAMA | 2023-05-28 00:45 | 2023-05-28 04:06 | 25 | 3:21 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CL Y 1 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | P23052800020 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 201 | 2023-05-28 | 5025 | keep | 0 | May | 2023 | 0.0034225 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-05-28 01:16 | 2023-05-28 05:34 | 13 | 4:18 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA AVERIADA EN TRANSFORMADOR | P23052800028 | New_Event | Cutout Failure | Include | Include | Equipment | 258 | 2023-05-28 | 3354 | keep | 0 | May | 2023 | 0.0022844 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
UTUADO | 2023-05-28 02:19 | 2023-05-28 20:10 | 150 | 17:51 | P | ARBOL SOBRE LINEA | 2 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEAS | A23052800007 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 1071 | 2023-05-28 | 160650 | keep | 0 | May | 2023 | 0.10942 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-05-28 02:20 | 2023-05-28 04:30 | 397 | 2:10 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA ELIMINAR NEUTRAL PRIMARIO PARTIDO | M23052800005 | New_Event | Primary Wire Break | Include | Include | Equipment | 130 | 2023-05-28 | 51610 | keep | 0 | May | 2023 | 0.035151 | 0.00027039 | Sustained | FALSE | FALSE | Not_TMED_Event | 397
ARECIBO | 2023-05-28 02:50 | 2023-05-28 14:10 | 30 | 11:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30, 2 X 40 Y 2 X 50 EN CORTE DE LINEA POR LLUVIAS | A23052800009 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 680 | 2023-05-28 | 20400 | keep | 0 | May | 2023 | 0.013894 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-05-28 03:17 | 2023-05-28 10:34 | 100 | 7:17 | P | DESGANCHE | 1 X 200 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23052800011 | New_Event | Vegetation Contact | Include | Include | Vegetation | 437 | 2023-05-28 | 43700 | keep | 0 | May | 2023 | 0.029764 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
HUMACAO | 2023-05-28 03:42 | 2023-05-28 03:43 | 3025 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 3025 | keep | 0 | May | 2023 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
BAYAMON | 2023-05-28 03:59 | 2023-05-28 04:00 | 766 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE 50% X 1909-07 | S2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 766 | keep | 0 | May | 2023 | 0.00052172 | 0.00052172 | Momentary | FALSE | FALSE | Not_TMED_Event | 766
SAN JUAN | 2023-05-28 04:29 | 2023-05-28 13:00 | 29 | 8:31 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | S23052800005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 511 | 2023-05-28 | 14819 | keep | 0 | May | 2023 | 0.010093 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
BAYAMON | 2023-05-28 04:35 | 2023-05-28 04:36 | 1746 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | B23052800004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 1746 | keep | 0 | May | 2023 | 0.0011892 | 0.0011892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1746
BARRANQUITAS | 2023-05-28 04:51 | 2023-05-28 11:57 | 50 | 7:06 | P | CAUSAS EXTERNAS | 3 X 50 C/L VEHICULO IMPACTO POSTE QUE OCASIONO CRUCE DE LINEAS EVENTO TRANSFERIDO DE PONCE | P23052800053 | New_Event | Damage From Public | Include | Include | Public | 426 | 2023-05-28 | 21300 | keep | 0 | May | 2023 | 0.014507 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
PONCE | 2023-05-28 04:56 | 2023-05-28 04:57 | 1478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23052800054 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 1478 | keep | 0 | May | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
AGUADILLA | 2023-05-28 05:34 | 2023-05-28 09:45 | 50 | 4:11 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE CORTE DE LINEA | M23052800013 | New_Event | Primary Wire Break | Include | Include | Equipment | 251 | 2023-05-28 | 12550 | keep | 0 | May | 2023 | 0.0085477 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-28 06:14 | 2023-05-28 06:15 | 1367 | 0:01 | P | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE SOLO LLEVA 80% DE SU CARGA | C23052800019 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-28 | 1367 | keep | 0 | May | 2023 | 0.00093106 | 0.00093106 | Momentary | FALSE | FALSE | Not_TMED_Event | 1367
CAGUAS | 2023-05-28 06:15 | 2023-05-28 09:10 | 8 | 2:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L MAL TIEMPO LLUVIAS | C23052800037 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 175 | 2023-05-28 | 1400 | keep | 0 | May | 2023 | 0.00095353 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BAYAMON | 2023-05-28 06:33 | 2023-05-28 06:34 | 1180 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 1180 | keep | 0 | May | 2023 | 0.00080369 | 0.00080369 | Momentary | FALSE | FALSE | Not_TMED_Event | 1180
GUAYAMA | 2023-05-28 06:35 | 2023-05-28 09:00 | 10 | 2:25 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REMPLAZO CAJA EN XMR | P23052800064 | New_Event | Cutout Failure | Include | Include | Equipment | 145 | 2023-05-28 | 1450 | keep | 0 | May | 2023 | 0.00098759 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-28 06:43 | 2023-05-28 06:44 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23052800023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 1565 | keep | 0 | May | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-28 06:43 | 2023-05-28 06:44 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23052800023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 976 | keep | 0 | May | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-28 06:43 | 2023-05-28 06:44 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23052800023 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 548 | keep | 0 | May | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-28 06:43 | 2023-05-28 06:44 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23052800024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 315 | keep | 0 | May | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-28 06:43 | 2023-05-28 06:44 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23052800024 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 870 | keep | 0 | May | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-28 06:43 | 2023-05-28 06:44 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 0800 LLEVA 20% DEL 3010-01 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23052800025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 2906 | keep | 0 | May | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-28 06:43 | 2023-05-28 06:44 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23052800025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 2343 | keep | 0 | May | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
MAYAGÃœEZ | 2023-05-28 06:46 | 2023-05-28 08:22 | 1 | 1:36 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA NO SE REPORTO CAUSA | M23052800067 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 96 | 2023-05-28 | 96 | keep | 0 | May | 2023 | 6.5385e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-28 06:48 | 2023-05-28 06:49 | 1862 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052800021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 1862 | keep | 0 | May | 2023 | 0.0012682 | 0.0012682 | Momentary | FALSE | FALSE | Not_TMED_Event | 1862
CANOVANAS | 2023-05-28 06:48 | 2023-05-28 06:49 | 1613 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052800021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 1613 | keep | 0 | May | 2023 | 0.0010986 | 0.0010986 | Momentary | FALSE | FALSE | Not_TMED_Event | 1613
CANOVANAS | 2023-05-28 06:48 | 2023-05-28 06:49 | 1448 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 | R23052800021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 1448 | keep | 0 | May | 2023 | 0.00098623 | 0.00098623 | Momentary | FALSE | FALSE | Not_TMED_Event | 1448
BAYAMON | 2023-05-28 06:50 | 2023-05-29 08:34 | 33 | 25:44 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN C/L LINEA CRUZADA | B23052800007 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1544 | 2023-05-28 | 50952 | keep | 0 | May | 2023 | 0.034703 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-05-28 06:50 | 2023-05-29 08:47 | 3 | 25:57 | P | ANIMAL | 1 X 40 EN SU-4 Y 1 X 30 EN RISER Y 2 X 15 EN MONTURA DE XMR CRUCE X AVE EVENTO TRANSFERIDO DE PONCE | P23052800080 | New_Event | Animals | Include | Include | Wildlife | 1557 | 2023-05-28 | 4671 | keep | 0 | May | 2023 | 0.0031814 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
PONCE | 2023-05-28 06:50 | 2023-05-28 13:30 | 30 | 6:40 | P | DESGANCHE | 2 X 40 EN C/L DESGANCHE | P23052800068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 400 | 2023-05-28 | 12000 | keep | 0 | May | 2023 | 0.0081731 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-28 07:00 | 2023-05-28 07:01 | 581 | 0:01 | P | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 0800. 20% DE SU CARGA X 3604-06 | C23052800025 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 581 | keep | 0 | May | 2023 | 0.00039572 | 0.00039572 | Momentary | FALSE | FALSE | Not_TMED_Event | 581
UTUADO | 2023-05-28 07:00 | 2023-05-28 18:18 | 150 | 11:18 | P | CONDUCTOR ARRIADO O CRUZADO | 2 X 40 EN CORTE DE LINEA Y 1 X 30 EN CORVERTIDO POR LINEA ARRIADA | A23052800022 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 678 | 2023-05-28 | 101700 | keep | 0 | May | 2023 | 0.069267 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CANOVANAS | 2023-05-28 07:01 | 2023-05-28 12:41 | 129 | 5:40 | P | ANIMAL | 1 X 65 Y 1 X 80 EN CORTES DE LINEA CRUCE POR AVE | R23052800023 | New_Event | Animals | Include | Include | Wildlife | 340 | 2023-05-28 | 43860 | keep | 0 | May | 2023 | 0.029873 | 8.7861e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 129
MAYAGÃœEZ | 2023-05-28 07:01 | 2023-05-28 12:15 | 30 | 5:14 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REQUIERE DESGANCHE | P23052800071 | New_Event | Vegetation Contact | Include | Include | Vegetation | 314 | 2023-05-28 | 9420 | keep | 0 | May | 2023 | 0.0064159 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-05-28 07:07 | 2023-05-28 07:09 | 3006 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 17800 AISLACION CONTAMINADA POR PÃJAROS | M23052800017 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-05-28 | 6012 | keep | 0 | May | 2023 | 0.0040947 | 0.0020474 | Momentary | FALSE | FALSE | Not_TMED_Event | 3006
YAUCO | 2023-05-28 07:07 | 2023-05-28 07:09 | 179 | 0:02 | S | DISPARO DE BARRA DE TRANSMISION | DISPARO DE LINEA 17800 AISLACION CONTAMINADA POR PÃJAROS | M23052800017 | New_Event | Transmission Substation Bus Outage | Include | Include | Power supply | 2 | 2023-05-28 | 358 | keep | 0 | May | 2023 | 0.00024383 | 0.00012192 | Momentary | FALSE | FALSE | Not_TMED_Event | 179
BARRANQUITAS | 2023-05-28 07:14 | 2023-05-28 08:20 | 40 | 1:06 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L EVENTO TRANSFERIDO DE PONCE | P23052800076 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 66 | 2023-05-28 | 2640 | keep | 0 | May | 2023 | 0.0017981 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-28 07:37 | 2023-05-28 10:35 | 87 | 2:58 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23052800033 | New_Event | Animals | Include | Include | Wildlife | 178 | 2023-05-28 | 15486 | keep | 0 | May | 2023 | 0.010547 | 5.9255e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 87
CANOVANAS | 2023-05-28 07:42 | 2023-05-28 07:43 | 1937 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR CONTROL | R23052800030 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 1937 | keep | 0 | May | 2023 | 0.0013193 | 0.0013193 | Momentary | FALSE | FALSE | Not_TMED_Event | 1937
MAYAGÃœEZ | 2023-05-28 07:47 | 2023-05-28 07:48 | 1352 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 6014-03 | M23052800028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 1352 | keep | 0 | May | 2023 | 0.00092084 | 0.00092084 | Momentary | FALSE | FALSE | Not_TMED_Event | 1352
MAYAGÃœEZ | 2023-05-28 07:47 | 2023-05-28 07:48 | 871 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL INTERRUPTOR 6012-05 EL CUAL LLEVA LA CARGA DEL 6014-03 | M23052800028 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-28 | 871 | keep | 0 | May | 2023 | 0.00059323 | 0.00059323 | Momentary | FALSE | FALSE | Not_TMED_Event | 871
AGUADILLA | 2023-05-28 08:03 | 2023-05-28 10:15 | 100 | 2:12 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA AVE CRUZO LINEAS | M23052800035 | New_Event | Animals | Include | Include | Wildlife | 132 | 2023-05-28 | 13200 | keep | 0 | May | 2023 | 0.0089905 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-05-28 08:14 | 2023-05-28 14:18 | 15 | 6:04 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | C23052800057 | New_Event | Primary Wire Break | Include | Include | Equipment | 364 | 2023-05-28 | 5460 | keep | 0 | May | 2023 | 0.0037188 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CAGUAS | 2023-05-28 08:15 | 2023-05-28 08:16 | 1590 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C23052800060 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 1590 | keep | 0 | May | 2023 | 0.0010829 | 0.0010829 | Momentary | FALSE | FALSE | Not_TMED_Event | 1590
CAGUAS | 2023-05-28 08:21 | 2023-05-28 11:24 | 30 | 3:03 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 30 EN C/L Y SE REMPLAZO AISLADOR EVENTO TRANSFERIDO DE PONCE | P23052800097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 183 | 2023-05-28 | 5490 | keep | 0 | May | 2023 | 0.0037392 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-28 08:30 | 2023-05-28 16:05 | 100 | 7:35 | P | DESGANCHE | 1 X 65 EN CL DESGANCHE | M23052800045 | New_Event | Vegetation Contact | Include | Include | Vegetation | 455 | 2023-05-28 | 45500 | keep | 0 | May | 2023 | 0.03099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CAGUAS | 2023-05-28 08:38 | 2023-05-28 14:27 | 359 | 5:49 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMA DE LA LINEA | C23052800075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 349 | 2023-05-28 | 125291 | keep | 0 | May | 2023 | 0.085335 | 0.00024451 | Sustained | FALSE | FALSE | Not_TMED_Event | 359
CAGUAS | 2023-05-28 08:44 | 2023-05-29 07:30 | 6 | 22:46 | P | ANIMAL | 1 X 15 EN XMR. CRUCE X AVE. EVENTO TRANSFERIDO DE PONCE | P23052800104 | New_Event | Animals | Include | Include | Wildlife | 1366 | 2023-05-28 | 8196 | keep | 0 | May | 2023 | 0.0055823 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-05-28 08:50 | 2023-05-28 13:00 | 10 | 4:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23052800109 | New_Event | Secondary Wire Break | Include | Include | Equipment | 250 | 2023-05-28 | 2500 | keep | 0 | May | 2023 | 0.0017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-28 08:51 | 2023-05-28 10:04 | 315 | 1:13 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | R23052800036 | New_Event | Animals | Include | Include | Wildlife | 73 | 2023-05-28 | 22995 | keep | 0 | May | 2023 | 0.015662 | 0.00021455 | Sustained | FALSE | FALSE | Not_TMED_Event | 315
CANOVANAS | 2023-05-28 08:53 | 2023-05-28 08:54 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23052800037 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 7621 | keep | 0 | May | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-05-28 08:54 | 2023-05-28 11:42 | 23 | 2:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23052700071 | Partial_restoration | Secondary Wire Break | Include | Include | Equipment | 168 | 2023-05-28 | 3864 | keep | 0 | May | 2023 | 0.0026318 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-28 09:10 | 2023-05-28 10:20 | 5 | 1:10 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23052800125 | New_Event | Secondary Wire Break | Include | Include | Equipment | 70 | 2023-05-28 | 350 | keep | 0 | May | 2023 | 0.00023838 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-28 09:31 | 2023-05-28 15:50 | 16 | 6:19 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23052800015 | New_Event | Vegetation Contact | Include | Include | Vegetation | 379 | 2023-05-28 | 6064 | keep | 0 | May | 2023 | 0.0041302 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BARRANQUITAS | 2023-05-28 09:44 | 2023-05-28 10:38 | 80 | 0:54 | P | DESGANCHE | 1 X 80 EN C/L Y DESGANCHE | C23052800107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-05-28 | 4320 | keep | 0 | May | 2023 | 0.0029423 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-05-28 09:48 | 2023-05-28 15:06 | 285 | 5:18 | P | ARBOL SOBRE LINEA | SE LEVANTO DOS CONDUCTORES PRIMARIOS SE CERRO TRIPSAVER Y DESGANCHE ARBOL TUMBO LINEAS | C23052800190 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 318 | 2023-05-28 | 90630 | keep | 0 | May | 2023 | 0.061728 | 0.00019411 | Sustained | FALSE | FALSE | Not_TMED_Event | 285
MAYAGÃœEZ | 2023-05-28 10:07 | 2023-05-28 12:03 | 45 | 1:56 | P | MAL TIEMPO/RAYOS | 2 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | M23052800065 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 116 | 2023-05-28 | 5220 | keep | 0 | May | 2023 | 0.0035553 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-05-28 10:18 | 2023-05-28 16:35 | 7 | 6:17 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23052800151 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 377 | 2023-05-28 | 2639 | keep | 0 | May | 2023 | 0.0017974 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
HUMACAO | 2023-05-28 10:39 | 2023-05-28 10:40 | 2450 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | C23052800130 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-28 | 2450 | keep | 0 | May | 2023 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-05-28 10:40 | 2023-05-28 12:10 | 362 | 1:30 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | C23052800133 | 1st_after_momentary | Animals | Include | Include | Wildlife | 90 | 2023-05-28 | 32580 | keep | 0 | May | 2023 | 0.02219 | 0.00024656 | Sustained | FALSE | FALSE | Not_TMED_Event | 362
SAN JUAN | 2023-05-28 10:45 | 2023-05-28 14:40 | 41 | 3:55 | P | CONDUCTOR ROTO O ABIERTO | 2 X 00 EN C/L SE LEVANTO CONDUCTOR PRIMARIO | S23052800032 | New_Event | Primary Wire Break | Include | Include | Equipment | 235 | 2023-05-28 | 9635 | keep | 0 | May | 2023 | 0.0065624 | 2.7925e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 41
BAYAMON | 2023-05-28 10:45 | 2023-05-28 12:31 | 10 | 1:46 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23052800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-28 | 1060 | keep | 0 | May | 2023 | 0.00072196 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-05-28 10:50 | 2023-05-28 17:27 | 1 | 6:37 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN BANCO DE XMRS DESGANCHE | R23052800042 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 397 | 2023-05-28 | 397 | keep | 0 | May | 2023 | 0.00027039 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-28 10:52 | 2023-05-28 12:47 | 3798 | 1:55 | S | PROTECCION DEFECTUOSA | DISPARO DE BREAKERS DE SUBESTACION Y ALTA NO TIRO LOCKOUT SE AMARRO EXTERNAMENTE CONTRA 1718-02 EN FID-1738829. SE ENCONTRO PROTECCION DESACTIVADA DE GR EN EL CAMPO. | B23052800034 | New_Event | Protection Miscoordination | Include | Include | Other | 115 | 2023-05-28 | 436770 | keep | 0 | May | 2023 | 0.29748 | 0.0025868 | Sustained | FALSE | FALSE | Not_TMED_Event | 3798
BAYAMON | 2023-05-28 10:52 | 2023-05-28 12:13 | 4622 | 1:21 | S | CONDUCTOR ROTO O ABIERTO | DISPARO DE BREAKERS DE SUBESTACION Y ALTA NO TIRO LOCKOUT SE AMARRO EXTERNAMENTE CONTRA 1717-01 EN FID-16917927 | B23052800034 | New_Event | Primary Wire Break | Include | Include | Equipment | 81 | 2023-05-28 | 374382 | keep | 0 | May | 2023 | 0.25499 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
BAYAMON | 2023-05-28 10:52 | 2023-05-28 13:13 | 4089 | 2:21 | S | PROTECCION DEFECTUOSA | DISPARO DE BREAKERS DE SUBESTACION Y ALTA NO TIRO LOCKOUT SE AMARRO EXTERNAMENTE CONTRA 1801-05 CERRADO EN FID-17256463. SE ENCONTRO PROTECCION DESACTIVADA DE GR EN EL CAMPO. | B23052800034 | New_Event | Protection Miscoordination | Include | Include | Other | 141 | 2023-05-28 | 576549 | keep | 0 | May | 2023 | 0.39268 | 0.002785 | Sustained | FALSE | FALSE | Not_TMED_Event | 4089
FAJARDO | 2023-05-28 10:53 | 2023-05-28 13:20 | 10 | 2:27 | P | ANIMAL | 1 X 10 EN XMR CRUCE X AVE TRANSFERIDO DE CAGUAS | C23052800139 | New_Event | Animals | Include | Include | Wildlife | 147 | 2023-05-28 | 1470 | keep | 0 | May | 2023 | 0.0010012 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-28 10:57 | 2023-05-28 15:26 | 724 | 4:29 | P | DESGANCHE | 1 X 100 EN C/L Y SE REALIZO DESGANCHE | C23052800140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 269 | 2023-05-28 | 194756 | keep | 0 | May | 2023 | 0.13265 | 0.00049311 | Sustained | FALSE | FALSE | Not_TMED_Event | 724
MAYAGÃœEZ | 2023-05-28 11:07 | 2023-05-28 14:30 | 35 | 3:23 | P | DESGANCHE | 2 X 50 EN CL DESGANCHE | M23052800026 | New_Event | Vegetation Contact | Include | Include | Vegetation | 203 | 2023-05-28 | 7105 | keep | 0 | May | 2023 | 0.0048392 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-28 11:10 | 2023-05-29 06:35 | 25 | 19:25 | P | CONDUCTOR ROTO O ABIERTO | SE LLEVO PUENTE DE LINEA A CAJA NO FUNDIO FUSIBLE | S23052800006 | New_Event | Primary Wire Break | Include | Include | Equipment | 1165 | 2023-05-28 | 29125 | keep | 0 | May | 2023 | 0.019837 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-28 11:14 | 2023-05-28 11:15 | 338 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 338 | keep | 0 | May | 2023 | 0.00023021 | 0.00023021 | Momentary | FALSE | FALSE | Not_TMED_Event | 338
FAJARDO | 2023-05-28 11:23 | 2023-05-28 11:24 | 1234 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR | R23052800043 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-28 | 1234 | keep | 0 | May | 2023 | 0.00084047 | 0.00084047 | Momentary | FALSE | FALSE | Not_TMED_Event | 1234
FAJARDO | 2023-05-28 11:24 | 2023-05-28 11:54 | 3 | 0:30 | P | ANIMAL | 1 X 20 EN C/L CRUCE X AVE EVENTO TRANSFERIDO DE PONCE | P23052800153 | 1st_after_momentary | Animals | Include | Include | Wildlife | 30 | 2023-05-28 | 90 | keep | 0 | May | 2023 | 6.1299e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-05-28 11:27 | 2023-05-28 11:30 | 2490 | 0:03 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1619-03 LLEVA 50 % 1336-06 SE CERRO POR CONTROL | R2305280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 3 | 2023-05-28 | 7470 | keep | 0 | May | 2023 | 0.0050878 | 0.0016959 | Momentary | FALSE | FALSE | Not_TMED_Event | 2490
CANOVANAS | 2023-05-28 11:27 | 2023-05-28 11:30 | 5062 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1619-03 LLEVA 50 % 1336-06 SE CERRO POR CONTROL | R2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-28 | 15186 | keep | 0 | May | 2023 | 0.010343 | 0.0034477 | Momentary | FALSE | FALSE | Not_TMED_Event | 5062
BAYAMON | 2023-05-28 11:27 | 2023-05-28 11:28 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 5252 | keep | 0 | May | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
CAGUAS | 2023-05-28 11:45 | 2023-05-28 18:43 | 14 | 6:58 | P | TRANSFORMADOR AVERIADO | XMR PROBO MALO SE LE TRANSFIRIO LA CARGA AL XMR CON FID 30091100. SE REFIRIO PARA REEMPLAZO DEL XMR | C23052800146 | New_Event | Service Transformer Failure | Include | Include | Equipment | 418 | 2023-05-28 | 5852 | keep | 0 | May | 2023 | 0.0039858 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
UTUADO | 2023-05-28 11:50 | 2023-05-28 14:58 | 50 | 3:08 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | DAMAGE ID-04542283 INSTALAR POSTE Y RELOCALIZAR LINEAS PRIMARIAS | A23052800052 | New_Event | Primary Pole Failure | Include | Include | Equipment | 188 | 2023-05-28 | 9400 | keep | 0 | May | 2023 | 0.0064023 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-28 11:54 | 2023-05-28 11:55 | 1320 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23052800152 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 1320 | keep | 0 | May | 2023 | 0.00089905 | 0.00089905 | Momentary | FALSE | FALSE | Not_TMED_Event | 1320
GUAYAMA | 2023-05-28 11:54 | 2023-05-28 13:50 | 10 | 1:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 20 EN XMR MAL TIEMPO LLUVIAS | P23052800189 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 116 | 2023-05-28 | 1160 | keep | 0 | May | 2023 | 0.00079007 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-05-28 12:15 | 2023-05-28 17:14 | 4 | 4:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 25 EN RISER REMPLAZO 3 CAJAS AVERIADAS Y 20 PIES DE CABLE ORDEN CERRADA | R23052800054 | New_Event | Cutout Failure | Include | Include | Equipment | 299 | 2023-05-28 | 1196 | keep | 0 | May | 2023 | 0.00081459 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-28 12:18 | 2023-05-28 12:20 | 3438 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO LLEVA 1806-01 | B2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-28 | 6876 | keep | 0 | May | 2023 | 0.0046832 | 0.0023416 | Momentary | FALSE | FALSE | Not_TMED_Event | 3438
BAYAMON | 2023-05-28 12:18 | 2023-05-28 12:20 | 3798 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO CARGA POR 1718-02 | B2305280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-28 | 7596 | keep | 0 | May | 2023 | 0.0051736 | 0.0025868 | Momentary | FALSE | FALSE | Not_TMED_Event | 3798
CANOVANAS | 2023-05-28 12:27 | 2023-05-28 14:23 | 6 | 1:56 | P | SECUNDARIA/DESGANCHE | 1 X 8 EN XMR DESGANCHE | R23052800055 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 116 | 2023-05-28 | 696 | keep | 0 | May | 2023 | 0.00047404 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-05-28 12:30 | 2023-05-28 17:02 | 30 | 4:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA POR DESGANCHE | A23052800087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 272 | 2023-05-28 | 8160 | keep | 0 | May | 2023 | 0.0055577 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-28 12:31 | 2023-05-28 12:49 | 30 | 0:18 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23052700259 | New_Event | Secondary Wire Break | Include | Include | Equipment | 18 | 2023-05-28 | 540 | keep | 0 | May | 2023 | 0.00036779 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-05-28 12:33 | 2023-05-28 16:00 | 100 | 3:27 | P | CONDUCTOR ROTO O ABIERTO | 2 X 100 EN C/L SE REPARO ALAMBRE PRIMARIO | P23052800203 | New_Event | Primary Wire Break | Include | Include | Equipment | 207 | 2023-05-28 | 20700 | keep | 0 | May | 2023 | 0.014099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
PONCE | 2023-05-28 12:33 | 2023-05-28 15:10 | 1 | 2:37 | P | ANIMAL | 1 X 50 EN C/L AVE CRUZO LINEAS | P23052800088 | New_Event | Animals | Include | Include | Wildlife | 157 | 2023-05-28 | 157 | keep | 0 | May | 2023 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-28 12:39 | 2023-05-28 12:40 | 4079 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE LLEVA 1806-02 10% POR 1801-02 | B2305280000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-28 | 4079 | keep | 0 | May | 2023 | 0.0027782 | 0.0027782 | Momentary | FALSE | FALSE | Not_TMED_Event | 4079
BAYAMON | 2023-05-28 12:39 | 2023-05-28 12:40 | 4622 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE CARGA POR 1717-01 | B2305280000X | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-28 | 4622 | keep | 0 | May | 2023 | 0.003148 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-28 12:42 | 2023-05-28 14:46 | 600 | 2:04 | P | CONDUCTOR ROTO O ABIERTO | CERRO PUENTE Y SE REMPLAZO CONECTORES QUEMADOS EN EL TRONCAL EVENTO TRANSFERIDO DE PONCE | P23052800206 | New_Event | Primary Wire Break | Include | Include | Equipment | 124 | 2023-05-28 | 74400 | keep | 0 | May | 2023 | 0.050674 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
GUAYAMA | 2023-05-28 12:42 | 2023-05-28 13:08 | 610 | 0:26 | T | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23052800204 | New_Event | Primary Wire Break | Include | Include | Equipment | 26 | 2023-05-28 | 15860 | keep | 0 | May | 2023 | 0.010802 | 0.00041547 | Sustained | FALSE | FALSE | Not_TMED_Event | 610
AGUADILLA | 2023-05-28 12:48 | 2023-05-28 14:21 | 4 | 1:33 | P | MAL TIEMPO/RAYOS | 2 X 15 EN TRANSFORMADOR DESCARGAS ELECTRICAS | M23052800086 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2023-05-28 | 372 | keep | 0 | May | 2023 | 0.00025337 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 108 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S23052800059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 324 | keep | 0 | May | 2023 | 0.00022067 | 7.3558e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 108
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 1368 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S23052800059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 4104 | keep | 0 | May | 2023 | 0.0027952 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 2064 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S23052800059 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 6192 | keep | 0 | May | 2023 | 0.0042173 | 0.0014058 | Momentary | FALSE | FALSE | Not_TMED_Event | 2064
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 1681 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S23052800057 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 5043 | keep | 0 | May | 2023 | 0.0034348 | 0.0011449 | Momentary | FALSE | FALSE | Not_TMED_Event | 1681
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 2435 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 LLEVA 45% DEL 1401-08 | S23052800057 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 7305 | keep | 0 | May | 2023 | 0.0049754 | 0.0016585 | Momentary | FALSE | FALSE | Not_TMED_Event | 2435
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 726 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 | S23052800057 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 2178 | keep | 0 | May | 2023 | 0.0014834 | 0.00049448 | Momentary | FALSE | FALSE | Not_TMED_Event | 726
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 225 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 98% POR EL 1303-05 | S23052800057 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 675 | keep | 0 | May | 2023 | 0.00045974 | 0.00015325 | Momentary | FALSE | FALSE | Not_TMED_Event | 225
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 870 | 0:03 | S | LINEA DE TRANSMISION 115KV | DISPARO DE LINEA 36200 LLEVA 98% DEL 1303-04 | S23052800057 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 2610 | keep | 0 | May | 2023 | 0.0017777 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
SAN JUAN | 2023-05-28 12:57 | 2023-05-28 13:00 | 20 | 0:03 | P | LINEA DE TRANSMISION 115KV | DISPARO DE LA 36200 45% DE SU CARGA POR EL 1303-02 | S23052800057 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 60 | keep | 0 | May | 2023 | 4.0866e-05 | 1.3622e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-28 12:57 | 2023-05-28 17:19 | 11 | 4:22 | P | MAL TIEMPO/RAYOS | 1 X 20 EN TRANSFORMADOR DESCARGA ELECTRICA | M23052800088 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 262 | 2023-05-28 | 2882 | keep | 0 | May | 2023 | 0.0019629 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
CANOVANAS | 2023-05-28 13:11 | 2023-05-28 13:41 | 10 | 0:30 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | R23052800061 | New_Event | Secondary Wire Break | Include | Include | Equipment | 30 | 2023-05-28 | 300 | keep | 0 | May | 2023 | 0.00020433 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-28 13:13 | 2023-05-29 13:51 | 15 | 24:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 25 EN C/L MAL TIEMPO VIENTO EVENTO TRANSFERIDO DE PONCE | P23052700315 | Partial_restoration | Bad Weather (Rain & Wind) | Include | Include | Weather | 1478 | 2023-05-28 | 22170 | keep | 0 | May | 2023 | 0.0151 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-28 13:18 | 2023-05-28 15:09 | 200 | 1:51 | P | DESGANCHE | 1 X 100 EN CL SE RETIRO BAMBU | M23052800092 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-05-28 | 22200 | keep | 0 | May | 2023 | 0.01512 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-05-28 13:21 | 2023-05-28 16:40 | 10 | 3:19 | P | NO SE REPORTO CAUSA | 1 X 80 EN CL NO SE REPORTA CAUSA | M23052800094 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 199 | 2023-05-28 | 1990 | keep | 0 | May | 2023 | 0.0013554 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-28 13:25 | 2023-05-28 13:45 | 4079 | 0:20 | P | ALIMENTADOR AMARRADO | DISPARO 1717-01 LLEVA 1806-02 Y 10% POR 1801-02. SE ABRIO AMARRE CON 1806-02 Y SE CERRO POR SCADA | B2305280000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 20 | 2023-05-28 | 81580 | keep | 0 | May | 2023 | 0.055564 | 0.0027782 | Sustained | FALSE | FALSE | Not_TMED_Event | 4079
BAYAMON | 2023-05-28 13:25 | 2023-05-28 16:00 | 4622 | 2:35 | T | CONDUCTOR ROTO O ABIERTO | DISPARO DEL 1717-01 POR PUENTE ABIERTO DEL 1806-02, SE ABRIO N/O Y SE CERRO 1717-01 MEDIANTE BY-230528-01 SE CERRO PUENTE Y SE CERRO N/O NUEVAMENTE ENTRANDO UN 2% DEL 1806-02 POR 1717-01 | B2305280000X | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 155 | 2023-05-28 | 716410 | keep | 0 | May | 2023 | 0.48794 | 0.003148 | Sustained | FALSE | FALSE | Not_TMED_Event | 4622
VEGA BAJA | 2023-05-28 13:37 | 2023-05-28 14:47 | 7 | 1:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN TRANSFORMADOR SE REEMPLAZO PORTAFUSIBLE NO TIENE DISPOSITIVO VA CAER EN PONCE | P23052800223 | New_Event | Cutout Failure | Include | Include | Equipment | 70 | 2023-05-28 | 490 | keep | 0 | May | 2023 | 0.00033374 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-05-28 13:44 | 2023-05-28 13:47 | 1228 | 0:03 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14400 | C23052800168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 3684 | keep | 0 | May | 2023 | 0.0025092 | 0.00083639 | Momentary | FALSE | FALSE | Not_TMED_Event | 1228
CAGUAS | 2023-05-28 13:44 | 2023-05-28 13:47 | 1271 | 0:03 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14400 | C23052800168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 3813 | keep | 0 | May | 2023 | 0.002597 | 0.00086567 | Momentary | FALSE | FALSE | Not_TMED_Event | 1271
CAGUAS | 2023-05-28 13:44 | 2023-05-28 13:47 | 1893 | 0:03 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14400 | C23052800168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 5679 | keep | 0 | May | 2023 | 0.0038679 | 0.0012893 | Momentary | FALSE | FALSE | Not_TMED_Event | 1893
CAGUAS | 2023-05-28 13:44 | 2023-05-28 13:47 | 473 | 0:03 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 14400 | C23052800168 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-05-28 | 1419 | keep | 0 | May | 2023 | 0.00096647 | 0.00032216 | Momentary | FALSE | FALSE | Not_TMED_Event | 473
BAYAMON | 2023-05-28 14:13 | 2023-05-29 09:34 | 7 | 19:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23052800102 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1161 | 2023-05-28 | 8127 | keep | 0 | May | 2023 | 0.0055353 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
ARECIBO | 2023-05-28 14:13 | 2023-05-28 20:08 | 25 | 5:55 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA POR RAMA | A23052800096 | New_Event | Vegetation Contact | Include | Include | Vegetation | 355 | 2023-05-28 | 8875 | keep | 0 | May | 2023 | 0.0060447 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-05-28 14:29 | 2023-05-28 16:20 | 38 | 1:51 | P | DESGANCHE | 3 X 40 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LA LINEA | C23052800186 | New_Event | Vegetation Contact | Include | Include | Vegetation | 111 | 2023-05-28 | 4218 | keep | 0 | May | 2023 | 0.0028729 | 2.5882e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 38
ARECIBO | 2023-05-28 14:38 | 2023-05-28 16:30 | 15 | 1:52 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA POR DESGANCHE | A23052800099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 112 | 2023-05-28 | 1680 | keep | 0 | May | 2023 | 0.0011442 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-28 14:43 | 2023-05-29 09:42 | 35 | 18:59 | P | ANIMAL | 2 X 40 EN SU-7 Y 2 X 30 EN RISER CRUCE X AVE | B23052800005 | New_Event | Animals | Include | Include | Wildlife | 1139 | 2023-05-28 | 39865 | keep | 0 | May | 2023 | 0.027152 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-28 14:43 | 2023-05-29 10:05 | 10 | 19:22 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BARRAS EN PEDESTAL | S23052800036 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1162 | 2023-05-28 | 11620 | keep | 0 | May | 2023 | 0.0079143 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-28 15:18 | 2023-05-28 15:19 | 3701 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO | C23052800194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 3701 | keep | 0 | May | 2023 | 0.0025207 | 0.0025207 | Momentary | FALSE | FALSE | Not_TMED_Event | 3701
HUMACAO | 2023-05-28 15:18 | 2023-05-28 15:19 | 989 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO | C23052800194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 989 | keep | 0 | May | 2023 | 0.0006736 | 0.0006736 | Momentary | FALSE | FALSE | Not_TMED_Event | 989
HUMACAO | 2023-05-28 15:18 | 2023-05-28 15:19 | 1467 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5400 DE RIO BLANCO A NAGUABO | C23052800194 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-28 | 1467 | keep | 0 | May | 2023 | 0.00099917 | 0.00099917 | Momentary | FALSE | FALSE | Not_TMED_Event | 1467
AGUADILLA | 2023-05-28 15:21 | 2023-05-28 20:17 | 541 | 4:56 | P | LINEA DE TRANSMISION 38KV | GOI MY-230528-01A SE SECCIONALIZA TRAMO ALIMENTADOR 7805-13 POR LINEA 1900 SOBRE CIRCUITO Y SE TRANSFIERE CARGA PARCIAL AL 7903-07 CONDUCTOR AVERIADO SAN SEBASTIAN 1910-ACB 1905A | M23052800127 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 296 | 2023-05-28 | 160136 | keep | 0 | May | 2023 | 0.10907 | 0.00036847 | Sustained | FALSE | FALSE | Not_TMED_Event | 541
AGUADILLA | 2023-05-28 15:21 | 2023-05-28 16:18 | 3522 | 0:57 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE CIERRA TRAMO MOD 1925 HACIA DOS BOCAS ABIERTO EN MOD 1917 HACIA LARES CONDUCTOR AVERIADO SAN SEBASTIAN 1910-ACB 1905A | M23052800111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 57 | 2023-05-28 | 200754 | keep | 0 | May | 2023 | 0.13673 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
AGUADILLA | 2023-05-28 15:21 | 2023-05-28 16:18 | 1337 | 0:57 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE CIERRA TRAMO MOD 1925 HACIA DOS BOCAS ABIERTO EN MOD 1917 HACIA LARES CONDUCTOR AVERIADO SAN SEBASTIAN 1910-ACB 1905A | M23052800111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 57 | 2023-05-28 | 76209 | keep | 0 | May | 2023 | 0.051906 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-05-28 15:21 | 2023-05-28 16:18 | 2825 | 0:57 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE CIERRA TRAMO MOD 1925 HACIA DOS BOCAS ABIERTO EN MOD 1917 HACIA LARES CONDUCTOR AVERIADO SAN SEBASTIAN 1910-ACB 1905A | M23052800111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 57 | 2023-05-28 | 161025 | keep | 0 | May | 2023 | 0.10967 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
AGUADILLA | 2023-05-28 15:21 | 2023-05-28 16:18 | 1287 | 0:57 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE CIERRA TRAMO MOD 1925 HACIA DOS BOCAS ABIERTO EN MOD 1917 HACIA LARES CONDUCTOR AVERIADO SAN SEBASTIAN 1910-ACB 1905A | M23052800111 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 57 | 2023-05-28 | 73359 | keep | 0 | May | 2023 | 0.049964 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
AGUADILLA | 2023-05-28 15:21 | 2023-05-28 16:18 | 1417 | 0:57 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE CIERRA TRAMO MOD 1925 HACIA DOS BOCAS ABIERTO EN MOD 1917 HACIA LARES CONDUCTOR AVERIADO SAN SEBASTIAN 1910-ACB 1905A | M23052800112 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 57 | 2023-05-28 | 80769 | keep | 0 | May | 2023 | 0.055011 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
AGUADILLA | 2023-05-28 15:21 | 2023-05-28 16:18 | 80 | 0:57 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE CIERRA TRAMO MOD 1925 HACIA DOS BOCAS ABIERTO EN MOD 1917 HACIA LARES CONDUCTOR AVERIADO SAN SEBASTIAN 1910-ACB 1905A | M23052800112 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 57 | 2023-05-28 | 4560 | keep | 0 | May | 2023 | 0.0031058 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CAGUAS | 2023-05-28 15:26 | 2023-05-28 15:27 | 1772 | 0:01 | T | DESGANCHE | RECIERRE DE BKR HACIENDO OPERACIONES PROBO MALO | C23052800196 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-28 | 1772 | keep | 0 | May | 2023 | 0.0012069 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-28 15:27 | 2023-05-28 16:40 | 724 | 1:13 | P | DESGANCHE | 1 X 100 EN C/L Y SE REALIZO DESGANCHE | C23052800140 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 73 | 2023-05-28 | 52852 | keep | 0 | May | 2023 | 0.035997 | 0.00049311 | Sustained | FALSE | FALSE | Not_TMED_Event | 724
BAYAMON | 2023-05-28 15:30 | 2023-05-28 17:30 | 14 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23052800110 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-05-28 | 1680 | keep | 0 | May | 2023 | 0.0011442 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
HUMACAO | 2023-05-28 15:50 | 2023-05-28 18:04 | 198 | 2:14 | P | DESGANCHE | 1 X 30 Y 1 X 40 EN C/LS DESGANCHE DE BAMBUAS | C23052800201 | New_Event | Vegetation Contact | Include | Include | Vegetation | 134 | 2023-05-28 | 26532 | keep | 0 | May | 2023 | 0.018071 | 0.00013486 | Sustained | FALSE | FALSE | Not_TMED_Event | 198
MAYAGÃœEZ | 2023-05-28 15:51 | 2023-05-28 17:36 | 60 | 1:45 | P | DESGANCHE | 1 X 80 EN CL DESGANCHE | M23052800115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-05-28 | 6300 | keep | 0 | May | 2023 | 0.0042909 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-28 16:00 | 2023-05-28 20:30 | 4529 | 4:30 | P | CONDUCTOR ROTO O ABIERTO | BY-230528-01 SE SECCIONALIZO ALIMENTADOR LUEGO DE ENERGIZADA SUBESTACION Y SE CERRO POR SCADA ENTRANDO UN 10% EN SERVICIO | B2305280000X | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 270 | 2023-05-28 | 1222830 | keep | 0 | May | 2023 | 0.83286 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-28 16:06 | 2023-05-28 17:00 | 30 | 0:54 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | P23052800282 | New_Event | Vegetation Contact | Include | Include | Vegetation | 54 | 2023-05-28 | 1620 | keep | 0 | May | 2023 | 0.0011034 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
AGUADILLA | 2023-05-28 16:15 | 2023-05-28 19:22 | 10 | 3:07 | P | OTRAS CAUSAS | 1 X 15 EN TRANSFORMADOR POR SULFATADO | A23052800118 | New_Event | Other Causes | Include | Include | Other | 187 | 2023-05-28 | 1870 | keep | 0 | May | 2023 | 0.0012736 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-28 16:21 | 2023-05-28 17:10 | 1 | 0:49 | P | NO SE REPORTO CAUSA | 1 RVA EN BOVEDA | S23052800087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 49 | 2023-05-28 | 49 | keep | 0 | May | 2023 | 3.3374e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-28 16:24 | 2023-05-28 17:41 | 33 | 1:17 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23052800116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 77 | 2023-05-28 | 2541 | keep | 0 | May | 2023 | 0.0017307 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
ARECIBO | 2023-05-28 16:32 | 2023-05-29 18:55 | 40 | 26:23 | P | DESGANCHE | 2 X 30 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO VERIFICADO EN BITACORA | A23052800121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1583 | 2023-05-28 | 63320 | keep | 0 | May | 2023 | 0.043127 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-05-28 16:40 | 2023-05-28 20:05 | 240 | 3:25 | P | ANIMAL | 1 X 30 Y 1 X 40 EN C/LS CRUCE X AVE | C23052800212 | New_Event | Animals | Include | Include | Wildlife | 205 | 2023-05-28 | 49200 | keep | 0 | May | 2023 | 0.03351 | 0.00016346 | Sustained | FALSE | FALSE | Not_TMED_Event | 240
SAN JUAN | 2023-05-28 17:01 | 2023-05-29 13:23 | 20 | 20:22 | P | TRANSFORMADOR AVERIADO | XMR PROBO MALO SE TRANSFIRIO SU CARGA AL OTRO XMR DEBIDO A QUE TENIA PANAL DE ABEJAS NO SE PUDO REEMPLAZAR | S23052800089 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1222 | 2023-05-28 | 24440 | keep | 0 | May | 2023 | 0.016646 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-28 17:01 | 2023-05-28 17:02 | 2203 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | S23052800090 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 2203 | keep | 0 | May | 2023 | 0.0015005 | 0.0015005 | Momentary | FALSE | FALSE | Not_TMED_Event | 2203
ARECIBO | 2023-05-28 17:04 | 2023-05-28 22:40 | 20 | 5:36 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A23052800141 | New_Event | Animals | Include | Include | Wildlife | 336 | 2023-05-28 | 6720 | keep | 0 | May | 2023 | 0.004577 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-28 17:17 | 2023-05-28 22:24 | 20 | 5:07 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052800126 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 307 | 2023-05-28 | 6140 | keep | 0 | May | 2023 | 0.0041819 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-05-28 17:20 | 2023-05-29 08:52 | 15 | 15:32 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE | S23052800091 | New_Event | Vegetation Contact | Include | Include | Vegetation | 932 | 2023-05-28 | 13980 | keep | 0 | May | 2023 | 0.0095217 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-05-28 17:29 | 2023-05-28 19:02 | 24 | 1:33 | P | ANIMAL | 1 X 25 EN C/L CURCE X AVE | C23052800208 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-05-28 | 2232 | keep | 0 | May | 2023 | 0.0015202 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
UTUADO | 2023-05-28 17:45 | 2023-05-28 21:50 | 9 | 4:05 | P | CONDUCTOR ROTO O ABIERTO | 2 X 10 EN TRANSFORMADOR SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | A23052800141 | New_Event | Primary Wire Break | Include | Include | Equipment | 245 | 2023-05-28 | 2205 | keep | 0 | May | 2023 | 0.0015018 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CAGUAS | 2023-05-28 17:46 | 2023-05-29 16:18 | 10 | 22:32 | P | CONDUCTOR ROTO O ABIERTO | SE REEMPLAZARON 2 CAJAS PRIMARIAS Y SE LEVANTO CONDUCTOR PRIMARIO | C23052800213 | New_Event | Primary Wire Break | Include | Include | Equipment | 1352 | 2023-05-28 | 13520 | keep | 0 | May | 2023 | 0.0092084 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-28 18:48 | 2023-05-28 18:49 | 320 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 320 | keep | 0 | May | 2023 | 0.00021795 | 0.00021795 | Momentary | FALSE | FALSE | Not_TMED_Event | 320
MAYAGÃœEZ | 2023-05-28 19:05 | 2023-05-29 09:50 | 60 | 14:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA POR LLUVIA Y VIENTO | M23052800152 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 885 | 2023-05-28 | 53100 | keep | 0 | May | 2023 | 0.036166 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-28 19:20 | 2023-05-29 02:48 | 30 | 7:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X50 EN C/L SE REMPLAZO CAJA PRIMARIA | B23052800188 | New_Event | Cutout Failure | Include | Include | Equipment | 448 | 2023-05-28 | 13440 | keep | 0 | May | 2023 | 0.0091539 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
ARECIBO | 2023-05-28 19:28 | 2023-05-28 21:13 | 50 | 1:45 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | A23052800152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 105 | 2023-05-28 | 5250 | keep | 0 | May | 2023 | 0.0035758 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-05-28 19:31 | 2023-05-29 09:59 | 1 | 14:28 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | R23052800085 | New_Event | Animals | Include | Include | Wildlife | 868 | 2023-05-28 | 868 | keep | 0 | May | 2023 | 0.00059119 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-28 19:48 | 2023-05-29 09:10 | 12 | 13:22 | P | DESGANCHE | 1 X 20 EN C/L DESGANCHE | R23052800086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 802 | 2023-05-28 | 9624 | keep | 0 | May | 2023 | 0.0065549 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-28 19:53 | 2023-05-29 07:50 | 83 | 11:57 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 50 EN C/L CRUCE X AVE | B23052800209 | New_Event | Animals | Include | Include | Wildlife | 717 | 2023-05-28 | 59511 | keep | 0 | May | 2023 | 0.040533 | 5.6531e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 83
BAYAMON | 2023-05-28 19:54 | 2023-05-29 14:32 | 5 | 18:38 | P | PARARRAYOS DEFECTUOSO | 1 X 12 EN PM SE ELIMINO PARARAYO | B23052800210 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 1118 | 2023-05-28 | 5590 | keep | 0 | May | 2023 | 0.0038073 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-05-28 20:02 | 2023-05-29 14:31 | 39 | 18:29 | P | CABLE SOTERRADO AVERIADO | 1 X 140 EN RISER AVERIA NUEVA SU-1 @ T-44A SE CORRIO EL N/O DEL T-40 @ T-44A 100% EN SERVICIO | C23052800220 | New_Event | UG Cable Fault | Include | Include | Equipment | 1109 | 2023-05-28 | 43251 | keep | 0 | May | 2023 | 0.029458 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
BAYAMON | 2023-05-28 20:07 | 2023-05-29 11:55 | 15 | 15:48 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER EVENTO TRANSFERIDO | P23052800341 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 948 | 2023-05-28 | 14220 | keep | 0 | May | 2023 | 0.0096852 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-28 20:20 | 2023-05-28 20:21 | 2067 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | M23052800160 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-28 | 2067 | keep | 0 | May | 2023 | 0.0014078 | 0.0014078 | Momentary | FALSE | FALSE | Not_TMED_Event | 2067
MAYAGÃœEZ | 2023-05-28 20:21 | 2023-05-29 11:57 | 60 | 15:36 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA ROTA SE ABRIO MACHETES PARA REPARARLA | M23052800165 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 936 | 2023-05-28 | 56160 | keep | 0 | May | 2023 | 0.03825 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
GUAYAMA | 2023-05-28 20:29 | 2023-05-29 10:32 | 4 | 14:03 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN TRANSFORMADOR DESGANCHE | P23052800347 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 843 | 2023-05-28 | 3372 | keep | 0 | May | 2023 | 0.0022967 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-28 20:30 | 2023-05-28 21:17 | 4067 | 0:47 | P | CONDUCTOR ROTO O ABIERTO | BY-230528-01 SE SECCIONALIZOTRAMO POR MONTE AVERIADO Y SE CERRO N/O CONTRA 1806-01, ENTRO 80% EN SERVICIO | B2305280000X | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 47 | 2023-05-28 | 191149 | keep | 0 | May | 2023 | 0.13019 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-05-28 20:49 | 2023-05-28 21:45 | 1 | 0:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 15 EN CORTE DE LINEA POR LLUVIA | A23052800164 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 56 | 2023-05-28 | 56 | keep | 0 | May | 2023 | 3.8141e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-28 21:17 | 2023-05-28 22:09 | 924 | 0:52 | P | CONDUCTOR ROTO O ABIERTO | BY-230528-01 SE SECCIONALIZO TRAMO POR MONTE AVERIADO Y SE CERRO N/O CONTRA 1806-01 | B2305280000X | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 52 | 2023-05-28 | 48048 | keep | 0 | May | 2023 | 0.032725 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-05-28 21:22 | 2023-05-29 01:58 | 3522 | 4:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | M23052800182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 276 | 2023-05-28 | 972072 | keep | 0 | May | 2023 | 0.66207 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
AGUADILLA | 2023-05-28 21:22 | 2023-05-29 01:58 | 1337 | 4:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | M23052800182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 276 | 2023-05-28 | 369012 | keep | 0 | May | 2023 | 0.25133 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-05-28 21:22 | 2023-05-29 01:58 | 2825 | 4:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | M23052800182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 276 | 2023-05-28 | 779700 | keep | 0 | May | 2023 | 0.53105 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
AGUADILLA | 2023-05-28 21:22 | 2023-05-29 01:58 | 1287 | 4:36 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | M23052800182 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 276 | 2023-05-28 | 355212 | keep | 0 | May | 2023 | 0.24193 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
AGUADILLA | 2023-05-28 21:22 | 2023-05-29 02:09 | 1417 | 4:47 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | M23052800183 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 287 | 2023-05-28 | 406679 | keep | 0 | May | 2023 | 0.27699 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
AGUADILLA | 2023-05-28 21:22 | 2023-05-29 02:09 | 80 | 4:47 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | M23052800183 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 287 | 2023-05-28 | 22960 | keep | 0 | May | 2023 | 0.015638 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-05-28 21:22 | 2023-05-28 23:56 | 1405 | 2:34 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE SECCIONALIZO LINEA Y SE PASO LA CARGA A LINEA 2400 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | A23052800178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 154 | 2023-05-28 | 216370 | keep | 0 | May | 2023 | 0.14737 | 0.00095694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2023-05-28 21:22 | 2023-05-28 23:56 | 669 | 2:34 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE SECCIONALIZO LINEA Y SE PASO LA CARGA A LINEA 2400 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | A23052800178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 154 | 2023-05-28 | 103026 | keep | 0 | May | 2023 | 0.070171 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2023-05-28 21:22 | 2023-05-28 23:56 | 1527 | 2:34 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE SECCIONALIZO LINEA Y SE PASO LA CARGA A LINEA 2400 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | A23052800178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 154 | 2023-05-28 | 235158 | keep | 0 | May | 2023 | 0.16017 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2023-05-28 21:22 | 2023-05-28 23:56 | 1054 | 2:34 | S | LINEA DE TRANSMISION 230KV | DISPARO LINEA 1900 SE SECCIONALIZO LINEA Y SE PASO LA CARGA A LINEA 2400 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | A23052800178 | New_Event | 230 kV Transmission Line Source | Include | Include | Power supply | 154 | 2023-05-28 | 162316 | keep | 0 | May | 2023 | 0.11055 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2023-05-28 21:22 | 2023-05-28 23:56 | 932 | 2:34 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE SECCIONALIZO LINEA Y SE PASO LA CARGA A LINEA 2400 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | A23052800178 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 154 | 2023-05-28 | 143528 | keep | 0 | May | 2023 | 0.097756 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2023-05-28 21:22 | 2023-05-29 00:56 | 1633 | 3:34 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE PASO LA CARGA POR LA LINEA 2400 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | A23052800180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 214 | 2023-05-28 | 349462 | keep | 0 | May | 2023 | 0.23802 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-05-28 21:22 | 2023-05-29 00:56 | 1624 | 3:34 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 SE PASO LA CARGA POR LA LINEA 2400 CONDUCTOR AVERIADO DOS BOCAS 1960-ACB 1927B | A23052800180 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 214 | 2023-05-28 | 347536 | keep | 0 | May | 2023 | 0.23671 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
CAGUAS | 2023-05-28 21:33 | 2023-05-28 21:34 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305280000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-28 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
AGUADILLA | 2023-05-28 21:36 | 2023-05-28 23:10 | 125 | 1:34 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052800184 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 94 | 2023-05-28 | 11750 | keep | 0 | May | 2023 | 0.0080029 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
PONCE | 2023-05-28 21:44 | 2023-05-29 10:11 | 4 | 12:27 | P | SECUNDARIA/DESGANCHE | 2 X 8 EN TRANSFORMADOR DESGANCHE | P23052800383 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 747 | 2023-05-28 | 2988 | keep | 0 | May | 2023 | 0.0020351 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-05-28 21:58 | 2023-05-28 22:47 | 13 | 0:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO EN XMR PARA REPARAR SECUNDARIA | B23052800276 | New_Event | Secondary Wire Break | Include | Include | Equipment | 49 | 2023-05-28 | 637 | keep | 0 | May | 2023 | 0.00043386 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
ARECIBO | 2023-05-28 22:31 | 2023-05-29 | 110 | 1:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23052800220 | New_Event | Cutout Failure | Include | Include | Equipment | 89 | 2023-05-28 | 9790 | keep | 0 | May | 2023 | 0.0066679 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
BAYAMON | 2023-05-29 00:15 | 2023-05-29 17:23 | 59 | 17:08 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN PROVISIONAL SE REMPLAZO CAJA | B23052900002 | New_Event | Cutout Failure | Include | Include | Equipment | 1028 | 2023-05-29 | 60652 | keep | 0 | May | 2023 | 0.04131 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
GUAYAMA | 2023-05-29 00:19 | 2023-05-29 00:20 | 1945 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23052900001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 1945 | keep | 0 | May | 2023 | 0.0013247 | 0.0013247 | Momentary | FALSE | FALSE | Not_TMED_Event | 1945
HUMACAO | 2023-05-29 01:34 | 2023-05-29 07:21 | 60 | 5:47 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23052900001 | New_Event | Animals | Include | Include | Wildlife | 347 | 2023-05-29 | 20820 | keep | 0 | May | 2023 | 0.01418 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CAGUAS | 2023-05-29 01:42 | 2023-05-29 01:43 | 1367 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SOLO LLEVA 80% DE SU CARGA | C23052900002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 1367 | keep | 0 | May | 2023 | 0.00093106 | 0.00093106 | Momentary | FALSE | FALSE | Not_TMED_Event | 1367
BAYAMON | 2023-05-29 02:13 | 2023-05-29 11:55 | 60 | 9:42 | P | DESGANCHE | 1 X 50 EN C/L SE DESGANCHO | B23052900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 582 | 2023-05-29 | 34920 | keep | 0 | May | 2023 | 0.023784 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-29 02:13 | 2023-05-29 13:47 | 30 | 11:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23052900048 | New_Event | Secondary Wire Break | Include | Include | Equipment | 694 | 2023-05-29 | 20820 | keep | 0 | May | 2023 | 0.01418 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-29 02:54 | 2023-05-29 12:21 | 155 | 9:27 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23052900001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 567 | 2023-05-29 | 87885 | keep | 0 | May | 2023 | 0.059858 | 0.00010557 | Sustained | FALSE | FALSE | Not_TMED_Event | 155
CAGUAS | 2023-05-29 03:22 | 2023-05-29 03:23 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23052900003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
FAJARDO | 2023-05-29 04:26 | 2023-05-29 05:45 | 710 | 1:19 | T | OTRAS CAUSAS | SE RETIRO LA CARGA PARA COMPLETAR EL NIVEL DE ACEITE DEL MAIN XMR | R23052900002 | New_Event | Other Causes | Include | Include | Other | 79 | 2023-05-29 | 56090 | keep | 0 | May | 2023 | 0.038203 | 0.00048358 | Sustained | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-05-29 04:26 | 2023-05-29 05:45 | 1197 | 1:19 | T | OTRAS CAUSAS | SE RETIRO LA CARGA PARA COMPLETAR EL NIVEL DE ACEITE DEL MAIN XMR | R23052900003 | New_Event | Other Causes | Include | Include | Other | 79 | 2023-05-29 | 94563 | keep | 0 | May | 2023 | 0.064406 | 0.00081527 | Sustained | FALSE | FALSE | Not_TMED_Event | 1197
BAYAMON | 2023-05-29 05:16 | 2023-05-29 05:17 | 1159 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 17% DE SU CARGA POR 9202-02 | B23052900012 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 1159 | keep | 0 | May | 2023 | 0.00078939 | 0.00078939 | Momentary | FALSE | FALSE | Not_TMED_Event | 1159
HUMACAO | 2023-05-29 05:36 | 2023-05-29 08:45 | 200 | 3:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN C/L MAL TIEMPO LLUVIAS | C23052900007 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 189 | 2023-05-29 | 37800 | keep | 0 | May | 2023 | 0.025745 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BARRANQUITAS | 2023-05-29 05:37 | 2023-05-29 10:09 | 1617 | 4:32 | T | CAUSAS EXTERNAS | DISPARO DE BKR SE SECCIONALIZO TRAMO Y SE CERRO POR CONTROL 90% EN SERVICIO | P23052900024 | New_Event | Damage From Public | Include | Include | Public | 272 | 2023-05-29 | 439824 | keep | 0 | May | 2023 | 0.29956 | 0.0011013 | Sustained | FALSE | FALSE | Not_TMED_Event | 1617
SAN JUAN | 2023-05-29 06:02 | 2023-05-29 09:42 | 76 | 3:40 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23052900006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-05-29 | 16720 | keep | 0 | May | 2023 | 0.011388 | 5.1763e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 76
GUAYAMA | 2023-05-29 06:26 | 2023-05-30 06:25 | 25 | 23:59 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA POR DESCARGA ELECTRICA | P23052900341 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1439 | 2023-05-29 | 35975 | keep | 0 | May | 2023 | 0.024502 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
HUMACAO | 2023-05-29 06:34 | 2023-05-29 11:23 | 124 | 4:49 | P | CONDUCTOR ROTO O ABIERTO | 2 X 80 EN C/L SE FIJO CONDUCTOR EN AISLADOR | C23052900016 | New_Event | Primary Wire Break | Include | Include | Equipment | 289 | 2023-05-29 | 35836 | keep | 0 | May | 2023 | 0.024408 | 8.4456e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 124
CAGUAS | 2023-05-29 06:35 | 2023-05-29 13:39 | 44 | 7:04 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | C23052900017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 424 | 2023-05-29 | 18656 | keep | 0 | May | 2023 | 0.012707 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
BAYAMON | 2023-05-29 06:41 | 2023-05-29 15:58 | 40 | 9:17 | P | CABLE SOTERRADO AVERIADO | 1 X 30 EN PROVISIONAL AN DEL T203 @ T202 AV DEL T201 @ T202 | B23052900017 | New_Event | UG Cable Fault | Include | Include | Equipment | 557 | 2023-05-29 | 22280 | keep | 0 | May | 2023 | 0.015175 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
AGUADILLA | 2023-05-29 06:50 | 2023-05-29 08:40 | 80 | 1:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO PORTAFUSIBLES AVERIADO | A23052900005 | New_Event | Cutout Failure | Include | Include | Equipment | 110 | 2023-05-29 | 8800 | keep | 0 | May | 2023 | 0.0059936 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-05-29 06:56 | 2023-05-29 09:04 | 43 | 2:08 | P | ANIMAL | 1 X 200 Y SE REMPLAZO AISLADOR CRUCE POR AVE | R23052900008 | New_Event | Animals | Include | Include | Wildlife | 128 | 2023-05-29 | 5504 | keep | 0 | May | 2023 | 0.0037487 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
HUMACAO | 2023-05-29 07:00 | 2023-05-29 11:13 | 4 | 4:13 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE SECUNDARIO | C23052900030 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 253 | 2023-05-29 | 1012 | keep | 0 | May | 2023 | 0.00068927 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-05-29 07:30 | 2023-05-29 13:25 | 1 | 5:55 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23052900026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2023-05-29 | 355 | keep | 0 | May | 2023 | 0.00024179 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-29 07:44 | 2023-05-29 07:46 | 3046 | 0:02 | T | NO SE REPORTO CAUSA | LLEVA 1647-10 LLEVA 15% 1647-09 | R23052900026 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-29 | 6092 | keep | 0 | May | 2023 | 0.0041492 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-05-29 07:44 | 2023-05-29 07:46 | 308 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DEL 1646-03 CERRADO POR CONTROL 15% X 1646-03 | R23052900026 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-29 | 616 | keep | 0 | May | 2023 | 0.00041955 | 0.00020978 | Momentary | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-05-29 07:44 | 2023-05-29 07:46 | 61 | 0:02 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1646-03 CERRADO POR CONTROL CARGA X 1646-03 | R23052900026 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-29 | 122 | keep | 0 | May | 2023 | 8.3094e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
MAYAGÃœEZ | 2023-05-29 07:45 | 2023-05-29 14:38 | 20 | 6:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 Y 1 X 30 EN CORTE DE LINEA POR LLUVIA | M23052900028 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 413 | 2023-05-29 | 8260 | keep | 0 | May | 2023 | 0.0056258 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-29 07:50 | 2023-05-29 11:55 | 80 | 4:05 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO PUENTE PRIMARIO ABIERTO | A23052900015 | New_Event | Primary Wire Break | Include | Include | Equipment | 245 | 2023-05-29 | 19600 | keep | 0 | May | 2023 | 0.013349 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
HUMACAO | 2023-05-29 08:00 | 2023-05-29 14:42 | 1 | 6:42 | P | ANIMAL | 1 X 25 EN RISER CRUCE X AVE | C23052900127 | New_Event | Animals | Include | Include | Wildlife | 402 | 2023-05-29 | 402 | keep | 0 | May | 2023 | 0.0002738 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-29 08:05 | 2023-05-29 17:33 | 6 | 9:28 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | C23052900033 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 568 | 2023-05-29 | 3408 | keep | 0 | May | 2023 | 0.0023212 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-29 08:08 | 2023-05-29 08:09 | 2366 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23052900018 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 2366 | keep | 0 | May | 2023 | 0.0016115 | 0.0016115 | Momentary | FALSE | FALSE | Not_TMED_Event | 2366
AGUADILLA | 2023-05-29 08:09 | 2023-05-29 14:36 | 3522 | 6:27 | S | LINEA DE TRANSMISION 38KV | LINEA 2400 AVERIADA PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | M23052900052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 387 | 2023-05-29 | 1363014 | keep | 0 | May | 2023 | 0.92834 | 0.0023988 | Sustained | FALSE | FALSE | Not_TMED_Event | 3522
AGUADILLA | 2023-05-29 08:09 | 2023-05-29 14:36 | 1337 | 6:27 | S | LINEA DE TRANSMISION 38KV | LINEA 2400 AVERIADA PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | M23052900052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 387 | 2023-05-29 | 517419 | keep | 0 | May | 2023 | 0.35241 | 0.00091062 | Sustained | FALSE | FALSE | Not_TMED_Event | 1337
AGUADILLA | 2023-05-29 08:09 | 2023-05-29 14:36 | 2825 | 6:27 | S | LINEA DE TRANSMISION 38KV | LINEA 2400 AVERIADA PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | M23052900052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 387 | 2023-05-29 | 1093275 | keep | 0 | May | 2023 | 0.74462 | 0.0019241 | Sustained | FALSE | FALSE | Not_TMED_Event | 2825
AGUADILLA | 2023-05-29 08:09 | 2023-05-29 14:36 | 1287 | 6:27 | S | LINEA DE TRANSMISION 38KV | LINEA 1900 AVERIADA PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | M23052900052 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 387 | 2023-05-29 | 498069 | keep | 0 | May | 2023 | 0.33923 | 0.00087657 | Sustained | FALSE | FALSE | Not_TMED_Event | 1287
AGUADILLA | 2023-05-29 08:09 | 2023-05-29 14:36 | 1417 | 6:27 | S | LINEA DE TRANSMISION 38KV | LINEA 2400 AVERIADA PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | M23052900053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 387 | 2023-05-29 | 548379 | keep | 0 | May | 2023 | 0.3735 | 0.00096511 | Sustained | FALSE | FALSE | Not_TMED_Event | 1417
AGUADILLA | 2023-05-29 08:09 | 2023-05-29 14:36 | 80 | 6:27 | S | LINEA DE TRANSMISION 38KV | LINEA 2400 AVERIADA PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | M23052900053 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 387 | 2023-05-29 | 30960 | keep | 0 | May | 2023 | 0.021087 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 1405 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 400425 | keep | 0 | May | 2023 | 0.27273 | 0.00095694 | Sustained | FALSE | FALSE | Not_TMED_Event | 1405
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 669 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 190665 | keep | 0 | May | 2023 | 0.12986 | 0.00045565 | Sustained | FALSE | FALSE | Not_TMED_Event | 669
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 1527 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 435195 | keep | 0 | May | 2023 | 0.29641 | 0.00104 | Sustained | FALSE | FALSE | Not_TMED_Event | 1527
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 1054 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 300390 | keep | 0 | May | 2023 | 0.20459 | 0.00071787 | Sustained | FALSE | FALSE | Not_TMED_Event | 1054
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 932 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900073 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 265620 | keep | 0 | May | 2023 | 0.18091 | 0.00063478 | Sustained | FALSE | FALSE | Not_TMED_Event | 932
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 1633 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 465405 | keep | 0 | May | 2023 | 0.31699 | 0.0011122 | Sustained | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 1624 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900074 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 462840 | keep | 0 | May | 2023 | 0.31524 | 0.0011061 | Sustained | FALSE | FALSE | Not_TMED_Event | 1624
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 705 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 200925 | keep | 0 | May | 2023 | 0.13685 | 0.00048017 | Sustained | FALSE | FALSE | Not_TMED_Event | 705
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 1521 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 433485 | keep | 0 | May | 2023 | 0.29524 | 0.0010359 | Sustained | FALSE | FALSE | Not_TMED_Event | 1521
UTUADO | 2023-05-29 08:09 | 2023-05-29 12:54 | 882 | 4:45 | S | LINEA DE TRANSMISION 38KV | SE REPARO AVERIA EN LA LINEA 2400 Y SE ENERGIZO LA SUBESTACION PUENTE ABIERTO ACB 2409A - ACB 2425, TENIA ENLAZADA TODA LA CARGA DE LA LINEA 1900 | A23052900075 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 285 | 2023-05-29 | 251370 | keep | 0 | May | 2023 | 0.17121 | 0.00060073 | Sustained | FALSE | FALSE | Not_TMED_Event | 882
SAN JUAN | 2023-05-29 08:10 | 2023-05-29 16:08 | 20 | 7:58 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO BAJANTE SECUNDARIO | S23052900030 | New_Event | Secondary Wire Break | Include | Include | Equipment | 478 | 2023-05-29 | 9560 | keep | 0 | May | 2023 | 0.0065113 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-29 08:50 | 2023-05-29 08:56 | 1541 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23052900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-29 | 9246 | keep | 0 | May | 2023 | 0.0062974 | 0.0010496 | Sustained | FALSE | FALSE | Not_TMED_Event | 1541
AGUADILLA | 2023-05-29 08:50 | 2023-05-29 08:56 | 307 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23052900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-29 | 1842 | keep | 0 | May | 2023 | 0.0012546 | 0.0002091 | Sustained | FALSE | FALSE | Not_TMED_Event | 307
AGUADILLA | 2023-05-29 08:50 | 2023-05-29 08:56 | 1277 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23052900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-29 | 7662 | keep | 0 | May | 2023 | 0.0052186 | 0.00086976 | Sustained | FALSE | FALSE | Not_TMED_Event | 1277
AGUADILLA | 2023-05-29 08:50 | 2023-05-29 08:56 | 1644 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23052900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-29 | 9864 | keep | 0 | May | 2023 | 0.0067183 | 0.0011197 | Sustained | FALSE | FALSE | Not_TMED_Event | 1644
AGUADILLA | 2023-05-29 08:50 | 2023-05-29 08:56 | 1831 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23052900113 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-29 | 10986 | keep | 0 | May | 2023 | 0.0074825 | 0.0012471 | Sustained | FALSE | FALSE | Not_TMED_Event | 1831
AGUADILLA | 2023-05-29 08:50 | 2023-05-29 08:56 | 1483 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23052900114 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-29 | 8898 | keep | 0 | May | 2023 | 0.0060604 | 0.0010101 | Sustained | FALSE | FALSE | Not_TMED_Event | 1483
AGUADILLA | 2023-05-29 08:50 | 2023-05-29 08:56 | 89 | 0:06 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23052900114 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 6 | 2023-05-29 | 534 | keep | 0 | May | 2023 | 0.0003637 | 6.0617e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 89
CAGUAS | 2023-05-29 08:51 | 2023-05-29 08:52 | 918 | 0:01 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | RECIERRE DE INTERRUPTOR | C2305290000X | New_Event | Cutout Failure | Include | Include | Equipment | 1 | 2023-05-29 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-29 08:52 | 2023-05-29 14:37 | 150 | 5:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y 1 X65 EN C/L SE REEMPLAZO DE CAJA PRIMARIA Y DESGANCHE | C23052900093 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 345 | 2023-05-29 | 51750 | keep | 0 | May | 2023 | 0.035247 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-05-29 08:52 | 2023-05-29 12:00 | 30 | 3:08 | P | ANIMAL | 2 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | M23052900059 | New_Event | Animals | Include | Include | Wildlife | 188 | 2023-05-29 | 5640 | keep | 0 | May | 2023 | 0.0038414 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
GUAYAMA | 2023-05-29 08:59 | 2023-05-29 10:34 | 1 | 1:35 | P | PROBLEMA DEL CLIENTE | SE CERRO RISER PROBLEMA INTERNO | P23052900096 | New_Event | Customer-Related Interruption | Include | Include | Public | 95 | 2023-05-29 | 95 | keep | 0 | May | 2023 | 6.4704e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
YAUCO | 2023-05-29 09:05 | 2023-05-29 09:07 | 1475 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23052900102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-29 | 2950 | keep | 0 | May | 2023 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
VEGA BAJA | 2023-05-29 09:18 | 2023-05-29 12:25 | 30 | 3:07 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO FASE A TIERRA | A23052900108 | New_Event | Animals | Include | Include | Wildlife | 187 | 2023-05-29 | 5610 | keep | 0 | May | 2023 | 0.0038209 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-29 09:22 | 2023-05-29 13:56 | 30 | 4:34 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BUSHIN SECUNDARIO | S23052900044 | New_Event | Secondary Wire Break | Include | Include | Equipment | 274 | 2023-05-29 | 8220 | keep | 0 | May | 2023 | 0.0055986 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
YAUCO | 2023-05-29 09:39 | 2023-05-29 11:52 | 5 | 2:13 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR DESGANCHE SECUNDARIO | P23052900115 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 133 | 2023-05-29 | 665 | keep | 0 | May | 2023 | 0.00045293 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
FAJARDO | 2023-05-29 09:49 | 2023-05-29 10:13 | 1 | 0:24 | P | ANIMAL | 1 X50 CRUCE POR AVE | R23052900060 | New_Event | Animals | Include | Include | Wildlife | 24 | 2023-05-29 | 24 | keep | 0 | May | 2023 | 1.6346e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-29 09:53 | 2023-05-29 09:54 | 27 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE LLEVA 1602-05 | R2305290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 27 | keep | 0 | May | 2023 | 1.839e-05 | 1.839e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 27
CANOVANAS | 2023-05-29 09:53 | 2023-05-29 09:54 | 188 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 1602-02 LLEVA 1602-05 | R2305290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-29 | 188 | keep | 0 | May | 2023 | 0.00012805 | 0.00012805 | Momentary | FALSE | FALSE | Not_TMED_Event | 188
CANOVANAS | 2023-05-29 09:53 | 2023-05-29 09:54 | 1026 | 0:01 | T | PROBLEMA DEL CLIENTE | RECIERRE | R2305290000X | New_Event | Customer-Related Interruption | Include | Include | Public | 1 | 2023-05-29 | 1026 | keep | 0 | May | 2023 | 0.0006988 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
BAYAMON | 2023-05-29 09:53 | 2023-05-29 10:18 | 45 | 0:25 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23052900025 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2023-05-29 | 1125 | keep | 0 | May | 2023 | 0.00076623 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
CANOVANAS | 2023-05-29 09:54 | 2023-05-29 13:20 | 14 | 3:26 | P | PROBLEMA DEL CLIENTE | 2 X 100 EN C/L SE DEJO FUERA A GENERAL ELECTRIC POR PROBLEMAS INTERNOS EN TRANSCLOSURE | R23052900068 | 1st_after_momentary | Customer-Related Interruption | Include | Include | Public | 206 | 2023-05-29 | 2884 | keep | 0 | May | 2023 | 0.0019643 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
BARRANQUITAS | 2023-05-29 10:09 | 2023-05-29 16:10 | 162 | 6:01 | P | CAUSAS EXTERNAS | SE REEMPLAZO POSTE PARTIDO A CAUSA DE IMPACTO DE VEHICULO. 100% EN SERVICIO. EVENTO TRANSFERIDO DE PONCE. OMS NO CREO EVENTO DE FEEDER. | P23052900024 | New_Event | Damage From Public | Include | Include | Public | 361 | 2023-05-29 | 58482 | keep | 0 | May | 2023 | 0.039832 | 0.00011034 | Sustained | FALSE | FALSE | Not_TMED_Event | 162
AGUADILLA | 2023-05-29 10:19 | 2023-05-29 19:47 | 1 | 9:28 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23052900126 | New_Event | Vegetation Contact | Include | Include | Vegetation | 568 | 2023-05-29 | 568 | keep | 0 | May | 2023 | 0.00038686 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-29 10:19 | 2023-05-29 15:25 | 2 | 5:06 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO CAJA PRIMARIA AVERIADA EN TRANSFORMADOR Y SE REPARO BAJANTE PRIMARIO EN TRANSFORMADOR | A23052900127 | New_Event | Primary Wire Break | Include | Include | Equipment | 306 | 2023-05-29 | 612 | keep | 0 | May | 2023 | 0.00041683 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
HUMACAO | 2023-05-29 10:37 | 2023-05-29 15:35 | 15 | 4:58 | P | DESGANCHE | 1 X 25 EN C/L DESGANCHE. EVENTO TRANSFERIDO DE PONCE. | P23052900153 | New_Event | Vegetation Contact | Include | Include | Vegetation | 298 | 2023-05-29 | 4470 | keep | 0 | May | 2023 | 0.0030445 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-29 10:37 | 2023-05-29 13:53 | 3 | 3:16 | P | NO SE REPORTO CAUSA | 1 X 30 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | A23052900130 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 196 | 2023-05-29 | 588 | keep | 0 | May | 2023 | 0.00040048 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-05-29 10:40 | 2023-05-29 14:30 | 5 | 3:50 | P | SECUNDARIA/OTROS | ABRIR CAJAS DE TRANSFORMADOR PARA REPARAR PEDESTAL SECUNDARIO | M23052900081 | New_Event |  |  |  |  | 230 | 2023-05-29 | 1150 | keep | 0 | May | 2023 | 0.00078326 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
SAN JUAN | 2023-05-29 10:46 | 2023-05-29 15:14 | 145 | 4:28 | P | DESGANCHE | DESGANCHE 1 X 100 EN C/L | S23052900060 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-05-29 | 38860 | keep | 0 | May | 2023 | 0.026467 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
YAUCO | 2023-05-29 10:57 | 2023-05-29 14:05 | 6 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO SE ENCONTRO CAUSA VERIFICADO EN BITACORA EVENTO DE YAUCO -PONCE | P23052900166 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-05-29 | 1128 | keep | 0 | May | 2023 | 0.00076828 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
HUMACAO | 2023-05-29 11:07 | 2023-05-29 11:08 | 2450 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 12600 | C23052900100 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-29 | 2450 | keep | 0 | May | 2023 | 0.0016687 | 0.0016687 | Momentary | FALSE | FALSE | Not_TMED_Event | 2450
HUMACAO | 2023-05-29 11:07 | 2023-05-29 11:08 | 640 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LINEA 12600 | C23052900100 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-29 | 640 | keep | 0 | May | 2023 | 0.0004359 | 0.0004359 | Momentary | FALSE | FALSE | Not_TMED_Event | 640
SAN JUAN | 2023-05-29 11:09 | 2023-05-29 17:27 | 10 | 6:18 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | S23052900065 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 378 | 2023-05-29 | 3780 | keep | 0 | May | 2023 | 0.0025745 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
VEGA BAJA | 2023-05-29 11:27 | 2023-05-29 16:20 | 50 | 4:53 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 40 EN CORTE DE LINEA SE REMPLAZO AISLADOR ROTO | A23052900136 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 293 | 2023-05-29 | 14650 | keep | 0 | May | 2023 | 0.009978 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-29 11:35 | 2023-05-29 15:10 | 6 | 3:35 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | B23052900068 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 215 | 2023-05-29 | 1290 | keep | 0 | May | 2023 | 0.00087861 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-05-29 11:54 | 2023-05-29 12:07 | 24 | 0:13 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23052900039 | New_Event | Animals | Include | Include | Wildlife | 13 | 2023-05-29 | 312 | keep | 0 | May | 2023 | 0.0002125 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
BARRANQUITAS | 2023-05-29 11:54 | 2023-05-29 13:40 | 1017 | 1:46 | T | DESGANCHE | DISPARO DE BKR, SE SECCIONALIZO TRAMO Y SE CERRO POR CONTROL 80% EN SERVICIO | C23052900107 | New_Event | Vegetation Contact | Include | Include | Vegetation | 106 | 2023-05-29 | 107802 | keep | 0 | May | 2023 | 0.073423 | 0.00069267 | Sustained | FALSE | FALSE | Not_TMED_Event | 1017
MAYAGÃœEZ | 2023-05-29 11:57 | 2023-05-29 14:20 | 200 | 2:23 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PRIMARIA PARTIDA Y SE CIERRAN MACHETES | M23052800165 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 143 | 2023-05-29 | 28600 | keep | 0 | May | 2023 | 0.019479 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-29 11:59 | 2023-05-29 15:15 | 50 | 3:16 | P | ARBOL SOBRE LINEA | SE ABRIO C/L TOTAL PARA RETIRAR ARBOL SOBRE LA LINEA | B23052900057 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 196 | 2023-05-29 | 9800 | keep | 0 | May | 2023 | 0.0066747 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
VEGA BAJA | 2023-05-29 11:59 | 2023-05-29 12:12 | 10 | 0:13 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR | B23052900074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 13 | 2023-05-29 | 130 | keep | 0 | May | 2023 | 8.8542e-05 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-05-29 12:25 | 2023-05-29 14:42 | 1 | 2:17 | P | ARBOL SOBRE LINEA | 1 X 40 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LINEA VERIFICADO EN BITACORA EVENTO YAUCO- PONCE | P23052900224 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 137 | 2023-05-29 | 137 | keep | 0 | May | 2023 | 9.331e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
ARECIBO | 2023-05-29 12:27 | 2023-05-30 10:15 | 50 | 21:48 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTES PRIMARIOS | A23052900149 | New_Event | Primary Wire Break | Include | Include | Equipment | 1308 | 2023-05-29 | 65400 | keep | 0 | May | 2023 | 0.044544 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-29 12:37 | 2023-05-29 16:15 | 25 | 3:38 | P | AISLADOR ROTO, PARTIDO O SAFADO | REMPLAZAR AISLADOR ROTO EN SALIDA DE LAS SUBESTACION | M23052900137 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 218 | 2023-05-29 | 5450 | keep | 0 | May | 2023 | 0.003712 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-05-29 12:48 | 2023-05-29 12:49 | 1843 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23052900114 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 1843 | keep | 0 | May | 2023 | 0.0012553 | 0.0012553 | Momentary | FALSE | FALSE | Not_TMED_Event | 1843
BAYAMON | 2023-05-29 12:51 | 2023-05-29 15:59 | 40 | 3:08 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | B23052900080 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 188 | 2023-05-29 | 7520 | keep | 0 | May | 2023 | 0.0051218 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
MAYAGÃœEZ | 2023-05-29 12:53 | 2023-05-29 16:45 | 150 | 3:52 | P | NO SE REPORTO CAUSA | 1 X 100 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23052900129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 232 | 2023-05-29 | 34800 | keep | 0 | May | 2023 | 0.023702 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-05-29 13:04 | 2023-05-29 18:06 | 70 | 5:02 | P | DESGANCHE | 1 X 100 EN CONVERTIDOR DESGANCHE | S23052900083 | New_Event | Vegetation Contact | Include | Include | Vegetation | 302 | 2023-05-29 | 21140 | keep | 0 | May | 2023 | 0.014398 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-05-29 13:20 | 2023-05-29 13:24 | 1026 | 0:04 | T | PROBLEMA DEL CLIENTE | DISPARO CERRDADO POR CONTROL | R2305290000X | New_Event | Customer-Related Interruption | Include | Include | Public | 4 | 2023-05-29 | 4104 | keep | 0 | May | 2023 | 0.0027952 | 0.0006988 | Momentary | FALSE | FALSE | Not_TMED_Event | 1026
AGUADILLA | 2023-05-29 13:20 | 2023-05-29 14:00 | 3 | 0:40 | P | PARARRAYOS DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REMPLAZR PARARRAYOS | M23052900133 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 40 | 2023-05-29 | 120 | keep | 0 | May | 2023 | 8.1731e-05 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
VEGA BAJA | 2023-05-29 13:23 | 2023-05-29 15:15 | 13 | 1:52 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR CULEBRA | B23052900085 | New_Event | Animals | Include | Include | Wildlife | 112 | 2023-05-29 | 1456 | keep | 0 | May | 2023 | 0.00099167 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
CANOVANAS | 2023-05-29 13:24 | 2023-05-29 14:29 | 14 | 1:05 | P | PROBLEMA DEL CLIENTE | 2 X 100 EN C/L SE DEJO FUERA A GENERAL ELECTRIC POR PROBLEMAS INTERNOS EN TRANSCLOSURE | R23052900068 | 1st_after_momentary | Customer-Related Interruption | Include | Include | Public | 65 | 2023-05-29 | 910 | keep | 0 | May | 2023 | 0.0006198 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
ARECIBO | 2023-05-29 13:33 | 2023-05-29 13:34 | 2703 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23052900149 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 2703 | keep | 0 | May | 2023 | 0.001841 | 0.001841 | Momentary | FALSE | FALSE | Not_TMED_Event | 2703
AGUADILLA | 2023-05-29 13:34 | 2023-05-29 13:35 | 1617 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | M23052900141 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 1617 | keep | 0 | May | 2023 | 0.0011013 | 0.0011013 | Momentary | FALSE | FALSE | Not_TMED_Event | 1617
UTUADO | 2023-05-29 13:39 | 2023-05-29 15:00 | 20 | 1:21 | P | ARBOL SOBRE LINEA | 1 X 50 EN CORTE DE LINEA SE RETIRO ARBOL DE LAS LINEAS | A23052900151 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 81 | 2023-05-29 | 1620 | keep | 0 | May | 2023 | 0.0011034 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BARRANQUITAS | 2023-05-29 13:40 | 2023-05-29 18:05 | 203 | 4:25 | P | DESGANCHE | SE RETIRO RAMA QUE CAYO SOBRE LA LINEA Y SE CERRARON 2 PUENTES ABIERTOS EN EL TRONCAL. 100% EN SERVICIO | C23052900107 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 265 | 2023-05-29 | 53795 | keep | 0 | May | 2023 | 0.03664 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-05-29 13:54 | 2023-05-29 17:22 | 50 | 3:28 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA POR 1 X 20 EN TRANSFORMADOR POR ANIMAL | P23052900256 | New_Event | Animals | Include | Include | Wildlife | 208 | 2023-05-29 | 10400 | keep | 0 | May | 2023 | 0.0070834 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
HUMACAO | 2023-05-29 13:55 | 2023-05-29 13:56 | 4830 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR LLEVA 4830 CLIENTES | C2305290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 4830 | keep | 0 | May | 2023 | 0.0032897 | 0.0032897 | Momentary | FALSE | FALSE | Not_TMED_Event | 4830
SAN JUAN | 2023-05-29 13:58 | 2023-05-29 18:02 | 145 | 4:04 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REEMPLAZO PORTA FUSIBLE | S23052900091 | New_Event | Cutout Failure | Include | Include | Equipment | 244 | 2023-05-29 | 35380 | keep | 0 | May | 2023 | 0.024097 | 9.8759e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 145
BAYAMON | 2023-05-29 14:14 | 2023-05-29 15:31 | 8 | 1:17 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA @ XMR | B23052900093 | New_Event | Primary Wire Break | Include | Include | Equipment | 77 | 2023-05-29 | 616 | keep | 0 | May | 2023 | 0.00041955 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-29 14:37 | 2023-05-29 14:38 | 250 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1401-08 LLEVA EL 1348-08. LLEVA 20% DEL 1348-06 | S2305290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-29 | 250 | keep | 0 | May | 2023 | 0.00017027 | 0.00017027 | Momentary | FALSE | FALSE | Not_TMED_Event | 250
SAN JUAN | 2023-05-29 14:37 | 2023-05-29 14:38 | 1290 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 1401-08 LLEVA EL 1348-08. LLEVA 20% DEL 1348-06 | S2305290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-29 | 1290 | keep | 0 | May | 2023 | 0.00087861 | 0.00087861 | Momentary | FALSE | FALSE | Not_TMED_Event | 1290
SAN JUAN | 2023-05-29 14:37 | 2023-05-29 14:38 | 74 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO DE BKR SOLO LLEVA EL 55% DE SU CARGA LLEVA EL 1348-08. LLEVA 20% DEL 1348-06 | S2305290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 74 | keep | 0 | May | 2023 | 5.0401e-05 | 5.0401e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 74
UTUADO | 2023-05-29 14:46 | 2023-05-29 20:53 | 30 | 6:07 | P | MAL TIEMPO/RAYOS | 1 X 25 EN CONVERTIDOR DESCARGAS ELECTRICAS | A23052900160 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 367 | 2023-05-29 | 11010 | keep | 0 | May | 2023 | 0.0074989 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
SAN JUAN | 2023-05-29 14:56 | 2023-05-29 15:10 | 1 | 0:14 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23052900102 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 14 | 2023-05-29 | 14 | keep | 0 | May | 2023 | 9.5353e-06 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-29 15:07 | 2023-05-29 16:17 | 12 | 1:10 | P | PROBLEMA DEL CLIENTE | 2 X 50 EN C/L SE DEJO RISER FUERA DE FABRICA ROWLAND IMPORTS AVERIA INTERNA | R23052900074 | New_Event | Customer-Related Interruption | Include | Include | Public | 70 | 2023-05-29 | 840 | keep | 0 | May | 2023 | 0.00057212 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-29 15:07 | 2023-05-29 16:52 | 200 | 1:45 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 100 EN C/L SE ELIMINO PIN POLE TOP | B23052900097 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 105 | 2023-05-29 | 21000 | keep | 0 | May | 2023 | 0.014303 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-05-29 15:08 | 2023-05-29 16:37 | 25 | 1:29 | P | DESGANCHE | 2 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M23052900151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-05-29 | 2225 | keep | 0 | May | 2023 | 0.0015154 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-05-29 15:09 | 2023-05-29 16:37 | 50 | 1:28 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CL SE REPARO BAJANTE PRIMARIO | P23052900276 | New_Event | Primary Wire Break | Include | Include | Equipment | 88 | 2023-05-29 | 4400 | keep | 0 | May | 2023 | 0.0029968 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-29 15:26 | 2023-05-29 15:29 | 573 | 0:03 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR CONTROL | B2305290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 3 | 2023-05-29 | 1719 | keep | 0 | May | 2023 | 0.0011708 | 0.00039027 | Momentary | FALSE | FALSE | Not_TMED_Event | 573
FAJARDO | 2023-05-29 15:33 | 2023-05-29 19:05 | 52 | 3:32 | P | DESGANCHE | 1 X 20 EN C/L Y 1 X 25 EN C/L DESGANCHE DE BAMBUAS | R23052900069 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2023-05-29 | 11024 | keep | 0 | May | 2023 | 0.0075084 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
MAYAGÃœEZ | 2023-05-29 15:49 | 2023-05-29 17:42 | 20 | 1:53 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA POR AVE | M23052900160 | New_Event | Animals | Include | Include | Wildlife | 113 | 2023-05-29 | 2260 | keep | 0 | May | 2023 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-29 15:52 | 2023-05-29 18:04 | 50 | 2:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEAS POR LLUVIAS | M23052900161 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 132 | 2023-05-29 | 6600 | keep | 0 | May | 2023 | 0.0044952 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-05-29 16:01 | 2023-05-30 14:13 | 1 | 22:12 | P | DESGANCHE | 2 X 65 EN C/L DESGANCHE | S23052900108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1332 | 2023-05-29 | 1332 | keep | 0 | May | 2023 | 0.00090722 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-29 16:02 | 2023-05-29 16:54 | 70 | 0:52 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23052900073 | New_Event | Animals | Include | Include | Wildlife | 52 | 2023-05-29 | 3640 | keep | 0 | May | 2023 | 0.0024792 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
GUAYAMA | 2023-05-29 16:09 | 2023-05-29 18:05 | 6 | 1:56 | P | ARBOL SOBRE LINEA | ARBOL SOBRE LINEA 1 X 40 EN CORTE DE LINEA | P23052900284 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 116 | 2023-05-29 | 696 | keep | 0 | May | 2023 | 0.00047404 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-05-29 16:17 | 2023-05-29 17:01 | 3046 | 0:44 | T | PROBLEMA DEL CLIENTE | SJ-230529-50 DISPARO DE BKR PERONAL REALIZANDO PRUEBAS EN EVENTO R23052900074. LLEVA EL 1647-10 Y UN 15% DEL 1647-09. ENTRO UN 72% DEL 1646-03. UN 100% DEL 1647-10 Y EL 15% DEL 1646-09 | R23052900076 | Additional_clients | Customer-Related Interruption | Include | Include | Public | 44 | 2023-05-29 | 134024 | keep | 0 | May | 2023 | 0.091283 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-29 16:17 | 2023-05-29 17:01 | 308 | 0:44 | P | ALIMENTADOR AMARRADO | SJ-230529-50 DISPARO DE BKR 1646-03 PERONAL REALIZANDO PRUEBAS EN EVENTO R23052900074. LLEVA EL 1647-10 Y UN 15% DEL 1647-09 | R23052900076 | New_Event | Feeder Load Transferred | Include | Include | Other | 44 | 2023-05-29 | 13552 | keep | 0 | May | 2023 | 0.0092302 | 0.00020978 | Sustained | FALSE | FALSE | Not_TMED_Event | 308
CANOVANAS | 2023-05-29 16:17 | 2023-05-29 17:01 | 61 | 0:44 | T | ALIMENTADOR AMARRADO | SJ-230529-50 DISPARO DE BKR 1646-03 PERONAL REALIZANDO PRUEBAS EN EVENTO R23052900074. LLEVA EL 1647-10 Y UN 15% DEL 1647-09 | R23052900076 | New_Event | Feeder Load Transferred | Include | Include | Other | 44 | 2023-05-29 | 2684 | keep | 0 | May | 2023 | 0.0018281 | 4.1547e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 61
PONCE | 2023-05-29 16:18 | 2023-05-30 19:19 | 10 | 27:01 | P | TRANSFORMADOR AVERIADO | SE HIZO CAMBIO DE TRANSFORMADOR AVERIADO DE 15 KVA-4KV POR UNO DE 25KVA-4KV | P23052900287 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1621 | 2023-05-29 | 16210 | keep | 0 | May | 2023 | 0.011041 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-29 16:32 | 2023-05-31 12:50 | 1 | 44:18 | P | TRANSFORMADOR AVERIADO | SE REMPPLAZO XMR DE 37.5 POR 37.50 KVA EVENTO TRANSFERIDO | P23052900293 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2658 | 2023-05-29 | 2658 | keep | 0 | May | 2023 | 0.0018104 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-29 16:58 | 2023-05-29 18:35 | 60 | 1:37 | P | ANIMAL | 1 X 100 EN CONVERTIDOR AVE CRUZO FASE A TIERRA | A23052900174 | New_Event | Animals | Include | Include | Wildlife | 97 | 2023-05-29 | 5820 | keep | 0 | May | 2023 | 0.003964 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-29 17:01 | 2023-05-29 17:17 | 837 | 0:16 | P | PROBLEMA DEL CLIENTE | SJ-230529-50 DISPARO DE BKR SE HICIERON OPERACIONES. ENTRO EL 28% QUE FALTABA | R23052900076 | Partial_restoration | Customer-Related Interruption | Include | Include | Public | 16 | 2023-05-29 | 13392 | keep | 0 | May | 2023 | 0.0091212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-05-29 17:02 | 2023-05-29 22:00 | 25 | 4:58 | P | MAL TIEMPO/RAYOS | 1 X 50 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052900177 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 298 | 2023-05-29 | 7450 | keep | 0 | May | 2023 | 0.0050742 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-05-29 17:17 | 2023-05-29 17:34 | 309 | 0:17 | P | PROTECCION DEFECTUOSA | 1 SMU 20 DE 40 AMP. FUSIBLE ESTABA DE 30 AMP. AL REMONTAR LA CARGA FUNDIO SE CORDINO CON LOS DEMAS FUSIBLES | R23052900076 | New_Event | Protection Miscoordination | Include | Include | Other | 17 | 2023-05-29 | 5253 | keep | 0 | May | 2023 | 0.0035778 | 0.00021046 | Sustained | FALSE | FALSE | Not_TMED_Event | 309
CAGUAS | 2023-05-29 17:19 | 2023-05-29 19:39 | 171 | 2:20 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | C23052900160 | New_Event | Vegetation Contact | Include | Include | Vegetation | 140 | 2023-05-29 | 23940 | keep | 0 | May | 2023 | 0.016305 | 0.00011647 | Sustained | FALSE | FALSE | Not_TMED_Event | 171
CANOVANAS | 2023-05-29 17:38 | 2023-05-30 09:28 | 1 | 15:50 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE XMR 1 X 25 EN C/L. EVENTO TRANSFERIDO DE PONCE. | P23052900314 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 950 | 2023-05-29 | 950 | keep | 0 | May | 2023 | 0.00064704 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-29 17:51 | 2023-05-30 03:07 | 1 | 9:16 | P | DESGANCHE | DESGANCHE 1 X 25 EN CORTE DE LINEA | P23052900317 | New_Event | Vegetation Contact | Include | Include | Vegetation | 556 | 2023-05-29 | 556 | keep | 0 | May | 2023 | 0.00037869 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-29 18:08 | 2023-05-30 07:19 | 1 | 13:11 | P | DESGANCHE | 1 X 20 EN RISER Y DESGANCHE | B23052900123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 791 | 2023-05-29 | 791 | keep | 0 | May | 2023 | 0.00053875 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-05-29 18:10 | 2023-05-29 20:09 | 1 | 1:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA QUEMADA. EVENTO TRANSFERIDO DE PONCE. | P23052900321 | New_Event | Cutout Failure | Include | Include | Equipment | 119 | 2023-05-29 | 119 | keep | 0 | May | 2023 | 8.105e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-29 18:20 | 2023-05-29 19:27 | 82 | 1:07 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | R23052900121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 67 | 2023-05-29 | 5494 | keep | 0 | May | 2023 | 0.0037419 | 5.585e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 82
FAJARDO | 2023-05-29 18:20 | 2023-05-29 20:54 | 269 | 2:34 | P | ANIMAL | 1 X 80 EN C/L CRUCE X AVE | R23052900072 | New_Event | Animals | Include | Include | Wildlife | 154 | 2023-05-29 | 41426 | keep | 0 | May | 2023 | 0.028215 | 0.00018321 | Sustained | FALSE | FALSE | Not_TMED_Event | 269
BARRANQUITAS | 2023-05-29 18:23 | 2023-05-29 19:17 | 6 | 0:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR SECUNDARIA | C23052900079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 54 | 2023-05-29 | 324 | keep | 0 | May | 2023 | 0.00022067 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
VEGA BAJA | 2023-05-29 18:24 | 2023-05-30 11:26 | 100 | 17:02 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REPARO LINEAS PRIMARIAS CRUZADAS | P23052900326 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1022 | 2023-05-29 | 102200 | keep | 0 | May | 2023 | 0.069608 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-05-29 18:39 | 2023-05-30 14:11 | 30 | 19:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23052900330 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1172 | 2023-05-29 | 35160 | keep | 0 | May | 2023 | 0.023947 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-29 18:46 | 2023-05-30 07:08 | 1 | 12:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | B23052900126 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 742 | 2023-05-29 | 742 | keep | 0 | May | 2023 | 0.00050537 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-29 19:13 | 2023-05-30 08:40 | 3 | 13:27 | P | NO SE REPORTO CAUSA | 1 X 20 EN RISER NO SE REPORTO CAUSA | P23052900338 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 807 | 2023-05-29 | 2421 | keep | 0 | May | 2023 | 0.0016489 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
MAYAGÃœEZ | 2023-05-29 19:21 | 2023-05-30 09:05 | 10 | 13:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA FUERTES VIENTOS | M23052900174 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 824 | 2023-05-29 | 8240 | keep | 0 | May | 2023 | 0.0056122 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-29 19:30 | 2023-05-30 11:19 | 13 | 15:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA PRIMARIA | C23052900175 | New_Event | Cutout Failure | Include | Include | Equipment | 949 | 2023-05-29 | 12337 | keep | 0 | May | 2023 | 0.0084027 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
SAN JUAN | 2023-05-29 19:38 | 2023-05-29 19:39 | 4944 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 4944 | keep | 0 | May | 2023 | 0.0033673 | 0.0033673 | Momentary | FALSE | FALSE | Not_TMED_Event | 4944
ARECIBO | 2023-05-29 19:43 | 2023-05-29 19:44 | 3431 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | A23052900217 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 3431 | keep | 0 | May | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
SAN JUAN | 2023-05-29 19:44 | 2023-05-29 19:45 | 291 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1345-02 LLEVA 65% DEL 1345-05 | S2305290000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 291 | keep | 0 | May | 2023 | 0.0001982 | 0.0001982 | Momentary | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2023-05-29 19:44 | 2023-05-29 19:45 | 435 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1342-05 | S2305290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-29 | 435 | keep | 0 | May | 2023 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-05-29 19:44 | 2023-05-29 19:45 | 625 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 65% DE SU CARGA POR E 1342-05 | S2305290000X | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-29 | 625 | keep | 0 | May | 2023 | 0.00042568 | 0.00042568 | Momentary | FALSE | FALSE | Not_TMED_Event | 625
BARRANQUITAS | 2023-05-29 19:46 | 2023-05-29 22:19 | 100 | 2:33 | P | OTRAS CAUSAS | 1 X 65 EN C/L FUSIBLE FATIGADO | C23052900178 | New_Event | Other Causes | Include | Include | Other | 153 | 2023-05-29 | 15300 | keep | 0 | May | 2023 | 0.010421 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-29 19:58 | 2023-05-29 19:59 | 291 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA LLEVA LA CARGA DEL 1345-02 LLEVA 65% DEL 1345-05 | S2305290000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-29 | 291 | keep | 0 | May | 2023 | 0.0001982 | 0.0001982 | Momentary | FALSE | FALSE | Not_TMED_Event | 291
SAN JUAN | 2023-05-29 19:58 | 2023-05-29 19:59 | 435 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA CARGA POR EL 1342-05 | S2305290000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-29 | 435 | keep | 0 | May | 2023 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-05-29 19:58 | 2023-05-29 19:59 | 625 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR SE CERRO POR SCADA 65% DE SU CARGA POR E 1342-05 | S2305290000X | 1st_after_momentary | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-29 | 625 | keep | 0 | May | 2023 | 0.00042568 | 0.00042568 | Momentary | FALSE | FALSE | Not_TMED_Event | 625
SAN JUAN | 2023-05-29 20:00 | 2023-05-29 21:23 | 245 | 1:23 | P | NO SE REPORTO CAUSA | 3 X 80 EN RISER | S23052900165 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2023-05-29 | 20335 | keep | 0 | May | 2023 | 0.01385 | 0.00016687 | Sustained | FALSE | FALSE | Not_TMED_Event | 245
SAN JUAN | 2023-05-29 20:02 | 2023-05-30 01:39 | 110 | 5:37 | P | SECUNDARIA/DESGANCHE | SE REPARO BAJANTE PRIMARIO EN CAJA DE XMR NO FUNDIO | S23052900169 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 337 | 2023-05-29 | 37070 | keep | 0 | May | 2023 | 0.025248 | 7.492e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 110
MAYAGÃœEZ | 2023-05-29 20:27 | 2023-05-30 01:30 | 1 | 5:03 | P | MAL TIEMPO/RAYOS | 1 X 80 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | P23052900359 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 303 | 2023-05-29 | 303 | keep | 0 | May | 2023 | 0.00020637 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-29 20:44 | 2023-05-30 08:40 | 7 | 11:56 | P | ANIMAL | 1 X 10 EN CORTE DE LINEA RANA CRUZO PARARRAYO | M23052900184 | New_Event | Animals | Include | Include | Wildlife | 716 | 2023-05-29 | 5012 | keep | 0 | May | 2023 | 0.0034137 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-05-29 21:02 | 2023-05-30 08:51 | 85 | 11:49 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23052900136 | New_Event | Animals | Include | Include | Wildlife | 709 | 2023-05-29 | 60265 | keep | 0 | May | 2023 | 0.041046 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
BAYAMON | 2023-05-29 21:47 | 2023-05-30 01:04 | 127 | 3:17 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B23052900143 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 197 | 2023-05-29 | 25019 | keep | 0 | May | 2023 | 0.01704 | 8.6499e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 127
AGUADILLA | 2023-05-29 21:52 | 2023-05-29 23:25 | 150 | 1:33 | P | MAL TIEMPO/RAYOS | 1 X 100 EN CORTE DE LINEA MAL TIEMPO DESCARGAS ELECTRICAS | A23052900031 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 93 | 2023-05-29 | 13950 | keep | 0 | May | 2023 | 0.0095013 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-05-29 21:57 | 2023-05-30 00:50 | 200 | 2:53 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | M23052900188 | New_Event | Primary Wire Break | Include | Include | Equipment | 173 | 2023-05-29 | 34600 | keep | 0 | May | 2023 | 0.023566 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
FAJARDO | 2023-05-29 22:01 | 2023-05-30 08:51 | 85 | 10:50 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | R23052900136 | New_Event | Animals | Include | Include | Wildlife | 650 | 2023-05-29 | 55250 | keep | 0 | May | 2023 | 0.037631 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
MAYAGÃœEZ | 2023-05-29 22:02 | 2023-05-30 18:40 | 140 | 20:38 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 3 X 100 EN CORTE DE LINEA SE REMPLAZO POSTE PARTIDO | M23052900190 | New_Event | Primary Pole Failure | Include | Include | Equipment | 1238 | 2023-05-29 | 173320 | keep | 0 | May | 2023 | 0.11805 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
VEGA BAJA | 2023-05-29 22:08 | 2023-05-30 02:06 | 150 | 3:58 | P | NO SE REPORTO CAUSA | 1X50 EN C/L | B23052900147 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2023-05-29 | 35700 | keep | 0 | May | 2023 | 0.024315 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
HUMACAO | 2023-05-29 22:55 | 2023-05-30 00:59 | 30 | 2:04 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | C23052900195 | New_Event | Animals | Include | Include | Wildlife | 124 | 2023-05-29 | 3720 | keep | 0 | May | 2023 | 0.0025337 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-30 00:38 | 2023-05-30 08:35 | 12 | 7:57 | P | ANIMAL | 1 X 8 EN XMR CRUCE POR AVE | R23053000001 | New_Event | Animals | Include | Include | Wildlife | 477 | 2023-05-30 | 5724 | keep | 0 | May | 2023 | 0.0038986 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-30 02:06 | 2023-05-30 07:49 | 4 | 5:43 | P | DESGANCHE | 1 X 25 EN RISER Y DESGANCHE | B23053000001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 343 | 2023-05-30 | 1372 | keep | 0 | May | 2023 | 0.00093446 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-05-30 03:07 | 2023-05-30 03:08 | 4009 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR SECUNDARIO PORTATIL 14 REALIZA UNA OPERACION Y QUEDA EN SERVICIO | P23053000017 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 4009 | keep | 0 | May | 2023 | 0.0027305 | 0.0027305 | Momentary | FALSE | FALSE | Not_TMED_Event | 4009
PONCE | 2023-05-30 03:08 | 2023-05-30 08:17 | 1 | 5:09 | P | DESGANCHE | DESGANCHE 1 X 25 EN CORTE DE LINEA | P23052900317 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 309 | 2023-05-30 | 309 | keep | 0 | May | 2023 | 0.00021046 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-05-30 03:14 | 2023-05-30 07:24 | 160 | 4:10 | P | PARARRAYOS DEFECTUOSO | 2 X 200 EN CORTE DE LINEA PARARRAYOS ACTIVADO | P23053000014 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 250 | 2023-05-30 | 40000 | keep | 0 | May | 2023 | 0.027244 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
AGUADILLA | 2023-05-30 04:14 | 2023-05-30 09:40 | 4 | 5:26 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR IGUANA CRUZO LINEAS | A23053000002 | New_Event | Animals | Include | Include | Wildlife | 326 | 2023-05-30 | 1304 | keep | 0 | May | 2023 | 0.00088815 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
HUMACAO | 2023-05-30 04:49 | 2023-05-30 09:00 | 12 | 4:11 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 10 EN XMR SE REMPLAZO BAJANTE SECUNDARIO Y PORTAFUSIBLE | C23053000004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 251 | 2023-05-30 | 3012 | keep | 0 | May | 2023 | 0.0020515 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
VEGA BAJA | 2023-05-30 04:59 | 2023-05-30 05:00 | 215 | 0:01 | T | DESGANCHE | SE CERRO POR CONTROL | B23053000004 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-30 | 215 | keep | 0 | May | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
VEGA BAJA | 2023-05-30 05:00 | 2023-05-30 09:00 | 105 | 4:00 | P | DESGANCHE | 1 X 100 C/L Y DESGANCHE | B23053000005 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 240 | 2023-05-30 | 25200 | keep | 0 | May | 2023 | 0.017164 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
PONCE | 2023-05-30 05:20 | 2023-05-30 09:37 | 100 | 4:17 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA ANIMAL | P23053000028 | New_Event | Animals | Include | Include | Wildlife | 257 | 2023-05-30 | 25700 | keep | 0 | May | 2023 | 0.017504 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
CANOVANAS | 2023-05-30 05:34 | 2023-05-30 09:22 | 3 | 3:48 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23053000002 | New_Event | Vegetation Contact | Include | Include | Vegetation | 228 | 2023-05-30 | 684 | keep | 0 | May | 2023 | 0.00046587 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-05-30 06:15 | 2023-05-30 09:12 | 50 | 2:57 | P | DESGANCHE | 2 X 65 EN C/L SE REALIZO DESGANCHE | S23053000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 177 | 2023-05-30 | 8850 | keep | 0 | May | 2023 | 0.0060277 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-30 06:18 | 2023-05-30 13:09 | 94 | 6:51 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23053000005 | New_Event | Vegetation Contact | Include | Include | Vegetation | 411 | 2023-05-30 | 38634 | keep | 0 | May | 2023 | 0.026313 | 6.4023e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 94
AGUADILLA | 2023-05-30 06:19 | 2023-05-30 08:25 | 125 | 2:06 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23053000006 | New_Event | Vegetation Contact | Include | Include | Vegetation | 126 | 2023-05-30 | 15750 | keep | 0 | May | 2023 | 0.010727 | 8.5137e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 125
CANOVANAS | 2023-05-30 06:22 | 2023-05-30 06:24 | 1615 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-30 | 3230 | keep | 0 | May | 2023 | 0.0021999 | 0.0011 | Momentary | FALSE | FALSE | Not_TMED_Event | 1615
GUAYAMA | 2023-05-30 06:25 | 2023-05-30 06:26 | 4132 | 0:01 | T | DESGANCHE | RECIERRE LLEVA LA CARGA DEL 4006-00 | P23053000040 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-30 | 4132 | keep | 0 | May | 2023 | 0.0028143 | 0.0028143 | Momentary | FALSE | FALSE | Not_TMED_Event | 4132
GUAYAMA | 2023-05-30 06:25 | 2023-05-30 06:26 | 1173 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 4003-01 | P23053000040 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-30 | 1173 | keep | 0 | May | 2023 | 0.00079892 | 0.00079892 | Momentary | FALSE | FALSE | Not_TMED_Event | 1173
GUAYAMA | 2023-05-30 06:25 | 2023-05-30 06:26 | 215 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 4003-01 | P23053000040 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-30 | 215 | keep | 0 | May | 2023 | 0.00014644 | 0.00014644 | Momentary | FALSE | FALSE | Not_TMED_Event | 215
GUAYAMA | 2023-05-30 06:25 | 2023-05-30 06:26 | 464 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL 4003-01 | P23053000040 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-30 | 464 | keep | 0 | May | 2023 | 0.00031603 | 0.00031603 | Momentary | FALSE | FALSE | Not_TMED_Event | 464
GUAYAMA | 2023-05-30 06:26 | 2023-05-30 10:00 | 25 | 3:34 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23053000049 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-05-30 | 5350 | keep | 0 | May | 2023 | 0.0036439 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
GUAYAMA | 2023-05-30 06:26 | 2023-05-30 08:41 | 25 | 2:15 | P | MAL TIEMPO/RAYOS | 2 X 80 EN CORTE DE LINEA POR DESCARGA ELECTRICA | P23052900341 | Partial_restoration | Bad Weather (Lightning) | Include | Include | Lightning | 135 | 2023-05-30 | 3375 | keep | 0 | May | 2023 | 0.0022987 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-05-30 06:49 | 2023-05-30 10:53 | 150 | 4:04 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE LEVANTO ALAMBRE PRIMARIO DESGANCHE | P23053000048 | New_Event | Vegetation Contact | Include | Include | Vegetation | 244 | 2023-05-30 | 36600 | keep | 0 | May | 2023 | 0.024928 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-30 06:54 | 2023-05-31 17:37 | 23 | 34:43 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR DE 75KVA AVERIADO POR UNO DE IGUAL CAPACIDAD | S23053000011 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2083 | 2023-05-30 | 47909 | keep | 0 | May | 2023 | 0.032631 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
BAYAMON | 2023-05-30 06:57 | 2023-05-30 06:58 | 5252 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 5252 | keep | 0 | May | 2023 | 0.0035771 | 0.0035771 | Momentary | FALSE | FALSE | Not_TMED_Event | 5252
VEGA BAJA | 2023-05-30 07:00 | 2023-05-30 08:59 | 30 | 1:59 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | B23053000033 | New_Event | Vegetation Contact | Include | Include | Vegetation | 119 | 2023-05-30 | 3570 | keep | 0 | May | 2023 | 0.0024315 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-30 07:13 | 2023-05-30 10:00 | 20 | 2:47 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO LINEAS | M23053000013 | New_Event | Animals | Include | Include | Wildlife | 167 | 2023-05-30 | 3340 | keep | 0 | May | 2023 | 0.0022749 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-30 07:25 | 2023-05-30 08:15 | 25 | 0:50 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA CRUCE POR AVE | C23053000012 | New_Event | Animals | Include | Include | Wildlife | 50 | 2023-05-30 | 1250 | keep | 0 | May | 2023 | 0.00085137 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-30 07:36 | 2023-05-31 09:48 | 71 | 26:12 | P | ANIMAL | 1 X 100 EN C/L CRUCE X AVE | B23053000017 | New_Event | Animals | Include | Include | Wildlife | 1572 | 2023-05-30 | 111612 | keep | 0 | May | 2023 | 0.076018 | 4.8358e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 71
BAYAMON | 2023-05-30 07:49 | 2023-05-30 07:50 | 3798 | 0:01 | T | DESGANCHE | DISPARO CERRADO POR CONTROL | B23053000019 | Additional_clients | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-30 | 3798 | keep | 0 | May | 2023 | 0.0025868 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-30 07:50 | 2023-05-30 12:37 | 4 | 4:47 | P | DESGANCHE | 1 X 25 EN RISER Y DESGANCHE | B23053000001 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 287 | 2023-05-30 | 1148 | keep | 0 | May | 2023 | 0.0007819 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
CANOVANAS | 2023-05-30 08:05 | 2023-05-30 10:39 | 8 | 2:34 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE. EVENTO TRANSFERIDO DE PONCE. | P23053000074 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 154 | 2023-05-30 | 1232 | keep | 0 | May | 2023 | 0.00083911 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
PONCE | 2023-05-30 08:30 | 2023-05-30 11:43 | 1 | 3:13 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN CORTE DE LINEA POR MAL TIEMPO | P23053000083 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 193 | 2023-05-30 | 193 | keep | 0 | May | 2023 | 0.00013145 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-30 08:36 | 2023-05-30 08:37 | 1709 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23053000021 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 1709 | keep | 0 | May | 2023 | 0.001164 | 0.001164 | Momentary | FALSE | FALSE | Not_TMED_Event | 1709
BARRANQUITAS | 2023-05-30 08:44 | 2023-05-30 08:45 | 2907 | 0:01 | T | ERROR HUMANO | SE ABRIO INTERRUPTOR ERRONEAMENTE. TODO EL PERSONAL ESTA SECCIONALIZADO SE CERRO NUEVAMENTE. | C23053000024 | New_Event | Human Error | Include | Include | Other | 1 | 2023-05-30 | 2907 | keep | 0 | May | 2023 | 0.0019799 | 0.0019799 | Momentary | FALSE | FALSE | Not_TMED_Event | 2907
BARRANQUITAS | 2023-05-30 08:47 | 2023-05-30 08:48 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA FUSIBLE FUNDIDO EN SUB 3602 LAS CRUCES | C23053000027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 1565 | keep | 0 | May | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-30 08:47 | 2023-05-30 08:48 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA FUSIBLE FUNDIDO EN SUB 3602 LAS CRUCES | C23053000027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 976 | keep | 0 | May | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-30 08:47 | 2023-05-30 08:48 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA FUSIBLE FUNDIDO EN SUB 3602 LAS CRUCES | C23053000027 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 548 | keep | 0 | May | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-05-30 08:47 | 2023-05-30 08:48 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA FUSIBLE FUNDIDO EN SUB 3602 LAS CRUCES | C23053000028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 315 | keep | 0 | May | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-05-30 08:47 | 2023-05-30 08:48 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA FUSIBLE FUNDIDO EN SUB 3602 LAS CRUCES | C23053000028 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 870 | keep | 0 | May | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-05-30 08:47 | 2023-05-30 08:48 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA FUSIBLE FUNDIDO EN SUB 3602 LAS CRUCES | C23053000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 2906 | keep | 0 | May | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-05-30 08:47 | 2023-05-30 08:48 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0800 DE COMSAT A CIDRA FUSIBLE FUNDIDO EN SUB 3602 LAS CRUCES | C23053000002 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 2343 | keep | 0 | May | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
CAGUAS | 2023-05-30 08:48 | 2023-05-30 09:09 | 5 | 0:21 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA PARARRAYO PRIVADO AVERIADO EVENTO TRANSFERIDO | P23053000088 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 21 | 2023-05-30 | 105 | keep | 0 | May | 2023 | 7.1515e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BARRANQUITAS | 2023-05-30 08:48 | 2023-05-30 11:04 | 11 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REEMPLAZO DE 70 PIES DE SECUNDARIA | C23052900174 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-05-30 | 1496 | keep | 0 | May | 2023 | 0.0010189 | 7.492e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 11
SAN JUAN | 2023-05-30 08:49 | 2023-05-30 14:44 | 1 | 5:55 | P | NO SE REPORTO CAUSA | 1 X 40 EN RISER | S23053000023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 355 | 2023-05-30 | 355 | keep | 0 | May | 2023 | 0.00024179 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-30 09:03 | 2023-05-30 10:00 | 300 | 0:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 50 EN CORTE DE LINEA FUERTES VIENTOS | M23053000027 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 57 | 2023-05-30 | 17100 | keep | 0 | May | 2023 | 0.011647 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
CAGUAS | 2023-05-30 09:09 | 2023-05-30 09:10 | 918 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRO | C2305300000X | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-05-30 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-30 09:09 | 2023-05-30 09:10 | 1725 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRO | C2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 1725 | keep | 0 | May | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
CAGUAS | 2023-05-30 09:10 | 2023-05-30 09:36 | 5 | 0:26 | P | PARARRAYOS DEFECTUOSO | 1 X 80 EN CORTE DE LINEA PARARRAYO PRIVADO AVERIADO EVENTO TRANSFERIDO | P23053000088 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 26 | 2023-05-30 | 130 | keep | 0 | May | 2023 | 8.8542e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-05-30 09:15 | 2023-05-30 19:46 | 19 | 10:31 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L SE REEMPLAZO PORTA FUSIBLE | B23053000041 | New_Event | Cutout Failure | Include | Include | Equipment | 631 | 2023-05-30 | 11989 | keep | 0 | May | 2023 | 0.0081657 | 1.2941e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 19
HUMACAO | 2023-05-30 09:26 | 2023-05-30 11:42 | 25 | 2:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 30 EN C/L MAL TIEMPO FUERTES LLUVIAS | C23053000055 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 136 | 2023-05-30 | 3400 | keep | 0 | May | 2023 | 0.0023157 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-05-30 09:29 | 2023-05-30 12:00 | 10 | 2:31 | P | SECUNDARIA/OTROS | SE REPARO TOMA AVERIADA Y PEDESTAL SECUNDARIO COMPLETO | P23053000116 | New_Event |  |  |  |  | 151 | 2023-05-30 | 1510 | keep | 0 | May | 2023 | 0.0010285 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-30 09:36 | 2023-05-30 11:16 | 1 | 1:40 | P | PARARRAYOS DEFECTUOSO | SE REMPLAZO PARARRAYO DE BORINQUEN METAL Y 1 X 65 EN RISER | C23053000118 | Partial_restoration | Lightning Arrester Failure | Include | Include | Equipment | 100 | 2023-05-30 | 100 | keep | 0 | May | 2023 | 6.811e-05 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-30 09:37 | 2023-05-30 10:41 | 33 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR Y SE REPARO SECUNDARIA SOTERRADA AVERIADA | B23052700089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-05-30 | 2112 | keep | 0 | May | 2023 | 0.0014385 | 2.2476e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 33
BAYAMON | 2023-05-30 09:39 | 2023-05-30 11:03 | 5 | 1:24 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA | B23053000045 | New_Event | Cutout Failure | Include | Include | Equipment | 84 | 2023-05-30 | 420 | keep | 0 | May | 2023 | 0.00028606 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-05-30 09:40 | 2023-05-30 10:20 | 60 | 0:40 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CORTE DE LINEA PARA REPARAR BAJANTE EN MALAS CONDICIONES | M23053000037 | New_Event | Primary Wire Break | Include | Include | Equipment | 40 | 2023-05-30 | 2400 | keep | 0 | May | 2023 | 0.0016346 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
VEGA BAJA | 2023-05-30 09:41 | 2023-05-30 12:08 | 1 | 2:27 | P | NO SE REPORTO CAUSA | 1 X 30 EN RISER | B23053000047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 147 | 2023-05-30 | 147 | keep | 0 | May | 2023 | 0.00010012 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-30 09:42 | 2023-05-30 12:02 | 156 | 2:20 | P | ANIMAL | 2 X 65 EN RISER AVE CRUZO LINEAS | S23053000034 | New_Event | Animals | Include | Include | Wildlife | 140 | 2023-05-30 | 21840 | keep | 0 | May | 2023 | 0.014875 | 0.00010625 | Sustained | FALSE | FALSE | Not_TMED_Event | 156
CANOVANAS | 2023-05-30 09:43 | 2023-05-30 10:25 | 1 | 0:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 2 X 15 EN RISER SE REEMPLAZO PORTAFUSIBLE QUEMADO. EVENTO TRANSFERIDO DE PONCE. | P23053000134 | New_Event | Cutout Failure | Include | Include | Equipment | 42 | 2023-05-30 | 42 | keep | 0 | May | 2023 | 2.8606e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-05-30 09:45 | 2023-05-30 09:46 | 62 | 0:01 | P | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL 90% POR 1330-01 | S23053000039 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 62 | keep | 0 | May | 2023 | 4.2228e-05 | 4.2228e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 62
BAYAMON | 2023-05-30 09:49 | 2023-05-30 09:50 | 61 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23053000048 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 61 | keep | 0 | May | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-05-30 09:50 | 2023-05-30 10:35 | 278 | 0:45 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO MACHETES Y SE SECCIONALIZO POSTE PRIMARIO PARTIDO | R23053000028 | New_Event | Primary Pole Failure | Include | Include | Equipment | 45 | 2023-05-30 | 12510 | keep | 0 | May | 2023 | 0.0085205 | 0.00018934 | Sustained | FALSE | FALSE | Not_TMED_Event | 278
BAYAMON | 2023-05-30 09:51 | 2023-05-30 09:53 | 580 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO CERRADO POR CONTROL 30% POR 1708-02 | B2305300000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-05-30 | 1160 | keep | 0 | May | 2023 | 0.00079007 | 0.00039504 | Momentary | FALSE | FALSE | Not_TMED_Event | 580
BAYAMON | 2023-05-30 09:51 | 2023-05-30 09:53 | 1715 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO CERRADO POR CONTROL LLEVA 30% 1707-01 | B2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-30 | 3430 | keep | 0 | May | 2023 | 0.0023362 | 0.0011681 | Momentary | FALSE | FALSE | Not_TMED_Event | 1715
CAGUAS | 2023-05-30 09:56 | 2023-05-30 09:57 | 4369 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C23053000079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 4369 | keep | 0 | May | 2023 | 0.0029757 | 0.0029757 | Momentary | FALSE | FALSE | Not_TMED_Event | 4369
CAGUAS | 2023-05-30 09:56 | 2023-05-30 09:57 | 676 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C23053000079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 676 | keep | 0 | May | 2023 | 0.00046042 | 0.00046042 | Momentary | FALSE | FALSE | Not_TMED_Event | 676
CAGUAS | 2023-05-30 09:56 | 2023-05-30 09:57 | 1606 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C23053000079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
CAGUAS | 2023-05-30 09:56 | 2023-05-30 09:57 | 725 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECERRO LA LINEA 0600 DE CAGUAS TC A GAUTIER BENITEZ | C23053000079 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 725 | keep | 0 | May | 2023 | 0.00049379 | 0.00049379 | Momentary | FALSE | FALSE | Not_TMED_Event | 725
CANOVANAS | 2023-05-30 09:59 | 2023-05-30 17:13 | 10 | 7:14 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE Y RETIRO LAGARTO. EVENTO TRANSFERIDO DE PONCE. | P23053000140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 434 | 2023-05-30 | 4340 | keep | 0 | May | 2023 | 0.002956 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-30 10:03 | 2023-05-30 15:06 | 31 | 5:03 | P | DESGANCHE | 2 X 100 EN C/L DESGANCHE | S23053000046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 303 | 2023-05-30 | 9393 | keep | 0 | May | 2023 | 0.0063975 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
SAN JUAN | 2023-05-30 10:04 | 2023-05-30 14:02 | 147 | 3:58 | P | NO SE REPORTO CAUSA | 1 X 100 EN C/L NO CAUSA | S23053000047 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 238 | 2023-05-30 | 34986 | keep | 0 | May | 2023 | 0.023829 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
HUMACAO | 2023-05-30 10:11 | 2023-05-30 12:10 | 8 | 1:59 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 75 KVA X 50 KVA | C23053000085 | New_Event | Service Transformer Failure | Include | Include | Equipment | 119 | 2023-05-30 | 952 | keep | 0 | May | 2023 | 0.0006484 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-05-30 10:12 | 2023-05-30 13:28 | 10 | 3:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA AVERIADA EVENTO TRANSFERIDO DE PONCE | P23052900289 | New_Event | Secondary Wire Break | Include | Include | Equipment | 196 | 2023-05-30 | 1960 | keep | 0 | May | 2023 | 0.0013349 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-30 10:17 | 2023-05-30 11:46 | 1565 | 1:29 | S | AVERIA EN BARRA DE DISTRIBUCION | SE RETIRO LA CARGA POR FUSIBLE DE LA ALTA FUNDIDO SE ENCONTRO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION Y SE TRANSFIRIO LA CARGA SE CERRO N/O CONTRA 3602-03 Y SE PASO AL 3406-02 | C23053000107 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 89 | 2023-05-30 | 139285 | keep | 0 | May | 2023 | 0.094866 | 0.0010659 | Sustained | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-05-30 10:17 | 2023-05-30 10:55 | 976 | 0:38 | S | AVERIA EN BARRA DE DISTRIBUCION | SE RETIRO LA CARGA POR FUSIBLE DE LA ALTA FUNDIDO SE ENCONTRO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION Y SE TRANSFIRIO LA CARGA AL 3603-02 | C23053000107 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 38 | 2023-05-30 | 37088 | keep | 0 | May | 2023 | 0.02526 | 0.00066475 | Sustained | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-05-30 10:17 | 2023-05-30 11:46 | 548 | 1:29 | S | AVERIA EN BARRA DE DISTRIBUCION | SE RETIRO LA CARGA POR FUSIBLE DE LA ALTA FUNDIDO SE ENCONTRO PARARRAYO AVERIADO EN BARRA DE DISTRIBUCION Y SE TRANSFIRIO LA CARGA SE CERRO N/O CONTRA 3406-02 | C23053000107 | New_Event | Distribution Substation Bus Support/Structure Failure | Include | Include | Equipment | 89 | 2023-05-30 | 48772 | keep | 0 | May | 2023 | 0.033218 | 0.00037324 | Sustained | FALSE | FALSE | Not_TMED_Event | 548
BAYAMON | 2023-05-30 10:18 | 2023-05-30 13:00 | 29 | 2:42 | P | PARARRAYOS DEFECTUOSO | 1 X 40 C/L Y SE REMPLAZO PARA RAYO | B23053000058 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 162 | 2023-05-30 | 4698 | keep | 0 | May | 2023 | 0.0031998 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
HUMACAO | 2023-05-30 10:18 | 2023-05-30 10:19 | 3902 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 3902 | keep | 0 | May | 2023 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
CAGUAS | 2023-05-30 10:20 | 2023-05-30 14:00 | 80 | 3:40 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | C23053000103 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 220 | 2023-05-30 | 17600 | keep | 0 | May | 2023 | 0.011987 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-05-30 10:20 | 2023-05-30 12:14 | 1159 | 1:54 | P | DESGANCHE | DISPARO DE INTERRUPTOR SE RETIRO RAMA SOBRE LINEA Y SE CERRO POR SCADA 17% POR 9202-02 | B23053000068 | New_Event | Vegetation Contact | Include | Include | Vegetation | 114 | 2023-05-30 | 132126 | keep | 0 | May | 2023 | 0.08999 | 0.00078939 | Sustained | FALSE | FALSE | Not_TMED_Event | 1159
SAN JUAN | 2023-05-30 10:23 | 2023-05-30 10:24 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
AGUADILLA | 2023-05-30 10:25 | 2023-05-30 11:00 | 5 | 0:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS DE TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | M23053000016 | New_Event | Secondary Wire Break | Include | Include | Equipment | 35 | 2023-05-30 | 175 | keep | 0 | May | 2023 | 0.00011919 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
MAYAGÃœEZ | 2023-05-30 10:26 | 2023-05-30 13:25 | 200 | 2:59 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO DOS CAJAS DE 200 AMP QUEMADAS | M23053000049 | New_Event | Cutout Failure | Include | Include | Equipment | 179 | 2023-05-30 | 35800 | keep | 0 | May | 2023 | 0.024383 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-05-30 10:35 | 2023-05-30 16:27 | 52 | 5:52 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO PUENTES Y SE REEMPLAZO POSTE PRIMARIO PARTIDO | R23053000028 | New_Event | Primary Pole Failure | Include | Include | Equipment | 352 | 2023-05-30 | 18304 | keep | 0 | May | 2023 | 0.012467 | 3.5417e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 52
CANOVANAS | 2023-05-30 10:41 | 2023-05-30 10:42 | 7621 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23053000036 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 7621 | keep | 0 | May | 2023 | 0.0051906 | 0.0051906 | Momentary | FALSE | FALSE | Not_TMED_Event | 7621
CANOVANAS | 2023-05-30 10:41 | 2023-05-30 12:06 | 3699 | 1:25 | T | AISLADOR ROTO, PARTIDO O SAFADO | RECERRO 3 VECES Y QUEDO FUERA SE REEMPLAZO AISLADOR PARTIDO CERCA DE LA SALIDA DEL ALIMENTADOR 100% EN SERVICIO | R23053000035 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 85 | 2023-05-30 | 314415 | keep | 0 | May | 2023 | 0.21415 | 0.0025194 | Sustained | FALSE | FALSE | Not_TMED_Event | 3699
HUMACAO | 2023-05-30 10:42 | 2023-05-30 10:43 | 2586 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 2586 | keep | 0 | May | 2023 | 0.0017613 | 0.0017613 | Momentary | FALSE | FALSE | Not_TMED_Event | 2586
BAYAMON | 2023-05-30 10:50 | 2023-05-30 14:00 | 1210 | 3:10 | T | ERROR HUMANO | EN LA VIA LIBRE D2023-4112 SE REALIZO UNA OPERACION DE TRANSFERENCIA DEL 1718-01 CON EL 1713-05 EL MISMO SE CERRO Y NO ASUMIO LA CARGA SE PENALIZARON LOS LIENTES DEL 1718-01 | B23053000276 | New_Event | Human Error | Include | Include | Other | 190 | 2023-05-30 | 229900 | keep | 0 | May | 2023 | 0.15658 | 0.00082413 | Sustained | FALSE | FALSE | Not_TMED_Event | 1210
UTUADO | 2023-05-30 10:54 | 2023-05-30 14:31 | 3 | 3:37 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23053000043 | New_Event | Vegetation Contact | Include | Include | Vegetation | 217 | 2023-05-30 | 651 | keep | 0 | May | 2023 | 0.00044339 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
UTUADO | 2023-05-30 11:04 | 2023-05-30 16:20 | 60 | 5:16 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | A23053000044 | New_Event | Cutout Failure | Include | Include | Equipment | 316 | 2023-05-30 | 18960 | keep | 0 | May | 2023 | 0.012914 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-30 11:13 | 2023-05-30 21:11 | 15 | 9:58 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR DE 75KVA X 75 KVA | B23053000077 | New_Event | Service Transformer Failure | Include | Include | Equipment | 598 | 2023-05-30 | 8970 | keep | 0 | May | 2023 | 0.0061094 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
MAYAGÃœEZ | 2023-05-30 11:13 | 2023-05-30 13:40 | 100 | 2:27 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23053000063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 147 | 2023-05-30 | 14700 | keep | 0 | May | 2023 | 0.010012 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-05-30 11:13 | 2023-05-30 13:40 | 3 | 2:27 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE DE LINEA A CAJA DE TRANSFORMADOR | M23053000062 | New_Event | Primary Wire Break | Include | Include | Equipment | 147 | 2023-05-30 | 441 | keep | 0 | May | 2023 | 0.00030036 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-05-30 11:19 | 2023-05-30 11:20 | 45 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2305300000X | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 45 | keep | 0 | May | 2023 | 3.0649e-05 | 3.0649e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 45
ARECIBO | 2023-05-30 11:19 | 2023-05-30 15:10 | 15 | 3:51 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR DEFECTUOSO DE 37.5KVA X 25KVA | A23053000051 | New_Event | Service Transformer Failure | Include | Include | Equipment | 231 | 2023-05-30 | 3465 | keep | 0 | May | 2023 | 0.00236 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-30 11:25 | 2023-05-30 11:27 | 1368 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE CERRO POR SCADA | S23053000063 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-30 | 2736 | keep | 0 | May | 2023 | 0.0018635 | 0.00093174 | Momentary | FALSE | FALSE | Not_TMED_Event | 1368
BAYAMON | 2023-05-30 11:57 | 2023-05-30 15:31 | 25 | 3:34 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | B23053000103 | New_Event | Vegetation Contact | Include | Include | Vegetation | 214 | 2023-05-30 | 5350 | keep | 0 | May | 2023 | 0.0036439 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
YAUCO | 2023-05-30 12:00 | 2023-05-30 17:40 | 3 | 5:40 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO | P23053000215 | New_Event | Primary Wire Break | Include | Include | Equipment | 340 | 2023-05-30 | 1020 | keep | 0 | May | 2023 | 0.00069472 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CAGUAS | 2023-05-30 12:07 | 2023-05-30 12:08 | 1367 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE SOLO LLEVA EL 80% DE SU CARGA | C2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 1367 | keep | 0 | May | 2023 | 0.00093106 | 0.00093106 | Momentary | FALSE | FALSE | Not_TMED_Event | 1367
BAYAMON | 2023-05-30 12:10 | 2023-05-30 13:25 | 511 | 1:15 | P | ARBOL SOBRE LINEA | BY-230530-01 VIA LIBRE EMERGENCIA POR ARBOL ENCIMA DE LINEAS, SE SECCIONALIZA PARA WRIGHT TREE SERVICES | B23053000117 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 75 | 2023-05-30 | 38325 | keep | 0 | May | 2023 | 0.026103 | 0.00034804 | Sustained | FALSE | FALSE | Not_TMED_Event | 511
VEGA BAJA | 2023-05-30 12:30 | 2023-05-30 18:05 | 20 | 5:35 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23053000064 | New_Event | Vegetation Contact | Include | Include | Vegetation | 335 | 2023-05-30 | 6700 | keep | 0 | May | 2023 | 0.0045633 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-30 12:31 | 2023-05-30 12:50 | 200 | 0:19 | P | CONDUCTOR ROTO O ABIERTO | LINEA PRIMARIA PARTIDA SE ABRIO CORTE DE LINEA PARA SECCIONALIZAR | M23053000094 | New_Event | Primary Wire Break | Include | Include | Equipment | 19 | 2023-05-30 | 3800 | keep | 0 | May | 2023 | 0.0025882 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-30 12:38 | 2023-05-30 12:39 | 3511 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B23053000119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 3511 | keep | 0 | May | 2023 | 0.0023913 | 0.0023913 | Momentary | FALSE | FALSE | Not_TMED_Event | 3511
BAYAMON | 2023-05-30 12:44 | 2023-05-30 20:38 | 21 | 7:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLZO CAJA PRIMARIA | B23053000124 | New_Event | Cutout Failure | Include | Include | Equipment | 474 | 2023-05-30 | 9954 | keep | 0 | May | 2023 | 0.0067796 | 1.4303e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 21
CANOVANAS | 2023-05-30 12:48 | 2023-05-30 12:49 | 1648 | 0:01 | T | ANIMAL | RECIERRE DE INTERRUPTOR LLEVA 75% DEL 2402-02 | R23053000057 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-05-30 | 1648 | keep | 0 | May | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-05-30 12:48 | 2023-05-30 12:49 | 3141 | 0:01 | P | ALIMENTADOR AMARRADO | RECIERRE DE INTERRUPTOR 2302-03 LLEVA 75% DEL 2402-02 | R23053000057 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-30 | 3141 | keep | 0 | May | 2023 | 0.0021393 | 0.0021393 | Momentary | FALSE | FALSE | Not_TMED_Event | 3141
CANOVANAS | 2023-05-30 12:49 | 2023-05-30 14:26 | 150 | 1:37 | P | ANIMAL | 1 X 40 Y 1 X 100 EN C/L CRUCE X AVE | R23053000059 | 1st_after_momentary | Animals | Include | Include | Wildlife | 97 | 2023-05-30 | 14550 | keep | 0 | May | 2023 | 0.0099099 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
AGUADILLA | 2023-05-30 12:50 | 2023-05-30 14:25 | 643 | 1:35 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO LINEA PARTIDA Y SE CERRO CORTE DE LINEA | M23053000100 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 95 | 2023-05-30 | 61085 | keep | 0 | May | 2023 | 0.041605 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-05-30 13:00 | 2023-05-30 15:37 | 1 | 2:37 | P | DESGANCHE | 2 X 40 EN C/L Y DESGANCHE | C23053000142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 157 | 2023-05-30 | 157 | keep | 0 | May | 2023 | 0.00010693 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-30 13:00 | 2023-05-30 14:30 | 1 | 1:30 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | M23053000106 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 90 | 2023-05-30 | 90 | keep | 0 | May | 2023 | 6.1299e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-30 13:10 | 2023-05-30 17:05 | 15 | 3:55 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA AVERIADA | S23053000089 | New_Event | Secondary Wire Break | Include | Include | Equipment | 235 | 2023-05-30 | 3525 | keep | 0 | May | 2023 | 0.0024009 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-05-30 13:11 | 2023-05-30 15:35 | 167 | 2:24 | T | DESGANCHE | SE CONFIRMA INTERRUPTOR ABIERTO Y SE CIERRA MANUALMENTE SE RETIRO RAMA SOBRE LINEA | P23053000252 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-05-30 | 24048 | keep | 0 | May | 2023 | 0.016379 | 0.00011374 | Sustained | FALSE | FALSE | Not_TMED_Event | 167
VEGA BAJA | 2023-05-30 13:15 | 2023-05-30 13:32 | 10 | 0:17 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRO XMR Y SE REPARO SECUNDARIA | B23052900133 | New_Event | Secondary Wire Break | Include | Include | Equipment | 17 | 2023-05-30 | 170 | keep | 0 | May | 2023 | 0.00011579 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-30 13:24 | 2023-05-30 15:27 | 20 | 2:03 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23053000148 | New_Event | Vegetation Contact | Include | Include | Vegetation | 123 | 2023-05-30 | 2460 | keep | 0 | May | 2023 | 0.0016755 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-05-30 13:29 | 2023-05-30 17:42 | 190 | 4:13 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO LINEA PRIMARIA ZAFADA A CRUCETA 1 X 100 EN CORTE DE LINEA | P23053000260 | New_Event | Primary Wire Break | Include | Include | Equipment | 253 | 2023-05-30 | 48070 | keep | 0 | May | 2023 | 0.03274 | 0.00012941 | Sustained | FALSE | FALSE | Not_TMED_Event | 190
SAN JUAN | 2023-05-30 13:31 | 2023-05-30 13:32 | 7 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 7 | keep | 0 | May | 2023 | 4.7677e-06 | 4.7677e-06 | Momentary | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-05-30 13:31 | 2023-05-30 13:32 | 15 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | S2305300000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 15 | keep | 0 | May | 2023 | 1.0216e-05 | 1.0216e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-30 13:47 | 2023-05-30 16:36 | 55 | 2:49 | P | CAUSAS EXTERNAS | SE REEMPLAZO XMR T-229 POR BUSHING AVERIADO A CAUSA DE IMPACTO DE ESCAVADORA. | R23053000064 | New_Event | Damage From Public | Include | Include | Public | 169 | 2023-05-30 | 9295 | keep | 0 | May | 2023 | 0.0063308 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2023-05-30 13:49 | 2023-05-30 17:16 | 56 | 3:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIA | C23053000161 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 207 | 2023-05-30 | 11592 | keep | 0 | May | 2023 | 0.0078953 | 3.8141e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 56
BAYAMON | 2023-05-30 13:50 | 2023-05-30 14:10 | 178 | 0:20 | T | NO SE REPORTO CAUSA | EN SERVICIO CERRADO EN SUBESTACION | S23053000100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 20 | 2023-05-30 | 3560 | keep | 0 | May | 2023 | 0.0024247 | 0.00012123 | Sustained | FALSE | FALSE | Not_TMED_Event | 178
BAYAMON | 2023-05-30 13:52 | 2023-05-30 16:50 | 18 | 2:58 | P | DESGANCHE | 1 X 140 EN C/L DESGANCHE | B23053000142 | New_Event | Vegetation Contact | Include | Include | Vegetation | 178 | 2023-05-30 | 3204 | keep | 0 | May | 2023 | 0.0021822 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
SAN JUAN | 2023-05-30 13:53 | 2023-05-30 14:30 | 114 | 0:37 | P | ANIMAL | 2 X 25 C/L CRUCE POR AVE | S23053000101 | New_Event | Animals | Include | Include | Wildlife | 37 | 2023-05-30 | 4218 | keep | 0 | May | 2023 | 0.0028729 | 7.7645e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 114
CANOVANAS | 2023-05-30 13:53 | 2023-05-30 14:50 | 60 | 0:57 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO LLUVIAS | R23053000065 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 57 | 2023-05-30 | 3420 | keep | 0 | May | 2023 | 0.0023293 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-05-30 13:56 | 2023-05-30 18:34 | 66 | 4:38 | P | DESGANCHE | 1 X 100 Y DESGANCHE | B23053000146 | New_Event | Vegetation Contact | Include | Include | Vegetation | 278 | 2023-05-30 | 18348 | keep | 0 | May | 2023 | 0.012497 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
CAGUAS | 2023-05-30 14:04 | 2023-05-31 09:50 | 5 | 19:46 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y REPARO BAJANTE SECUNDARIO | C23053000167 | New_Event | Secondary Wire Break | Include | Include | Equipment | 1186 | 2023-05-30 | 5930 | keep | 0 | May | 2023 | 0.0040389 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
YAUCO | 2023-05-30 14:06 | 2023-05-30 15:01 | 35 | 0:55 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA POR MAL TIEMPO | P23053000283 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 55 | 2023-05-30 | 1925 | keep | 0 | May | 2023 | 0.0013111 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
SAN JUAN | 2023-05-30 14:08 | 2023-05-31 10:32 | 7 | 20:24 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23053000110 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1224 | 2023-05-30 | 8568 | keep | 0 | May | 2023 | 0.0058356 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
BAYAMON | 2023-05-30 14:13 | 2023-05-30 17:21 | 168 | 3:08 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO LLUVIAS | B23053000158 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 188 | 2023-05-30 | 31584 | keep | 0 | May | 2023 | 0.021512 | 0.00011442 | Sustained | FALSE | FALSE | Not_TMED_Event | 168
VEGA BAJA | 2023-05-30 14:17 | 2023-05-30 16:10 | 6 | 1:53 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23053000078 | New_Event | Primary Wire Break | Include | Include | Equipment | 113 | 2023-05-30 | 678 | keep | 0 | May | 2023 | 0.00046178 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BARRANQUITAS | 2023-05-30 14:34 | 2023-05-30 18:29 | 45 | 3:55 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | C23053000173 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 235 | 2023-05-30 | 10575 | keep | 0 | May | 2023 | 0.0072026 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
MAYAGÃœEZ | 2023-05-30 14:38 | 2023-05-30 17:55 | 3 | 3:17 | P | EXCAVACIONES | 1 X 30 EN TRANSFORMADOR MAQUINA REALIZANDO EXCAVACION CRUZO SECUNDARIA | M23053000141 | New_Event | Excavation | Include | Include | Public | 197 | 2023-05-30 | 591 | keep | 0 | May | 2023 | 0.00040253 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-05-30 14:39 | 2023-05-30 14:44 | 1 | 0:05 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 30 EN RISER MAL TIEMPO LLUVIAS | B23053000169 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 5 | 2023-05-30 | 5 | keep | 0 | May | 2023 | 3.4055e-06 | 6.811e-07 | Momentary | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-30 14:41 | 2023-05-30 16:40 | 35 | 1:59 | P | CONDUCTOR ROTO O ABIERTO | ALAMBRE PARTIDO | M23053000161 | New_Event | Primary Wire Break | Include | Include | Equipment | 119 | 2023-05-30 | 4165 | keep | 0 | May | 2023 | 0.0028368 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
BAYAMON | 2023-05-30 14:59 | 2023-05-30 18:17 | 1 | 3:18 | P | ANIMAL | SE REEMPLAZO CAJA Y 2 X 40 EN RISER CRUCE POR IGUANA | B23053000176 | New_Event | Animals | Include | Include | Wildlife | 198 | 2023-05-30 | 198 | keep | 0 | May | 2023 | 0.00013486 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-30 15:09 | 2023-05-30 15:10 | 1902 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053000072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 1902 | keep | 0 | May | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-05-30 15:09 | 2023-05-30 15:10 | 970 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053000072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 970 | keep | 0 | May | 2023 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-05-30 15:09 | 2023-05-30 15:10 | 3003 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053000072 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 3003 | keep | 0 | May | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-05-30 15:09 | 2023-05-30 15:10 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 2343 | keep | 0 | May | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-05-30 15:09 | 2023-05-30 15:10 | 1830 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 1830 | keep | 0 | May | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-05-30 15:09 | 2023-05-30 15:10 | 710 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 710 | keep | 0 | May | 2023 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-05-30 15:09 | 2023-05-30 15:10 | 1197 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053000071 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 1197 | keep | 0 | May | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
BAYAMON | 2023-05-30 15:17 | 2023-05-31 11:44 | 20 | 20:27 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23053000182 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1227 | 2023-05-30 | 24540 | keep | 0 | May | 2023 | 0.016714 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-30 15:22 | 2023-05-30 19:02 | 1 | 3:40 | P | NO SE REPORTO CAUSA | 2 X 50 EN C/L | C23053000215 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 220 | 2023-05-30 | 220 | keep | 0 | May | 2023 | 0.00014984 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-30 15:22 | 2023-05-30 15:23 | 1367 | 0:01 | P | DESGANCHE | RECIERRE DE BKR SOLO LLEVA UN 80% DE SU CARGA | C23053000217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-30 | 1367 | keep | 0 | May | 2023 | 0.00093106 | 0.00093106 | Momentary | FALSE | FALSE | Not_TMED_Event | 1367
HUMACAO | 2023-05-30 15:23 | 2023-05-30 18:33 | 152 | 3:10 | P | DESGANCHE | 2 X 50 EN C/L Y 2 X 65 EN C/L Y DESGANCHE | C2305300218 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-05-30 | 28880 | keep | 0 | May | 2023 | 0.01967 | 0.00010353 | Sustained | FALSE | FALSE | Not_TMED_Event | 152
CAGUAS | 2023-05-30 15:23 | 2023-05-30 19:05 | 47 | 3:42 | P | DESGANCHE | 2 X 50 EN C/L Y DESGANCHE | C23053000295 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 222 | 2023-05-30 | 10434 | keep | 0 | May | 2023 | 0.0071065 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
VEGA BAJA | 2023-05-30 15:23 | 2023-05-30 15:38 | 15 | 0:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO DE TRANSFORMADOR | A23053000090 | New_Event | Primary Wire Break | Include | Include | Equipment | 15 | 2023-05-30 | 225 | keep | 0 | May | 2023 | 0.00015325 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-30 15:25 | 2023-05-30 17:20 | 14 | 1:55 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 10 EN XMR SE REEMPLAZO PORTAFUSIBLE | R23053000074 | New_Event | Cutout Failure | Include | Include | Equipment | 115 | 2023-05-30 | 1610 | keep | 0 | May | 2023 | 0.0010966 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
GUAYAMA | 2023-05-30 15:29 | 2023-05-30 15:30 | 1606 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23053000342 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 1606 | keep | 0 | May | 2023 | 0.0010938 | 0.0010938 | Momentary | FALSE | FALSE | Not_TMED_Event | 1606
BARRANQUITAS | 2023-05-30 15:30 | 2023-05-30 15:31 | 2725 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA 8500 DE CAYEY TC A SANTA ISABEL TC | C23053000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 2725 | keep | 0 | May | 2023 | 0.001856 | 0.001856 | Momentary | FALSE | FALSE | Not_TMED_Event | 2725
BARRANQUITAS | 2023-05-30 15:30 | 2023-05-30 15:31 | 1834 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA 8500 DE CAYEY TC A SANTA ISABEL TC | C23053000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 1834 | keep | 0 | May | 2023 | 0.0012491 | 0.0012491 | Momentary | FALSE | FALSE | Not_TMED_Event | 1834
BARRANQUITAS | 2023-05-30 15:30 | 2023-05-30 15:31 | 1437 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA 8500 DE CAYEY TC A SANTA ISABEL TC | C23053000227 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 1437 | keep | 0 | May | 2023 | 0.00097873 | 0.00097873 | Momentary | FALSE | FALSE | Not_TMED_Event | 1437
BARRANQUITAS | 2023-05-30 15:30 | 2023-05-30 15:31 | 2565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA 8500 DE CAYEY TC A SANTA ISABEL TC | C23053000229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 2565 | keep | 0 | May | 2023 | 0.001747 | 0.001747 | Momentary | FALSE | FALSE | Not_TMED_Event | 2565
BARRANQUITAS | 2023-05-30 15:30 | 2023-05-30 15:31 | 3565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA 8500 DE CAYEY TC A SANTA ISABEL TC | C23053000229 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-30 | 3565 | keep | 0 | May | 2023 | 0.0024281 | 0.0024281 | Momentary | FALSE | FALSE | Not_TMED_Event | 3565
VEGA BAJA | 2023-05-30 15:40 | 2023-05-30 18:55 | 25 | 3:15 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23053000099 | New_Event | Vegetation Contact | Include | Include | Vegetation | 195 | 2023-05-30 | 4875 | keep | 0 | May | 2023 | 0.0033203 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
SAN JUAN | 2023-05-30 15:41 | 2023-05-30 15:42 | 1452 | 0:01 | T | DESGANCHE | RECIERERE | S2305300000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-30 | 1452 | keep | 0 | May | 2023 | 0.00098895 | 0.00098895 | Momentary | FALSE | FALSE | Not_TMED_Event | 1452
UTUADO | 2023-05-30 15:43 | 2023-05-30 18:53 | 80 | 3:10 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE NECESITA DESGANCHE | A23053000101 | New_Event | Vegetation Contact | Include | Include | Vegetation | 190 | 2023-05-30 | 15200 | keep | 0 | May | 2023 | 0.010353 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
FAJARDO | 2023-05-30 15:47 | 2023-05-30 17:40 | 20 | 1:53 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | R23053000077 | New_Event | Vegetation Contact | Include | Include | Vegetation | 113 | 2023-05-30 | 2260 | keep | 0 | May | 2023 | 0.0015393 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-30 15:48 | 2023-05-30 18:19 | 150 | 2:31 | P | DESGANCHE | 3 X 100 EN C/L DESGANCHE | S23053000138 | New_Event | Vegetation Contact | Include | Include | Vegetation | 151 | 2023-05-30 | 22650 | keep | 0 | May | 2023 | 0.015427 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-05-30 15:49 | 2023-05-30 15:51 | 842 | 0:02 | T | NO SE REPORTO CAUSA | CERRADO POR SCADA | S23053000139 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-05-30 | 1684 | keep | 0 | May | 2023 | 0.001147 | 0.00057348 | Momentary | FALSE | FALSE | Not_TMED_Event | 842
BARRANQUITAS | 2023-05-30 15:49 | 2023-05-30 16:53 | 1 | 1:04 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REEMPLAZO BAJANTE SECUNDARIO | C23053000249 | New_Event | Secondary Wire Break | Include | Include | Equipment | 64 | 2023-05-30 | 64 | keep | 0 | May | 2023 | 4.359e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-30 15:51 | 2023-05-30 17:56 | 362 | 2:05 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23053000140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-05-30 | 45250 | keep | 0 | May | 2023 | 0.03082 | 0.00024656 | Sustained | FALSE | FALSE | Not_TMED_Event | 362
FAJARDO | 2023-05-30 16:03 | 2023-05-30 16:21 | 15 | 0:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | R23053000080 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 18 | 2023-05-30 | 270 | keep | 0 | May | 2023 | 0.0001839 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-05-30 16:08 | 2023-05-30 17:14 | 2402 | 1:06 | T | DESGANCHE | DISPARO DE INTERRUPTOR SE SECCIONALIZO TRAMO BUSCANDO AVERIA Y SE CERRO POR SCADA BY-230530-03 | S23053000179 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-05-30 | 158532 | keep | 0 | May | 2023 | 0.10798 | 0.001636 | Sustained | FALSE | FALSE | Not_TMED_Event | 2402
BAYAMON | 2023-05-30 16:11 | 2023-05-31 09:29 | 118 | 17:18 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 50 EN C/L SE REEMPLAZO DISCO PARTIDO | B23053000264 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 1038 | 2023-05-30 | 122484 | keep | 0 | May | 2023 | 0.083423 | 8.0369e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 118
BAYAMON | 2023-05-30 16:14 | 2023-05-30 18:57 | 70 | 2:43 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE DE LINEA A CAJA | B23053000199 | New_Event | Primary Wire Break | Include | Include | Equipment | 163 | 2023-05-30 | 11410 | keep | 0 | May | 2023 | 0.0077713 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
AGUADILLA | 2023-05-30 16:15 | 2023-05-30 17:35 | 60 | 1:20 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23053000159 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 80 | 2023-05-30 | 4800 | keep | 0 | May | 2023 | 0.0032693 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
CANOVANAS | 2023-05-30 16:27 | 2023-05-30 17:15 | 278 | 0:48 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE ABRIO MACHETES PARA CERRAR PUENTES Y SE ENERGIZO | R23053000028 | Additional_clients | Primary Pole Failure | Include | Include | Equipment | 48 | 2023-05-30 | 13344 | keep | 0 | May | 2023 | 0.0090885 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
GUAYAMA | 2023-05-30 16:32 | 2023-05-30 18:53 | 1 | 2:21 | P | DESGANCHE | DESGANCHE EN VARIOS PUNTOS 1 X 200 EN CORTE DE LINEA | P23053000384 | New_Event | Vegetation Contact | Include | Include | Vegetation | 141 | 2023-05-30 | 141 | keep | 0 | May | 2023 | 9.6034e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-05-30 16:36 | 2023-05-30 18:00 | 8 | 1:24 | P | CAUSAS EXTERNAS | SE REPARO LA SECUNDARIA DE T-229 Y SE ENERGIZO EL XMR | R23053000064 | Partial_restoration | Damage From Public | Include | Include | Public | 84 | 2023-05-30 | 672 | keep | 0 | May | 2023 | 0.0004577 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-30 16:40 | 2023-05-30 19:00 | 60 | 2:20 | P | CONDUCTOR ROTO O ABIERTO | 1 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO Y SE CERRO CORTE DE LINEA PRINCIPAL | M23053000161 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 140 | 2023-05-30 | 8400 | keep | 0 | May | 2023 | 0.0057212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-05-30 17:06 | 2023-05-30 18:45 | 30 | 1:39 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASES | M23053000173 | New_Event | Animals | Include | Include | Wildlife | 99 | 2023-05-30 | 2970 | keep | 0 | May | 2023 | 0.0020229 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-05-30 17:10 | 2023-05-31 09:17 | 6 | 16:07 | P | DESGANCHE | DESGANCHE 1 X 30 EN CORTE DE LINEA | P23053000402 | New_Event | Vegetation Contact | Include | Include | Vegetation | 967 | 2023-05-30 | 5802 | keep | 0 | May | 2023 | 0.0039517 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
BAYAMON | 2023-05-30 17:14 | 2023-05-30 18:42 | 1230 | 1:28 | P | DESGANCHE | SE SECCIONALIZO TRAMO Y SE RETIRO RAMA SOBRE LINEA BY-230530-03 | S23053000179 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 88 | 2023-05-30 | 108240 | keep | 0 | May | 2023 | 0.073722 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-30 17:17 | 2023-05-30 19:12 | 20 | 1:55 | P | ANIMAL | 1 X 40 EN C/L CRUCE X AVE | C23053000310 | New_Event | Animals | Include | Include | Wildlife | 115 | 2023-05-30 | 2300 | keep | 0 | May | 2023 | 0.0015665 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
AGUADILLA | 2023-05-30 17:28 | 2023-05-30 19:30 | 70 | 2:02 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | M23053000178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 122 | 2023-05-30 | 8540 | keep | 0 | May | 2023 | 0.0058166 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
VEGA BAJA | 2023-05-30 17:29 | 2023-05-30 19:12 | 30 | 1:43 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A23053000126 | New_Event | Animals | Include | Include | Wildlife | 103 | 2023-05-30 | 3090 | keep | 0 | May | 2023 | 0.0021046 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-05-30 17:42 | 2023-05-30 17:51 | 14 | 0:09 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR IGUANA | B23053000174 | New_Event | Animals | Include | Include | Wildlife | 9 | 2023-05-30 | 126 | keep | 0 | May | 2023 | 8.5818e-05 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-05-30 17:53 | 2023-05-31 12:53 | 44 | 19:00 | P | DESGANCHE | 1 X 40 EN C/L Y DESGANCHE | S23053000194 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1140 | 2023-05-30 | 50160 | keep | 0 | May | 2023 | 0.034164 | 2.9968e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 44
FAJARDO | 2023-05-30 18:14 | 2023-05-30 18:32 | 5 | 0:18 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIAS | R23053000092 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 18 | 2023-05-30 | 90 | keep | 0 | May | 2023 | 6.1299e-05 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-05-30 18:22 | 2023-05-30 21:10 | 200 | 2:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA LLUVIA Y FUERTES VIENTOS | M23053000183 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 168 | 2023-05-30 | 33600 | keep | 0 | May | 2023 | 0.022885 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-05-30 18:29 | 2023-05-30 18:54 | 2484 | 0:25 | T | DESCONECTIVO DEFECTUOSO | SE CORRIGIO CIERRE DE AUX DE LINEA Y SE RECOMIENDA CAMBIARLO LUEGO Y SE CIERRA INTERRUPTOR | P23053000448 | New_Event | Switch Failure | Include | Include | Equipment | 25 | 2023-05-30 | 62100 | keep | 0 | May | 2023 | 0.042296 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
SAN JUAN | 2023-05-30 18:45 | 2023-05-30 23:21 | 147 | 4:36 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | S23053000217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 276 | 2023-05-30 | 40572 | keep | 0 | May | 2023 | 0.027633 | 0.00010012 | Sustained | FALSE | FALSE | Not_TMED_Event | 147
AGUADILLA | 2023-05-30 18:59 | 2023-05-31 10:55 | 1 | 15:56 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | M23053000184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 956 | 2023-05-30 | 956 | keep | 0 | May | 2023 | 0.00065113 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-30 19:06 | 2023-05-30 20:22 | 100 | 1:16 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23053000460 | New_Event | Animals | Include | Include | Wildlife | 76 | 2023-05-30 | 7600 | keep | 0 | May | 2023 | 0.0051763 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-05-30 19:07 | 2023-05-31 08:47 | 49 | 13:40 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23053000222 | New_Event | Vegetation Contact | Include | Include | Vegetation | 820 | 2023-05-30 | 40180 | keep | 0 | May | 2023 | 0.027366 | 3.3374e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 49
SAN JUAN | 2023-05-30 19:15 | 2023-05-30 21:15 | 1 | 2:00 | P | ARBOL SOBRE LINEA | SE RETIRO ARBOL SOBRE LINEA Y SE CERRO C/L. | S23053000223 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 120 | 2023-05-30 | 120 | keep | 0 | May | 2023 | 8.1731e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
MAYAGÃœEZ | 2023-05-30 19:25 | 2023-05-30 19:26 | 1097 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23053000187 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-30 | 1097 | keep | 0 | May | 2023 | 0.00074716 | 0.00074716 | Momentary | FALSE | FALSE | Not_TMED_Event | 1097
GUAYAMA | 2023-05-30 19:29 | 2023-05-31 09:44 | 20 | 14:15 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE ABIERTO Y 1 X 65 EN CORTE DE LINEA | P23053000470 | New_Event | Primary Wire Break | Include | Include | Equipment | 855 | 2023-05-30 | 17100 | keep | 0 | May | 2023 | 0.011647 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-05-30 19:34 | 2023-05-30 23:47 | 13 | 4:13 | P | CONDUCTOR ROTO O ABIERTO | REPARO BAJANTE DE LINEA A CAJA NO FUNDIO | C23053000376 | New_Event | Primary Wire Break | Include | Include | Equipment | 253 | 2023-05-30 | 3289 | keep | 0 | May | 2023 | 0.0022401 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
HUMACAO | 2023-05-30 19:35 | 2023-05-31 10:28 | 9 | 14:53 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 25 KVA X 25 KVA, NORMALIZO LOS TRIP SAVER | C23053000378 | New_Event | Service Transformer Failure | Include | Include | Equipment | 893 | 2023-05-30 | 8037 | keep | 0 | May | 2023 | 0.005474 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-05-30 19:44 | 2023-05-31 11:00 | 179 | 15:16 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO CONDUCTOR EN EL SUELO | S23053000230 | New_Event | Primary Wire Break | Include | Include | Equipment | 916 | 2023-05-30 | 163964 | keep | 0 | May | 2023 | 0.11168 | 0.00012192 | Sustained | FALSE | FALSE | Not_TMED_Event | 179
ARECIBO | 2023-05-30 19:48 | 2023-05-30 20:36 | 50 | 0:48 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23053000137 | New_Event | Animals | Include | Include | Wildlife | 48 | 2023-05-30 | 2400 | keep | 0 | May | 2023 | 0.0016346 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-30 19:49 | 2023-05-31 15:47 | 70 | 19:58 | P | DESGANCHE | SE LEVANTO CONDUCTOR Y DESGANCHE | B23053000263 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1198 | 2023-05-30 | 83860 | keep | 0 | May | 2023 | 0.057117 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
CANOVANAS | 2023-05-30 19:52 | 2023-05-30 20:58 | 75 | 1:06 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE EVENTO TRANSFERIDO DE PONCE. | P23053000478 | New_Event | Vegetation Contact | Include | Include | Vegetation | 66 | 2023-05-30 | 4950 | keep | 0 | May | 2023 | 0.0033714 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BARRANQUITAS | 2023-05-30 19:52 | 2023-05-31 16:22 | 13 | 20:30 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C23053000379 | New_Event | Service Transformer Failure | Include | Include | Equipment | 1230 | 2023-05-30 | 15990 | keep | 0 | May | 2023 | 0.010891 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
BARRANQUITAS | 2023-05-30 20:14 | 2023-05-31 11:30 | 17 | 15:16 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA DESGANCHE | C23053000381 | New_Event | Vegetation Contact | Include | Include | Vegetation | 916 | 2023-05-30 | 15572 | keep | 0 | May | 2023 | 0.010606 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
FAJARDO | 2023-05-30 20:33 | 2023-05-30 22:52 | 80 | 2:19 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN C/L LLUVIA | R23053000099 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 139 | 2023-05-30 | 11120 | keep | 0 | May | 2023 | 0.0075738 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
CANOVANAS | 2023-05-30 20:41 | 2023-05-31 10:43 | 57 | 14:02 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE DE BAMBUAS | R23053000383 | New_Event | Vegetation Contact | Include | Include | Vegetation | 842 | 2023-05-30 | 47994 | keep | 0 | May | 2023 | 0.032688 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
BAYAMON | 2023-05-30 20:48 | 2023-05-31 14:12 | 1 | 17:24 | P | DESGANCHE | 1 X 30 EN C/L DESGANCHE | B23053000272 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1044 | 2023-05-30 | 1044 | keep | 0 | May | 2023 | 0.00071106 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-30 21:47 | 2023-05-31 09:58 | 47 | 12:11 | P | DESGANCHE | 1 X 50 /CL Y DESGANCHE | S23053000253 | New_Event | Vegetation Contact | Include | Include | Vegetation | 731 | 2023-05-30 | 34357 | keep | 0 | May | 2023 | 0.0234 | 3.2011e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 47
ARECIBO | 2023-05-30 21:55 | 2023-05-31 09:10 | 15 | 11:15 | P | OTRAS CAUSAS | 1 X 25 EN TRANSFORMADOR FUSIBLE PODRIDO | A23053000149 | New_Event | Other Causes | Include | Include | Other | 675 | 2023-05-30 | 10125 | keep | 0 | May | 2023 | 0.0068961 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
AGUADILLA | 2023-05-30 21:57 | 2023-05-31 06:35 | 200 | 8:38 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN CORTE DE LINEA SE REPARO ALAMBRE PARTIDO | A23053000150 | New_Event | Primary Wire Break | Include | Include | Equipment | 518 | 2023-05-30 | 103600 | keep | 0 | May | 2023 | 0.070561 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
BAYAMON | 2023-05-30 21:59 | 2023-05-31 07:11 | 204 | 9:12 | P | NO SE REPORTO CAUSA | 1 X 25 EN PROVISIONAL AEREO Y 1 X 100 EN C/L | B23053000284 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 552 | 2023-05-30 | 112608 | keep | 0 | May | 2023 | 0.076697 | 0.00013894 | Sustained | FALSE | FALSE | Not_TMED_Event | 204
CANOVANAS | 2023-05-30 22:26 | 2023-05-31 09:56 | 18 | 11:30 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REEMPLAZO CAJA Y 1X 50 EN C/L | R23053000105 | New_Event | Cutout Failure | Include | Include | Equipment | 690 | 2023-05-30 | 12420 | keep | 0 | May | 2023 | 0.0084592 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-05-30 22:26 | 2023-05-31 02:30 | 288 | 4:04 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA | A23053000153 | New_Event | Primary Wire Break | Include | Include | Equipment | 244 | 2023-05-30 | 70272 | keep | 0 | May | 2023 | 0.047862 | 0.00019616 | Sustained | FALSE | FALSE | Not_TMED_Event | 288
BAYAMON | 2023-05-30 22:46 | 2023-05-30 22:47 | 4431 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO INTERRUPTOR | B23053000000 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-05-30 | 4431 | keep | 0 | May | 2023 | 0.0030179 | 0.0030179 | Momentary | FALSE | FALSE | Not_TMED_Event | 4431
BAYAMON | 2023-05-30 22:47 | 2023-05-31 03:55 | 383 | 5:08 | P | ALIMENTADOR AMARRADO | SE PATRULLO SE ENCONTRO PUENTE ABIERTO SE ESTABLECE GOI PARA REPARAR 80% POR 1717-03 | B23053000287 | New_Event | Feeder Load Transferred | Include | Include | Other | 308 | 2023-05-30 | 117964 | keep | 0 | May | 2023 | 0.080345 | 0.00026086 | Sustained | FALSE | FALSE | Not_TMED_Event | 383
BAYAMON | 2023-05-30 22:47 | 2023-05-31 03:55 | 1477 | 5:08 | P | CONDUCTOR ROTO O ABIERTO | SE PATRULLO SE ENCONTRO PUENTE ABIERTO SE ESTABLECE GOI PARA REPARAR LLEVA 80% DEL 1711-01 | B23053000287 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 308 | 2023-05-30 | 454916 | keep | 0 | May | 2023 | 0.30984 | 0.001006 | Sustained | FALSE | FALSE | Not_TMED_Event | 1477
VEGA BAJA | 2023-05-30 22:47 | 2023-05-31 02:00 | 150 | 3:13 | P | CONDUCTOR ROTO O ABIERTO | PUENTE PRIMARIO ABIERTO SE ABRIO CORTE DE LINEA PARA REPARAR | A23053000159 | New_Event | Primary Wire Break | Include | Include | Equipment | 193 | 2023-05-30 | 28950 | keep | 0 | May | 2023 | 0.019718 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
CAGUAS | 2023-05-30 23:06 | 2023-05-31 18:10 | 8 | 19:04 | P | NO SE REPORTO CAUSA | 1 RVA DE 10 AMP. EN EL SU-20 | C23053000394 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1144 | 2023-05-30 | 9152 | keep | 0 | May | 2023 | 0.0062334 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
YAUCO | 2023-05-30 23:09 | 2023-05-31 01:40 | 1352 | 2:31 | S | PROTECCION DEFECTUOSA | SE REPORTA PROBLEMA DE PROTECCION EN 5602-02 | P23053000553 | New_Event | Protection Miscoordination | Include | Include | Other | 151 | 2023-05-30 | 204152 | keep | 0 | May | 2023 | 0.13905 | 0.00092084 | Sustained | FALSE | FALSE | Not_TMED_Event | 1352
YAUCO | 2023-05-30 23:09 | 2023-05-31 02:40 | 3973 | 3:31 | S | DESGANCHE | RAMA SOBRE LINEAS | P23053000549 | New_Event | Vegetation Contact | Include | Include | Vegetation | 211 | 2023-05-30 | 838303 | keep | 0 | May | 2023 | 0.57096 | 0.002706 | Sustained | FALSE | FALSE | Not_TMED_Event | 3973
YAUCO | 2023-05-30 23:09 | 2023-05-31 01:40 | 2484 | 2:31 | S | PROTECCION DEFECTUOSA | SE REPORTA PROBLEMA DE PROTECCION EN 5602-02 | P23053000553 | New_Event | Protection Miscoordination | Include | Include | Other | 151 | 2023-05-30 | 375084 | keep | 0 | May | 2023 | 0.25547 | 0.0016918 | Sustained | FALSE | FALSE | Not_TMED_Event | 2484
BAYAMON | 2023-05-30 23:31 | 2023-05-31 01:43 | 139 | 2:12 | P | DESGANCHE | SE ABRE CORTE DE LINEA PARA REALIZAR DESGANCHE MASIVO REF.B23053000265 | B23053000296 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-05-30 | 18348 | keep | 0 | May | 2023 | 0.012497 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
CANOVANAS | 2023-05-31 00:05 | 2023-05-31 00:06 | 2708 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | R23053100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2708 | keep | 0 | May | 2023 | 0.0018444 | 0.0018444 | Momentary | FALSE | FALSE | Not_TMED_Event | 2708
VEGA BAJA | 2023-05-31 00:15 | 2023-05-31 14:00 | 8 | 13:45 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23053100001 | New_Event | Vegetation Contact | Include | Include | Vegetation | 825 | 2023-05-31 | 6600 | keep | 0 | May | 2023 | 0.0044952 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-31 00:27 | 2023-05-31 00:28 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23053100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2299 | keep | 0 | May | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-05-31 00:29 | 2023-05-31 00:30 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C23053100002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2299 | keep | 0 | May | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
VEGA BAJA | 2023-05-31 00:29 | 2023-05-31 03:39 | 50 | 3:10 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN CORTE DE LINEA SE REMPLAZO CAJA | B23053100007 | New_Event | Cutout Failure | Include | Include | Equipment | 190 | 2023-05-31 | 9500 | keep | 0 | May | 2023 | 0.0064704 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CAGUAS | 2023-05-31 00:48 | 2023-05-31 00:49 | 918 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23053100003 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-31 00:48 | 2023-05-31 00:49 | 1725 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23053100005 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 1725 | keep | 0 | May | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
HUMACAO | 2023-05-31 00:52 | 2023-05-31 00:53 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23053100004 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2299 | keep | 0 | May | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
CAGUAS | 2023-05-31 00:55 | 2023-05-31 00:56 | 853 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C23053100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 853 | keep | 0 | May | 2023 | 0.00058097 | 0.00058097 | Momentary | FALSE | FALSE | Not_TMED_Event | 853
HUMACAO | 2023-05-31 01:43 | 2023-05-31 01:46 | 3420 | 0:03 | T | DESGANCHE | DISPARO DE INTERRUPTOR CERRADO X CONTROL | C2305310000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 3 | 2023-05-31 | 10260 | keep | 0 | May | 2023 | 0.006988 | 0.0023293 | Momentary | FALSE | FALSE | Not_TMED_Event | 3420
HUMACAO | 2023-05-31 01:46 | 2023-05-31 08:40 | 493 | 6:54 | P | DESGANCHE | 2 X 80 EN CORTE DE LINEA DESGANCHE | C23053100029 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 414 | 2023-05-31 | 204102 | keep | 0 | May | 2023 | 0.13901 | 0.00033578 | Sustained | FALSE | FALSE | Not_TMED_Event | 493
VEGA BAJA | 2023-05-31 02:00 | 2023-05-31 02:25 | 370 | 0:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE PRIMARIO Y SE CERRO CORTE DE LINEA | A23053000159 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 25 | 2023-05-31 | 9250 | keep | 0 | May | 2023 | 0.0063001 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
HUMACAO | 2023-05-31 02:08 | 2023-05-31 02:09 | 3025 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2305310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 3025 | keep | 0 | May | 2023 | 0.0020603 | 0.0020603 | Momentary | FALSE | FALSE | Not_TMED_Event | 3025
CAGUAS | 2023-05-31 02:09 | 2023-05-31 07:25 | 170 | 5:16 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | C23053100012 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-05-31 | 53720 | keep | 0 | May | 2023 | 0.036588 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
FAJARDO | 2023-05-31 02:20 | 2023-05-31 02:21 | 3003 | 0:01 | T | DESGANCHE | RECIERRE DE INTERRUPTOR | R2305310000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-31 | 3003 | keep | 0 | May | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-05-31 02:21 | 2023-05-31 09:58 | 222 | 7:37 | P | DESGANCHE | 2 X 100 EN C/L Y DESGANCHE | R23053100004 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 457 | 2023-05-31 | 101454 | keep | 0 | May | 2023 | 0.0691 | 0.0001512 | Sustained | FALSE | FALSE | Not_TMED_Event | 222
AGUADILLA | 2023-05-31 02:25 | 2023-05-31 04:00 | 722 | 1:35 | P | CAUSAS EXTERNAS | SE RETIRO POSTE DE TELEFONO SOBRE EL ALIMENTADOR SE CERRO CORTE DE LINEA | M23053100005 | New_Event | Damage From Public | Include | Include | Public | 95 | 2023-05-31 | 68590 | keep | 0 | May | 2023 | 0.046716 | 0.00049175 | Sustained | FALSE | FALSE | Not_TMED_Event | 722
CAGUAS | 2023-05-31 03:30 | 2023-05-31 13:14 | 43 | 9:44 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN C/L MAL TIEMPO LLUVIA | C23053100014 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 584 | 2023-05-31 | 25112 | keep | 0 | May | 2023 | 0.017104 | 2.9287e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 43
BAYAMON | 2023-05-31 03:55 | 2023-05-31 05:20 | 1149 | 1:25 | P | ALIMENTADOR AMARRADO | SE CERRO PUENTE PRIMARIO ABIERTO 80% POR 1717-03 | B23053100025 | Additional_clients | Feeder Load Transferred | Include | Include | Other | 85 | 2023-05-31 | 97665 | keep | 0 | May | 2023 | 0.066519 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-31 03:55 | 2023-05-31 05:20 | 1111 | 1:25 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO ABIERTO LLEVA 80% DEL 1711-01 | B23053100020 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 85 | 2023-05-31 | 94435 | keep | 0 | May | 2023 | 0.064319 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-31 05:12 | 2023-05-31 14:03 | 16 | 8:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN CORTE DE LINEA Y 1 X 10 EN TRANSFORMADOR MAL TIEMPO LLUVIA | C23053100016 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 531 | 2023-05-31 | 8496 | keep | 0 | May | 2023 | 0.0057866 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
CAGUAS | 2023-05-31 05:15 | 2023-05-31 05:16 | 918 | 0:01 | T | UNIDAD SECCIONADORA (SWITCHING UNIT) | RECIERRE DE INTERRUPTOR | C23053100018 | New_Event | UG Switching Unit Failure | Include | Include | Equipment | 1 | 2023-05-31 | 918 | keep | 0 | May | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-05-31 05:16 | 2023-05-31 12:54 | 46 | 7:38 | P | UNIDAD SECCIONADORA (SWITCHING UNIT) | 3 X 100 EN C/L CONTAMINACION EN GABINETES SU-11/SU-10 | C23053100036 | 1st_after_momentary | UG Switching Unit Failure | Include | Include | Equipment | 458 | 2023-05-31 | 21068 | keep | 0 | May | 2023 | 0.014349 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
PONCE | 2023-05-31 05:51 | 2023-05-31 05:52 | 2696 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23053100028 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2696 | keep | 0 | May | 2023 | 0.0018362 | 0.0018362 | Momentary | FALSE | FALSE | Not_TMED_Event | 2696
ARECIBO | 2023-05-31 05:57 | 2023-05-31 09:58 | 35 | 4:01 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE RETIRO PARARRAYO CRUZADO | A23053100004 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 241 | 2023-05-31 | 8435 | keep | 0 | May | 2023 | 0.005745 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
HUMACAO | 2023-05-31 06:10 | 2023-05-31 06:11 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C23053100024 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2299 | keep | 0 | May | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-05-31 06:12 | 2023-05-31 06:13 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR | C23053100025 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2299 | keep | 0 | May | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
CANOVANAS | 2023-05-31 06:19 | 2023-05-31 08:34 | 30 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO BAJANTE SECUNDARIO | R23053100008 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2023-05-31 | 4050 | keep | 0 | May | 2023 | 0.0027584 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
MAYAGÃœEZ | 2023-05-31 06:20 | 2023-05-31 14:10 | 9 | 7:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA AVERIADA | M23053100006 | New_Event | Cutout Failure | Include | Include | Equipment | 470 | 2023-05-31 | 4230 | keep | 0 | May | 2023 | 0.002881 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BARRANQUITAS | 2023-05-31 06:25 | 2023-05-31 09:19 | 3565 | 2:54 | T | AISLADOR ROTO, PARTIDO O SAFADO | SJ-230531-01 INTERRUPTOR RECERRO QUEDO FUERA SE PROBO Y SE LLEVO LA SUBESTACION A LOCK OUT. SE CERRO N/O CON EL 3502-01 50% EN SERVICIO | C23053100028 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 174 | 2023-05-31 | 620310 | keep | 0 | May | 2023 | 0.42249 | 0.0024281 | Sustained | FALSE | FALSE | Not_TMED_Event | 3565
GUAYAMA | 2023-05-31 06:57 | 2023-05-31 10:42 | 30 | 3:45 | P | ANIMAL | 1 X 65 EN CORTE DE LINEA POR AVE | P23053100047 | New_Event | Animals | Include | Include | Wildlife | 225 | 2023-05-31 | 6750 | keep | 0 | May | 2023 | 0.0045974 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-05-31 07:04 | 2023-05-31 07:05 | 234 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23053100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 234 | keep | 0 | May | 2023 | 0.00015938 | 0.00015938 | Momentary | FALSE | FALSE | Not_TMED_Event | 234
PONCE | 2023-05-31 07:04 | 2023-05-31 07:05 | 2468 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23053100052 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2468 | keep | 0 | May | 2023 | 0.0016809 | 0.0016809 | Momentary | FALSE | FALSE | Not_TMED_Event | 2468
CANOVANAS | 2023-05-31 07:07 | 2023-05-31 10:05 | 30 | 2:58 | P | ANIMAL | 1 X 80 EN PROVISIONAL AEREO CRUCE POR AVE | R23053100011 | New_Event | Animals | Include | Include | Wildlife | 178 | 2023-05-31 | 5340 | keep | 0 | May | 2023 | 0.003637 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CAGUAS | 2023-05-31 07:14 | 2023-05-31 13:39 | 45 | 6:25 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | C23053100040 | New_Event | Animals | Include | Include | Wildlife | 385 | 2023-05-31 | 17325 | keep | 0 | May | 2023 | 0.0118 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
PONCE | 2023-05-31 07:24 | 2023-05-31 11:31 | 26 | 4:07 | P | ANIMAL | 1 X25 EN MONTURA POR AVE | P23053100060 | New_Event | Animals | Include | Include | Wildlife | 247 | 2023-05-31 | 6422 | keep | 0 | May | 2023 | 0.004374 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
BARRANQUITAS | 2023-05-31 07:26 | 2023-05-31 09:03 | 2565 | 1:37 | S | AISLADOR ROTO, PARTIDO O SAFADO | EN PRUEBA AL 3502-02 SE LLEVO LA SUBESTACION A LOCK OUT CG-230531-01. SE LEVANTO CONDUCTOR PRIMARIO DEBIDO A AISLADOR PARTIDO | C23053100044 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 97 | 2023-05-31 | 248805 | keep | 0 | May | 2023 | 0.16946 | 0.001747 | Sustained | FALSE | FALSE | Not_TMED_Event | 2565
SAN JUAN | 2023-05-31 07:33 | 2023-05-31 14:42 | 2 | 7:09 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 50 EN RISER SE REMPLAZO CAJA PRIMARIA EVENTO TRANSFERIDO | P23053100064 | New_Event | Cutout Failure | Include | Include | Equipment | 429 | 2023-05-31 | 858 | keep | 0 | May | 2023 | 0.00058438 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
YAUCO | 2023-05-31 07:54 | 2023-05-31 17:05 | 20 | 9:11 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | P23053100075 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 551 | 2023-05-31 | 11020 | keep | 0 | May | 2023 | 0.0075057 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-05-31 07:59 | 2023-05-31 12:04 | 312 | 4:05 | P | ANIMAL | 1 X 140 EN C/L CRUCE X AVE | C23053100060 | New_Event | Animals | Include | Include | Wildlife | 245 | 2023-05-31 | 76440 | keep | 0 | May | 2023 | 0.052063 | 0.0002125 | Sustained | FALSE | FALSE | Not_TMED_Event | 312
CANOVANAS | 2023-05-31 08:07 | 2023-05-31 13:34 | 1 | 5:27 | P | NO SE REPORTO CAUSA | 1 X 15 EN BANCO DE XMR | R23053100089 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 327 | 2023-05-31 | 327 | keep | 0 | May | 2023 | 0.00022272 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
GUAYAMA | 2023-05-31 08:08 | 2023-05-31 12:34 | 15 | 4:26 | P | DESGANCHE | DESGANCHE 1 X 50 EN CORTE DE LINEA | P23053100090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 266 | 2023-05-31 | 3990 | keep | 0 | May | 2023 | 0.0027176 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-31 08:18 | 2023-05-31 08:19 | 1310 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B23053100044 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 1310 | keep | 0 | May | 2023 | 0.00089224 | 0.00089224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1310
BARRANQUITAS | 2023-05-31 08:21 | 2023-05-31 08:22 | 598 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DE BKR 3405-03 SE CERRO POR CONTROL LLEVA 3403-01 | C23053100077 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-31 | 598 | keep | 0 | May | 2023 | 0.0004073 | 0.0004073 | Momentary | FALSE | FALSE | Not_TMED_Event | 598
BARRANQUITAS | 2023-05-31 08:21 | 2023-05-31 08:22 | 1001 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO DE BKR SE CERRO POR CONTROL LLEVA 3403-01 | C23053100077 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 1001 | keep | 0 | May | 2023 | 0.00068178 | 0.00068178 | Momentary | FALSE | FALSE | Not_TMED_Event | 1001
SAN JUAN | 2023-05-31 08:45 | 2023-05-31 13:12 | 5 | 4:27 | P | DESGANCHE | 1 X 100 C/L DESGANCHE | S23053100036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 267 | 2023-05-31 | 1335 | keep | 0 | May | 2023 | 0.00090926 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-05-31 08:45 | 2023-05-31 12:35 | 1 | 3:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA | P23053100114 | New_Event | Cutout Failure | Include | Include | Equipment | 230 | 2023-05-31 | 230 | keep | 0 | May | 2023 | 0.00015665 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
FAJARDO | 2023-05-31 08:48 | 2023-05-31 10:15 | 4 | 1:27 | P | ANIMAL | 1 X 10 EN XMR CRUCE POR AVE | R23053100115 | New_Event | Animals | Include | Include | Wildlife | 87 | 2023-05-31 | 348 | keep | 0 | May | 2023 | 0.00023702 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
PONCE | 2023-05-31 08:48 | 2023-05-31 10:44 | 2 | 1:56 | P | ANIMAL | 2 X 15 EN MONTURA POR AVE | P23053100118 | New_Event | Animals | Include | Include | Wildlife | 116 | 2023-05-31 | 232 | keep | 0 | May | 2023 | 0.00015801 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
MAYAGÃœEZ | 2023-05-31 08:48 | 2023-05-31 21:29 | 12 | 12:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23053100017 | New_Event | Vegetation Contact | Include | Include | Vegetation | 761 | 2023-05-31 | 9132 | keep | 0 | May | 2023 | 0.0062198 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
ARECIBO | 2023-05-31 08:51 | 2023-06-01 00:30 | 15 | 15:39 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR AVERIADO DE 50 KVA X 50 KVA | A23053100069 | New_Event | Service Transformer Failure | Include | Include | Equipment | 939 | 2023-05-31 | 14085 | keep | 0 | May | 2023 | 0.0095932 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
HUMACAO | 2023-05-31 08:53 | 2023-05-31 08:54 | 3902 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE BKR | C2305310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 3902 | keep | 0 | May | 2023 | 0.0026576 | 0.0026576 | Momentary | FALSE | FALSE | Not_TMED_Event | 3902
YAUCO | 2023-05-31 09:00 | 2023-06-01 07:45 | 70 | 22:45 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 80 EN CORTE DE LINEA SE DESENREDO LINEAS | M23053100173 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1365 | 2023-05-31 | 95550 | keep | 0 | May | 2023 | 0.065079 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
ARECIBO | 2023-05-31 09:11 | 2023-05-31 09:12 | 3431 | 0:01 | T | MAL TIEMPO/LLUVIA O VIENTO | RECIERRE DE INTERRUPTOR | A23053100022 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1 | 2023-05-31 | 3431 | keep | 0 | May | 2023 | 0.0023368 | 0.0023368 | Momentary | FALSE | FALSE | Not_TMED_Event | 3431
ARECIBO | 2023-05-31 09:12 | 2023-05-31 12:55 | 50 | 3:43 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA FUERTES VIENTOS | A23053100025 | 1st_after_momentary | Bad Weather (Rain & Wind) | Include | Include | Weather | 223 | 2023-05-31 | 11150 | keep | 0 | May | 2023 | 0.0075942 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-31 09:14 | 2023-05-31 16:16 | 1 | 7:02 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN BANCO DE XMR DESGANCHE SECUNDARIO | B23053100049 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 422 | 2023-05-31 | 422 | keep | 0 | May | 2023 | 0.00028742 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-31 09:15 | 2023-05-31 15:00 | 50 | 5:45 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | P23053100140 | New_Event | Vegetation Contact | Include | Include | Vegetation | 345 | 2023-05-31 | 17250 | keep | 0 | May | 2023 | 0.011749 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-05-31 09:19 | 2023-05-31 14:15 | 8 | 4:56 | P | SECUNDARIA/OTROS | SE ABRIO XMR Y SE REEMPLAZO PEDESTAL Y 3 BARRAS EN PESDESTAL | B23053100050 | New_Event |  |  |  |  | 296 | 2023-05-31 | 2368 | keep | 0 | May | 2023 | 0.0016128 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-05-31 09:19 | 2023-05-31 09:48 | 1782 | 0:29 | P | AISLADOR ROTO, PARTIDO O SAFADO | SJ-230531-01 INTERRUPTOR RECERRO QUEDO FUERA SE PROBO Y SE LLEVO LA SUBESTACION A LOCK OUT. SE CERRO N/O CON EL 3501-02 86% EN SERVICIO | C23053100028 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 29 | 2023-05-31 | 51678 | keep | 0 | May | 2023 | 0.035198 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
FAJARDO | 2023-05-31 09:24 | 2023-05-31 11:40 | 1 | 2:16 | P | DESGANCHE | 1 X 25 EN RISER Y DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23053100145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 136 | 2023-05-31 | 136 | keep | 0 | May | 2023 | 9.2629e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-31 09:27 | 2023-05-31 14:13 | 20 | 4:46 | P | ARBOL SOBRE LINEA | SE REPARO LINEA PRIMARIA PARTIDA Y SE RETIRO ARBOL | M23053100030 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 286 | 2023-05-31 | 5720 | keep | 0 | May | 2023 | 0.0038959 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
SAN JUAN | 2023-05-31 09:35 | 2023-05-31 16:27 | 8 | 6:52 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23053100047 | New_Event | Vegetation Contact | Include | Include | Vegetation | 412 | 2023-05-31 | 3296 | keep | 0 | May | 2023 | 0.0022449 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
HUMACAO | 2023-05-31 09:35 | 2023-05-31 12:43 | 1 | 3:08 | P | ANIMAL | 1 X 30 EN C/L CRUCE X AVE EVENTO TRANSFERIDO DE PONCE | P23053100158 | New_Event | Animals | Include | Include | Wildlife | 188 | 2023-05-31 | 188 | keep | 0 | May | 2023 | 0.00012805 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-05-31 09:41 | 2023-05-31 12:46 | 50 | 3:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA POR DESGANCHE | P23053100162 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-05-31 | 9250 | keep | 0 | May | 2023 | 0.0063001 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-05-31 09:48 | 2023-05-31 13:18 | 491 | 3:30 | P | AISLADOR ROTO, PARTIDO O SAFADO | SJ-230531-01 SE LEVANTO CONDUCTOR PRIMARIO DEBIDO A AISLADOR PARTIDO 100% EN SERVICIO | C23053100028 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 210 | 2023-05-31 | 103110 | keep | 0 | May | 2023 | 0.070228 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-05-31 09:50 | 2023-06-01 09:40 | 10 | 23:50 | P | DESGANCHE | 1 X 65 C/L Y DESGANCHE | S23053100169 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1430 | 2023-05-31 | 14300 | keep | 0 | May | 2023 | 0.0097397 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
HUMACAO | 2023-05-31 09:50 | 2023-05-31 12:15 | 1 | 2:25 | P | ANIMAL | 2 X 65 EN CORTE DE LINEA CRUCE POR AVE | C23053100168 | New_Event | Animals | Include | Include | Wildlife | 145 | 2023-05-31 | 145 | keep | 0 | May | 2023 | 9.8759e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CAGUAS | 2023-05-31 09:51 | 2023-05-31 09:52 | 6197 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | C2305310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 6197 | keep | 0 | May | 2023 | 0.0042207 | 0.0042207 | Momentary | FALSE | FALSE | Not_TMED_Event | 6197
ARECIBO | 2023-05-31 09:58 | 2023-05-31 09:59 | 2201 | 0:01 | T | PARARRAYOS DEFECTUOSO | RECIERRE DE INTERRUPTOR | A23053100040 | Additional_clients | Lightning Arrester Failure | Include | Include | Equipment | 1 | 2023-05-31 | 2201 | keep | 0 | May | 2023 | 0.0014991 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-05-31 09:59 | 2023-05-31 11:00 | 35 | 1:01 | P | PARARRAYOS DEFECTUOSO | 1 X 40 EN CORTE DE LINEA SE RETIRO PARARRAYO CRUZADO | A23053100004 | 1st_after_momentary | Lightning Arrester Failure | Include | Include | Equipment | 61 | 2023-05-31 | 2135 | keep | 0 | May | 2023 | 0.0014541 | 2.3838e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 35
MAYAGÃœEZ | 2023-05-31 10:06 | 2023-05-31 12:25 | 85 | 2:19 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA AVE CRUZO LINEAS | M23053100036 | New_Event | Animals | Include | Include | Wildlife | 139 | 2023-05-31 | 11815 | keep | 0 | May | 2023 | 0.0080471 | 5.7893e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 85
CANOVANAS | 2023-05-31 10:13 | 2023-05-31 18:50 | 2 | 8:37 | P | DESGANCHE | 1 X 25 EN TRANSFORMADOR DESGANCHE | R23053100052 | New_Event | Vegetation Contact | Include | Include | Vegetation | 517 | 2023-05-31 | 1034 | keep | 0 | May | 2023 | 0.00070425 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
FAJARDO | 2023-05-31 10:26 | 2023-05-31 12:00 | 50 | 1:34 | P | CONDUCTOR ROTO O ABIERTO | SE REMPLAZO BAJANTE DE LINEA A CAJA 1 X 40 C/L 1 X 50 EN C/L | R23053100048 | New_Event | Primary Wire Break | Include | Include | Equipment | 94 | 2023-05-31 | 4700 | keep | 0 | May | 2023 | 0.0032011 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-31 10:51 | 2023-05-31 13:15 | 25 | 2:24 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | M23053100053 | New_Event | Vegetation Contact | Include | Include | Vegetation | 144 | 2023-05-31 | 3600 | keep | 0 | May | 2023 | 0.0024519 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BARRANQUITAS | 2023-05-31 10:57 | 2023-05-31 16:13 | 75 | 5:16 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE REALIZO DESGANCHE | C23053100164 | New_Event | Vegetation Contact | Include | Include | Vegetation | 316 | 2023-05-31 | 23700 | keep | 0 | May | 2023 | 0.016142 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-05-31 11:00 | 2023-05-31 12:40 | 739 | 1:40 | P | CONDUCTOR ROTO O ABIERTO | SE LEVANTO CONDUCTOR PRIMARIO | S23053000230 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 100 | 2023-05-31 | 73900 | keep | 0 | May | 2023 | 0.050333 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BARRANQUITAS | 2023-05-31 11:10 | 2023-05-31 16:33 | 1 | 5:23 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA DESGANCHE | C23053100167 | New_Event | Vegetation Contact | Include | Include | Vegetation | 323 | 2023-05-31 | 323 | keep | 0 | May | 2023 | 0.00021999 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-05-31 11:36 | 2023-05-31 13:55 | 20 | 2:19 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO RAMA | P23053100231 | New_Event | Vegetation Contact | Include | Include | Vegetation | 139 | 2023-05-31 | 2780 | keep | 0 | May | 2023 | 0.0018934 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
PONCE | 2023-05-31 11:44 | 2023-05-31 13:35 | 50 | 1:51 | P | ANIMAL | 2 X 50 EN CORTE DE LINEA POR AVE | P23053100237 | New_Event | Animals | Include | Include | Wildlife | 111 | 2023-05-31 | 5550 | keep | 0 | May | 2023 | 0.0037801 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
AGUADILLA | 2023-05-31 11:44 | 2023-05-31 13:40 | 200 | 1:56 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 65 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | M23053100064 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 116 | 2023-05-31 | 23200 | keep | 0 | May | 2023 | 0.015801 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
CANOVANAS | 2023-05-31 11:45 | 2023-05-31 12:46 | 12 | 1:01 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23053100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 61 | 2023-05-31 | 732 | keep | 0 | May | 2023 | 0.00049856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
GUAYAMA | 2023-05-31 11:57 | 2023-05-31 14:11 | 10 | 2:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23053100243 | New_Event | Secondary Wire Break | Include | Include | Equipment | 134 | 2023-05-31 | 1340 | keep | 0 | May | 2023 | 0.00091267 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CAGUAS | 2023-05-31 12:19 | 2023-05-31 14:45 | 98 | 2:26 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA CRUCE POR AVE | C23053100195 | New_Event | Animals | Include | Include | Wildlife | 146 | 2023-05-31 | 14308 | keep | 0 | May | 2023 | 0.0097451 | 6.6747e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 98
SAN JUAN | 2023-05-31 12:21 | 2023-05-31 16:01 | 68 | 3:40 | P | DESGANCHE | SE REALIZO DESGANCHE RAMAS EN FUEGO Y SE CERRO C/L | S23053100255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 220 | 2023-05-31 | 14960 | keep | 0 | May | 2023 | 0.010189 | 4.6314e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 68
SAN JUAN | 2023-05-31 12:26 | 2023-05-31 13:00 | 2 | 0:34 | P | DESGANCHE | 2 X 100 EN C/L Y DESGANCHE | S23053100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2023-05-31 | 68 | keep | 0 | May | 2023 | 4.6314e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-05-31 12:28 | 2023-05-31 15:38 | 197 | 3:10 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE CAJA A LINEA | C23053100198 | New_Event | Primary Wire Break | Include | Include | Equipment | 190 | 2023-05-31 | 37430 | keep | 0 | May | 2023 | 0.025493 | 0.00013418 | Sustained | FALSE | FALSE | Not_TMED_Event | 197
VEGA BAJA | 2023-05-31 12:30 | 2023-05-31 13:31 | 12 | 1:01 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR PARA REPARAR SECUNDARIA Y DESGANCHE | B23053100086 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 61 | 2023-05-31 | 732 | keep | 0 | May | 2023 | 0.00049856 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-05-31 12:38 | 2023-05-31 18:49 | 6 | 6:11 | P | SECUNDARIA/DESGANCHE | 1 X 15 EN XMR DESGANCHE SECUNDARIO | S23053100080 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 371 | 2023-05-31 | 2226 | keep | 0 | May | 2023 | 0.0015161 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
GUAYAMA | 2023-05-31 12:45 | 2023-05-31 18:50 | 10 | 6:05 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA | P23053100267 | New_Event | Secondary Wire Break | Include | Include | Equipment | 365 | 2023-05-31 | 3650 | keep | 0 | May | 2023 | 0.002486 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
SAN JUAN | 2023-05-31 12:46 | 2023-05-31 14:35 | 1 | 1:49 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L Y SE REMPLAZO PORTA FUSIBLE MAL TIEMPO EVENTO TRANSFERIDO | P23053100268 | New_Event | Cutout Failure | Include | Include | Equipment | 109 | 2023-05-31 | 109 | keep | 0 | May | 2023 | 7.4239e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-05-31 12:55 | 2023-05-31 12:56 | 29 | 0:01 | T | DESGANCHE | DISPARO CERRADO POR CONTROL LLEVA 1345-03 LLEVA 1345-01 LLEVA 1345-02 | S23053100086 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-31 | 29 | keep | 0 | May | 2023 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-05-31 12:55 | 2023-05-31 12:56 | 660 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1342-03 CARGA POR 1342-03 | S23053100086 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-31 | 660 | keep | 0 | May | 2023 | 0.00044952 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-05-31 12:55 | 2023-05-31 12:56 | 435 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1342-03 CARGA POR 1342-03 | S23053100086 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-31 | 435 | keep | 0 | May | 2023 | 0.00029628 | 0.00029628 | Momentary | FALSE | FALSE | Not_TMED_Event | 435
SAN JUAN | 2023-05-31 12:55 | 2023-05-31 12:56 | 259 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO DEL 1342-03 CARGA POR 1342-03 | S23053100086 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-31 | 259 | keep | 0 | May | 2023 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-05-31 12:56 | 2023-05-31 15:00 | 74 | 2:04 | P | DESGANCHE | 1 X 100 EN C/L SE REALIZO DESGANCHE | S23053100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 124 | 2023-05-31 | 9176 | keep | 0 | May | 2023 | 0.0062497 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
UTUADO | 2023-05-31 12:56 | 2023-05-31 17:10 | 8 | 4:14 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1 X 15 EN TRANSFORMADOR SE REPARO SECUNDARIA AVERIADA | A23053100079 | New_Event | Secondary Wire Break | Include | Include | Equipment | 254 | 2023-05-31 | 2032 | keep | 0 | May | 2023 | 0.001384 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-05-31 12:59 | 2023-05-31 13:00 | 2770 | 0:01 | T | DESGANCHE | RECIERRE DE BKR | C23053100203 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-31 | 2770 | keep | 0 | May | 2023 | 0.0018866 | 0.0018866 | Momentary | FALSE | FALSE | Not_TMED_Event | 2770
BARRANQUITAS | 2023-05-31 13:00 | 2023-05-31 15:35 | 182 | 2:35 | P | DESGANCHE | 2 X 100 EN CORTE DE LINEA SE RETIRO BAMBUAS DE LA LINEA | C23053100206 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 155 | 2023-05-31 | 28210 | keep | 0 | May | 2023 | 0.019214 | 0.00012396 | Sustained | FALSE | FALSE | Not_TMED_Event | 182
BAYAMON | 2023-05-31 13:23 | 2023-05-31 13:57 | 30 | 0:34 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23053100095 | New_Event | Vegetation Contact | Include | Include | Vegetation | 34 | 2023-05-31 | 1020 | keep | 0 | May | 2023 | 0.00069472 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-05-31 13:40 | 2023-05-31 14:59 | 180 | 1:19 | P | CONDUCTOR ROTO O ABIERTO | SJ-230531-51 SE SECCIONALIZO ALIMENTADOR PARA LEVANTAR CONDUCTOR EN EL SUELO | R23053100059 | New_Event | Primary Wire Break | Include | Include | Equipment | 79 | 2023-05-31 | 14220 | keep | 0 | May | 2023 | 0.0096852 | 0.0001226 | Sustained | FALSE | FALSE | Not_TMED_Event | 180
MAYAGÃœEZ | 2023-05-31 13:40 | 2023-06-01 14:59 | 50 | 25:19 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE MASIVO | M23053100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1519 | 2023-05-31 | 75950 | keep | 0 | May | 2023 | 0.051729 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-05-31 13:46 | 2023-05-31 14:51 | 2067 | 1:05 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR SE VERIFICO PERSONAL FUERA Y SE CERRO INTERRUPTOR | M23053100087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 65 | 2023-05-31 | 134355 | keep | 0 | May | 2023 | 0.091509 | 0.0014078 | Sustained | FALSE | FALSE | Not_TMED_Event | 2067
SAN JUAN | 2023-05-31 13:49 | 2023-05-31 15:30 | 10 | 1:41 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR SE REMPLAZARON BARRAS EN PEDESTAL | S23053100099 | New_Event | Secondary Wire Break | Include | Include | Equipment | 101 | 2023-05-31 | 1010 | keep | 0 | May | 2023 | 0.00068791 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-31 13:51 | 2023-05-31 15:07 | 15 | 1:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJA PRIMARIA DEL TRANSFORMADOR PARA REEMPLAZAR 3 BARRAS EN PEDESTAL | C23053100222 | New_Event | Secondary Wire Break | Include | Include | Equipment | 76 | 2023-05-31 | 1140 | keep | 0 | May | 2023 | 0.00077645 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
VEGA BAJA | 2023-05-31 13:53 | 2023-05-31 15:55 | 20 | 2:02 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA 1 X 15 EN TRANSFORMADOR AVE CRUZO LINEAS | A23053100093 | New_Event | Animals | Include | Include | Wildlife | 122 | 2023-05-31 | 2440 | keep | 0 | May | 2023 | 0.0016619 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
HUMACAO | 2023-05-31 13:59 | 2023-05-31 17:45 | 26 | 3:46 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO TRANSFORMADOR DE 37.5 KVA X 37.5 KVA | C23053100225 | New_Event | Service Transformer Failure | Include | Include | Equipment | 226 | 2023-05-31 | 5876 | keep | 0 | May | 2023 | 0.0040021 | 1.7708e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 26
HUMACAO | 2023-05-31 14:11 | 2023-05-31 15:56 | 15 | 1:45 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR CHANGO | C23053100228 | New_Event | Animals | Include | Include | Wildlife | 105 | 2023-05-31 | 1575 | keep | 0 | May | 2023 | 0.0010727 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
PONCE | 2023-05-31 14:44 | 2023-05-31 14:45 | 3744 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23053100323 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 3744 | keep | 0 | May | 2023 | 0.00255 | 0.00255 | Momentary | FALSE | FALSE | Not_TMED_Event | 3744
GUAYAMA | 2023-05-31 15:00 | 2023-05-31 18:27 | 100 | 3:27 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L SE REMPLAZO CAJA EN C/L | P23053100329 | New_Event | Cutout Failure | Include | Include | Equipment | 207 | 2023-05-31 | 20700 | keep | 0 | May | 2023 | 0.014099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
ARECIBO | 2023-05-31 15:04 | 2023-05-31 17:25 | 75 | 2:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA QUEMADA EN CORTE DE LINEA | A23053100103 | New_Event | Cutout Failure | Include | Include | Equipment | 141 | 2023-05-31 | 10575 | keep | 0 | May | 2023 | 0.0072026 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
CANOVANAS | 2023-05-31 15:12 | 2023-05-31 17:55 | 2 | 2:43 | P | DESGANCHE | 1 X 65 EN XMR DESGANCHE | R23053100075 | New_Event | Vegetation Contact | Include | Include | Vegetation | 163 | 2023-05-31 | 326 | keep | 0 | May | 2023 | 0.00022204 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-05-31 15:15 | 2023-05-31 16:48 | 20 | 1:33 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | B23053100111 | Partial_restoration | Vegetation Contact | Include | Include | Vegetation | 93 | 2023-05-31 | 1860 | keep | 0 | May | 2023 | 0.0012668 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-05-31 15:21 | 2023-06-01 09:08 | 57 | 17:47 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23053100116 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1067 | 2023-05-31 | 60819 | keep | 0 | May | 2023 | 0.041424 | 3.8822e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 57
SAN JUAN | 2023-05-31 15:25 | 2023-06-01 08:57 | 39 | 17:32 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23053100118 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1052 | 2023-05-31 | 41028 | keep | 0 | May | 2023 | 0.027944 | 2.6563e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 39
CAGUAS | 2023-05-31 15:25 | 2023-05-31 19:36 | 48 | 4:11 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA DE LA LINEA | C23053100256 | New_Event | Vegetation Contact | Include | Include | Vegetation | 251 | 2023-05-31 | 12048 | keep | 0 | May | 2023 | 0.0082058 | 3.2693e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 48
CAGUAS | 2023-05-31 15:26 | 2023-05-31 20:58 | 90 | 5:32 | P | NO SE REPORTO CAUSA | 1 X 80 EN CORTE DE LINEA | C23053100257 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 332 | 2023-05-31 | 29880 | keep | 0 | May | 2023 | 0.020351 | 6.1299e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 90
SAN JUAN | 2023-05-31 15:30 | 2023-05-31 18:27 | 46 | 2:57 | P | NO SE REPORTO CAUSA | 2 X 80 EN RISER Y 2 X 100 EN C/L | S23053100124 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 177 | 2023-05-31 | 8142 | keep | 0 | May | 2023 | 0.0055455 | 3.133e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 46
SAN JUAN | 2023-05-31 15:52 | 2023-05-31 20:09 | 32 | 4:17 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23053100132 | New_Event | Vegetation Contact | Include | Include | Vegetation | 257 | 2023-05-31 | 8224 | keep | 0 | May | 2023 | 0.0056013 | 2.1795e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 32
SAN JUAN | 2023-05-31 15:52 | 2023-05-31 15:53 | 390 | 0:01 | T | DESGANCHE | RECIERRE | S23053100133 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-31 | 390 | keep | 0 | May | 2023 | 0.00026563 | 0.00026563 | Momentary | FALSE | FALSE | Not_TMED_Event | 390
MAYAGÃœEZ | 2023-05-31 15:52 | 2023-06-01 11:15 | 350 | 19:23 | P | CONDUCTOR ROTO O ABIERTO | PUENTE ABIERTO | M23053100117 | New_Event | Primary Wire Break | Include | Include | Equipment | 1163 | 2023-05-31 | 407050 | keep | 0 | May | 2023 | 0.27724 | 0.00023838 | Sustained | FALSE | FALSE | Not_TMED_Event | 350
SAN JUAN | 2023-05-31 15:53 | 2023-05-31 18:26 | 170 | 2:33 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | S23053100155 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-05-31 | 26010 | keep | 0 | May | 2023 | 0.017715 | 0.00011579 | Sustained | FALSE | FALSE | Not_TMED_Event | 170
SAN JUAN | 2023-05-31 15:57 | 2023-05-31 19:02 | 1 | 3:05 | P | SECUNDARIA/DESGANCHE | 1 X 20 EN XMR DESGANCHE SECUNDARIO | S23053100134 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 185 | 2023-05-31 | 185 | keep | 0 | May | 2023 | 0.000126 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-31 16:06 | 2023-05-31 20:34 | 150 | 4:28 | P | DESGANCHE | SE REPARO LINEA PRIMARIA ROTA | M23053100120 | New_Event | Vegetation Contact | Include | Include | Vegetation | 268 | 2023-05-31 | 40200 | keep | 0 | May | 2023 | 0.02738 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BARRANQUITAS | 2023-05-31 16:07 | 2023-05-31 18:20 | 9 | 2:13 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO RAMA DE LA SECUNDARIA | C23053100267 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 133 | 2023-05-31 | 1197 | keep | 0 | May | 2023 | 0.00081527 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-05-31 16:09 | 2023-05-31 19:46 | 30 | 3:37 | P | NO SE REPORTO CAUSA | 1 X 65 EN C/L | S23053100145 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 217 | 2023-05-31 | 6510 | keep | 0 | May | 2023 | 0.0044339 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-05-31 16:12 | 2023-05-31 17:56 | 159 | 1:44 | P | ANIMAL | 2 X 40 EN CORTE DE LINEA CRUCE POR CHANGO | C23053100269 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-05-31 | 16536 | keep | 0 | May | 2023 | 0.011263 | 0.00010829 | Sustained | FALSE | FALSE | Not_TMED_Event | 159
ARECIBO | 2023-05-31 16:32 | 2023-06-01 15:30 | 6 | 22:58 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 20 EN CORTE DE LINEA SE REPARO LINEAS PRIMARIAS CRUZADAS | A23053100110 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 1378 | 2023-05-31 | 8268 | keep | 0 | May | 2023 | 0.0056313 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
SAN JUAN | 2023-05-31 16:33 | 2023-05-31 17:30 | 7 | 0:57 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23053100158 | New_Event | Secondary Wire Break | Include | Include | Equipment | 57 | 2023-05-31 | 399 | keep | 0 | May | 2023 | 0.00027176 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CAGUAS | 2023-05-31 16:33 | 2023-05-31 19:06 | 74 | 2:33 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA SE RETIRO CHANGO DE PARARRAYO | C23053100275 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-05-31 | 11322 | keep | 0 | May | 2023 | 0.0077114 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
MAYAGÃœEZ | 2023-05-31 16:53 | 2023-05-31 20:06 | 25 | 3:13 | P | ARBOL SOBRE LINEA | 2 X 50 EN CORTE DE LINEA SE RETIRO ARBOL SOBRE LAS LINEAS | M23053100131 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 193 | 2023-05-31 | 4825 | keep | 0 | May | 2023 | 0.0032863 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-05-31 17:04 | 2023-05-31 17:05 | 2956 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | B2305310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2956 | keep | 0 | May | 2023 | 0.0020133 | 0.0020133 | Momentary | FALSE | FALSE | Not_TMED_Event | 2956
ARECIBO | 2023-05-31 17:08 | 2023-05-31 19:30 | 40 | 2:22 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO SE REPORTO CAUSA | A23053100123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 142 | 2023-05-31 | 5680 | keep | 0 | May | 2023 | 0.0038686 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-05-31 17:35 | 2023-05-31 19:10 | 10 | 1:35 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO TRANSFORMADOR PARA REPARAR BAJANTES SECUNDARIOS | A23053100124 | New_Event | Secondary Wire Break | Include | Include | Equipment | 95 | 2023-05-31 | 950 | keep | 0 | May | 2023 | 0.00064704 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BARRANQUITAS | 2023-05-31 17:37 | 2023-05-31 20:00 | 9 | 2:23 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN TRANSFORMADOR SE RETIRO ENREDADERA | C23053100285 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 143 | 2023-05-31 | 1287 | keep | 0 | May | 2023 | 0.00087657 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
CANOVANAS | 2023-05-31 17:47 | 2023-05-31 19:19 | 40 | 1:32 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | R23053100087 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-05-31 | 3680 | keep | 0 | May | 2023 | 0.0025064 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-05-31 17:53 | 2023-06-01 15:00 | 15 | 21:07 | P | MAL TIEMPO/RAYOS | 1 X 10 EN TRANSFORMADOR MAL TIEMPO DESCARGAS ELECTRICAS | A23053100129 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 1267 | 2023-05-31 | 19005 | keep | 0 | May | 2023 | 0.012944 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
CANOVANAS | 2023-05-31 18:02 | 2023-05-31 18:03 | 1648 | 0:01 | T | DESGANCHE | RECIERRE | R2305310000X | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-05-31 | 1648 | keep | 0 | May | 2023 | 0.0011224 | 0.0011224 | Momentary | FALSE | FALSE | Not_TMED_Event | 1648
CANOVANAS | 2023-05-31 18:03 | 2023-05-31 21:05 | 31 | 3:02 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | R23053100093 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 182 | 2023-05-31 | 5642 | keep | 0 | May | 2023 | 0.0038427 | 2.1114e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 31
BAYAMON | 2023-05-31 18:05 | 2023-06-01 09:00 | 8 | 14:55 | P | DESGANCHE | 1 X 40 C/L DESGANCHE | B23053100130 | New_Event | Vegetation Contact | Include | Include | Vegetation | 895 | 2023-05-31 | 7160 | keep | 0 | May | 2023 | 0.0048766 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
AGUADILLA | 2023-05-31 18:17 | 2023-05-31 19:24 | 60 | 1:07 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23053100146 | New_Event | Animals | Include | Include | Wildlife | 67 | 2023-05-31 | 4020 | keep | 0 | May | 2023 | 0.002738 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
HUMACAO | 2023-05-31 18:25 | 2023-05-31 18:50 | 2 | 0:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRE XMR Y SE REPARA BARRA EN PEDESTAL | C23053100303 | New_Event | Secondary Wire Break | Include | Include | Equipment | 25 | 2023-05-31 | 50 | keep | 0 | May | 2023 | 3.4055e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
SAN JUAN | 2023-05-31 18:58 | 2023-05-31 18:59 | 837 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO 1401-07 Y LLEVA 1401-06 SE CERRO POR SCADA | S23053100186 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-05-31 | 837 | keep | 0 | May | 2023 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-05-31 18:58 | 2023-05-31 18:59 | 908 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO 1401-07 Y LLEVA 1401-06 SE CERRO POR SCADA | S23053100186 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 908 | keep | 0 | May | 2023 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
BARRANQUITAS | 2023-05-31 19:00 | 2023-05-31 19:05 | 373 | 0:05 | P | AISLADOR ROTO, PARTIDO O SAFADO | SE VERIFICO PERSONAL FUERA CERRADO POR CONTROL CARGA TRANSFERIDA POR VIA LIBRE | C23053100316 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 5 | 2023-05-31 | 1865 | keep | 0 | May | 2023 | 0.0012702 | 0.00025405 | Momentary | FALSE | FALSE | Not_TMED_Event | 373
BARRANQUITAS | 2023-05-31 19:05 | 2023-05-31 19:28 | 140 | 0:23 | P | AISLADOR ROTO, PARTIDO O SAFADO | DISPARO INTERRUPTOR LLEVA SOLO 10% DE SU CARGA POR VIA LIBRE D2023-4152, SE REEMPLAZO AISLADOR Y PIN POLE TOP AVERIADO | C23053100317 | Partial_restoration | Insulator/ Pin Failure | Include | Include | Equipment | 23 | 2023-05-31 | 3220 | keep | 0 | May | 2023 | 0.0021931 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-05-31 19:10 | 2023-05-31 20:43 | 91 | 1:33 | P | ANIMAL | 1 X 50 EN C/L CRUCE POR AVE | R23053100107 | New_Event | Animals | Include | Include | Wildlife | 93 | 2023-05-31 | 8463 | keep | 0 | May | 2023 | 0.0057641 | 6.198e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 91
AGUADILLA | 2023-05-31 19:11 | 2023-06-01 09:25 | 3 | 14:14 | P | MAL TIEMPO/RAYOS | 1 X 65 EN CORTE DE LINEA DESCARGAS ELECTRICAS | M23053100155 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 854 | 2023-05-31 | 2562 | keep | 0 | May | 2023 | 0.001745 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
SAN JUAN | 2023-05-31 19:13 | 2023-05-31 23:27 | 24 | 4:14 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 80 1 X 65 Y 1 X 50 EN RISERSE REEMPLAZO CAJA PRIMARIA Y SE REPARO PUENTE PRIMARIO | S23053100188 | New_Event | Cutout Failure | Include | Include | Equipment | 254 | 2023-05-31 | 6096 | keep | 0 | May | 2023 | 0.004152 | 1.6346e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 24
CAGUAS | 2023-05-31 19:17 | 2023-05-31 19:18 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO INTERRUPTOR EN SERVICIO | C2305310000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 2178 | keep | 0 | May | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
BAYAMON | 2023-05-31 19:20 | 2023-06-01 14:20 | 8 | 19:00 | P | ANIMAL | 1 X 15 EN XMR CRUCE DE AVE | B23053100138 | New_Event | Animals | Include | Include | Wildlife | 1140 | 2023-05-31 | 9120 | keep | 0 | May | 2023 | 0.0062116 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
VEGA BAJA | 2023-05-31 19:21 | 2023-05-31 21:18 | 130 | 1:57 | P | ANIMAL | 1 X 50 EN C/L CRUCE X AVE | B23053100140 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-05-31 | 15210 | keep | 0 | May | 2023 | 0.010359 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
PONCE | 2023-05-31 19:36 | 2023-06-01 07:20 | 16 | 11:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO CONEXIONES EN PEDESTAL SECUNDARIO | P23053100447 | New_Event | Secondary Wire Break | Include | Include | Equipment | 704 | 2023-05-31 | 11264 | keep | 0 | May | 2023 | 0.0076719 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
HUMACAO | 2023-05-31 19:52 | 2023-06-01 08:04 | 10 | 12:12 | P | ANIMAL | 1 X 20 EN XMR CRUCE X AVE | C23053100329 | New_Event | Animals | Include | Include | Wildlife | 732 | 2023-05-31 | 7320 | keep | 0 | May | 2023 | 0.0049856 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-05-31 20:00 | 2023-05-31 21:26 | 130 | 1:26 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | B23053100145 | New_Event | Vegetation Contact | Include | Include | Vegetation | 86 | 2023-05-31 | 11180 | keep | 0 | May | 2023 | 0.0076146 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
CANOVANAS | 2023-05-31 20:04 | 2023-05-31 21:45 | 15 | 1:41 | P | NO SE REPORTO CAUSA | 1 X 10 EN XMR NO CAUSA | R23053100119 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 101 | 2023-05-31 | 1515 | keep | 0 | May | 2023 | 0.0010319 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-05-31 20:05 | 2023-06-01 03:10 | 139 | 7:05 | P | CONDUCTOR ROTO O ABIERTO | CONDUCTOR PRIMARIO VIVO EN EL SUELO TRASPATIO SE DEJO CONDUCTOR SECCIONALIZADO Y TAG | S23053100208 | New_Event | Primary Wire Break | Include | Include | Equipment | 425 | 2023-05-31 | 59075 | keep | 0 | May | 2023 | 0.040236 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
BAYAMON | 2023-05-31 20:16 | 2023-06-01 03:21 | 117 | 7:05 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA POR DESGANCHE | S23053100211 | New_Event | Vegetation Contact | Include | Include | Vegetation | 425 | 2023-05-31 | 49725 | keep | 0 | May | 2023 | 0.033867 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
VEGA BAJA | 2023-05-31 20:50 | 2023-06-01 11:00 | 20 | 14:10 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23053100152 | New_Event | Vegetation Contact | Include | Include | Vegetation | 850 | 2023-05-31 | 17000 | keep | 0 | May | 2023 | 0.011579 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
ARECIBO | 2023-05-31 20:56 | 2023-05-31 23:25 | 55 | 2:29 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA REQUIERE DESGANCHE | A23053100158 | New_Event | Vegetation Contact | Include | Include | Vegetation | 149 | 2023-05-31 | 8195 | keep | 0 | May | 2023 | 0.0055816 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2023-05-31 21:20 | 2023-06-01 08:15 | 20 | 10:55 | P | CAUSAS EXTERNAS | 1 X 15 EN XMR Y 1 50 EN C/L SE RETIRO GLOBO | C23053100334 | New_Event | Damage From Public | Include | Include | Public | 655 | 2023-05-31 | 13100 | keep | 0 | May | 2023 | 0.0089224 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-05-31 21:40 | 2023-06-01 00:25 | 80 | 2:45 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23053100186 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 165 | 2023-05-31 | 13200 | keep | 0 | May | 2023 | 0.0089905 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
AGUADILLA | 2023-05-31 21:48 | 2023-06-01 10:30 | 300 | 12:42 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA REQUIERE DESGANCHE | M23053100190 | New_Event | Vegetation Contact | Include | Include | Vegetation | 762 | 2023-05-31 | 228600 | keep | 0 | May | 2023 | 0.1557 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-05-31 21:57 | 2023-06-01 01:35 | 100 | 3:38 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 80 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | A23053100198 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 218 | 2023-05-31 | 21800 | keep | 0 | May | 2023 | 0.014848 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
AGUADILLA | 2023-05-31 22:32 | 2023-06-01 10:05 | 1 | 11:33 | P | PROBLEMA DEL CLIENTE | 1 X 20 EN TRANSFORMADOR "MAIN BREAKER" QUEMADO | M23053100212 | New_Event | Customer-Related Interruption | Include | Include | Public | 693 | 2023-05-31 | 693 | keep | 0 | May | 2023 | 0.000472 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-05-31 22:46 | 2023-06-01 11:25 | 3 | 12:39 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE ZAFADO EN TRANSFORMADOR | M23053100219 | New_Event | Primary Wire Break | Include | Include | Equipment | 759 | 2023-05-31 | 2277 | keep | 0 | May | 2023 | 0.0015509 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
CANOVANAS | 2023-05-31 23:10 | 2023-05-31 23:11 | 3464 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | R23053100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-05-31 | 3464 | keep | 0 | May | 2023 | 0.0023593 | 0.0023593 | Momentary | FALSE | FALSE | Not_TMED_Event | 3464
BARRANQUITAS | 2023-05-31 23:25 | 2023-06-01 02:20 | 378 | 2:55 | P | DESGANCHE | 2 X 50 EN CORTE DE LINEA DESGANCHE | C23053100336 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-05-31 | 66150 | keep | 0 | May | 2023 | 0.045054 | 0.00025745 | Sustained | FALSE | FALSE | Not_TMED_Event | 378
ARECIBO | 2023-05-31 23:28 | 2023-06-01 00:46 | 5042 | 1:18 | T | POSTE PRIMARIO PARTIDO O DEFECTUOSO | POSTE PRIMARIO PARTIDO (PAJARO CARPINTERO) SE SECCIONALIZO ALIMENTADOR EN MACHETES FID-1002008336 Y SE CERRO INTERRUPTOR SE CONTINUA TRABAJANDO SE PREPARO GOI PARA LOS TRABAJOS. | A23053100187 | New_Event | Primary Pole Failure | Include | Include | Equipment | 78 | 2023-05-31 | 393276 | keep | 0 | May | 2023 | 0.26786 | 0.0034341 | Sustained | FALSE | FALSE | Not_TMED_Event | 5042
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 1902 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 1902 | keep | 0 | May | 2023 | 0.0012954 | 0.0012954 | Momentary | FALSE | FALSE | Not_TMED_Event | 1902
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 970 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 970 | keep | 0 | May | 2023 | 0.00066066 | 0.00066066 | Momentary | FALSE | FALSE | Not_TMED_Event | 970
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 3003 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100136 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 3003 | keep | 0 | May | 2023 | 0.0020453 | 0.0020453 | Momentary | FALSE | FALSE | Not_TMED_Event | 3003
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 1394 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 1394 | keep | 0 | May | 2023 | 0.00094945 | 0.00094945 | Momentary | FALSE | FALSE | Not_TMED_Event | 1394
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 412 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO L-3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100138 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 412 | keep | 0 | May | 2023 | 0.00028061 | 0.00028061 | Momentary | FALSE | FALSE | Not_TMED_Event | 412
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 2343 | keep | 0 | May | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 1830 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 1830 | keep | 0 | May | 2023 | 0.0012464 | 0.0012464 | Momentary | FALSE | FALSE | Not_TMED_Event | 1830
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 710 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 710 | keep | 0 | May | 2023 | 0.00048358 | 0.00048358 | Momentary | FALSE | FALSE | Not_TMED_Event | 710
FAJARDO | 2023-05-31 23:33 | 2023-05-31 23:34 | 1197 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 3100 GLOBO ENREDADO EN LA LINEA ENTRE FAJARDO TC - ACB 3197A | R23053100137 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-05-31 | 1197 | keep | 0 | May | 2023 | 0.00081527 | 0.00081527 | Momentary | FALSE | FALSE | Not_TMED_Event | 1197
CANOVANAS | 2023-05-31 23:40 | 2023-06-01 08:47 | 117 | 9:07 | P | NO SE REPORTO CAUSA | 1 X 140 EN RISER | R23053100140 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 547 | 2023-05-31 | 63999 | keep | 0 | May | 2023 | 0.043589 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
UTUADO | 2023-05-31 23:55 | 2023-06-01 11:45 | 100 | 11:50 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23053100181 | New_Event | Vegetation Contact | Include | Include | Vegetation | 710 | 2023-05-31 | 71000 | keep | 0 | May | 2023 | 0.048358 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-06-01 00:07 | 2023-06-01 02:51 | 183 | 2:44 | P | NO SE REPORTO CAUSA | 1 X 25 EN CORTE DE LINEA NO CAUSA SE VERIFICO CON BITACORA | B23060100001 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 164 | 2023-06-01 | 30012 | keep | 0 | Jun | 2023 | 0.020441 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
ARECIBO | 2023-06-01 00:46 | 2023-06-02 15:50 | 300 | 39:04 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE RELOCALIZO LINEA PRIMARIA POR POSTE PARTIDO | A23060100001 | Partial_restoration | Primary Pole Failure | Include | Include | Equipment | 2344 | 2023-06-01 | 703200 | keep | 0 | Jun | 2023 | 0.47895 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-01 00:51 | 2023-06-01 01:30 | 2 | 0:39 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE RETIRO TRAMO DE SECUNDARIA QUEMADA | B23060100004 | New_Event | Secondary Wire Break | Include | Include | Equipment | 39 | 2023-06-01 | 78 | keep | 0 | Jun | 2023 | 5.3125e-05 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
BAYAMON | 2023-06-01 00:54 | 2023-06-01 12:27 | 30 | 11:33 | P | TRANSFORMADOR AVERIADO | 1 X 65 RISER SE SECCIONALIZO TRAMO PARA REMPLAZO DE XMR | B23060100005 | New_Event | Service Transformer Failure | Include | Include | Equipment | 693 | 2023-06-01 | 20790 | keep | 0 | Jun | 2023 | 0.01416 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
HUMACAO | 2023-06-01 01:02 | 2023-06-01 01:03 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23060100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 2299 | keep | 0 | Jun | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-06-01 01:05 | 2023-06-01 01:06 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23060100000 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 2299 | keep | 0 | Jun | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
HUMACAO | 2023-06-01 01:08 | 2023-06-01 01:09 | 2299 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | C23060100002 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 2299 | keep | 0 | Jun | 2023 | 0.0015658 | 0.0015658 | Momentary | FALSE | FALSE | Not_TMED_Event | 2299
YAUCO | 2023-06-01 01:39 | 2023-06-01 09:14 | 100 | 7:35 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE CAMBIO CAJA PRIMARIA 200A 1 X 100 EN CORTE DE LINEA | P23060100019 | New_Event | Cutout Failure | Include | Include | Equipment | 455 | 2023-06-01 | 45500 | keep | 0 | Jun | 2023 | 0.03099 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-01 03:10 | 2023-06-01 03:11 | 790 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | SE ABRIO INTERRUPTOR 1342-03 A PETICION PERSONAL EN EL CAMPO PARA PODER ABRIR CAJAS PRIMARIAS Y SECCIONALIZAR CONDUCTOR EN EL SUELO. 1342-03 LLEVA CARGA 1342-02 1345-03 Y 1345-01 | S23060100003 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-01 | 790 | keep | 0 | Jun | 2023 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2023-06-01 03:10 | 2023-06-01 03:11 | 29 | 0:01 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA PODER ABRIR CAJAS PRIMARIAS Y SECCIONALIZAR CONDUCTOR EN EL SUELO. 1342-03 LLEVA CARGA 1342-02 1345-03 Y 1345-01 | S23060100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 29 | keep | 0 | Jun | 2023 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-06-01 03:10 | 2023-06-01 03:11 | 660 | 0:01 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA PODER ABRIR CAJAS PRIMARIAS Y SECCIONALIZAR CONDUCTOR EN EL SUELO. 1342-03 LLEVA CARGA 1342-02 1345-03 Y 1345-01 | S23060100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 660 | keep | 0 | Jun | 2023 | 0.00044952 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-06-01 03:10 | 2023-06-01 03:11 | 259 | 0:01 | T | ALIMENTADOR AMARRADO | SE ABRIO INTERRUPTOR A PETICION PERSONAL EN EL CAMPO PARA PODER ABRIR CAJAS PRIMARIAS Y SECCIONALIZAR CONDUCTOR EN EL SUELO. 1342-03 LLEVA CARGA 1342-02 1345-03 Y 1345-01 | S23060100003 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 259 | keep | 0 | Jun | 2023 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-06-01 03:11 | 2023-06-01 21:11 | 139 | 18:00 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CL Y SE LEVANTO CONDUCTOR PRIMARIO CARGA POR EL 1342-03 | S23053100208 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1080 | 2023-06-01 | 150120 | keep | 0 | Jun | 2023 | 0.10225 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
CAGUAS | 2023-06-01 05:35 | 2023-06-01 05:36 | 2178 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO SU CARGA POR 3015-07 (SPARE) | C23060100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 2178 | keep | 0 | Jun | 2023 | 0.0014834 | 0.0014834 | Momentary | FALSE | FALSE | Not_TMED_Event | 2178
SAN JUAN | 2023-06-01 05:37 | 2023-06-01 05:39 | 937 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE INTERRUPTOR 1336-08 CON 20% DE SU CARGA TRANSFERIDA Y LLEVANDO 15% 1336-07 | S2306010000X | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-01 | 1874 | keep | 0 | Jun | 2023 | 0.0012764 | 0.00063819 | Momentary | FALSE | FALSE | Not_TMED_Event | 937
SAN JUAN | 2023-06-01 05:37 | 2023-06-01 05:39 | 4232 | 0:02 | P | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR 1336-08 CON 20% DE SU CARGA TRANSFERIDA Y LLEVANDO 15% 1336-07 | S2306010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-01 | 8464 | keep | 0 | Jun | 2023 | 0.0057648 | 0.0028824 | Momentary | FALSE | FALSE | Not_TMED_Event | 4232
BARRANQUITAS | 2023-06-01 05:47 | 2023-06-01 05:48 | 1131 | 0:01 | T | DESGANCHE | RECERRO | C23060100003 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-01 | 1131 | keep | 0 | Jun | 2023 | 0.00077032 | 0.00077032 | Momentary | FALSE | FALSE | Not_TMED_Event | 1131
FAJARDO | 2023-06-01 05:48 | 2023-06-01 09:10 | 50 | 3:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 100 EN C/L REMPLAZO DE CAJA | R23060100003 | New_Event | Cutout Failure | Include | Include | Equipment | 202 | 2023-06-01 | 10100 | keep | 0 | Jun | 2023 | 0.0068791 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BARRANQUITAS | 2023-06-01 05:48 | 2023-06-01 11:22 | 2 | 5:34 | P | DESGANCHE | 1 X 50 EN C/L SE REALIZO DESGANCHE Y SE REEMPLAZO BAJANTE PRIMARIO | C23060100053 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 334 | 2023-06-01 | 668 | keep | 0 | Jun | 2023 | 0.00045497 | 1.3622e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 2
CAGUAS | 2023-06-01 05:57 | 2023-06-01 05:58 | 476 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | C23060100005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 476 | keep | 0 | Jun | 2023 | 0.0003242 | 0.0003242 | Momentary | FALSE | FALSE | Not_TMED_Event | 476
CAGUAS | 2023-06-01 05:57 | 2023-06-01 05:58 | 1655 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | C23060100005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 1655 | keep | 0 | Jun | 2023 | 0.0011272 | 0.0011272 | Momentary | FALSE | FALSE | Not_TMED_Event | 1655
CAGUAS | 2023-06-01 05:57 | 2023-06-01 05:58 | 361 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | C23060100005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 361 | keep | 0 | Jun | 2023 | 0.00024588 | 0.00024588 | Momentary | FALSE | FALSE | Not_TMED_Event | 361
CAGUAS | 2023-06-01 05:57 | 2023-06-01 05:58 | 2842 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | C23060100005 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 2842 | keep | 0 | Jun | 2023 | 0.0019357 | 0.0019357 | Momentary | FALSE | FALSE | Not_TMED_Event | 2842
CAGUAS | 2023-06-01 05:57 | 2023-06-01 05:58 | 1362 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 LLEVA 80% DE SU CARGA NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | C23060100006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 1362 | keep | 0 | Jun | 2023 | 0.00092765 | 0.00092765 | Momentary | FALSE | FALSE | Not_TMED_Event | 1362
CAGUAS | 2023-06-01 05:57 | 2023-06-01 05:58 | 918 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | C23060100006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 918 | keep | 0 | Jun | 2023 | 0.00062525 | 0.00062525 | Momentary | FALSE | FALSE | Not_TMED_Event | 918
CAGUAS | 2023-06-01 05:57 | 2023-06-01 05:58 | 1725 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 3000 NO SE ENCONTRÃ“ CAUSA EN PATRULLAJE. | C23060100006 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 1725 | keep | 0 | Jun | 2023 | 0.0011749 | 0.0011749 | Momentary | FALSE | FALSE | Not_TMED_Event | 1725
BAYAMON | 2023-06-01 05:57 | 2023-06-01 08:24 | 1834 | 2:27 | S | CONDUCTOR ROTO O ABIERTO | BY-230601-01 PROTECCION DEL 9203-02 NO VIO LA AVERIA Y ABRIO Y FUSIBLE DE LA ALTA DEL XMR 10 % EN SERVICIO DEL 9203-02 | B23060100050 | New_Event | Primary Wire Break | Include | Include | Equipment | 147 | 2023-06-01 | 269598 | keep | 0 | Jun | 2023 | 0.18362 | 0.0012491 | Sustained | FALSE | FALSE | Not_TMED_Event | 1834
BAYAMON | 2023-06-01 05:57 | 2023-06-01 08:16 | 2324 | 2:19 | S | PROTECCION DEFECTUOSA | BY-230601-01 PROTECCION DEL 9203-02 NO VIO LA AVERIA Y ABRIO Y FUSIBLE DE LA ALTA DEL XMR | B23060100050 | New_Event | Protection Miscoordination | Include | Include | Other | 139 | 2023-06-01 | 323036 | keep | 0 | Jun | 2023 | 0.22002 | 0.0015829 | Sustained | FALSE | FALSE | Not_TMED_Event | 2324
BAYAMON | 2023-06-01 05:57 | 2023-06-01 08:16 | 1570 | 2:19 | S | PROTECCION DEFECTUOSA | BY-230601-01 PROTECCION DEL 9203-02 NO VIO LA AVERIA Y ABRIO Y FUSIBLE DE LA ALTA DEL XMR | B23060100050 | New_Event | Protection Miscoordination | Include | Include | Other | 139 | 2023-06-01 | 218230 | keep | 0 | Jun | 2023 | 0.14864 | 0.0010693 | Sustained | FALSE | FALSE | Not_TMED_Event | 1570
ARECIBO | 2023-06-01 06:10 | 2023-06-01 06:11 | 199 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA | A23060100008 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 199 | keep | 0 | Jun | 2023 | 0.00013554 | 0.00013554 | Momentary | FALSE | FALSE | Not_TMED_Event | 199
SAN JUAN | 2023-06-01 06:23 | 2023-06-01 06:24 | 837 | 0:01 | T | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR CONTROL 1401-07 LLEVA LA CARGA DEL 1401-06 | S23060100010 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 837 | keep | 0 | Jun | 2023 | 0.00057008 | 0.00057008 | Momentary | FALSE | FALSE | Not_TMED_Event | 837
SAN JUAN | 2023-06-01 06:23 | 2023-06-01 06:24 | 908 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO SE CERRO POR CONTROL LLEVA LA CARGA DEL 1401-06 | S23060100010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 908 | keep | 0 | Jun | 2023 | 0.00061843 | 0.00061843 | Momentary | FALSE | FALSE | Not_TMED_Event | 908
SAN JUAN | 2023-06-01 06:27 | 2023-06-01 13:17 | 144 | 6:50 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23060100011 | New_Event | Primary Wire Break | Include | Include | Equipment | 410 | 2023-06-01 | 59040 | keep | 0 | Jun | 2023 | 0.040212 | 9.8078e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 144
AGUADILLA | 2023-06-01 06:44 | 2023-06-01 06:45 | 3309 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DEL INTERRUPTOR NO SE REPORTO CAUSA LLEVA LA CARGA DEL 7502-03 | A23060100009 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 3309 | keep | 0 | Jun | 2023 | 0.0022537 | 0.0022537 | Momentary | FALSE | FALSE | Not_TMED_Event | 3309
AGUADILLA | 2023-06-01 06:44 | 2023-06-01 06:45 | 713 | 0:01 | T | ALIMENTADOR AMARRADO | RECIERRE DEL INTERRUPTOR 7502-02 QUE LLEVA LA CARGA DEL 7502-03 | A23060100009 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 713 | keep | 0 | Jun | 2023 | 0.00048562 | 0.00048562 | Momentary | FALSE | FALSE | Not_TMED_Event | 713
CAGUAS | 2023-06-01 06:57 | 2023-06-01 06:58 | 906 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2306010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 906 | keep | 0 | Jun | 2023 | 0.00061707 | 0.00061707 | Momentary | FALSE | FALSE | Not_TMED_Event | 906
CAGUAS | 2023-06-01 06:58 | 2023-06-01 13:20 | 17 | 6:22 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER | C23060100039 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 382 | 2023-06-01 | 6494 | keep | 0 | Jun | 2023 | 0.004423 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
BARRANQUITAS | 2023-06-01 07:09 | 2023-06-02 07:21 | 78 | 24:12 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L MAL TIEMPO FUERTES VIENTOS | C23060100150 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 1452 | 2023-06-01 | 113256 | keep | 0 | Jun | 2023 | 0.077138 | 5.3125e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 78
MAYAGÃœEZ | 2023-06-01 07:17 | 2023-06-01 09:50 | 50 | 2:33 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER NO SE REPORTO CAUSA | P23060100074 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 153 | 2023-06-01 | 7650 | keep | 0 | Jun | 2023 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-01 07:21 | 2023-06-01 07:22 | 450 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2306010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 450 | keep | 0 | Jun | 2023 | 0.00030649 | 0.00030649 | Momentary | FALSE | FALSE | Not_TMED_Event | 450
CANOVANAS | 2023-06-01 07:22 | 2023-06-01 11:34 | 40 | 4:12 | P | NO SE REPORTO CAUSA | 1 X 50 EN RISER PROVISIONAL AEREO | R23060100006 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 252 | 2023-06-01 | 10080 | keep | 0 | Jun | 2023 | 0.0068654 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
HUMACAO | 2023-06-01 07:28 | 2023-06-01 10:01 | 12 | 2:33 | P | SECUNDARIA/OTROS | SE ABRIO PARA REEMPLAZO PEDESTAL Y BARRAS | C23060100012 | New_Event |  |  |  |  | 153 | 2023-06-01 | 1836 | keep | 0 | Jun | 2023 | 0.0012505 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BAYAMON | 2023-06-01 07:35 | 2023-06-01 09:24 | 5 | 1:49 | P | ANIMAL | 1X 20 EN C/L CRUCE POR AVE | B23060100085 | New_Event | Animals | Include | Include | Wildlife | 109 | 2023-06-01 | 545 | keep | 0 | Jun | 2023 | 0.0003712 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
CAGUAS | 2023-06-01 07:44 | 2023-06-01 10:22 | 23 | 2:38 | P | CAUSAS EXTERNAS | 1 X 40 EN C/L A CAUSA DE IMPACTO DE ESCAVADORA CRUZO FASE | C23060100014 | New_Event | Damage From Public | Include | Include | Public | 158 | 2023-06-01 | 3634 | keep | 0 | Jun | 2023 | 0.0024751 | 1.5665e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 23
SAN JUAN | 2023-06-01 07:53 | 2023-06-01 12:30 | 22 | 4:37 | P | DESGANCHE | 1 X 50 EN C/L DESGANCHE | S23060100019 | New_Event | Vegetation Contact | Include | Include | Vegetation | 277 | 2023-06-01 | 6094 | keep | 0 | Jun | 2023 | 0.0041506 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
YAUCO | 2023-06-01 07:59 | 2023-06-01 10:55 | 80 | 2:56 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA POR AVE | P23060100095 | New_Event | Animals | Include | Include | Wildlife | 176 | 2023-06-01 | 14080 | keep | 0 | Jun | 2023 | 0.0095898 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-01 08:24 | 2023-06-01 10:11 | 1650 | 1:47 | P | CONDUCTOR ROTO O ABIERTO | BY-230601-01 SE LEVANTO CONDUCTOR PRIMARIO 85% EN SERVICIO | B23060100050 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 107 | 2023-06-01 | 176550 | keep | 0 | Jun | 2023 | 0.12025 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-01 08:31 | 2023-06-01 10:00 | 14 | 1:29 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23060100030 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-06-01 | 1246 | keep | 0 | Jun | 2023 | 0.00084864 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
SAN JUAN | 2023-06-01 08:31 | 2023-06-01 12:20 | 14 | 3:49 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23060100021 | New_Event | Vegetation Contact | Include | Include | Vegetation | 229 | 2023-06-01 | 3206 | keep | 0 | Jun | 2023 | 0.0021836 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
MAYAGÃœEZ | 2023-06-01 08:37 | 2023-06-01 20:20 | 50 | 11:43 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | 2 X 40 EN CORTE DE LINEA SE REEMPLAZO POSTE PRIMARIO PARTIDO | M23060100125 | New_Event | Primary Pole Failure | Include | Include | Equipment | 703 | 2023-06-01 | 35150 | keep | 0 | Jun | 2023 | 0.023941 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
CANOVANAS | 2023-06-01 08:40 | 2023-06-01 09:52 | 12 | 1:12 | P | TRANSFORMADOR AVERIADO | SE REEMPLAZO XMR AVERIADO Y SE NORMALIZO CARGA TRANSFERIDA A OTRO XMR | R23060100014 | New_Event | Service Transformer Failure | Include | Include | Equipment | 72 | 2023-06-01 | 864 | keep | 0 | Jun | 2023 | 0.00058847 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-06-01 08:43 | 2023-06-01 15:36 | 30 | 6:53 | P | CONDUCTOR ROTO O ABIERTO | EVENTO TRANSFERIDO DE PONCE 1 X 80 EN CORTE DE LINEA SE FIJO PUENTE A AISLADOR | P23060100116 | New_Event | Primary Wire Break | Include | Include | Equipment | 413 | 2023-06-01 | 12390 | keep | 0 | Jun | 2023 | 0.0084388 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
CANOVANAS | 2023-06-01 08:54 | 2023-06-01 10:18 | 3 | 1:24 | P | DESGANCHE | 2 X 50 EN C/L DESGANCHE EVENTO TRANSFERIDO DE PONCE | P23060100123 | New_Event | Vegetation Contact | Include | Include | Vegetation | 84 | 2023-06-01 | 252 | keep | 0 | Jun | 2023 | 0.00017164 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
AGUADILLA | 2023-06-01 09:07 | 2023-06-01 14:35 | 30 | 5:28 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN CORTE DE LINEA SE REMPLAZO CAJA PRIMARIA AVERIADA | A23060100021 | New_Event | Cutout Failure | Include | Include | Equipment | 328 | 2023-06-01 | 9840 | keep | 0 | Jun | 2023 | 0.006702 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BAYAMON | 2023-06-01 09:18 | 2023-06-01 12:24 | 136 | 3:06 | P | SOBRECARGA | 1 X 80 C/L POR CARGA | B23060100086 | New_Event | Trip Due To Overload | Include | Include | Other | 186 | 2023-06-01 | 25296 | keep | 0 | Jun | 2023 | 0.017229 | 9.2629e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 136
CANOVANAS | 2023-06-01 09:19 | 2023-06-01 10:52 | 17 | 1:33 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REEMPLAZO BAJANTE SECUNDARIO | R23060100015 | New_Event | Secondary Wire Break | Include | Include | Equipment | 93 | 2023-06-01 | 1581 | keep | 0 | Jun | 2023 | 0.0010768 | 1.1579e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 17
MAYAGÃœEZ | 2023-06-01 09:23 | 2023-06-01 15:28 | 400 | 6:05 | P | CONDUCTOR ARRIADO O CRUZADO | 3 X 100 EN CORTE DE LINEA SE RETEZO LINEA PRIMARIA | M23060100044 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 365 | 2023-06-01 | 146000 | keep | 0 | Jun | 2023 | 0.09944 | 0.00027244 | Sustained | FALSE | FALSE | Not_TMED_Event | 400
AGUADILLA | 2023-06-01 09:25 | 2023-06-01 12:40 | 30 | 3:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060100138 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 195 | 2023-06-01 | 5850 | keep | 0 | Jun | 2023 | 0.0039844 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-06-01 09:37 | 2023-06-01 12:36 | 1 | 2:59 | P | NO SE REPORTO CAUSA | 1 X 65 EN RISER Y 1 X 65 EN MONTURA PRIVADA | C23060100071 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 179 | 2023-06-01 | 179 | keep | 0 | Jun | 2023 | 0.00012192 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-01 09:43 | 2023-06-01 16:04 | 16 | 6:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REAPARO SECUNDARIA | R23060100018 | New_Event | Secondary Wire Break | Include | Include | Equipment | 381 | 2023-06-01 | 6096 | keep | 0 | Jun | 2023 | 0.004152 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
BAYAMON | 2023-06-01 09:58 | 2023-06-01 12:40 | 7 | 2:42 | P | ANIMAL | 1 X 15 EN XMR CRUCE POR AVE | B23060100100 | New_Event | Animals | Include | Include | Wildlife | 162 | 2023-06-01 | 1134 | keep | 0 | Jun | 2023 | 0.00077236 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
SAN JUAN | 2023-06-01 10:00 | 2023-06-01 10:01 | 222 | 0:01 | P | ALIMENTADOR AMARRADO | DISPARO SE CERRO POR SCADA 1303-05 LEVA 98% DE LA CARGA DEL 1303-04 | S23060100051 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 222 | keep | 0 | Jun | 2023 | 0.0001512 | 0.0001512 | Momentary | FALSE | FALSE | Not_TMED_Event | 222
SAN JUAN | 2023-06-01 10:00 | 2023-06-01 10:01 | 870 | 0:01 | T | DESGANCHE | DISPARO SE CERRO POR SCADA LLEVA 98% DE LA CARGA DEL 1303-04 | S23060100051 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1 | 2023-06-01 | 870 | keep | 0 | Jun | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
FAJARDO | 2023-06-01 10:00 | 2023-06-01 12:30 | 1 | 2:30 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO PUENTE LINEA A RISER | R23060100019 | New_Event | Primary Wire Break | Include | Include | Equipment | 150 | 2023-06-01 | 150 | keep | 0 | Jun | 2023 | 0.00010216 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-01 10:01 | 2023-06-01 12:29 | 14 | 2:28 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23060100030 | 1st_after_momentary | Vegetation Contact | Include | Include | Vegetation | 148 | 2023-06-01 | 2072 | keep | 0 | Jun | 2023 | 0.0014112 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
YAUCO | 2023-06-01 10:04 | 2023-06-01 10:06 | 1475 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO INTERRUPTOR SE LE DIO PRUEBA Y QUEDO EN SERVICIO | P23060100157 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-01 | 2950 | keep | 0 | Jun | 2023 | 0.0020092 | 0.0010046 | Momentary | FALSE | FALSE | Not_TMED_Event | 1475
BAYAMON | 2023-06-01 10:09 | 2023-06-01 12:17 | 20 | 2:08 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23060100123 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 128 | 2023-06-01 | 2560 | keep | 0 | Jun | 2023 | 0.0017436 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-01 10:11 | 2023-06-01 13:35 | 183 | 3:24 | P | CONDUCTOR ROTO O ABIERTO | BY-230601-01 SE REPARO RISER HACIA RESIDENCIAL AVERIADO Y SE CERRO ENTRANDO EL 10% QUE FALTABA | B23060100050 | New_Event | Primary Wire Break | Include | Include | Equipment | 204 | 2023-06-01 | 37332 | keep | 0 | Jun | 2023 | 0.025427 | 0.00012464 | Sustained | FALSE | FALSE | Not_TMED_Event | 183
MAYAGÃœEZ | 2023-06-01 10:14 | 2023-06-01 10:15 | 1597 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060100086 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 1597 | keep | 0 | Jun | 2023 | 0.0010877 | 0.0010877 | Momentary | FALSE | FALSE | Not_TMED_Event | 1597
MAYAGÃœEZ | 2023-06-01 10:30 | 2023-06-01 10:31 | 810 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 PUENTE ABIERTO EN ACB 9227. HAY TRAMO DE LINEA 9200 ENLAZADO CON LINEA 5600. | M23060100082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 810 | keep | 0 | Jun | 2023 | 0.00055169 | 0.00055169 | Momentary | FALSE | FALSE | Not_TMED_Event | 810
MAYAGÃœEZ | 2023-06-01 10:30 | 2023-06-01 10:31 | 1235 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 PUENTE ABIERTO EN ACB 9227. HAY TRAMO DE LINEA 9200 ENLAZADO CON LINEA 5600. | M23060100082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 1235 | keep | 0 | Jun | 2023 | 0.00084115 | 0.00084115 | Momentary | FALSE | FALSE | Not_TMED_Event | 1235
MAYAGÃœEZ | 2023-06-01 10:30 | 2023-06-01 10:31 | 93 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 PUENTE ABIERTO EN ACB 9227. HAY TRAMO DE LINEA 9200 ENLAZADO CON LINEA 5600. | M23060100082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 93 | keep | 0 | Jun | 2023 | 6.3342e-05 | 6.3342e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 93
MAYAGÃœEZ | 2023-06-01 10:30 | 2023-06-01 10:31 | 1825 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 PUENTE ABIERTO EN ACB 9227. HAY TRAMO DE LINEA 9200 ENLAZADO CON LINEA 5600. | M23060100082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 1825 | keep | 0 | Jun | 2023 | 0.001243 | 0.001243 | Momentary | FALSE | FALSE | Not_TMED_Event | 1825
MAYAGÃœEZ | 2023-06-01 10:30 | 2023-06-01 10:31 | 3230 | 0:01 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 5600 PUENTE ABIERTO EN ACB 9227. HAY TRAMO DE LINEA 9200 ENLAZADO CON LINEA 5600. | M23060100082 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-01 | 3230 | keep | 0 | Jun | 2023 | 0.0021999 | 0.0021999 | Momentary | FALSE | FALSE | Not_TMED_Event | 3230
VEGA BAJA | 2023-06-01 10:30 | 2023-06-01 11:20 | 5 | 0:50 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR CON ESCAPE DE ACEITE DE 50 KVA X 50 KVA | A23060100028 | New_Event | Service Transformer Failure | Include | Include | Equipment | 50 | 2023-06-01 | 250 | keep | 0 | Jun | 2023 | 0.00017027 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-06-01 10:37 | 2023-06-01 16:33 | 9 | 5:56 | P | POSTE PRIMARIO PARTIDO O DEFECTUOSO | SE REMPLAZO POSTE PARTIDO DE 45FT. Y SE CERRO C/L | B23060100108 | New_Event | Primary Pole Failure | Include | Include | Equipment | 356 | 2023-06-01 | 3204 | keep | 0 | Jun | 2023 | 0.0021822 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
AGUADILLA | 2023-06-01 10:40 | 2023-06-01 10:41 | 1192 | 0:01 | T | ALIMENTADOR AMARRADO | CARGA POR 7008-05 | M23060100087 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 1192 | keep | 0 | Jun | 2023 | 0.00081187 | 0.00081187 | Momentary | FALSE | FALSE | Not_TMED_Event | 1192
AGUADILLA | 2023-06-01 10:40 | 2023-06-01 10:41 | 3041 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | M23060100087 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 3041 | keep | 0 | Jun | 2023 | 0.0020712 | 0.0020712 | Momentary | FALSE | FALSE | Not_TMED_Event | 3041
YAUCO | 2023-06-01 10:44 | 2023-06-01 12:26 | 1 | 1:42 | P | AISLADOR ROTO, PARTIDO O SAFADO | 1 X 25 EN CORTE DE LINEA SE CAMBIO AISLADOR POR BRACITO | P23060100174 | New_Event | Insulator/ Pin Failure | Include | Include | Equipment | 102 | 2023-06-01 | 102 | keep | 0 | Jun | 2023 | 6.9472e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-01 10:57 | 2023-06-01 15:16 | 1 | 4:19 | P | NO SE REPORTO CAUSA | 1 X 15 EN TRANSFORMADOR NO CAUSA | C23060100055 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 259 | 2023-06-01 | 259 | keep | 0 | Jun | 2023 | 0.0001764 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
CANOVANAS | 2023-06-01 11:11 | 2023-06-01 15:29 | 45 | 4:18 | P | CONDUCTOR ROTO O ABIERTO | SE SECCIONALIZO TRAMO Y SE LEVANTO CONDUCTOR PRIMARIO SJ-230429-50 | R23060100025 | New_Event | Primary Wire Break | Include | Include | Equipment | 258 | 2023-06-01 | 11610 | keep | 0 | Jun | 2023 | 0.0079075 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
BARRANQUITAS | 2023-06-01 11:11 | 2023-06-01 13:10 | 70 | 1:59 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L | C23060100061 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 119 | 2023-06-01 | 8330 | keep | 0 | Jun | 2023 | 0.0056735 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
MAYAGÃœEZ | 2023-06-01 11:15 | 2023-06-01 12:42 | 600 | 1:27 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO MACHETES PARA REPARAR PUENTE ABIERTO | M23053100117 | New_Event | Primary Wire Break | Include | Include | Equipment | 87 | 2023-06-01 | 52200 | keep | 0 | Jun | 2023 | 0.035553 | 0.00040866 | Sustained | FALSE | FALSE | Not_TMED_Event | 600
SAN JUAN | 2023-06-01 11:16 | 2023-06-01 13:51 | 4 | 2:35 | P | NO SE REPORTO CAUSA | 1 X 50 EN C/L NO CAUSA | S23060100064 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 155 | 2023-06-01 | 620 | keep | 0 | Jun | 2023 | 0.00042228 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-06-01 11:18 | 2023-06-01 13:08 | 59 | 1:50 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 C/L MAL TIEMPO VIENTO | B23060100115 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 110 | 2023-06-01 | 6490 | keep | 0 | Jun | 2023 | 0.0044203 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
SAN JUAN | 2023-06-01 11:20 | 2023-06-01 16:38 | 140 | 5:18 | P | NO SE REPORTO CAUSA | 1 X 80 EN C/L | S23060100066 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 318 | 2023-06-01 | 44520 | keep | 0 | Jun | 2023 | 0.030322 | 9.5353e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 140
PONCE | 2023-06-01 11:23 | 2023-06-01 13:39 | 18 | 2:16 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE REPARO SECUNDARIA 1 X 15 EN TRASNFORMADOR | P23060100186 | New_Event | Secondary Wire Break | Include | Include | Equipment | 136 | 2023-06-01 | 2448 | keep | 0 | Jun | 2023 | 0.0016673 | 1.226e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 18
ARECIBO | 2023-06-01 11:29 | 2023-06-01 12:23 | 8 | 0:54 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 25 EN MONTURA DE TRANSFORMADORES SE REMPLAZO PORTAFUSIBLES DEFECTUOSO | A23060100043 | New_Event | Cutout Failure | Include | Include | Equipment | 54 | 2023-06-01 | 432 | keep | 0 | Jun | 2023 | 0.00029423 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CANOVANAS | 2023-06-01 11:31 | 2023-06-01 11:39 | 2094 | 0:08 | P | PROBLEMA DEL CLIENTE | SE VERIFICO PERSONAL FUERA Y SE CERRO POR CONTROL PERSONAL HACIENDO RECONECTE HACIA ESCUELA LE PROBO MALO 50% DE SU CARGA TRANSFERIDA | R23060100028 | New_Event | Customer-Related Interruption | Include | Include | Public | 8 | 2023-06-01 | 16752 | keep | 0 | Jun | 2023 | 0.01141 | 0.0014262 | Sustained | FALSE | FALSE | Not_TMED_Event | 2094
PONCE | 2023-06-01 11:37 | 2023-06-01 16:00 | 25 | 4:23 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO TRANSFORMADOR QUEMADO DE 37.5 A 4KV POR UNO MISMA CAPACIDAD | P23060100192 | New_Event | Service Transformer Failure | Include | Include | Equipment | 263 | 2023-06-01 | 6575 | keep | 0 | Jun | 2023 | 0.0044782 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
BAYAMON | 2023-06-01 12:02 | 2023-06-01 12:46 | 1 | 0:44 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23053100150 | New_Event | Secondary Wire Break | Include | Include | Equipment | 44 | 2023-06-01 | 44 | keep | 0 | Jun | 2023 | 2.9968e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-01 12:02 | 2023-06-01 12:03 | 2635 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | C2306010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 2635 | keep | 0 | Jun | 2023 | 0.0017947 | 0.0017947 | Momentary | FALSE | FALSE | Not_TMED_Event | 2635
BARRANQUITAS | 2023-06-01 12:03 | 2023-06-01 16:09 | 160 | 4:06 | P | NO SE REPORTO CAUSA | 2 X 80 EN CORTE DE LINEA NO CAUSA | C23060100083 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 246 | 2023-06-01 | 39360 | keep | 0 | Jun | 2023 | 0.026808 | 0.00010898 | Sustained | FALSE | FALSE | Not_TMED_Event | 160
CAGUAS | 2023-06-01 12:13 | 2023-06-01 12:37 | 22 | 0:24 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23060100037 | New_Event | Secondary Wire Break | Include | Include | Equipment | 24 | 2023-06-01 | 528 | keep | 0 | Jun | 2023 | 0.00035962 | 1.4984e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 22
BAYAMON | 2023-06-01 12:17 | 2023-06-01 12:18 | 1570 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2306010000X | Additional_clients | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 1570 | keep | 0 | Jun | 2023 | 0.0010693 | 0 | Momentary | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-01 12:18 | 2023-06-01 16:34 | 20 | 4:16 | P | NO SE REPORTO CAUSA | 1 X 15 EN XMR | B23060100123 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 256 | 2023-06-01 | 5120 | keep | 0 | Jun | 2023 | 0.0034872 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CANOVANAS | 2023-06-01 12:27 | 2023-06-01 14:13 | 1 | 1:46 | P | ANIMAL | 1 X 25 EN RISER AVE EVENTO TRANSFERIDO DE PONCE | P23060100182 | New_Event | Animals | Include | Include | Wildlife | 106 | 2023-06-01 | 106 | keep | 0 | Jun | 2023 | 7.2196e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-01 12:27 | 2023-06-01 17:30 | 10 | 5:03 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO PM- T-4 AVERIADO MEDIANTE BY-230601-02 | B23060100005 | Partial_restoration | Service Transformer Failure | Include | Include | Equipment | 303 | 2023-06-01 | 3030 | keep | 0 | Jun | 2023 | 0.0020637 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-01 12:30 | 2023-06-01 19:26 | 55 | 6:56 | P | DESGANCHE | SE ABRIO C/L PARA QUE COMPANIA PRIVADA REALIZARA DESGANCHE | B23060100122 | New_Event | Vegetation Contact | Include | Include | Vegetation | 416 | 2023-06-01 | 22880 | keep | 0 | Jun | 2023 | 0.015583 | 3.746e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 55
CAGUAS | 2023-06-01 12:30 | 2023-06-01 15:24 | 185 | 2:54 | P | ANIMAL | 1 X 80 EN CORTE DE LINEA AVE CRUZO FASE | C23060100081 | New_Event | Animals | Include | Include | Wildlife | 174 | 2023-06-01 | 32190 | keep | 0 | Jun | 2023 | 0.021924 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
UTUADO | 2023-06-01 12:34 | 2023-06-01 16:15 | 15 | 3:41 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060100057 | New_Event | Vegetation Contact | Include | Include | Vegetation | 221 | 2023-06-01 | 3315 | keep | 0 | Jun | 2023 | 0.0022578 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
BAYAMON | 2023-06-01 12:44 | 2023-06-02 13:25 | 1 | 24:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EVENTO TRANSFERIDO DE PONCE | P23060100210 | New_Event | Cutout Failure | Include | Include | Equipment | 1481 | 2023-06-01 | 1481 | keep | 0 | Jun | 2023 | 0.0010087 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
AGUADILLA | 2023-06-01 12:53 | 2023-06-01 13:40 | 1 | 0:47 | P | NO SE REPORTO CAUSA | 1 X 10 EN TRANSFORMADOR | P23060100212 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 47 | 2023-06-01 | 47 | keep | 0 | Jun | 2023 | 3.2011e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BAYAMON | 2023-06-01 13:20 | 2023-06-01 13:21 | 61 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2306010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 61 | keep | 0 | Jun | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CAGUAS | 2023-06-01 13:26 | 2023-06-01 14:37 | 4 | 1:11 | P | NO SE REPORTO CAUSA | 2 X 40 EN CORTE DE LINEA NO CAUSA | C23060100091 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 71 | 2023-06-01 | 284 | keep | 0 | Jun | 2023 | 0.00019343 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-01 13:33 | 2023-06-01 16:18 | 74 | 2:45 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE | S23060100084 | New_Event | Vegetation Contact | Include | Include | Vegetation | 165 | 2023-06-01 | 12210 | keep | 0 | Jun | 2023 | 0.0083162 | 5.0401e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 74
GUAYAMA | 2023-06-01 13:38 | 2023-06-01 15:39 | 15 | 2:01 | P | PARARRAYOS DEFECTUOSO | 1 X 100 EN CORTE DE LINEA POR PARARRAYOS ACTIVADO | P23060100225 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 121 | 2023-06-01 | 1815 | keep | 0 | Jun | 2023 | 0.0012362 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
SAN JUAN | 2023-06-01 13:42 | 2023-06-01 16:56 | 184 | 3:14 | P | DESGANCHE | 1 X 1OO EN C/L DESGANCHE | S23060100090 | New_Event | Vegetation Contact | Include | Include | Vegetation | 194 | 2023-06-01 | 35696 | keep | 0 | Jun | 2023 | 0.024312 | 0.00012532 | Sustained | FALSE | FALSE | Not_TMED_Event | 184
VEGA BAJA | 2023-06-01 13:44 | 2023-06-01 18:50 | 20 | 5:06 | P | ANIMAL | 1 X 30 EN CORTE DE LINEA AVE CRUZO LINEAS | A23060100075 | New_Event | Animals | Include | Include | Wildlife | 306 | 2023-06-01 | 6120 | keep | 0 | Jun | 2023 | 0.0041683 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-01 14:09 | 2023-06-01 16:24 | 1 | 2:15 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060100142 | New_Event | Secondary Wire Break | Include | Include | Equipment | 135 | 2023-06-01 | 135 | keep | 0 | Jun | 2023 | 9.1948e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
UTUADO | 2023-06-01 14:09 | 2023-06-02 16:37 | 100 | 26:28 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060100081 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1588 | 2023-06-01 | 158800 | keep | 0 | Jun | 2023 | 0.10816 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
MAYAGÃœEZ | 2023-06-01 14:15 | 2023-06-01 16:20 | 200 | 2:05 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LA LINEA | M23060100147 | New_Event | Vegetation Contact | Include | Include | Vegetation | 125 | 2023-06-01 | 25000 | keep | 0 | Jun | 2023 | 0.017027 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
MAYAGÃœEZ | 2023-06-01 14:26 | 2023-06-01 18:13 | 75 | 3:47 | P | DESGANCHE | 2 X 40 EN CORTE DE LINEA SE RETIRO BAMBUA SOBRE LA LINEA | M23060100156 | New_Event | Vegetation Contact | Include | Include | Vegetation | 227 | 2023-06-01 | 17025 | keep | 0 | Jun | 2023 | 0.011596 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-06-01 14:26 | 2023-06-01 16:14 | 5 | 1:48 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060100145 | New_Event | Secondary Wire Break | Include | Include | Equipment | 108 | 2023-06-01 | 540 | keep | 0 | Jun | 2023 | 0.00036779 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-06-01 14:35 | 2023-06-01 15:27 | 6 | 0:52 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR SE REMPLAZO CAJA PRIMARIA | B23060101002 | New_Event | Cutout Failure | Include | Include | Equipment | 52 | 2023-06-01 | 312 | keep | 0 | Jun | 2023 | 0.0002125 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-06-01 14:40 | 2023-06-01 16:16 | 12 | 1:36 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE REALIZO DESGANCHE | M23060100168 | New_Event | Vegetation Contact | Include | Include | Vegetation | 96 | 2023-06-01 | 1152 | keep | 0 | Jun | 2023 | 0.00078462 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
PONCE | 2023-06-01 14:57 | 2023-06-01 17:14 | 10 | 2:17 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 15 EN TRANSFORMADOR POR CRUCE EN TOMA | P23060100251 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 137 | 2023-06-01 | 1370 | keep | 0 | Jun | 2023 | 0.0009331 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
AGUADILLA | 2023-06-01 14:57 | 2023-06-01 14:59 | 1541 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23060100104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-01 | 3082 | keep | 0 | Jun | 2023 | 0.0020991 | 0.0010496 | Momentary | FALSE | FALSE | Not_TMED_Event | 1541
AGUADILLA | 2023-06-01 14:57 | 2023-06-01 14:59 | 307 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23060100104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-01 | 614 | keep | 0 | Jun | 2023 | 0.00041819 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
AGUADILLA | 2023-06-01 14:57 | 2023-06-01 14:59 | 1277 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23060100104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-01 | 2554 | keep | 0 | Jun | 2023 | 0.0017395 | 0.00086976 | Momentary | FALSE | FALSE | Not_TMED_Event | 1277
AGUADILLA | 2023-06-01 14:57 | 2023-06-01 14:59 | 1644 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23060100104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-01 | 3288 | keep | 0 | Jun | 2023 | 0.0022394 | 0.0011197 | Momentary | FALSE | FALSE | Not_TMED_Event | 1644
AGUADILLA | 2023-06-01 14:57 | 2023-06-01 14:59 | 1831 | 0:02 | S | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 2700 | A23060100104 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 2 | 2023-06-01 | 3662 | keep | 0 | Jun | 2023 | 0.0024942 | 0.0012471 | Momentary | FALSE | FALSE | Not_TMED_Event | 1831
VEGA BAJA | 2023-06-01 15:00 | 2023-06-01 17:00 | 10 | 2:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | ABRIR CAJAS DE TRANSFORMADOR PARA REPARAR BARRAS SECUNDARIAS | A23060100092 | New_Event | Secondary Wire Break | Include | Include | Equipment | 120 | 2023-06-01 | 1200 | keep | 0 | Jun | 2023 | 0.00081731 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-06-01 15:02 | 2023-06-01 16:54 | 165 | 1:52 | P | CAUSAS EXTERNAS | 2 X 40 EN CORTE DE LINEA SE ELIMINO TOMAS AVERIADAS POR CAMION Y CONTADORES HASTA QUE REPAREN | P23060100253 | New_Event | Damage From Public | Include | Include | Public | 112 | 2023-06-01 | 18480 | keep | 0 | Jun | 2023 | 0.012587 | 0.00011238 | Sustained | FALSE | FALSE | Not_TMED_Event | 165
VEGA BAJA | 2023-06-01 15:08 | 2023-06-01 18:40 | 40 | 3:32 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 30 EN CORTE DE LINEA SE REPARO LINEA PRIMARIA ARRIADA | A23060100099 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 212 | 2023-06-01 | 8480 | keep | 0 | Jun | 2023 | 0.0057757 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-06-01 15:40 | 2023-06-01 19:16 | 50 | 3:36 | P | ANIMAL | 1 X 40 EN CORTE DE LINEA AVE CRUZO LINEAS | A23060100105 | New_Event | Animals | Include | Include | Wildlife | 216 | 2023-06-01 | 10800 | keep | 0 | Jun | 2023 | 0.0073558 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
SAN JUAN | 2023-06-01 15:42 | 2023-06-01 20:01 | 150 | 4:19 | P | DESGANCHE | DESGANCHE Y 2 X 80 EN C/L TRANSFERIDO DE PONCE | P23060100269 | New_Event | Vegetation Contact | Include | Include | Vegetation | 259 | 2023-06-01 | 38850 | keep | 0 | Jun | 2023 | 0.026461 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
MAYAGÃœEZ | 2023-06-01 15:45 | 2023-06-01 18:00 | 70 | 2:15 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA MAL TIEMPO VIENTOS FUERTES | M23060100186 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 135 | 2023-06-01 | 9450 | keep | 0 | Jun | 2023 | 0.0064364 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
UTUADO | 2023-06-01 15:49 | 2023-06-01 19:21 | 40 | 3:32 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23060100108 | New_Event | Vegetation Contact | Include | Include | Vegetation | 212 | 2023-06-01 | 8480 | keep | 0 | Jun | 2023 | 0.0057757 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
UTUADO | 2023-06-01 15:50 | 2023-06-01 15:53 | 1633 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | A23060100120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-01 | 4899 | keep | 0 | Jun | 2023 | 0.0033367 | 0.0011122 | Momentary | FALSE | FALSE | Not_TMED_Event | 1633
UTUADO | 2023-06-01 15:50 | 2023-06-01 15:53 | 1624 | 0:03 | S | LINEA DE TRANSMISION 38KV | DISPARO LINEA 1900 | A23060100120 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 3 | 2023-06-01 | 4872 | keep | 0 | Jun | 2023 | 0.0033183 | 0.0011061 | Momentary | FALSE | FALSE | Not_TMED_Event | 1624
SAN JUAN | 2023-06-01 15:51 | 2023-06-01 19:39 | 189 | 3:48 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA Y SE REEMPLAZO CAJA | S23060100115 | New_Event | Primary Wire Break | Include | Include | Equipment | 228 | 2023-06-01 | 43092 | keep | 0 | Jun | 2023 | 0.02935 | 0.00012873 | Sustained | FALSE | FALSE | Not_TMED_Event | 189
VEGA BAJA | 2023-06-01 15:55 | 2023-06-01 20:13 | 20 | 4:18 | P | DESGANCHE | 1 X 25 EN CORTE DE LINEA SE RETIRO BAMBUS SOBRE LAS LINEAS | A23060100111 | New_Event | Vegetation Contact | Include | Include | Vegetation | 258 | 2023-06-01 | 5160 | keep | 0 | Jun | 2023 | 0.0035145 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
FAJARDO | 2023-06-01 15:59 | 2023-06-01 19:22 | 4 | 3:23 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | R23060100050 | New_Event | Secondary Wire Break | Include | Include | Equipment | 203 | 2023-06-01 | 812 | keep | 0 | Jun | 2023 | 0.00055305 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
BAYAMON | 2023-06-01 16:16 | 2023-06-01 19:23 | 40 | 3:07 | P | PARARRAYOS DEFECTUOSO | 1 X 65 EN C/L SE ELIMINO PARARRAYO | S23060100121 | New_Event | Lightning Arrester Failure | Include | Include | Equipment | 187 | 2023-06-01 | 7480 | keep | 0 | Jun | 2023 | 0.0050946 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
ARECIBO | 2023-06-01 16:22 | 2023-06-01 20:03 | 10 | 3:41 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR SE REMPLAZO CAJA PRIMARIA AVERIADA | A23060100125 | New_Event | Cutout Failure | Include | Include | Equipment | 221 | 2023-06-01 | 2210 | keep | 0 | Jun | 2023 | 0.0015052 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
CANOVANAS | 2023-06-01 16:32 | 2023-06-01 18:16 | 500 | 1:44 | P | ANIMAL | 1 X 140 EN CORTE DE LINEA AVE CRUZO FASE | R23060100055 | New_Event | Animals | Include | Include | Wildlife | 104 | 2023-06-01 | 52000 | keep | 0 | Jun | 2023 | 0.035417 | 0.00034055 | Sustained | FALSE | FALSE | Not_TMED_Event | 500
CAGUAS | 2023-06-01 16:32 | 2023-06-01 18:56 | 6 | 2:24 | P | ANIMAL | 1 X 15 EN TRANSFORMADOR IGUANA CRUZO FASE | C23060100118 | New_Event | Animals | Include | Include | Wildlife | 144 | 2023-06-01 | 864 | keep | 0 | Jun | 2023 | 0.00058847 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
MAYAGÃœEZ | 2023-06-01 16:33 | 2023-06-01 19:06 | 50 | 2:33 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | M23060100207 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-06-01 | 7650 | keep | 0 | Jun | 2023 | 0.0052104 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
BAYAMON | 2023-06-01 16:33 | 2023-06-01 16:34 | 2234 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO | B2306010000X | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-01 | 2234 | keep | 0 | Jun | 2023 | 0.0015216 | 0.0015216 | Momentary | FALSE | FALSE | Not_TMED_Event | 2234
BAYAMON | 2023-06-01 16:34 | 2023-06-01 20:06 | 700 | 3:32 | P | CONDUCTOR ROTO O ABIERTO | BY-230601-03 SE SECCIONALIZO ALIMENTADOR SE SUBIO PRIMARIA Y SE NORMALIZO LA CARGA | B23060100169 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 212 | 2023-06-01 | 148400 | keep | 0 | Jun | 2023 | 0.10107 | 0.00047677 | Sustained | FALSE | FALSE | Not_TMED_Event | 700
CANOVANAS | 2023-06-01 16:37 | 2023-06-01 19:10 | 30 | 2:33 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23060100058 | New_Event | Vegetation Contact | Include | Include | Vegetation | 153 | 2023-06-01 | 4590 | keep | 0 | Jun | 2023 | 0.0031262 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
VEGA BAJA | 2023-06-01 16:44 | 2023-06-02 16:33 | 20 | 23:49 | P | DESGANCHE | 2 X 80 // 2 X 65 // Y 1 X 50 EN CORTES DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060100131 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1429 | 2023-06-01 | 28580 | keep | 0 | Jun | 2023 | 0.019466 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
CAGUAS | 2023-06-01 16:53 | 2023-06-01 18:22 | 188 | 1:29 | P | DESGANCHE | 1 X 100 EN CORTE DE LINEA DESGANCHE | C23060100121 | New_Event | Vegetation Contact | Include | Include | Vegetation | 89 | 2023-06-01 | 16732 | keep | 0 | Jun | 2023 | 0.011396 | 0.00012805 | Sustained | FALSE | FALSE | Not_TMED_Event | 188
AGUADILLA | 2023-06-01 16:53 | 2023-06-02 12:25 | 70 | 19:32 | P | DESGANCHE | 1 X 50 EN CORTE DE LINEA SE REALIZO DESGANCHE Y SE REMPLAZO CAJA PRIMARIA AVERIADA EN CORTE DE LINEA | M23060100217 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1172 | 2023-06-01 | 82040 | keep | 0 | Jun | 2023 | 0.055877 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
SAN JUAN | 2023-06-01 16:55 | 2023-06-01 18:42 | 6 | 1:47 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | S23060100130 | New_Event | Secondary Wire Break | Include | Include | Equipment | 107 | 2023-06-01 | 642 | keep | 0 | Jun | 2023 | 0.00043726 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CANOVANAS | 2023-06-01 16:58 | 2023-06-01 17:23 | 10 | 0:25 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | R23060100046 | New_Event | Vegetation Contact | Include | Include | Vegetation | 25 | 2023-06-01 | 250 | keep | 0 | Jun | 2023 | 0.00017027 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
FAJARDO | 2023-06-01 16:59 | 2023-06-01 17:38 | 9 | 0:39 | P | NO SE REPORTO CAUSA | EVENTO TRANSFERIDO DE PONCE 1 X 65 EN C/L | P23060100295 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 39 | 2023-06-01 | 351 | keep | 0 | Jun | 2023 | 0.00023906 | 6.1299e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 9
BAYAMON | 2023-06-01 17:05 | 2023-06-01 17:26 | 13 | 0:21 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060100179 | New_Event | Secondary Wire Break | Include | Include | Equipment | 21 | 2023-06-01 | 273 | keep | 0 | Jun | 2023 | 0.00018594 | 8.8542e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 13
FAJARDO | 2023-06-01 17:14 | 2023-06-01 20:19 | 139 | 3:05 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | R23060100063 | New_Event | Vegetation Contact | Include | Include | Vegetation | 185 | 2023-06-01 | 25715 | keep | 0 | Jun | 2023 | 0.017514 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
BAYAMON | 2023-06-01 17:22 | 2023-06-02 09:57 | 1 | 16:35 | P | ANIMAL | 1 X 20 EN SUB. PRIVADA CRUCE X AVE EVENTO TRANSFERIDO DE PONCE | P23060100307 | New_Event | Animals | Include | Include | Wildlife | 995 | 2023-06-01 | 995 | keep | 0 | Jun | 2023 | 0.00067769 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
PONCE | 2023-06-01 17:25 | 2023-06-01 18:27 | 1 | 1:02 | P | SOBRECARGA | 1 X 15 EN TRANSFORMADOR POR CARGA | P23060100308 | New_Event | Trip Due To Overload | Include | Include | Other | 62 | 2023-06-01 | 62 | keep | 0 | Jun | 2023 | 4.2228e-05 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
SAN JUAN | 2023-06-01 17:26 | 2023-06-01 17:27 | 4133 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR | S2306010000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 4133 | keep | 0 | Jun | 2023 | 0.002815 | 0.002815 | Momentary | FALSE | FALSE | Not_TMED_Event | 4133
MAYAGÃœEZ | 2023-06-01 17:27 | 2023-06-01 19:44 | 200 | 2:17 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 100 EN CORTE DE LINEA POR LINEA PRIMARIA CRUZADA | M23060100228 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 137 | 2023-06-01 | 27400 | keep | 0 | Jun | 2023 | 0.018662 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
AGUADILLA | 2023-06-01 17:35 | 2023-06-01 18:57 | 7 | 1:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 20 EN TRANSFORMADOR POR PORTAFUSIBLE QUEMADO | M23060100230 | New_Event | Cutout Failure | Include | Include | Equipment | 82 | 2023-06-01 | 574 | keep | 0 | Jun | 2023 | 0.00039095 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
CANOVANAS | 2023-06-01 17:37 | 2023-06-01 17:38 | 3046 | 0:01 | T | ANIMAL | RECERRO LLEVA 1647-10 Y 15% DEL 1647-09 | R23060100070 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-06-01 | 3046 | keep | 0 | Jun | 2023 | 0.0020746 | 0.0020746 | Momentary | FALSE | FALSE | Not_TMED_Event | 3046
CANOVANAS | 2023-06-01 17:37 | 2023-06-01 17:38 | 307 | 0:01 | P | ALIMENTADOR AMARRADO | RECERRO 15% POR 1646-03 | R23060100070 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 307 | keep | 0 | Jun | 2023 | 0.0002091 | 0.0002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 307
CANOVANAS | 2023-06-01 17:37 | 2023-06-01 17:38 | 61 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO SU CARGA POR 1646-03 Y 15% DEL 1647-09 | R23060100070 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 61 | keep | 0 | Jun | 2023 | 4.1547e-05 | 4.1547e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 61
CANOVANAS | 2023-06-01 17:38 | 2023-06-01 19:16 | 80 | 1:38 | P | ANIMAL | 1 X 65 Y 1 X 50 EN C/L CRUCE POR AVE | R23060100072 | 1st_after_momentary | Animals | Include | Include | Wildlife | 98 | 2023-06-01 | 7840 | keep | 0 | Jun | 2023 | 0.0053398 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-01 17:39 | 2023-06-02 16:45 | 8 | 23:06 | P | DESGANCHE | 1 X 15 EN XMR DESGANCHE PRIMARIO | B23060100192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1386 | 2023-06-01 | 11088 | keep | 0 | Jun | 2023 | 0.007552 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
MAYAGÃœEZ | 2023-06-01 17:43 | 2023-06-02 15:56 | 12 | 22:13 | P | DESGANCHE | 1 X 40 EN CL DESGANCHE | M23060100232 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1333 | 2023-06-01 | 15996 | keep | 0 | Jun | 2023 | 0.010895 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-06-01 17:56 | 2023-06-02 13:18 | 50 | 19:22 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN SE C/L REMPLAZO CAJA PRIMARIA | S23060100141 | New_Event | Cutout Failure | Include | Include | Equipment | 1162 | 2023-06-01 | 58100 | keep | 0 | Jun | 2023 | 0.039572 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-06-01 17:58 | 2023-06-01 20:53 | 50 | 2:55 | P | DESGANCHE | 1 X 40 EN CORTE DE LINEA SECTOR REQUIERE DESGANCHE | A23060100151 | New_Event | Vegetation Contact | Include | Include | Vegetation | 175 | 2023-06-01 | 8750 | keep | 0 | Jun | 2023 | 0.0059596 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
MAYAGÃœEZ | 2023-06-01 18:00 | 2023-06-02 09:27 | 6 | 15:27 | P | MAL TIEMPO/RAYOS | 1 X 5 EN TRANSFORMADOR DESCARGA ELECTRICA | P23060100321 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 927 | 2023-06-01 | 5562 | keep | 0 | Jun | 2023 | 0.0037883 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
CAGUAS | 2023-06-01 18:05 | 2023-06-01 19:28 | 105 | 1:23 | P | NO SE REPORTO CAUSA | 1 X 65 EN CORTE DE LINEA NO CAUSA | C23060100129 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 83 | 2023-06-01 | 8715 | keep | 0 | Jun | 2023 | 0.0059357 | 7.1515e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 105
SAN JUAN | 2023-06-01 18:11 | 2023-06-01 21:24 | 30 | 3:13 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE DE LINEA A CAJA | S23060100144 | New_Event | Primary Wire Break | Include | Include | Equipment | 193 | 2023-06-01 | 5790 | keep | 0 | Jun | 2023 | 0.0039435 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-06-01 18:45 | 2023-06-01 18:46 | 2446 | 0:01 | T | ANIMAL | RECIERRE | P23060100345 | New_Event | Animals | Include | Include | Wildlife | 1 | 2023-06-01 | 2446 | keep | 0 | Jun | 2023 | 0.001666 | 0.001666 | Momentary | FALSE | FALSE | Not_TMED_Event | 2446
PONCE | 2023-06-01 18:46 | 2023-06-01 19:41 | 20 | 0:55 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA POR ANIMAL | P23060100346 | 1st_after_momentary | Animals | Include | Include | Wildlife | 55 | 2023-06-01 | 1100 | keep | 0 | Jun | 2023 | 0.0007492 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
BAYAMON | 2023-06-01 18:46 | 2023-06-01 19:48 | 174 | 1:02 | P | DESCONECTIVO DEFECTUOSO | SE CERRO PUENTE ABIERTO | B23060100221 | New_Event | Switch Failure | Include | Include | Equipment | 62 | 2023-06-01 | 10788 | keep | 0 | Jun | 2023 | 0.0073477 | 0.00011851 | Sustained | FALSE | FALSE | Not_TMED_Event | 174
SAN JUAN | 2023-06-01 18:48 | 2023-06-02 21:09 | 12 | 26:21 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | SE REMPLAZO CAJA PRIMARIA EN XMR NO FUNDIO | S23060100153 | New_Event | Cutout Failure | Include | Include | Equipment | 1581 | 2023-06-01 | 18972 | keep | 0 | Jun | 2023 | 0.012922 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-06-01 19:00 | 2023-06-01 20:09 | 95 | 1:09 | P | DESGANCHE | 1 X 80 EN CORTE DE LINEA DESGANCHE | C23060100135 | New_Event | Vegetation Contact | Include | Include | Vegetation | 69 | 2023-06-01 | 6555 | keep | 0 | Jun | 2023 | 0.0044646 | 6.4704e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 95
BAYAMON | 2023-06-01 19:03 | 2023-06-02 01:10 | 387 | 6:07 | P | SOBRECARGA | 1 X 65 EN C/L POR CARGA | B23060100236 | New_Event | Trip Due To Overload | Include | Include | Other | 367 | 2023-06-01 | 142029 | keep | 0 | Jun | 2023 | 0.096735 | 0.00026358 | Sustained | FALSE | FALSE | Not_TMED_Event | 387
PONCE | 2023-06-01 19:15 | 2023-06-01 19:16 | 1478 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | P23060100359 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 1478 | keep | 0 | Jun | 2023 | 0.0010067 | 0.0010067 | Momentary | FALSE | FALSE | Not_TMED_Event | 1478
MAYAGÃœEZ | 2023-06-01 19:16 | 2023-06-02 14:40 | 30 | 19:24 | P | CONDUCTOR ROTO O ABIERTO | SE FIJO BAJANTE SAFADO EN COORTE DE LINEA Y SE CERRO CAJA PRIMARIA | M23060100261 | New_Event | Primary Wire Break | Include | Include | Equipment | 1164 | 2023-06-01 | 34920 | keep | 0 | Jun | 2023 | 0.023784 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
UTUADO | 2023-06-01 19:21 | 2023-06-01 19:30 | 50 | 0:09 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA MAL TIEMPO LLUVIA Y VIENTOS FUERTES | P23060100361 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 9 | 2023-06-01 | 450 | keep | 0 | Jun | 2023 | 0.00030649 | 3.4055e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 50
ARECIBO | 2023-06-01 19:28 | 2023-06-01 22:25 | 2381 | 2:57 | P | CONDUCTOR ROTO O ABIERTO | SE ABRE MACHETES Y SE SECCIONALIZA AVERIA DE LINEA PRIMARIA ROTA | A23060100169 | New_Event | Primary Wire Break | Include | Include | Equipment | 177 | 2023-06-01 | 421437 | keep | 0 | Jun | 2023 | 0.28704 | 0.0016217 | Sustained | FALSE | FALSE | Not_TMED_Event | 2381
BAYAMON | 2023-06-01 19:42 | 2023-06-01 19:43 | 1498 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23060100282 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
AGUADILLA | 2023-06-01 19:43 | 2023-06-02 14:45 | 146 | 19:02 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO | M23060100282 | New_Event | Primary Wire Break | Include | Include | Equipment | 1142 | 2023-06-01 | 166732 | keep | 0 | Jun | 2023 | 0.11356 | 9.944e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 146
BAYAMON | 2023-06-01 19:48 | 2023-06-01 19:49 | 3070 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B23060100295 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-01 | 3070 | keep | 0 | Jun | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-06-01 19:49 | 2023-06-01 20:08 | 174 | 0:19 | P | DESCONECTIVO DEFECTUOSO | SE CERRO PUENTE ABIERTO | B23060100221 | Partial_restoration | Switch Failure | Include | Include | Equipment | 19 | 2023-06-01 | 3306 | keep | 0 | Jun | 2023 | 0.0022517 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-01 19:54 | 2023-06-01 19:55 | 1498 | 0:01 | T | NO SE REPORTO CAUSA | DISPARO Y SE CERRO POR SCADA | B23060100300 | 1st_after_momentary | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 1498 | keep | 0 | Jun | 2023 | 0.0010203 | 0.0010203 | Momentary | FALSE | FALSE | Not_TMED_Event | 1498
SAN JUAN | 2023-06-01 20:02 | 2023-06-02 07:06 | 117 | 11:04 | P | DESGANCHE | 1X65 EN C/L DESGANCHE | S23060100175 | New_Event | Vegetation Contact | Include | Include | Vegetation | 664 | 2023-06-01 | 77688 | keep | 0 | Jun | 2023 | 0.052913 | 7.9688e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 117
BAYAMON | 2023-06-01 20:03 | 2023-06-01 20:04 | 5809 | 0:01 | T | NO SE REPORTO CAUSA | RECERRO | B23060100000 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 5809 | keep | 0 | Jun | 2023 | 0.0039565 | 0.0039565 | Momentary | FALSE | FALSE | Not_TMED_Event | 5809
HUMACAO | 2023-06-01 20:03 | 2023-06-02 08:28 | 12 | 12:25 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR PARA REPARAR BAJANTE SECUNDARIO | C23060100143 | New_Event | Secondary Wire Break | Include | Include | Equipment | 745 | 2023-06-01 | 8940 | keep | 0 | Jun | 2023 | 0.006089 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
BARRANQUITAS | 2023-06-01 20:06 | 2023-06-01 22:17 | 150 | 2:11 | P | SOBRECARGA | 1 X 80 EN CORTE DE LINEA TENIA FUSIBLE DE 50 AMP. | C23060100146 | New_Event | Trip Due To Overload | Include | Include | Other | 131 | 2023-06-01 | 19650 | keep | 0 | Jun | 2023 | 0.013384 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
BAYAMON | 2023-06-01 20:08 | 2023-06-01 22:04 | 1498 | 1:56 | T | CONDUCTOR ROTO O ABIERTO | BY-230601-04 SE ABRIERON UNOS MACHETES Y SE CERRO BKR 20% EN SERVICIO | B23060100455 | New_Event | Primary Wire Break | Include | Include | Equipment | 116 | 2023-06-01 | 173768 | keep | 0 | Jun | 2023 | 0.11835 | 0.0010203 | Sustained | FALSE | FALSE | Not_TMED_Event | 1498
BAYAMON | 2023-06-01 20:08 | 2023-06-01 20:09 | 3070 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B23060100325 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-01 | 3070 | keep | 0 | Jun | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-06-01 20:09 | 2023-06-01 20:28 | 174 | 0:19 | P | DESCONECTIVO DEFECTUOSO | SE CERRO PUENTE ABIERTO | B23060100221 | Partial_restoration | Switch Failure | Include | Include | Equipment | 19 | 2023-06-01 | 3306 | keep | 0 | Jun | 2023 | 0.0022517 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
MAYAGÃœEZ | 2023-06-01 20:10 | 2023-06-02 08:58 | 100 | 12:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CL FUERTE LLUVIA | M23060100300 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 768 | 2023-06-01 | 76800 | keep | 0 | Jun | 2023 | 0.052308 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-01 20:15 | 2023-06-02 04:58 | 158 | 8:43 | P | DESGANCHE | 1 X 100 EN SALIDA SU-2 DESGANCHE | B23060100332 | New_Event | Vegetation Contact | Include | Include | Vegetation | 523 | 2023-06-01 | 82634 | keep | 0 | Jun | 2023 | 0.056282 | 0.00010761 | Sustained | FALSE | FALSE | Not_TMED_Event | 158
MAYAGÃœEZ | 2023-06-01 20:25 | 2023-06-02 14:23 | 10 | 17:58 | P | ANIMAL | 1 X 10 EN TRANSFORMADOR CRUCE POR AVE | M23060100314 | New_Event | Animals | Include | Include | Wildlife | 1078 | 2023-06-01 | 10780 | keep | 0 | Jun | 2023 | 0.0073422 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
BAYAMON | 2023-06-01 20:28 | 2023-06-01 20:29 | 3070 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECIERRE | B23060100340 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-01 | 3070 | keep | 0 | Jun | 2023 | 0.002091 | 0.002091 | Momentary | FALSE | FALSE | Not_TMED_Event | 3070
BAYAMON | 2023-06-01 20:29 | 2023-06-02 08:30 | 1023 | 12:01 | P | DESCONECTIVO DEFECTUOSO | SE ENCONTRO MACHETE QUEMADO YCERRO N/O 9501-01 Y 9502-01 PARA LUEGO SECCIONALIZAR | B23060100221 | Additional_clients | Switch Failure | Include | Include | Equipment | 721 | 2023-06-01 | 737583 | keep | 0 | Jun | 2023 | 0.50236 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
UTUADO | 2023-06-01 20:46 | 2023-06-02 18:45 | 3 | 21:59 | P | DESGANCHE | 1 X 30 EN CORTE DE LINEA SE RETIRO RAMAS SOBRE LAS LINEAS | A23060100192 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1319 | 2023-06-01 | 3957 | keep | 0 | Jun | 2023 | 0.0026951 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-06-01 20:47 | 2023-06-02 11:40 | 80 | 14:53 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN C/L Y 1 X 45 EN C/L MAL TIEMPO FUERTES VIENTOS | B23060100352 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 893 | 2023-06-01 | 71440 | keep | 0 | Jun | 2023 | 0.048657 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-06-01 20:49 | 2023-06-02 01:53 | 132 | 5:04 | P | DESGANCHE | 1 X 65 EN C/L DESGANCHE | S23060100178 | New_Event | Vegetation Contact | Include | Include | Vegetation | 304 | 2023-06-01 | 40128 | keep | 0 | Jun | 2023 | 0.027331 | 8.9905e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 132
CAGUAS | 2023-06-01 20:57 | 2023-06-01 22:54 | 185 | 1:57 | P | ANIMAL | 1 X 100 EN CORTE DE LINEA CHANGO CRUZO FASE | C23060100175 | New_Event | Animals | Include | Include | Wildlife | 117 | 2023-06-01 | 21645 | keep | 0 | Jun | 2023 | 0.014742 | 0.000126 | Sustained | FALSE | FALSE | Not_TMED_Event | 185
BAYAMON | 2023-06-01 21:01 | 2023-06-02 08:36 | 6 | 11:35 | P | DESGANCHE | 1 X 10 EN XMR Y DESGANCHE | B23060100372 | New_Event | Vegetation Contact | Include | Include | Vegetation | 695 | 2023-06-01 | 4170 | keep | 0 | Jun | 2023 | 0.0028402 | 4.0866e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 6
ARECIBO | 2023-06-01 21:04 | 2023-06-01 23:01 | 130 | 1:57 | P | DESGANCHE | 1 X 80 Y 1 X 50 EN CORTE DE LINEA POR DESGANCH | A23060100200 | New_Event | Vegetation Contact | Include | Include | Vegetation | 117 | 2023-06-01 | 15210 | keep | 0 | Jun | 2023 | 0.010359 | 8.8542e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 130
SAN JUAN | 2023-06-01 21:11 | 2023-06-01 21:12 | 790 | 0:01 | T | CONDUCTOR ROTO O ABIERTO | RECERRO SU CARGA POR 1342-03 | S23060100181 | New_Event | Primary Wire Break | Include | Include | Equipment | 1 | 2023-06-01 | 790 | keep | 0 | Jun | 2023 | 0.00053807 | 0.00053807 | Momentary | FALSE | FALSE | Not_TMED_Event | 790
SAN JUAN | 2023-06-01 21:11 | 2023-06-01 21:12 | 29 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO LLEVA 1342-02, 1345-03 Y 1345-01 | S23060100181 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 29 | keep | 0 | Jun | 2023 | 1.9752e-05 | 1.9752e-05 | Momentary | FALSE | FALSE | Not_TMED_Event | 29
SAN JUAN | 2023-06-01 21:11 | 2023-06-01 21:12 | 660 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO SU CARGA POR 1342-03 | S23060100181 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 660 | keep | 0 | Jun | 2023 | 0.00044952 | 0.00044952 | Momentary | FALSE | FALSE | Not_TMED_Event | 660
SAN JUAN | 2023-06-01 21:11 | 2023-06-01 21:12 | 259 | 0:01 | T | ALIMENTADOR AMARRADO | RECERRO SU CARGA POR 1342-03 | S23060100181 | New_Event | Feeder Load Transferred | Include | Include | Other | 1 | 2023-06-01 | 259 | keep | 0 | Jun | 2023 | 0.0001764 | 0.0001764 | Momentary | FALSE | FALSE | Not_TMED_Event | 259
SAN JUAN | 2023-06-01 21:12 | 2023-06-01 21:49 | 139 | 0:37 | P | CONDUCTOR ROTO O ABIERTO | SE ABRIO CL Y SE LEVANTO CONDUCTOR PRIMARIO CARGA POR EL 1342-03 | S23053100208 | 1st_after_momentary | Primary Wire Break | Include | Include | Equipment | 37 | 2023-06-01 | 5143 | keep | 0 | Jun | 2023 | 0.0035029 | 9.4672e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 139
YAUCO | 2023-06-01 21:12 | 2023-06-02 00:16 | 2179 | 3:04 | T | MAL TIEMPO/LLUVIA O VIENTO | SE DESENRREDO CABLES CRUZADOS POR FUERTES VIENTOS | P23060100423 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 184 | 2023-06-01 | 400936 | keep | 0 | Jun | 2023 | 0.27308 | 0.0014841 | Sustained | FALSE | FALSE | Not_TMED_Event | 2179
BAYAMON | 2023-06-01 21:12 | 2023-06-02 13:27 | 5 | 16:15 | P | SECUNDARIA/DESGANCHE | SE ABRIO XMR Y PARA REALIZAR DESGANCHE SECUNDARIO Y 1X15 EN XMR | B23060100380 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 975 | 2023-06-01 | 4875 | keep | 0 | Jun | 2023 | 0.0033203 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
AGUADILLA | 2023-06-01 21:20 | 2023-06-02 01:11 | 300 | 3:51 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CORTE DE LINEA POR LLUVIAS | M23060100354 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 231 | 2023-06-01 | 69300 | keep | 0 | Jun | 2023 | 0.0472 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
AGUADILLA | 2023-06-01 21:21 | 2023-06-02 00:23 | 200 | 3:02 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 50 EN CORTE DE LINEA POR LLUVIA | A23060100210 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 182 | 2023-06-01 | 36400 | keep | 0 | Jun | 2023 | 0.024792 | 0.00013622 | Sustained | FALSE | FALSE | Not_TMED_Event | 200
YAUCO | 2023-06-01 21:24 | 2023-06-02 07:20 | 10 | 9:56 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 10 EN XMR MAL TIEMPO LLUVIAS | P23060100431 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 596 | 2023-06-01 | 5960 | keep | 0 | Jun | 2023 | 0.0040593 | 6.811e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 10
YAUCO | 2023-06-01 21:33 | 2023-06-01 21:34 | 2671 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE HIZO 2 OPERACIONES | P23060100442 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-01 | 2671 | keep | 0 | Jun | 2023 | 0.0018192 | 0.0018192 | Momentary | FALSE | FALSE | Not_TMED_Event | 2671
VEGA BAJA | 2023-06-01 21:35 | 2023-06-02 15:45 | 7 | 18:10 | P | DESGANCHE | 1 X 15 EN TRANSFORMADOR SE RETIRO RAMAS SOBRE LAS LINEAS | A23060100215 | New_Event | Vegetation Contact | Include | Include | Vegetation | 1090 | 2023-06-01 | 7630 | keep | 0 | Jun | 2023 | 0.0051968 | 4.7677e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 7
YAUCO | 2023-06-01 21:36 | 2023-06-02 02:30 | 2671 | 4:54 | T | ARBOL SOBRE LINEA | SE SECCIONALIZO AVERIA CABLES PARTIDOS POR ARBOL FID100119585 ENTRO 50% DE LOS CLIENTES | P23060100447 | New_Event | Vegetation Uprooted Tree | Include | Include | Vegetation | 294 | 2023-06-01 | 785274 | keep | 0 | Jun | 2023 | 0.53485 | 0.0018192 | Sustained | FALSE | FALSE | Not_TMED_Event | 2671
BAYAMON | 2023-06-01 21:36 | 2023-06-02 14:35 | 115 | 16:59 | P | ANIMAL | 1 X 80 EN C/L CRUCE POR AVE | B23060100394 | New_Event | Animals | Include | Include | Wildlife | 1019 | 2023-06-01 | 117185 | keep | 0 | Jun | 2023 | 0.079814 | 7.8326e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 115
SAN JUAN | 2023-06-01 21:40 | 2023-06-02 09:07 | 250 | 11:27 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN CONVERTIDOR MAL TIEMPO LLUVIA | S23060100185 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 687 | 2023-06-01 | 171750 | keep | 0 | Jun | 2023 | 0.11698 | 0.00017027 | Sustained | FALSE | FALSE | Not_TMED_Event | 250
BAYAMON | 2023-06-01 22:04 | 2023-06-01 22:25 | 400 | 0:21 | P | CONDUCTOR ROTO O ABIERTO | BY-230601-04 SE HACEN OPERACIONES EN EL CAMPO ABRIENDO MACHETES Y CERRANDO OTROS MACHETES 40% EN SERVICIO. | B23060100455 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 21 | 2023-06-01 | 8400 | keep | 0 | Jun | 2023 | 0.0057212 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
PONCE | 2023-06-01 22:17 | 2023-06-02 10:39 | 8 | 12:22 | P | CONDUCTOR ROTO O ABIERTO | SE REPARO BAJANTE PRIMARIO EN XMR | P23060100474 | New_Event | Primary Wire Break | Include | Include | Equipment | 742 | 2023-06-01 | 5936 | keep | 0 | Jun | 2023 | 0.004043 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
SAN JUAN | 2023-06-01 22:22 | 2023-06-02 10:59 | 80 | 12:37 | P | DESGANCHE | 1X100 EN C/L DESGANCHE | S23060100210 | New_Event | Vegetation Contact | Include | Include | Vegetation | 757 | 2023-06-01 | 60560 | keep | 0 | Jun | 2023 | 0.041247 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
BAYAMON | 2023-06-01 22:25 | 2023-06-01 23:24 | 300 | 0:59 | P | CONDUCTOR ROTO O ABIERTO | BY-230601-04 SE ENCONTRO PUENTE ABIERTO EN TRONCAL PERSONAL PIDE DISPARAR EL FEEDER PARA REALIZAR OPERACIONES YA CON UN 40% EN SERVICIO. | B23060100455 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 59 | 2023-06-01 | 17700 | keep | 0 | Jun | 2023 | 0.012055 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-01 22:25 | 2023-06-01 23:50 | 776 | 1:25 | P | CONDUCTOR ROTO O ABIERTO | SE REPARA LINEA PRIMARIA ROTA Y SE CIERRA MACHETES | A23060100169 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 85 | 2023-06-01 | 65960 | keep | 0 | Jun | 2023 | 0.044925 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CANOVANAS | 2023-06-01 22:31 | 2023-06-02 10:00 | 16 | 11:29 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 15 EN XMR REMPLAZO CAJA QUEMADA | R23060100094 | New_Event | Cutout Failure | Include | Include | Equipment | 689 | 2023-06-01 | 11024 | keep | 0 | Jun | 2023 | 0.0075084 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
AGUADILLA | 2023-06-01 22:40 | 2023-06-02 02:25 | 300 | 3:45 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 125 EN CORTE DE LINEA SE REEMPLAZO MASETILLA | A23060100241 | New_Event | Cutout Failure | Include | Include | Equipment | 225 | 2023-06-01 | 67500 | keep | 0 | Jun | 2023 | 0.045974 | 0.00020433 | Sustained | FALSE | FALSE | Not_TMED_Event | 300
PONCE | 2023-06-01 22:51 | 2023-06-02 09:35 | 75 | 10:44 | P | DESGANCHE | 2 X 80 EN C/L DESGANCHE | P23060100488 | New_Event | Vegetation Contact | Include | Include | Vegetation | 644 | 2023-06-01 | 48300 | keep | 0 | Jun | 2023 | 0.032897 | 5.1082e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 75
BAYAMON | 2023-06-01 23:05 | 2023-06-02 04:06 | 172 | 5:01 | P | ANIMAL | 1 X 65 EN C/L Y 1 X 50 EN PROVISIONAL AEREO CRUCE POR AVE | B23060100438 | New_Event | Animals | Include | Include | Wildlife | 301 | 2023-06-01 | 51772 | keep | 0 | Jun | 2023 | 0.035262 | 0.00011715 | Sustained | FALSE | FALSE | Not_TMED_Event | 172
AGUADILLA | 2023-06-01 23:15 | 2023-06-02 01:54 | 100 | 2:39 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 65 EN CORTE DE LINEA POR LLUVIA | M23060100395 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 159 | 2023-06-01 | 15900 | keep | 0 | Jun | 2023 | 0.010829 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BAYAMON | 2023-06-01 23:24 | 2023-06-01 23:47 | 1498 | 0:23 | T | CONDUCTOR ROTO O ABIERTO | BY-230601-04 SE SECIONALIZO ALIMENTADOR PARA CERRA PUENTE ABIERTO EN TRONCAL. 100% EN SERVICIO. | B23060100455 | Additional_clients | Primary Wire Break | Include | Include | Equipment | 23 | 2023-06-01 | 34454 | keep | 0 | Jun | 2023 | 0.023466 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
ARECIBO | 2023-06-01 23:37 | 2023-06-02 09:40 | 70 | 10:03 | P | DESGANCHE | 1 X 65 EN CORTE DE LINEA SE RETIRO RAMA | A23060100255 | New_Event | Vegetation Contact | Include | Include | Vegetation | 603 | 2023-06-01 | 42210 | keep | 0 | Jun | 2023 | 0.028749 | 4.7677e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 70
YAUCO | 2023-06-01 23:38 | 2023-06-02 09:04 | 25 | 9:26 | P | MAL TIEMPO/RAYOS | 1 X 40 EN CORTE DE LINEA 1 X 10 EN TRANSFORMADOR POR DESCARGAS ELECTRICAS | M23060100402 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 566 | 2023-06-01 | 14150 | keep | 0 | Jun | 2023 | 0.0096375 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
PONCE | 2023-06-01 23:42 | 2023-06-02 12:30 | 100 | 12:48 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 100 EN C/L MAL TIEMPO LLUVIAS | P23060100508 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 768 | 2023-06-01 | 76800 | keep | 0 | Jun | 2023 | 0.052308 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-01 23:50 | 2023-06-02 15:32 | 59 | 15:42 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1X65 EN C/L SE REMPLAZO CAJA PRIMARIA | S23060100225 | New_Event | Cutout Failure | Include | Include | Equipment | 942 | 2023-06-01 | 55578 | keep | 0 | Jun | 2023 | 0.037854 | 4.0185e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 59
BARRANQUITAS | 2023-06-01 23:50 | 2023-06-01 23:52 | 229 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO SE PROBO QUEDO EN SERVICIO | C23060100183 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-01 | 458 | keep | 0 | Jun | 2023 | 0.00031194 | 0.00015597 | Momentary | FALSE | FALSE | Not_TMED_Event | 229
BAYAMON | 2023-06-02 00:09 | 2023-06-02 02:42 | 949 | 2:33 | P | ANIMAL | 1 X 80 EN PROVISIONAL AEREO CRUCE POR AVE | B23060200003 | New_Event | Animals | Include | Include | Wildlife | 153 | 2023-06-02 | 145197 | keep | 0 | Jun | 2023 | 0.098893 | 0.00064636 | Sustained | FALSE | FALSE | Not_TMED_Event | 949
VEGA BAJA | 2023-06-02 00:28 | 2023-06-02 06:21 | 1500 | 5:53 | T | LINEA DE TRANSMISION 115KV | SE ABRIO MACHETES PARA SECCIONALIZAR LINEA 36100 SOBRE ALIMENTADOR TORRE DE LINEA 36100 EN EL PISO. | A23060200005 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 353 | 2023-06-02 | 529500 | keep | 0 | Jun | 2023 | 0.36064 | 0.0010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 1500
CANOVANAS | 2023-06-02 00:47 | 2023-06-02 04:07 | 30 | 3:20 | P | NO SE REPORTO CAUSA | 1 X 40 EN C/L NO CAUSA | R23060200002 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 200 | 2023-06-02 | 6000 | keep | 0 | Jun | 2023 | 0.0040866 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
PONCE | 2023-06-02 01:10 | 2023-06-02 07:30 | 100 | 6:20 | P | CONDUCTOR ROTO O ABIERTO | 2 X 65 EN C/L SE ELIMINO CABLE PARTIDO FUERA DE SERVICIO | P23060200027 | New_Event | Primary Wire Break | Include | Include | Equipment | 380 | 2023-06-02 | 38000 | keep | 0 | Jun | 2023 | 0.025882 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
SAN JUAN | 2023-06-02 01:12 | 2023-06-03 10:52 | 14 | 33:40 | P | TRANSFORMADOR AVERIADO | SE REMPLAZO XMR 75KVA POR 75KVA | S23060200002 | New_Event | Service Transformer Failure | Include | Include | Equipment | 2020 | 2023-06-02 | 28280 | keep | 0 | Jun | 2023 | 0.019261 | 9.5353e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 14
PONCE | 2023-06-02 02:15 | 2023-06-02 14:21 | 100 | 12:06 | P | MAL TIEMPO/RAYOS | SE CERRO PUENTE PRIMARIO INTERIOR DESCARGAS ELECTRICAS | P23060200051 | New_Event | Bad Weather (Lightning) | Include | Include | Lightning | 726 | 2023-06-02 | 72600 | keep | 0 | Jun | 2023 | 0.049448 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
VEGA BAJA | 2023-06-02 02:27 | 2023-06-02 12:10 | 20 | 9:43 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 60 EN C/L SE REMPLAZO PORTAFUSIBLE | B23060200019 | New_Event | Cutout Failure | Include | Include | Equipment | 583 | 2023-06-02 | 11660 | keep | 0 | Jun | 2023 | 0.0079416 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
YAUCO | 2023-06-02 02:30 | 2023-06-02 13:00 | 1161 | 10:30 | P | ARBOL SOBRE LINEA | SE CERRO MACHETES SE REPARO 3 ALAMBRES PRIMARIOS PARTIDOS POR ARBOL | P23060200055 | Partial_restoration | Vegetation Uprooted Tree | Include | Include | Vegetation | 630 | 2023-06-02 | 731430 | keep | 0 | Jun | 2023 | 0.49817 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
BAYAMON | 2023-06-02 02:38 | 2023-06-02 09:31 | 150 | 6:53 | P | DESGANCHE | 1 X 100 EN C/L DESGANCHE | B23060200028 | New_Event | Vegetation Contact | Include | Include | Vegetation | 413 | 2023-06-02 | 61950 | keep | 0 | Jun | 2023 | 0.042194 | 0.00010216 | Sustained | FALSE | FALSE | Not_TMED_Event | 150
SAN JUAN | 2023-06-02 02:45 | 2023-06-02 02:47 | 513 | 0:02 | P | ALIMENTADOR AMARRADO | DISPARO DE BKR 1118-10 CERRADO POR SCADA | S23060200004 | New_Event | Feeder Load Transferred | Include | Include | Other | 2 | 2023-06-02 | 1026 | keep | 0 | Jun | 2023 | 0.0006988 | 0.0003494 | Momentary | FALSE | FALSE | Not_TMED_Event | 513
SAN JUAN | 2023-06-02 02:45 | 2023-06-02 02:47 | 2782 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE BKR CERRADO POR SCADA LLEVA 20% 1111-01 | S23060200004 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-02 | 5564 | keep | 0 | Jun | 2023 | 0.0037896 | 0.0018948 | Momentary | FALSE | FALSE | Not_TMED_Event | 2782
SAN JUAN | 2023-06-02 03:04 | 2023-06-02 07:03 | 418 | 3:59 | T | CABLE SOTERRADO AVERIADO | SE TRANSFIRIO PARTE DE SU CARGA AL 1014-16 PARA SECCIONALIZAR POSIBLE AVERIA SJ-230602-01 - 95% EN SERVICIO | S23060200007 | New_Event | UG Cable Fault | Include | Include | Equipment | 239 | 2023-06-02 | 99902 | keep | 0 | Jun | 2023 | 0.068043 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
CANOVANAS | 2023-06-02 03:40 | 2023-06-02 15:31 | 8 | 11:51 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 65 EN C/L SE REMPLAZO CAJA PRIMARIA. | R23060200009 | New_Event | Cutout Failure | Include | Include | Equipment | 711 | 2023-06-02 | 5688 | keep | 0 | Jun | 2023 | 0.0038741 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
BARRANQUITAS | 2023-06-02 04:32 | 2023-06-02 10:40 | 16 | 6:08 | P | CONDUCTOR ROTO O ABIERTO | 1 X 8 EN XMR SE REEMPLAZO BAJANTE DE LINEA A CAJA PRIMARIA DE XMR | C23060200004 | New_Event | Primary Wire Break | Include | Include | Equipment | 368 | 2023-06-02 | 5888 | keep | 0 | Jun | 2023 | 0.0040103 | 1.0898e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 16
MAYAGÃœEZ | 2023-06-02 05:30 | 2023-06-02 12:30 | 15 | 7:00 | P | CONDUCTOR SECUNDARIO ARRIADO O CRUZADO | 1 X 20 EN TRANSFORMADOR SE REPARO LINEA SECUNDARIA CRUZADA | P23060200087 | New_Event | Secondary To Secondary Contact (Including Neutral) | Include | Include | Equipment | 420 | 2023-06-02 | 6300 | keep | 0 | Jun | 2023 | 0.0042909 | 1.0216e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 15
GUAYAMA | 2023-06-02 05:54 | 2023-06-02 05:55 | 449 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE NO CAUSA | P23060200100 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 449 | keep | 0 | Jun | 2023 | 0.00030581 | 0.00030581 | Momentary | FALSE | FALSE | Not_TMED_Event | 449
BARRANQUITAS | 2023-06-02 06:00 | 2023-06-02 11:15 | 29 | 5:15 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23060200007 | New_Event | Vegetation Contact | Include | Include | Vegetation | 315 | 2023-06-02 | 9135 | keep | 0 | Jun | 2023 | 0.0062218 | 1.9752e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 29
UTUADO | 2023-06-02 06:08 | 2023-06-02 11:45 | 40 | 5:37 | P | CONDUCTOR ARRIADO O CRUZADO | 1 X 40 EN CORTE DE LINEA SE RETEZO LINEAS | A23060200032 | New_Event | Primary To Primary Contact | Include | Include | Equipment | 337 | 2023-06-02 | 13480 | keep | 0 | Jun | 2023 | 0.0091812 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CANOVANAS | 2023-06-02 06:13 | 2023-06-02 08:53 | 36 | 2:40 | P | DESGANCHE | 2 X 50 EN C/L | R23060200013 | New_Event | Vegetation Contact | Include | Include | Vegetation | 160 | 2023-06-02 | 5760 | keep | 0 | Jun | 2023 | 0.0039231 | 2.4519e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 36
GUAYAMA | 2023-06-02 06:16 | 2023-06-02 09:00 | 8 | 2:44 | P | ANIMAL | 1 X 65 EN C/L AVE CRUZO LINEAS | P23060200118 | New_Event | Animals | Include | Include | Wildlife | 164 | 2023-06-02 | 1312 | keep | 0 | Jun | 2023 | 0.0008936 | 5.4488e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 8
CAGUAS | 2023-06-02 06:18 | 2023-06-02 06:19 | 851 | 0:01 | P | NO SE REPORTO CAUSA | RECIERRE DE INTERRUPTOR 50% X 3103-02 | C23060200010 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 851 | keep | 0 | Jun | 2023 | 0.00057961 | 0.00057961 | Momentary | FALSE | FALSE | Not_TMED_Event | 851
VEGA BAJA | 2023-06-02 06:21 | 2023-06-02 09:51 | 750 | 3:30 | P | LINEA DE TRANSMISION 115KV | REPARAR ALAMBRE PARTIDO Y REMPLAZO DE TORRE LINEA 36100 SOBRE ALIMENTADOR | A23060200038 | New_Event | 115 kV Transmission Line Source | Include | Include | Power supply | 210 | 2023-06-02 | 157500 | keep | 0 | Jun | 2023 | 0.10727 | 0.00051082 | Sustained | FALSE | FALSE | Not_TMED_Event | 750
SAN JUAN | 2023-06-02 07:03 | 2023-06-02 07:29 | 20 | 0:26 | P | CABLE SOTERRADO AVERIADO | SE REALIZARON OPERACIONES DE CAMPO SJ-230602-01 - 100% EN SERVICIO NO SE HABIA ENCONTRADO LA AVERIA (HASTA ESE MOMENTO) | S23060200007 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 26 | 2023-06-02 | 520 | keep | 0 | Jun | 2023 | 0.00035417 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
YAUCO | 2023-06-02 07:05 | 2023-06-02 11:32 | 30 | 4:27 | P | CONDUCTOR ROTO O ABIERTO | SE CERRO PUENTE PRIMARIO SIGUEN SALIENDO DE MAYAGÃœEZ LOS EVENTOS | M23060100014 | New_Event | Primary Wire Break | Include | Include | Equipment | 267 | 2023-06-02 | 8010 | keep | 0 | Jun | 2023 | 0.0054556 | 2.0433e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 30
BARRANQUITAS | 2023-06-02 07:08 | 2023-06-02 15:25 | 20 | 8:17 | P | DESGANCHE | 1 X 40 EN C/L DESGANCHE | C23060200016 | New_Event | Vegetation Contact | Include | Include | Vegetation | 497 | 2023-06-02 | 9940 | keep | 0 | Jun | 2023 | 0.0067701 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20
MAYAGÃœEZ | 2023-06-02 07:11 | 2023-06-02 10:53 | 25 | 3:42 | P | MAL TIEMPO/LLUVIA O VIENTO | 2 X 100 EN CORTE DE LINEA FUERTE VIENTO EN EL AREA | P23060200147 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 222 | 2023-06-02 | 5550 | keep | 0 | Jun | 2023 | 0.0037801 | 1.7027e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 25
CANOVANAS | 2023-06-02 07:14 | 2023-06-02 07:16 | 2891 | 0:02 | T | NO SE REPORTO CAUSA | DISPARO DE INTERRUPTOR NO RECERRO CERRADO X CONTROL | R23060200015 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 2 | 2023-06-02 | 5782 | keep | 0 | Jun | 2023 | 0.0039381 | 0.001969 | Momentary | FALSE | FALSE | Not_TMED_Event | 2891
CAGUAS | 2023-06-02 07:16 | 2023-06-02 08:52 | 40 | 1:36 | P | ANIMAL | 1 X 65 EN C/L CRUCE X AVE | C23060200018 | New_Event | Animals | Include | Include | Wildlife | 96 | 2023-06-02 | 3840 | keep | 0 | Jun | 2023 | 0.0026154 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 474 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 20% POR 3604-06 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 474 | keep | 0 | Jun | 2023 | 0.00032284 | 0.00032284 | Momentary | FALSE | FALSE | Not_TMED_Event | 474
BARRANQUITAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 1565 | keep | 0 | Jun | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 976 | keep | 0 | Jun | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200020 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 548 | keep | 0 | Jun | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 315 | keep | 0 | Jun | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200021 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 870 | keep | 0 | Jun | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 LLEVA 20% DEL 3010-01 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 2906 | keep | 0 | Jun | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-06-02 07:24 | 2023-06-02 07:25 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200022 | New_Event | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 2343 | keep | 0 | Jun | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
PONCE | 2023-06-02 07:30 | 2023-06-02 11:32 | 80 | 4:02 | P | CONDUCTOR ROTO O ABIERTO | 1 X 100 EN C/L RELACIONADO A CASO ANTERIOR DE ALAMBRE PARTIDO | P23060200171 | Partial_restoration | Primary Wire Break | Include | Include | Equipment | 242 | 2023-06-02 | 19360 | keep | 0 | Jun | 2023 | 0.013186 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
AGUADILLA | 2023-06-02 07:42 | 2023-06-02 13:30 | 40 | 5:48 | P | NO SE REPORTO CAUSA | 1 X 50 EN CORTE DE LINEA NO SE ENCONTRO CAUSA | M23060200023 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 348 | 2023-06-02 | 13920 | keep | 0 | Jun | 2023 | 0.0094808 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
VEGA BAJA | 2023-06-02 07:48 | 2023-06-02 07:50 | 1494 | 0:02 | T | CAJA PRIMARIA DEFECTUOSA O QUEMADA | DISPARO DE INTERRUPTOR NO RECERRO CON RECIERRE EN ON CERRADO POR SCADA | A23060200052 | New_Event | Cutout Failure | Include | Include | Equipment | 2 | 2023-06-02 | 2988 | keep | 0 | Jun | 2023 | 0.0020351 | 0.0010176 | Momentary | FALSE | FALSE | Not_TMED_Event | 1494
VEGA BAJA | 2023-06-02 07:50 | 2023-06-02 13:10 | 40 | 5:20 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 40 EN CORTE DE LINEA Y 1 X 15 EN TRANSFORMADOR SE REMPLAZO CAJA QUEMADA | A23060200061 | 1st_after_momentary | Cutout Failure | Include | Include | Equipment | 320 | 2023-06-02 | 12800 | keep | 0 | Jun | 2023 | 0.008718 | 2.7244e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 40
CAGUAS | 2023-06-02 07:58 | 2023-06-02 12:52 | 1 | 4:54 | P | DESGANCHE | 1 X 80 EN C/L DESGANCHE EVENTO TRANSFERIDO DE PONCE. | P23060200184 | New_Event | Vegetation Contact | Include | Include | Vegetation | 294 | 2023-06-02 | 294 | keep | 0 | Jun | 2023 | 0.00020024 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-02 07:59 | 2023-06-02 10:12 | 227 | 2:13 | P | NO SE REPORTO CAUSA | 2 X 100 EN C/L | B23060200079 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 133 | 2023-06-02 | 30191 | keep | 0 | Jun | 2023 | 0.020563 | 0.00015461 | Sustained | FALSE | FALSE | Not_TMED_Event | 227
FAJARDO | 2023-06-02 08:01 | 2023-06-02 08:51 | 66 | 0:50 | P | CAJA PRIMARIA DEFECTUOSA O QUEMADA | 1 X 30 EN C/L REMPLAZO CAJA QUEMADA | R23060200027 | New_Event | Cutout Failure | Include | Include | Equipment | 50 | 2023-06-02 | 3300 | keep | 0 | Jun | 2023 | 0.0022476 | 4.4952e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 66
PONCE | 2023-06-02 08:01 | 2023-06-02 09:51 | 100 | 1:50 | P | ANIMAL | 1 X 140 EN C/L ANIMAL CRUZO LINEAS | P23060200186 | New_Event | Animals | Include | Include | Wildlife | 110 | 2023-06-02 | 11000 | keep | 0 | Jun | 2023 | 0.007492 | 6.811e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 100
BARRANQUITAS | 2023-06-02 08:05 | 2023-06-02 15:21 | 4 | 7:16 | P | MAL TIEMPO/LLUVIA O VIENTO | 1 X 40 EN C/L MAL TIEMPO FUERTES VIENTOS EVENTO TRANSFERIDO | P23060200188 | New_Event | Bad Weather (Rain & Wind) | Include | Include | Weather | 436 | 2023-06-02 | 1744 | keep | 0 | Jun | 2023 | 0.0011878 | 2.7244e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 4
SAN JUAN | 2023-06-02 08:07 | 2023-06-02 08:08 | 10211 | 0:01 | T | NO SE REPORTO CAUSA | SE CERRO POR CONTROL | S23060200045 | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 10211 | keep | 0 | Jun | 2023 | 0.0069547 | 0.0069547 | Momentary | FALSE | FALSE | Not_TMED_Event | 10211
HUMACAO | 2023-06-02 08:07 | 2023-06-02 10:55 | 1 | 2:48 | P | CAUSAS EXTERNAS | 2 X 40 EN C/L PERSONA AJENA A LUMA CORTO RAMA Y CAYO SOBRE LA LINEA | C23060200027 | New_Event | Damage From Public | Include | Include | Public | 168 | 2023-06-02 | 168 | keep | 0 | Jun | 2023 | 0.00011442 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
BARRANQUITAS | 2023-06-02 08:15 | 2023-06-02 16:00 | 1 | 7:45 | P | SECUNDARIA/DESGANCHE | 1 X 10 EN XMR DESGANCHE SECUNDARIO | C23060200028 | New_Event | Secondary Vegetation | Include | Include | Vegetation | 465 | 2023-06-02 | 465 | keep | 0 | Jun | 2023 | 0.00031671 | 6.811e-07 | Sustained | FALSE | FALSE | Not_TMED_Event | 1
VEGA BAJA | 2023-06-02 08:15 | 2023-06-02 14:30 | 80 | 6:15 | P | ANIMAL | 1 X 50 EN CORTE DE LINEA AVE CRUZO LINEAS | A23060200060 | New_Event | Animals | Include | Include | Wildlife | 375 | 2023-06-02 | 30000 | keep | 0 | Jun | 2023 | 0.020433 | 5.4488e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 80
SAN JUAN | 2023-06-02 08:30 | 2023-06-02 08:46 | 418 | 0:16 | T | CABLE SOTERRADO AVERIADO | INTERRUPTOR SE VOLVIO A DISPARAR DURANTE OPERACIONES DE CAMPO PARA NORMALIZAR LAS CARGAS TRANSFERIDAS SJ-230602-01 | S23060200007 | New_Event | UG Cable Fault | Include | Include | Equipment | 16 | 2023-06-02 | 6688 | keep | 0 | Jun | 2023 | 0.0045552 | 0.0002847 | Sustained | FALSE | FALSE | Not_TMED_Event | 418
AGUADILLA | 2023-06-02 08:30 | 2023-06-02 09:30 | 5 | 1:00 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO CAJAS EN TRANSFORMADOR PARA REMPLAZO BAJANTES SECUNDARIOS | P23060200216 | New_Event | Secondary Wire Break | Include | Include | Equipment | 60 | 2023-06-02 | 300 | keep | 0 | Jun | 2023 | 0.00020433 | 3.4055e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 5
BAYAMON | 2023-06-02 08:30 | 2023-06-02 10:25 | 614 | 1:55 | P | DESCONECTIVO DEFECTUOSO | SE SECCIONALIZO ALIMENTADOR Y SE REMPLAZO MACHETE QUEMADO | B23060100221 | Partial_restoration | Switch Failure | Include | Include | Equipment | 115 | 2023-06-02 | 70610 | keep | 0 | Jun | 2023 | 0.048092 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
SAN JUAN | 2023-06-02 08:35 | 2023-06-02 15:24 | 12 | 6:49 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | 1X20 EN XMR SE REPARO/LEVANTO CONDUCTOR SECUNDARIO DEL SUELO TRASPATIO | S23060200064 | New_Event | Secondary Wire Break | Include | Include | Equipment | 409 | 2023-06-02 | 4908 | keep | 0 | Jun | 2023 | 0.0033428 | 8.1731e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 12
SAN JUAN | 2023-06-02 08:46 | 2023-06-02 09:17 | 376 | 0:31 | P | CABLE SOTERRADO AVERIADO | SE ENCONTRO TRAMO SOTERRADO AVERIADO DEL SU-13 @ MH-17A SJ-230602-01 - 90% EN SERVICIO | S23060200007 | Partial_restoration | UG Cable Fault | Include | Include | Equipment | 31 | 2023-06-02 | 11656 | keep | 0 | Jun | 2023 | 0.0079388 | 0 | Sustained | FALSE | FALSE | Not_TMED_Event | 0
CAGUAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 474 | 0:01 | P | LINEA DE TRANSMISION 38KV | DISPARO DE LINEA 0800 20% POR 3604-06 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200065 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 474 | keep | 0 | Jun | 2023 | 0.00032284 | 0.00032284 | Momentary | FALSE | FALSE | Not_TMED_Event | 474
BARRANQUITAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 1565 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200063 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 1565 | keep | 0 | Jun | 2023 | 0.0010659 | 0.0010659 | Momentary | FALSE | FALSE | Not_TMED_Event | 1565
BARRANQUITAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 976 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200063 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 976 | keep | 0 | Jun | 2023 | 0.00066475 | 0.00066475 | Momentary | FALSE | FALSE | Not_TMED_Event | 976
BARRANQUITAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 548 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200063 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 548 | keep | 0 | Jun | 2023 | 0.00037324 | 0.00037324 | Momentary | FALSE | FALSE | Not_TMED_Event | 548
BARRANQUITAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 315 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 315 | keep | 0 | Jun | 2023 | 0.00021455 | 0.00021455 | Momentary | FALSE | FALSE | Not_TMED_Event | 315
BARRANQUITAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 870 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200064 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 870 | keep | 0 | Jun | 2023 | 0.00059255 | 0.00059255 | Momentary | FALSE | FALSE | Not_TMED_Event | 870
BARRANQUITAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 2906 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 LLEVA 20% DEL 3010-01 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200065 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 2906 | keep | 0 | Jun | 2023 | 0.0019793 | 0.0019793 | Momentary | FALSE | FALSE | Not_TMED_Event | 2906
BARRANQUITAS | 2023-06-02 08:50 | 2023-06-02 08:51 | 2343 | 0:01 | S | LINEA DE TRANSMISION 38KV | RECIERRE DE LA LINEA 0800 VARIOS PUNTOS DE DESGANCHE CRITICO EN LA CARR #1 Y CARR #787 BARRIO BEATRIZ | C23060200065 | 1st_after_momentary | 38 kV Transmission Line Source | Include | Include | Power supply | 1 | 2023-06-02 | 2343 | keep | 0 | Jun | 2023 | 0.0015958 | 0.0015958 | Momentary | FALSE | FALSE | Not_TMED_Event | 2343
CANOVANAS | 2023-06-02 08:51 | 2023-06-02 10:58 | 45 | 2:07 | P | DESGANCHE | 1 X 25 EN C/L | R23060200036 | New_Event | Vegetation Contact | Include | Include | Vegetation | 127 | 2023-06-02 | 5715 | keep | 0 | Jun | 2023 | 0.0038925 | 3.0649e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 45
SAN JUAN | 2023-06-02 08:56 | 2023-06-02 10:28 | 3 | 1:32 | P | DESGANCHE | 1X80 EN C/L DESGANCHE (EVENTO TRANSFERIDO DE REGION PONCE) | P23060200239 | New_Event | Vegetation Contact | Include | Include | Vegetation | 92 | 2023-06-02 | 276 | keep | 0 | Jun | 2023 | 0.00018798 | 2.0433e-06 | Sustained | FALSE | FALSE | Not_TMED_Event | 3
BAYAMON | 2023-06-02 09:03 | 2023-06-02 11:15 | 60 | 2:12 | P | DESGANCHE | 3 X 50 EN C/L DESGANCHE | B23060200115 | New_Event | Vegetation Contact | Include | Include | Vegetation | 132 | 2023-06-02 | 7920 | keep | 0 | Jun | 2023 | 0.0053943 | 4.0866e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 60
BAYAMON | 2023-06-02 09:04 | 2023-06-02 09:05 | 1210 | 0:01 | T | NO SE REPORTO CAUSA | RECIERRE | B2306020000X | New_Event | No Probable Cause Reported | Include | Include | Unknown | 1 | 2023-06-02 | 1210 | keep | 0 | Jun | 2023 | 0.00082413 | 0.00082413 | Momentary | FALSE | FALSE | Not_TMED_Event | 1210
BAYAMON | 2023-06-02 09:12 | 2023-06-02 11:06 | 20 | 1:54 | P | CONDUCTOR SECUNDARIO ROTO, ABIERTO O DEFECTUOSO | SE ABRIO XMR Y SE REPARO SECUNDARIA | B23060200120 | New_Event | Secondary Wire Break | Include | Include | Equipment | 114 | 2023-06-02 | 2280 | keep | 0 | Jun | 2023 | 0.0015529 | 1.3622e-05 | Sustained | FALSE | FALSE | Not_TMED_Event | 20